## Cleaned Data
ActionTaken | Address | AssetLabel | CauseCommunity | CauseEnvironment | CausePre | CauseTechnical | CauseWorkP | ContactType | CorrectProtection | EventDescription | FailedAssets | FailedExplosion | FailedOilFilled | FailedOtherAssets | FailedOtherAssetsOther | FeederNumber | IncidentCause | IncidentConsequence | IncidentDatetime | IncidentFireFFactorReportable | IncidentFireSeverity | IncidentID | IncidentLocationType | IncidentLocationTypeOther | IncidentNumber | IncidentType | Lat | Long | MadeSafe | NetworkType | Status | SubmissionID | SubmittedDateTimeString | Voltage | WeatherStation | Postcode | Locality | Category
Crew isolated supply and undertook repairs | PARA PARK, 1490 HENDY MAIN ROAD, PARAPARAP VIC 3240 |  |  |  |  | Earth fault |  |  |  | A nearby customer reported sparking of electrical lines at the above location. On attendance the crew found that a High Voltage ABC conductor had faulted midspan resulting in a ground fire (Approx 30 sqm). There were no reported injuries. | Conductor (ABC) | 0 | 0 | 0 |  |  | HVABC cable faulted midspan | Grassfire | 42134.8583 | 1 | Small: 10 - 1000 sq.m | 56 | Roadway |  | 20151009PWA_1 | Infrastructure (network-based) | -38.289 | 144.1915 | 1 | Powercor | Report | 1030 | 0.00075 | 22kV AC | Avalon Airport | 3240 | Paraparap | OH Cable
Crew undertook repairs | 1154-1198 CHRISTIES ROAD, RAVENHALL VIC 3023 |  | Working too close to underground cables | [6 empty] | A contractor reported that he had contacted an earthing cable while excavating a trench at the above location. On arrival the crew found that the contractor (Dennis James, Ph: 0418 390 584) was digging a trench and contacted an earthing cable, causing damage to the cable. There were no reported injuries or third party property damages. | No failed asset | 0 | 0 | 0 |  |  | Contractor contacted earthing conductor | No Go Zone (contact) | 42195.4583 |  |  | 64 |  |  | 20151012PWA_5 | Infrastructure (network-based) | -37.7674 | 144.7385 | 1 | Powercor | Report | 96 | 0.027419 | Earthing cable | Laverton Raaf | 3023 | Ravenhall | Dug up
Crew isolated supply and undertook repairs | 326 DUNBARS ROAD, PETERBOROUGH VIC 3270 |  |  |  |  | Corrosion |  |  | 1 | A field crew attending an outage found that a 22kV conductor had broken due to rust at a connecting sleeve and had fallen to the ground where one end remained alive due to a high impedance backfeed through downline transformer windings. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Conductor broke due to rust | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42287.3583 |  |  | 67 | Agricultural |  | 20151013PWA_1 | Infrastructure (network-based) | -38.5866 | 142.9011 | 1 | Powercor | Report | 86 | 0.031483 | 22kV AC | Warrnambool Airport Ndb | 3270 | Peterborough | Connection
Crew undertook repairs | 41-49 BANK STREET, SOUTH MELBOURNE VIC 3205 |  | Vandalism | [5 empty] | 1 | Interfere and vandalism in substation. Unknown third parties used an unknown object to interfere with two HV fuses which blew in an Indoor Substation. â€˜Little Bank â€“ Kingswayâ€™ Indoor substation affected. Also, Secure Parking at the rear of 19-29 Bank Street had theft and vandalism of their Ticket Machine in conjunction with this substation interfere and vandalism. | Indoor | 0 | 2 | 0 |  |  | Vandalism | Loss of supply;Damage to network assets | 42104.4375 |  |  | 73 |  |  | 20151015PWA_4 | Infrastructure (network-based) | -37.8324 | 144.9685 | 1 | CitiPower | Report | 92 | 0.0026262 | 22kV AC | Essendon Airport | 3205 | South Melbourne | Other
Crew isolated supply and undertook repairs | 199 WILSONS ROAD, WHITTINGTON VIC 3219 |  | Vehicle | [6 empty] | A nearby customer reported that a high load had pulled down wires at the above location. On arrival the crew found that a LV service cable had been contacted by an unknown vehicle, breaking the cable which fell to the ground. There were no reported injuries or third party property damages. Following repairs the cable was measured at 5.3m at the kerb. | Service conductor | 0 | 0 | 0 |  |  | Unknown high load contacted LV service cable | No Go Zone (contact);Damage to network assets | 42134.6118 |  |  | 77 |  |  | 20151016PWA_1 | Infrastructure (network-based) | -38.1774 | 144.3905 | 1 | Powercor | Report | 98 | 0.0091088 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Whittington | Vehicle
A faults crew attended and replaced the red phase 6amp Boric Acid HV fuse restoring supply to the 4 customers supplied from the substation. | 2754 FRANKSTON-FLINDERS ROAD, BALNARRING VIC 3926 |  |  |  |  | Age |  |  | 1 | Customers supplied from "Flinders-Pallant" substation advised of a loss of supply. A HV fuse candled at "Flinders-Pallant" substation that caused a loss of supply to customers who reside in Frankston-Flinders Road, Balnarring. | Boric acid | 0 | 0 | 0 |  | HGS 23 | HV fuse candled. | Loss of supply | 16/10/2015 8:51 |  |  | 79 | Residential |  | 20151016UTD_1 | Infrastructure (network-based) | -38.3564 | 145.15 | 1 | United Energy Distribution | Report | 100 | 0.037971 | 22kV AC | Moorabbin Airport | 3926 | Balnarring | Fuse
The overhead service was removed by the faults crew and the site made safe. A photo was taken of the demolition companies signage on the front fence. | 110 SPRINGFIELD ROAD, BLACKBURN NORTH VIC 3130 | LIS 7039411 | Unauthorised work | [5 empty] | 2 | Caller reports there is a electricity service line that has been wrapped around a pole outside a demolished property. An overhead service that supplied 110 Springfield Road Blackburn, North was removed from a property being demolished and left coiled up around pole No. LIS 7039411. The service cable was alive and coiled with the Optus cable. The electricity meter/s could not be found at the site. Demolisher - Sustainable Demolition 1300 123 366 www.sustainabledemolition.com.au | Service conductor | 0 | 0 | 0 |  |  | An overhead service that supplied 110 Springfield Road Blackburn, North was removed by a demolition company and left coiled up around pole No. LIS 7039411. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/10/2015 15:00 |  |  | 80 | Roadway |  | 20151016UTD_2 | Infrastructure (network-based) | -37.8106 | 145.1539 | 1 | United Energy Distribution | Report | 108 | 0.029156 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn North | Other
Isolated and Made Safe | 328 TRARALGON-BALOOK ROAD, CALLIGNEE VIC 3844 |  |  |  |  | Insulator |  |  |  | Burnt Out 5A EDO Fuse Tube at Sunday Rd 1, Lis 2605640. No Damage. | EDO fuse | 0 | 0 | 0 |  |  | Burnt Out 5A EDO Fuse Tube. | Pole-top fire | 13/10/2015 21:00 |  | Negligible: no ground fire | 109 |  |  | 20151022SPN_3 | Infrastructure (network-based) | -38.3163 | 146.5656 | 1 | AusNet Services Distribution | Report | 168 | 0.032828 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Callignee | Fuse
The attending fault crew had isolated the supply due to the bare conductors on the ground and suspect HVI, awaiting support from LEI to assess damage. Attending LEI inspected affected properties on Stud Rd (500, 616 and VicRoads traffic signal control cabinet) and found evidence of HV injection. No-access letters left for 500 Stud Rd, Vic Roads informed of damage and damage report left with owner of 616 Stud Rd. These were the only customers connected and subsequently affected by a HVI on the circuit. Control Room (CEOT) notified. Pole replaced, conductors reinstated and supply restored. | 500 STUD ROAD, WANTIRNA SOUTH VIC 3152 |  | Vehicle | Precipitation |  | HV injection |  | Three phase | 1 | IMS 218704. A vehicle incident just past 500 Stud Rd, caused the car to collide with an AusNet Services pole, bringing down entire pole and all bare HV and LV conductors. Incident resulted in HVI damage to two properties and a VicRoads traffic signal control cabinet. BRA21 feeder CB operated. At time of the incident there was inclement weather and the roads were wet. | Pole (wood) | 0 | 0 | 0 |  | BRA21 | Car hit pole in Stud Rd causing HV injection damage to properties. Inclement weather and wet roads. | HV injection | 20/10/2015 19:35 |  |  | 111 | Roadway |  | 20151022SPN_5 | Infrastructure (network-based) | -37.8824 | 145.2327 | 1 | AusNet Services Distribution | Report | 167 | 0.023266 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3152 | Wantirna South | Vehicle
Downer contacted United Energy who discussed the breach with ESV and a site visit was to be arranged with a WorkSafe representative for that area. | 52 FOURTH STREET, BLACK ROCK VIC 3193 |  | Building too close or within the No Go Zone | [5 empty] | 2 | No Go Zone infringement. An Extec No Go Zone Co-Ordinator advised Downer of a building under construction that has infringed into a No Go Zone. Photos were provided to Downer that demonstrate the balcony is located approximately 1.5m from the HV road side conductor. A Permit to Work (No. 008288) was issued to the builder who was instructed to cease all works immediately including any scaffolding construction on the first floor. | No failed asset | 0 | 0 | 0 |  |  | Building under construction that has infringed into a No Go Zone. | No Go Zone (no contact) | 16/10/2015 15:00 |  |  | 114 | Residential |  | 20151023UTD_1 | Infrastructure (network-based) | -37.9812 | 145.0244 | 1 | United Energy Distribution | Report | 169 | 0.0061412 | 11kV AC | Moorabbin Airport | 3193 | Black Rock | Other
The faults crew completed a NST at the POA that failed. They continued to check the connections at the pole end and identified a neutral connection was loose at a IPC. The faults crew re-terminated the neutral connection and the LEI arrived a short time afterwards and tested the installation with 0.05v measured between an independent earth to the kitchen taps and sink that confirmed the fault had been rectified. | 13 WESTALL ROAD, CLAYTON SOUTH VIC 3169 |  |  |  |  | Neutral fault;Electrical breakdown | Poor workmanship | Phase to earth | 2 | AMI meter reporting under voltage events. AMI technician have requested a faults crew to check connections at the pole, POA, complete a NST and the neutral connection at the transformer if required. A faults crew were on site following an alarm from a smart meter with a report of a under voltage event. Upon arrival, the occupier advised the crew that electric shocks have been received from the kitchen taps at the premise for some time. The faults crew contacted the Dispatch and requested that a LEI attend and assist to complete an investigation into the cause. | Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | The fault crew identified a neutral connection was loose at a IPC at the pole end. | Minor shock | 20/10/2015 11:30 |  |  | 118 | Residential |  | 20151026UTD_1 | Infrastructure (network-based) | -37.9416 | 145.1397 | 1 | United Energy Distribution | Report | 157 | 0.0082743 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Connection
Crew isolated supply and undertook repairs | TWO BRIDGES ROAD, ROKEWOOD VIC 3330 |  |  | Fallen | Unlikely |  |  | Three phase | 1 | VicFire reporting a grass fire and wires down at the location. On arrival the crew found that a privately owned pine tree (from outside the clearance space) had fallen across an adjacent 22kV line causing one conductor to break and fall to the ground and the other two conductors to fall to the ground intact resulting in a ground fire (Approx 5m x 50m) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 27/10/2015 8:59 | 1 | Medium: 1000 sq.m - 10 ha | 124 | Roadway |  | 20151028PWA_1 | Infrastructure (network-based) | -37.933 | 143.6856 | 1 | Powercor | Report | 272 | 0.02864 | 22kV AC | Ballarat Aerodrome | 3330 | Rokewood | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the HV intermediate, LV strain pole was replaced under Access Authority conditions. | 37 NELLBERN ROAD, MOORABBIN VIC 3189 | 1816591 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 2114hrs on 26/10/2015, 22kV feeder HT 08 circuit breaker reclosed to lockout affecting 210 customers. During light drizzly conditions, a pole fire occurred on a HV intermediate, LV strain pole (LIS No. 1816591) located outside 37 Nelburn Road, Moorabbin 1 pole east of Bignell Road. The pole top was severely damaged and the pole was required to be replaced. | Pole (wood);Pole top | 0 | 0 | 0 |  | HT 08 | During light drizzly conditions, a pole fire occurred on a HV intermediate, LV strain pole (LIS No. 1816591) located outside 37 Nelburn Road, Moorabbin. | Pole-top fire;Loss of supply | 26/10/2015 21:14 |  | Negligible: no ground fire | 130 | Roadway |  | 20151029UTD_2 | Infrastructure (network-based) | -37.9399 | 145.0678 | 1 | United Energy Distribution | Report | 183 | 0.0016678 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the HV intermediate crossarm was replaced under Access Authority conditions prior to supply being restored. The construction crew installed two sets of HV mid span isolators to maintain supply to the shopping area. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 58 SPRINGFIELD ROAD, BOX HILL NORTH VIC 3129 | 7028094 |  |  |  | Age;HV injection |  |  | 1 | At 12.37PM on 23/10/2015, 22kV feeder DC 07 circuit breaker successfully reclosed and held. A HV intermediate crossarm failed due to deterioration on pole No. LIS 7028094 located outside 58 Springfield Road, Box Hill North and came to rest on the LV crossarm. The reduced clearances between the HV and LV conductors enabled two birds to contact each other and a high voltage injection to occur. The faults crew requested a LEI to attend and investigate for any possible damage to customers installations supplied from "Fortune-Ashley" substation. The LEI confirmed a high voltage injection occurred (BWD 1518) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Crossarm (wood);Aluminium | 0 | 0 | 0 |  | DC 07 | A HV intermediate crossarm failed due to deterioration on a staked pole. | HV injection;Loss of supply;Less than $50k damage | 23/10/2015 12:27 |  |  | 131 | Roadway |  | 20151029UTD_3 | Infrastructure (network-based) | -37.8092 | 145.1386 | 1 | United Energy Distribution | Report | 184 | 0.04078 | 22kV AC | Moorabbin Airport | 3129 | Box Hill North | Crossarm
Isolated & made area safe, made repairs to overhead conductor. Fire put out & conductor restored with new wrap on, conductor condition considered good for restoration. | 1015 FAIRBANK ROAD, FAIRBANK VIC 3951 | 2004259 |  |  |  | Corrosion |  | Phase to earth | 1 | 3/12 steel HV conductor wrap-on termination broke at crossarm, causing the HV conductor to drop to the ground resulting in a small grass fire on edge of road embankment of approximate size 43 metres long up to 2 metres wide. The wind was blowing strong from the East and forced the fire up the embankment towards the road reducing its burn area. Bay of conductor was on a 1 phase span spur, back at nearest protection which is 3 phase fuse LA168, 1 x 12k BA fuse blew and dropped open, 1 fuse blew and was still closed and the other fuse was OK. | Conductor (bare) | 0 | 0 | 0 |  | lga22 | 3/12 steel HV conductor wrap-on termination broke due to corrosion. | Grassfire | 27/10/2015 14:10 |  | Small: 10 - 1000 sq.m | 151 |  |  | 20151030SPN_1 | Infrastructure (network-based) | -38.4023 | 145.9264 | 1 | AusNet Services Distribution | Report | 210 | 0.022274 | 22kV AC | Morwell (Latrobe Valley Airport) | 3951 | Fairbank | Conductor
Crew isolated supply and undertook repairs | 209 COMMERCIAL ROAD, KOROIT VIC 3282 |  |  |  | Neutral | Leakage |  |  | 1 | A passing employee reported a pole top fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the pole and the crossarm however they both remained intact. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42046.6806 | 1 | Negligible: no ground fire | 179 | Roadway |  | 20151105PWA_1 | Infrastructure (network-based) | -38.2915 | 142.3588 | 1 | Powercor | Report | 253 | 0.022426 | 22kV AC | Warrnambool Airport Ndb | 3282 | Koroit | Crossarm
Crew Isolated supply and undertook repairs | 1321 SANDMOUNT ROAD, KATUNGA VIC 3640 | 3788 | Vehicle |  | Unlikely |  |  | Phase to phase | 1 | Emergency services reported a vehicle accident at the incident location. On arrival the crew found that following an accident involving a truck and a car, the truck (Owned by Andrew Goldman Excavations. Phone:(03) 5748 4372, Rego: 1AH7IF, Trailer Rego: WO9 856) drove under 22kV lines with its trailer extended contacting the lines causing them to break and fall to the ground.. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  | NKA003 | Vehicle drove into conductors | No Go Zone (contact);Damage to network assets | 30/10/2015 12:23 |  |  | 180 | Agricultural |  | 20151105PWA_2 | Infrastructure (network-based) | -36.0044 | 145.4859 | 1 | Powercor | Report | 252 | 0.018036 | 22kV AC | Shepparton Airport | 3640 | Katunga | Vehicle
The pole top had sustained damage and the pole was assessed to determine if it requires replacement. It was determined the pole was safe and load worthy after the centre phase eyebolt was re-positioned as a temporary measure. The pole will be planned for replacement in November 2015. | 86-88 HOWARD ROAD, DINGLEY VIC 3172 | 206431 |  | Precipitation |  | Electrical breakdown |  |  | 2 | MFB report a pole fire on the corner of Glenway Drive and Howard Road, Dingley Village. During light drizzly rain, a pole fire occurred at the 22kV centre phase tee-off eyebolt on pole No. LIS 0623137 located on the corner of Howard Road and Glenway Drive. The pole is a 66kV intermediate with 22kV and LV tee-off construction. | Pole (wood) | 0 | 0 | 0 |  | SS 23 | During light drizzly rain, a pole fire occurred at the 22kV centre phase tee-off eyebolt on pole No. LIS 0623137. | Pole-top fire | 28/10/2015 21:53 |  | Negligible: no ground fire | 182 | Roadway |  | 20151105UTD_1 | Infrastructure (network-based) | -37.9823 | 145.1211 | 1 | United Energy Distribution | Report | 270 | 0.0048287 | 22kV AC | Moorabbin Airport | 3172 | Dingley | Pole
Crew isolated supply and undertook repairs | 13 BRANSTON ROAD, ST ALBANS VIC 3021 |  | Vehicle | [5 empty] | 2 | A customer reported a service cable pulled down by a vehicle when it was U-turning at the incident location and that the truck had left the scene. On arrival the crew found that a LV service cable had been de-attached from the POA and was laying on the ground. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Contact by unknown truck | No Go Zone (contact);Damage to network assets | 29/10/2015 12:58 |  |  | 194 | Roadway |  | 20151109PWA_2 | Infrastructure (network-based) | -37.7516 | 144.8236 | 1 | Powercor | Report | 296 | 0.013152 | Low voltage AC (<1kV) | Essendon Airport | 3021 | St Albans | Vehicle
The 22kV kiosk substation is live and the Downer substation supervisor was following up to ensure the substation is secured. | 59 LOGIS BOULEVARD, DANDENONG SOUTH VIC 3175 |  | Vandalism;Unauthorised access | [5 empty] | 2 | Caller reports that outside 131 Logis Boulevard, the substation has been graffitied and the substation door ripped off. There was an attempted copper theft at "Logis L116-Smeaton" kiosk substation with damage occurring to the door. The copper bus work perspex cover was removed but no actual theft of copper. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | DSH 24 | Unknown persons attempted a copper theft at "Logis L116-Smeaton" kiosk substation with damage occurring to the door. It appears that no electric shocks or injuries were sustained. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42258 |  |  | 198 | Residential |  | 20151109UTD_2 | Infrastructure (network-based) | -38.0055 | 145.2024 | 1 | United Energy Distribution | Report | 300 | 0.013448 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Other
Crew isolated supply for CASA investigation | 27 DYAR AVENUE, CABARITA VIC 3505 |  | Manned aircraft | [5 empty] | 1 | VicFire reported an aeroplane had crashed into powerlines and exploded at the incident location. On arrival the crew found that an aeroplane had made contact with 22KV conductors, bringing the conductors to the ground and breaking one conductor and resulting in fatal injuries to the pilot. Protection operated. The incident also resulted in a ground fire (Approx. 10m x 12m) on private property and also damage to grape vines. Crew isolated supply for the CASA Investigations Team to investigate. | Conductor (bare) | 0 | 0 | 0 |  | MBN022 | Aeroplane hit 22kV line | Loss of supply;Not involving electrocution;Damage to network assets | 42166.7743 |  |  | 200 | Agricultural |  | 20151110PWA_1 | Infrastructure (network-based) | -34.2095 | 142.0938 | 1 | Powercor | Report | 308 | 0.035084 | 22kV AC | Mildura Airport | 3505 | Cabarita | Vehicle
Crew isolated supply and undertook repairs | 622 TOORAK ROAD, TOORAK VIC 3142 |  | Working too close to overhead lines | [5 empty] | 2 | A builder reported that the excavator on their site hit the service cable at the incident site. On arrival the crew found that a contractor (Browns Piling, 4 John St Dandenong, Contact: Dean Moseley, Ph: 0418 174 462) was operating an excavator and contacted a LV service cable causing damage to the cable and associated POA. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Excavator contacted LV service cable | No Go Zone (contact);Damage to network assets | 42166.3243 |  |  | 222 | Residential |  | 20151113PWA_16 | Infrastructure (network-based) | -37.8433 | 145.0257 | 1 | CitiPower | Report | 335 | 0.03425 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Vehicle
Crew isolated supply for repairs | 309 ALBERT STREET, BRUNSWICK VIC 3056 |  | Working too close to overhead lines | [5 empty] | 2 | The truck company owner of the truck that caused the incident, reported that one of his trucks came into contact with lines that pass over the road at the incident location. On arrival the crew found that an LV service cable had been had been contacted by a truck (Modern Towing, Contact: Chris, Ph: 0448 212 520), causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. Service height was not measured as service was not replaced. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42319.4194 |  |  | 224 | Roadway |  | 20151113PWA_18 | Infrastructure (network-based) | -37.7683 | 144.9584 | 1 | CitiPower | Report | 337 | 0.0086644 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
Crew isolated supply and undertook repairs | 18-24 FOREST STREET, COLAC VIC 3250 |  | Working too close to overhead lines | [5 empty] | 1 | A customer reported that an excavator has struck an overhead power line at the incident location. On arrival the crew found that an excavator (Operated by Calco Timber ( Colac ) Pty Ltd. Contact: Mr. David Colless, Ph: 0428 522 924) had struck a 22kV overhead conductor at the customers industrial site causing damage to 1 phase of the 3 phase conductors. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator contacted 22kV line | No Go Zone (contact);Damage to network assets | 42166.4806 |  |  | 225 | Industrial |  | 20151113PWA_19 | Infrastructure (network-based) | -38.3382 | 143.6063 | 1 | Powercor | Report | 338 | 0.016277 | 22kV AC | Ballarat Aerodrome | 3250 | Colac | Vehicle
Crew undertook repairs | 529 MORPUNG AVENUE, IRYMPLE VIC 3498 |  | Working too close to underground cables | [5 empty] | 2 | A REC reported that they had contacted an underground cable at the incident location. On arrival the crew found that a contractor (Employed by property owner, Jason Rahmel, 529 Morpung Ave, Irymple, Ph: 0427 310 192) was excavating to install irrigation pipes and contacted an LV earthing cable causing damage to the cable. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Excavator contacted LV earthing cable | No Go Zone (contact);Damage to network assets | 29/10/2015 12:32 |  |  | 212 | Roadway |  | 20151113PWA_6 | Infrastructure (network-based) | -34.2555 | 142.1667 | 1 | Powercor | Report | 325 | 0.038932 | Earthing cable | Mildura Airport | 3498 | Irymple | Dug up
Crew isolated supply and undertook repairs | 425 ROMSEY ROAD, WOODEND VIC 3442 |  |  |  |  | Candled fuse |  |  | 2 | A Fault crew attending following an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out | Plant/equipment | 42074.8792 |  | Negligible: no ground fire | 213 | Roadway |  | 20151113PWA_7 | Infrastructure (network-based) | -37.3464 | 144.58 | 1 | Powercor | Report | 326 | 0.0017535 | 22kV AC | Wallan (Kilmore Gap) | 3442 | Woodend | Fuse
Crew isolated supply and undertook repairs | 50 KARRAMOMUS ROAD, ARCADIA VIC 3631 |  |  |  |  | Candled fuse |  |  | 2 | A Fault crew attending following an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out | Plant/equipment | 42105.8792 |  | Negligible: no ground fire | 214 | Roadway |  | 20151113PWA_8 | Infrastructure (network-based) | -36.5273 | 145.377 | 1 | Powercor | Report | 327 | 0.0048056 | 22kV AC | Shepparton Airport | 3631 | Arcadia | Fuse
Crew isolated supply and undertook repairs | NHILL-MURRAYVILLE ROAD, YANAC VIC 3418 |  |  |  |  | Leakage |  |  | 2 | A Powercor contractor reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the pole causing the top of the pole to break and fall to the ground however the conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42135.9521 |  | Negligible: no ground fire | 215 | Roadway |  | 20151113PWA_9 | Infrastructure (network-based) | -36.0754 | 141.4083 | 1 | Powercor | Report | 328 | 0.026301 | 22kV AC | Horsham Aerodrome | 3418 | Yanac | Pole
Area isolated to conduct repairs | 357 BELL STREET, BELLFIELD VIC 3081 |  | Vehicle | [5 empty] | 1 | Car hit pole cnr Bell St and Skeffington St Bellfield causing HV conductor to contact LV | Conductor (bare) | 0 | 0 | 0 |  |  | Vehicle into pole | HV injection | 18/11/2015 0:00 |  |  | 242 | Residential |  | 20151118JEM_10 | Infrastructure (network-based) | -37.7495 | 145.038 | 1 | Jemena | Report | 408 | 0.031838 | 6.6kV AC | Essendon Airport | 3081 | Bellfield | Vehicle
Made safe | 4 DERBY STREET, PASCOE VALE VIC 3044 |  |  |  |  | Conductor clashing |  |  | 2 | LV conductors on ground | Conductor (covered uninsulated) | 0 | 0 | 0 |  |  | Conductor clashing | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42105 |  |  | 241 | Residential |  | 20151118JEM_9 | Infrastructure (network-based) | -37.7351 | 144.9456 | 1 | Jemena | Report | 525 | 0.020061 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Conductor
Crew isolated supply and undertook repairs | HACKETTS ROAD, POINT COOK VIC 3030 |  | Working too close to underground cables | [5 empty] | 2 | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location. On arrival the crew found that a contractor (LOJAC Civil Pty Ltd, Contact: Kenton Burnett, Ph: 0401 093 938, working for Watsons (Developer), Contact Dario: 0400 851 551) was operating an excavator and contacted a LV underground mains cable causing damage to the cable. There were no civil workers on site when the crew arrived and found the damaged cable live and exposed in the trench. The contractor had undertaken a DBYD enquiry for this location (Sequence No: 48519900). There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Excavator contacted LV mains cable | No Go Zone (contact);Damage to network assets | 16/11/2015 14:40 |  |  | 249 | Roadway |  | 20151120PWA_1 | Infrastructure (network-based) | -37.9058 | 144.7154 | 1 | Powercor | Report | 373 | 0.02324 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
Crew isolated supply and undertook repairs | 1840 SUNRAYSIA HIGHWAY, ADDINGTON VIC 3352 |  | Vehicle | [5 empty] | 2 | A customer reported that a truck has pulled down a service wire at the incident location. On arrival the crew found that an LV service cable had been contacted, causing the cable to break and fall to the ground. No vehicle was onsite when the crew arrived. There were no reported injuries or third party property damages. Upon restoration the service height was measured at 6.75m at the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Third party contact | No Go Zone (contact);Damage to network assets | 42349.7458 |  |  | 254 | Roadway |  | 20151120PWA_2 | Infrastructure (network-based) | -37.3682 | 143.6588 | 1 | Powercor | Report | 378 | 0.028505 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Addington | Vehicle
An occupier received a slight electric shock when using a shower tap and contacted a REC to investigate. The REC tested the installation and identified a disconnected neutral conductor at the pole end was the cause. A LEI and faults truck attended and identified the neutral conductor from the single phase grey twisted overhead service was disconnected from the line tap and was hanging down. A NST failed and the LEI measured a voltage of 12v (no load) and 105v (under load) between an independent earth and the metallic water pipe system. The faults crew cleaned, greased and reconnected the neutral conductor and the LEI tested the installation that confirmed the fault had been rectified. | 1 WINSLOW COURT, KEYSBOROUGH VIC 3173 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Customer called to advise her daughter received an electric shock whilst in the shower. Her daughter is okay and a REC was called who advised there is a shortage of supply coming in from outside and he can see a wire has come off the pole in the street. The REC turned off the main switch and advised the customer to contact the electricity company. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | A LEI and faults truck attended and identified the neutral conductor from the single phase grey twisted overhead service was disconnected from the line tap and was hanging down. | Minor shock | 17/11/2015 17:00 |  |  | 250 | Residential |  | 20151120UTD_1 | Infrastructure (network-based) | -37.9887 | 145.1812 | 1 | United Energy Distribution | Report | 374 | 0.024041 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Conductor
A faults crew identified the deceased possum and burnt grassed area during a patrol of the feeder following the successful reclose. | 346 MAIN CREEK ROAD, MAIN RIDGE VIC 3928 | LIS No. 9829162 |  | Animal |  |  |  |  | 1 | At approximately 0400hrs on 18/11/2015, ACR RB7294 located in Main Creek Road on 22kV feeder DMA 13 successfully reclosed and held. The cause of the ACR auto reclose was attributed to a possum that caused hot debris/possum to ignite a small grassed area under pole No. LIS 9829162 (HVABC /open wire interface) outside 346 Main Creek Road, Main Ridge. The small 2sqm grass fire appears to have self extinguished. | Pole top | 0 | 0 | 0 |  | DMA 13 | Animal Incident | Grassfire | 18/11/2015 4:00 | 1 | Localised: less than 10 sq.m | 251 | Roadway |  | 20151120UTD_2 | Infrastructure (network-based) | -38.3929 | 144.9721 | 2 | United Energy Distribution | Report | 676 | 0.032522 | 22kV AC | Moorabbin Airport | 3928 | Main Ridge | Animal
Crew checked assets for damage, minor damage to EDO unit, crew initiatedrepairs | SCULTHORPE ROAD, NANGILOC VIC 3494 |  |  | Bird |  |  |  |  | 2 | Customer reported a fire at the above location. On arrival the crew found that a bird had caused a flashover on a 22kV fuse unit, resulting in a ground fire (approx. 2 sqm) in the road reserve. Customer put out fire and reported the incident the following day. There were no reported injuries. | EDO fuse | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 25/11/2015 10:40 |  | Localised: less than 10 sq.m | 268 | Roadway |  | 20151126PWA_1 | Infrastructure (network-based) | -34.4964 | 142.3408 | 1 | Powercor | Report | 397 | 0.03306 | 22kV AC | Mildura Airport | 3494 | Nangiloc | Animal
Crew isolated supply and undertook repairs | 25 TOWNSEND ROAD, CRESWICK VIC 3363 |  |  | Fallen |  |  |  |  | 2 | Vic Fire reported a grass fire at the incident location. On arrival the crew found that a tree (from outside the clearance space) had fallen across an adjacent low voltage conductor resulting in a grass fire (Approx. 200sqm) on the road reserve. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 25/11/2015 12:57 |  | Small: 10 - 1000 sq.m | 269 | Roadway |  | 20151126PWA_2 | Infrastructure (network-based) | -37.4267 | 143.8805 | 1 | Powercor | Report | 399 | 0.040796 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3363 | Creswick | Trees
Crew isolated supply and undertook repairs | 854 MOUNT EMU SETTLEMENT ROAD, PITTONG VIC 3360 |  |  | Fallen |  |  |  |  | 1 | CFA reported tree had brought conductor down and a fire at the incident location. On arrival the crew found that a tree (from outside the clearance space) had fallen across an adjacent SWER conductor, causing the conductor to break and fall to the ground resulting in a ground fire (Approx. 2000sqm) on private property. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 25/11/2015 13:34 |  | Medium: 1000 sq.m - 10 ha | 271 | Agricultural |  | 20151126PWA_4 | Infrastructure (network-based) | -37.6402 | 143.4396 | 1 | Powercor | Report | 403 | 0.017806 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3360 | Pittong | Trees
Crew undertook repairs | 15 BELLEVIEW DRIVE, IRYMPLE VIC 3498 |  | Working too close to underground cables | [5 empty] | 2 | A passer by reported that a tree removalist had made contact with a service pit at the incident location. On arrival the crew found a service pit lid had been damaged by the stump removal equipment (Operated by Mildura Tree Services, Contact: Peter Luke, Ph: 5023 6452). There were no reported injuries or third party property damages. | Services pit | 0 | 0 | 0 |  |  | Damage by third party | Damage to network assets | 13/11/2015 18:17 |  |  | 278 | Roadway |  | 20151127PWA_6 | Infrastructure (network-based) | -34.2305 | 142.1702 | 1 | Powercor | Report | 412 | 0.02424 | Not applicable | Mildura Airport | 3498 | Irymple | Vehicle
Crew arranged repairs | RING ROAD, WENDOUREE VIC 3355 |  | Theft | [5 empty] | 2 | A Powercor employee reported copper earths removed from a pole at the below incident location. On arrival the crew found that both the high and low voltage earths on a 22kV substation pole had been removed. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Theft | Damage to network assets | 18/11/2015 10:44 |  |  | 280 | Roadway |  | 20151127PWA_7 | Infrastructure (network-based) | -37.5338 | 143.8024 | 1 | Powercor | Report | 416 | 0.04036 | Not applicable | Ballarat Aerodrome | 3355 | Wendouree | Other
Fuse replaced and supply successfully restored. Request sent to Works Planning to raise a work order to replace EDO fuse units with Boric Acid fuse units. | 1 CORNWALLS ROAD, BRUTHEN VIC 3885 | 1612270 |  |  | Unlikely | Age;Corrosion;Electrical breakdown |  | Phase to earth | 2 | IMS 219142. Burnt out (candled) EDO fuse tube was found at Comwell 2 substation. No fire damage. No other apparent damage. | EDO fuse | 0 | 0 | 0 |  | bdl8 | Burnt out EDO fuse - Equipment failure. | Loss of supply;Other electricity related | 18/11/2015 7:20 | 1 | Negligible: no ground fire | 285 | Residential |  | 20151130SPN_1 | Infrastructure (network-based) | -37.6978 | 147.8336 | 1 | AusNet Services Distribution | Report | 1139 | 0.030731 | 22kV AC | Bairnsdale Airport | 3885 | Bruthen | Fuse
Already isolated - site made safe | 8 NORTHERNHAY STREET, RESERVOIR VIC 3073 | [5 empty] | Not followed |  | 2 | While undertaking pole replacement work, a pole adjacent to two poles being replaced by ZNX work crews failed. This resulted in the pole falling and landing on an Elevated Work Platform (EWP) vehicle and a light construction truck (LCT). No one was injured and the two vehicles sustained minor damage. | Pole (wood) | 0 | 0 | 0 |  |  | The work crew did not identify the hazardous conditions created by removing the HV conductors. The work crew failed to install a temporary stay to adjacent pole #13 as per the VESI Fieldworkers Handbook, Section 4, page 18. | Damage to network assets | 42047.2514 |  |  | 311 |  |  | 20151203JEM_1 | Infrastructure (network-based) | -37.7247 | 145.0136 | 1 | Jemena | Report | 2698 | 0.0152 | 22kV AC | Essendon Airport | 3073 | Reservoir | Pole
Supply isolated to assets | 57-69 FORSYTH ROAD, HOPPERS CROSSING VIC 3029 |  | Working too close to overhead lines | [5 empty] | 2 | A Powercor field operator reported that a brick / colour-bond wall had been removed from the substation following demolition works at the incident location. This resulted in security to the ground type substation being compromised. The demolition works (Undertaken by Merchi Demolitions, Site manager: Joe, Ph: 0459 035 388, subcontracted to Dynon Properties, Contact: Kerri, Ph: 0417 034 790) were carried out with the assets alive at 22kV. There were no reported injuries. CitiPower has isolated supply to the substation. The site manager advised that the site is under 24 hour surveillance, with a guard positioned on site. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  |  | Demolition company demolished wall at live substation | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/11/2015 9:45 |  |  | 326 | Commercial |  | 20151204PWA_12 | Infrastructure (network-based) | -37.865 | 144.7324 | 1 | Powercor | Report | 484 | 0.012935 | 22kV AC | Laverton Raaf | 3029 | Hoppers Crossing | Other
Crew isolated supply and undertook repairs, pole replaced following day | 5449 MIDLAND HIGHWAY, ELAINE VIC 3334 |  |  |  |  | Unknown technical factor |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a pole fire was in progress near the base of a SWER isolating substation where the copper earth cables are located and smoke was emanating out of the pole. There was no ground fire. Protection had not operated. There were no reported injuries. The crew unable to determine the cause of the fire. | Pole (wood) | 0 | 0 | 0 |  |  | Crew unable to determine cause | Pole-top fire | 28/11/2015 20:56 |  | Negligible: no ground fire | 328 | Roadway |  | 20151204PWA_14 | Infrastructure (network-based) | -37.7672 | 144.0146 | 1 | Powercor | Report | 486 | 0.026907 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3334 | Elaine | Pole
Crew isolated supply for repairs | 577 ROKEWOOD-SHELFORD ROAD, SHELFORD VIC 3329 |  |  |  |  | Overheated connection |  |  | 2 | The fire brigade reported a grass fire at the incident location. On arrival the crew found that an overheated connection in a customerâ€™s 240 Volt fuse box mounted on the substation pole, had caused debris to fall to the ground causing a grassfire of approx. 3 Hectares (500m x 50m plus other patches). The fire was on private property, and a substantial amount of the area burnt was a crop paddock. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 30/11/2015 18:44 |  | Medium: 1000 sq.m - 10 ha | 330 | Agricultural |  | 20151204PWA_15 | Infrastructure (customer connection) | -37.9795 | 143.9273 | 1 | Powercor | Report | 535 | 0.033932 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3329 | Shelford | Connection
Crew isolated supply and undertook repairs | 143 ARGYLE STREET, ST KILDA VIC 3182 |  |  |  |  | Overheated connection |  |  | 1 | A field crew patrolling a line following an outage found that a fault had occurred at a 11kV cable head pole resulting in a fire at the white phase insulator of the cable termination box. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | connection fault | Pole-top fire | 16/10/2015 22:18 |  | Negligible: no ground fire | 315 | Roadway |  | 20151204PWA_2 | Infrastructure (network-based) | -37.8634 | 144.9906 | 1 | CitiPower | Report | 470 | 0.014887 | 11kV AC | Moorabbin Airport | 3182 | St Kilda | AF Other
Crew isolated supply and undertook repairs | SCHOOL ROAD, WALLACEDALE VIC 3303 |  | No external/community cause | No environment cause |  | Candled Fuse;Other | No work practice factor |  | 2 | A field crew patrolling a line following an outage found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a fire to start in the vicinity of the base of the pole. Lightning storms in the area. An area of approximately 40 square meters of grassed road reserve was burnt. No injuries were reported. | EDO fuse | 0 | 0 | 0 |  |  | Candled fuse | Grassfire | 25/10/2015 16:50 |  | Moderate: 5-100 sqm | 316 | Roadway |  | 20151204PWA_3 | Infrastructure (network-based) | -37.9261 | 141.8199 | 1 | Powercor | Report | 472 | 0.017867 | 22kV AC | Hamilton Airport | 3303 | Wallacedale | Fuse
10am (approx) Civil Contractor Greg Morrissey (0407 446 710) rang this morning requesting a site inspection for works he was doing at the incident site, his crew was onsite working near overhead cables. Powercor asked if he had a DBYD â€“ response was â€œ12 months ago. Works were on hold for some time.â€ He was unable to give details of the site but advised that he would get his Site Supervisor to give Powercor a call. Kurt Good, Site Supervisor (0427 446 710) rang, advised the LIS number of the pole. He was asked if he had a DBYD ref; he did not. He was advised that Powercor could not get an inspector onsite today as they did not have the ability to locate u/g cables. He would have to apply online for a Site Inspection and someone will contact him next week. Powercor spoke with The local service agent to see if they had anyone in the area that could issue a Permit to Work and a field employee worker was arranged to call by the site however they could not locate cables. 1.44pm The field employee attended onsite and advised that it appears the works went ahead. 1.50pm Powercor confirmed that the contractor had dug 1meter from transformer pole to a depth of 1meter. Powercor then spoke with the site supervisor, Kurt, advising that â€˜Works are to Stopâ€™. The field employee advised that he would need to test the LV/HV earths. Contractor had area barricaded for his works. The field employee advised that he tested earths and the result was all ok â€“ no indication of a broken earth. He is fairly confident that no earths have been compromised. | BORUNG STREET, INGLEWOOD VIC 3517 |  | Working too close to underground cables | [5 empty] | 2 | A field worker found that a civil contractor (ONE STOP CIVIL / TACTILE AUSTRALIA, 33-35 William St, TATURA, Contact: Greg Morrissey, Ph: 0407 446 710) had excavated to within 1000mm of a 22kV/LV substation pole at a depth of 1000mm breaching VESI Guidelines. Location on corner of Borung and Reef Streets. | Earth/earthing | 0 | 0 | 0 |  |  | Contractor breached VESI guidelines | No Go Zone (no contact) | 16/11/2015 13:45 |  |  | 317 | Roadway |  | 20151204PWA_4 | Infrastructure (network-based) | -36.5805 | 143.8667 | 1 | Powercor | Report | 473 | 0.0007037 | Earthing cable | Bendigo Airport | 3517 | Inglewood | Dug up
Crew undertook repairs | SYDENHAM ROAD, DELAHEY VIC 3037 |  | Theft | [5 empty] | 2 | An Asset Inspector reported that copper earths had been stolen from a pole type substation at the incident location. On arrival the crew found that the copper earths from Sydenham â€“ Taylors substation had been stolen. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 23/11/2015 11:19 |  |  | 319 | Industrial |  | 20151204PWA_6 | Infrastructure (network-based) | -37.7275 | 144.7927 | 1 | Powercor | Report | 475 | 0.019214 | Earthing cable | Melbourne Airport | 3037 | Delahey | Other
Crew isolated supply and undertook repairs | 8 ATHOL STREET, PRAHRAN VIC 3181 |  | Working too close to overhead lines | [5 empty] | 2 | A representative of the company (Malcolm of Walters Steel, Mesh and Hardware Ph 9788 5444) reported that a truck had contacted and bought down a service wire which was sitting on the top of the truck in the laneway behind the incident location. On arrival the crew found that an LV service had been hit by a truck, resulting in it breaking and coming to rest on the truck. There were no reported injuries or third party damages. Following repairs the service height was measured at 4.3m at the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted cable | No Go Zone (contact);Damage to network assets | 24/11/2015 11:52 |  |  | 320 | Roadway |  | 20151204PWA_7 | Infrastructure (network-based) | -37.8475 | 144.9856 | 1 | CitiPower | Report | 476 | 0.030549 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Prahran | Vehicle
Crew isolated supply and undertook repairs | 27 MCKELLAR DRIVE, MINERS REST VIC 3352 |  | Working too close to underground cables | [5 empty] | 1 | A customer reported that an excavator had struck and damaged an underground cable at the incident location (near corner of McKellar Drive and Hodge Street). On arrival the crew found that a contactor (Pipecon Pty Ltd, Contact: Sean. Ph. 0438 508 792) was undertaking excavation works and contacted a low voltage underground service cable causing damage to the cable. Protection operated. There were no reported injuries or third party property damages. The contractor had undertaken DBYD enquiries, however a Permit to Work on issue did not cover the area where the incident occurred. | Cable | 0 | 0 | 0 |  |  | Excavator contacted LV cable | No Go Zone (contact) | 25/11/2015 12:55 |  |  | 321 | Roadway |  | 20151204PWA_8 | Infrastructure (network-based) | -37.5053 | 143.8101 | 1 | Powercor | Report | 477 | 0.038894 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Miners Rest | Dug up
Crew isolated supply and checked assets for damage, LEI crews undertook inspections of customers premises for damages. | 46A BERKSHIRE ROAD, SUNSHINE NORTH VIC 3020 |  |  | Wind |  |  |  |  | 1 | A customer reported no supply and an explosion from their meter box at the incident location. On arrival the crew found that a sheet of corrugated roofing iron had blown across 22kV and LV lines causing a HV injection which resulted in damaged metering and damages to customers premises. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Sheet of corrugated iron blew across lines | HV injection;Less than $50k damage | 25/11/2015 22:19 |  |  | 322 | Roadway |  | 20151204PWA_9 | Infrastructure (network-based) | -37.7653 | 144.8412 | 1 | Powercor | Report | 480 | 0.038497 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Other
Isolated and made safe | 8 CURTIN AVENUE, HADFIELD VIC 3046 |  | Vehicle | [5 empty] | 2 | Low voltage conductor on ground | Conductor (bare) | 0 | 0 | 0 |  |  | Truck snagged white phase LV conductor | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42136.5625 |  |  | 334 | Residential |  | 20151207JEM_1 | Infrastructure (network-based) | -37.7093 | 144.9472 | 1 | Jemena | Report | 494 | 0.022275 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Conductor
Crew undertook repairs | 120 SCHOOL ROAD, BALLIANG EAST VIC 3340 |  | Vehicle | [5 empty] | 2 | A customer reported that he had â€œjust arrived home after being out since 3pm, notes pole has been on fire during this time, and transformer has blown up and that he had an overhead connection but can no longer see his service wireâ€. On arrival, the crew found that the LV service cable across the road servicing the customers installation was missing. The crew found that the cable had been pulled down by an unknown vehicle/load and there was no sign of the service cable at the location. There were no witnesses and therefore, no details of the vehicle obtained. Further, the crew did not find any evidence of fire or damage to the transformer. There were no reported injuries or third party property damages. Following repairs the cable height was measured at 5.8m above the roadway. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle/load contacted LV service cable | Damage to network assets | 27/11/2015 17:22 |  |  | 342 | Roadway |  | 20151207PWA_4 | Infrastructure (network-based) | -37.7966 | 144.4345 | 1 | Powercor | Report | 503 | 0.025943 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Balliang East | Vehicle
Crew isolated supply and undertook repairs | 547-549 SUTTON STREET, SEBASTOPOL VIC 3356 |  |  |  |  | Overheated connection |  |  | 2 | A customer reported that a transformer on the pole near Greenhillâ€™s Road is buzzing and random sparking has become more frequent coming from the transformer at the incident location. On arrival the crew found the top contact connection on the 22kV EDO fuse had overheated causing hot debris to fall to the ground, resulting in a ground fire (approx. 0.5m x 0.5m) in the road reserve. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 42136.6562 |  | Localised: less than 10 sq.m | 348 | Roadway |  | 20151208PWA_2 | Infrastructure (network-based) | -37.5856 | 143.8268 | 1 | Powercor | Report | 514 | 0.02142 | 22kV AC | Ballarat Aerodrome | 3356 | Sebastopol | Fuse
Crew checked assets for damage - none found. | 100 WHITELAW AVENUE, DELACOMBE VIC 3356 |  |  | Bird |  |  |  |  | 1 | VicFire reported a wire down and tree / shrub on fire at the incident location. On arrival the crew found a bird had caused a flashover between the steel cross arm and the 22kV conductors resulting in 4 separate ground fires with the largest being approx. 10m x 5m, all of which occurred in the road reserve. Protection operated. There were no reported injuries. The incident also caused a HV injection into the pay TV cable on the pole causing damage to the cable. | Conductor (bare);Crossarm (steel) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 42167.6347 |  | Small: 10 - 1000 sq.m | 349 | Roadway |  | 20151208PWA_3 | Infrastructure (network-based) | -37.5796 | 143.8196 | 1 | Powercor | Report | 516 | 0.028608 | 22kV AC | Ballarat Aerodrome | 3356 | Delacombe | Animal
Crew isolated supply and undertook repairs (pole replaced). | 635 CAPE OTWAY ROAD, MORIAC VIC 3240 |  | Vehicle | [5 empty] | 1 | VicPol reported a fatality when a car hit a pole at the incident location. On arrival the crew found that a single vehicle had veered off the road and collided with a wooden transformer pole. There was no ground fire. The young male driver, who was the sole occupant of the vehicle, suffered fatal injuries. No oil spill was reported. | Pole (wood) | 0 | 1 | 0 |  |  | Car hit pole | Not involving electrocution;Damage to network assets | 42228.0694 |  |  | 354 | Roadway |  | 20151209PWA_1 | Infrastructure (network-based) | -38.2434 | 144.1663 | 1 | Powercor | Report | 531 | 0.0038113 | Not applicable | Avalon Airport | 3240 | Moriac | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the HV crossarm was replaced under Access Authority conditions prior to the supply being restored. | 1 SUNRISE DRIVE, MULGRAVE VIC 3170 | LIS No. 0625027 |  | Precipitation |  | Corrosion;Electrical breakdown |  |  | 1 | At 0643hrs on 26/11/2015, 22kV feeder MGE 24 circuit breaker reclosed to lockout affecting 1201 customers. A customer at 1 Sunrise Drive advised there was a fire on the pole outside her house. Following light drizzly rain, a HV crossarm fire occurred on a HV/LV pole with angle type 2 construction (LIS No. 0625027) located outside 1 Sunrise Drive, Mulgrave. The pole fire originated at the HV crossarm with burn marks identified on the crossarm. The HV conductor fell and contacted a LV isolator mounting bolt that caused sparking and a LEI was dispatched to the site as the faults crew suspected that a HVI may have occurred. The LEI inspected properties in the vicinity and confirmed that a HVI did not occur. | Conductor (bare);Crossarm (wood);Aluminium | 0 | 0 | 0 |  | MGE 24 | A HV crossarm fire occurred on a HV/LV pole located outside 1 Sunrise Drive, Mulgrave. | Pole-top fire;Loss of supply | 26/11/2015 6:43 |  | Negligible: no ground fire | 353 | Roadway |  | 20151209UTD_1 | Infrastructure (network-based) | -37.9272 | 145.1738 | 1 | United Energy Distribution | Report | 523 | 0.014696 | 22kV AC | Moorabbin Airport | 3170 | Mulgrave | Crossarm
A LEI met the faults crew on site and could not explain what appeared to have transpired. The LEI took a photo of the burn mark to the roof rack (attached) and suggested that a day light patrol of the area is completed to check the reticulation in the vicinity of the incident for any signs of flashing. The immediate area was patroled in day light and no evidence of a fault could be found. A review of faults at the time of the event, could not explain the customers claim. There was a successful reclose of ACR DT7049 located in King Street earlier in the day (3.43PM) caused by a council tree in Anders Creek Road. | 140 KING STREET, DONCASTER EAST VIC 3109 |  |  |  |  | Unknown technical factor |  | Phase to earth | 2 | Caller reported that he was driving west bound opposite the overhead reticulation and saw a flash from either pole numbers 70600204, 70600205, 70600206 or 70600207. The car has a roof rack and a flash has struck the roof rack on the passenger side with a discharge across the roof and down the window pillar on the drivers side. The driver claimed to have received an electric shock to his right arm. The person who received the electric shock advised the faults crew that he was driving down King Street and saw a flash and shock to his right arm which was resting on the car door arm rest. He mentioned that he experienced tingles for approximately 10 minutes. He stopped and noticed a humming noise and a red blue green light surrounding the car. There was a burn mark on the roof rack on the passenger side of the car. A witness travelling behind stopped and saw a flash originate from the pole that struck the vehicle. The driver insisted that he was well and did not require medical attention or observation. | No failed asset | 0 | 0 | 0 |  | DC 02 | Unknown | Minor shock | 28/11/2015 23:00 |  |  | 355 | Roadway |  | 20151209UTD_2 | Infrastructure (network-based) | -37.775 | 145.161 | 1 | United Energy Distribution | Report | 532 | 0.015271 | 22kV AC | Moorabbin Airport | 3109 | Doncaster East | Conductor
Section isolated and conductor made safe | 545-555 MACAULAY ROAD, KENSINGTON VIC 3031 |  |  |  |  | Unknown technical factor |  |  | 1 | LV conductor connection failed causing conductor to come to ground de-energised. | Conductor (insulated) | 0 | 0 | 0 |  |  | LV conductor connection failed | Less than $50k damage | 30/11/2015 19:49 |  |  | 361 | Residential |  | 20151210JEM_1 | Infrastructure (network-based) | -37.7943 | 144.9277 | 1 | Jemena | Report | 545 | 0.029547 | 22kV AC | Essendon Airport | 3031 | Kensington | Conductor
Crew isolated supply and undertook repairs | 19 DAINTREE DRIVE, WINCHELSEA VIC 3241 |  | Working too close to underground cables | [5 empty] | 1 | A Civil contractor reported some houses in the street have lost power when he was boring to install a gas pipe. On arrival crew found that the contractor (Drapers Civil Contracting, 54-56 Leather Street, Breakwater VIC 3216, Contact: Samuel Robertson, Ph: 0408 400 066, Gas Manager: Tony Wright, Ph: 0408 521 762) was carrying out underground boring works and contacted an underground LV mains cable causing damage to the cable. He incident also resulted in damage to customers premises and equipment connected to the circuit. Protection operated. There were no reported injuries. The contractor had undertaken DBYD enquiries, Sequence No 9787418. | Cable | 0 | 0 | 0 |  |  | Contractor contacted UG cable | Less than $50k damage | 23/11/2015 12:47 |  |  | 362 | Roadway |  | 20151210PWA_3 | Infrastructure (network-based) | -38.2354 | 143.9949 | 1 | Powercor | Report | 546 | 0.010503 | Low voltage AC (<1kV) | Avalon Airport | 3241 | Winchelsea | Dug up
Crew isolated supply and undertook repairs | 40 GLENELG STREET, PORTLAND VIC 3305 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A passer-by reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 3 phase 22kV strain pole which burnt the top of the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | crossarm fire | Pole-top fire | 42047.3833 |  | Negligible: no ground fire | 363 | Roadway |  | 20151210PWA_4 | Infrastructure (network-based) | -38.3524 | 141.6007 | 1 | Powercor | Report | 547 | 0.020917 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Pole
The United Energy Connections Team Leader tried to contact Angela at Super Safe Hire, however there was no one there by that name and was advised that Angela may be a customer. She spoke with Debbie at Super Safe Hire and was advised that other meters are also there and they would not remove a BSP with a live meter. Debbie was informed that are not allowed to remove a BSP with a meter attached as this is United Energyâ€™s property and a very unsafe practice. Debbie confirmed that Super Safe Hire do have those meters and she asked why UE would not remove the meters when they were abolished. Debbie was advised they were not abolished and this is the reason why the meters where still attached to the BSP. The faults crew attended the site at 5 Flame Tree Grove, Mornington and confirmed the BSP and meters had been removed. There were live tails at the base of where the BSP was located in the URD. Supply was isolated and the site was made safe. The builder on site advised the owner has taken the BSP and work has ceased at the site. A faults crew were arranged to pick up the meters from Super Safe Hire who are located at 34-36 Gatwick Road Bayswater. Check out www.rushire.com.au/mobile/temporary-power-pole | 5 FLAME TREE GROVE, MORNINGTON VIC 3931 |  | Unauthorised work | [5 empty] | 2 | The United Energy Connections Team Leader was advised by Origin Energy that two sites have had the BSP removed with the meter still attached. Origin advised the business is Super Safe Hire (Phone 9761 6180). The two events were reported to Origin by a lady named Angela. The two sites are as follows: - 7 Warrandyte Road, Langwarrin. This was abolished on 18/09/2015 as the meter had not been communicating since 19/12/2013 as per notes on the account. - 5 Flame Tree Grove Mornington. Meter is still active in our systems and a faults truck was promptly arranged to ensure there are no live wires or any hazards. | Cable | 0 | 0 | 0 |  |  | The BSP was removed by unknown persons that left live consumers mains. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42320.4479 |  |  | 370 | Construction |  | 20151211UTD_5 | Infrastructure (network-based) | -38.2163 | 145.0426 | 1 | United Energy Distribution | Report | 554 | 0.013322 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Other
Fence was secured and theft reported to Police | 90 WILLIS STREET, WINCHELSEA VIC 3241 |  | Theft | [5 empty] | 2 | A Powercor employee reported that the fencing at a Zone substation (ZSS) had been cut in two places and a cable bypass trailer stolen. Nothing else was removed. The thieves left the ZSS fencing compromised. There were no reported injuries or third party property damages. | Zone substation | 0 | 0 | 0 |  |  | Theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42167.7083 |  |  | 382 | Industrial |  | 20151214PWA_1 | Infrastructure (network-based) | -38.236 | 144.0029 | 1 | Powercor | Report | 568 | 0.011412 | Not applicable | Avalon Airport | 3241 | Winchelsea | Other
A faults truck attended and removed the tree branch from the overhead conductors with a HV stick before supply was restored to the HV feeder. | 215 ORRONG ROAD, ST KILDA EAST VIC 3183 | LIS No. 2306479 |  | Blown branch/vegetation |  |  |  |  | 1 | At 1920hrs on 30/11/2015, 11kV feeder BC 23 circuit breaker reclosed to lockout affecting 1355 customers. The occupier from 215 Orrong Road advised the tree opposite was on fire and there is no power in the street. During strong winds, a tree branch from a council tree located outside 215 Orrong Road, Balaclava contacted the 11kV overhead conductors that resulted in the tree branch catching fire and falling onto the conductors. In addition, there was charring evident in the adjacent branches in the tree canopy. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | BC 23 | Vegetation: Trees Incident | Loss of supply;Other vegetation | 30/11/2015 19:20 |  | Negligible: no ground fire | 377 | Roadway |  | 20151214UTD_3 | Infrastructure (network-based) | -37.8726 | 145.008 | 1 | United Energy Distribution | Report | 561 | 0.038735 | 11kV AC | Moorabbin Airport | 3183 | St Kilda East | Trees
Repaired neutral connection at pole end | 78 COMMERCIAL ROAD, FOOTSCRAY VIC 3011 |  |  |  |  | Neutral fault |  |  | 2 | Customer received tingles from shower taps | Service conductor | 0 | 0 | 0 |  |  | Service neutral connection issue at pole end | Minor shock | 28/11/2015 11:54 |  |  | 386 |  |  | 20151216JEM_1 | Infrastructure (network-based) | -37.7962 | 144.8921 | 1 | Jemena | Report | 582 | 0.0083681 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Connection
Line inspected and no damage found | 71-79 KYLE ROAD, ALTONA NORTH VIC 3025 |  |  | Bird |  |  |  |  | 1 | A fault crew patrolling a feeder following an auto reclose event and found that a magpie had contacted a 22kV line resulting in a grass fire (Approx. 1m x 1m) in the Terminal Station grounds. The incident also caused damage to surge arrestors on the feeder. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 42134.866 |  | Localised: less than 10 sq.m | 396 | Industrial |  | 20151217PWA_1 | Infrastructure (network-based) | -37.8311 | 144.8563 | 1 | Powercor | Report | 596 | 0.020302 | 22kV AC | Laverton Raaf | 3025 | Altona North | Animal
Crew isolated supply and undertook repairs | 395 HESKETHS ROAD, NULLAWARRE VIC 3268 |  |  |  |  | Corrosion;Electrical overload |  |  | 1 | Customer reported a supply outage and a cable laying across a fence at the incident location. On arrival the crew found that a 22kV steel conductor had broken at a helical splice. The conductor was corroded but the crew could not determine if the cause was the corrosion or a downstream fault current. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Crew unable to determine | Loss of supply | 13/12/2015 3:48 |  |  | 404 | Agricultural |  | 20151218PWA_4 | Infrastructure (network-based) | -38.5027 | 142.7252 | 1 | Powercor | Report | 608 | 0.023409 | 22kV AC | Warrnambool Airport Ndb | 3268 | Nullawarre | Conductor
CFA attended, fire controlled. AusNet Services' crew attended to make safe, check assets for damage and investigate. Investigation undertaken on the following morning found a fire area of approximately 180 sq. meters covering the edge of Merriang Gap Rd and some of the adjoining landholder's paddock. Approximately 30m of the six strand barbwire boundary fence line was burnt, but largely undamaged. The 8 concrete fence posts were undamaged and the bottom stand of barbwire is discoloured at a few locations. Two burnt magpies were at the base on the pole (Site ID 4501219) 238 of the WN-MYT 66KV line. The centre phase 66KV 12 shed porcelain insulator had black marks on the insulator sheds and part of the bottom shed missing on the northern side of the pole. Fragments of porcelain were found spread across the Merriang Rd up to 10m from the pole. | 20 MERRIANG GAP ROAD, WHOROULY EAST VIC 3735 | 4501219 |  | Bird |  | Insulator |  | Phase to phase | 1 | 2 magpies caused a flashover at a 66kV intermediate pole structure. CFA reported a fire on Merriang Gap Rd, which they extinguished, with our assets inside the fire area. Observed a grass fire of approximate size of 120 sq. metres. A fault crew was dispatched to check our assets which were assessed as acceptable, as the concrete pole was not damaged and the 66k WN-MYT line was still in service with minor damage to one insulator. The Information from SCADA showed the WN-MYT 66K line completed a successful auto reclose due to a ground fault at 21:14 on the 17/12/15. | Insulators;Pole (concrete) | 0 | 0 | 0 |  | WN-MYT 66kV line | Bird Incident | Grassfire | 17/12/2015 21:15 | 1 | Small: 10 - 1000 sq.m | 399 | Agricultural |  | 20151218SPN_2 | Infrastructure (network-based) | -36.5383 | 146.6413 | 1 | AusNet Services Distribution | Report | 603 | 0.011002 | 66kV AC | Wangaratta Aero | 3735 | Whorouly East | Animal
Crew dispatched to isolate make safe. Repairs organised. Pole req replacing, tx rebuild and repair conductors. An AusNet Services fault crew were dispatched to isolate supply and make the site safe. Repairs were organised. The pole required replacing, a transformer rebuild and repair conductors. The pole was replaced including the transformer, and repairs were made to the HV conductor that was broken. Co-ordination had to be done by work site leader as the pole had to be held so as the car could be removed. | 260 AGAR ROAD, BASS VIC 3991 | 2803370 | Vehicle | [5 empty] | 1 | IMS218525 - Car hit and broke conc pole lis#2803370. Car hit and broke a concrete pole lis#2803370. The vehicle incident caused a HV conductor to break and fall to the ground and the report received that the conductor could have been alive through back feed. The AusNet Services' Linesman disconnected supply as the vehicle was still on the pole. Further advice from the Leongatha Site Manager is: it was only the centre phase conductor broken and the upstream ACR was open on arrival so there was no back feed. No live conductors on ground or at severly reduced clearances. | Pole (concrete) | 0 | 0 | 0 |  | wgi23 | Car hit and broke a concrete pole. | Damage to network assets | 42134.0347 |  |  | 46 |  |  | 20151006SPN_1 | Infrastructure (network-based) | -38.4499 | 145.4439 | 1 | AusNet Services Distribution | Report | 101 | 0.0082882 | 22kV AC | Moorabbin Airport | 3991 | Bass | Vehicle
Tree clearing crew advised to stand down, stay clear and wait until operator arrives on site. Upstream protection suppressed until operator arrives. Asplundh General Foreman Adam Simmonds was notified of this incident by phone at 1000 on Wednesday 7th October 2015 by Colin Lee from Taylors Trees who stated an incident had occurred involving a climbing crew in which a limb has come into contact with the 22kV. He further advised the Climber had potentially received an electric shock and had been transported to Box Hill hospital for precautionary ECG monitoring. Key actions and undertakings include: Climbers stood down from the network until re-trained and re-instructed. Also, not to return until approved by Select Solutions. We are currently going through this process. Remaining Taylors Trees temporarily stood down from the network. Crews Trained in the use of Asplundh's own JSA. Permitted to return to the network. Asplundh have increased their level of supervision of all the Taylors crews. Remedial & Corrective Actions and Recommendations: Remedial Action: * Detailed discussion with the workers on how the incident could have been avoided. (Completed) * Crew stood down from vegetation management work pending completion of investigation and recommendations. (In place). Corrective Action: * Both workers are to receive comprehensive reinstruction on Asplundh`s Hazard Assessment Check (SWP8) process. (Prior to reinstatement on Network). * Both workers to be retrained in VESI Safe Approach Distances before returning to Network works. * Asplundh to develop a process for confirming daily subcontractor suppressions and work locations. Further Recommendations: * Both workers are to be put on six months probation performance management with a particular focus on the implementation of control measures referenced on JSAs/HAC form. * Inclusion of and verification sign off that Safety Gram #217593is communicated to all Asplundh crews and Asplundh subcontractor crews as part of the next weekly tailgate meeting. * Asplundh ensures any work instructions provided to crews contain all relevant information including comments. * Asplundh`s Hazard Assessment Check form is utilised to replace the current JSA. The Asplundh form is more comprehensive in listing hazards and controls, risk before and after ratings and includes a section which can verify current suppression. Form to be submitted to Brett Nelson of Select Solutions for approval. * Asplundh has recently completed a full revision of our Safe Work Practices and created a comprehensive suite of Safe Work Method Statements which are highly detailed, current and relevant to all National Regulations including Victoria. Copies to be submitted to Brett Nelson of Select Solutions for approval. * A safety /training presentation specific to hazard identification and risk management created by Asplundh`s Safety Department is delivered to all Asplundh and Asplundh subcontract personnel working on SP Ausnet contracts. | 67 POUND ROAD, WARRANDYTE VIC 3113 | 125679 |  | Within clearances |  |  | Not followed | Phase to earth |  | IMS218536 Tree clearer, advised of branch with rope attached on overhead due to tree clearing at LIS 1205679. Tree clearer advised he had not recieved permission to proceed from CEOT or his Supervisor. He was also unable to advise the application he was working under. No suppression on network where work was being performed. Ambulance attended and tree clearer was taken to Box Hill hospital. On the morning of Wednesday 7th October 2015 a two person tree climbing crew employed by Taylors Trees, an approved Asplundh subcontractor, set out to complete three tree climbing jobs in the Warrandyte area on feeder RWN 26. The crew arrived at their first intended location and identified what they believed was the correct tree. They have then approached and made contact with the resident at 62 Pound Rd, Warrandyte, who advised as it was early would they mind coming back around 9 am in the morning. The crew have complied with this request and attended and completed work at the next location at 35 Hutchinson Ave, Warrandyte. Upon completion of the work the crew has returned to 62 Pound Rd and rigged the tree in preparation for trimming. During the course of the trimming the Climber has cut a limb approximately 6 metres long and 125mm diameter at the determined cut point. The Observer has attempted to control the limb with the attached rope, however it has fallen ninety degrees to the intended direction of fall and come into contact with one phase of the 22kV line. The Climber has stated he managed to push the limb away from himself using both hands and it has remained suspended approximately one meter below the cut point. The Observer has tied off the limb whilst at the same time the Climber has lowered himself to the ground. The crew has then commenced initial notifications and called for an ambulance as the climber believed he may have sustained an electric shock. | Conductor (bare) | 0 | 0 | 0 |  | rwn26 | Vegetation: Trees Incident | Medical attention (first aid/doctor/hospital) | 42195 |  |  | 47 | Residential |  | 20151006SPN_2 | Infrastructure (network-based) | -37.7425 | 145.1995 | 1 | AusNet Services Distribution | Report | 141 | 0.033315 | 22kV AC | Moorabbin Airport | 3113 | Warrandyte | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the HVABC was repaired under Access Permit conditions. | 14 CHURCH ROAD, DONCASTER VIC 3108 |  |  | Heat | Unlikely | Electrical breakdown |  |  | 1 | At 1209hrs on 06/10/2015, 22kV feeder DC 01 circuit breaker reclosed to lockout affecting 2169 customers. During strong northerly winds on the Total Fire Ban day, a 22kV HVABC conductor failed mid-span near the CHP located in Church Road, Doncaster. The location is in close proximity to the freeway easement at the rear of the Doncaster Zone Substation. A large grass fire commenced after molten metal fell into the dry grass causing a grass fire with multiple fire trucks in attendance. A request has been made to ZNX for the failed section of the of HVABC is quarantined to assist determining the exact cause or contributing factors. | Conductor (ABC);Aluminium | 0 | 0 | 0 |  | DC 01 | The a 22kV HVABC conductor failed mid-span. Cause under investigation. | Loss of supply;Grassfire | 42165.5062 |  | Small: 10 - 1000 sq.m | 51 | Public space |  | 20151007UTD_2 | Infrastructure (network-based) | -37.7957 | 145.1363 | 1 | United Energy Distribution | Report | 64 | 0.016631 | 22kV AC | Moorabbin Airport | 3108 | Doncaster | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. The 200amp red and white LV fuses had operated and were replaced when supply was restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 28 KANOWNA STREET, HASTINGS VIC 3915 |  |  | Blown branch/vegetation |  |  |  |  | 1 | At 1845hrs on 06/10/2015, 22kV feeder HGS 23 circuit breaker reclosed to lockout affecting 4582 customers During strong windy conditions, a tree branch contacted the HV conductors in Kanowna Street, Hastings that resulted in a HV conductor contacting the LV conductors below. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Kanowna-Haddock" ground type substation. The LEI confirmed a high voltage injection occurred (MOR 1508) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | HGS 23 | Vegetation: Trees Incident | HV injection | 42165 |  |  | 52 | Industrial |  | 20151007UTD_3 | Infrastructure (network-based) | -38.2891 | 145.187 | 1 | United Energy Distribution | Report | 65 | 0.014991 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Trees
Emergency high voltage switching was completed with the 22kV feeder HGS33 isolated to allow the attending CFA crew to extinguish the pole fire. The HV droppers were replaced under Access Permit conditions when the CFA had made the site safe. The pole requires replacement and was assessed as load worthy for overnight. Detailed planning is required for the pole change due to the assets on the pole. | 3 DANDENONG-HASTINGS ROAD, TYABB VIC 3913 | 9679248 |  |  | Unlikely | Electrical breakdown |  |  | 1 | At 2324hrs on 06/10/2015, ACR MT0492 located in Tyabb-Tooradin Road on 22kV feeder HGS33 reclosed and held. The section of the 22kV feeder was patrolled and the cause was found to be a fault at "Tyabb TDN- Denham" pole type substation that is located on Westernport Highway, north of the Frankston-Flinders Road roundabout at pole No. LIS 9679248. The pole is a double circuit 66kV, 22kV strain construction with a 2 phase pole type substation attached that supplies two customers. The pole fire has occurred on the timber pole near where the HV dropper clamps are located between the overhead conductors to the transformer and the CFA were in attendance. | Conductor (insulated);Aluminium | 0 | 0 | 0 |  | HGS 33 | Suspect tracking was the cause | Pole-top fire;Loss of supply | 42165.9819 |  | Localised: less than 10 sq.m | 55 | Roadway |  | 20151009UTD_2 | Infrastructure (network-based) | -38.2704 | 145.1897 | 1 | United Energy Distribution | Report | 102 | 0.033125 | 22kV AC | Moorabbin Airport | 3913 | Tyabb | Pole
A faults crew attended and completed a NST that passed and tested the area for any live wires and confirmed the site was safe with supply left on. The occupier was advised that a LEI would be attending the following morning to complete installation tests during daylight hours. The LEI attended and completed installation tests that could not identify any faults and zero volts at various parts of the installation. It was concluded the unsafe situation was created when the meter was replaced by a Service Stream employee on 10/05/2012 during the mass meter rollout. A request has been made to Service Stream for before and after photos to confirm the initial investigations findings. Following the conclusion of the meter rollout, Service Stream has disbanded its team of meter installers and has no contracts in place presently with United Energy. | 53 DERINYA DRIVE, FRANKSTON SOUTH VIC 3199 | [5 empty] | Poor workmanship | Phase to earth |  | The customer received an electric shock to has hand and contacted a friend (Tenix employee) to investigate. The Tenix employee removed a live fuse wire that was hanging from the meter and contacted United Energy. The occupier went to his switchboard to replace a fuse which had blown and made accidental contact with a coil of spare fuse wire located directly below the meter and received an electric shock to his hand. He was standing in bare feet on the concrete floor when the contact was made. The customer called a friend who is a Tenix employee (Jody Friend 0409 082 695) who attended and found the tail of the spare fuse coil had been caught behind the meter terminal cover. Following the installation of the meter, it appears a tail from the coil of fuse wire sitting at the bottom of the meter enclosure, somehow was caught behind the terminal cover when it was being replaced. The tail managed to enter the load side active terminal of the meter and energised the spare fuse coil to 240v. The Tenix employee removed the fuse coil from behind the meter and ensured the site was safe. He contacted the United Energy faults number advising that a live wire was hanging out of the meter. | No failed asset | 0 | 0 | 0 |  |  | Following the installation of the meter, it appears a tail from the coil of fuse wire sitting at the bottom of the meter enclosure, somehow was caught behind the terminal cover when it was being replaced. The tail managed to enter the load side active terminal of the meter and energised the spare fuse coil to 240v | Minor shock | 42165.9688 |  |  | 57 | Residential |  | 20151009UTD_3 | Infrastructure (network-based) | -38.1752 | 145.1244 | 1 | United Energy Distribution | Report | 73 | 0.032015 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston South | Other
Site made safe and balloons removed from the conductors | 81 HIGH STREET, NEWPORT VIC 3015 |  | Recreation - Helium (party) balloons | [5 empty] | 1 | Balloons caught in High Voltage conductors in Rosshire Rd caused an AMPAC to give way in High St and the wire fell setting the tree on fire. | Conductor (bare) | 0 | 0 | 0 |  | NT003 | Balloons cause connection to fail | Grassfire | 42287.5743 |  | Localised: less than 10 sq.m | 58 | Residential |  | 20151012JEM_1 | Infrastructure (network-based) | -37.839 | 144.8862 | 1 | Jemena | Report | 2866 | 0.022087 | 22kV AC | Essendon Airport | 3015 | Newport | Other
Crew isolated supply and undertook repairs | 151 PHILLIPS ROAD, KERANG EAST VIC 3579 |  |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 1 | Whilst in the process of by-passing a SWER ACR for planned works, a Powercor crew closed the installed high voltage by-pass fuse. The crew then opened the ACR unit, and the HV fuse began to candle and catch fire, the crew promptly closed the ACR unit again, which extinguished the fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out | Other electricity related | 42226.3785 |  | Negligible: no ground fire | 59 |  |  | 20151012PWA_1 | Infrastructure (network-based) | -35.7636 | 144.0133 | 1 | Powercor | Report | 76 | 0.0042338 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3579 | Kerang East | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. The faults crew replaced the 3 damaged boric acid HV fuse units and the two phase overhead service supplying 28 Franklin Road before supply was restored. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 33 FRANKLIN ROAD, DONCASTER EAST VIC 3109 | 7062538 |  | Lightning | Unlikely | HV injection;Electrical breakdown |  |  | 1 | At 7.05PM on 10/10/2015, 66kV feeder TSTS-DC No 2 circuit breaker locked out but no customers were affected. At the same time, 22kV feeder DC 10 and ACR DT7125 located in Beverley Street reclosed to lockout affecting 3650 customers. During stormy conditions, a lightning strike caused damage to multiple premises in Franklin Road, Doncaster East supplied from the west circuit of "Franklin-Leeds" substation. It appeared the lightning bolt directly struck pole No. LIS 7062538 that damaged 3 x HV boric acid fuse units at DT1140. The faults crew requested that a LEI attend as a HVI was suspected to customers connected to the white phase. The LEI confirmed a high voltage injection occurred (BWD 1517) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Boric acid;Pole mounted | 0 | 0 | 0 |  | TSTS-DC 66kV, DC10 22kV | During storm conditions, lightning struck a HV LV pole in Franklin Road, Doncaster East | HV injection;Loss of supply | 42287.7951 |  |  | 60 | Roadway |  | 20151012UTD_1 | Infrastructure (network-based) | -37.7897 | 145.157 | 1 | United Energy Distribution | Report | 77 | 0.02261 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3109 | Doncaster East | Lightning
Crew isolated supply and undertook repairs | 2495 GREAT OCEAN ROAD, HORDERN VALE VIC 3238 |  |  |  |  | Leakage |  |  |  | A Powercor Asset Inspector reported the top of a SWER pole burnt off at the above location. On arrival the crew found that a pole fire had occurred on a SWER pole which burnt the pole causing the top section of the pole to fall to the ground, and breaking the tie on the SWER conductor, with the conductor remaining aloft. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42257.4917 |  | Negligible: no ground fire | 68 |  |  | 20151014PWA_1 | Infrastructure (network-based) | -38.7696 | 143.4953 | 1 | Powercor | Report | 87 | 0.0045301 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3238 | Hordern Vale | Pole
Crew isolated supply and undertook repairs | 251 BOOROOK ROAD, COORIEMUNGLE VIC 3268 |  | Vehicle | [6 empty] | A customer reported that a tractor had pulled a wire down at the above location. On arrival the crew found that the customer (Johan Scholte) was driving a tractor and contacted and broke a LV service cable, pulling the cable from the POA end and causing it to fall to the ground across the tractor. There was no ground fire. There were no reported injuries or third party property damages. The service height was measured following repairs at 3.7m at the point of contact (driveway). | No failed asset | 0 | 0 | 0 |  |  | Tractor contacted overhead line | No Go Zone (contact) | 42257.6917 |  |  | 69 |  |  | 20151014PWA_2 | Infrastructure (network-based) | -38.5498 | 143.113 | 1 | Powercor | Report | 88 | 0.020721 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Cooriemungle | Vehicle
Crew isolated supply and undertook repairs | 5 DRURY LANE, HOPPERS CROSSING VIC 3029 |  | Vehicle | [5 empty] | 2 | A customer reported that their service cable had been broken by a truck at the above location. On arrival the crew found that a truck (R ego: ZLT 173, Driver: Raj, Ph:0468 352 729 Melbourne Fast Movers, 4 McFadzean Ave, Reservoir, Vic 3073) had contacted a LV service cable breaking the cable which fell to the ground. The incident also caused damage to the customers POA. There was no ground fire. There were no reported injuries. Following repairs the cable was measured at 3.7m over the driveway. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV overhead service cable | Damage to network assets | 42226.4625 |  |  | 75 |  |  | 20151015PWA_5 | Infrastructure (network-based) | -37.8783 | 144.684 | 1 | Powercor | Report | 94 | 0.013858 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Vehicle
Crew isolated supply and undertook repairs | 196 DRAFFINS ROAD, CARDIGAN VIC 3352 |  | Vehicle | [6 empty] | A customer reported that a service line had been pulled down by their truck at the above location. On arrival the crew found that a vehicle (Owner: Allan Pearson, Ph: 0408 457 902) had contacted a LV service cable breaking the cable at the POA end and causing it to fall to the ground. There were no reported injuries or third party property damages. Following repairs, the height of the cable was measured at 3.6m over the driveway at the point of contact. There was no ground fire. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service | No Go Zone (contact);Damage to network assets | 42287.4931 |  |  | 82 |  |  | 20151016PWA_4 | Infrastructure (network-based) | -37.5073 | 143.7455 | 1 | Powercor | Report | 106 | 0.030769 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Cardigan | Vehicle
Crew isolated supply and undertook repairs | 7 THOMPSON STREET, ABBOTSFORD VIC 3067 |  | Vehicle | [6 empty] | A customer reported a service cable had been pulled down by a vehicle at the above location. On arrival the crew found that a LV service cable had been contacted by an unknown vehicle, causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. Following repairs the cable height was measured at 7.1m above the road. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | No Go Zone (contact);Damage to network assets | 13/10/2015 14:06 |  |  | 90 |  |  | 20151020PWA_4 | Infrastructure (network-based) | -37.8103 | 145.003 | 1 | CitiPower | Report | 117 | 0.0041748 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | Vehicle
Crew isolated supply and undertook repairs | 78 GRAHAM STREET, NEWPORT VIC 3015 |  | Working too close to underground cables | [6 empty] | A contractor reported that they had hit a service cable at the above location. On arrival the crew found that the contractor (Citi Wide Bobcat / tipper hire contractors, Ph:0402 257 125) were excavating on a building site, when their excavator contacted a LV service causing damage to the cable and loss of supply to 80 Graham Street, Newport. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Excavator contacted LV service cable | No Go Zone (contact);Damage to network assets | 14/10/2015 9:45 |  |  | 91 |  |  | 20151020PWA_5 | Infrastructure (network-based) | -37.8345 | 144.8688 | 1 | Powercor | Report | 5300 | 0.026537 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Vehicle
Crew inspected line for damage and cause of fire, nothing found | 455 BULMANS ROAD, MELTON WEST VIC 3337 |  |  |  |  | Unknown technical factor |  |  |  | MFB reported a fire at the above location. On arrival the crew found that a grass fire (Approx 300 sqm) had occurred around the base of a 22kV/LV substation pole. The crew could not find anything that would link the pole to the initiation of the fire. There were no reported injuries. | Outdoor | 0 | 0 | 0 |  |  | Crew unable to determine cause | Grassfire | 42257.5278 |  | Localised: less than 10 sq.m | 94 |  |  | 20151020PWA_6 | Infrastructure (network-based) | -37.6578 | 144.5548 | 1 | Powercor | Report | 123 | 0.03853 | Not applicable | Melbourne Airport | 3337 | Melton West | AF Other
A LEI and faults truck attended and completed installation tests to determine the cause. Voltage tests between an independent earth and various points of the electrical installation, including the Distributors assets, identified a defective neutral connection at the service pole after 65v was measured on the water piping system. The faults crew proceeded to clean, grease and reconnect the neutral connection after the corroded aluminium line tap was identified as the cause. The premise is located in close proximity to Port Phillip Bay and salt borne contaminants was the probable cause. The LEI tested the installation and measured zero volts on the water piping system after the completion of the repairs. | 592 ESPLANADE, MOUNT MARTHA VIC 3934 |  |  | Prone to salt deposition | Likely | Corrosion |  | Phase to earth | 2 | The customer had received slight electric shocks from the shower taps and contacted a REC. A REC contacted the United Energy faults and emergencies number after being contacted by the resident who received electric shocks from the shower taps when standing on the wet shower base. | Services cable;Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | The faults crew proceeded to clean, grease and reconnect the neutral connection after the corroded aluminium line tap was identified as the cause. The premise is located in close proximity to Port Phillip Bay and salt borne contaminants was the probable cause. | Minor shock | 16/10/2015 14:10 |  |  | 102 | Residential |  | 20151021UTD_4 | Infrastructure (network-based) | -38.2483 | 145.0291 | 1 | United Energy Distribution | Report | 131 | 0.02926 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | Connection
A LEI and faults truck attended and completed installation tests to determine the cause. Voltage tests between an independent earth and various points of the electrical installation, including the Distributors assets, identified a defective neutral connection at the pole end with 115v measured on the water piping system. The faults crew proceeded to replace the corroded aluminium line tap that was identified as the cause. The premise is located in close proximity to Western Port Bay and salt borne contaminants was the probable cause. The LEI tested the installation and measured zero volts on the water piping system after the completion of the repairs. A NST passed and supply was left on. | 85 LORIMER STREET, CRIB POINT VIC 3919 |  |  | Prone to salt deposition | Likely | Corrosion |  | Phase to earth | 2 | The customer advised that he received a strong tingle from the taps but he's okay. The occupier received a strong electric shock from the shower taps when standing on the wet shower base and contacted the United Energy faults and emergencies number. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | The faults crew proceeded to replace the corroded aluminium line tap that was identified as the cause. The premise is located in close proximity to Western Port Bay and salt borne contaminants was the probable cause. | Minor shock | 17/10/2015 18:30 |  |  | 103 | Residential |  | 20151021UTD_5 | Infrastructure (network-based) | -38.3563 | 145.1992 | 1 | United Energy Distribution | Report | 133 | 0.01123 | Low voltage AC (<1kV) | Moorabbin Airport | 3919 | Crib Point | Connection
Crew isolated supply and undertook repairs | 214 MADANG ROAD, ROBINVALE IRRIGATION DISTRICT SECTION E VIC 3549 |  |  |  |  | Leakage |  |  | 1 | Vic Fire reported a wire down and fire at the above location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the crossarm causing the end of the arm to break off however the conductor remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 17/10/2015 12:32 |  | Negligible: no ground fire | 104 |  |  | 20151022PWA_1 | Infrastructure (network-based) | -34.6637 | 142.7641 | 1 | Powercor | Report | 134 | 0.00068981 | 22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section E | Crossarm
Crew isolated supply, trimmed the tree and undertook repairs | 15 ALDRIN COURT, WHITTINGTON VIC 3219 |  |  | Within clearances | Unlikely |  |  |  | 2 | CFA reported a pole fire at the above location. On arrival the crew found that an LV overhead service cable had been rubbing on a customer responsible tree resulting in a fire in the tree and also a ground fire (approx. 2m x 5m) on private property. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire;Other vegetation | 20/10/2015 21:41 | 1 | Localised: less than 10 sq.m | 105 | Residential |  | 20151022PWA_2 | Infrastructure (network-based) | -38.176 | 144.3952 | 1 | Powercor | Report | 277 | 0.00739 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Whittington | Trees
Crew isolated supply and undertook repairs | 1551 LISMORE-PITFIELD ROAD, WALLINDUC VIC 3351 |  | Working too close to underground cables |  | Highly likely |  |  |  | 1 | REC reported excavator had dug up SWER earth cable at the location. On arrival the crew found that a property owner (Graham Croft, Ph: 0418 372 759) was using an excavator and contacted a SWER earth cable breaking the cable. There was no ground fire. There were no reported injuries or third party property damages. | Outdoor;No failed asset | 0 | 0 | 0 |  |  | Excavator contact | No Go Zone (contact);Damage to network assets | 15/10/2015 9:35 |  |  | 113 | Agricultural |  | 20151023PWA_1 | Infrastructure (network-based) | -37.8465 | 143.5045 | 1 | Powercor | Report | 5299 | 0.03756 | Earthing cable | Ballarat Aerodrome | 3351 | Wallinduc | Dug up
Crew isolated supply and undertook repairs | 80 GHERINGHAP STREET, GEELONG VIC 3220 |  |  |  | Unlikely | Leakage |  |  | 2 | CFA reported a fire on a pole at the above location. On arrival the crew found that a pole fire had occurred on a 22kV pole which had damaged the top section of the pole. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  | GCY022 | Pole fire | Pole-top fire | 22/10/2015 5:31 | 1 | Negligible: no ground fire | 115 | Roadway |  | 20151023PWA_2 | Infrastructure (network-based) | -38.1503 | 144.356 | 1 | Powercor | Report | 5298 | 0.014177 | 22kV AC | Avalon Airport | 3220 | Geelong | Pole
Crew Isolated supply for repairs | 23 GRANT STREET, BRUNSWICK VIC 3056 |  | Vehicle |  | Likely |  |  |  | 2 | MFB reported that a service cable was down on a truck the location. On arrival, the CitiPower crew found that a LV service cable had been contacted by an unknown vehicle, causing the cable to break and fall to the ground and also caused damage to the POA of a connected premise. The truck was not on site when the crew arrived. A builder working nearby reported to the crew that the rego number for the truck was QPE 159. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Vehicle contacted LV service cable | No Go Zone (contact);Damage to network assets | 20/10/2015 12:14 |  |  | 116 | Roadway |  | 20151023PWA_3 | Infrastructure (network-based) | -37.757 | 144.973 | 1 | CitiPower | Report | 173 | 0.019351 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
Crew isolated supply and undertook repairs | 508 CHAPEL ROAD, MUCKATAH VIC 3644 |  |  |  | Unlikely | Rot |  |  | 2 | VicFire reported a fire at the location. On arrival the crew found that a LV crossarm had broken causing the LV conductors to clash resulting in a ground fire (approx. 15m x 2m) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Broken LV crossarm | Grassfire | 24/10/2015 12:40 | 1 | Small: 10 - 1000 sq.m | 121 | Roadway |  | 20151027PWA_2 | Infrastructure (network-based) | -36.0079 | 145.692 | 1 | Powercor | Report | 276 | 0.0036609 | Low voltage AC (<1kV) | Shepparton Airport | 3644 | Muckatah | Crossarm
Crew checked assets for damage, none found | 960 OLD DOOKIE ROAD, PINE LODGE VIC 3631 |  |  | Bird | Unlikely |  |  |  | 2 | VicFire reported a fire at the above location. On arrival the crew found that a bird had cause a flashover on a 22kV/LV substation pole and had fallen to the ground resulting in a ground fire (approx.. 10m x 10m) on the road reserve and adjoining private property. There were no reported injuries. | Insulators | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 24/10/2015 19:11 | 1 | Localised: less than 10 sq.m | 122 | Roadway |  | 20151027PWA_3 | Infrastructure (network-based) | -36.3779 | 145.5235 | 1 | Powercor | Report | 275 | 0.0090382 | 22kV AC | Shepparton Airport | 3631 | Pine Lodge | Animal
The fault crew isolated supply to the street lantern and referred to CEOT for replacement. | 1 MORRIS ROAD, UPWEY VIC 3158 | 1032867 |  |  |  | Electrical breakdown |  | Phase to neutral |  | Fire Brigade called in Street Light fire, Fault Crew Dispatched. Fault crew responded to a report from the Fire Brigade regarding a street light on fire in Morris Rd on the North Side of Burwood Hwy. Upon arrival the crew found that a 250 Watt HPS lantern had caught fire (it was extinguished by the time they arrived). No damage to any other assets or property. | Public lighting | 0 | 0 | 0 |  | fgy23 | Equipment failure. | Pole-top fire | 22/10/2015 20:25 |  | Negligible: no ground fire | 132 | Roadway |  | 20151029SPN_1 | Infrastructure (network-based) | -37.9029 | 145.3287 | 1 | AusNet Services Distribution | Report | 186 | 0.0015162 | Low voltage AC (<1kV) | Moorabbin Airport | 3158 | Upwey | AF Other
Crew isolated supply and undertook repairs | 37 HAZEL STREET, CAMBERWELL VIC 3124 |  | Vehicle |  | Unlikely |  |  |  |  | MFB reported that a truck had brought down a service wire at the location. On arrival the crew found that a LV service cable had been contacted by a vehicle breaking the cable and causing it to fall to the ground. The truck had left the scene by the time crew arrived. Following repairs the crew measured the cable height at 4.6m. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Contact by vehicle/load | No Go Zone (contact);Damage to network assets | 29/10/2015 15:15 |  |  | 150 | Residential |  | 20151030PWA_14 | Infrastructure (network-based) | -37.8435 | 145.0648 | 1 | CitiPower | Report | 254 | 0.039512 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Vehicle
Crew secured site and arrange repairs | 17 FAIRWAYS BOULEVARD, DEER PARK VIC 3023 |  | Theft |  | Unlikely |  |  |  | 2 | A Powercor employee reported a copper theft at the location. On arrival the crew found that several Kiosk Substations in the area had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 26/10/2015 19:13 |  |  | 140 | Public space |  | 20151030PWA_4 | Infrastructure (network-based) | -37.7798 | 144.7691 | 1 | Powercor | Report | 262 | 0.03776 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
Crew secured site and arrange repairs | 20 WESTMINSTER PARKWAY, DERRIMUT VIC 3030 |  | Theft |  | Unlikely |  |  |  | 2 | A Powercor employee reported a copper theft at the location. On arrival the crew found that several Kiosk Substations in the area had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 26/10/2015 19:13 |  |  | 141 | Public space |  | 20151030PWA_5 | Infrastructure (network-based) | -37.7832 | 144.7573 | 1 | Powercor | Report | 263 | 0.040163 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
Attending Faults crew and attending LEI located and isolated the cable at the FOLCB on Sub Pole 1400960 (pole is located on the property). NCID 73814 was issued to the home owner to have an REC disconnect the damaged cable from the installation and make safe. Control Room (CEOT) notified Inspector required to reconnect premises once CES has been issued from REC. Installation Left OFF SUPPLY. | 2991 HEALESVILLE-KINGLAKE ROAD, KINGLAKE VIC 3763 | 1400960 |  |  |  | Unknown technical factor | Ineffective planning/procedures/processes | Phase to earth | 2 | Michael Laukart was walking around a vacant block at 2991 Healesville Kinglake Road, Kinglake, when he received an electric shock as he made simultaneous contact with his hand as he touched an exposed cable laying on the ground whilst standing on the ground. The customer received tingles from u/g cable that did supply a house that was destroyed by fire years ago. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets revealed the conductor was at 240 Volts potential. This condition caused current to flow through the the general mass of earth to the substation located on the property. | No failed asset | 0 | 0 | 0 |  | klk1 | An exposed underground consumer's mains cable laying on the ground. | Minor shock | 42195.8611 |  |  | 159 | Residential |  | 20151102SPN_4 | Infrastructure (network-based) | -37.5433 | 145.3688 | 1 | AusNet Services Distribution | Report | 303 | 0.037784 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3763 | Kinglake | Other
Crew isolated section, made safe and investigating. Pole replaced by crew 12.5/8 wood SWER Intermediate. | 263 HOLLANDS LANDING ROAD, MEERLIEU VIC 3862 | 1601294 |  | Lightning |  |  |  | Phase to earth | 2 | Reports of pole smouldering. Crew on arrival advised pole had burnt down almost to the base (LIS#1601294) as the pole was struck by lightning. It was an intermediate pole with fog pin type insulators with 3/12 steel conductor. No ground fire occurred as the pole was sitting in water. | Pole (wood) | 0 | 0 | 0 |  | bdl1 | Pole struck and destroyed by lightning. Thunderstorm activity. | Pole-top fire | 42074 |  | Negligible: no ground fire | 171 | Agricultural |  | 20151104SPN_1 | Infrastructure (network-based) | -38.0135 | 147.4199 | 1 | AusNet Services Distribution | Report | 305 | 0.017664 | 12.7kV AC (SWER) | Bairnsdale Airport | 3862 | Meerlieu | Lightning
Crew made safe, replaced the fuse tube and restored supply to customer. | 62 WILLIAMS ROAD, ROSEDALE VIC 3847 | 2613539 |  |  |  | Insulator |  |  | 2 | On arrival, crew found EDO fuse tube burnt, LIS#2613539. Crew called to All Supply Failure to find EDO fuse tube burnt in half. No fire was present. | EDO fuse | 0 | 0 | 0 |  | tgn41 | Burnt EDO fuse tube. Equipment failure. | Pole-top fire | 42074 |  | Negligible: no ground fire | 177 | Agricultural |  | 20151104SPN_2 | Infrastructure (network-based) | -38.1658 | 146.7822 | 1 | AusNet Services Distribution | Report | 306 | 0.024186 | 22kV AC | Morwell (Latrobe Valley Airport) | 3847 | Rosedale | Fuse
Crew undertook repairs | 465 DOHERTYS ROAD, TRUGANINA VIC 3029 |  | Theft | [6 empty] | A Powercor employee reported that the earth has been stolen from the substation at the incident location. On arrival the crew found that the substation earth had been stolen from a pole type substation. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Stolen earthing cable | Damage to network assets | 30/10/2015 13:33 |  |  | 189 | Roadway |  | 20151106PWA_4 | Infrastructure (network-based) | -37.8239 | 144.7355 | 1 | Powercor | Report | 291 | 0.019903 | Earthing cable | Laverton Raaf | 3029 | Truganina | Other
A faults truck attended and the crew proceeded to complete a NST that failed. They commenced to check connections prior to the LEI attending and identified loose connections at the LVABC interface at pole number LIS 2320916. The LEI tested the electrical installation after the rectification work was completed and measured 1.1v with a load of 45amps applied. A NST passed and the premise was left on supply. | 20 CUMMINS GROVE, MALVERN VIC 3144 |  |  |  |  | Electrical breakdown | Poor workmanship | Phase to earth | 2 | Customer advised he received a shock from the shower head and lights have been dimming for the past two weeks. The occupier contacted the United Energy faults and emergencies number advising that he received slight electric shocks from the shower head and lights have been fluctuating for the past two weeks. | No failed asset | 0 | 0 | 0 |  |  | The LEI attending and identified loose connections at the LVABC interface at pole number LIS 2320916. | Minor shock | 30/10/2015 16:00 |  |  | 185 | Residential |  | 20151106UTD_2 | Infrastructure (network-based) | -37.8646 | 145.036 | 1 | United Energy Distribution | Report | 287 | 0.0057708 | Low voltage AC (<1kV) | Moorabbin Airport | 3144 | Malvern | Connection
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. REC No. 11105 (Robbie 0458 616 240) provided non-prescribed CES No. 507359571 and supply was re-connected after a damaged smart meter with no display was replaced. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 10 CENTRAL AVENUE, DANDENONG NORTH VIC 3175 | 9830074 |  | Lightning |  | HV injection |  |  | 2 | Caller reports lights are dimming and most of the appliances not working after the storm. Following storm activity, a customer at No. 10 Central Avenue reported appliance damage and a faults crew attended to investigate the cause following a lightning strike on a pole outside the property. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Brady - Gladstone" substation as the FOLCB on pole No. LIS 9830074 appeared to be damaged. The LEI confirmed a high voltage injection occurred (KEY 1505) affecting 2 customers who reside in the vicinity that sustained minor damage to electrical appliances and equipment. There was lightning strikes on various 22kV feeders earlier this morning in the Dandenong and Noble Park areas. | Pole top | 0 | 0 | 0 |  | LD 33 | The faults crew attended to investigate the cause following a lightning strike on a pole outside the property. | HV injection;Loss of supply | 31/10/2015 13:56 |  |  | 186 | Residential |  | 20151106UTD_3 | Infrastructure (network-based) | -37.955 | 145.2102 | 1 | United Energy Distribution | Report | 288 | 0.0066493 | 22kV AC | Moorabbin Airport | 3175 | Dandenong North | Lightning
Initial CEOT report: Crew isolated supply and made site safe. Arranged repair with Supervisor. Investigation details: Tenix Downer changed the pole/crossarm. | 773-775 MAROONDAH HIGHWAY, COLDSTREAM VIC 3770 | 1409343 |  | Prone to dust deposition |  | Leakage |  | Phase to phase | 2 | Initial CEOT report: Lis pole 14-09343 burnt at middle at pole top. Conditions misty rain. Investigation details: The pole fire appears to have started on the center phase (W) when moisture from the rain has travelled down the old brown fog pin type insulator causing the king bolt to become energised which has caused the xarm/top of the pole to ignite. The fire burnt through the top of the pole and part of the xarm. | Pole (wood) | 0 | 0 | 0 |  | ldl23 | Voltage / current tracking from fog pin type insulator to king bolt on crossarm caused by insulator pollution (salt / dust). | Pole-top fire | 42135 |  | Negligible: no ground fire | 204 |  |  | 20151112SPN_1 | Infrastructure (network-based) | -37.684 | 145.4759 | 1 | AusNet Services Distribution | Report | 315 | 0.037334 | 22kV AC | Moorabbin Airport | 3770 | Coldstream | Pole
Local Field Team Manager has arranged for ThermoView and actions necessary to rectify the bridge insulation. | Firmins Ln, Hazelwood North, VIC 3840 | 2615189 | Bird/ caused flashover.;Other | Bird |  | Insulator | No work practice factor | Phase to phase | 1 | CEOT - contacted fault crew and advised of pole fire and CFA on-site at Crn of Tramway Road and Firmans Lane, Morwell. (Lis NO 2615189). Reported magpies in the area. On arrival the fault crew found a small burnt patch of grass (0.1 sq, m) and noticed poly had melted off the HV bridge from line to a 3 phase two insulator air break switch. Burnt patch size 10cm X 10cm (note: grassed area, green, no dry grass near site). Feeder CB tripped. | Melted insulation off HV conductor bridge from overhead HV line to Air Break Switch.;Other | 0 | 0 | 0 |  | mwts32 | Bird Incident | Grassfire | 42227.5 |  | Low: Less than 5 sqm | 205 | Roadway |  | 20151112SPN_2 | Infrastructure (network-based) | -38.248 | 146.4315 | 1 | AusNet Services Distribution | Report | 317 | 0.017442 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 |  | Pole
Crew isolated supply and undertook repairs | 72A JOHNSTON STREET, COLLINGWOOD VIC 3066 |  |  |  |  | Unknown technical factor |  |  | 2 | MFB reported a fire in a street light at the incident location. On arrival the crew found that a fire had started in a street lighting lantern. There was no ground fire. There were no reported injuries or third party property damages. | Public lighting | 0 | 0 | 0 |  |  | Crew unable to determine | Pole-top fire | 42105.0819 |  | Negligible: no ground fire | 216 | Roadway |  | 20151113PWA_10 | Infrastructure (network-based) | -37.7993 | 144.9873 | 1 | CitiPower | Report | 329 | 0.03155 | Low voltage AC (<1kV) | Essendon Airport | 3066 | Collingwood | AF Other
Crew isolated supply and undertook repairs | 1295 LEMNOS-COSGROVE ROAD, LEMNOS VIC 3631 |  |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire on a transformer at the incident location. On arrival the crew found that a connection had overheated in a pole mounted FOLCB causing the box to catch fire. Crew found evidence of bird nest at FOLCB. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Pole-top fire | 42135.6813 |  | Negligible: no ground fire | 217 | Roadway |  | 20151113PWA_11 | Infrastructure (network-based) | -36.3465 | 145.478 | 1 | Powercor | Report | 330 | 0.0012801 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Lemnos | Connection
Crew isolated supply and undertook repairs | 166 MOORE ROAD, FAIRY DELL (NORTH) VIC 3561 |  |  |  |  | Leakage |  |  | 1 | A field crew attending an outage found that a crossarm fire had occurred on a 22kV pole which burnt the crossarm only.. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 31/10/2015 8:26 |  | Negligible: no ground fire | 219 | Roadway |  | 20151113PWA_13 | Infrastructure (network-based) | -36.3366 | 144.732 | 1 | Powercor | Report | 332 | 0.015264 | 22kV AC | Bendigo Airport | 3561 |  | Crossarm
Made safe | 9 MELBOURNE ROAD, WILLIAMSTOWN VIC 3016 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Council trees came down causing LV conductors to fall to the ground | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/10/2015 0:00 |  |  | 233 | Residential |  | 20151118JEM_1 | Infrastructure (network-based) | -37.8637 | 144.8987 | 1 | Jemena | Report | 351 | 0.035258 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Trees
Initial CEOT report: Fault crew made site safe, inspector dispatched to investigate. Investigation report: Crew made necessary repairs, replaced a SWER transformer and the supply was restored to the HV line. Visited multiple substations - all back on supply around 8pm. A generator was arranged for the customer's water pressure pump and freezer. The customer was required to engage a REC to repair or replace the electrical Installation. | 175 MCNAUGHTONS ROAD, WILD DOG VALLEY VIC 3953 | 2004810 |  | Lightning |  |  |  | Phase to earth | 2 | Initial CEOT report: Customer reports of damage in the area and power is out. Fault truck attended and found a wire down between poles 004275 & 2004810. Transformer Rusmussen 3 also damaged. Inspector confirms customer's house affected by HVI. Investigation report: AusNet Services' fault crew attended. The crew believes it was a lighting strike that either hit the power line and damaged the customer's property or vice versa, or multiple lightning strikes. Damage includes burnt out telephone line, burnt out electric fence unit and some house appliances. The line was back on supply around 6.30 pm but still had to visit multiple substations - all of them back on supply around 8 pm. Customer will not be back on supply until afternoon of 13/11/2015 due to crews having to go back and change a SWER TX. The crew organized a Leongatha depot generator for the customer's water pressure pump and for their freezer. No fire was started but there were marks on the ground - at both ends of where the line fell. Looks like the lightning super heated the conductor. The customer required to engage a REC before power can be restored to their property as significant damage has been sustained to their electrical installation and appliances. The customer's house needs rewiring. | Conductor (bare) | 0 | 0 | 0 |  | lga22 | Lightning strike. | HV injection | 42349 |  |  | 245 | Residential |  | 20151119SPN_1 | Infrastructure (network-based) | -38.3835 | 145.9142 | 1 | AusNet Services Distribution | Report | 366 | 0.024256 | Low voltage AC (<1kV);12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3953 | Wild Dog Valley | Conductor
Isolated and made safe. Investigation report: removed fuse tube and replaced with new tube. | 243 MERRIANG ROAD, MERRIANG VIC 3737 |  | No external/community cause | Bird |  | No technical cause | No work practice factor |  |  | IMS 219123. Initial CEOT report: Hung-up HV fuse at Lis 4506018, caused by bird. Investigation report: hung-up only, no burnt fuse tube / candling, no fire occurred. Therefore a Schedule 2 report is not required. This incident will be included as a statistic in the quarterly report to ESV. | EDO fuse | 0 | 0 | 0 |  |  | Bird Incident | Hung-up fuse only.;Other | 18/11/2015 12:00 |  |  | 246 |  |  | 20151119SPN_2 | Infrastructure (network-based) | -36.5602 | 146.6927 | 1 | AusNet Services Distribution | Report | 369 | 0.0339 | 22kV AC | Wangaratta Aero | 3737 | Merriang | Animal
Made safe | 460 SOMERVILLE ROAD, WEST FOOTSCRAY VIC 3012 |  |  | Fire;Industrial or urban pollution | [5 empty] | Pole fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Wood x-arm fire due to polluted(dust) insulator pin | Pole-top fire | 42074.7889 |  | Negligible: no ground fire | 253 | Industrial |  | 20151120JEM_2 | Infrastructure (network-based) | -37.8109 | 144.8676 | 1 | Jemena | Report | 377 | 0.040611 | 22kV AC | Essendon Airport | 3012 | West Footscray | Pole
Isolated cable and made safe. | 30 EXPORT ROAD, CRAIGIEBURN VIC 3064 |  | Working too close to underground cables | [5 empty] | 1 | High voltage underground cable hit by external contractor | Cable | 0 | 0 | 0 |  |  | Breach of No Go Zone. | No Go Zone (contact) | 21/11/2015 9:33 |  |  | 255 |  |  | 20151123JEM_1 | Infrastructure (network-based) | -37.6025 | 144.9475 | 1 | Jemena | Report | 379 | 0.022678 | 22kV AC | Melbourne Airport | 3064 | Craigieburn | Dug up
Crew isolated supply and undertook repairs | 184 OLD WILBY ROAD, YARRAWONGA VIC 3730 |  |  |  |  | Candled fuse |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (Approx. 50sqm) on the road reserve. There were no reported injuries. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse unit did not drop out | Grassfire | 19/11/2015 16:47 |  | Small: 10 - 1000 sq.m | 259 | Roadway |  | 20151123PWA_3 | Infrastructure (network-based) | -36.043 | 146.0137 | 1 | Powercor | Report | 386 | 0.0097141 | 22kV AC | Wangaratta Aero | 3730 | Yarrawonga | Fuse
Crew isolated supply and undertook repairs | 10 BRIDGE STREET, BATESFORD VIC 3213 |  |  |  |  | Overheated connection |  |  | 2 | A passer-by reported that they saw something fall from the pole and start a grass fire at the incident location. On arrival the crew found that a connection in a low voltage pole mounted fuse box had overheated causing hot debris to fall to the ground resulting in a ground fire (Approx. 3 sqm), on private property which self extinguished. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 20/11/2015 10:54 |  | Localised: less than 10 sq.m | 260 | Residential |  | 20151123PWA_4 | Infrastructure (network-based) | -38.0891 | 144.2876 | 1 | Powercor | Report | 388 | 0.024935 | Low voltage AC (<1kV) | Avalon Airport | 3213 | Batesford | Connection
Emergency switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. The construction crew replaced the HV strain crossarm with the LV east circuit of "Acheron-Keotong" substation isolated for the duration of the repairs. Supply was restored on completion. | 46 ACHERON AVENUE, MOUNT ELIZA VIC 3930 | 3314426 |  | Prone to salt deposition |  | Corrosion |  |  | 2 | Caller reports the support beam is on fire next to his property and the wires have moved. A pole fire occurred on a high voltage strain crossarm at timber pole LIS No. 3314426 located outside 46 Acheron Avenue, Mount Eliza as the crossarm had burnt through at the brace. The pole is situated in close proximity to Port Phillip Bay and the glass discs and brown fog type insulators had been tracking. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | MTN 22 | The pole is situated in close proximity to Port Phillip Bay and the glass discs and brown fog type insulators had been tracking. | Pole-top fire | 28/10/2015 8:30 |  | Negligible: no ground fire | 256 | Roadway |  | 20151123UTD_1 | Infrastructure (network-based) | -38.1896 | 145.0841 | 1 | United Energy Distribution | Report | 380 | 0.029983 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Crossarm
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 14 GRANGE ROAD, BLACKBURN SOUTH VIC 3130 |  |  | Lightning |  | HV injection |  |  | 2 | Caller advised of appliance damage following the storm that crossed Melbourne earlier in the day. Following storm activity, there were reports of damage to customer installations supplied from "Paramount-Bermuda" substation in Blackburn South. A LEI was dispatched as a high voltage injection was suspected following a lightning strike in the area. The LEI confirmed a high voltage injection occurred (BWD 1519) affecting 2 customers who reside in the vicinity that sustained minor damage to electrical appliances and equipment. There was lightning strikes on various distribution feeders earlier this morning throughout the United Energy area of supply. | No failed asset | 0 | 0 | 0 |  | BH 22 | Lightning | HV injection | 20/11/2015 2:30 |  |  | 261 | Residential |  | 20151124UTD_1 | Infrastructure (network-based) | -37.8466 | 145.1482 | 1 | United Energy Distribution | Report | 389 | 0.034258 | 22kV AC | Moorabbin Airport | 3130 | Blackburn South | Lightning
Crew isolated supply and undertook repairs | 11 LITTLE BOUNDARY ROAD, LAVERTON NORTH VIC 3026 |  |  |  |  | Overheated connection |  |  | 2 | A field crew attending an outage found that a connection in a pole mounted LV junction box had overheated causing debris to fall to the ground resulting in a ground fire (approx. 8 sqm) on the road reserve. There were no reported injuries. | Connection box | 0 | 0 | 0 |  | BLT016 | Overheated connection | Grassfire | 42014.3944 | 1 | Localised: less than 10 sq.m | 41 | Roadway |  | 20151005PWA_1 | Infrastructure (network-based) | -37.8246 | 144.8188 | 1 | Powercor | Report | 795 | 0.02266 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Connection
Line was isolated and prepared for EAP to inspect for any damages, non were found and line restored back to normal. Fault truck attended removed fuses issued EAP cleaned grease off conductors and inspected for damage. No damage found cancelled EAP and Restored supply. Height of 22KV O/H line at point of contact was measured at 10.0m. These ground clearance heights meet the regulatory requirement to AusNet Services ESMS Standards / Technical Manuals. Excavator driver / company has been advised of No Go Zone Requirements. | 5 SELECTORS ROAD, SEYMOUR VIC 3660 | 4708498 | Working too close to overhead lines |  |  |  |  | Phase to phase | 1 | Long reach Excavator controlled by Camillo Gianarelli from Goulburn Valley Resources (0419574470) made contact with HV Overhead conductors at Pole # 4708498. HV Fuses blew at 5697167. No injuries occured and no damage was caused. | Conductor (bare) | 0 | 0 | 0 |  | smr8 | Excavator made contact with overhead HV conductors. | Loss of supply;No Go Zone (contact) | 42014.4549 |  |  | 43 | Construction |  | 20151005SPN_2 | Infrastructure (network-based) | -36.9816 | 145.1332 | 1 | AusNet Services Distribution | Report | 52 | 0.0056991 | 22kV AC | Mangalore Airport | 3660 | Seymour | Other
Crew isolated supply and undertook repairs | 26 ANDERSON STREET W, BALLARAT CENTRAL VIC 3350 |  | Vehicle |  |  |  |  | Phase to phase | 1 | Police reported a car had hit a pole at the above location. On arrival the crew found that a car had collided with a 22kV/LV pole causing the LV conductors to contact the HV conductors resulting in a high voltage injection which caused damage to Powercor assets as well as approximately 127 customer electrical installations. Police have details of vehicle and driver. Protection operated. | Copper | 0 | 0 | 0 |  |  | Car hit pole | HV injection;Loss of supply | 42045.6049 |  |  | 48 | Roadway |  | 20151007PWA_1 | Infrastructure (network-based) | -37.5664 | 143.8592 | 1 | Powercor | Report | 282 | 0.037876 | 22kV AC | Ballarat Aerodrome | 3350 | Ballarat Central | Vehicle
Crew isolated supply and undertook repairs | 42-50 PINNACLE ROAD, ALTONA NORTH VIC 3025 |  | Vehicle | [5 empty] | 1 | A field crew attending an outage found that a car had hit a pole causing a 22kV conductor to break and fall to the ground resulting in a ground fire (approx. 3m x 20m) on the road reserve. The vehicle was not at the location when the crew arrived, the crew found signs of vehicle contact on the pole. Protection operated. There were no reported injuries. | Steel | 0 | 0 | 0 |  |  | Car hit pole | Grassfire | 42165.5771 | 1 | Small: 10 - 1000 sq.m | 53 | Roadway |  | 20151007PWA_3 | Infrastructure (network-based) | -37.8379 | 144.8151 | 1 | Powercor | Report | 1031 | 0.040242 | 22kV AC | Laverton Raaf | 3025 | Altona North | Vehicle
Emergency high voltage switching was completed and the damaged aluminium 66kV conductor was sleeved and re-sagged under Access Permit conditions. | 2 REGINA TERRACE, DONCASTER EAST VIC 3109 |  |  | Blown branch/vegetation |  |  |  |  | 1 | At 1.50PM on 06/10/2015, 66kV feeder TSTS-DC No 2 circuit breaker locked out but no customers were affected. During strong northerly winds, the TSTS - DC #2 66kV line locked out as a result of a 66kV conductor falling to the ground in Blackburn Road near the corner of Warrandyte Road, Doncaster East from pole No. LIS 7065064. The cause was due to a municipal council tree falling and bringing the 66kV conductor to the ground causing a large grass fire that damaged two properties. The fire jumped across two lanes of traffic and set alight a row of old pine trees that spread to the neighbouring properties that caused damage to fencing and the two properties. At 4 Regina Terrace, the fence was burnt away with damage sustained to the rear air-conditioner, roof mounted air-conditioner and the house and guttering. The premises windows also cracked due to the heat. Emergency services were in attendance along with United Energy Customer Relations team members to assist the home owners. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | 66kV feeder TSTS-DC No 2 | Vegetation: Trees Incident | Less than $50k damage;Other vegetation | 42165.5764 |  | Small: 10 - 1000 sq.m | 50 | Residential |  | 20151007UTD_1 | Infrastructure (network-based) | -37.752 | 145.1696 | 1 | United Energy Distribution | Report | 69 | 0.014876 | 66kV AC | Moorabbin Airport | 3109 | Doncaster East | Conductor
REC isolated supply at pole circuit breaker | 20 GILBERT STREET, ELPHINSTONE VIC 3448 |  | Working too close to underground cables | [6 empty] | A contractor working onsite reported a dug up cable at the above address. The crew arrived to find an excavator contracted to Coliban Water (operated by Contractor: Dale, Ph: 03 5434 1224) had made contact with a 25mm consumer mains while digging a new water channel, approx. 60mtrs west of the substation pole. REC isolated at circuit breaker on sub pole. No fire or third party damages. | Services cable | 0 | 0 | 0 |  |  | Excavator contacted private UG mains | No Go Zone (contact) | 42134.5424 |  |  | 70 |  |  | 20151015PWA_1 | Infrastructure (network-based) | -37.1072 | 144.3297 | 1 | Powercor | Report | 97 | 0.021655 | Low voltage AC (<1kV) | Bendigo Airport | 3448 | Elphinstone | Dug up
Crew isolated supply and undertook repairs | 33 THE BROADWAY, ALTONA NORTH VIC 3025 |  | Vehicle | [6 empty] | A nearby customer reported that a high load had pulled down wires at the above location. On arrival the crew found that a LV service cable had been contacted by an unknown vehicle, breaking the cable which fell to the ground. There were no reported injuries or third party property damages. Following repairs the cable was measured at 4.6m at the point of contact over the driveway. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted service cable | No Go Zone (contact);Damage to network assets | 42134.6743 |  |  | 78 |  |  | 20151016PWA_2 | Infrastructure (network-based) | -37.8338 | 144.8612 | 1 | Powercor | Report | 99 | 0.017551 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Vehicle
Crew isolated supply and checked conductors for damage, none found | 1144 PENTAL ISLAND ROAD, PENTAL ISLAND VIC 3586 |  |  | Bird | Unlikely |  |  |  | 1 | A nearby customer reported a fire at the above location. On arrival the crew found that an EDO fuse had operated and that a ground fire (Approx 2500 sqm) had started mid span beneath 22kV conductors. The fire had been extinguished prior to their arrival. There were no reported injuries. The crew suspect that the fire was caused by bird activity. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 15/10/2015 17:08 | 1 | Medium: 1000 sq.m - 10 ha | 86 | Agricultural |  | 20151019PWA_1 | Infrastructure (network-based) | -35.3903 | 143.6771 | 1 | Powercor | Report | 797 | 1.1574e-06 | 22kV AC | Swan Hill Aerodrome | 3586 | Pental Island | Fuse
Crew isolated supply and undertook repairs | 278 WESTERN HIGHWAY, ARARAT VIC 3377 |  |  |  |  | Leakage |  |  |  | CFA reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 66/22kV pole which burnt the middle crossarm only. Protection operated. There was no ground fire. There were no reported injuries or other third party property damage. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42348.0493 |  | Negligible: no ground fire | 87 |  |  | 20151020PWA_1 | Infrastructure (network-based) | -37.2615 | 142.918 | 1 | Powercor | Report | 121 | 0.021399 | 22kV AC;66kV AC | Ballarat Aerodrome | 3377 | Ararat | Crossarm
Crew isolated supply and undertook repairs | 47 MACARTHURS ROAD, BALLIANG VIC 3340 |  |  |  |  | Leakage |  |  | 1 | CFA reported a pole on fire at the above location. On arrival the crew found that a pole fire had occurred on a SWER pole which burnt the pole top and caused hot particles to fall to the ground resulting in a ground fire (Approx 25m x 100m). There were no reported injuries. Protection operated. | Pole top | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 14/10/2015 10:00 |  | Medium: 1000 sq.m - 10 ha | 89 |  |  | 20151020PWA_3 | Infrastructure (network-based) | -37.8311 | 144.33 | 1 | Powercor | Report | 116 | 0.041211 | 12.7kV AC (SWER) | Avalon Airport | 3340 | Balliang | Pole
Crew isolated supply and undertook repairs | 15 MOURELL STREET, SUNSHINE WEST VIC 3020 |  | Vehicle | [6 empty] | A customer reported that the service line to his house was low at the above location. On arrival the crew found that an unknown vehicle had contacted a LV service cable, causing the cable to hang low (but not within reach) and also causing damage to the fascia of the property. There were no reported injuries. The customer stated that he suspects the damage was caused by a rubbish truck during the day. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | Damage to network assets | 13/10/2015 18:14 |  |  | 95 |  |  | 20151021PWA_1 | Infrastructure (network-based) | -37.8018 | 144.8127 | 1 | Powercor | Report | 124 | 0.0051285 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
Crew isolated supply and undertook repairs | 18 LITTLE LA TROBE STREET, MELBOURNE VIC 3000 |  | Suicide (incidental contact with assets) | [6 empty] | A passer-by reported that a street light cable was hanging down in Lt Latrobe St, Melbourne. It was originally reported that the cable had been hit by a vehicle. On arrival, the crew found that a LV street light service cable was hanging at approx. 3.3m and one wire of the 2-wire cable was broken. A neighbour at the location informed the crew that an unknown person had attempted suicide by jumping from a building and had contacted the cable. Upon contact, Police confirmed the incident however no details were given. | Service conductor | 0 | 0 | 0 |  |  | Police confirmed attempted suicide by jumping from bulding | Damage to network assets | 20/10/2015 9:18 |  |  | 101 |  |  | 20151021PWA_3 | Infrastructure (network-based) | -37.8092 | 144.9629 | 1 | CitiPower | Report | 132 | 0.036994 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
Crew secured site and arranged oil clean up | 284 ALBERT STREET, BRUNSWICK VIC 3056 |  | Theft | [5 empty] | 2 | A passer by reported that the transformer had been pushed over at this location. On arrival the crew found that unknown third parties had broken into a disconnected ground type substation and stolen copper conductor. They had also pushed over the transformer and stolen copper from the transformer, and in doing so had released the oil contents of the transformer onto the ground. There were no reported injuries. The disused substation had been disconnected in the past due to a unrelated fire in an adjacent property. | Outdoor | 0 | 1 | 0 |  |  | Copper theft by unknown third parties | More than $50k damage;Damage to network assets | 15/10/2015 0:00 |  |  | 106 |  |  | 20151022PWA_3 | Infrastructure (network-based) | -37.769 | 144.9608 | 1 | CitiPower | Report | 137 | 0.030249 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3056 | Brunswick | Other
Prepared line for EAP and repaired fault. | 61 ROSS STREET, MEENIYAN VIC 3956 | 2010196 |  |  |  | Corrosion |  |  | 2 | IMS 218543. At pole #2010196 conductor on ground due to a loose connection which caused a small bush fire. What caused the conductor to break was the connection that was made between the top circuit to the bottom circuit with a steel ampact, the top circuit was 3/12 alum coated steel and the tee off was 3/12 gal steel. | Conductor (bare) | 0 | 0 | 0 |  | lga14 | What caused the conductor to break was the connection that was made beetween the top circuit to the bottom circuit with a steel ampact, the top circuit was 3/12 aluminimum coated steel and the tee off was 3/12 galvanized steel. | Bushfire | 42226.1917 |  | Small: 10 - 1000 sq.m | 108 | Agricultural |  | 20151022SPN_2 | Infrastructure (network-based) | -38.586 | 146.0139 | 1 | AusNet Services Distribution | Report | 144 | 0.025971 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Meeniyan | Connection
Crew attended and found damage to OH conductors. Supervisor attended and found excavator on site with track mark going under lines. Repairs were carried out and supply restored. | 5 GEORGIAN TERRACE, SOUTH MORANG VIC 3752 |  | Crane, excavator or other construction/farming equipment |  |  | Earth fault |  | Phase to earth | 1 | IMS218670. Received incd for All Supply Failures in Sth Morang. On the date this job occurred, 16/10/2015, a faults crew was sent as it appeared to be a line fuse fault or similar. A crew arrived and discovered that the overhead conductor had been damaged. A construction crew attended and found that an excavator was working in the vicinity and there were excavator marks on the ground below the conductors. When questioned the excavator operator denied all knowledge. The DAO was not advised as it was not decided until the following day that an IMS should be raised and that ESV be advised. Offending party details not provided. | Conductor (bare) | 0 | 0 | 0 |  | smg21 | Crew attended and found damage to OH conductors. Supervisor attended and found excavator on site with track mark going under lines. | No Go Zone (contact) | 16/10/2015 8:25 |  |  | 110 | Residential |  | 20151022SPN_4 | Infrastructure (network-based) | -37.6299 | 145.0862 | 1 | AusNet Services Distribution | Report | 2821 | 0.040227 | 22kV AC | Essendon Airport | 3752 | South Morang | Vehicle
Crew isolated supply and undertook repairs | 6862-7084 HENTY HIGHWAY, BRANXHOLME VIC 3302 |  |  |  | Unlikely | Overheated connection |  |  | 2 | VicFire reported a fire at the above location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (approx. 150 sqm) on the road reserve. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out | Grassfire | 25/10/2015 16:51 | 1 | Small: 10 - 1000 sq.m | 119 | Roadway |  | 20151026PWA_2 | Infrastructure (network-based) | -37.8387 | 141.8428 | 1 | Powercor | Report | 274 | 0.023899 | 22kV AC | Hamilton Airport | 3302 | Branxholme | Fuse
Crew isolated supply for repairs | 207 BURNSIDE ROAD, BANNOCKBURN VIC 3331 |  | Vehicle |  | Unlikely |  |  |  | 2 | A customer reported that a truck had contacted the overhead wire to his property. On arrival the crew found that an unknown vehicle (reported to be a truck however no details were obtained) had contacted a LV service, damaging the service cable and causing the service to hang low (approx. 2m from the ground) and also resulting in damage to the customers POA. Following repairs the cable was measured at 6m at the centre of the road. | Service conductor | 0 | 0 | 0 |  |  | Contact by unknown vehicle | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/10/2015 16:19 |  |  | 127 | Roadway |  | 20151028PWA_3 | Infrastructure (network-based) | -38.06 | 144.1816 | 1 | Powercor | Report | 268 | 0.017057 | Low voltage AC (<1kV) | Avalon Airport | 3331 | Bannockburn | Vehicle
Crew isolated supply and undertook repairs | 3610 GLENELG HIGHWAY, PITTONG VIC 3360 |  |  |  | Unlikely | Leakage |  |  | 1 | Vicfire reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22 KV pole which caused the cross arm to break and fall to the ground resulting in a ground fire (approx. 0.3m x 0.3m) in the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Grassfire | 26/10/2015 23:45 | 1 | Localised: less than 10 sq.m | 128 | Roadway |  | 20151028PWA_4 | Infrastructure (network-based) | -37.6666 | 143.4871 | 1 | Powercor | Report | 273 | 0.017499 | 22kV AC | Ballarat Aerodrome | 3610 | Pittong | Crossarm
An Electrix fault crew attended on site to repair the damaged conductors and substation. LEI's on site - checked for property damage. Damaged and inaccessible properties were taken off supply. Details of properties left off supply were supplied to the Control Room (CEOT). Customer damage claim forms were issued. The fault crew restored supply, replaced blown substation bus fuses. | 10 LAURIE AVENUE, TECOMA VIC 3160 | 1307802 |  | Fallen |  | HV injection |  | Phase to phase | 1 | A tree branch from a tree located on the road reserve out the front of 16 Laurie Avenue, Tecoma, near AusNet Services' pole asset number 1307802, fell across the 22 kV bare conductors causing contact with the Blue Phase of the 400 V bare conductor line. The cause of the branch falling is not known. There were no storms at the time of the incident. Substation fuses operated | Conductor (bare) | 0 | 0 | 0 |  | bge23 | Vegetation: Trees Incident | HV injection | 25/10/2015 16:30 |  |  | 136 | Roadway |  | 20151029SPN_5 | Infrastructure (network-based) | -37.9099 | 145.343 | 1 | AusNet Services Distribution | Report | 194 | 0.029531 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
Crew isolated supply and undertook repairs | 71 BELLARINE HIGHWAY, NEWCOMB VIC 3219 |  |  |  | Unlikely | Leakage |  |  | 2 | VicFire reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole. Crossarm did not break and conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/10/2015 21:10 | 1 | Negligible: no ground fire | 137 | Roadway |  | 20151030PWA_1 | Infrastructure (network-based) | -38.17 | 144.3922 | 1 | Powercor | Report | 259 | 0.024284 | 22kV AC | Avalon Airport | 3219 | Newcomb | Crossarm
Crew Isolated supply and undertook repairs | 1365 HAMILTON HIGHWAY, STONEHAVEN VIC 3221 |  | Vehicle |  | Unlikely |  |  | Phase to earth | 1 | A field crew attending an outage found a black arc mark on the ground and that 22kV conductors had been contacted by a vehicle causing damage to the conductors. Protection operated. The property owner advised the company name (Dirt Shift Excavations PO Box 1025, St Leonards, Vic 3223,, Contact Adam, 0419 323 785 and Brad Harris, Ph: 0407 507 863) and two drivers were contacted however both advised that they had no knowledge of contacting the line. The Business was also contacted but did not admit involvement of this incident or any damage to their vehicles. There was no ground fire. There were no reported injuries or third party property damages. The cable height was measured at 6.6m at the point of contact. | Conductor (bare) | 0 | 0 | 0 |  |  | Contact with HV conductors by high load | Damage to network assets | 28/10/2015 10:14 |  |  | 146 | Agricultural |  | 20151030PWA_10 | Infrastructure (network-based) | -38.122 | 144.2096 | 1 | Powercor | Report | 257 | 0.025728 | 22kV AC | Avalon Airport | 3221 | Stonehaven | Vehicle
Crew inspected assets and arranged repairs | 574 PLUMMER STREET, PORT MELBOURNE VIC 3207 |  |  |  |  | Leakage |  |  |  | VicFire reported a fire on a pole at the above location. On arrival the crew found that a pole fire had occurred on a 66kV pole which burnt the pole and crossarm and the crossarm remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 26/10/2015 22:00 |  | Negligible: no ground fire | 148 | Roadway |  | 20151030PWA_12 | Infrastructure (network-based) | -37.8312 | 144.9344 | 1 | CitiPower | Report | 256 | 0.014565 | 66kV AC | Essendon Airport | 3207 | Port Melbourne | Pole
Crew isolated supply and undertook repairs | 1243 GLENELG HIGHWAY, BOCHARA VIC 3301 |  |  |  | Unlikely | Leakage |  |  | 2 | VicFire reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole. Crossarm did not break and conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/10/2015 0:21 | 1 | Negligible: no ground fire | 138 | Roadway |  | 20151030PWA_2 | Infrastructure (network-based) | -37.6954 | 141.8911 | 1 | Powercor | Report | 267 | 0.026823 | 22kV AC | Hamilton Airport | 3301 | Bochara | Crossarm
Crew secured site and arrange repairs | 1 MUIRFIELD STREET, DEER PARK VIC 3023 |  | Theft |  | Unlikely |  |  |  | 2 | A Powercor employee reported a copper theft at the location. On arrival the crew found that several Kiosk Substations in the area had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 26/10/2015 19:13 |  |  | 142 | Public space |  | 20151030PWA_6 | Infrastructure (network-based) | -37.7787 | 144.7658 | 1 | Powercor | Report | 264 | 0.00084722 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
Crew isolated supply and undertook repairs | GLENELG HIGHWAY, HAMILTON VIC 3300 |  |  |  | Unlikely | Leakage |  |  | 2 | VicFire reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole. Crossarm did not break and conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/10/2015 3:37 | 1 | Negligible: no ground fire | 144 | Roadway |  | 20151030PWA_8 | Infrastructure (network-based) | -37.7423 | 142.0325 | 1 | Powercor | Report | 266 | 0.0062014 | 22kV AC | Hamilton Airport | 3300 | Hamilton | Crossarm
Crew sent to investigate. DOA - Jacqueline Drapos - advised and will attend to do fire report. AusNet Services' fault crews attended and replaced the failed HV ABC. The crew cut away the faulty section of HV ABC and replaced the section with new HVABC. AusNet Services is aware of recent failures of HV ABC and has communicated its strategy to address these incidents to Energy Safe Victoria on 8 November 2013. The strategy is summarized below: â€¢ New cable standard implemented: o Fully screened high voltage ABC introduced to replace previous unscreened cable â€¢ Targeted replacement program developed: o 60km to be replaced over 2014-2016 period. o Cable targeted within Kallista, Mount Dandenong, Lakes Entrance, Monbulk, The Patch, Olinda, Belgrave, Cockatoo, Selby, Mount Evelyn, Kalorama, Arthurs Creek, The Basin and Toolangi. â€¢ Continued monitoring of existing cable condition and performance: o Integration with broader bushfire mitigation programs, including implementation of Victorian Bushfire Royal Commission recommendations. | 7-9 BAYVIEW ROAD, BELGRAVE VIC 3160 | 5746954 |  |  |  | Electrical breakdown |  | Phase to earth | 1 | IMS218819. Customer heard loud bang. Roof caught fire and they have no supply. One phase of a 150 sq, mm HV ABC failed mid-span causing sparks to fall resulting in a small fire in the roof guttering of a commercial property building. Resulting sparks also fell onto the bonnet of a nearby parked, vehicle with registration number TQO98, causing small burn marks. The small fire was extinguished by a local bar owner from Oscar's Ale House. BGE11 feeder CB operated. | Conductor (ABC) | 0 | 0 | 0 |  | bge11 | One phase of HV ABC conductor failure mid-span. Insulation deterioration. | Property | 28/10/2015 17:45 |  | Negligible: no ground fire | 152 | Commercial |  | 20151030SPN_2 | Infrastructure (network-based) | -37.9086 | 145.3566 | 1 | AusNet Services Distribution | Report | 212 | 0.030065 | 22kV AC | Moorabbin Airport | 3160 | Belgrave | OH Cable
Crew isolated supply and undertook repairs | 67 PRINCES HIGHWAY, WERRIBEE VIC 3030 | 956496 | Working too close to underground cables | [6 empty] | A civil contractor reported that they had dug up an underground cable at the incident location. On arrival the fault crew found a contractor (Negri Constructions, 32 Randor St, Campbellfield, Contact; Hashem, Ph: 0458 974 481) were undertaking excavation work and contact a low voltage underground cable causing damage to the cable. The contractor was not on site when the crew arrived and the crew were unable to determine if DYBD plans were obtained by the contractor.. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Contractor contacted KV UG cable | No Go Zone (contact);Damage to network assets | 30/10/2015 13:24 |  |  | 187 | Roadway |  | 20151106PWA_2 | Infrastructure (network-based) | -37.8967 | 144.6733 | 1 | Powercor | Report | 13234 | 0.0045359 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
Crew isolated supply and undertook repairs | 109 WANGANUI ROAD, SHEPPARTON VIC 3630 |  |  | Prone to dust deposition |  | Leakage |  |  | 1 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 66/22kV pole which burnt the crossarm only causing the crossarm to break however the conductor remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 31/10/2015 17:08 |  | Negligible: no ground fire | 193 | Roadway |  | 20151109PWA_1 | Infrastructure (network-based) | -36.3476 | 145.3891 | 1 | Powercor | Report | 295 | 0.037131 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Crossarm
Crew isolated supply and undertook repairs | 744 BOUNDARY ROAD, TRUGANINA VIC 3029 |  | Vandalism | [5 empty] | 2 | Vic Fire reported that a car had hit a pole and started a pole fire at the incident location. On arrival the crew found that an abandoned car which was left next to a Powercor pole had been set alight at some point during the evening resulting in fire damage to the pole, LV underground service cable, earth and cover guards. There were no reported injuries. | Pole (wood);Cable | 0 | 0 | 0 |  |  | Car fire beside pole | Vehicle;Damage to network assets | 42196.9861 |  | Localised: less than 10 sq.m | 221 | Roadway |  | 20151113PWA_15 | Infrastructure (network-based) | -37.806 | 144.7283 | 1 | Powercor | Report | 334 | 0.024029 | Not applicable | Laverton Raaf | 3029 | Truganina | Vehicle
Crew isolated supply and undertook repairs | 480 TURRONG ROAD, COORIEMUNGLE VIC 3268 |  | Working too close to overhead lines | [5 empty] | 2 | A customer reported a wire pulled down by a machine at the incident location. On arrival the crew found that a hay rake being towed by a tractor had contacted an LV overhead service to a dairy, resulting in the service breaking, and damage to the raiser bracket and POA of the dairy. Protection operated. There were no reported injuries, or third party damage. | Service conductor | 0 | 0 | 0 |  |  | Hay rake contacted LV service | No Go Zone (contact);Damage to network assets | 42288.6569 |  |  | 223 | Agricultural |  | 20151113PWA_17 | Infrastructure (network-based) | -38.5742 | 143.1586 | 1 | Powercor | Report | 336 | 0.040464 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Cooriemungle | Vehicle
Crew isolated supply and undertook repairs. Adjacent substations also checked and two additional substations found with stolen earth cables | CANICO DRIVE, CARNGHAM VIC 3352 |  | Theft | [5 empty] | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a pole fire was in progress on a SWER substation wooden pole, with smoke emanating out of cracks in the pole causing the pole to be considered unsafe and requiring replacement. The crew found that the copper earthing cables had been previously cut and stolen off the pole, which eventually resulted in the pole fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Stolen earthing cables on SWER substation pole | Pole-top fire | 42196.4576 |  | Negligible: no ground fire | 208 | Agricultural |  | 20151113PWA_2 | Infrastructure (network-based) | -37.5331 | 143.6415 | 1 | Powercor | Report | 321 | 0.038447 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3352 | Carngham | Other
Crew isolated supply and undertook repairs | 198 CORIO STREET, SHEPPARTON VIC 3630 |  | Vehicle | [5 empty] | 2 | A nearby customer reported that a truck had hiot a overhead wire at the incident location. On arrival the crew found that a high vehicle (Rego: XPX-839, Cahill Automotive Logistics, 88-90 William Angliss Dr, Laverton North, Ph: (03) 9369 9555) had contacted a low voltage service cable causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. No cable or vehicle heights were obtained. | Service conductor | 0 | 0 | 0 |  |  | High load contacted LV service cable | No Go Zone (contact);Damage to network assets | 30/10/2015 10:23 |  |  | 210 | Roadway |  | 20151113PWA_4 | Infrastructure (network-based) | -36.3828 | 145.4028 | 1 | Powercor | Report | 323 | 0.015928 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
The network alterations were arranged to take place on 14/11/2015 and this was questioned by Jarrad Dunstone of Concept 7 that evening. The NGZ supervisor spoke with Jarrad on 15/11/2015 who was questioning if the rectification works had been completed at 1852 Malvern Road, Malvern East. The NGZ supervisor drive past the site on 16/11/2015 to check if the planned work had been completed. The NGZ supervisor arrived onsite at approximately 6:15AM and discovered the works (installation of the HV gas switch and mid span isolators) had been completed. The supervisor investigated further and identified the LV assests were isolated but the HV remained alive with Concept 7 proceeded with their building construction work without a Permit to Work. The Supervisor contacted Jarrad Dunstone of Concept 7 and advised the HV conductors were alive and a Permit to Work had not been issued and therefore a breach of the No Go Zone Framwork had occurred. The supervisor advised Concept 7 that no further work was to be completed at the front of the building and he will be informing Worksafe and ESV. Copies of photos and the inspection report were provided to ESV by the NGZ supervisor. | 1852-1858 MALVERN ROAD, MALVERN EAST VIC 3145 |  | Working too close to overhead lines |  |  |  | Not followed |  | 2 | ZNX No Go Zone (NGZ) supervisor reported a breach of the NGZ Guidelines at 1852 Malvern Road, Malvern East. The ZNX No Go Zone supervisor attended the site at the end of August following a request from a NGZ colleague. Following the site inspection, a quote was provided to the requestor for a HV & LV shutdown or isolation. The Customer informed the coordinator after receiving the quote for an eight hour shutdown, they required the supply to be isolated for at least 3-4 weeks. After discussions with the UE control room, the NGZ coordinator informed the requestor (Concept 7) the two available options to complete the works safely was to: - underground the assets at a huge cost and possible a 6-8 month wait, or - install a HV gas switch and install a set of HV mid span isolators that would allow the network to be operated. The costs for this option was sent to the company on 18/09/2015 but ZNX did not receive conformation that Concept 7 were proceeding until 14/10/2015 that required detailed planning of the rectification work. | Conductor (bare);No failed asset | 0 | 0 | 2 |  |  | No Go Zone clearance breach. | No Go Zone (no contact) | 16/11/2015 0:00 |  |  | 230 | Commercial |  | 20151117UTD_2 | Infrastructure (network-based) | -37.8703 | 145.0612 | 1 | United Energy Distribution | Report | 345 | 0.016375 | 11kV AC | Moorabbin Airport | 3145 | Malvern East | Other
Area isolated to conduct repairs | 32 MCFADZEAN AVENUE, RESERVOIR VIC 3073 |  |  | Fallen |  |  |  |  | 2 | Tree caused conductors to clash bringing down LV conductor | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42165 |  |  | 238 | Residential |  | 20151118JEM_6 | Infrastructure (network-based) | -37.7052 | 144.9981 | 1 | Jemena | Report | 355 | 0.027459 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Trees
Isolated for safety and restrained conductor | 6 LANGTON STREET, GLENROY VIC 3046 |  |  |  |  | Conductor clashing |  |  | 2 | Suspected clashing with blue phase caused red phase LV conductor to fall to ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Conductor clashing due to leaning pole causing the conductors to go slack | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/11/2015 0:00 |  |  | 240 | Residential |  | 20151118JEM_8 | Infrastructure (network-based) | -37.7016 | 144.9141 | 1 | Jemena | Report | 684 | 0.013444 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Conductor
Crew isolated supply for fire fighters to fight fire. Damaged assets isolated after fire out. Supply restored. | 7 HAMILTON ROAD, HORSHAM VIC 3400 | [7 empty] | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found the No1 66/22kv transformer at Horsham zone sub-station on fire, resulting in Loss of supply to the Horsham area and the No1 transformer damaged. Protection operated. Two fire fighters were taken to hospital by ambulance suffering the effects of heat stress. There were no third party damages. | Zone substation;Transformer | 0 | 1 | 0 |  |  | Unknown, investigation into cause is ongoing | Loss of supply;Plant/equipment | 18/11/2015 17:40 | 1 | Negligible: no ground fire | 248 | Commercial |  | 20151119PWA_2 | Infrastructure (network-based) | -36.7348 | 142.2058 | 1 | Powercor | Report | 372 | 0.0017002 | 22kV AC;66kV AC | Horsham Aerodrome | 3400 | Horsham | AF Other
Crew isolated supply and checked line for damages - none found | 2599 MURRAY VALLEY HIGHWAY, COBRAM EAST VIC 3644 |  |  | Fallen;Property owner/customer |  |  |  |  | 1 | Vic Fire reported fire at the above location. On arrival the crew found that a tree from outaside the clearance space had broken and fallen across an adjacent 22kV line, resulting in a ground fire (Approx. 400 sqm) on the road reserve and a small area on private property. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 19/11/2015 19:20 |  | Small: 10 - 1000 sq.m | 257 | Roadway |  | 20151123PWA_1 | Infrastructure (network-based) | -35.9772 | 145.7364 | 1 | Powercor | Report | 382 | 0.03252 | 22kV AC | Shepparton Airport | 3644 | Cobram East | Trees
ACE attended and replaced the defective 250w HPS lantern. A NST was completed that passed and supply was left on. | 75 SOUTH GIPPSLAND HIGHWAY, DANDENONG SOUTH VIC 3175 | 8813235 |  | Unknown environment factor |  | Electrical breakdown |  |  | 2 | Caller reports the pole is on fire in the South Gippsland Highway between the Princes Highway and the Dandenong bypass about 200m south of the railway crossing. A 250w HPS lantern on pole No. 8813235 located at the South Gippsland Highway 1 pole north of Fowler Road caught fire that self extinguished. A faults crew attended and isolated the supply and a further trouble order was created for ACE to attend and replace the defective 250w HPS lantern. | Public lighting | 0 | 0 | 0 |  |  | A 250w HPS lantern on pole No. 8813235 located at the South Gippsland Highway 1 pole north of Fowler Road caught fire that self extinguished. The cause was unknown. | Other electricity related | 42015.7917 |  | Negligible: no ground fire | 263 | Public space |  | 20151124UTD_3 | Infrastructure (network-based) | -38.0043 | 145.2273 | 1 | United Energy Distribution | Report | 391 | 0.015186 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | AF Other
Crew isolated supply and undertook repairs | PRINCES HIGHWAY, YAMBUK VIC 3285 |  |  |  |  | Leakage |  |  | 2 | Vic Fire reported a fire at the incident location. On arrival the crew found that the insulation on an insulated HV lead had broken down causing hot embers to fall to the ground resulting in a ground fire (Approx. 800sqm) on the road reserve. The fire also cause damage to farm fencing. There were no reported injuries. | Cable sealing end | 0 | 0 | 0 |  |  | Insulation on HV leads broke down | Grassfire | 25/11/2015 12:06 |  | Small: 10 - 1000 sq.m | 270 | Roadway |  | 20151126PWA_3 | Infrastructure (network-based) | -38.3133 | 142.0624 | 1 | Powercor | Report | 401 | 0.01215 | 22kV AC | Warrnambool Airport Ndb | 3285 | Yambuk | OH Cable
Crew arranged repairs | 85-95 CREAMERY ROAD, BELL POST HILL VIC 3215 |  | Vandalism | [5 empty] | 2 | CFA reported rubbish set on fire at the base of at the incident location. On arrival the crew found that a fire had been lit at the base of a pole burning the pole, which remained intact, as well as burning an area of ground surrounding the pole. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Vandalism | Grassfire | 14/11/2015 10:54 |  | Localised: less than 10 sq.m | 275 | Roadway |  | 20151127PWA_4 | Infrastructure (network-based) | -38.0988 | 144.3199 | 1 | Powercor | Report | 3702 | 0.031174 | Not applicable | Avalon Airport | 3215 | Bell Post Hill | Other
Crew isolated supply and undertook repairs | 19 FAIRWAY CRESCENT, TEESDALE VIC 3328 |  |  | Fallen |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival, the crew found that a tree branch (from outside the clearance space) had fallen across an adjacent 22kV line causing the line to break and fall to the ground resulting in a ground fire (Approx. 400 sqm) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 26/11/2015 13:26 |  | Small: 10 - 1000 sq.m | 283 | Roadway |  | 20151127PWA_9 | Infrastructure (network-based) | -38.0198 | 144.0376 | 1 | Powercor | Report | 577 | 0.010499 | 22kV AC | Avalon Airport | 3328 | Teesdale | Trees
Fault truck dispatched to investigate and isolate - ESV and claims contacted. Fault crew made necessary repairs to the HV conductor, replaced BA fuse and restored supply. A request has been made for assessment for re-conductoring. | 75 BINGINWARRI SOUTH ROAD, WOORARRA EAST VIC 3962 | 2012673 |  |  | Likely | Corrosion |  | Phase to earth | 1 | IMS 219205. A HV conductor of a single phase 22kV line came down onto a paddock electric fence and a calf got too close to the fence and was electrocuted and died. The load side HV conductor was live on the fence due to back feed from a downstream distribution transformer windings. The line side Boric Acid fuse operated. The conductor was very rusty and it broke about 50 mm into the sleeve which caused it to fall down. | Conductor (bare) | 0 | 0 | 0 |  | FTR12 | Rusty HV conductor. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2015 8:00 |  |  | 286 |  |  | 20151130SPN_2 | Infrastructure (network-based) | -38.5931 | 146.386 | 1 | AusNet Services Distribution | Report | 5302 | 0.0090104 | 22kV AC | Morwell (Latrobe Valley Airport) | 3962 | Woorarra East | Conductor
CEOT dispatched a fault crew to make safe and investigate. The crew repaired the damaged HV conductors. | 1-3 ST HUBERTS ROAD, COLDSTREAM VIC 3770 | 1008350 |  | Wind | Likely | Conductor clashing |  | Phase to phase |  | IMS 219320. CEOT received a call from the Fire Brigade notifying that there was a fire as a result from a tree bringing the overhead HV down to the ground between poles 10-8350 to 10-8349 (1 bay of copper conductor). Strong wind caused the upper branches on a gum tree to fail and fall across the HV conductors, clashing the HV conductors together causing a ground fire of 1200 sq. metres in size. | Conductor (bare) | 0 | 0 | 0 |  | LDL14 | Vegetation: Trees Incident | Grassfire | 25/11/2015 23:55 |  | Medium: 1000 sq.m - 10 ha | 288 | Roadway |  | 20151130SPN_4 | Infrastructure (network-based) | -37.697 | 145.4203 | 1 | AusNet Services Distribution | Report | 430 | 0.026627 | 22kV AC | Moorabbin Airport | 3770 | Coldstream | Conductor
Area isolated and repaired. | 4 HARRISON STREET, BELLFIELD VIC 3081 |  |  |  |  | Mechanical breakdown |  |  | 1 | High voltage isolator contacted concrete pole | Disconnector/isolator;Pole (concrete) | 0 | 0 | 0 |  |  | Crossarm brace failed. | HV injection | 30/11/2015 19:43 |  |  | 295 | Residential |  | 20151201JEM_1 | Infrastructure (network-based) | -37.7528 | 145.039 | 1 | Jemena | Report | 683 | 0.003912 | 6.6kV AC | Essendon Airport | 3081 | Bellfield | Crossarm
Crew isolated supply and undertook repairs | 250 GHERANG ROAD, GHERANG VIC 3240 |  |  |  |  | Fuse failed to eject |  |  | 2 | A field crew undertaking work adjacent to the incident site noticed that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a crossarm fire. The field crew isolated supply extinguishing the fire. There was no ground fire. There were no reported injuries or third party damages. | Crossarm (wood);EDO fuse | 0 | 0 | 0 |  |  | EDO fuse did not drop out | Pole-top fire | 18/11/2015 7:35 |  | Negligible: no ground fire | 301 | Roadway |  | 20151201PWA_5 | Infrastructure (network-based) | -38.2991 | 144.0868 | 1 | Powercor | Report | 453 | 0.025132 | 22kV AC | Avalon Airport | 3240 | Gherang | Fuse
MFB put out small fire. Jemena isolated and made safe | 2 OPHIR STREET, BROADMEADOWS VIC 3047 |  | Vehicle | [5 empty] | 1 | Vehicle impact into pole causing high voltage conductor to fall off the insulator. The conductor was resting against the wooden pole. Resulting in pole fire and small grass fire at the base of the pole. #A015933, in easement at north of the Ring Rd and 1st pole east of Ophir St. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Vehicle impact | Pole-top fire;Grassfire | 42016.7847 | 1 | Localised: less than 10 sq.m | 302 | Roadway |  | 20151202JEM_1 | Infrastructure (network-based) | -37.6934 | 144.9334 | 1 | Jemena | Report | 791 | 0.0066539 | 22kV AC | Essendon Airport | 3047 | Broadmeadows | Vehicle
A LEI and faults truck attended and completed installation tests to determine the cause. Voltage tests between an independent earth and various points of the electrical installation, including the Distributors assets, identified a defective neutral connection at the service pole after 195v was measured on the water piping system. The faults crew proceeded to clean, grease and reconnect the neutral connection after the corroded aluminium line tap was identified as the cause. The LEI tested the installation and measured zero volts on the water piping system after the completion of the repairs. | 7 BONA VISTA AVENUE, ASPENDALE VIC 3195 |  |  |  |  | Corrosion |  | Phase to earth | 2 | REC advised there is a broken neutral to the property and the customer had received shocks from the taps. Access is via Sofia Avenue. A REC contacted the United Energy faults and emergencies number after being contacted by the resident who received electric shocks from the shower taps when standing on the wet shower base. | Aluminium twisted (grey) | 0 | 0 | 0 |  |  | A defective neutral connection at the service pole | Minor shock | 24/11/2015 14:00 |  |  | 306 | Residential |  | 20151202UTD_3 | Infrastructure (network-based) | -38.0244 | 145.0991 | 1 | United Energy Distribution | Report | 459 | 0.01319 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Investigation on the north circuit found no signs of damage. A total of 59 customers were isolated on the south circuit and the fault crews closed the north and south circuit substation fuses. Energisation and inspection of customer appliances then commenced with defect notices issued to 87, 89 Atkinson Street and units 1 & 2 80 Wood Street. The defects at 87 and 89 were rectified and supply was restored. Units 1 & 2 80 Wood Street remained off supply and a REC will be in attendance on 27/11/2015. Inspection and testing of customer installations found significant damage to electrical equipment, wiring and metering equipment. 6 premises were left off supply as there was no access. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 54 MCLACHLAN STREET, TEMPLESTOWE VIC 3106 |  |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | At 2211hrs on 25/11/2015, 11kV feeder BU 14 circuit breaker reclosed to lockout affecting 1659 customers. During strong windy conditions, a large tree branch contacted the HV conductors in McLachlan Street, Templestowe that resulted in a HV conductor contacting the LV conductors below. Molten metal from the suspected conductor clash caused a small grass fire outside 54 McLachlan Street that was quickly extinguished. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from the south circuit of "McLachlan-Atkinson" substation as there was signs of visible damage. The LEI confirmed a high voltage injection occurred (BWD 1520) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | BU14 | Vegetation: Trees Incident | HV injection;Loss of supply;Grassfire | 25/11/2015 22:11 |  | Localised: less than 10 sq.m | 312 | Residential |  | 20151203UTD_1 | Infrastructure (network-based) | -37.7549 | 145.1257 | 1 | United Energy Distribution | Report | 467 | 0.037024 | 11kV AC | Essendon Airport | 3106 | Templestowe | Trees
Crew isolated supply and undertook repairs | 21 SHEPHERDSON AVENUE, CORIO VIC 3214 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | Vicfire reported a burnt crossarm has fallen on the LV at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV crossarm causing the arm to break and fall onto the LV below. There was no HV injection. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/11/2015 4:41 |  | Negligible: no ground fire | 323 | Roadway |  | 20151204PWA_10 | Infrastructure (network-based) | -38.0728 | 144.3418 | 1 | Powercor | Report | 479 | 0.028609 | 22kV AC | Avalon Airport | 3214 | Corio | Crossarm
Crew isolated supply and undertook repairs | QUEENS COLLEGE, 1-17 COLLEGE CRESCENT, PARKVILLE VIC 3052 |  | Working too close to underground cables | [5 empty] | 1 | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location. On arrival the crew found that a contractor (Pearce Brothers Pty Ltd, Contact: Ph: 9357 8766, working for Melbourne University at Queens College, Contact Ivan Tudor: 9349 0521) was operating an excavator and contacted a LV underground mains cable causing damage to the cable. Protection operated. While the cable was on Queens College property, it was found to be a CitiPower cable which feeds a street circuit from the indoor substation on the property. Powercor have no record of a DBYD enquiry for this contractor at this location. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Excavator contacted LV cable | Loss of supply | 20/11/2015 11:58 |  |  | 318 | Commercial |  | 20151204PWA_5 | Infrastructure (network-based) | -37.7932 | 144.9642 | 1 | CitiPower | Report | 474 | 0.0053194 | Low voltage AC (<1kV) | Essendon Airport | 3052 | Parkville | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. The white and blue 200amp LV Din fuses had operated and were replaced by the faults crew after the tree was cleared. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 43 DEEP CREEK ROAD, MITCHAM VIC 3132 | LIS 7031215 |  | Blown branch/vegetation |  | HV injection |  |  | 1 | At 2344hrs on 25/11/2015, 22kV feeder RWT 23 circuit breaker reclosed to lockout affecting 1423 customers. During strong winds, a large council tree branch located opposite 43 Deep Creek Road, Mitcham contacted the HV conductors that resulted in a HV conductor to contact the LV blue phase conductor below. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from the south circuit of "Deep Creek-Edgerton" substation. The LEI confirmed a high voltage injection occurred (BWD 1521) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | RWT 23 | Vegetation: Trees Incident | HV injection;Loss of supply | 25/11/2015 0:36 |  |  | 329 | Roadway |  | 20151204UTD_2 | Infrastructure (network-based) | -37.815 | 145.2093 | 1 | United Energy Distribution | Report | 874 | 0.031058 | 22kV AC | Moorabbin Airport | 3132 | Mitcham | Trees
Crew isolated supply and undertook repairs | 8 NOLAN STREET, NARRAWONG VIC 3285 |  |  |  |  | Fuse failed to eject |  |  | 2 | A Fault crew attending following an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. There was no ground fire. There were no reported injuries or third party property damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out | Plant/equipment | 42197.5243 |  | Negligible: no ground fire | 337 |  |  | 20151207PWA_3 | Infrastructure (network-based) | -38.2533 | 141.7143 | 1 | Powercor | Report | 497 | 0.026172 | 22kV AC | Portland (Cashmore Airport) | 3285 | Narrawong | Fuse
Contractor advised to cease work. Incident reported for followup. | 62 ERIN STREET, RICHMOND VIC 3121 |  | Working too close to underground cables | [5 empty] | 2 | A field officer attending to review a Permit to Work application found that a contractor (Civiworks, 4/34 Plateau Road, Reservoir, 3073, Contact: Jay Wilkes, Ph: 0449 968 586) had undertaken excavation works within the no go zone for underground cables, reducing the cover height of 11kV and LV underground cables immediately adjacent a substation. The works also left an underground pit level above the finished road surface height approx. 80-100mm. Work was undertaken without reference to CitiPower in breach of VESI guidelines. There were no reported injuries. Corner of Erin St and Leigh Place. Site visit Notes: CitiPower visited site 3/12/15 and met Jay Wilkes-0449968586 (Civiworks) and Hugh Lockie (0417348601 Kane Construction). The following observations and discussions were made during the inspection The road reconstruction, Kerb works are almost complete between Erin St and Leigh-Erin Substation The footpath in front of substation needs to be lowered thus reducing cover on assets entering/exiting Substation. This is why the customer applied for a Permit to Work site visit. An existing service pit is now protruding ground level by approx. 80-100mm of the new road (was in footpath previously) at the corner of Leigh Place and Erin St which contractor thinks is abandoned but is not sure. CitiPower GIS states the pit is still in service. Contactor is going on advice given by Kane construction that the pit is abandoned. This means cover on the LV cable is reduced. Southern footpath of Erin St west of Leigh Place all excavated (asphalt) and cover on the assets in the footpath will be significantly reduced as per advice by the contractor (about 250-350mm for a significant distance) Road reconstruction, Kerb works in Erin St west of Leigh Place started but was clear of assets. Note: All these works which have been completed and were carried out without an inspection or permit from Citipower. Jay Wilkes advised that works commenced on the instructions of Kane Constructions and also they said based on the asset location, they were minimum 500mm clear from assets all the time as they only went down 300mm however the plans dispute this. All depths of assets were based on private asset locators depths marked on ground and in report as per customer and no consultation with CitiPower Permit to Work team. | Cable;Services pit | 0 | 0 | 0 |  |  | Contractor breached VESI/NGZ guidelines | No Go Zone (no contact) | 42075 |  |  | 344 | Roadway |  | 20151207PWA_5 | Infrastructure (network-based) | -37.8168 | 144.9942 | 1 | CitiPower | Report | 506 | 0.041132 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3121 | Richmond | Dug up
A LEI and faults truck attended and completed a NST that passed. The LEI measured between an independent earth and the bathroom taps and recorded 1.3 volts. Volts on the earthing and the neutral bar loaded with the oven and the air-conditioning running identified 3 volts. The fault crew proceeded to check all terminations on the service pole and FOLCB for the pole to pit and found the screws on the neutral terminal very loose. The connections were cleaned, greased and tightened. The neutral connection to the overhead reticulation was also replaced. The LEI re-tested the installation following the rectification work and measured 0.8 volts. A NST was completed that passed. | UNIT 4 34 PANORAMA STREET, CLAYTON VIC 3168 |  |  |  |  | Neutral fault | Poor workmanship | Phase to earth | 2 | The owner called for the tenant who received a strong electric shock when touching the tap in the bathroom. Itâ€™s the first time this has happened. The occupier received a strong electric shock to his hand from the bathroom tap and contacted the owner who contacted the United Energy faults and emergencies number. | Services cable;Connector/termination | 0 | 0 | 0 |  |  | The fault crew proceeded to check all terminations on the service pole and FOLCB for the pole to pit and found the screws on the neutral terminal very loose. | Minor shock | 30/11/2015 17:00 |  |  | 339 | Residential |  | 20151207UTD_1 | Infrastructure (network-based) | -37.9201 | 145.1301 | 1 | United Energy Distribution | Report | 499 | 0.023047 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Connection
Dispatched fault crew to make safe and investigate. Crew attended the substation and replaced EDO fuse tube and fuse link. A work order is being raised to replace the EDO fuse unit with a Boric Acid fuse unit. | 25 MCINTOSHS ROAD N, STRZELECKI VIC 3950 | 2004969 |  | Lightning | Unlikely |  |  |  | 2 | IMS 219478. EDO fuse had candled right out. May have possibly been due to a lightning strike as other strikes had recently occured in the area, but no real known cause. No pole fire or ground fire occurred. | EDO fuse | 0 | 0 | 0 |  | LGA24 | Lightning / thunderstorm. | Plant/equipment | 42136.5312 | 1 | Negligible: no ground fire | 351 |  |  | 20151208SPN_1 | Infrastructure (network-based) | -38.3447 | 145.9183 | 1 | AusNet Services Distribution | Report | 520 | 0.034564 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3950 | Strzelecki | Fuse
CEOT dispatched a fault crew to investigate and make safe. Crew replaced the broken fuse tube and the fuse link and restored supply. | 390 KORRINE ROAD, GLEN ALVIE VIC 3979 | 2804070 | [7 empty] | IMS 219479. LIS#2804070 - EDO fuse tube was hung-up and had broken. It had not burnt. No pole fire or ground fire occurred. As a result this incident has been reclassified as an electrical near-miss incident and will be included in the Quarterly Report to ESV. No Schedule 2 report is required for this incident. | EDO fuse | 0 | 0 | 0 |  | WGI22 | Possibly a lightning strike. | Hung-up fuse only | 42167.8403 |  |  | 352 |  |  | 20151208SPN_2 | Infrastructure (network-based) | -38.5034 | 145.6418 | 1 | AusNet Services Distribution | Report | 522 | 0.041065 | 22kV AC | Moorabbin Airport | 3979 | Glen Alvie | Lightning
Wayne Kelly (United Energy) contacted Michael from Ausgrid (9482 5424) who was involved for the meter changeover and stated the work was completed on Monday night with CESâ€™s lodged through the ESV electronic system. United Energy discussed the possibility of isolating supply to the shopping centres due to the irregularities around the process that have been followed and concerns about compliance with multiple metrology procedures arising from the metering alterations. Phil Walters (UE) discussed this matter with Neil Fraser (ESV) who requested that United Energy provide a schedule 2 report and he will assign an investigator to follow up. Wayne Kelly also spoke with REC Filip who understood that after the current transformers and the gate meter are installed, the truck appointment would not be required. Filip will ensure to arrange truck appointments are organised for future embedded network installations. Filip also sent through copies of the prescribed certificate of electrical safety for the Nilsen work (attached). Filip was going to contact the ENO David Regenspurger to ensure his paperwork has been completed and forwarded to United Energy. | 230 CRANBOURNE-FRANKSTON ROAD, LANGWARRIN VIC 3910 |  | Unauthorised work | [5 empty] | 2 | United Energy was advised that an embedded network has been established at the Gateway Langwarrin Shopping Centre and Mornington Shopping Centre without a truck appointment as a failure of following industry policies. 19/11/2015 - Existing two shopping centres (Gateway Langwarrin Shopping Centre and Mornington Shopping Centre) converting to embedded networks. REC will require truck appointments to isolate the main switch board, re-supply new main switchboard via new CT meters in accordance with United Energy procedure/checklist. ERM Business Energy raised a service order to accompany an EWR with Retailer Service Order Number: 201511013116. They requested a NMI to be created to enable a metering installation request to be established for an embedded network. The contact is Electrical Engineer Filip Suleski from Nilsen on 0409 164 169 or filipsuleski@nilsen.com.au. ERM advised further that a truck appointment is required in order for United Energy to proceed with the connection requests for both Mornington and Gateway Langwarrin Shopping Centres. United Energy approved the connection with NMI 6408201543 0 and 2001 Change Request ID: 836692107 created with EN code UGTLANSC1. United Energy left a voicemail for the REC Fillip regarding the go live date for the embedded network as a truck appointment is required after CTâ€™s and metering are installed. 01/12/2015 - ERM and United Energy were informed that Langwarrin went live on 25/11/2015 and a truck appointment is not required. The REC was contacted who advised that he energised the site on 23/11/2015 and 78 Barkly St, Mornington (6408201539) on the 30/11/2015. The REC was under the impression there would be no issues and turned the unmetered isolator on. Therefore, the embedded networks at Langwarrin and Mornington Shopping Centres have gone live without a service order / truck appointment being issued from the United Energy connections team. United Energy have not been paid for the back office work and these embedded networks are not set up in the systems and are not being billed. The back office fees are for the administration and truck appointment fees for updating systems and MSATS. A truck appointment is always required for energisation of the parent NMI. This has always been the process as per the metrology procedures with the Distributors representative energising the site. Ausgrid (Michael 9482 5424) were the meter providers and the embedded network operator is Energy Intel - David Regenspurger 0418 993 150 or david@energyintel.com.au. David was instructed by United Energy of the responsibilities of the ENO to ensure coordination of all processes for the connection of an embedded network. It is believed the existing meters were removed and returned to Formway Metering Services (United Energy Specialist Meter Provider) apparently as part of the AEMO Service Level Procedures ensuring the Meter Provider is accredited by AEMO within the National Electricity Market (NEM). | Other meter | 0 | 0 | 0 |  |  | The REC was under the impression there would be no issues and turned the un-metered isolator on. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/11/2015 21:00 |  |  | 356 | Commercial |  | 20151209UTD_3 | Infrastructure (network-based) | -38.1506 | 145.1957 | 2 | United Energy Distribution | Report | 533 | 0.033203 | Low voltage AC (<1kV) | Moorabbin Airport | 3910 | Langwarrin | Other
Crew isolated supply and undertook repairs | 35 COPPARDS ROAD, MOOLAP VIC 3224 |  | Vehicle | [5 empty] | 1 | A passer-by reported that a wire down at the incident location. On arrival the crew found that an unknown vehicle had driven across the nature strip and struck a guy wire causing a shock load on the pole leading to conductor clashing and a switch wire to break and fall to the ground. No details were obtained of the vehicle or driver. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Unknown vehicle contacted guy wire | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42075.5181 |  |  | 364 | Roadway |  | 20151210PWA_5 | Infrastructure (network-based) | -38.1679 | 144.4038 | 1 | Powercor | Report | 548 | 0.025693 | Low voltage AC (<1kV) | Avalon Airport | 3224 | Moolap | Vehicle
CEOT sent an Electrical Inspector (LEI) and a fault crew to investigate. The fault crew carried out repairs to the line on 8/12/15 and re-instated power to top of meter panel fuses after carrying out all tests. Customer ran installation on generator and due to time of night and the LEI attending other faults the LEI was not able to attend till am on 9/12/15. After carrying out tests at the switchboard, installation and disconnecting affected appliances, the inspector re-instated supply to normal. | 31 KORUMBURRA-WARRAGUL ROAD, WARRAGUL VIC 3820 | 2794754 |  | Lightning |  |  |  |  | 2 | IMS 219520. The suspected lightning strike caused damage to white phase LV isolator on the pole causing the fuse to blow causing sparks which caused a minor grass fire at the base of the pole and some equipment at the Southern Cross Austereo Radio Station showed signs of minor voltage injection damage. There was evidence of a small fire at the bottom of the pole and the CFA apparently attended. The fault crew carried out repairs to the LV isolator and after carrying out tests re-instated supply to the meter board. The customer chose to run limited equipment on generator supply until the AusNet Services' LEI could attend. CEOT advised that the LEI would be better attending site in morning as the site would be vacant. | Disconnector/isolator;Outdoor;Transformer | 0 | 0 | 0 |  | WGL13 | Lightning strike on line. | HV injection;Grassfire | 42228.8507 | 1 | Localised: less than 10 sq.m | 359 | Commercial |  | 20151210SPN_1 | Infrastructure (network-based) | -38.1759 | 145.9298 | 1 | AusNet Services Distribution | Report | 544 | 0.030284 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3820 | Warragul | Lightning
Fault crew attended and found 200 Volts from meter box to an independent earth. Supply was isolated at fused mains box on pole 2510807. IR on consumer's mains was measured at 0.0 Ohms and continuity test on mains to number 14 failed. Underground crew was called in to locate the service pit and upon opening the pit it smelt of burning conductor and 2 out of the 3 consumer's mains cables to number 14 came loose out of conduit. The cables were damaged 3.5m away from pit where they had previously been redirected from pole to pit on front boundary of number 12. IPCs were replaced in the pit and a pit to pit installed to number 14. Customer was issued with a Customer Installation Defect Notice (NCID) and supply was left off. | 14 ALMEDA DRIVE, COONGULLA VIC 3860 | 2510807 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 219211. Amy Rundle and partner were staying at the family holiday home when they noticed the lights were dimming and part of the house wasn't working. A local friend, Trevor Frost, attended site to check the problem when he received a tingle off the meter box. Rob Heckman's company Electricians, (tel. 0427489479) attended the site and called AusNet Services when he measured 140-200 Volts on the meter box. The cause was found to be 2 of the 3 underground consumer's mains (an active and neutral 35 sq.mm building wire previously routed directly from the pole) were completely broken and melted and were smouldering 3.5 m all the way to the service pit located on the front boundary of number 12. | No failed asset | 0 | 0 | 0 |  | MFA22 | Damaged insulation on 2 phase underground consumer's mains approximately 15 m outside property boundary and 3.5 m from pit it was redirected to. | Minor shock | 21/11/2015 12:30 |  |  | 400 | Residential |  | 20151218SPN_3 | Infrastructure (network-based) | -37.8877 | 146.779 | 1 | AusNet Services Distribution | Report | 604 | 0.024557 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3860 | Coongulla | UG Cable
Site was safe on arrival | YARRA BEND ROAD, FAIRFIELD VIC 3078 | A012204 |  | Blown branch/vegetation |  |  |  |  | 1 | Tree branch from a tree in Yarrabend park fell (due to high winds) on pole A012204 causing the centre phase HV disc to break. As a result started a small fire which was self extinguished. fiCs #2053 | Pole (wood);Pole top | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 19/12/2015 14:24 | 1 | Localised: less than 10 sq.m | 405 | Public space |  | 20151221JEM_1 | Infrastructure (network-based) | -37.7863 | 145.0091 | 1 | Jemena | Report | 611 | 0.00070602 | 6.6kV AC | Essendon Airport | 3078 | Fairfield | Trees
Crew on site raised cable with assistance of bucket crew. | 78 CLIFTON STREET, ABERFELDIE VIC 3040 |  |  |  |  | Mechanical breakdown |  |  | 2 | LV conductor on ground. Corner of Clifton and Jean Streets. | Conductor (bare) | 0 | 0 | 0 |  |  | Clamp failure | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/12/2015 11:37 |  |  | 406 | Residential |  | 20151221JEM_2 | Infrastructure (network-based) | -37.7621 | 144.8919 | 1 | Jemena | Report | 612 | 0.0082789 | 11kV AC | Essendon Airport | 3040 | Aberfeldie | Conductor
Fault crew attended, isolated supply and made safe. Passed onto underground construction crew for repairs. LV UG cable replaced under EAP on the 19/12. | 37 TOSCANA WAY, WALLAN VIC 3756 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 219745. Fault crew attended, isolated supply and made safe, passed onto underground construction crew. Construction crew unavailable to attend on 18/12 due to attending HV faults and crew hours too high. Construction crew attended 06:30 on 19/12/2015 - damaged LV UG service cable replaced under EAP. ASR 14:18. LV UG cable damaged due to a member of the public striking the LV cable with an auger. Person unknown. | Cable | 0 | 0 | 0 |  | klo14 | Unknown 3rd party using a auger/boring machine damaged underground LV service cable. | No Go Zone (contact) | 18/12/2015 13:00 |  |  | 409 | Residential |  | 20151221SPN_1 | Infrastructure (network-based) | -37.3946 | 145.009 | 1 | AusNet Services Distribution | Report | 616 | 0.034447 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3756 | Wallan | Dug up
CEOT sent crew to make safe and repair x-arm. Isolated HV and made safe to replace LV sub bus fuse. Downer on site to repair damaged conductors and cross arm. LEI's on site - checked for property damage. Damaged & inaccessible properties taken off supply. Customer Advice forms were issued where required. The x-arm on this pole was last inspected on the 8/2/2011 and is planned to be done in this yearâ€™s inspections. Termites have eaten the x-arm out and the pole may also be in poor condition. In Q4 or SAP there is no history of termite active and the HV x-arm was serviceable at the time of inspection. | 57 EDWARD ROAD, CHIRNSIDE PARK VIC 3116 | 13629 |  | Animal |  | HV injection |  | Phase to phase | 1 | IMS 219751. Broken HV cross arm at AusNet Services' pole no.1013629 caused the HV lines to come into contact with the white phase of the LV lines below. Incident caused Feeder CPK 22 to trip. Broken HV termination x-arm due to termites. HVI damaged occurred to customers' properties. | Crossarm (wood) | 0 | 0 | 0 |  | cpk12 | Animal Incident | HV injection | 19/12/2015 21:55 |  |  | 410 | Residential |  | 20151221SPN_2 | Infrastructure (network-based) | -37.7511 | 145.317 | 1 | AusNet Services Distribution | Report | 618 | 0.040938 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3116 | Chirnside Park | Crossarm
Crew isolated supply and undertook repairs | 14 SHARP STREET, NORTHCOTE VIC 3070 |  |  |  |  | Overheated connection |  |  | 2 | Vic Fire reported a fire on a pole at the incident location. On arrival, the crew found that a connection in a LV fuse box on the substation pole had overheated causing debris to fall to the ground resulting in a ground fire (Approx. 1sqm) at the pole base. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Medical attention (first aid/doctor/hospital);Grassfire | 17/12/2015 18:07 | 1 | Localised: less than 10 sq.m | 422 | Roadway |  | 20151222PWA_1 | Infrastructure (network-based) | -37.7739 | 145.0063 | 1 | CitiPower | Report | 637 | 0.021741 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Fuse
Crew isolated supply and undertook repairs | 638 BACCHUS MARSH ROAD, BACCHUS MARSH VIC 3340 |  |  |  |  | Overheated connection |  |  | 1 | MFB reported a fire on a pole at the incident location. On arrival, the crew found that a connection in a pole mounted LV fuse box had overheated causing the box to melt and catch fire. The heating also caused the insulation to deteriorate on the connected underground cable resulting in the base of the customers pillar becoming alive and shorting out to nearby fencing wire. This resulted in a ground fire (Approx. 1 sqm) at the base of a fence post. Protection operated. There were no reported injuries | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 18/12/2015 10:56 | 1 | Localised: less than 10 sq.m | 424 | Roadway |  | 20151222PWA_2 | Infrastructure (network-based) | -37.6878 | 144.4774 | 1 | Powercor | Report | 642 | 0.022934 | Low voltage AC (<1kV) | Laverton Raaf | 3340 | Bacchus Marsh | Connection
Crew isolated supply and undertook repairs | 3 ROBIN STREET, MELTON VIC 3337 |  |  |  |  | Overheated connection |  |  | 2 | A nearby customer reported a fire at the incident location. On arrival the crew found that a connection on a LV D-Loop bridge overheated causing hot debris to fall to the ground resulting in a ground fire (Approx. 20 sqm) on the road reserve. There were no reported injuries. The fire self extinguished. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 20/12/2015 13:34 | 1 | Small: 10 - 1000 sq.m | 428 | Roadway |  | 20151222PWA_6 | Infrastructure (network-based) | -37.6769 | 144.5764 | 1 | Powercor | Report | 648 | 0.0094896 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
The auto reclose was suppressed on 11kV feeder MR 13 and the red phase HV insulator was replaced at pole No. 1808380 using glove and barrier techniques. | 170 SOUTH ROAD, BRIGHTON EAST VIC 3187 | LIS No. 1808380 | Vehicle |  |  | Insulator;Mechanical breakdown |  |  | 2 | The customer from 168 South Road called to advise that a small grass fire has started under the pole outside 170 South Road, Brighton East. 15/11/2015 - A vehicle struck a HV/LV timber pole (LIS No. 1808382) located outside 156 South Road, Brighton East. The pole was severely damaged and was replaced. 16/11/2015 - A HV tie was suspected to have broke following the vehicle hitting the HV/LV pole at the above location the previous day. This caused the red phase 11kV conductor to fall from the HV insulator at pole No. LIS 18008380 and make contact with the red phase LV conductor below. Splash marks were evident on the conductors and a small grass fire occurred at the base of the pole that was quickly extinguished. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "South-Imbros" substation. The LEI confirmed a high voltage injection did not occur. | Conductor (bare);Insulator tie wires/connections | 0 | 0 | 0 |  | MR 13 | Red phase HV conductor contacted the red phase LV conductor below following a vehicle hitting an adjacent pole the previous day. | Grassfire | 16/11/2015 11:58 | 1 | Localised: less than 10 sq.m | 421 | Roadway |  | 20151222UTD_5 | Infrastructure (network-based) | -37.9306 | 145.0128 | 1 | United Energy Distribution | Report | 635 | 0.0047801 | 11kV AC | Moorabbin Airport | 3187 | Brighton East | Vehicle
Emergency high voltage switching took place and a faults crew identified the deceased possum and a burnt grassed area under the HVABC strain pole. Repairs are required to the north side HVABC at pole No. LIS 1313823 prior to the supply being restored to normal. | 1080 NEPEAN HIGHWAY, MORNINGTON VIC 3931 | LIS No. 1313823 |  | Animal |  | Electrical breakdown |  |  | 1 | At 0356hrs on 22/12/2015, 22kV feeder DMA 23 circuit breaker reclosed to lockout affecting 123 customers. The cause of the 22kV feeder to auto reclose to lockout was attributed to a possum that crossed phase to phase on a HVABC strain structure that caused the burning possum to ignite a small grassed area under pole No. LIS 1313823 located outside 1088 Mornington-Flinders Road, Dromana. The CFA is believed to have attended the site and extinguished the grass fire. Photos are attached. | Conductor (ABC);Pole top | 0 | 0 | 0 |  | DMA 23 | Animal Incident | Grassfire | 22/12/2015 3:56 | 1 | Localised: less than 10 sq.m | 423 | Forest - native (not park) |  | 20151222UTD_6 | Infrastructure (network-based) | -38.3499 | 145.0091 | 1 | United Energy Distribution | Report | 638 | 0.00081944 | 22kV AC | Moorabbin Airport | 3931 | Mornington | Animal
Crew isolated supply and undertook repairs | 39 MONT ALBERT ROAD, CANTERBURY VIC 3126 |  | Vehicle | [5 empty] | 2 | MFB reported that a truck has hit a tree at the incident location. On arrival the crew found that a semi-trailer (registration SY49BX) had contacted the branch of a tree which broke and fell onto an adjacent low voltage service causing it to pull away from the attached house POA causing damage at the POA. The occupant of the truck was unable to leave the vehicle due to concerns the truck maybe a â€œAliveâ€. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/12/2015 11:03 |  |  | 454 | Roadway |  | 20151224PWA_2 | Infrastructure (network-based) | -37.8162 | 145.0645 | 1 | CitiPower | Report | 8000 | 0.030271 | Low voltage AC (<1kV) | Moorabbin Airport | 3126 | Canterbury | Vehicle
Crew isolated supply and undertook repairs | 4731 HENTY HIGHWAY, ROSEBERY VIC 3395 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, which burnt the crossarm causing it to break and fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 20/12/2015 18:00 | 1 | Negligible: no ground fire | 455 | Agricultural |  | 20151224PWA_3 | Infrastructure (network-based) | -35.867 | 142.422 | 1 | Powercor | Report | 694 | 0.037701 | 22kV AC | Horsham Aerodrome | 3395 | Rosebery | Crossarm
Crew made site safe and arranged repairs - reported to Police | 1 ELM GROVE, BRUNSWICK EAST VIC 3057 |  | Theft | [5 empty] | 2 | A Moreland City Council Worker reported an Oil Leak coming from CitiPower Indoor substation at the incident location. On arrival the crew found the door was open and that unknown third parties had stolen the LV/HV switch gear and associated copper wiring. The parties also attempted to access the copper windings from one of the three 1000kva transformers which resulted in an oil spill. There were no reported injuries. | Copper;Indoor;Transformer | 0 | 1 | 0 |  |  | Copper theft | Damage to network assets | 19/12/2015 7:18 |  |  | 456 | Other | Substation | 20151224PWA_4 | Infrastructure (network-based) | -37.7707 | 144.9777 | 1 | CitiPower | Report | 8002 | 0.028568 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3057 | Brunswick East | Other
The attending Powercor Fault Crew replaced the Copper to Aluminium Sleeve connection at the reticulation mains and reconnected the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system and the distribution assets identified Zero Volts following repairs and reconnection of the O/H Service Cable. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 888 WARRNAMBOOL-CARAMUT ROAD, MAILORS FLAT VIC 3275 |  |  |  |  | Corrosion |  |  | 2 | Mr Lachlan Gilmore was showering when he received an electric shock as he made simultaneous contact between his hands on the metal shower taps and his feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor, Copper to Aluminium Sleeve termination on the reticulation mains which was identified as the cause of the high impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 12.9 Volts on the water piping system and between the points of contact. | Customer installation | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral Conductor, Copper to Aluminium Sleeve termination on the reticulation mains. | Minor shock | 42016 |  |  | 457 | Residential |  | 20151224PWA_5 | Infrastructure (customer connection) | -38.2871 | 142.4763 | 1 | Powercor | Report | 696 | 0.036057 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3275 | Mailors Flat | Connection
A faults truck attended and repaired the blue phase LV fused isolator and installed a new length of copper for the connection between the isolator and the street mains. Supply was restored to customers upon completion. | 2 FRASER AVENUE, EDITHVALE VIC 3196 | Pole LIS No. 13303761 |  | Heat |  | Fatigue;Electrical breakdown |  |  | 2 | Customers supplied from "Fraser-Station" substation advised they have lost their electricity supply. The ampact connection for the blue phase LV fused isolator failed (load side) at "Fraser-Station substation that caused hot copper shrapnel to fall into the dry nature strip grass below and start a small grass fire estimated to be 0.5sqm in diameter below the pole - LIS No. 13303761. A customer on site said he quickly extinguished the fire with water and the CFA were not in attendance. | Conductor (bare);Copper;Any other type;Connector/termination | 0 | 0 | 0 |  | CRM 22 | An ampact connection failed at the pole mounted LV fused isolator. | Grassfire | 24/12/2015 18:05 | 1 | Localised: less than 10 sq.m | 465 | Roadway |  | 20151229UTD_1 | Infrastructure (network-based) | -38.0405 | 145.1108 | 1 | United Energy Distribution | Report | 708 | 0.0085035 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Edithvale | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored after 3 x 40amp HV Boric Acid fuses were replaced. | 936 STUMPY GULLY ROAD, TUERONG VIC 3915 | Between pole No. LIS 1112632 and 111183 |  |  |  | Fatigue;Electrical breakdown;Leakage |  |  | 1 | The CFA called to report a pole fire has occurred in Stumpy Gully Road and there is a grass fire on the nature strip. It appeared the 185mm HVABC failed mid-span in Stumpy Gully Road, Hastings between pole No. LIS 1112632 and 111183 near Graydens Road. This resulted in the 22kV conductors to fail and a grass fire of approximately 2sqm started on the road reserve caused by the molten aluminium contacting the dry grass. Secondary damage occurred due to fault current with 3 x 40amp HV Boric Acid fuses operating at the spur fusing at MT 0344 located a short distance away in Graydens Road. Probable molten metal from the fuse operation dropped into the dry scrubland below that caused a fire estimated to be approximately 90sqm to start that was extinguished by the CFA. Minor damage was sustained to a customers fence, tree and grass at 133 Graydens Road with charring evident at the base of the pole. No high voltage injection or major damage was sustained and the cause was suspected to be as a result of the HV conductors failing midspan after tracking to the bare support cable. ESV were notified by United Energy with reference number 4188153 provided. | Conductor (ABC) | 0 | 0 | 0 |  | HGS 22 | HVABC failure | Loss of supply;Grassfire | 26/12/2015 1:38 | 1 | Small: 10 - 1000 sq.m | 466 | Roadway |  | 20151229UTD_2 | Infrastructure (network-based) | -38.2889 | 145.1274 | 1 | United Energy Distribution | Report | 709 | 0.039542 | 22kV AC | Moorabbin Airport | 3915 | Tuerong | OH Cable
Emergency high voltage switching was completed and the HV intermediate crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 580-584 CANTERBURY ROAD, VERMONT VIC 3133 | LIS No. 8484444 |  | Precipitation |  | Age;Electrical breakdown;Insulator |  |  | 2 | Customer called to report arcing from the pole opposite the Vermont Post Office. During light drizzly rain, a pole fire occurred at a HV intermediate crossarm on pole No. LIS 848444 located outside 580 Canterbury Road, Vermont. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | RWT 24 | Probable aged insulator tracking during light drizzle. | Pole-top fire;Loss of supply | 26/12/2015 23:16 | 1 | Negligible: no ground fire | 469 | Roadway |  | 20151230UTD_2 | Infrastructure (network-based) | -37.8366 | 145.194 | 1 | United Energy Distribution | Report | 712 | 0.025656 | 22kV AC | Moorabbin Airport | 3133 | Vermont | Crossarm
Emergency high voltage switching was completed and the HV intermediate crossarm was replaced using glove and barrier techniques. | 11 MCCLURE ROAD, DINGLEY VILLAGE VIC 3172 | LIS No. 0607455 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 0029hrs on 28/12/2015, 22kV feeder SS 23 circuit breaker successfully reclosed and held. Following the successful auto reclose of 22kV feeder SS 23, a patrol of the feeder identified a broken HV intermediate crossarm due to a crossarm fire on pole LIS No. 0607455 located outside 11 McClure Road, Dingley. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | SS 23 | Crossarm fire attributed to tracking on a older style HV insulator. | Pole-top fire | 28/12/2015 0:29 | 1 | Negligible: no ground fire | 472 | Roadway |  | 20151230UTD_3 | Infrastructure (network-based) | -37.968 | 145.126 | 1 | United Energy Distribution | Report | 715 | 0.00034838 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Crossarm
Emergency high voltage switching was completed and the HV isolators were replaced using glove and barrier (G&B) techniques on 29/12/2015. The G&B crew required traffic control to be in attendance at the intersection of Porter Street and Tuscany Road, Templestowe. | 1A TUSCANY RISE, TEMPLESTOWE VIC 3106 | LIS No. 7060294 |  | Heat |  | Overheated connection |  |  | 1 | Per MFB - grass fire has started caused by the powerlines at the intersection of Porter Street and Tuscany Road. A HV connection on the blue phase isolator appeared to heat up under load and molten metal has fallen onto the nature strip and caused a small grass fire estimated to be 1sqm in size to start in the dry grass below. The three HV isolators (DT 0786) require replacement at pole LIS No. 7060294. | Disconnector/isolator | 0 | 0 | 0 |  | DC 01 | The HV blue phase isolator appeared to heat up under load and molten metal has fallen onto the nature strip. | Grassfire | 28/12/2015 15:09 | 1 | Localised: less than 10 sq.m | 473 | Roadway |  | 20151230UTD_4 | Infrastructure (network-based) | -37.7538 | 145.1468 | 1 | United Energy Distribution | Report | 718 | 0.018875 | 22kV AC | Moorabbin Airport | 3106 | Templestowe | Connection
A LEI and faults truck attended and measured 3v between the water pipes and a independent earth. The faults crew proceeded to check and tighten all connections for the underground service and identified a very loose neutral connection in the pole box installed at pole No. LIS 8829234. The LEI re-tested and measured 0.2v between the water pipe and the independent earth. The Water Worx personnel where then given the all clear to complete their work. | 290-292 MIDDLEBOROUGH ROAD, BLACKBURN SOUTH VIC 3130 | LIS No. 8829234 |  |  |  | Neutral fault | Poor workmanship | Phase to earth | 2 | A Plumber called to advise that he received an electric shock when he was working in a trench in front of the property. Another plumber working in the trench also received a shock and they are both okay. A plumbing labourer and plumber were undertaking works in the nature strip outside the above address replacing a water pipe for the building's fire protection system. The labourer received a tingle from the existing water piping and the water it lay in during the course of their work. The plumber also reported a minor tingle from another section of the same piping a few metres way. | Cable;Connection box | 0 | 0 | 0 |  |  | The faults crew identified a very loose neutral connection in the pole box. | Minor shock | 15/12/2015 12:15 |  |  | 476 | Roadway |  | 20151230UTD_5 | Infrastructure (network-based) | -37.8312 | 145.1364 | 1 | United Energy Distribution | Report | 721 | 0.0019803 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn South | Connection
HV EDO fuse tube was replaced with a new tube & fuse. Supply was restored to the customer and meter display now working. | 48 WATERS LANE, COLAC COLAC VIC 3707 | 5215116 | [7 empty] | IMS 219842. Initial CEOT fault report: Fault crew attended site and discovered a candling fuse on the substation COLAC 14. Investigation officer (DAO) attended and reported that the EDO fuse tube was found still in its normal position in one piece with the fuse link firmly wedged inside the tube. It was a fuse hang-up only, no burnt fuse tube. As a result a Schedule 1 report was not required to be sent to ESV but the CEOT did forward a Schedule 1 report. No Schedule 2 report is required for this event. It will be included in the Quarterly report to ESV. Incident category changed to a near miss electrical incident. | EDO fuse | 0 | 0 | 0 |  | wots24 | Equipment failure. | Fuse hang-up only - not a reportable Schedule 1 or 2 incident.;Other | 30/12/2015 10:35 |  |  | 497 |  |  | 20160103SPN_3 | Infrastructure (network-based) | -36.2182 | 147.8481 | 1 | AusNet Services Distribution | Report | 752 | 0.001537 | 22kV AC | Wangaratta Aero | 3707 | Colac Colac | Fuse
CEOT dispatched a fault truck to attend job and make safe. DAO was called to attend and investigate the incident.. The failed branch was pruned clear of the pole and conductors. The findings in a report from AusNet Services' Vegetation Management states "A Select Solutions assessor had assessed this span on 1/05/2015 and the latest assessment code is PT720. WGL13 has not been a part of Select Solutions Hazardous Tree Assessment Program since its inception and its switching zones are ranked low from number 421 to 466 on the Tollhurst priority list. A complete hazardous tree assessment of the whole feeder is unlikely to be untaken in the near future due to higher priorities. Other trees at this locality exhibit poor heath or structural conditions that present a risk to our assets and these will be added to our program." | 42 CONWAY ROAD, DROUIN SOUTH VIC 3818 | 2703599 |  | Dead |  |  |  |  | 2 | IMS 219843. Vicfire reported that a branch had fallen on HV conductor and allegedly started a ground fire of approximate size 120m x 80m, extinguished by the CFA. The CFA were departing as the DAO arrived. The DAO spoke with the fault crew that attended and they advised that a tree branch had partially failed and was resting on the line. The incident was investigated by AusNet Services Vegetation Management and the report states "One large branch failed from outside the clearance space and landed on HV conductors at pole 44 resulting in a grass fire. Partial failure occurred because decay at the point of failure had weakened the branch to an extent that it could not support the branch under the environment conditions of the time. The branch was located in the crown of a 20m high Shire gum tree on the road reserve whose trunk is approximately 11m west of the power lines." No electrical protection operated. | Conductor (bare) | 0 | 0 | 0 |  | wgl13 | Vegetation: Trees Incident | Grassfire | 30/12/2015 14:10 | 1 | Medium: 1000 sq.m - 10 ha | 498 | Agricultural |  | 20160103SPN_4 | Infrastructure (network-based) | -38.2137 | 145.8517 | 1 | AusNet Services Distribution | Report | 754 | 0.018399 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Drouin South | Trees
Made safe | 14 SNOW STREET, KEILOR PARK VIC 3042 |  |  |  |  | Age |  |  | 1 | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Earth leakage | Pole-top fire | 20/12/2015 18:13 | 1 | Negligible: no ground fire | 507 | Residential |  | 20160104JEM_4 | Infrastructure (network-based) | -37.723 | 144.8618 | 1 | Jemena | Report | 769 | 0.029337 | 22kV AC | Essendon Airport | 3042 | Keilor Park | Crossarm
MFB put out fire | 8 BUTLER STREET, BRAYBROOK VIC 3019 |  | Vehicle | [5 empty] | 2 | Truck contacted Optus cable resulting it contacting live conductor causing a fire at the base of the pole. | Conductor (bare) | 0 | 0 | 0 |  |  | Truck hit Optus cable causing to contact live HV conductor | Grassfire | 28/12/2015 12:21 | 1 | Localised: less than 10 sq.m | 508 | Residential |  | 20160104JEM_5 | Infrastructure (network-based) | -37.7786 | 144.8523 | 1 | Jemena | Report | 770 | 0.039715 | 22kV AC | Essendon Airport | 3019 | Braybrook | Vehicle
Made safe | 2 HOCKING STREET, COBURG NORTH VIC 3058 |  |  |  |  | Age |  |  | 1 | Pole fire | Pole (wood) | 0 | 0 | 0 |  |  | Earth leakage | Pole-top fire | 26/12/2015 6:05 | 1 | Negligible: no ground fire | 509 | Residential |  | 20160104JEM_6 | Infrastructure (network-based) | -37.7277 | 144.9571 | 1 | Jemena | Report | 793 | 0.041648 | 22kV AC | Essendon Airport | 3058 | Coburg North | Crossarm
Fault crew dispatched. DAO notified. The fault crew attended the incident and carried out the following actions: Isolated the supply, earthed and made safe KETTLE RD ISO and overhead SWER line; Cut the tree clear of the overhead line; Replaced a small section of overhead line, Aluminum Clad conductor was damaged by the fire and to prevent rusting of the conductor; Re-energised KETTLE RD ISO and overhead SWER line. The DAO attended the incident and gathered the necessary information. | 415 KETTLES ROAD, LANG LANG VIC 3984 | 514140 |  | Wind;Fallen |  |  |  | Phase to earth | 1 | IMS 219857. Fire around our assets Lis #514141 - #514140 (the size of the fire was approximately 3,000 sq.m). Whilst a neighbour (Doreen) was putting out her garbage bin she noticed a puff of smoke and flames ignite in a paddock where a tree had fallen over a SWER line. Doreen reported the fire and the CFA attended. The CFA were delayed in gaining access to the paddock as the gate was too close to the tree that was contacting the electricity line. CFA dropped the fence an accessed the paddock. Approximate height of the tree was 15-16 m and it was in road reserve and approximately 10m from the SWER overhead Line. Signs of timber rot 1m from the ground level. The trees were planted by the local Scout Group within the last 10 years (according to the neighbour). AusNet Services' division Select Solutions' Vegetation Management group have been asked to assess other trees within the vicinity to determine if they are hazardous trees. Electrical protection operated - the ACR tripped to Lockout. | Conductor (bare) | 0 | 0 | 0 |  | llg12 | Vegetation: Trees Incident | Grassfire | 42430.7153 | 1 | Medium: 1000 sq.m - 10 ha | 510 | Agricultural |  | 20160104SPN_1 | Infrastructure (network-based) | -38.2827 | 145.5711 | 1 | AusNet Services Distribution | Report | 774 | 0.0041042 | 12.7kV AC (SWER) | Moorabbin Airport | 3984 | Lang Lang | Trees
The pole type substation was isolated and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 327 GOVERNOR ROAD, BRAESIDE VIC 3195 | LIS No. 0633501 |  | Heat |  | Fatigue |  |  | 2 | Pole fire per MFB - Police on site. At "Governor-Springvale" pole type substation, a customers FOLCB with a LV underground cable attached, caught fire and emergency services were called to attend. The pole top fire damaged the underground cable, FOLCB and the LV transformer leads. The transformer supplied the single customer only. The exact cause of the fire at the FOLCB was unknown but probable lose connection or consumers load may be a contributing factor. | Services cable;Connection box | 0 | 0 | 0 |  |  | The exact cause of the fire at the FOLCB was unknown but probable lose connection or consumers load may be a contributing factor. | Pole-top fire | 25/12/2015 12:04 | 1 | Negligible: no ground fire | 524 | Roadway |  | 20160105UTD_2 | Infrastructure (network-based) | -38.0107 | 145.1369 | 1 | United Energy Distribution | Report | 790 | 0.018817 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Braeside | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 39 NORMANBY STREET, BRIGHTON VIC 3186 | LIS No. 1805821 |  | Heat |  | Fatigue;Electrical breakdown |  |  | 1 | At 1626hrs on 31/12/2015, 11kV feeder NB 24 circuit breaker successfully reclosed and held. At 1628hrs, 11kV feeder NB 24 circuit breaker reclosed to lockout affecting 1242 customers. During very hot and windy conditions, LA's on pole LIS No. 1805821 located near the corner of Normanby and New Streets, Brighton failed and damaged the LV underground cable. The HV termination and LV strain pole also has the HV CHP to "Normanby-New 245" substation attached. The feeder had a successful reclose 2 minutes prior to the lockout and passerby's advised they heard a load bang before the hedge outside the HV CHP caught fire at 39 Normanby Street with the MFB and Police in attendance. The cause of the hedge fire was undetermined and this report is based upon information that was available at the time of the investigation and does not preclude other possible sources of ignition. | Pole top;Cable;Surge diverter | 0 | 0 | 0 |  | NB 24 | The cause of the hedge fire was undetermined and this report is based upon information that was available at the time of the investigation and does not preclude other possible sources of ignition. | Loss of supply;Other vegetation | 31/12/2015 16:28 | 1 | Small: 10 - 1000 sq.m | 527 | Roadway |  | 20160105UTD_3 | Infrastructure (network-based) | -37.9112 | 144.9915 | 1 | United Energy Distribution | Report | 799 | 0.020818 | 11kV AC | Moorabbin Airport | 3186 | Brighton | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 301 PORTER STREET, TEMPLESTOWE VIC 3106 | LIS No. 7065409 - 7065219 |  | Heat |  | Age;Fatigue;Electrical overload |  |  | 1 | At 1743hrs on 31/12/2015, 22kV feeder DC 02 circuit breaker reclosed to lockout. During very hot and windy conditions, a 7/080 copper sleeve failed between pole LIS No. 7065409 and 7065219 located outside 301 Porter Street, Templestowe. It was suspected the cable connection failed due to possible overload and was showing signs of annealing. LV parallels were installed to restore supply to customers supplied from "Roslo-Princetown" substation. Molten metal had fallen from the copper sleeve and started a small grass fire outside 293 Porter Street. A urther trouble order was created to have the HV copper conductors upgraded. | Conductor (bare);Copper | 0 | 0 | 0 |  | DC 02 | It was suspected the cable connection failed due to possible overload and was showing signs of annealing. | Grassfire | 31/12/2015 17:43 | 1 | Localised: less than 10 sq.m | 528 | Roadway |  | 20160105UTD_4 | Infrastructure (network-based) | -37.755 | 145.1576 | 1 | United Energy Distribution | Report | 800 | 0.020293 | 22kV AC | Moorabbin Airport | 3106 | Templestowe | Connection
Crew isolated supply and undertook repairs | 52 HECKFIELD STREET, MACARTHUR VIC 3286 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, resulting in a ground fire (Approx. 10 sqm) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Grassfire | 42401.5174 | 1 | Small: 10 - 1000 sq.m | 554 | Roadway |  | 20160107PWA_14 | Infrastructure (network-based) | -38.0315 | 142.0097 | 1 | Powercor | Report | 837 | 0.038084 | 22kV AC | Hamilton Airport | 3286 | Macarthur | Crossarm
Crew isolated supply and undertook repairs | 1307 HENTY HIGHWAY, LAH VIC 3393 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which burnt the arm causing it to break however the crossarm remained aloft supported by the crossarm braces. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 15:40 | 1 | Negligible: no ground fire | 544 | Roadway |  | 20160107PWA_4 | Infrastructure (network-based) | -36.134 | 142.4181 | 1 | Powercor | Report | 825 | 0.022549 | 22kV AC | Horsham Aerodrome | 3393 | Lah | Crossarm
Crew isolated supply and undertook repairs | 315 LILLIMUR-YEARINGA ROAD, LILLIMUR VIC 3420 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a crossarm fire had occurred on a 22kV pole which burnt the crossarm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 13:10 | 1 | Negligible: no ground fire | 545 | Agricultural |  | 20160107PWA_5 | Infrastructure (network-based) | -36.3199 | 141.1422 | 1 | Powercor | Report | 826 | 0.028044 | 22kV AC | Horsham Aerodrome | 3420 | Lillimur | Crossarm
Crew isolated supply and undertook repairs | 629 BOUNDARY ROAD, TELOPEA DOWNS VIC 3420 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole, resulting in a ground fire (Approx. 5 sqm) on the road reserve. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 26/12/2015 11:10 | 1 | Localised: less than 10 sq.m | 546 | Agricultural |  | 20160107PWA_6 | Infrastructure (network-based) | -36.0894 | 141.2415 | 1 | Powercor | Report | 828 | 0.032198 | 22kV AC | Horsham Aerodrome | 3420 | Telopea Downs | Pole
Crew isolated supply for REC to undertake repairs | 30 REEF STREET, WEDDERBURN VIC 3518 |  |  |  |  | Overheated connection |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that a connection in the fused mains box mounted on the fascia had overheated causing the box to catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Other electricity related | 42552.2722 | 1 | Negligible: no ground fire | 563 | Residential |  | 20160108PWA_2 | Infrastructure (customer connection) | -36.4166 | 143.6108 | 1 | Powercor | Report | 848 | 0.038036 | Low voltage AC (<1kV) | Bendigo Airport | 3518 | Wedderburn | Connection
Crew checked assets for damages | 8 RYDER STREET, SUNSHINE WEST VIC 3020 |  | Vehicle | [5 empty] | 1 | Fire Brigade reported a fire at the above location. On arrival the crew found that a truck had contacted a cable TV cable causing LV conductors to clash resulting in four small ground fire (Totalling approx. 40 sqm) on the road reserve and private property. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Unknown truck contacted Cable TV cable | Grassfire | 42552.6729 | 0 | Small: 10 - 1000 sq.m | 565 | Roadway |  | 20160108PWA_4 | Infrastructure (network-based) | -37.7898 | 144.8215 | 1 | Powercor | Report | 852 | 0.018547 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
Fault crew extinguished the grass fire. To avoid further customer outages, Glove and Barrier crews were called in to make repairs. Once repairs were completed the supply was restored. | 2 BOLDEN STREET, STRATFORD VIC 3862 | 2513714 |  |  |  | Conductor clashing |  |  | 2 | At HV SW 808240 the Blue and White Phase droppers from the Switch to the HV fuses clashed and then one of the HV Boric Acid fuses was seen to be candling and caused a small grass fire of approximately 1 m square. The fault crew were on site whilst this was happening and they put the fire out. | Boric acid;Dropper/bridge | 0 | 0 | 0 |  | mfa21 | Small fire caused by candling BA fuse unit, fuse blew due to phase to phase fault on HV dropper switch leads. Conductor clashing/reduced clearance. | Grassfire | 42614.7222 | 1 | Localised: less than 10 sq.m | 571 | Residential |  | 20160111SPN_1 | Infrastructure (network-based) | -37.9729 | 147.0845 | 1 | AusNet Services Distribution | Report | 861 | 0.020997 | 22kV AC | Bairnsdale Airport | 3862 | Stratford | Fuse
CEOT sent crew to isolate, make safe and investigate. DAO requested to also attend the site to report on the incident. Crew replaced the LV isolator and lead. | 65 GREENHILLS ROAD, BUNDOORA VIC 3083 |  |  |  |  | Overheated connection |  |  | 1 | IMS 219983. Report of a fire at the base of a pole. The attending DAO found that the fire had already been put out and the fire damage to the nature strip measured 4mx13m surrounding pole 906246. After taking some photos the DAO rang CEOT and they confirmed that the fire was caused by a transformer LV isolator lead on the Red Phase that had burnt off. DAO left site at 21.15. LV Red Phase fuse operated. | Pole (concrete);Dropper/bridge | 0 | 0 | 0 |  |  | A transformer isolator lead on the Red Phase had burnt off. Deteriorated equipment / electrical connection failure. | Grassfire | 42705.7604 | 1 | Small: 10 - 1000 sq.m | 590 |  |  | 20160113SPN_4 | Infrastructure (network-based) | -37.6912 | 145.0565 | 1 | AusNet Services Distribution | Report | 891 | 0.031233 | 22kV AC | Essendon Airport | 3083 | Bundoora | AF Other
CEOT sent fault crew to isolate supply, make safe and investigate. DAO advised. Sub OK, customers restored. Replaced with dual action fuse tube. Action raised to replace with Boric Acid fuse. | 6 MINNS ROAD, KOONWARRA VIC 3954 | 2008131 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 219992. 2 HV fuses found burnt / blown apart on LIS#2008131 - No fire on arrival of fault crew. 1/2 of one fuse on ground burnt in half. No fire on pole or on the ground was evident. 1 fuse still in the air - candled, bowed and burnt - EDO fuse blown. | EDO fuse | 0 | 0 | 0 |  | lga14 | Burnt EDO fuse tube. | Other electricity related | 13/01/2016 8:05 | 1 | Negligible: no ground fire | 591 | Agricultural |  | 20160113SPN_5 | Infrastructure (network-based) | -38.5655 | 145.9654 | 1 | AusNet Services Distribution | Report | 893 | 0.036589 | 22kV AC | Morwell (Latrobe Valley Airport) | 3954 | Koonwarra | Fuse
Crew isolated supply and undertook repairs. | 1255 COSGROVE-LEMNOS ROAD, LEMNOS VIC 3631 |  |  |  |  | Unknown technical factor |  |  | 1 | Vicfire reported a fire at the incident location. On arrival the crew found that a 22kV conductor had dislodged off the insulator and fallen onto the LV circuit below, causing molten material from the electrical arcing to fall to the ground and resulting in a ground fire (approx. 4000 sqm) on road reserve and private property. A LEI attended the site and found no damage to installations at the time, however a customer reported a damaged domestic irrigation system at their premises on the 13th of January, which was assumed to be resulting from the suspected HV injection. Protection operated. There were no reported injuries. | Conductor (insulated) | 0 | 0 | 0 |  |  | Dislodged 22kV conductor falling onto an LV conductor below | HV injection;Less than $50k damage;Grassfire | 13/01/2016 16:05 | 1 | Medium: 1000 sq.m - 10 ha | 595 | Agricultural |  | 20160114PWA_2 | Infrastructure (network-based) | -36.3476 | 145.4822 | 1 | Powercor | Report | 2716 | 0.026122 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3631 | Lemnos | Conductor
Pit has been barricaded and scheduled to be lowered to ground level. | 8 DRUMMOND STREET, CRESWICK VIC 3363 |  |  | Erosion |  |  |  |  | 2 | Customer reported on the 8th January 2016 that he had tripped over a protruding electrical pit on the 17th November 2015 at the incident location. The customer advised that he required medical attention for injuries sustained. On arrival the crew found that the pit was approx. 100mm above ground level. The pit has been barricaded off and has been scheduled to have the pit lowered. There was no ground fire. There were no third party property damages. The customer initially reported the incident to Telstra, who advised him only on the week starting 4th January 2016 that the pit was owned by Powercor. | Services pit | 0 | 0 | 0 |  |  | Protruding electrical pit | Medical attention (first aid/doctor/hospital) | 17/11/2015 11:29 |  |  | 596 | Residential |  | 20160114PWA_3 | Infrastructure (network-based) | -37.4202 | 143.8903 | 1 | Powercor | Report | 1032 | 0.028247 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3363 | Creswick | UG Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions | 26 COOMOORA ROAD, SPRINGVALE SOUTH VIC 3172 | LIS No. 0631003 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 1024hrs on 14/01/2016, 22kV feeder ACR DN9898 located in Darren Road reclosed to lockout affecting 206 customers. Following light drizzly rain after a very hot day, a HV intermediate crossarm fire occurred at pole No. LIS 0631003 located in Coomoora Road, Springvale South adjacent to the Coomoora Reserve. There was evidence of the HV conductors making contact with the LV conductors below and a LEI was dispatched to investigate. The LEI checked installations in the vicinity and confirmed that no high voltage injection or damage was sustained to electrical installations supplied from "Serpentine-Coomoora" substation. | Crossarm (wood) | 0 | 0 | 0 |  | NP 14 | Insulator tracking following drizzle. | Pole-top fire | 14/01/2016 10:24 | 1 | Negligible: no ground fire | 607 | Roadway |  | 20160115UTD_6 | Infrastructure (network-based) | -37.9826 | 145.1503 | 1 | United Energy Distribution | Report | 915 | 0.031269 | 22kV AC | Moorabbin Airport | 3172 | Springvale South | Crossarm
Emergency high voltage switching was completed by lifting the live line clamps at the tee-off pole after the substation was isolated. LV parallels were installed to restore supply to customers supplied from "Singer-York" substation and it was planned to complete the rectification work tomorrow in daylight. The substation pole will be replaced under Access Authority conditions with supply restored to normal upon completion. | 1 SINGER AVENUE, GLEN WAVERLEY VIC 3150 | LIS No. 0637896 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 1826hrs on 14/01/2016, 66kV feeder EB-SVTS No. 1 circuit breaker locked out. At the same time 22kV feeder GW 07 and GW 11 circuit breakers reclosed to lockout and GW 04 successfully reclosed and held. A customer from 1 Singer Avenue called to report there is a wire down following a loud explosion resulting in debris laying on the road. Following light drizzly rain, a pole fire occurred at a HV intermediate crossarm at "Singer-York" substation on pole No. LIS 0637896 located outside 1 Singer Avenue, Glen Waverley. Secondary damage occurred due to probable fault current that caused HV conductors to clash between 66kV feeder EB-SVTS and 22kV feeders GW 7 & 11. GW 04 successfully reclosed and held at the same time. No high voltage injection occurred. The 12m substation pole was damaged and requires replacement along with the 100kVA transformer. The pole replacement will be completed tomorrow and will be okay overnight. The 22kV feeders are to be patrolled to determine where the conductor clashing occurred. | Pole (wood);Crossarm (wood);Pole mounted;Transformer | 0 | 0 | 0 |  | 66kV EB-SVTS No. 1 and 22kV feeders GW 7 and 11. | A pole fire occurred at a HV intermediate crossarm at "Singer-York" substation following drizzle after a hot spell. | Pole-top fire | 14/01/2016 18:26 | 1 | Negligible: no ground fire | 611 | Roadway |  | 20160115UTD_8 | Infrastructure (network-based) | -37.8682 | 145.176 | 1 | United Energy Distribution | Report | 920 | 0.024169 | 22kV AC;66kV AC | Moorabbin Airport | 3150 | Glen Waverley | Pole
Crew isolated supply and arranged repairs | 6 RIVER STREET, RICHMOND VIC 3121 |  |  |  |  | Unknown technical factor |  |  | 1 | MFB reported a fire at the incident location. On arrival the crew found that a fire had started in dry debris under the kiosk substation. The crew found that a flashover within the kiosk had occurred which caused the fire. Protection operated. There were no reported injuries. | Equipment | 0 | 0 | 0 |  |  | Flashover in Kiosk cabinet | Other vegetation | 13/01/2016 15:50 | 1 | Localised: less than 10 sq.m | 639 | Roadway |  | 20160118PWA_09 | Infrastructure (network-based) | -37.8155 | 145.0128 | 1 | CitiPower | Report | 970 | 0.014796 | 11kV AC | Essendon Airport | 3121 | Richmond | AF Other
Crew isolated supply and undertook repairs | 561 MELROSE ROAD, COORIEMUNGLE VIC 3268 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV crossarm, causing the crossarm to break and the 22kV High Voltage conductor to fall however the conductor remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42675.7583 | 1 | Negligible: no ground fire | 640 | Roadway |  | 20160118PWA_10 | Infrastructure (network-based) | -38.5802 | 143.0842 | 1 | Powercor | Report | 971 | 0.019902 | 22kV AC | Warrnambool Airport Ndb | 3268 | Cooriemungle | Crossarm
CEOT sent a fault crew to make safe and investigate the incident. Crew replaced 160 Amp White Phase LV Sub bus fuse West cct, Lis 1013685. CFA attended to fire. AusNet Services' Vegetation Management section have conducted an investigation: Tree is Shire responsibility; Decay; tree/branches outside clearance space; strong winds; 65 customers off supply. | 19 DAVID DRIVE, MOOROOLBARK VIC 3138 | 1013685 |  | Blown branch/vegetation |  |  |  | Phase to phase | 1 | IMS 220012. A large eucalyptus tree failed and fell across the opposite side of the road and contacted the LV conductors causing LV to clash. A 2 sq. m burnt area was observed. Blown LV sub bus fuse LIS # 1013685. | Conductor (bare) | 0 | 0 | 0 |  | cpk13 | Vegetation: Trees Incident | Grassfire | 13/01/2016 6:55 | 1 | Localised: less than 10 sq.m | 622 | Residential |  | 20160118SPN_01 | Infrastructure (network-based) | -37.7661 | 145.3113 | 1 | AusNet Services Distribution | Report | 937 | 0.017184 | Low voltage AC (<1kV) | Moorabbin Airport | 3138 | Mooroolbark | Trees
Fault crew made safe and restored supply. Fire report organized. Repairs made - replaced EDO fuse and LA. | 24 WYLIE ROAD, SILVAN VIC 3795 | 1011574 |  | Lightning |  |  |  | Phase to earth | 1 | IMS 220020. Initial CEOT report: CEOT dispatched a fault crew to make safe and investigate. EDO fuse hung- up, charred marks at base of the pole, 1m x 1m, fire out on arrival. No injuries or damage occurred. Final report: The DAO attended site, took photos and prepared a report based on his observations. From my observations it appears that the centre phase (Red) lightning arrestor caused a phase to earth fault which caused a 2mx2m grass fire around the base of pole 1011574. The grass fire cause minor surface damage to the pole and no damage to the adjacent property. lis 1011574, ncf 1 x blown centre phase 10A EDO fuse hung-up (fuse tube wasnâ€™t burnt/candled). There were storms in the area at that time. | Surge diverter | 0 | 0 | 0 |  | ldl13 | LA failed possibly caused by the lightning storm in the area. | Grassfire | 14/01/2016 7:15 | 1 | Localised: less than 10 sq.m | 625 | Residential |  | 20160118SPN_02 | Infrastructure (network-based) | -37.8346 | 145.4336 | 1 | AusNet Services Distribution | Report | 940 | 0.032499 | 22kV AC | Moorabbin Airport | 3795 | Silvan | Fuse
The fault crew isolated the area and replaced the crossarm. 22 KV isolated. On inspection the 22KV 40E Boric Acid fuse had blown on section fuse at 814612 (White phase). Crossarm replaced and fog pin insulators - SL21 and 17 sheds x 2. | 5 BLACK DUCK DRIVE, HAZELWOOD NORTH VIC 3840 |  |  | Precipitation;Prone to salt deposition |  | Leakage |  |  | 1 | IMS 220037. CEOT dispatched fault crew to investigate, make safe and repair. The crew found a burnt 66kV crossarm at pole lis 2605991. Crew arrived on site - crossarm burnt off near crossarm strap bolt and 66kV conductor sitting on 22kV crossarm below. 66kV insulator tracking to crossarm strap. Rain conditions. Confirmed through CEOT CB tripped at MWTS for MWTS / YRM 66kV CB locked out. No pole or ground fire occurred. | Crossarm (wood);Insulators | 0 | 0 | 0 |  |  | 66kV insulator tracking to cross arm strap. Cross arm pollution (dust, salt). | Pole-top fire | 14/01/2016 10:05 | 1 | Negligible: no ground fire | 626 | Agricultural |  | 20160118SPN_03 | Infrastructure (network-based) | -38.2738 | 146.4831 | 1 | AusNet Services Distribution | Report | 942 | 0.039515 | 66kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | Crossarm
CEOT dispatched fault crew to investigate, isolate and make safe. Pole and insulators replaced. | 279 LEES ROAD, VENUS BAY VIC 3956 | 2806123 |  | Precipitation;Prone to salt deposition |  | Leakage |  | Phase to earth | 2 | IMS 220038. CEOT received reports of a pole top arcing - LIS#2806123. CFA attended. No ground fire occurred. Pole top burnt. Pole fire at pole 2806123 Venus Bay spur 120 (Staked HV intermediate pole with HV raiser bracket and 10 shed cyclo-aliphatic insulators). Pole burnt half way down pole where pole was moist and lots of sap wood. Light drizzle in area and salt build up from recent dry spell. Tracking across insulator through steel crossarm and down pole to ground. Ignited mid point of pole where pole was moist. CFA on site to extinguish fire prior to attendance of fault crews. | Pole (wood);Crossarm (steel);Insulators | 0 | 0 | 0 |  | wgi14 | Tracking across insulator through steel crossarm and down pole to ground. | Pole-top fire | 14/01/2016 15:20 | 1 | Negligible: no ground fire | 627 | Residential |  | 20160118SPN_04 | Infrastructure (network-based) | -38.6917 | 145.8033 | 1 | AusNet Services Distribution | Report | 945 | 0.0046863 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Venus Bay | Pole
A faults truck attended and re-terminated the LVABC blue phase connection before supply was restored. | 69-81 GARDEN ROAD, CLAYTON VIC 3168 |  |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | MFB are reporting that a spark from the powerlines caused a grass fire. During warm conditions with a strong north wind, a LVABC IPC connection failed that caused molten metal to fall into the dry grass below and a small grass fire to ignite in front of a factory that was extinguished by the MFB. The grass fire was estimated to be 10sqm in size. The 95mm LVABC blue phase IPC failed at the pole end that supplied a group of factories via a customers private service pole. The cause of the LV connection failure was unknown. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  |  | Probable lose connection or possibly overload. | Grassfire | 18/01/2016 13:23 | 1 | Localised: less than 10 sq.m | 652 | Roadway |  | 20160119UTD_04 | Infrastructure (network-based) | -37.9218 | 145.146 | 1 | United Energy Distribution | Report | 990 | 0.02634 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Connection
Crew removed service from roadway and arranged repairs | 413 BALLARAT ROAD, SUNSHINE VIC 3020 |  | Vehicle | [5 empty] | 2 | A passer-by reported that a pole has fallen over on the nature strip at the incident location. On arrival the crew found that a LV service cable had been contacted by an unknown vehicle/high load and had fallen to the ground. The cable had detached at the supply end and was not alive. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | contact by unknown vehicle/high load | No Go Zone (contact);Damage to network assets | 13/01/2016 13:17 |  |  | 663 | Roadway |  | 20160120PWA_04 | Infrastructure (network-based) | -37.7788 | 144.8423 | 1 | Powercor | Report | 2717 | 0.0093542 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Vehicle
Crew isolated supply and arranged repairs | 61 DEVONSHIRE ROAD, SUNSHINE VIC 3020 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Fire brigade reported a fire on a pole and wires down at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole causing the top crossarm to burn through at the king bolt, and the crossarm to dislodge and the two outer phases to shift from their normal position and come to rest on the bottom 22kV circuit. There were no reported injuries, no shocks, no ground fire, no HVI and no third party damages reported. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 14/01/2016 20:58 | 1 | Negligible: no ground fire | 664 | Roadway |  | 20160120PWA_05 | Infrastructure (network-based) | -37.7852 | 144.8362 | 1 | Powercor | Report | 1005 | 0.015329 | 22kV AC | Essendon Airport | 3020 | Sunshine | Crossarm
Crew attended and inspected lines | 161 QUEEN STREET, ALTONA VIC 3018 |  | Recreation - Kites | [5 empty] | 2 | MFB reported a kite surfer kite stuck on street mains at the incident location. On arrival the crew were unable to find any evidence of a kite surfer kite stuck on the lv mains nor anybody present at the incident location. Residents within the area advised the crew, that the kite had landed on the LV Mains and the wind had blown it off onto the nature strip below. The crew did, however, find evidence of LV mains clashing between the White & Blue Phases of the LV. There were no reported injuries, no shocks, no ground fire, no HVI and no third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Kite surfer kite contacted LV mains | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/01/2016 17:20 |  |  | 665 | Roadway |  | 20160120PWA_06 | Infrastructure (network-based) | -37.8694 | 144.8262 | 2 | Powercor | Report | 8060 | 0.0211 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
Crew arranged supply isolations and repairs | 70-84 KYLE ROAD, ALTONA NORTH VIC 3025 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A passer by reported a crossarm burnt at the incident location. On arrival the crew found the crossarm fire had occurred on a 22kV crossarm within a Zone substation, which had burnt the crossarm at each end and the two outer phases both fell where they remained aloft supported by the 22kV droppers on the pole. There were no reported injuries, no shocks, no ground fire, no HVI and no third party damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 16/01/2016 9:48 | 1 | Negligible: no ground fire | 666 | Other | Substation | 20160120PWA_07 | Infrastructure (network-based) | -37.8256 | 144.8577 | 1 | Powercor | Report | 1007 | 0.025569 | 22kV AC | Laverton Raaf | 3025 | Altona North | Crossarm
Advised Darren Bailey and Leigh to dismantle scaffold and that further work at site to ensure greater than 3000mm clearance to Low Voltage Overhead conductors. Referred to CitiPower Asset Relocations | 82 HUNTER STREET, RICHMOND VIC 3121 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - NGZ Notification 305573855 - Site Visit Incident - Scaffold erected in breach VESI guidelines â€“ Building under construction appears not to comply with Table 313 Asset type - LV Overhead Clearance to asset - 1500mm to scaffold Structure in NGZ: Residential Building â€“ 1600mm adjacent - Proposed Balcony Less than Row A Table 313. Builder - Darren Bailey, 521 Ringwood Warrandyte Rd, Warrandyte South, 0414 371 979 Owner - Darren Bailey Developer - As Above | Conductor (bare) | 0 | 0 | 0 |  |  | Scaffold in NGZ | No Go Zone (no contact) | 18/01/2016 11:02 |  |  | 667 | Roadway |  | 20160120PWA_08 | Infrastructure (network-based) | -37.8217 | 145.0051 | 1 | CitiPower | Report | 1008 | 0.031 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Crew inspected line and referred for checking in daylight | 59 BEND ROAD, TERANG VIC 3264 |  |  | Animal |  |  |  |  | 1 | VicFire reported a fire at the base of a pole at the incident location. On arrival the crew found that a possum had caused a flashover on a 22kV pole and fell to the ground resulting in a grass fire (Approx. 15m x 45m) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Animal Incident | Grassfire | 18/01/2016 3:01 | 1 | Small: 10 - 1000 sq.m | 669 | Roadway |  | 20160120PWA_10 | Infrastructure (network-based) | -38.2556 | 142.8996 | 1 | Powercor | Report | 1011 | 0.039568 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Animal
Crew isolated supply and undertook repairs | 3193 PRINCES HIGHWAY, DRUMBORG VIC 3304 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break and the conductors to fall to the ground, resulting in a ground fire (Approx. 1 sqm) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire;Grassfire | 24/01/2016 20:40 | 1 | Localised: less than 10 sq.m | 721 | Roadway |  | 20160125PWA_03 | Infrastructure (network-based) | -38.0514 | 141.5503 | 1 | Powercor | Report | 1086 | 0.037565 | 22kV AC | Portland (Cashmore Airport) | 3193 | Drumborg | Crossarm
The faults crew cut away the palm tree fronds from the overhead conductors and ensured the site was safe. | 76 LANGHORNE STREET, DANDENONG VIC 3175 |  |  | Blown branch/vegetation |  |  |  |  | 2 | The MFB are reporting there is arcing and sparking power lines behind the property and they are on their way. A customers large palm tree located at the rear of a property on the corner of Langhorne and Power street, Dandenong came into contact with the 22kV overhead conductors and briefly caught fire. The MFB were promptly in attendance and extinguished the burning palm tree fronds that were growing into the electrical assets. | Conductor (bare) | 0 | 0 | 0 |  | DN 07 | Vegetation: Trees Incident | Other vegetation | 23/01/2016 19:39 | 1 | Negligible: no ground fire | 722 | Residential |  | 20160127UTD_01 | Infrastructure (network-based) | -37.9926 | 145.2194 | 1 | United Energy Distribution | Report | 1090 | 0.014421 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Trees
A faults crew attended and found that no damage occurred to the overhead conductors or infrastructure. | 47 DOUGLAS STREET, NOBLE PARK VIC 3174 | LIS No. 9841987 |  | Bird |  |  |  |  | 1 | At 1054hrs on 25/01/2016, 22kV feeder NP 25 circuit breaker successfully reclosed and held. The MFB called to report that a power line is on the ground outside the Noble Park railway station opposite Douglas Street and a small fire has started. A crow made contact with the overhead conductors whilst standing on a steel crossarm on pole No. LIS 9841987 in the railway easement opposite Douglas Street. The burning crow dropped into the dry grass below and a 20sqm grass fire started that was extinguished by the MFB. There was no wire down as reported by the fire brigade. | Pole top | 0 | 0 | 0 |  | DN 25 | Bird Incident | Grassfire | 25/01/2016 11:05 | 1 | Small: 10 - 1000 sq.m | 723 | Public space |  | 20160127UTD_02 | Infrastructure (network-based) | -37.9673 | 145.1769 | 1 | United Energy Distribution | Report | 1091 | 0.036856 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | Animal
Crew isolated supply and undertook repairs | 461 POLKEMMET ROAD, VECTIS VIC 3401 |  |  |  |  | Candled fuse |  |  | 2 | A fault crew attending an outage found that an EDO fuse had operated at the above location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | Candled Fuse | Pole-top fire | 27/01/2016 12:47 | 1 | Negligible: no ground fire | 729 | Agricultural |  | 20160128PWA_01 | Infrastructure (network-based) | -36.6627 | 142.1082 | 1 | Powercor | Report | 1102 | 0.0028912 | 22kV AC | Horsham Aerodrome | 3401 | Vectis | Fuse
Crew isolated supply and arranged repairs | 1500 ST ARNAUD-DUNOLLY ROAD, BEALIBA VIC 3475 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A nearby customer reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole. The crossarm did not break and the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 22/01/2016 13:30 | 1 | Negligible: no ground fire | 741 | Roadway |  | 20160128PWA_10 | Infrastructure (network-based) | -36.7875 | 143.5358 | 1 | Powercor | Report | 1115 | 0.03114 | 22kV AC | Ballarat Aerodrome | 3475 | Bealiba | Crossarm
Crew isolated Low Voltage conductors by breaking bridges. | 13 BERTY STREET, NEWPORT VIC 3015 |  |  | Wind |  |  |  |  | 1 | Low Voltage Conductors on ground - Private tree located at 13 Berty Street Newport fell across Low Voltage conductors bringing all three phases to ground in bay. | Conductor (insulated) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply | 25/11/2015 19:05 |  |  | 267 | Residential |  | 20151126JEM_1 | Infrastructure (network-based) | -37.8479 | 144.8703 | 1 | Jemena | Report | 413 | 0.035979 | 22kV AC | Laverton Raaf | 3015 | Newport | Trees
Isolated HV and LV area | 204 WAIORA ROAD, ROSANNA VIC 3084 |  |  | Wind |  |  |  |  | 1 | Tree brought down HV and LV conductors - Tree fell across High Voltage causing it to fall into Low Voltage and causing High Voltage Injection | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | HV injection | 25/11/2015 23:42 |  |  | 279 | Residential |  | 20151127JEM_2 | Infrastructure (network-based) | -37.7326 | 145.0606 | 1 | Jemena | Report | 415 | 0.0087755 | 22kV AC | Essendon Airport | 3084 | Rosanna | Trees
Crew undertook repairs | 62 HASTINGS ROAD, GREENDALE VIC 3341 |  | Theft | [5 empty] | 2 | A customer reported a wire hanging down from a transformerat the incident location. On arrival the crew found that the substation earthing cable had been pulled out of the ground by unknown third parties, in an attempt to steal the copper conductor. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/11/2015 13:01 |  |  | 273 | Roadway |  | 20151127PWA_2 | Infrastructure (network-based) | -37.5719 | 144.3211 | 1 | Powercor | Report | 405 | 0.01042 | Earthing cable | Avalon Airport | 3341 | Greendale | Other
Area isolated and made safe. Vegetation Management team notified of potential opportunity to re-assess hazard trees and open up easement. Action created to review vegetation management practices in this area. | 106 PAYNESVILLE ROAD, PAYNESVILLE VIC 3880 | 1610605 |  | Fallen | Unlikely |  |  | Phase to earth | 1 | IMS 219317. Trees on HV, caused conductors to clash. CFA attended. Tree broke off at approximately 2.5m from ground and fell through single phase HV conductors. One conductor broke while the other remained under the tree. Feeder CB protection tripped to lockout. BA fuses on Switch Pole 807159 did not operate - action created to review line protection. No evidence of a ground fire but there were burn marks on the tree limb where the conductor was pinned under the tree. The powerline runs through a Parks Victoria managed flora and fauna reserve adjacent to Paynesville Road. | Conductor (bare) | 0 | 0 | 0 |  | bdl4 | Vegetation: Trees Incident | Other vegetation | 26/11/2015 22:25 |  | Negligible: no ground fire | 290 | Roadway |  | 20151130SPN_6 | Infrastructure (network-based) | -37.9063 | 147.7116 | 1 | AusNet Services Distribution | Report | 434 | 0.01077 | 22kV AC | Bairnsdale Airport | 3880 | Paynesville | Trees
Isolated, made safe, replaced fuse and restored supply. A work order to be raised to replace EDO fuse units with BA fuse units. | 507 COBAINS ROAD, COBAINS VIC 3851 | [8 empty] | IMS 219337. Crew arrived at S/S KAY 2 and investigated an all supply failure. Discovered EDO fuse blown and hung-up. No fire occurred. No burnt fuse tube - PLEASE NOTE - incident category has been changed from serious to an electrical near miss incident, therefore no Schedule 2 report is required. Incident will be included as a statistic in the quarterly report to ESV. | EDO fuse | 0 | 0 | 0 |  |  | Hung-up EDO fuse only. | Hung-up fuse only | 27/11/2015 12:20 |  |  | 291 | Agricultural |  | 20151130SPN_7 | Infrastructure (network-based) | -38.0932 | 147.1275 | 1 | AusNet Services Distribution | Report | 436 | 0.019992 | 22kV AC | Bairnsdale Airport | 3851 | Cobains | Fuse
Faults crew isolated LV on transformer and isolated customers' premises. Substation was found to have HV fuses intact and lightning arrestors were not blown. CEOT (control room) reported no lightning hit on nearby ACR. Transformer volts were found to be 245/245V, transformer passed NST test, all connections were checked and found to be OK, although one connection on the transformer looked to be corroded and it seemed to be leaking oil, sounding slightly hollow. NST tests were carried out at all customers meter boards and all passed. The transformer as upgraded to a 25KVA as no other faults were found. Transformer was replaced and all tests were carried out and passed. Supply was then restored as per AusNet Services' procedure Restoration of Supply after HV Incident. | 116 KELLY AND MOSSES ROAD, KORUMBURRA VIC 3950 | 2006466 |  | Lightning | Unlikely |  |  | Phase to earth | 2 | IMS219361. Faults crew attended and were advised by customers that they had appliances that smelt burnt, were not functioning and had heard a loud bang. All customers on substation KELLY LANE 12E numbers 88/90/97/116 Kelly and Mosses Lane were affected. Significant HVI damage was found at properties at 88/90/116 Kelly and Mosses Rd while number 97 was left off supply till access could be arranged, customer was advised and a date was still to be arranged for him to attend. Speaking to customer at number 97 he advised that supply was playing up since the area suffered a severe thunderstorm on the Wednesday / Thursday prior to the fault call. As the transformer was a 1967 model 10 kVA feeding 4 customers and showed signs of loading and possible internal problems. it was decided to upgrade the transformer to a 25kVA, as no other faults were found. Circuit breakers and safety switches tripped on customers' installations. | Pole mounted | 0 | 0 | 0 |  | LGA21 | Lightning / thunderstorm activity. | HV injection | 29/11/2015 11:30 |  |  | 292 | Residential |  | 20151130SPN_8 | Infrastructure (network-based) | -38.4078 | 145.7973 | 1 | AusNet Services Distribution | Report | 438 | 0.019976 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3950 | Korumburra | AF Other
Removed and replaced EDO fuse tube to restore customer supply. | YALBARA, 758 HUON CREEK ROAD, HUON CREEK VIC 3691 | 5203002 |  |  | Unlikely | Age;Corrosion;Electrical breakdown |  |  |  | IMS219358. Operator on call found 6A EDO fuse tube candled. Found no cause. No fires or any damage occurred. | EDO fuse | 0 | 0 | 0 |  | WOTS25 | Equipment failure. | Other electricity related | 28/11/2015 11:45 | 1 | Negligible: no ground fire | 293 | Agricultural |  | 20151130SPN_9 | Infrastructure (network-based) | -36.1508 | 146.8084 | 1 | AusNet Services Distribution | Report | 1148 | 0.028013 | 22kV AC | Wangaratta Aero | 3691 | Huon Creek | Fuse
Isolated and made safe | 4 BOGGY GATE ROAD, CLARKEFIELD VIC 3430 |  | Vehicle | [5 empty] | 1 | Vehicle impact, LV conductors on ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Vehicle impact into HV pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/11/2015 15:18 |  |  | 296 | Agricultural |  | 20151201JEM_2 | Infrastructure (network-based) | -37.5048 | 144.7896 | 1 | Jemena | Report | 529 | 0.03113 | 22kV AC | Melbourne Airport | 3430 | Clarkefield | Vehicle
Crew isolated supply and arranged repairs. | 310 KATANDRA MAIN ROAD, MARUNGI VIC 3634 |  | Vehicle | [5 empty] | 1 | Vicfire reported a fatality when a car hit a pole at the incident location. On arrival the crew found that two cars had collided at the intersection of Labuan Rd and Katandra Main Rd resulting in one of the cars impacting the pole on the south west corner of the intersection. There was no ground fire. The occupant of one of the vehicles that hit the pole suffered fatal injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Car hit pole | Not involving electrocution;Damage to network assets | 30/11/2015 8:30 |  |  | 297 | Roadway |  | 20151201PWA_1 | Infrastructure (network-based) | -36.2391 | 145.525 | 1 | Powercor | Report | 447 | 0.038346 | Not applicable | Shepparton Airport | 3634 | Marungi | Vehicle
Crew checked assets for damage none found | 290 PRINCES HIGHWAY, COLAC WEST VIC 3250 |  | No external/community cause | Fallen |  | No technical cause | No work practice factor |  | 2 | A passer by reported arcing and that a tree had caught fire at the incident location. On arrival the crew found that a tree branch (from outside the clearance space) had fallen onto an adjacent 22kV line, causing the tree branch to smolder and burn. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Other vegetation | 30/11/2015 17:41 |  | No ground fire | 298 | Roadway |  | 20151201PWA_2 | Infrastructure (network-based) | -38.3354 | 143.5572 | 1 | Powercor | Report | 449 | 0.012374 | 22kV AC | Ballarat Aerodrome | 3250 | Colac West | Trees
Crew isolated supply and undertook repairs | 2254 POWERLINE ROAD, KATAMATITE VIC 3649 |  |  |  |  | Overheated connection |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a connection in a pole mounted FOLCB had overheated causing the box to catch fire resulting in a ground fire (Approx. 0.4m x 0.5m) at the base of the pole which self extinguished. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 29/11/2015 9:09 |  | Localised: less than 10 sq.m | 299 | Roadway |  | 20151201PWA_3 | Infrastructure (network-based) | -36.0109 | 145.7057 | 1 | Powercor | Report | 576 | 0.023568 | Low voltage AC (<1kV) | Shepparton Airport | 3649 | Katamatite | Connection
Crew isolated supply and undertook repairs | 1A DURHAM STREET, NEWINGTON VIC 3350 |  | Vehicle | [5 empty] | 2 | A customer reported that a truck has struck a wire and the wire was hanging low at the incident location. On arrival the crew found that a delivery van (Rego: ZXU 218, Operated by: Early Settler, 21 Doveton St Nth, Ballarat, Ph: 03 5331 9890) was reversing down a driveway and contacted an LV service cable causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. Following repairs, the service cable height was measured at 3.8m above the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted service cable | No Go Zone (contact);Damage to network assets | 19/11/2015 8:28 |  |  | 303 | Residential |  | 20151202PWA_1 | Infrastructure (network-based) | -37.5603 | 143.8374 | 1 | Powercor | Report | 456 | 0.021069 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Newington | Vehicle
Crew isolated supply and LEI checked installations for damage | 43 GORDON STREET, BALWYN VIC 3103 |  |  | Blown branch/vegetation |  |  |  |  | 1 | A customer reported a switchboard had been burnt adjacent to above incident location. On arrival the crew found that a tree branch (from outside the clearance space) had fallen across an adjacent 11kV line causing a HV injection resulting in damage to premises connected to the circuit. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Less than $50k damage | 30/11/2015 19:30 |  |  | 308 | Roadway |  | 20151202PWA_2 | Infrastructure (network-based) | -37.8074 | 145.0673 | 1 | CitiPower | Report | 947 | 0.015047 | 11kV AC | Moorabbin Airport | 3103 | Balwyn | Trees
Advised Justin Francis that access to and work from scaffold should be prevented until Scaffold meets VESI requirements and Permit to Work is issued. | 52 SIMPSON STREET, EAST MELBOURNE VIC 3002 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - No Go Zone inspection Incident - Scaffold erected in breach VESI guidelines Asset type - LV aerial service cable and Public Lighting service cable Clearance to asset - 100mm Structure in NGZ: Scaffold Builder - South Eastern Electrics, Justin Francis, Ph: 9590 9066 / 0417 513 007 Scaffold â€“ All Trade Scaffold â€“ Ph: 1300kstage | Conductor (ABC);Service conductor | 0 | 0 | 0 |  |  | Work in NGZ | No Go Zone (no contact) | 16/11/2015 11:59 |  |  | 314 | Roadway |  | 20151204PWA_1 | Infrastructure (network-based) | -37.8152 | 144.9883 | 1 | CitiPower | Report | 469 | 0.0088762 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Other
Reported to ESV, Cable covering left in place pending rectification. | 67 SMITH STREET, FITZROY VIC 3065 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Reason attending site - Permit To Work inspection Incident - Building breaches table 313 building clearance Asset type - LV service cable: Clearance to asset - Service line to adjacent property touching brickwork of new building in Lt Smith St Structure in NGZ: Building Builder - David McKinnon, Longbow constructions Ph 0401 882 103 david@longbowconstructions.com.au Note: Builder was advised on initial inspection that building must comply with Table 313. He has ignored this and built the new building. Service cable to adjoining property is touching the roof of the new building. | Service conductor | 0 | 0 | 0 |  |  | Builder built in no go zone, ignoring advice from permit officer. | No Go Zone (contact) | 26/11/2015 0:00 |  |  | 335 | Residential |  | 20151207PWA_1 | Infrastructure (network-based) | -37.8068 | 144.9827 | 1 | CitiPower | Report | 7988 | 0.032822 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Other
Crew attended and found a possum at base of pole LIS 1012920. AusNet Services' LEI spoke with the customer. Re-instated blown fuses. | 242 EDWARD ROAD, CHIRNSIDE PARK VIC 3116 | 1012920 |  | Animal |  |  |  | Phase to earth | 1 | The fault crew found a dead possum at the base of pole LIS 1012920. LD 579 looked fine according to the 1st responder. An arc has hit a car from a transformer at Cnr of Edwards Rd & Paynes Rd. Reported by Chris Parpa, car registration: 1EB3TB. The caller said he felt a tingle. Reclose at the time and blown fuses. | Outdoor;Pole mounted | 0 | 0 | 0 |  | cpk12 | Animal Incident | Minor shock | 42016.7118 |  |  | 338 | Agricultural |  | 20151207SPN_1 | Infrastructure (network-based) | -37.7368 | 145.3199 | 1 | AusNet Services Distribution | Report | 510 | 0.0095868 | 22kV AC | Moorabbin Airport | 3116 | Chirnside Park | Animal
The Downer work crew contacted CEOT to advise of the incident also reported it to their local site manager. AusNet Services confirmed there was feeder fault on ELM32. Repairs were carried out by an underground crew by installing a new HV cable joint. | 396 RYANS ROAD, ELTHAM NORTH VIC 3095 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 219486. A Downer line crew were changing a LV crossarm when HV shattered in same bay they were working on. Evidently a Banyule City Council contractor was installing a Council sign for the suburb of St Helena when they damaged AusNet Services' live underground HV cable. The feeder protection operated and the crew installed a HV joint. Please note the incident address is difficult to ascertain apart from the fact the Council sign in question is directly under the Transmission lines that run over Ryans Rd, which is an extension of Wattletree Rd. | Cable | 0 | 0 | 0 |  | ELM32 | 3rd party damage. | No Go Zone (contact) | 24/11/2015 10:50 |  |  | 341 | Public space |  | 20151207SPN_2 | Infrastructure (network-based) | -37.6841 | 145.1437 | 1 | AusNet Services Distribution | Report | 2811 | 0.030197 | 22kV AC | Essendon Airport | 3095 | Eltham North | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. The large tree branch was removed in Union Street and the HV mid-span isolators were removed in McKinnon Road and the conductors sleeved. The 66kV conductor has strands missing following the clashing and a helical termination was installed. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 119 UNION STREET, BRIGHTON EAST VIC 3187 | LIS No. 2333175 and 2303480 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1920hrs on 30/11/2015, 66kV feeder BT-NB locked out. At the same time, 11kV feeder BT05 circuit breaker reclosed to lockout affecting 742 customers. During strong winds, a large private tree branch from 119 Union Street, Brighton East contacted the 66kV, 11kV conductors that resulted in a HV conductor to contact the LV conductors below near pole No. LIS 2333175 near the corner of Trinity Court. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Mackie-Union" substation. The LEI confirmed a high voltage injection occurred (CLA 1508) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. Secondary damage occurred following HV mid-span isolators clashing as a result of probable fault current near pole No. LIS 2303480. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | 66kV feeder BT-NB and 11kV feeder BT 05 | Vegetation: Trees Incident | HV injection;Loss of supply | 30/11/2015 19:20 |  |  | 340 | Roadway |  | 20151207UTD_2 | Infrastructure (network-based) | -37.9095 | 145.0207 | 1 | United Energy Distribution | Report | 500 | 0.014615 | Low voltage AC (<1kV);11kV AC;66kV AC | Moorabbin Airport | 3187 | Brighton East | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to supply being restored. | 39 WETHERBY ROAD, DONCASTER VIC 3108 | LIS No. 7061588 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | At 1923hrs on 30/11/2015, 22kV feeder DC 10 circuit breaker reclosed to lockout affecting 4810 customers. At the time of the fault, 22kV feeder DC 03 was switched abnormally that resulted in a small number of customers supplied from this feeder to lose supply for a short duration. During strong winds, 22kV feeder DC 10 circuit breaker reclosed to lockout. The cause was a tree within an reserve, 3 poles west of Weatherby Road, Doncaster (north of the Eastern Freeway) falling over the conductors near pole No. LIS 7061588. This caused molten metal to fall into the dry grass below and sparks fanned by the strong winds, burnt a large grassed area estimated at 4000sqm. The fire quickly spread into surrounding scrub and bush of the reserve along a bike track. In addition, the strong winds also caused the fallen tree canopy to catch fire and flying embers flew over Middleborough Road causing an additional grass fire in dry scrub land next to the road reserve. Eight MFB trucks and an estimated 30 fire-fighters responded quickly and extinguished the fire with Middleborough Road closed for several hours. It took MFB crews one hour and twenty minutes to contain the blaze and 2.5 hours to extinguish it completely. There are homes in the area and a smoke warning was issued, however no homes were evacuated. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | DC 10 | Vegetation: Trees Incident | Loss of supply;Grassfire | 30/11/2015 19:23 |  | Medium: 1000 sq.m - 10 ha | 345 | Residential |  | 20151207UTD_3 | Infrastructure (network-based) | -37.7905 | 145.1429 | 1 | United Energy Distribution | Report | 507 | 0.0074479 | 22kV AC | Moorabbin Airport | 3108 | Doncaster | Trees
Crew isolated supply and undertook repairs | 501 CRESWICK ROAD, BALLARAT VIC 3350 |  |  |  |  | Overheated connection |  |  | 2 | VicFire reported a transformer fire had started a grass fire at the incident location. On arrival the crew found that the PG clamp on the 22kV conductor had overheated causing hot debris to fall to the ground resulting is a ground fire (approx. 10m x 1m) in the road reserve. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 42136.9556 |  | Small: 10 - 1000 sq.m | 350 | Roadway |  | 20151208PWA_4 | Infrastructure (network-based) | -37.5463 | 143.8504 | 1 | Powercor | Report | 518 | 0.034441 | 22kV AC | Ballarat Aerodrome | 3350 | Ballarat | Connection
Crew isolated supply and undertook repairs | 55 ROHS ROAD, EAST BENDIGO VIC 3550 |  | Vehicle | [5 empty] | 2 | A property owner reported that a truck he was driving had hit a service cable at the incident location. On arrival the crew found that a truck (driven by George Bobin, Ph: 0428 510 426) was entering the property and contacted a LV service cable, breaking the cable which fell to the ground resulting in a grass fire (Approx. 1m x 7m) that was put out by the truck driver. There were no reported injuries. Following repairs the cable height was measured at 5.0m at the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | Grassfire;No Go Zone (contact);Damage to network assets | 42197.4514 |  | Localised: less than 10 sq.m | 358 | Residential |  | 20151210PWA_2 | Infrastructure (network-based) | -36.74 | 144.3162 | 1 | Powercor | Report | 541 | 0.0094144 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | East Bendigo | Vehicle
Crew isolated supply for repairs to be undertaken | 82 FARNSWORTH STREET, CASTLEMAINE VIC 3450 |  | Vehicle | [5 empty] | 2 | The property owner reported that a truck had contacted and bought down a service wire and it was sitting on the top of the truck at the incident location. On arrival the crew found that a truck (Driven by Steve, Hi-Haul, 51 Gatwick Road, Bayswater North, Ph: 0425 718 948) had contacted an LV service cable causing the cable to pull away from the fascia of the house and come to rest on the truck. There were no reported injuries. The truck height was measured at 5.2m. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | No Go Zone (contact);Damage to network assets | 42106.441 |  |  | 371 | Roadway |  | 20151211PWA_1 | Infrastructure (network-based) | -37.0615 | 144.2099 | 1 | Powercor | Report | 555 | 0.03198 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Vehicle
Crew isolated supply and undertook repairs | 105-275 WARNCOORT-BIRREGURRA ROAD, WANCOORT VIC 3243 |  | Vehicle | [5 empty] | 2 | VicFire reported a car into pole and low wire in the Warncoort area. When crews arrived it took some time to establish the exact incident location based on the information provided, however the crew eventually found a 22kV HV conductor resting on a wooden crossarm (HV insulator tie had been broken). The crashed vehicle and emergency authorities had already left the scene. Upon arrival by the repair crew they found that a pole fire had occurred which burnt the pole and crossarm. The assets remained aloft and intact. There were no reported injuries or third party property damages. There was no ground fire. | Pole (wood) | 0 | 0 | 0 |  |  | Car hit pole | Pole-top fire | 42106.6951 |  | Negligible: no ground fire | 372 | Roadway |  | 20151211PWA_2 | Infrastructure (network-based) | -38.3177 | 143.7358 | 1 | Powercor | Report | 556 | 0.039321 | 22kV AC | Avalon Airport | 3243 | Wancoort | Vehicle
Crew isolated supply and undertook repairs | 321 PRINCES HIGHWAY, WERRIBEE VIC 3030 | WBE013 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that he has dug up an underground cable at the incident location. On arrival the crew found that a contractor (Negri Constructions, 32 Randell Street, Campbellfield, Contact: Hasham, Ph: 0458 974 481) was undertaking works and contacted a LV underground cable supplying public lights. Powercor could find no record of a current DBYD enquiry by this contractor for this location. There were no reported injuries or third party property damages. | Services cable | 0 | 0 | 0 |  | 30324401 | underground dig-in | No Go Zone (contact) | 42106.4514 |  |  | 373 | Roadway |  | 20151211PWA_3 | Infrastructure (network-based) | -37.8842 | 144.7004 | 1 | Powercor | Report | 13235 | 0.024029 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
Crew checked cable for damage, none found. Crew arranged cable test to confirm | 552-554 VICTORIA PARADE, EAST MELBOURNE VIC 3002 |  | Working too close to underground cables | [5 empty] | 2 | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location. On arrival the crew found that the contractor (Bricker Plumbing & Drainage, Ph: 9588 0666, working for City West Water) was undertaking excavation works and contacted a 22kV cable which â€œbruisedâ€ the cable. No fault occurred when contact was made with the cable. DBYD enquiry for this location was made by the contractor and the number is 49347413. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Excavator contacted UG cable | No Go Zone (contact) | 42197.6653 |  |  | 383 | Roadway |  | 20151214PWA_2 | Infrastructure (network-based) | -37.8101 | 144.9898 | 1 | CitiPower | Report | 949 | 0.017052 | 22kV AC | Essendon Airport | 3002 | East Melbourne | Dug up
Crew isolated supply and undertook repairs | 70 CAMPBELL STREET, KEW VIC 3101 |  | Working too close to overhead lines | [5 empty] | 2 | A field crew attending an outage found that a contractor (Vic Low Loaders, 1350 Kooweerup-Longwary Rd, Katani, Contact: Peter, Ph: 0418 509 816) was loading an excavator onto a low loader and contacted LV overhead mains cables, causing two of the cables to break and fall to the ground. There was no ground fire. There were no reported injuries or third party property damages. The cable height was measured at approximately 6.0m. | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator contacted LV cables | No Go Zone (contact) | 42136.4076 |  |  | 384 | Roadway |  | 20151214PWA_3 | Infrastructure (network-based) | -37.8023 | 145.0573 | 1 | CitiPower | Report | 948 | 0.040264 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Vehicle
A fault crew attended and advised the service line fell down from a fallen massive tree branch. The DAO was informed to investigate. The existing overhead service cable required to be replaced and remove tree to gain access to the POA. | 30 ST HELENA ROAD, GREENSBOROUGH VIC 3088 | 3121 |  | Fallen |  |  |  | Phase to earth | 2 | IMS 219590. Report via VicFire of a tree branch fallen on a conductor. A large tree branch broke a 2 core overhead XLPE service cable. Broken cores resulted in a small grass fire of 10 sq. metres in size. | Service conductor | 0 | 0 | 0 |  | WT8 | Vegetation: Trees Incident | Grassfire | 42289.7396 | 1 | Localised: less than 10 sq.m | 379 | Residential |  | 20151214SPN_1 | Infrastructure (network-based) | -37.6999 | 145.1106 | 1 | AusNet Services Distribution | Report | 564 | 0.041255 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | Trees
CEOT dispatched a fault crew to make safe. The crew replaced the line fuses and restored supply. A protection investigation report was completed - Based on analysis of available event records of MFA31 feeder CB, the feeder protection picked up and dropped out correctly and as designed. The BA15E fuses operated correctly to clear the fault. There is no evidence to conclude that the conductor remained alive. No changes to the electrical protection is required. | 138 THREE CHAIN ROAD, MAFFRA VIC 3860 | 2514573 |  | Fallen |  |  |  | Phase to phase | 1 | A tree fell on the 22kV line (3/2.75 steel conductors) and its branches caught fire. Did not start a ground fire. Once burnt through, the line went back to its normal position. The tree branch fire was extinguished by the rain. Tree that fell was approximately 7m away from the outside phase. There are other trees in the area which are 5m away. The tree failed at it's trunk with no sign of termites. According to BOM wind gusts reached 59km/h at 5:30PM. No property damage from incident. The line was in good condition and only had small amount of charcoal from the tree. | Conductor (bare) | 0 | 0 | 0 |  | MFA31 | Vegetation: Trees Incident | Other vegetation | 42320.6944 | 1 | Negligible: no ground fire | 380 | Residential |  | 20151214SPN_2 | Infrastructure (network-based) | -37.9298 | 146.9783 | 1 | AusNet Services Distribution | Report | 566 | 0.023984 | 22kV AC | Morwell (Latrobe Valley Airport) | 3860 | Maffra | Trees
Discussed with Tom Dobson of McKimm. Advised that persons should be prevented (warning signs / barriers) from accessing and working from scaffold in vicinity where Aerial Service Cable passes thru. Further advised that incident to be reported to CP/Pal Risk Management. Tom advised that Scaffold installed by Lock Up Scaffold, Dan ?, 0438 330 917 | 1 ST JAMES PLACE, TOORAK VIC 3142 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - NGZ Notification305448126 â€“ (We require Tiger Tails to low voltage power supply to house.) Incident - Scaffold erected in breach of VESI guidelines Asset type - LV service cable Clearance to asset - Scaffold erected around Aerial Service Cable, > 250mm to scaffold Structure in NGZ: Scaffold Builder - Name and contact details: McKimm â€“ 422 New St, Brighton, 3186. 9592 1166. Project Manager Dan Stevens. Site Contact: Tom Dobson, 0418 357 878 | Service conductor | 0 | 0 | 0 |  |  | Scaffold in No Go Zone | No Go Zone (no contact) | 28/10/2015 10:30 |  |  | 391 | Roadway |  | 20151216PWA_3 | Infrastructure (network-based) | -37.8474 | 145.0192 | 2 | CitiPower | Report | 7996 | 0.031485 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Other
Opened BA fuse, replaced fuse tube and restored supply. | 34 ABECKETT ROAD, BUNYIP VIC 3815 | 2708886 |  |  |  | Mechanical breakdown |  |  | 2 | AusNet Services' Operator found a BA fuse candling at Bunyip River P002 substation, LIS : 2708886. Opened the Boric Acid fuse, replaced the BA fuse tube and restored supply. No ground or pole fire occurred. | Boric acid | 0 | 0 | 0 |  | WGL21 | Burnt fuse tube, equipment failure. | Plant/equipment | 14/12/2015 14:45 |  | Negligible: no ground fire | 393 | Residential |  | 20151217SPN_1 | Infrastructure (network-based) | -38.0951 | 145.7274 | 1 | AusNet Services Distribution | Report | 1236 | 0.027253 | 22kV AC | Moorabbin Airport | 3815 | Bunyip | Fuse
CEOT dispatched an underground fault crew to the site to isolate, make safe, investigate and repair. The crew repaired the damaged underground HV cable and restored supply. A No Go Zone Rules warning letter is to be sent to the offending party. | 6 NEVERN COURT, DIAMOND CREEK VIC 3089 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | A machine operator while digging a hole on 6 Nevern Ct, Diamond Creek, damaged a 22kV underground cable. The underground cable was located within its easement and at approximately 1 metre depth. The machine operator was Jason Smith of JNS Excavation, mobile: 0401 416 313 of 135 Wattletree Rd, Hurstbridge, VIC, 3099. Electrical protection operated at asset GB510, 25e BA fuses. No electrical shock or injuries were sustained. | Cable | 0 | 0 | 0 |  | elm12 | The incident was caused by an excavator operator. | No Go Zone (contact) | 15/12/2015 9:30 |  |  | 395 | Residential |  | 20151217SPN_3 | Infrastructure (network-based) | -37.6662 | 145.1542 | 1 | AusNet Services Distribution | Report | 597 | 0.011394 | 22kV AC | Essendon Airport | 3089 | Diamond Creek | Dug up
Crew isolated supply and undertook repairs | 2316 WAITCHIE ROAD, WAITCHIE VIC 3544 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Customer reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the crossarm and the top of the pole causing the pole top to break and fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42228.3639 |  | Negligible: no ground fire | 401 | Roadway |  | 20151218PWA_1 | Infrastructure (network-based) | -35.3624 | 143.0858 | 1 | Powercor | Report | 605 | 0.0014294 | 22kV AC | Swan Hill Aerodrome | 3544 | Waitchie | Crossarm
Crew isolated supply and undertook repairs. REC arranged repairs to POA | 117 ARTHURTON ROAD, NORTHCOTE VIC 3070 |  | Vehicle | [5 empty] | 2 | A passer by reported that a truck had contacted and bought down a service wire and it was lying on the footpath at the incident location. On arrival the crew found that an LV service had been contacted by a truck (Rego: ZXM 799 â€“ No other details reported to the crew, and the truck had left the scene of the incident), causing the service to be pulled away from the POA and falling to the ground resulting in damage to the POA. The height of the cable was measured following repairs at 5.1m at the POA and 5.3m at the kerb. | Service conductor | 0 | 0 | 0 |  |  | truck contacted LV service cable | No Go Zone (contact);Damage to network assets | 42289.3063 |  |  | 432 | Roadway |  | 20151222PWA_10 | Infrastructure (network-based) | -37.7682 | 144.989 | 1 | CitiPower | Report | 7998 | 0.035466 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
Crew isolated supply and undertook repairs | 15 AVONLEA STREET, NUMURKAH VIC 3636 |  | Working too close to underground cables | [6 empty] | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location. On arrival the crew found that a contractor (NL Drainage, contact Brad Wereszczuk : Ph: 0407 801 714) was operating an excavator and contacted a LV underground mains cable causing damage to the cable and conduit. A DBYD enquiry had been made for this contractor at this location. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Excavator contacted cable | No Go Zone (contact);Damage to network assets | 15/12/2015 8:39 |  |  | 433 | Roadway |  | 20151222PWA_11 | Infrastructure (network-based) | -36.0784 | 145.4429 | 1 | Powercor | Report | 677 | 0.041301 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Dug up
Crew checked assets for damage - only stolen earth found to be irregular and could not have been cause of fire | 490 HADDON-WINDERMERE ROAD, CARDIGAN VIC 3352 |  | Unknown external/community factor | [5 empty] | 2 | Vic Fire reported a fire at the incident location. On arrival the crew found that a 3m section of the HV earth had been stolen from a SWER ACR pole and a ground fire had occurred (Approx. 10m x 20m) on the road easement and private property. There were no reported injuries. The crew could not determine any asset related cause for the fire. | No failed asset | 0 | 0 | 0 |  |  | Crew unable to determine cause of fire | Grassfire | 19/12/2015 9:00 | 0 | Small: 10 - 1000 sq.m | 429 | Roadway |  | 20151222PWA_7 | Infrastructure (network-based) | -37.5558 | 143.707 | 2 | Powercor | Report | 1047 | 0.020407 | Not applicable | Ballarat Aerodrome | 3352 | Cardigan | Other
Crew isolated supply and undertook repairs | BONNIE DOONE, 17 DUGGANS ROAD, BENAYEO VIC 3319 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the pole causing the top of the pole to break and fall to the ground, resulting in a ground fire (Approx. 10m x 10m) on private property. Protection operated. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 20/12/2015 18:50 | 1 | Small: 10 - 1000 sq.m | 430 | Agricultural |  | 20151222PWA_8 | Infrastructure (network-based) | -36.8068 | 141.01 | 1 | Powercor | Report | 652 | 0.02541 | 22kV AC | Horsham Aerodrome | 3319 | Benayeo | Pole
Crew isolated supply and arranged repairs. LEI checked installations for damage. | 589-595 RAGLAN PARADE, WARRNAMBOOL VIC 3280 |  | Vehicle | [5 empty] | 1 | Vicfire reported a car had hit a pole at the incident location. On arrival the crew found that a car (Rego YTS-173) had struck a High Voltage/ Low Voltage pole, causing the 22kV High voltage conductors and the 240V Low voltage conductors to contact each other, causing a High Voltage Injection which damaged equipment at two connected installations. The driver decamped the scene, and Police are investigating. Protection operated. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Car hit pole | HV injection | 21/12/2015 6:22 |  |  | 431 | Roadway |  | 20151222PWA_9 | Infrastructure (network-based) | -38.3801 | 142.4837 | 1 | Powercor | Report | 654 | 0.017769 | Low voltage AC (<1kV);22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
Observations were conducted by attending field crews. Assets in the vicinity inspected. No remediation works were required. | 418 RILEYS ROAD, BARNAWARTHA VIC 3688 | 5208665 | [7 empty] | AusNet Services attended 418 Rileys Road, Barnawartha on Sunday 20 December, following notification from CFA of an alleged fire at the property. Police and CFA were in attendance. The property owner, Mr Bektash, alleged that a branch of a tree on his property had peeled away from its trunk and rested in the fork of another branch of the tree. Mr Bektash further alleged that he had observed foliage from this branch brushing the conductor intermittently in the wind. The tree is located approximately 6.3m from the conductor and had been cut down by Mr Bektash before AusNet Services arrived at the scene. AusNet Services' investigations continue into this incident | No failed asset | 0 | 0 | 0 |  | bwa22 | Vegetation: Trees Incident | Other vegetation | 20/12/2015 15:50 |  | Negligible: no ground fire | 420 | Agricultural |  | 20151222SPN_1 | Infrastructure (network-based) | -36.1115 | 146.653 | 1 | AusNet Services Distribution | Report | 3279 | 0.04149 | 22kV AC | Wangaratta Aero | 3688 | Barnawartha | Trees
The No Go Zone Supervisor attended, took photos and provided details of the No Go Zone breach to Worksafe and ESV to investigate the breach. | 483 GLEN HUNTLY ROAD, ELSTERNWICK VIC 3185 |  | Building too close or within the No Go Zone;Working too close to overhead lines |  | Highly likely |  | Not followed |  | 2 | ZNX No Go Zone (NGZ) supervisor reported a breach of the NGZ Guidelines at 483 Glenhuntly Road, Elsternwick. A ZNX No Go Zone Co-ordinator inspected the site on 06/03/2014 requesting visual aid battens to be installed on the LV open wire conductors. 25/03/2014 - PTW issued to Roy Amira with safety precautions identified and clearances to be maintained. Roy was also advised to contact a Project Planner regarding clearances that must be maintained from the overhead LV powerlines. The ZNX No Go Zone Co-ordinator instructed the builder not to proceed past the first floor. An offer to replace the LV open wire conductors with LVABC was accepted by the builder who requested the work to be completed as soon as possible. Please also find attached copies of the following documents" - copies of the ZNX letter of offer - Permit to Work inspection reports and completed PTW - Photos of the site | Conductor (bare) | 0 | 0 | 0 |  |  | No Go Zone breach | No Go Zone (no contact) | 22/12/2015 9:09 |  |  | 416 | Construction |  | 20151222UTD_1 | Infrastructure (network-based) | -37.8851 | 145.0084 | 1 | United Energy Distribution | Report | 629 | 0.0070046 | Low voltage AC (<1kV) | Moorabbin Airport | 3185 | Elsternwick | Other
An underground crew attended and replaced the LV pillar after repairing the conductors that had been damaged. Supply was restored upon completion. | 11 JONQUIL COURT, DONCASTER EAST VIC 3109 |  | Vehicle |  |  | Electrical breakdown;Mechanical breakdown |  |  | 2 | Customer called to report a tradesman has struck the power pit in front of the property on the nature strip. It was on fire with the wires exposed and they have lost their power supply. A tradesman's vehicle struck the LV pillar located outside 11 Jonquil Court, Doncaster East that caused dry grass surrounding the pillar to catch on fire with wires now exposed. The grass fire was estimated to be 20sqm in size and was quickly extinguished. | LV Pillar | 0 | 0 | 0 |  |  | A tradesman's vehicle struck the LV pillar that caused dry grass surrounding the pillar to catch on fire. | Grassfire | 18/12/2015 16:28 | 1 | Small: 10 - 1000 sq.m | 417 | Residential |  | 20151222UTD_2 | Infrastructure (network-based) | -37.7704 | 145.1721 | 1 | United Energy Distribution | Report | 630 | 0.026991 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Vehicle
Advised Jon Page not to work or approach within 2000mm Citipower LV ABC | 143 FARRELL STREET, PORT MELBOURNE VIC 3207 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Reason attending site - NGZ Enquiry â€“ Notification 305542661 Incident - Building under construction at rear of 143 Farrell St < 1000mm to LV ABC in Albert St frontage Asset type - LV ABC Clearance to asset - < 1000mm Structure in NGZ: Residential Building / Extension under construction Builder - Mil Constructions mike@milconstructions.com Site Contact: Jon Page 0419 140 395 Owner - Scott Jackson, 0427 447 970, scott_jackson31@hotmail.com | Conductor (ABC) | 0 | 0 | 0 |  |  | Breached VESI Guidelines - Building under construction not compliant to Table 313 | No Go Zone (no contact) | 23/12/2015 8:23 |  |  | 436 |  |  | 20151223PWA_2 | Infrastructure (network-based) | -37.8338 | 144.9384 | 1 | CitiPower | Report | 7999 | 0.018613 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Other
Crew isolated supply and undertook repairs | 6944 MILLEWA ROAD, WERRIMULL VIC 3496 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  |  | A field crew attending an outage found that a pole fire had occurred on a SWER pole which burnt the top of the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42349.5146 | 1 | Negligible: no ground fire | 441 | Agricultural |  | 20151223PWA_7 | Infrastructure (network-based) | -34.4066 | 141.447 | 1 | Powercor | Report | 664 | 0.024738 | 12.7kV AC (SWER) | Mildura Airport | 3496 | Werrimull | Pole
Dispatched fault crew to isolated supply, make safe and repair. Duty availability officer advised to investigate. Downer fault crew repaired the downed conductor and restored supply. | 1780 WESTERNPORT ROAD, HEATH HILL VIC 3981 | 513953 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | Report of SWER conductor down. Excavator parked in same bay as SWER wire down. No other damage. Incident occurred due to a farmer bringing the SWER wire down with an excavator. The farmer was unaware of the incident until a Downer fault crew attended the site. | Conductor (bare) | 0 | 0 | 0 |  | llg11 | An excavator contacted an overhead SWER conductor. | No Go Zone (contact) | 22/12/2015 13:25 |  |  | 446 | Agricultural |  | 20151223SPN_2 | Infrastructure (network-based) | -38.2352 | 145.7336 | 1 | AusNet Services Distribution | Report | 672 | 0.022775 | 12.7kV AC (SWER) | Moorabbin Airport | 3981 | Heath Hill | Vehicle
CEOT dispatched fault crew to isolate supply, make safe and investigate. The Lineworker pulled the sub when he arrived and notified operations (CEOT). Lineworkers put numerous sleeves on the .080 copper LV conductor. | 6 ROSE AVENUE, COWES VIC 3922 | 2805929 |  | Within clearances |  |  |  | Phase to earth |  | Whilst felling a tree on his property, the owner of the property caused the tree to fall onto the LV mains. Two phases of the LV mains were live on ground on the nature strip. Tree came down and burnt Blue and White phases to the ground on LV and splashed onto the Neutral and Red phase. No fire occurred. Fuses didn't blow. The responsible person was: Ben Lacarruba, 24 Merton St, Ivanhoe, tel 040095554. | Conductor (bare) | 0 | 0 | 0 |  | phi13 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/12/2015 19:50 |  |  | 447 | Residential |  | 20151223SPN_3 | Infrastructure (network-based) | -38.4502 | 145.2524 | 1 | AusNet Services Distribution | Report | 675 | 0.030897 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Cowes | Trees
Crew isolated supply and undertook repairs | 1101 MAIR STREET, BALLARAT CENTRAL VIC 3350 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, which burnt the arm causing the arm to break and fall on to a lower 22kV circuit. There was no ground fire. Protection operated. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 20/12/2015 18:17 | 1 | Negligible: no ground fire | 459 | Roadway |  | 20151224PWA_7 | Infrastructure (network-based) | -37.5581 | 143.8448 | 1 | Powercor | Report | 698 | 0.039773 | 22kV AC | Ballarat Aerodrome | 3350 | Ballarat Central | Crossarm
CEOT sent fault crew to make safe and tree clearers, Asplund, to clear tree. Necessary repairs were made to the HV conductors by a construction crew. | 5 VALERIE DRIVE, WONGA PARK VIC 3115 | 1203555 |  | Wind;Dead |  |  |  | Phase to earth | 2 | A private tree fell onto a single phase 22kV line and caused a HV conductor to fall to the ground. A small fire of 4m x 5m in size was observed underneath the line. DAO was dispatched to investigate the incident. IMS 219830. A 30 metre dead pine tree situated 22 metres from the line failed at its root plate. The tree branches were outside the clearance space but the tree was classed as a hazardous. Strong windy conditions prevailed at the time of the incident. | Conductor (bare) | 0 | 0 | 0 |  | cpk11 | Vegetation: Trees Incident | Grassfire | 26/12/2015 14:30 | 1 | Small: 10 - 1000 sq.m | 463 |  |  | 20151229SPN_1 | Infrastructure (network-based) | -37.7508 | 145.2766 | 1 | AusNet Services Distribution | Report | 705 | 0.0085845 | 22kV AC | Moorabbin Airport | 3115 | Wonga Park | Trees
Crew isolated supply and undertook repairs. | 43 BELLS BOULEVARDE, JAN JUC VIC 3228 |  |  |  |  | Overheated connection |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that a pole-mounted three phase fuse mains box had overheated due to a loose connection, causing hot embers to drop to the ground and resulting in a ground fire (Approx. 100 sqm) on road reserve. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 26/12/2015 0:15 | 1 | Small: 10 - 1000 sq.m | 485 | Roadway |  | 20151230PWA_10 | Infrastructure (network-based) | -38.356 | 144.283 | 1 | Powercor | Report | 1174 | 0.035642 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
Crew isolated supply and undertook repairs. | 3564 MURRAY VALLEY HIGHWAY, WOOD WOOD VIC 3596 |  |  |  |  | Overheated connection |  |  | 0 | Customer reported loss of supply and a fire at the incident location. On arrival the crew found that a LV connection on a LV pole had overheated, causing hot particles to fall to the ground and resulting in a ground fire (Approx. 12 sqm) on private property. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated low voltage connection | Grassfire | 25/12/2015 0:10 | 1 | Small: 10 - 1000 sq.m | 486 | Roadway |  | 20151230PWA_11 | Infrastructure (network-based) | -35.0696 | 143.3385 | 1 | Powercor | Report | 1095 | 0.011997 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3564 | Wood Wood | Connection
Crew isolated supply and undertook repairs. | 170 PITFIELD-SCARSDALE ROAD, NEWTOWN VIC 3351 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, which burnt the crossarm strap and caused the crossarm to break, however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire. | Pole-top fire | 26/12/2015 4:29 | 1 | Negligible: no ground fire | 474 | Roadway |  | 20151230PWA_3 | Infrastructure (network-based) | -37.6837 | 143.655 | 1 | Powercor | Report | 1171 | 0.022735 | 22kV AC | Ballarat Aerodrome | 3351 | Newtown | Crossarm
Crew isolated supply and undertook repairs. | 32 PARK STREET, DIMBOOLA VIC 3414 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break, however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire. | Pole-top fire | 26/12/2015 3:31 | 1 | Negligible: no ground fire | 475 | Roadway |  | 20151230PWA_4 | Infrastructure (network-based) | -36.4595 | 142.0361 | 1 | Powercor | Report | 1172 | 0.03549 | 22kV AC | Horsham Aerodrome | 3414 | Dimboola | Crossarm
Crew isolated supply and undertook repairs. | FERNLEA, 1004 PATYAH ROAD, PATYAH VIC 3318 |  |  | Lightning |  |  |  |  | 1 | A fault crew attending an outage found that a lightning strike had occurred on a 22kV pole at the incident location, resulting in a ground fire (approx. 20m x 40m) on private property. Protection operated. There were no reported injuries. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Lightning strike. | Grassfire | 26/12/2015 14:50 | 1 | Small: 10 - 1000 sq.m | 477 | Agricultural |  | 20151230PWA_5 | Infrastructure (network-based) | -36.9261 | 141.2322 | 1 | Powercor | Report | 1149 | 0.0080891 | 22kV AC | Horsham Aerodrome | 3318 | Patyah | Lightning
Crew isolated supply and undertook repairs. | 11 FREIGHT TERMINAL ROAD, DOOEN VIC 3401 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 0 | A passerby reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV/lv pole which caused the crossarm to break, however the conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire. | Pole-top fire | 26/12/2015 16:25 | 1 | Negligible: no ground fire | 478 | Agricultural |  | 20151230PWA_6 | Infrastructure (network-based) | -36.64 | 142.2598 | 1 | Powercor | Report | 1142 | 0.018478 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3401 | Dooen | Crossarm
Crew isolated supply and undertook repairs. | 92 CARRINGTON STREET, MACEDON VIC 3440 |  |  |  |  | Unknown technical factor |  |  | 2 | A public lighting fault crew attending an outage found that a fire had occurred on a low voltage lantern causing hot debris to fall to the ground and resulting in a ground fire (Approx. 1m x 1m) on the road reserve. There were no reported injuries. | Public lighting | 0 | 0 | 0 |  |  | The cause of the fire is unable to be determined. | Pole-top fire | 24/12/2015 8:00 | 1 | Localised: less than 10 sq.m | 490 | Roadway |  | 20151231PWA_4 | Infrastructure (network-based) | -37.4196 | 144.5682 | 1 | Powercor | Report | 1092 | 0.016741 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | AF Other
Crew isolated supply and undertook repairs. | 5610 PRINCES HIGHWAY, BOORCAN VIC 3265 |  |  |  |  | Mechanical breakdown;Unknown technical factor |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that the crossarm on a 66kV pole had broken and fallen to ground. This resulted in a ground fire (Approx.150m x 50m) on road reserve and private property. Protection operated. CFA attended and extinguished the fire. There was minor damage reported to farm fencing. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Broken crossarm which had fallen to the ground. | Grassfire | 24/12/2015 13:57 | 1 | Medium: 1000 sq.m - 10 ha | 491 | Roadway |  | 20151231PWA_5 | Infrastructure (network-based) | -38.2154 | 143.0206 | 1 | Powercor | Report | 1089 | 0.032556 | 66kV AC | Warrnambool Airport Ndb | 3265 | Boorcan | Crossarm
Crew isolated supply and undertook repairs. | 55 CUMMINGS ROAD, MADDINGLEY VIC 3340 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 0 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV/lv pole which burnt the top of the pole. There was no ground fire. There were no reported injuries or third party property damage. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 26/12/2015 7:52 | 1 | Negligible: no ground fire | 492 | Roadway |  | 20151231PWA_6 | Infrastructure (network-based) | -37.6993 | 144.4511 | 1 | Powercor | Report | 1151 | 0.010265 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3340 | Maddingley | Pole
Crew isolated supply and undertook repairs. | 382 CASTLES ROAD, KOYUGA VIC 3622 |  |  |  |  | Overheated connection |  |  | 1 | Customer reported a fire on a pole at the incident location. On arrival, the crew found that a connection in a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. Protection operated. There was no ground fire. There were no reported injuries or third party property damage. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Pole-top fire | 25/12/2015 11:40 | 1 | Negligible: no ground fire | 493 | Roadway |  | 20151231PWA_7 | Infrastructure (network-based) | -36.2648 | 144.9046 | 1 | Powercor | Report | 1094 | 0.032243 | Low voltage AC (<1kV) | Shepparton Airport | 3622 | Koyuga | Connection
CEOT dispatched a fault crew to isolate and make safe. Crew replaced the service cable and restored supply. | 24 JOHN STREET, PAKENHAM VIC 3810 | 500547 |  |  |  | Age;Corrosion |  | Phase to earth | 2 | IMS 219848. Neutral screen service cable failed at POA and a small fire was found on the front lawn. Approximately fire size was 4m x 5m grass fire. | Service conductor | 0 | 0 | 0 |  | phm11 | Failed overhead neutral screen service cable. | Grassfire | 31/12/2015 16:00 | 1 | Small: 10 - 1000 sq.m | 499 | Residential |  | 20160103SPN_5 | Infrastructure (network-based) | -38.0743 | 145.485 | 1 | AusNet Services Distribution | Report | 756 | 0.028175 | Low voltage AC (<1kV) | Moorabbin Airport | 3810 | Pakenham | OH Cable
CEOT dispatched fault crew to isolate supply, make safe and investigate. Transformer was found to be faulty and was replaced with a 100kVA 3 phase TX. All EDO fuse tubes replaced. Supply restored. | 58 HARBOUR LINE DRIVE, GOUGHS BAY VIC 3723 | 39 18391 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 219851. Report of pole fire but when crew arrived, the centre phase fuse had candled and burnt out. No fire was present at arrival. Burnt out fuse found at Lake Valley Drive 19 Substation. No ground fire. Transformer found unserviceable. | EDO fuse;Pole mounted | 0 | 0 | 0 |  | msd1 | Substation transformer failure and associated EDO fuse tube candled. | Other electricity related | 42370.7917 | 1 | Negligible: no ground fire | 500 | Residential |  | 20160103SPN_6 | Infrastructure (network-based) | -37.1807 | 146.0747 | 1 | AusNet Services Distribution | Report | 758 | 0.041557 | 22kV AC | Wangaratta Aero | 3723 | Goughs Bay | Fuse
Crew isolated supply and undertook repairs | 290 HIGH STREET, SHEPPARTON VIC 3630 |  |  |  |  | Unknown technical factor |  |  | 2 | Vic Fire reported a fire in a street light at the incident location. On arrival the crew found that a fire had started in a street lighting lantern. The cause of the street light fire was unable to be determined. There was no ground fire. There were no reported injuries or third party property damages. | Public lighting | 0 | 0 | 0 |  |  | Unable to be determined | Plant/equipment | 24/12/2015 5:57 | 1 | Negligible: no ground fire | 518 | Roadway |  | 20160104PWA_5 | Infrastructure (network-based) | -36.3827 | 145.4097 | 1 | Powercor | Report | 783 | 0.022797 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | AF Other
Crew isolated supply and undertook repairs | 99 WINDY RIDGE ROAD, ROSEBERY VIC 3395 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the pole causing the top of the pole to burn. There was no ground fire. Protection operated. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 20/12/2015 21:10 | 1 | Negligible: no ground fire | 520 | Roadway |  | 20160104PWA_6 | Infrastructure (network-based) | -35.8342 | 142.4215 | 1 | Powercor | Report | 785 | 0.025189 | 22kV AC | Horsham Aerodrome | 3395 | Rosebery | Pole
Crew isolated supply and undertook repairs | 60 POINT ROAD, WHARPARILLA VIC 3564 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A nearby customer reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole causing the HV cross arm to burn through and break, resulting in a ground fire (Approx. 50 sqm) on the road reserve. The conductors remained aloft. Protection operated. There were no reported injuries. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 31/12/2015 14:33 | 1 | Small: 10 - 1000 sq.m | 522 | Roadway |  | 20160104PWA_8 | Infrastructure (network-based) | -36.0792 | 144.6211 | 1 | Powercor | Report | 788 | 0.010167 | 22kV AC | Bendigo Airport | 3564 | Wharparilla | Pole
Crew isolated supply and undertook repairs | 124 TORGANNAH ROAD, KOONOOMOO VIC 3644 |  |  | Bird |  |  |  |  | 1 | A nearby customer reported that a bird had hit a power line and a fire had started at the incident location. On arrival the crew found that a crow had contacted 22kV substation apparatus and fell to the ground resulting in a grass fire (Approx. 1m x 4m) on private property. There were no reported injuries. | Equipment | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 42370.4576 | 1 | Localised: less than 10 sq.m | 534 | Agricultural |  | 20160105PWA_5 | Infrastructure (network-based) | -35.8722 | 145.5774 | 1 | Powercor | Report | 811 | 0.0052604 | 22kV AC | Shepparton Airport | 3644 | Koonoomoo | Animal
Crew replaced fuse | 13 AVENUE OF HONOUR, WOODEND VIC 3442 |  |  |  |  | Mechanical breakdown |  |  | 2 | A field crew attending an outage found that a 22kV Powder filled fuse had broken and had fallen to the ground resulting in a ground fire (Approx. 4 Ha) predominantly on private property. There were no reported injuries. | Powder filled | 0 | 0 | 0 |  |  | Broken PF fuse | Grassfire | 42370.6104 | 1 | Medium: 1000 sq.m - 10 ha | 535 | Agricultural |  | 20160105PWA_6 | Infrastructure (network-based) | -37.3451 | 144.5331 | 1 | Powercor | Report | 813 | 0.012392 | 22kV AC | Wallan (Kilmore Gap) | 3442 | Woodend | Fuse
Crew isolated supply and undertook repairs | 385 DRUMANURE ROAD, INVERGORDON VIC 3636 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | CFA reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV/LV substation pole which burnt the crossarm at the king bolt. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42401.8875 | 1 | Negligible: no ground fire | 561 | Roadway |  | 20160107PWA_19 | Infrastructure (network-based) | -36.1308 | 145.572 | 1 | Powercor | Report | 846 | 0.024999 | 22kV AC | Shepparton Airport | 3636 | Invergordon | Crossarm
A LEI and faults truck attended and completed tests on the electrical installation and measured 12v to the metallic water piping system to an independent earth with load applied. With no load applied, 2v was measured that indicated to the LEI the overhead neutral reticulation conductor may be undersized with the premise located at the end of the street circuit. The faults crew proceeded to check all service connections and neutral terminations / connections on poles back to the distribution transformer and no faults were identified. The LEI advised the Resource Coordinator to arrange for follow up action to investigate further. The LEI added an extra neutral / earth lead that doubled the original set up. | 3 OLIVE STREET, BLAIRGOWRIE VIC 3942 | LIS No. 883202 |  |  |  | Neutral fault |  | Phase to earth | 2 | The caller reports that all of the family are receiving tingles from the water taps at various times during the past 10 years. The family have been receiving very slight electric shocks from the metallic water pipes and single insulated appliances and contacted United Energy to investigate the cause. | No failed asset | 0 | 0 | 0 |  |  | Possible undersized reticulation neutral conductor - Under investigation. | Minor shock | 42461.375 |  |  | 559 | Residential |  | 20160107UTD_2 | Infrastructure (network-based) | -38.3592 | 144.7699 | 1 | United Energy Distribution | Report | 843 | 0.035159 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | OH Cable
Crew isolated supply and undertook repairs | 515 O'CONNORS ROAD, WERRIBEE SOUTH VIC 3030 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A customer reported a fire at the above location. On arrival the crew found that a pole fire had occurred on a 22kV pole, resulting in the pole top being burnt. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42583.659 | 1 | Negligible: no ground fire | 566 | Roadway |  | 20160108PWA_5 | Infrastructure (network-based) | -37.9614 | 144.6957 | 1 | Powercor | Report | 853 | 0.036215 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Pole
Crew isolated supply and undertook repairs | 4 HUNT DRIVE, ROBINVALE VIC 3549 |  |  | Bird |  |  |  |  | 1 | A Customerâ€™s REC reported a fire at the incident location. On arrival the crew found that a LV service cable had been damaged by birds causing the cable to short out between phases resulting in a ground fire (Approx. 5 m x 10m) in the road easement. Protection operated. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 42614.4125 | 1 | Small: 10 - 1000 sq.m | 570 | Roadway |  | 20160111PWA_1 | Infrastructure (network-based) | -34.5985 | 142.7637 | 1 | Powercor | Report | 860 | 0.011247 | Low voltage AC (<1kV) | Mildura Airport | 3549 | Robinvale | Animal
Crew isolated supply and undertook repairs | 54 CORIO QUAY ROAD, NORTH GEELONG VIC 3215 |  |  | Bird |  | Electrical overload |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a nearby open point switch pole, the resultant fault current caused a 22kV High Voltage conductor to break near a helical termination and fall to the ground resulting in a ground fire (approx. 8m x 50m) on road/rail reserve. The cause of the conductor breaking is under investigation. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Fault current for nearby fault caused conductor to break | Grassfire | 42644.7451 | 1 | Small: 10 - 1000 sq.m | 576 | Roadway |  | 20160111PWA_6 | Infrastructure (network-based) | -38.1085 | 144.3566 | 1 | Powercor | Report | 2714 | 0.039649 | 22kV AC | Avalon Airport | 3215 | North Geelong | Animal
Crew isolated supply and undertook repairs | 169/171 VICTORIA ROAD, NORTHCOTE VIC 3070 |  | Vehicle | [5 empty] | 2 | A contractor reported that they had contacted and broken overhead wires at the incident location. On arrival the crew found that a contractor (Matthew from Asphaltech, Ph: 0458 316 071) was moving portable lighting equipment mounted on a trailer (the lights had not been lowered), resulting in the lights contacting two LV service cables which broke away from their point of attachment at the house end and fell to the ground across the footpath. There were no reported injuries. There was no ground fire. | Service conductor | 0 | 0 | 0 |  |  | Contractor contacted LV services with lighting tower | No Go Zone (contact);Damage to network assets | 42644.4931 |  |  | 577 | Roadway |  | 20160111PWA_7 | Infrastructure (network-based) | -37.7691 | 145.0118 | 1 | CitiPower | Report | 954 | 0.034088 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
Emergency high voltage switching was completed and 4 bays of HVABC was replaced under Access Authority conditions on 07/10/2015. | 54 SHEEHANS ROAD, RED HILL VIC 3937 |  |  | Wind;Heat |  | Electrical breakdown |  |  | 1 | At 0602hrs on 06/10/2015, 22kV feeder DMA 13 circuit breaker reclosed to lockout affecting 2758 customers. A faults crew was sent to Sheehans Road on the corner of Arthurs Seat Road following the CFA calling to advise of a grass fire and HV conductors down. During strong northerly winds, 22kV feeder DMA 13 reclosed to lockout. The cause was 185mm HVABC failing midspan outside 60 Sheehans Road, Red Hill. This resulted in the 22kV conductor to fall to the ground and a small grass fire of approximately 40-50 square metres started next to the road reserve caused by molten aluminium contacting the dry grass and scrub land. The CFA responded quickly and extinguished the fire. No high voltage injection or major damage was sustained. | Conductor (ABC);Aluminium | 0 | 0 | 0 |  | DMA 13 | Under investigation. | Loss of supply;Grassfire | 42165.3049 |  | Small: 10 - 1000 sq.m | 54 | Roadway |  | 20151009UTD_1 | Infrastructure (network-based) | -38.3638 | 145.0059 | 1 | United Energy Distribution | Report | 68 | 0.009228 | 22kV AC | Moorabbin Airport | 3937 | Red Hill | Conductor
Crew isolated supply and undertook repairs | 163 FOX STREET, ST ALBANS VIC 3021 |  |  | Wind |  |  |  |  | 1 | A customer reported a power line sparking and grass fire at the above location. On arrival the crew found that a tree branch from a nearby tree had broken in strong winds and had fallen across adjacent LV conductors resulting in a ground fire (Approx 2 sqm) on the nature strip, which self extinguished. The tree is in the road reserve in a declared area. Protection operated. There were no reported injuries. | No failed asset | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 42165.5764 | 1 | Localised: less than 10 sq.m | 61 | Roadway |  | 20151012PWA_2 | Infrastructure (network-based) | -37.732 | 144.7956 | 1 | Powercor | Report | 280 | 0.0072546 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Trees
Field Officer undertook discussion with Customer who offered the excuse regarding time for CitiPower to undertake protective works. | 77 YORK STREET, RICHMOND VIC 3121 |  | Unauthorised work | [5 empty] | 2 | A shutdown was arranged for the erection of scaffold. The customer-Mathew Thong (CDM Building Group Ph: 0423 761 351, mathew.thong@bigpond.com) emailed CitiPower to arrange a return shutdown for the dismantle which was programmed. The customer requested more time so the job was rescheduled for 7/10/15. On passing the site the CitiPower Field Officer noticed the scaffold had been removed prior to our arranged shutdown. On discussion with the customer by phone regarding the above observation, the customer stated that he thought the shutdown was for the removal of the warning battens. All documentation clearly states shutdowns x (2) required and these were duly signed & it was made clear through emails regarding the reasons for the shutdowns. Field Officer undertook discussion with Customer who offered the excuse regarding time for CitiPower to undertake protective works. | Conductor (bare) | 0 | 0 | 0 |  |  | Customer did not wait for the agreed date of the shutdown to undertake work as per signed documentation. | No Go Zone (no contact) | 42134.5 |  |  | 71 |  |  | 20151015PWA_2 | Infrastructure (network-based) | -37.813 | 144.9943 | 1 | CitiPower | Report | 90 | 0.032461 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Crew isolated supply | 53 ELM AVENUE, KOORLONG VIC 3501 |  | Crane, excavator or other construction/farming equipment | [6 empty] | An REC reported that a service line had been pulled down by a sprayer at the above location. On arrival the crew found that an unknown vehicle had contacted a LV service cable, breaking the cable causing it to fall to the ground, also causing damage to the POA. The vehicle was not on site when the crew arrived. The REC stated that the customer did not want supply restored to the abandoned house. As the service was not reinstated no heights are recorded.. There was no ground fire. There were no reported injuries or other third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service | No Go Zone (contact);Damage to network assets | 42257.4375 |  |  | 81 |  |  | 20151016PWA_3 | Infrastructure (network-based) | -34.2407 | 142.0504 | 1 | Powercor | Report | 105 | 0.014628 | Low voltage AC (<1kV) | Mildura Airport | 3501 | Koorlong | Vehicle
Crew isolated supply for REC to undertake repairs | 42 FLOYDS ROAD, SCOTTS CREEK VIC 3267 |  |  | Animal | [5 empty] | A customer reported a fire at their switchboard at the above location. Ln arrival the crew found that rabbits had chewed through the customers cables resulting in a fire at the customers switchboard. There was no ground fire. There were no reported injuries. | No failed asset | 0 | 0 | 0 |  |  | Rabbits chewing customers mains | Meter board | 42287.7083 |  | Negligible: no ground fire | 88 |  |  | 20151020PWA_2 | Infrastructure (network-based) | -38.4075 | 143.0819 | 1 | Powercor | Report | 115 | 0.032456 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3267 | Scotts Creek | Animal
A faults truck attended and inspected concrete pole No. LIS 1105192 that had a small scorch mark on it following a private tree branch contacting it and a HV conductor that caused the tree branch to catch fire. There was no fire when the faults crew attended and the private tree was previously cut to code with adequate clearance. | 60 DANDENONG-HASTINGS ROAD, SOMERVILLE VIC 3912 | 1105192 |  | Wind |  |  |  |  | 1 | At 7.12PM on 11/10/2015, 22kV feeder HGS33 circuit breaker successfully reclosed and held. A customer who resides at 60 Dandenong-Hastings Road, Somerville heard a load bang and the lights flickered and they noticed a tree branch had caught fire outside the property. The small grass fire below "Dnong Hgs P196-Bngwr" substation was extinguished by the resident after the tree branch fell into the dry grass. | Conductor (bare) | 0 | 0 | 0 |  | HGS 33 | Vegetation: Trees Incident | Grassfire | 42318.3097 |  | Localised: less than 10 sq.m | 98 | Residential |  | 20151021UTD_1 | Infrastructure (network-based) | -38.2409 | 145.2136 | 1 | United Energy Distribution | Report | 127 | 0.024133 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Trees
A Downer-Tenix faults truck attended and measured slightly high volts as follows: Red phase - 256v White phase - 257v Blue phase - 257v. The faults crew arranged for a after hours transformer tap change at "Safeway-Willis" substation to lower the voltage. This planned work has been arranged to be completed on 17/10/2015. The LEI arrived and tested the electrical installation and no evidence of electric shocks being received was identified and the initial call was for high volts only. | 2 WILLIS LANE, HAMPTON VIC 3188 |  |  |  |  | Electrical overload |  | Phase to earth | 2 | Caller (Jacqui - Trident Body Corporate) reports there is a voltage irregularity and residents have mentioned that electric shocks have been received. Lift workers identified a high voltage was affecting the lifts and residents have received slight electric shocks from various parts of the installation. | No failed asset | 0 | 0 | 0 |  |  | A voltage irregularity was affecting the lifts - no electric shocks were received. | Minor shock | 16/10/2015 10:30 |  |  | 100 | Residential |  | 20151021UTD_3 | Infrastructure (network-based) | -37.9376 | 145.0018 | 2 | United Energy Distribution | Report | 139 | 0.0052593 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton | AF Other
Replaced Fuse Tube and restored supply. A work order has been raised to replace the EDO fuse with BA fuse. These types of fuses are no longer being installed on new construction and a program is in place to replace the EDO type models with BA fuses or Fault Tamer types. | 165 NEWELL ROAD, LONGWARRY VIC 3816 | 2709781 |  |  |  | Insulator |  |  | 2 | IMS218554. EDO fuse candled at WL278 #2709781. No fire caused. | EDO fuse | 0 | 0 | 0 |  | wgl21 | Fuse candled at WL278 #2709781. | Pole-top fire | 42226 |  | Negligible: no ground fire | 107 | Agricultural |  | 20151022SPN_1 | Infrastructure (network-based) | -38.0875 | 145.7649 | 1 | AusNet Services Distribution | Report | 142 | 0.018757 | 22kV AC | Moorabbin Airport | 3816 | Longwarry | Fuse
Crew isolated supply | 264 BALLAN-GREENDALE ROAD, BALLAN VIC 3342 |  |  |  |  | Fault on customer installation |  |  | 1 | Vicfire reported a transformer on fire at the above location. On arrival the crew found that the steel pole supporting a temporary builders supply meter box had leant over causing the customers underground cable to short out against the base of the steel pole resulting in a ground fire (approx. 0.3m x 0.3m) on the customers property. Protection operated. There were no reported injuries. | Cable;Customer installation | 0 | 0 | 0 |  |  | Customers underground mains short circuited | Grassfire | 25/10/2015 21:19 |  | Localised: less than 10 sq.m | 120 |  |  | 20151027PWA_1 | Infrastructure (network-based) | -37.5799 | 144.2392 | 1 | Powercor | Report | 161 | 0.033163 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Other
Crew checked cables for damage - none found, and arranged repairs | 29A SUNLINE DRIVE, TRUGANINA VIC 3029 |  | Vehicle |  | Unlikely |  |  |  |  | A Powercor employee reported a damaged LV pillar at the location. On arrival the crew found that damage had been sustained to a LV Pillar by an unknown vehicle. There were no exposed live cables. There was no ground fire. There were no reported injuries or third party property damages. | LV Pillar | 0 | 0 | 0 |  |  | Third party damaged Pillar | Damage to network assets | 23/10/2015 0:00 |  |  | 126 | Residential |  | 20151028PWA_2 | Infrastructure (network-based) | -37.806 | 144.7468 | 1 | Powercor | Report | 269 | 0.011926 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Vehicle
Dispatched Fault Crew and Duty Officer to isolate supply, make safe and investigate. The tree was removed and the conductors re-erected, tested and energized. A request has been made to the local Field Team Manager at Seymour to send a warning letter to the customer regarding the hazards involved in cutting trees in the vicinity of overhead power lines. | 15 SHELTON STREET, AVENEL VIC 3664 | 4708865 | Unauthorised work | Within clearances |  |  |  | Phase to earth | 1 | 218752. CFA report wire down and fire near wire. On the 23rd of October, the customer Ray Hill of 15 Shelton Street, Avenal, was cutting down trees on his private property. One of the trees between poles 4708865 and 5768876 (poles on the road reserve), struck the LV copper conductors and bought down two phases, (White and Blue). 2 x LV HRC fuses operated. This incident started a grass fire of approximately 30m x 30m in size. The fire was extinguished by the CFA on site. No injuries to any persons. | Conductor (bare) | 0 | 0 | 0 |  | smr8 | Vegetation: Trees Incident | Grassfire | 23/10/2015 13:30 |  | Small: 10 - 1000 sq.m | 134 | Residential |  | 20151029SPN_3 | Infrastructure (network-based) | -36.8994 | 145.2316 | 1 | AusNet Services Distribution | Report | 190 | 0.017362 | Low voltage AC (<1kV) | Mangalore Airport | 3664 | Avenel | Trees
A faults truck attended and removed the grey overhead twisted service that was laying down alive. The consumers FMJB was damaged and the faults crew issued a defect notice to the occupier advising that repairs are required prior to supply being restored. | 49 ST JOHNS AVENUE, SPRINGVALE VIC 3171 |  | Working too close to overhead lines | [5 empty] | 2 | Caller Fernando (0414 849 280) reported that he has hit the overhead service line with an excavator and ripped it from the house. An excavator operator contacted the single phase grey twisted overhead service supplying 49 St Johns Avenue, Springvale and brought it down from the POA that was damaged and requires repairs. No shocks or injuries were sustained. Building Practitioner Contact: Peter Tran ph: 0403 117 579 Builder Registration: DBU-28338 Building Permit #: 20150201/0 | Service conductor;Aluminium;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | An excavator operator contacted the single phase grey twisted overhead service supplying 49 St Johns Avenue, Springvale. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/10/2015 12:15 |  |  | 129 | Residential |  | 20151029UTD_1 | Infrastructure (network-based) | -37.9554 | 145.1487 | 1 | United Energy Distribution | Report | 182 | 0.023792 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Vehicle
Site made safe | 37-41 COOPER STREET, CAMPBELLFIELD VIC 3061 |  |  |  |  | Rot |  |  | 1 | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Broken X-arm | Pole-top fire;HV injection | 26/10/2015 16:51 |  | Negligible: no ground fire | 155 | Residential |  | 20151030JEM_2 | Infrastructure (network-based) | -37.6472 | 144.9733 | 1 | Jemena | Report | 217 | 0.039251 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Crossarm
Crew Isolated supply and undertook repairs | 27 HELLER STREET, BRUNSWICK VIC 3056 |  |  |  | Unlikely | Leakage |  |  | 2 | VicFire reported a fire at the above location. On arrival the crew found that a crossarm fire had occurred on a 66kV pole which burnt the crossarm only and the crossarm remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/10/2015 20:00 | 1 | Negligible: no ground fire | 147 | Roadway |  | 20151030PWA_11 | Infrastructure (network-based) | -37.775 | 144.9498 | 1 | CitiPower | Report | 260 | 0.0086817 | 66kV AC | Essendon Airport | 3056 | Brunswick | Crossarm
Crew secured site and arranged repairs | 93 CAPESTHORNE DRIVE, DERRIMUT VIC 3030 |  | Vandalism;Theft |  | Unlikely |  |  |  | 1 | A Powercor employee reported a copper theft at the location. The employee found that a Kiosk Substation had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 29/10/2015 0:00 |  |  | 149 | Residential |  | 20151030PWA_13 | Infrastructure (network-based) | -37.7927 | 144.761 | 1 | Powercor | Report | 255 | 0.018021 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
Crew secured site and arrange repairs | 54 WESTMINSTER PARKWAY, DERRIMUT VIC 3030 |  | Theft |  | Unlikely |  |  |  | 2 | A Powercor employee reported a copper theft at the location. On arrival the crew found that several Kiosk Substations in the area had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 26/10/2015 19:13 |  |  | 139 | Public space |  | 20151030PWA_3 | Infrastructure (network-based) | -37.7856 | 144.7573 | 1 | Powercor | Report | 261 | 0.034727 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
Crew secured site and arrange repairs | 16 HOLMEWOOD AVENUE, DEER PARK VIC 3023 |  | Theft |  | Unlikely |  |  |  | 2 | A Powercor employee reported a copper theft at the location. On arrival the crew found that several Kiosk Substations in the area had been broken into and copper earthing stolen by unknown third parties. There were no reported injuries or third party property damages. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 26/10/2015 19:13 |  |  | 143 | Public space |  | 20151030PWA_7 | Infrastructure (network-based) | -37.7785 | 144.7576 | 1 | Powercor | Report | 265 | 0.0029838 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
Crew made site safe and arranged repairs | 15 EDEN CRESCENT, HOPETOUN PARK VIC 3340 |  | Vehicle |  | Unlikely |  |  |  | 2 | A Powercor employee reported a damaged LV U/G pit at the location. On arrival the crew found that a LV UG pit had been damaged by an unknown vehicle. There were no reported injuries or third party property damages. Address 15 Eden Cres, Hopetoun Park | Services pit | 0 | 0 | 0 |  |  | Damaged by unknown third parties | Damage to network assets | 28/10/2015 8:37 |  |  | 145 | Roadway |  | 20151030PWA_9 | Infrastructure (network-based) | -37.6976 | 144.506 | 1 | Powercor | Report | 258 | 0.014299 | Low voltage AC (<1kV) | Laverton Raaf | 3340 | Hopetoun Park | Vehicle
Site made safe | 54 SHAFTSBURY STREET, COBURG VIC 3058 |  | Working too close to overhead lines | [5 empty] | 1 | Plumber installing guttering from scaffolding made contact with â€˜liveâ€™ 22kV overhead conductors | Conductor (bare) | 0 | 0 | 0 |  |  | Plumber installing guttering from scaffolding made contact with â€˜liveâ€™ 22Kv overhead conductors | Medical attention (first aid/doctor/hospital) | 28/10/2015 9:40 |  |  | 169 | Construction |  | 20151102JEM_1 | Infrastructure (network-based) | -37.7501 | 144.9551 | 1 | Jemena | Report | 245 | 0.027338 | 22kV AC | Essendon Airport | 3058 | Coburg | Other
Crew isolated supply and undertook repairs | 625 WIRIDGIL LANE, WEERITE VIC 3260 |  |  |  | Unlikely | Unknown technical factor |  |  | 1 | CFA reported a fire on a pole at the above location. On arrival the crew found that a 22kV conductor had broken at a line splice and had fallen to the ground resulting in a ground fire (Approx. 20m x 2m) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare);Steel | 0 | 0 | 0 |  |  | Broken 22kV conductor | Grassfire | 42046.8389 | 1 | Small: 10 - 1000 sq.m | 178 | Agricultural |  | 20151104PWA_1 | Infrastructure (network-based) | -38.2259 | 143.2303 | 1 | Powercor | Report | 271 | 0.017164 | 22kV AC | Warrnambool Airport Ndb | 3260 | Weerite | Conductor
Crew undertook repairs | 33 GRANT STREET, CLIFTON HILL VIC 3068 |  | Working too close to underground cables | [6 empty] | A site developer reported that contractors have excavated near the footpath and have exposed an electrical cable at the incident location. On arrival the crew found that a contractor (Contact: David Rodden, 3 Parkville Place, Templestowe, 3106. Ph: 0418 121 724) had undertaken excavation works and had exposed the earth conductor which connected to the catenary wire of a high voltage ABC cable. One of the earthing connections was also found severed. There were no reported injuries or third party property damages. The crew were not able to check of DBYD plans were onsite. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Contractor contacted earthing cables | No Go Zone (contact) | 30/10/2015 1:46 |  |  | 188 | Roadway |  | 20151106PWA_3 | Infrastructure (network-based) | -37.7882 | 144.9962 | 1 | CitiPower | Report | 290 | 0.015972 | Earthing cable | Essendon Airport | 3068 | Clifton Hill | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected. The HV tee-off crossarm was replaced under Access Authority conditions prior to supply being restored. | 2 BISHOP STREET, BOX HILL VIC 3128 | 7032424 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Caller reports crossarm on fire and high voltage lines are hanging from the pole. During light drizzly rain, a pole fire occurred at the 22kV tee-off crossarm on pole No. LIS 7032424 located outside 2 Bishop Street, Box Hill. The HV conductor stayed in the air and therefore no protection operated. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | DC 08 | Vegetation: Trees Incident | Pole-top fire | 27/10/2015 0:10 |  | Negligible: no ground fire | 184 | Roadway |  | 20151106UTD_1 | Infrastructure (network-based) | -37.8201 | 145.1301 | 1 | United Energy Distribution | Report | 286 | 0.0025521 | 22kV AC | Moorabbin Airport | 3128 | Box Hill | Crossarm
Initial CEOT report: Crew isolated substation. XLPE HV dropper and LA to be fixed. Further details: Construction crew replaced LA and XLPE dropper. They also arranged the LAs so there was the correct clearance from the XLPE dropper leads and restored supply to customers. | 51-53 ALBERT STREET, MOE VIC 3825 | 2205825 |  |  |  | Electrical breakdown |  | Phase to earth | 1 | Initial CEOT report: LA on fire, burnt onto HV dropper, no ground fire, no one hurt. Further details: Fault crew called to dim lights and pole fire fault. Crew found LA and XLPE dropper on fire on arrival so they isolated the substation. On further inspection it was found that the LAs were mounted closely to the XLPE droppers and the top section of the LA had actually rubbed through on the earthed section on the XLPE dropper lead. | Surge diverter | 0 | 0 | 0 |  | moe31 | The LAs were mounted closely to the XLPE droppers and the top section of the LA had actually rubbed through on the earthed section on the XLPE dropper lead. | Pole-top fire | 42135 |  | Negligible: no ground fire | 203 | Roadway |  | 20151111SPN_1 | Infrastructure (network-based) | -38.1749 | 146.2643 | 1 | AusNet Services Distribution | Report | 312 | 0.011977 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Moe | AF Other
Emergency high voltage switching was completed and the damaged HVABC was repaired under Access Authority conditions. | 4 WHITES ROAD, ARTHURS SEAT VIC 3936 | 1309132 |  |  |  | Fatigue;Defective component |  |  | 1 | At 1604hrs on 09/11/2015, ACR RB7227 located in Arthurs Seat Road on 22kV feeder DMA 13, reclosed to lockout affecting 198 customers. ACR RB 7227 located in Arthurs Street Road reclosed to lockout. The cause was 185mm HVABC failing midspan on the corner of Main Creek and Whites Roads between pole No's LIS 1309132 and 1309133. A grass fire of approximately 200 sqm started next to the road reserve caused by molten aluminium contacting the dry grass below. The Main Ridge CFA responded quickly and extinguished the fire. No high voltage injection or major damage was sustained. | Conductor (ABC) | 0 | 0 | 0 |  | DMA 13 | 185mm HVABC failing midspan on the corner of Main Creek and Whites Roads between pole No's LIS 1309132 and 1309133 | Grassfire | 42319 |  | Small: 10 - 1000 sq.m | 202 | Roadway |  | 20151111UTD_2 | Infrastructure (network-based) | -38.342 | 144.9587 | 1 | United Energy Distribution | Report | 310 | 0.015035 | 22kV AC | Moorabbin Airport | 3936 | Arthurs Seat | OH Cable
Crew attended and isolated supply. The broken 3/2.75 steel SWER conductor was joined & re-strung the same day. | 156 MOUNT JOY ROAD, TATONG VIC 3673 | 3909122 | Working too close to overhead lines | Within clearances |  |  |  | Phase to earth | 1 | Initial CEOT report: BN 059 off supply and a report of a wire down caused by a bulldozer. Investigation details: Fault crew attended and isolated supply and found 500 metres of HV conductor down caused by a bulldozer felling a pine tree for a fire track (allegedly). ESV notified. The bulldozer driver was: Luke Bell, 1 Old Mill Rd, Mansfield, telephone 0425 758054. | SWER conductor | 0 | 0 | 0 |  | bn6 | Vegetation: Trees Incident | Damage to network assets | 42319 |  |  | 206 | Agricultural |  | 20151112SPN_3 | Infrastructure (network-based) | -36.7737 | 146.1109 | 1 | AusNet Services Distribution | Report | 319 | 0.029667 | 12.7kV AC (SWER) | Wangaratta Aero | 3673 | Tatong | Vehicle
Crew isolated supply and undertook repairs | 5544 DONALD-SWAN HILL ROAD, SWAN HILL VIC 3585 |  |  |  |  | Leakage |  |  | 2 | A field crew attending an outage found that a crossarm fire had occurred on a 22kV pole which caused the crossarm causing the arm to break however the conductors remained clear of the ground.. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 31/10/2015 8:14 |  | Negligible: no ground fire | 218 | Roadway |  | 20151113PWA_12 | Infrastructure (network-based) | -35.3927 | 143.5595 | 1 | Powercor | Report | 331 | 0.011013 | 22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Crossarm
Crew isolated supply and undertook repairs | 471 IRYMPLE AVENUE, NICHOLS POINT VIC 3501 |  |  |  |  | Leakage |  |  | 1 | VicFire reported a pole fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the pole causing the cross arm to break at the king bolt and fall to the ground, Protection operated. There was no ground fire. There were no reported injuries. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42105.4201 |  | Negligible: no ground fire | 220 | Roadway |  | 20151113PWA_14 | Infrastructure (network-based) | -34.221 | 142.1978 | 1 | Powercor | Report | 333 | 0.017823 | 22kV AC | Mildura Airport | 3501 | Nichols Point | Pole
Crew isolated supply and undertook repairs | 164 CLARKES HILL ROAD, BULLAROOK VIC 3352 |  |  |  |  | Age |  |  | 1 | A customer reported arcing at the incident location. On arrival the crew found that a 3 wire overhead service to a dairy had arced through the insulation, dropping debris to the ground resulting in a ground fire (Less than 1sqm) on the road reserve, and minor damage to a wooden fence. Protection operated. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Insulation breakdown | Grassfire | 13/11/2015 8:24 |  | Localised: less than 10 sq.m | 227 | Roadway |  | 20151113PWA_21 | Infrastructure (network-based) | -37.5181 | 143.9933 | 1 | Powercor | Report | 342 | 0.038391 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Bullarook | Conductor
Crew isolated supply and undertook repairs | 161 WRIGHT STREET, SUNSHINE VIC 3020 |  |  |  |  | Leakage |  |  | 1 | MFB reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the pole and cross-arm causing the crossarm to break at the king bolt, resulting in conductor clashing, however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42046.5417 |  | Negligible: no ground fire | 209 | Roadway |  | 20151113PWA_3 | Infrastructure (network-based) | -37.7949 | 144.8195 | 1 | Powercor | Report | 322 | 0.0078032 | 22kV AC | Laverton Raaf | 3020 | Sunshine | Crossarm
Crew isolated supply and undertook repairs | 739 INGLEWOOD-KORONG VALE ROAD, KORONG VALE VIC 3520 |  |  |  |  | Leakage |  |  | 2 | A nearby customer reported a damaged insulator on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which burnt the crossarm causing the crossarm to break and the insulator and conductor to fall, coming to rest approx. 1m from the ground. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42046.7944 |  | Negligible: no ground fire | 211 | Agricultural |  | 20151113PWA_5 | Infrastructure (network-based) | -36.3969 | 143.6871 | 1 | Powercor | Report | 2812 | 0.030104 | 22kV AC | Bendigo Airport | 3520 | Korong Vale | Crossarm
Made safe | 1A ELPHINSTONE BOULEVARD, GREENVALE VIC 3059 |  | Vehicle | [5 empty] | 1 | Vehicle impacted pole causing pole to fall over resulting in HV conductors on the ground | Conductor (bare) | 0 | 0 | 0 |  |  | Vehicle | Loss of supply | 18/10/2015 0:00 |  |  | 235 | Peri-urban |  | 20151118JEM_3 | Infrastructure (network-based) | -37.6466 | 144.8801 | 1 | Jemena | Report | 359 | 0.011872 | 22kV AC | Melbourne Airport | 3059 | Greenvale | Vehicle
Made safe | 830 HIGH STREET, RESERVOIR VIC 3073 |  |  |  |  | Fatigue |  |  | 2 | LV connection failed | Conductor (bare) | 0 | 0 | 0 |  |  | LV connection failed | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42287 |  |  | 237 | Residential |  | 20151118JEM_5 | Infrastructure (network-based) | -37.7238 | 145.0067 | 1 | Jemena | Report | 2738 | 0.021738 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Connection
Repaired neutral connection up pole | 131-133 EVANS STREET, SUNBURY VIC 3429 |  |  |  |  | Neutral fault |  |  |  | Citywest water contractor received shock from water pipe | Services cable | 0 | 0 | 0 |  |  | Broken neutral connection - pole end | Minor shock | 19/11/2015 12:03 |  |  | 252 |  |  | 20151120JEM_1 | Infrastructure (network-based) | -37.5842 | 144.7264 | 1 | Jemena | Report | 376 | 0.022613 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Connection
Crew checked assets for damages - none found | 98 SAGO HILL ROAD, HADDON VIC 3352 |  |  | Lightning |  |  |  |  | 1 | Vic Fire reported a lightning strike and ground fire at the incident location. On arrival the crew found that protection had operated on the 22kV line, but no ground fire at this location. Further inspection during daylight hours found that a lightning strike had occurred on a 22kV/LV pole resulting in a ground fire (Approx. 35 sqm) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Lightning | Grassfire | 20/11/2015 0:46 |  | Small: 10 - 1000 sq.m | 258 | Roadway |  | 20151123PWA_2 | Infrastructure (network-based) | -37.5703 | 143.7423 | 1 | Powercor | Report | 384 | 0.040831 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3352 | Haddon | Lightning
A LEI and faults truck attended and completed a NST that failed. The faults crew proceeded to check all connections and identified a corroded neutral connection at the pole end. The neutral connection at pole No. LIS 1822299 was cleaned, greased and re-terminated. The LEI tested the installation that confirmed the fault had been rectified. | 30 SHORT STREET, HAMPTON EAST VIC 3188 | 1822299 |  |  |  | Corrosion |  | Phase to earth | 2 | REC No. 15288 (Matt) advised that a plumber received an electric shock earlier in the afternoon. A REC contacted the United Energy faults and emergencies number after he attended the premise today to investigate the cause of the plumber receiving a slight electric shock. The occupier had no issues with the supply but the REC has identified there is a neutral problem in the reticulation. The plumber was cutting through a water pipe at the time the shock was received. | Service conductor | 0 | 0 | 0 |  |  | A corroded neutral connection at the pole end. | Minor shock | 16/11/2015 19:00 |  |  | 262 | Residential |  | 20151124UTD_2 | Infrastructure (network-based) | -37.937 | 145.0247 | 1 | United Energy Distribution | Report | 390 | 0.0018611 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton East | Connection
Made safe | 500 MELTON HIGHWAY, SYDENHAM VIC 3037 | A059532 |  | Wind |  | Unknown technical factor |  |  | 1 | High voltage conductor on ground due to strong winds | Conductor (bare) | 0 | 0 | 0 |  | SHM21 | High winds | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/11/2015 18:19 |  |  | 277 | Public space |  | 20151127JEM_1 | Infrastructure (network-based) | -37.6945 | 144.768 | 1 | Jemena | Report | 528 | 0.032435 | 22kV AC | Melbourne Airport | 3037 | Sydenham | Conductor
Crew isolated supply and undertook repairs | 706 TENNYSON ROAD, TENNYSON VIC 3572 |  |  | Animal |  |  |  |  | 2 | CFA reported a fire due to pole fire at the incident location. On arrival the crew found that cross arm had broken and the conductor came to rest on an aerial stay wire resulting in a pole fire. The pole fire caused a ground fire (Approx. 1200 sqm) on private property and along the verge of a roadway. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Broken crossarm due to termite infestation | Grassfire | 25/11/2015 23:08 |  | Medium: 1000 sq.m - 10 ha | 284 | Roadway |  | 20151127PWA_10 | Infrastructure (network-based) | -36.3075 | 144.432 | 1 | Powercor | Report | 578 | 0.019281 | 22kV AC | Bendigo Airport | 3572 | Tennyson | Crossarm
Crew isolated supply and undertook repairs | 8 WATERSIDE WAY, MILDURA VIC 3500 |  | Working too close to underground cables | [5 empty] | 2 | A plumber reported a dug up cable at the incident location. On arrival the crew found that a plumber (Ross Mayne Plumbing 0411 030 896) was using an excavator to install storm water piping and contacted a LV underground service cable causing damage to the cable. The plumber made contact with the cable while inspecting it, resulting in him receiving an electric shock. There was no ground fire. There were no reported injuries or third party property damages. The plumber had not undertaken DBYD enquiries. | Services cable | 0 | 0 | 0 |  |  | Excavator contacted LV UG cable | Minor shock | 42349.5653 |  |  | 274 | Roadway |  | 20151127PWA_3 | Infrastructure (network-based) | -34.1852 | 142.1754 | 1 | Powercor | Report | 406 | 0.021 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Dug up
Crew isolated supply and undertook repairs | 8 AMOORE AVENUE, HIGHTON VIC 3216 |  | Vehicle | [5 empty] | 2 | A field crew attending an outage found that an LV service cable had been contacted by an unknown vehicle breaking the cable and stretching the insulation causing the cable to hang low (Approx. 1m) across a driveway. There was no vehicle on site when the crew arrived. There were no reported injuries or third party property damages. Following restoration the service height was measured at 3.2m above the driveway. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted cable | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/11/2015 18:30 |  |  | 276 | Residential |  | 20151127PWA_5 | Infrastructure (network-based) | -38.1843 | 144.3227 | 1 | Powercor | Report | 409 | 0.0030428 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Vehicle
Crew isolated supply and undertook repairs | PONTINGS ROAD, NOORAT EAST VIC 3265 |  |  |  |  | Overheated connection |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a connection had overheated on a 22kV line causing hot debris to fall to the ground, resulting in a ground fire (approx. 2.5m x 15m) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 25/11/2015 14:25 |  | Small: 10 - 1000 sq.m | 281 | Roadway |  | 20151127PWA_8 | Infrastructure (network-based) | -38.22 | 142.971 | 1 | Powercor | Report | 579 | 0.0018067 | 22kV AC | Warrnambool Airport Ndb | 3265 | Noorat East | Connection
Crew attended and reported a grass fire at LIS 2010766 which was out when they arrived on site. Made safe and replaced BA fuse. | 65 ROBERTS ROAD, POUND CREEK VIC 3996 | 2010766 |  |  | Unlikely |  |  |  |  | All Supply failures out of LA 193. A Boric Acid fuse tube had burnt out and had caused a grass fire of 4 sq.metres in size at LIS 2010766. | Boric acid | 0 | 0 | 0 |  | LGA14 | BA fuse failure. Burnt / candled fuse tube. | Grassfire | 29/11/2015 10:10 | 1 | Localised: less than 10 sq.m | 294 | Agricultural |  | 20151130SPN_10 | Infrastructure (network-based) | -38.6286 | 145.8834 | 1 | AusNet Services Distribution | Report | 442 | 0.0045498 | 22kV AC | Morwell (Latrobe Valley Airport) | 3996 | Pound Creek | Fuse
The attending fault crew repaired the damaged conductors and energised the HV. The crew left the LV blade fuses out so the AusNet Services' LEI could assess for suspected HVI damage. Attending LEIs inspected affected properties on South Valley Rd, Granard Ave, Park Rd, Arundel Rd and found no evidence of HV injection. Control Room (CEOT) was notified that there wasn't any signs of a HVI and it was safe to energise the LV. | 55-59 SOUTH VALLEY ROAD, PARK ORCHARDS VIC 3114 | 1205394 | Unauthorised work | Within clearances |  |  |  | Phase to neutral | 1 | Marcus Cook of 61 South Valley Rd, Park Orchards, (Ph: 0400 756 617) was cutting down a tree by the fence line on his property. As the tree fell down it made contact with the overhead 22kV and LV open bare power lines out on the street between Lis #1205394 & #1205393 opposite 64 South Valley Rd, Park Orchards. This caused feeder RWN 26 to operate. No LV fuses were found blown. The fault crew on site noticed splash marks on the LV conductors (RED phase and NEUTRAL). No injuries to any persons. | Conductor (bare) | 0 | 0 | 0 |  | RWN26 | Vegetation: Trees Incident | No Go Zone (contact);Damage to network assets | 22/11/2015 16:10 |  |  | 287 | Residential |  | 20151130SPN_3 | Infrastructure (network-based) | -37.7761 | 145.2125 | 1 | AusNet Services Distribution | Report | 428 | 0.018721 | 22kV AC | Moorabbin Airport | 3114 | Park Orchards | Trees
Dispatched Fault crew to isolate supply and make safe. Duty Availability Officer sent to investigate the incident. | 144 ZIG ZAG ROAD N, ELTHAM VIC 3095 | 929148 |  | Animal | Unlikely |  |  | Phase to earth | 1 | IMS 219260. Vic fires report sparks and flames on lis pole 929148. No fire on ground occurred. A possum made contact with the Lightning Arrestor and earthed structure. The LA was not damaged and the reference to a fire report re sparks and flames on lis pole 929148 were confined to the possum only. A reclose on feeder occurred. No other damage. As a result of the investigation, the incident category has been changed from serious to a near-miss electrical incident. This is not considered as an electrical fire incident. | Surge diverter | 0 | 0 | 0 |  | elm32 | Animal Incident | Flashover caused by a possum.;Other | 25/11/2015 1:00 | 0 | No ground fire | 289 | Residential |  | 20151130SPN_5 | Infrastructure (network-based) | -37.6935 | 145.1603 | 1 | AusNet Services Distribution | Report | 432 | 0.034836 | 22kV AC | Essendon Airport | 3095 | Eltham | Pole
Crew checked line for damage - none found | 906 WAITCHIE ROAD, NOWIE VIC 3585 |  | Working too close to overhead lines | [5 empty] | 1 | A farmer reported two days after the event (Monday) that a tipper he was operating had contacted an overhead line at the incident location on Saturday. On arrival the crew found a farmer (James Bell, Ph: 0428 396 295) was operating a tipper fully extended at the time and contacted a 22kV line causing black flash marks on a the conductor. A fault crew had attended and replaced a fuse on the Saturday and no cause had been found. There was no ground fire. There were no reported injuries or third party property damages. Crew advised conductor in paddock at a height greater than 7mtrs. | Conductor (bare) | 0 | 0 | 0 |  |  | Tipper contacted overhead line | Loss of supply | 42135.7618 |  |  | 300 | Agricultural |  | 20151201PWA_4 | Infrastructure (network-based) | -35.3904 | 143.2635 | 1 | Powercor | Report | 452 | 0.010045 | 22kV AC | Swan Hill Aerodrome | 3585 | Nowie | Vehicle
Crew isolated supply and arranged repairs | 261 WILLIAMS ROAD, SOUTH YARRA VIC 3141 |  |  | Lightning |  |  |  |  | 1 | A field crew patrolling a line after successful line reclose found that a 66kV pole had been struck by lightning at the incident location, damaging the pole requiring immediate replacement which caused significant traffic disruption in the area adjacent 261 Williams Rd between Toorak Rd and Malvern Rd. Protection operated. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Lightning | Significant disruption to the community;Damage to network assets | 20/11/2015 1:56 |  |  | 310 | Roadway |  | 20151202PWA_4 | Infrastructure (network-based) | -37.842 | 145.0042 | 1 | CitiPower | Report | 944 | 0.0030093 | 66kV AC | Essendon Airport | 3141 | South Yarra | Lightning
A LEI attended and completed installation tests following the earlier upgrade of the aerial service line. A steady 1v was measured with no load and load applied. At the rime of the investigation, no fault was identified that would account for the customer receiving an electric shock from the electrical installation. | 46 BRUCE STREET, BALNARRING VIC 3926 |  |  |  |  | Unknown technical factor |  | Phase to earth | 2 | Customer advised lights are dimming with low voltages to appliances. When the faults crew attended, the occupier advised that electric shocks have been received and they proceeded to replace the single phase grey twisted overhead service as a precaution prior to the LEI attending. The crew advised they couldn't identify any faults with the grey twisted service that was replaced with a XLPE type. | Aluminium twisted (grey) | 0 | 0 | 0 |  |  | Unknown | Minor shock | 27/11/2015 15:00 |  |  | 307 | Residential |  | 20151202UTD_4 | Infrastructure (network-based) | -38.3813 | 145.1241 | 1 | United Energy Distribution | Report | 460 | 0.011328 | Low voltage AC (<1kV) | Moorabbin Airport | 3926 | Balnarring | OH Cable
Crew isolated supply and checked for damages - none found | 2 CHANDLER HIGHWAY, KEW VIC 3101 |  | No external/community cause | No environment cause |  | Unknown technical factor | No work practice factor |  | 2 | MFB reported ground fire at the incident location. On arrival the crew found that a ground fire (Approx. 10m x 5m) had started below 22kV conductors. The crew were unable to determine a definite cause for the fire however there were mid-span isolators above the fire location and the crew believes that the fire may have been caused by arcing across these isolators as a result of a fault. There were no reported injuries. | Mid Span Isolators;Conductor (bare);Other | 0 | 0 | 0 |  |  | Crew unable to determine but suspect arcing between midspan isolators as a result of a fault | Grassfire | 26/11/2015 11:38 |  | High: More than 100 sqm | 324 | Roadway |  | 20151204PWA_11 | Infrastructure (network-based) | -37.7893 | 145.0265 | 1 | CitiPower | Report | 482 | 0.0025903 | 22kV AC | Essendon Airport | 3101 | Kew | AF Other
Crew checked assets for damage, none found | 32 MURPHY ROAD, TONGALA VIC 3621 |  |  |  |  | Unknown technical factor |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a ground fire (Approx. 50m x 180m) had occurred around the base of a 22kV concrete pole in the road reserve. An inspection of the insulators and conductors in immediate proximity of the structure failed to identify any cause for the fire. Protection operated. There were no reported injuries. | Pole top | 0 | 0 | 0 |  |  | Crew unable to determine | Grassfire | 42047.8472 |  | Medium: 1000 sq.m - 10 ha | 332 |  |  | 20151204PWA_16 | Infrastructure (network-based) | -36.2958 | 144.923 | 1 | Powercor | Report | 536 | 0.041494 | 22kV AC | Shepparton Airport | 3621 | Tongala | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 141 SHOREHAM ROAD, RED HILL SOUTH VIC 3937 | 1307978 |  |  |  | Electrical breakdown |  |  | 1 | At 1320hrs on 27/10/2015, 22kV feeder DMA 13 circuit breaker locked out affecting 344 customers. The HV feeder was suppressed for tree clearing activities at the time of the fault. The white phase of the 185mm HVABC failed mid-span in Shoreham Road, Red Hill South between pole No. LIS 1307978 and 9870271 south of the tee-off to Point Leo Road. This resulted in the 22kV conductor to fail and a small grass fire of approximately 1sqm started on the road reserve caused by the molten aluminium contacting the dry grass on the side of the road. Note: This small fire was not reported to United Energy at any time following the fault - United Energy were notified on 03/12/2015 by a local resident - Copy of the letter attached for reference. No high voltage injection or major damage was sustained and the cause was suspected to be as a result of the white phase active conductor failing midspan after tracking to the bare support cable. | Conductor (ABC) | 0 | 0 | 0 |  | DMA 13 | HVABC failed mid-span in Shoreham Road, Red Hill South between pole No. LIS 1307978 and 9870271 south of the tee-off to Point Leo Road. | Loss of supply;Grassfire | 27/10/2015 13:20 |  | Localised: less than 10 sq.m | 325 | Roadway |  | 20151204UTD_1 | Infrastructure (network-based) | -38.3822 | 145.0236 | 1 | United Energy Distribution | Report | 483 | 0.0044664 | 22kV AC | Moorabbin Airport | 3937 | Red Hill South | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. All three LV bus fuses operated at "Sycamore-Kooyong" substation and were replaced when supply was restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 10 BURREEL AVENUE, ELSTERNWICK VIC 3185 | LIS No. 2307325 |  | Blown branch/vegetation |  | HV injection |  |  | 1 | At 2031hrs on 25/11/2015, 11kV feeder EL 06 circuit breaker reclosed to lockout affecting 1532 customers. During strong winds, a large private tree branch from 331 Kooyong Road contacted the HV conductors on the corner of Burreel Avenue that resulted in a HV conductor to contact the LV conductors below. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from the north circuit of "Sycamore-Kooyong" substation. The LEI confirmed a high voltage injection occurred (CLA 1506) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | EL 06 | Vegetation: Trees Incident | HV injection;Loss of supply | 25/11/2015 20:31 |  |  | 331 | Residential |  | 20151204UTD_3 | Infrastructure (network-based) | -37.8868 | 145.0148 | 1 | United Energy Distribution | Report | 873 | 0.0043322 | 11kV AC | Moorabbin Airport | 3185 | Elsternwick | Trees
Crew isolated supply and undertook repairs | 110 CHURCH STREET, RICHMOND VIC 3121 |  | Working too close to underground cables | [5 empty] | 1 | A contractor reported that he had contacted cables at the incident location whilst excavating a basement for a new building. On arrival the crew found that the contractor (BRC Piling, 10 Littlejohn Ave, Mt Evelyn Vic 3796, sub-contracting to BUILDCEPT, 32 Hall Street, Hawthorn East, 3123, Site Manager, Branko Bazon, Ph: 0448 029 730) was undertaking excavation works and contacted two 11kV high voltage underground cables causing damage to the cables and resulting in 1666 customers off supply in the area. Protection operated. There were no reported injuries. | Cable | 0 | 0 | 0 |  |  | Contractor contacted 11kV cables | Loss of supply | 42075.5875 |  |  | 365 | Roadway |  | 20151210PWA_6 | Infrastructure (network-based) | -37.8144 | 144.9997 | 1 | CitiPower | Report | 7994 | 0.0035556 | 11kV AC | Essendon Airport | 3121 | Richmond | Dug up
Fault crews attended and replaced the service cable. CFA attended to ensure fire was correctly extinguished. | 160 BOYDS ROAD, HURSTBRIDGE VIC 3099 | 925868 |  | Bird |  |  |  | Phase to earth | 2 | Customer reported a Part Supply Failure. CEOT dispatched a fault crew to attend to isolate, make safe and investigate. A small 5m x 5m grass fire was observed caused by a 25 sq. mm LV overhead service cable down in a paddock due to bird/s (Cockatoo/s) that had chewed through the service cable. Fault crews attended and replaced the existing service cable with an XLPE type service cable. | Service conductor | 0 | 0 | 0 |  | DRN23 | Overhead service cable chewed by Cockatoos. | Grassfire | 42259.566 | 1 | Small: 10 - 1000 sq.m | 360 | Residential |  | 20151210SPN_2 | Infrastructure (network-based) | -37.6216 | 145.1856 | 1 | AusNet Services Distribution | Report | 1235 | 0.029065 | Low voltage AC (<1kV) | Essendon Airport | 3099 | Hurstbridge | Animal
A faults truck attended and isolated supply to the 150w HPS lantern. A new trouble order was created for ACE Energy (United Energy P/L contractor) to attend and replace the defective public lighting lantern. | 1479 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | LIS No. 1308952 |  | Precipitation |  | Corrosion;Electrical breakdown |  |  | 2 | Kristie from the CFA is reporting there is a pole fire outside the shop with molten plastic falling on the road and becoming a road hazard. During light drizzle, a 150w HPS public lighting lantern caught fire on pole No. LIS 1308952 located outside 1479 Point Nepean Road, Rosebud. | Public lighting | 0 | 0 | 0 |  |  | A 150w HPS public lighting lantern caught fire outside 1479 Point Nepean Road, Rosebud. | Plant/equipment | 42047.8958 |  | Negligible: no ground fire | 368 | Roadway |  | 20151211UTD_3 | Infrastructure (network-based) | -38.3606 | 144.8883 | 1 | United Energy Distribution | Report | 552 | 0.020052 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Pole
Crew pulled service fuse at 0815, immediately after test on meter box. Determined that FOLCB required replacement and following discussion with LEI and the customer's REC, the FOLCB was isolated to facilitate replacement. Gave contact details to customer and crew left site at approx. 0920. LEI coming from Melbourne, so coordinated REC & crew to restore supply to all meet on site between 1330 and 1400. Repairs affected by REC and installation reconnected following OK from LEI. LEI report: Voltage tests between an independent earth and various points of the electrical installation, including the shock site, did not reveal any defective conditions or equipment due the fault being rectified before the LEI attended. Final NST test performed which passed. Voltage from independent earth to point of contact metal meter box was measured at 0.73V (No load) & 1.113V (Load). | 10 CONLEYS LANE, HARRIETVILLE VIC 3741 | 4507687 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 219117. Call out to Electric Shock at 23 Mill Road, Harrietville. Incident No. 83319-r. Customer reported receiving an electric shock from meter box. Customer said lights had been dipping the previous evening and customer went to meter board the next morning when the electric shock was received. Crew arrived on site and found neutral of grey twisted service hanging out of customer's FOLCB at Point Of Attachment. Crew tested metal meter box and recorded 180 volts to independent earth. CEOT arranged for LEI to attend. Miss Skrypay received a tingle to her fingers and feet while she was standing on the wet lawn when attempting to check circuit breakers at the switchboard. She made simultaneous contact between the earth metal meter box door latch with her left hand, and the wet lawn that she was standing on. | Service conductor | 0 | 0 | 0 |  | BRT21 | Neutral of grey twisted service cable was hanging out of the customer's FOLCB at POA. Burnt out service neutral connection in FOLCB. | Minor shock not requiring medical attention | 18/11/2015 6:45 |  |  | 381 |  |  | 20151214SPN_3 | Infrastructure (network-based) | -36.9015 | 147.0569 | 1 | AusNet Services Distribution | Report | 567 | 0.028987 | Low voltage AC (<1kV) | Wangaratta Aero | 3741 | Harrietville | OH Cable
The crew quickly extinguished the fire (approximately less than 1sqm at the pole base) using the vehicle knapsack and the crew made the area safe. The ZNX subcontractor checked the LV supply and contacted their management to report the incident. ZNX advised United Energy and United Energy requested that an investigation takes place to ensure safe systems of work are in place prevent similar events occurring. | 9 CAMDEN ROAD, HUGHESDALE VIC 3166 |  |  |  |  | Neutral fault;Mechanical breakdown | Followed but inappropriate |  | 2 | While untying the white phase low voltage (LV) conductor using live work method, the tie wire has contacted the crossarm strap bolt which was at neutral potential due to damaged LV service insulation. This started a small grass fire at the base of the pole. The aluminium conductor tie contacted the crossarm brace bolt which caused a minor flash resulting in a small amount of molten aluminium falling to the ground and starting a small fire less than 1sqm at the base of the pole. Following the incident, the work crew found the insulation on a neutral screen service had worn through beneath the wire wrapon resulting in it being at the same potential as the neutral conductor and in direct contact with the crossarm brace. No injuries were sustained and there was no loss of supply. | Conductor (bare);Crossarm (wood);Aluminium;Neutral screen;Insulator tie wires/connections | 0 | 0 | 0 |  |  | While untying the white phase low voltage (LV) conductor, the tie wire has contacted the crossarm strap bolt which was at neutral potential due to damaged outer insulation on a neutral screened service. | Grassfire | 42106.5868 |  | Localised: less than 10 sq.m | 375 | Roadway |  | 20151214UTD_1 | Infrastructure (network-based) | -37.8989 | 145.0826 | 1 | United Energy Distribution | Report | 559 | 0.03548 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Hughesdale | OH Cable
Crew checked assets for damage none found | 202 SAUNDERS ROAD, NEW GISBORNE VIC 3438 |  |  | Animal |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival the crew found that a possum that had made contact with the HV apparatus and fell to the ground resulting in a ground fire (Approx. 15m x 15m) on the road reserve. There were no reported injuries. | Equipment | 0 | 0 | 0 |  |  | Animal Incident | Grassfire | 15/12/2015 5:14 |  | Small: 10 - 1000 sq.m | 390 | Roadway |  | 20151216PWA_2 | Infrastructure (network-based) | -37.4739 | 144.6163 | 1 | Powercor | Report | 587 | 0.0031678 | 22kV AC | Melbourne Airport | 3438 | New Gisborne | Animal
The branch was removed, or fell from the conductors and the HV feeder restored following consultation with the Citywide Trees Supervisor to ensure they were clear of the conductors. | 36 LAKE ROAD, BLACKBURN VIC 3130 | LIS No. 7025298 |  | Within clearances |  | Conductor clashing | Followed but inappropriate |  | 1 | At 1101hrs on 15/12/2015, 22kV feeder NW 11circuit breaker successfully locked out affecting 784 customers. The HV feeder had the auto reclose suppressed for tree clearing activities at the time of the fault. Craig from Citywide Tree Services rang the United Energy faults and emergencies number advising they were clearing trees in Lake Road, Blackburn and there was a gust of wind which has blown the branch and its now resting on the power line. No injuries or damage to plant was sustained and Citywide were working for the local council. Secondary damage occurred with HV conductors clashing at two locations due to fault current. Citywide Trees Supervisor Dan Borthwict 0438 477 810 | Conductor (bare) | 0 | 0 | 0 |  | NW 11 | Vegetation: Trees Incident | Loss of supply | 15/12/2015 11:01 |  |  | 388 | Roadway |  | 20151216UTD_1 | Infrastructure (network-based) | -37.8271 | 145.1592 | 1 | United Energy Distribution | Report | 584 | 0.011844 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Trees
A faults truck attended and isolated supply to the 150w HPS lantern. A new trouble order was created for ACE Energy (United Energy P/L contractor) to attend and replace the defective public lighting lantern. | 277A CANTERBURY ROAD, FOREST HILL VIC 3131 | LIS No. 0639613 | Unknown external/community factor | Unknown environment factor |  | Electrical breakdown | Unknown work practice factor |  | 2 | The MFB reported that a street light was on fire directly outside this address and needs to be isolated. During light drizzle, a 150w HPS public lighting lantern caught fire on pole No. LIS 0639613 located outside 277A Canterbury Road, Forest Hill. | Public lighting | 0 | 0 | 0 |  |  | The MFB were called to the site following a 150w HPS public lighting lantern caught fire. | Other electricity related | 42350.9097 |  | Negligible: no ground fire | 389 | Roadway |  | 20151216UTD_2 | Infrastructure (network-based) | -37.8342 | 145.1697 | 1 | United Energy Distribution | Report | 585 | 0.034503 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Forest Hill | AF Other
Dispatched Fault Crew and DAO to isolate, make safe and investigate the incident. Crew replaced the burnt HV dropper lead and restored supply. Faulty lead quarantined and tagged for follow-up investigation. | 167 DISTILLERY ROAD, WAHGUNYAH VIC 3687 | 5210166 |  |  |  | Under investigation;Other |  |  | 1 | Report to CEOT from CFA off a 40 metre x 40 metre square fire around an AusNet Services' pole and a fire on the pole. Ground fire out but pole on fire. AusNet Services' investigation revealed that the insulated HV transformer dropper lead appears to have failed in the joint just above the transformer bushing. The pole was not on fire, it was the HV dropper lead that was on fire and burning. The area of the burnt grass was 1200 sq. metres. Blown 15E BA HV fuse & 200 Amp LV fuse on the substation. | Pole mounted;Connector/termination | 0 | 0 | 0 |  | WN3 | Burnt HV dropper leads from overhead conductor to transformer. The HV lead is with AusNet Services' Lines Section for investigation. | Grassfire | 14/12/2015 19:35 | 1 | Medium: 1000 sq.m - 10 ha | 394 | Agricultural |  | 20151217SPN_2 | Infrastructure (network-based) | -36.0366 | 146.396 | 1 | AusNet Services Distribution | Report | 1243 | 0.035122 | 22kV AC | Wangaratta Aero | 3687 | Wahgunyah | Connection
De-energised from remote ACR YM005. A fault crew was dispatched. The fault crew made safe and isolated the line, tested and earthed and issued EAP 156876 and carried out repairs. The conductor was 3/12 steel and was repaired using splices and some additional conductor. When repairs had been completed the supply was restored and incident reported. | 236 BILLY CREEK ROAD, STACEYS BRIDGE VIC 3971 | 2622053 |  |  |  | Corrosion |  | Phase to earth | 1 | HV Conductor Rusted through at LIS# 2622053- 2622165. 2 x 25A BA Fuses Blown @ 817986 Cow killed. No Fire. At approx 08.00 fault call are recieved from the area a crew are dispatched and find fuses 817986 with 2 blown BA fuses. A patrol was conducted and it was found the conductor on the southern side of the pole 2622053 broke and fell to the ground, it appears a cow was either under the conductor or very close when it fell. The conductor was still live when it contacted the cow in the neck region and this killed the cow. The cow received phase to phase voltages until the protection operated, fuses 81786 both outside DOF operated. The broken conductor fell onto the live tee off below. Their where no burn marks evident around the body of the cow and no fire started. | Conductor (bare) | 0 | 0 | 0 |  | FTR12 | Corroded HV overhead bare conductor at/near a splice. | Fatality of livestock, pet or companion animal | 16/12/2015 7:45 |  |  | 397 | Agricultural |  | 20151217SPN_4 | Infrastructure (network-based) | -38.5699 | 146.5226 | 1 | AusNet Services Distribution | Report | 599 | 0.021223 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Staceys Bridge | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1-3 CREST GROVE, NUNAWADING VIC 3131 | LIS No. 7040330 |  | Animal |  | Conductor clashing;HV injection |  |  | 1 | At 0028hrs on 16/12/2015, 22kV feeder NW 22 circuit breaker reclosed to lockout affecting 2520 customers. Anthony from the MFB called to report power lines were down and there was a grass fire outside 3 Crest Grove, Nunawading. A faults crew found a possum at the base of "Crest-Springfield" pole type substation after contacting the HV fuses. The fault current caused two HV tee-off connections to fail resulting in the HV conductors to contact the LV below as they fell to the ground. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from the north circuit of "Crest-Springfield" substation. The south circuit of the substation was placed under LV parallel to restore partial supply to customers in the area. The faults crew removed two bays of damaged HV conductors along with the 22kV 315kVA transformer that also sustained damage and requires replacement. The LEI confirmed a high voltage injection occurred (BWD 1522) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The MFB were in attendance at pole No. LIS 7040330 after molten metal splash marks were found on the concrete substation pole. No grass fire occurred. | Conductor (bare);Aluminium;Powder filled;Pole mounted;Pole (concrete) | 0 | 1 | 0 |  | NW 22 | Animal Incident | HV injection;Loss of supply | 16/12/2015 0:28 |  |  | 392 | Roadway |  | 20151217UTD_1 | Infrastructure (network-based) | -37.8108 | 145.1828 | 1 | United Energy Distribution | Report | 589 | 0.015874 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Animal
CFA on site and contained the fire. The crew isolated the transformer and restored feeder which tripped off. CFA extinguished the fire on Saturday (19 December) afternoon & returned on Sunday (20 December) to re-wet the area. The single phase 25kVA transformer was replaced on the Saturday. | 161 DRYSDALES ROAD, OUTTRIM VIC 3951 | 2005817 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 1 | IMS219746. Calembeena 14 S/S - LIS : 2005817. Operator found HV fuse candling and observed bush under fire. 1 phase 25kVA transformer fault caused 1 EDO fuse to operate with the 2nd fuse hung-up and the ACR operating to isolate section of line. Hung-up fuse resulted in grass & scrub fire start. Temperature was 41 degrees C, wind speed 26 kph with gusts to 44 kph. Fire burnt south through scrub on west side of road (200mx3m scrub) & into grass of paddock on west side road (230mx50m grass). Fire then jumped to east side of road burning more scrub (80mx7m scrub) and into grass paddock on east side (80mx10m grass). Fire also burnt 22 farm fence posts & 3 fence rails on west side of road however the fence was still able to stand. On the east side the fire burnt 15 fence posts and the fence had to be temporary supported with star pickets to remain up. Feeder CB tripped. ACR tripped to lockout. | EDO fuse | 0 | 0 | 0 |  | LGA23 | Single phase transformer fault caused 1 EDO fuse to operate with the 2nd fuse hung-up resulting in a grass & scrub fire. | Bushfire;Grassfire | 19/12/2015 18:20 | 1 | Medium: 1000 sq.m - 10 ha | 412 | Agricultural |  | 20151221SPN_4 | Infrastructure (network-based) | -38.5291 | 145.79 | 1 | AusNet Services Distribution | Report | 622 | 0.016973 | 22kV AC | Morwell (Latrobe Valley Airport) | 3951 | Outtrim | Fuse
Dispatched fault crew to make safe and investigate. Fuse replaced. | 39 STREITBERGS ROAD, DARNUM VIC 3822 | [8 empty] | IMS219753. Hung-up fuse @ LIS #271861. No fire caused. Suspect animal on structure. Pleased note, further investigation revealed that this is a hung-up BA fuse only - no burnt fuse tube / candling, therefore a Schedule 2 report is not required. | Boric acid | 0 | 0 | 0 |  |  | Hung-up BA fuse only. | BA fuse hang-up only.;Other | 21/12/2015 8:30 | 1 | Negligible: no ground fire | 414 |  |  | 20151221SPN_6 | Infrastructure (network-based) | -38.1938 | 146.0103 | 1 | AusNet Services Distribution | Report | 626 | 0.032127 | 22kV AC | Morwell (Latrobe Valley Airport) | 3822 | Darnum | Fuse
Crew isolated supply and undertook repairs | 5 FITZGERALD ROAD, LAVERTON NORTH VIC 3026 |  |  |  |  | Overheated connection |  |  |  | VicFire reported a grass fire started by pole fire at the incident location. On arrival the crew found that an IPC connection had overheated where the LVABC connects to the overhead mains cables and had fallen to the ground resulting in a ground fire (Approx. 15cm x 15cm) on the road reserve. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 19/12/2015 22:14 | 1 | Localised: less than 10 sq.m | 426 | Roadway |  | 20151222PWA_4 | Infrastructure (network-based) | -37.8447 | 144.7813 | 1 | Powercor | Report | 644 | 0.032137 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Connection
Crew isolated supply and undertook repairs | LOT 2 EDEY ROAD, RED CLIFFS VIC 3496 |  |  |  |  | Candled fuse |  |  | 2 | A fault crew attending an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | Candled Fuse | Plant/equipment | 42197.4243 |  | Negligible: no ground fire | 374 | Roadway |  | 20151211PWA_4 | Infrastructure (network-based) | -34.3356 | 142.2743 | 1 | Powercor | Report | 558 | 0.041139 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Fuse
Emergency high voltage switching was completed on 22kV feeder RWT 28 to minimise the number of customers affected and the HV intermediate crossarm was replaced under Access Authority conditions prior to the supply being restored. | 917-921 DONCASTER ROAD, DONCASTER EAST VIC 3109 | LIS No. 7062981 |  | Precipitation |  | Electrical breakdown |  |  | 2 | A passing motorist advised on Doncaster Road between Middleborough Road and Dryden Street there are sparks coming from the power lines. Following light drizzly rain, a HV intermediate crossarm fire occurred at pole No. LIS 7062981 located outside 917 Doncaster Road, Doncaster East. The MFB were in attendance. | Crossarm (wood) | 0 | 0 | 0 |  | RWT 28 | Crossarm fire on a HV intermediate | Pole-top fire | 27/11/2015 17:14 |  | Negligible: no ground fire | 366 | Roadway |  | 20151211UTD_1 | Infrastructure (network-based) | -37.7876 | 145.1507 | 1 | United Energy Distribution | Report | 550 | 0.038306 | 22kV AC | Moorabbin Airport | 3109 | Doncaster East | Crossarm
Isolated supply and made safe. | 830 HIGH STREET, RESERVOIR VIC 3073 |  | Vehicle | [5 empty] | 2 | A car impacted a pole causing a LV conductor to fall to ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Car impacted pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42287.3132 |  |  | 387 | Residential |  | 20151216JEM_2 | Infrastructure (network-based) | -37.7238 | 145.0067 | 1 | Jemena | Report | 583 | 0.01388 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Vehicle
Crew isolated supply and arranged repairs. Crew advised worker to seek medical attention. | 148 BRUNSWICK ROAD, BRUNSWICK VIC 3056 |  | Working too close to underground cables | [5 empty] | 2 | A contractor reported that their excavation crew has contacted something which has caused a flash at the incident location. On arrival the crew found that a contractor (All Trenching and Boring Services mobile 0409 793 828) was undertaking excavation works to install an underground service cable and during the course of the work a worker (Dan Besley), using a sabre saw cut, through wooden troughing and cut into an 6.6kV underground cable, resulting in a flashover. The worker received minor burns to his hands. The fault crew advised him to seek medical assistance. The contractor had undertaken DBYD enquiries, sequence No: 49628873. The worker advised the crew that he thought the wooden troughing was just a piece of wood. | Cable | 0 | 0 | 0 |  |  | Contractor contacted 6.6kV cable with sabre saw | Medical attention (first aid/doctor/hospital) | 42320.6403 |  |  | 385 | Roadway |  | 20151216PWA_1 | Infrastructure (network-based) | -37.7776 | 144.9634 | 1 | CitiPower | Report | 7995 | 0.035264 | 6.6kV AC | Essendon Airport | 3056 | Brunswick | Dug up
Crew isolated supply and undertook repairs | 12 COLLINS STREET, THORNBURY VIC 3071 |  | Vehicle | [5 empty] | 2 | MFB reported that a service wire was on the ground at the incident location. On arrival the crew found a LV service wire was laying on the side of the road. The crew spoke to some people who lived in the street and they mentioned that a truck was parked on the side strip and when he left he contacted and broke the service wire. The truck left the scene of the incident and they did not see the number plate. There was no ground fire. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | No Go Zone (contact);Damage to network assets | 42289.7715 |  |  | 402 | Roadway |  | 20151218PWA_2 | Infrastructure (network-based) | -37.755 | 145.0025 | 1 | CitiPower | Report | 7997 | 0.0095104 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Vehicle
CEOT dispatched a fault crew to attend the incident site to make safe, investigate and repair. Substation Powder Filled type fuses were replaced with Boric Acid type fuses. | 1 YARRA STREET, YARRA JUNCTION VIC 3797 | 144482 |  | Bird |  | PPE failed to perform as designed |  | Phase to earth | 2 | CFA reported a small grass fire. A suspected bird flashover on a concrete pole with steel a crossarm caused a 22kV Powder Filled Fuse to fail with hot molten particles from the fuse falling to the ground causing a small grass fire of approximate size 3m x 3m. | Powder filled | 0 | 0 | 0 |  | WYK11 | Bird Incident | Other electricity related | 17/12/2015 16:55 | 1 | Negligible: no ground fire | 398 | Commercial |  | 20151218SPN_1 | Infrastructure (network-based) | -37.7823 | 145.6143 | 1 | AusNet Services Distribution | Report | 601 | 6.713e-05 | 22kV AC | Moorabbin Airport | 3797 | Yarra Junction | Animal
Faulted section of line isolated and prepared for repairs. HV and LV cables were repaired and customers restored to supply. | 37 KARDELLA ROAD, KORUMBURRA VIC 3950 | 2006907 |  | Fallen |  |  |  |  | 1 | IMS219750. Initial report to CEOT was that a tree fell on the line which caused HV and LV on the deck, 3 bays down between Kardella Rd 6 S/S and LIS: 2006907 and a possible HVI. Thus this was the reason for a Schedule 1 report to ESV. Subsequent investigation by the Leongatha Site Manager revealed that no HVI damage occurred to any properties, feeder CB operated, and there were no live conductors were on the ground. As result the incident category has been changed from serious to a near-miss electrical incident. Therefore a Schedule 2 report is not required. | Conductor (bare) | 0 | 0 | 0 |  | LGA21 | Vegetation: Trees Incident | HV injection | 19/12/2015 17:00 |  |  | 411 | Residential |  | 20151221SPN_3 | Infrastructure (network-based) | -38.4345 | 145.8356 | 1 | AusNet Services Distribution | Report | 1264 | 0.00364 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3950 | Korumburra | Trees
Fused replaced and customer's supply restored. A request has been raised to replace the EDO fuse units with Boric Acid fuse units. | 3522 YARRA JUNCTION-NOOJEE ROAD, PIEDMONT VIC 3833 | 2700315 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 219743. Burnt Out EDO Fuse found at lis 2700315. No ground fire, no other damage. | EDO fuse | 0 | 0 | 0 |  | WGL24 | Burnt EDO fuse tube. | Other electricity related | 19/12/2015 7:25 | 1 | Negligible: no ground fire | 413 | Agricultural |  | 20151221SPN_5 | Infrastructure (network-based) | -37.8897 | 145.9325 | 1 | AusNet Services Distribution | Report | 624 | 0.021992 | 22kV AC | Morwell (Latrobe Valley Airport) | 3522 | Piedmont | Fuse
Worker was taken to hospital and underwent an EGC before returning to work. Tool box meeting held. Employees advised not to touch cables in trenches until the investigation is complete. ESV notified. Cable repairs were carried out. A Safety Alert was issued by UGL. | 495-503 WARRIGAL ROAD, HEATHERTON VIC 3202 |  |  |  |  | Mechanical breakdown |  | Phase to earth | 2 | IMS219742. Heatherton Terminal Station Redevelopment Project. A UGL contractor employee was manually tracing a cable in a below cable trench together with another person. He reached into the trench and placed his right hand underneath a group of cables to grab a cable he was tracing at which time he received a slight electric shock. Initial investigation undertaken revealed it was found that the cable being traced had damage to its outer sheath and an exposed active conductor which was not visible at the time of tracing the cable. | Terminal substation | 0 | 0 | 0 |  |  | Damage to outer sheath of cable. | Medical attention (first aid/doctor/hospital) | 18/12/2015 21:55 |  |  | 415 | Other | Substation | 20151221SPN_7 | Infrastructure (network-based) | -37.9411 | 145.0789 | 1 | AusNet Services Transmission | Report | 628 | 0.0049097 | Low voltage AC (<1kV) | Moorabbin Airport | 3202 | Heatherton | UG Cable
Crew Isolated supply and undertook repairs | 265 HAMILTON HIGHWAY, FYANSFORD VIC 3218 |  |  |  |  | Overheated connection |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that a connection at a PG clamp on a 22kV conductor had overheated, causing hot debris to fall to the ground resulting in a ground fire (Approx. 1 Ha) on the road reserve and private property. The fire also caused damage to fencing, shedding and private property. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 19/12/2015 16:00 | 1 | Small: 10 - 1000 sq.m | 425 | Residential |  | 20151222PWA_3 | Infrastructure (network-based) | -38.1421 | 144.297 | 1 | Powercor | Report | 641 | 0.015752 | 22kV AC | Avalon Airport | 3218 | Fyansford | Connection
Crew isolated supply and undertook repairs | 26 CENTAURUS AVENUE, CLIFTON SPRINGS VIC 3222 |  |  |  |  | Overheated connection |  |  | 2 | Customer and CFA reported a fire at the incident location. On arrival the crew found that a connection on a LV transformer isolator had overheated resulting in a ground fire (Approx. 5m x 10m) on the road reserve. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 20/12/2015 12:40 | 1 | Small: 10 - 1000 sq.m | 427 | Roadway |  | 20151222PWA_5 | Infrastructure (network-based) | -38.149 | 144.5741 | 1 | Powercor | Report | 646 | 0.0026979 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | Connection
A faults truck attended and isolated the circuit to enable a underground crew to safely replace the LV pillar. Supply was restored to customers upon completion. | 8 PUSHKIN COURT, DONCASTER EAST VIC 3109 |  |  |  |  | Corrosion;Electrical breakdown;Overheated connection |  |  | 1 | Customers supplied from "Taunton-Leawarra" advised they have lost their electricity supply. A LV connection or joint in a LV pillar located outside 8 Pushkin Court, Doncaster East failed that caused a small grass fire estimated to be 5sqm in size to start in the dry grass that was quickly extinguished. | LV Pillar | 0 | 0 | 0 |  |  | A LV connection or joint in a LV pillar failed that caused a small grass fire. | Grassfire | 18/12/2015 16:05 | 1 | Localised: less than 10 sq.m | 418 | Roadway |  | 20151222UTD_3 | Infrastructure (network-based) | -37.7763 | 145.1555 | 1 | United Energy Distribution | Report | 631 | 0.0050035 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Connection
Crew isolated supply for repairs | 3275 GREAT OCEAN ROAD, NIRRANDA VIC 3268 |  | Working too close to underground cables |  |  | Fault on customer installation |  |  | 2 | A customer reported that a Contractor had dug up a cable at the above location. On arrival the crew found that a fencing contractor was using a post-hole borer, when he struck the customerâ€™s private Low Voltage underground service cable resulting in the contractor receiving a mild electrical shock. The contractor who received the shock was advised to seek medical treatment as a precaution, but refused. There was no ground fire. There were no reported injuries or third party property damages. | Private overhead electric line (POEL) | 0 | 0 | 0 |  |  | Post hole borer contacted private LV mains | Minor shock | 17/12/2015 12:30 |  |  | 438 | Agricultural |  | 20151223PWA_4 | Infrastructure (network-based) | -38.5 | 142.7554 | 1 | Powercor | Report | 661 | 0.00023727 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3275 | Nirranda | Dug up
Crew isolated supply and undertook repairs | 529 WESTERN HIGHWAY, VECTIS VIC 3401 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV cross arm however the crossarm remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42228.2701 | 1 | Negligible: no ground fire | 439 | Roadway |  | 20151223PWA_5 | Infrastructure (network-based) | -36.6879 | 142.1639 | 1 | Powercor | Report | 662 | 0.0071609 | 22kV AC | Horsham Aerodrome | 3401 | Vectis | Crossarm
Fault crew dispatched to patrol MYT 8 feeder after it went to lockout at the zone substation at 15:02. Patrolled the line sectionalizing as they went and found three HV wires on the ground with a large tree branch on top of them, line at Pole 30 Wood Spur on Sunday night . Wood Spur isolated at Fuses 870086 and supply restored to remainder of feeder that was still off at 23:10. Crew dispatched on Monday(21/12/15) morning to undertake repairs and restore supply. Access Permit issued, tree branch cut off the line and conductors came back up to sag once removed. Conductors checked and no damage found. Adjacent poles checked and no damage found to ties or insulators. Supply restored to Wood Spur by closing fuses 870086 at Tee-off pole at a 10:28 21/12/15. | 469 HAPPY VALLEY ROAD, ROSEWHITE VIC 3737 | 4506880 |  | Wind |  |  |  | Phase to earth | 1 | A large branch came out of a 26m high gum tree about 7-8m up during a "violent wind squall" (as described by the property owner). The trunk of the tree was located 10m from the centre line of the high voltage overhead line. A fire of approximately 300m surrounded the area where the conductors had touched the ground. It burnt grass in a paddock that was slightly green and was put out mainly by a shower of rain and then finally by the property owner with his spray rig. The CFA were called by the property owner and then cancelled following him putting out the fire. MYT 8 feeder went to lockout following one unsuccessful reclose based on a "Sensitive Earth Fault Target". It recorded a 55A fault current. | Conductor (bare) | 0 | 0 | 0 |  | myt8 | Vegetation: Trees Incident | Grassfire | 20/12/2015 21:22 | 1 | Small: 10 - 1000 sq.m | 443 | Agricultural |  | 20151223SPN_1 | Infrastructure (network-based) | -36.5835 | 146.8115 | 1 | AusNet Services Distribution | Report | 670 | 0.017944 | 22kV AC | Wangaratta Aero | 3737 | Rosewhite | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the HV/LV strain pole was replaced under Access Authority conditions prior to the supply being restored. | 627B CLAYTON ROAD, CLARINDA VIC 3169 | LIS No. 8829691 |  | Precipitation |  | Leakage |  |  | 2 | MFB called to report a pole fire has occurred at the corner of Clayton and Leslie Roads, Clayton South. Following light drizzly rain, a HV strain crossarm fire occurred at pole No. LIS 8829691 located in Leslie Road, 1 pole west of Clayton Road. The timber pole has HV spur fusing (DN2896) and is located on 22kV feeder SS 21 and required replacement. The MFB were in attendance who originally reported that top of the pole was badly burnt. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | SS 21 | Following light drizzly rain, a HV strain crossarm fire occurred after brief showers with "dirty rain" caused tracking on older style brown fog type insulators to occur. | Pole-top fire;Loss of supply | 21/12/2015 1:06 | 1 | Negligible: no ground fire | 445 | Roadway |  | 20151223UTD_2 | Infrastructure (network-based) | -37.9487 | 145.1148 | 1 | United Energy Distribution | Report | 669 | 0.024806 | 22kV AC | Moorabbin Airport | 3169 | Clarinda | Crossarm
Site was made safe. CFA attended and extinguished fire | 445 RIDDELL ROAD, SUNBURY VIC 3429 | Pole number A055266 |  | Bird |  |  |  |  | 1 | Crow bird has reportedly contacted ACR 55612 on Riddell Road (near Dalrymple Road), Sunbury causing SBY11 22kV feeder to trip, igniting a grass fire extending for approx 65m2 with two spots. | Conductor (bare);ACR/OCR;Surge diverter | 0 | 0 | 0 |  | SBY11 | Bird Incident | Grassfire | 29/12/2015 18:12 | 1 | Small: 10 - 1000 sq.m | 470 | Agricultural |  | 20151230JEM_1 | Infrastructure (network-based) | -37.5523 | 144.6963 | 1 | Jemena | Report | 717 | 0.010082 | 22kV AC | Melbourne Airport | 3429 | Sunbury | Animal
Crew isolated supply to POEL and advised a REC would be required to make repairs. | 1138 SEBASTOPOL-SMYTHESDALE ROAD, ROSS CREEK VIC 3351 |  |  |  |  | Fault on customer installation |  |  | 2 | VicFire reported a wire down and fire at the incident location. On arrival the crew found that a conductor on a customer's Private overhead electric line (POEL) had broken and fallen to the ground, resulting in a ground fire (approx. 1,250 sqm) on private property which was extinguished by the property owner. There were no reported injuries. | Private overhead electric line (POEL);Customer installation | 0 | 0 | 0 |  |  | Broken conductor on POEL | Grassfire | 24/12/2015 15:05 | 0 | Medium: 1000 sq.m - 10 ha | 471 | Agricultural |  | 20151230PWA_2 | Infrastructure (network-based) | -37.6161 | 143.8057 | 1 | Powercor | Report | 1087 | 0.0010914 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Ross Creek | Conductor
Crew isolated supply and undertook repairs. | 22-24 GRIFFITHS STREET, STAWELL VIC 3380 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A fault crew attending an outage found that a crossarm fire had occurred on a 22kV/lv pole at the incident location, which caused the crossarm to break however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire. | Pole-top fire | 26/12/2015 7:04 | 1 | Negligible: no ground fire | 481 | Roadway |  | 20151230PWA_7 | Infrastructure (network-based) | -37.0611 | 142.7638 | 1 | Powercor | Report | 1153 | 0.03956 | 22kV AC | Horsham Aerodrome | 3380 | Stawell | Crossarm
Crew isolated supply and undertook repairs. | 599 NUMURKAH ROAD, KATUNGA VIC 3640 |  |  | Blown branch/vegetation |  |  |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a tree branch had contacted and damaged an adjacent low voltage conductor resulting in a grass fire (Approx. 600 sqm) on the road reserve. Protection operated. There were no reported injuries. | Conductor (insulated) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 26/12/2015 16:40 | 1 | Small: 10 - 1000 sq.m | 484 | Roadway |  | 20151230PWA_9 | Infrastructure (network-based) | -36.0374 | 145.4599 | 1 | Powercor | Report | 1140 | 0.036795 | Low voltage AC (<1kV) | Shepparton Airport | 3640 | Katunga | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 50 SHEEHANS ROAD, RED HILL VIC 3937 | Between pole numbers LIS 1307730 and 1307731. |  | Wind;Alive;Fallen;MEC |  | Unknown technical factor |  |  | 1 | At 1829hrs on 26/12/2015, 22kV feeder DMA 23 circuit breaker reclosed to lockout affecting 126 customers. The customer at 50 Sheehans Road, Red Hill advised a pole fire has spread to a grass fire. During strong gusty southerly winds, a private tree from 50 Sheehans Road, Red Hill has fallen and contacted "Sheehans-Gorman" substation, including the HV and LV ABC causing the bay of conductors to fall to the ground between pole numbers LIS 1307730 and 1307731. Molten metal from the event caused a small grass fire to start that was estimated to be approximately 3sqm in size. The 25kVA transformer was also dislodged from the pole and was hanging by the transformer leads & bolts and required replacement. Emergency services were on site and the fire was extinguished. Tree clearers were called to the site with chainsaws to assist in removing the fallen tree. | Conductor (ABC);Aluminium;Pole mounted;Transformer | 0 | 0 | 0 |  | DMA 23 | Vegetation: Trees Incident | Loss of supply;Grassfire | 26/12/2015 18:29 | 1 | Localised: less than 10 sq.m | 467 | Roadway |  | 20151230UTD_1 | Infrastructure (network-based) | -38.3634 | 145.0063 | 1 | United Energy Distribution | Report | 710 | 0.007647 | 22kV AC | Moorabbin Airport | 3937 | Red Hill | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 69 RED HILL ROAD, RED HILL SOUTH VIC 3937 |  |  | Heat |  | Conductor clashing;Earth fault;Electrical breakdown |  |  | 1 | At 1213hrs on 30/12/2015, 22kV feeder DMA 15 circuit breaker reclosed to lockout affecting 595 customers. HVABC failed midspan in Red Hill Road between "Red Hill-Cherry" substation and the tee-off to RB 7430 located in Oceanview Road. This event resulted in the 22kV conductors to arc and a three small grass fires no larger than approximately 2sqm started on the road reserve caused by the molten aluminium contacting the dry grass that were promptly extinguished. No high voltage injection or major damage was sustained and the cause was suspected to be as a result of the HV conductors failing midspan after tracking to the bare catenary cable. ESV were notified by United Energy with reference number 4209561 provided. | Conductor (ABC);Aluminium | 0 | 0 | 0 |  | DMA 15 | HVABC failed midspan. | Loss of supply;Grassfire | 30/12/2015 12:13 | 1 | Localised: less than 10 sq.m | 483 | Roadway |  | 20151230UTD_8 | Infrastructure (network-based) | -38.3949 | 145.0179 | 1 | United Energy Distribution | Report | 730 | 0.03052 | 22kV AC | Moorabbin Airport | 3937 | Red Hill South | OH Cable
Crew isolated supply and undertook repairs. | 142 GRAY STREET, SWAN HILL VIC 3585 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A customer reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV/lv pole which caused the crossarm to break and the conductors to fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 15:55 | 1 | Negligible: no ground fire | 488 | Roadway |  | 20151231PWA_2 | Infrastructure (network-based) | -35.3458 | 143.5401 | 1 | Powercor | Report | 1147 | 0.022384 | Low voltage AC (<1kV);22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Crossarm
CEOT sent fault truck to make sure all is safe and advised technical officer/DAO to investigate the incident. Fault crew attended and found the White Phase Substation Bus Low Voltage Hinged Fuse Isolator, load side conductor had partially burnt through where the clamp contacted. The fault crew bridged out the Low Voltage isolators and replaced the aluminium conductor with copper to aluminium connectors to all 3 phases. | 88 MONBULK-SEVILLE ROAD, WANDIN EAST VIC 3139 | 1012349 |  |  |  | Age |  |  | 2 | IMS 219836. Small fire reported by customer at base of pole 1012349 which was extinguished by the customer. White Phase substation LV hinged fuse isolator load side conductor partially burnt through at its connection at the D clamp. Allegedly molten metal dropped to the ground and caused a fire. No electrical protection operated - below current fuse size. | Conductor (bare);Pole (wood);Disconnector/isolator | 0 | 0 | 0 |  | ldl13 | Conductor joint failure. | Grassfire | 29/12/2015 14:45 | 1 | Localised: less than 10 sq.m | 495 | Agricultural |  | 20160103SPN_1 | Infrastructure (network-based) | -37.8273 | 145.4536 | 1 | AusNet Services Distribution | Report | 748 | 0.013965 | Low voltage AC (<1kV) | Moorabbin Airport | 3139 | Wandin East | Connection
CEOT dispatched a fault crew, arrived on site and made area safe by de-energizing the EDO fuses under a short interruption from Switch Number LD15066. The fault crew replaced the High Voltage EDO fuse tube and fuse element and restored supply. | 48 HENDERSON ROAD, YARRA GLEN VIC 3775 | 1006567 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 1 | IMS 219854. Customer reported flame/fire of equipment on pole number 1006567/ Switch number LD 433 in Henderson Road. Fault crew attended and found the road side EDO HV fuse at LD433 hung-up and arcing/on fire (candled fuse tube). High Voltage EDO fuse at LD433 protect Fuseless substation HENDERSON STEELS CK. No evidence of any other network equipment of surrounding vegetation experiencing fire damage. CFA reported to have attended. Successful Reclose on Victoria Rd ACR @ 640 am 1/1/2016 may be related to start of candled High Voltage fuse. | EDO fuse | 0 | 0 | 0 |  | cpk12 | Burnt EDO fuse tube. | Other electricity related | 42370.559 | 1 | Negligible: no ground fire | 501 | Agricultural |  | 20160103SPN_7 | Infrastructure (network-based) | -37.64 | 145.3812 | 1 | AusNet Services Distribution | Report | 760 | 0.01092 | 22kV AC | Moorabbin Airport | 3775 | Yarra Glen | Fuse
MFB put out the grass fire and repaired fault | 5 BANKSIA COURT, WEST FOOTSCRAY VIC 3012 |  |  | Heat |  | Insulator |  |  | 2 | The Aluminium Connector failed and coming into contact the roadside LV crimp to transformer isolator, the subsequent contact caused an arc to occur and resulted in a grass fire. | Disconnector/isolator | 0 | 0 | 0 |  |  | The Aluminium Connector failed and coming into contact the roadside LV crimp to transformer isolator. | Grassfire | 31/12/2015 18:45 | 1 | Localised: less than 10 sq.m | 504 | Residential |  | 20160104JEM_1 | Infrastructure (network-based) | -37.8058 | 144.8683 | 1 | Jemena | Report | 766 | 0.020051 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Connection
Crew isolated supply and undertook repairs | 83 GRAHAM STREET, NEWPORT VIC 3015 |  |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire at the incident location. On arrival the crew found that a connection in a pole mounted FOLCB had overheated causing a conduit for an u/g service cable to catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Plant/equipment | 26/12/2015 6:10 | 1 | Negligible: no ground fire | 514 | Roadway |  | 20160104PWA_2 | Infrastructure (network-based) | -37.8341 | 144.8684 | 1 | Powercor | Report | 779 | 0.012218 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Connection
Crew isolated supply and undertook repairs | 278 MORPUNG AVENUE, IRYMPLE VIC 3498 |  |  |  |  | Overheated connection |  |  | 2 | CFA reported a fire on a pole at incident location. On arrival the crew found that a connection had overheated in a pole mounted LV mains box causing the box to catch fire which resulted in a fire on the pole which also damaged a second LV mains box. The incident also resulted in a ground fire (approx. 1m x 3m) on the road reserve. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 31/12/2015 17:12 | 1 | Localised: less than 10 sq.m | 530 | Roadway |  | 20160105PWA_1 | Infrastructure (network-based) | -34.2393 | 142.1856 | 1 | Powercor | Report | 803 | 0.021223 | Low voltage AC (<1kV) | Mildura Airport | 3498 | Irymple | Connection
Crew isolated supply and undertook repairs | 7370 PRINCES HIGHWAY, TYRENDARRA VIC 3285 |  |  |  |  | Leakage |  |  | 1 | VicFire reported a fire at incident location. On arrival the crew found that a pole fire had occurred on a SWER pole causing the top of the pole to burn resulting in a ground fire (Approx. 10 sqm) on the road reserve. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 42430.0007 | 1 | Small: 10 - 1000 sq.m | 532 | Roadway |  | 20160105PWA_3 | Infrastructure (network-based) | -38.2247 | 141.753 | 1 | Powercor | Report | 807 | 0.031936 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3285 | Tyrendarra | Pole
Crew isolated supply and undertook repairs | LOT 2 CODRINGTON-ORFORD ROAD, ST HELENS VIC 3285 |  |  |  |  | Leakage |  |  | 2 | CFA reported a wire sparking and a grass fire at the incident location. On arrival the crew found evidence of tracking across 66kV insulators resulting in a ground fire (Approx. 50m x 3m) on the road reserve. The fire also caused damage to fence posts. There were no reported injuries. | Insulators | 0 | 0 | 0 |  |  | Tracking across insulator | Grassfire | 42491.2146 | 1 | Small: 10 - 1000 sq.m | 541 | Roadway |  | 20160107PWA_1 | Infrastructure (network-based) | -38.2571 | 142.0138 | 1 | Powercor | Report | 820 | 0.035913 | 66kV AC | Warrnambool Airport Ndb | 3285 | St Helens | AF Other
Crew isolated supply and undertook repairs | 103 FERGUSONS ROAD, ALLESTREE VIC 3305 | 904509 |  |  |  | Leakage |  |  | 1 | A nearby customer reported a pole sparking and wires had fallen to the ground at the incident location. On arrival the crew found that a crossarm had occurred on a 22kV pole causing the crossarm to break and fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. Following restoration the crew found that a pole fire has occurred at an adjacent pole. The crew again isolated supply and undertook repairs at this second location. There was no ground fire, no reported injuries or third party property damages at this second location. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | PLD001 | Excessive Leakage Current | Pole-top fire | 42461.9563 | 1 | Negligible: no ground fire | 555 | Roadway |  | 20160107PWA_15 | Infrastructure (network-based) | -38.2846 | 141.6483 | 1 | Powercor | Report | 2952 | 0.036486 | 22kV AC | Portland (Cashmore Airport) | 3305 | Allestree | Crossarm
Crew secured pit rim and filled space around pit with cold mix | 4 KNOLLBROOK CLOSE, HIGHTON VIC 3216 |  |  |  |  | Incorrect design |  |  | 2 | A nearby customer reported that his wife had tripped on an underground pit at the incident location. On arrival the crew found that the plastic rim of an underground pit had loosened and the lady had stepped on the pit rim and tripped as the rim dislodged, causing the lady to fall to the ground resulting in her fracturing her arm and sustaining cuts and bruises to her arms, legs and chin. | Services pit | 0 | 0 | 0 |  |  | Pit rim dislodged | Medical attention (first aid/doctor/hospital) | 31/12/2015 13:56 |  |  | 558 | Roadway |  | 20160107PWA_17 | Infrastructure (network-based) | -38.1758 | 144.3106 | 1 | Powercor | Report | 842 | 0.0061088 | Not applicable | Avalon Airport | 3216 | Highton | AF Other
Crew isolated supply and undertook repairs | 92 WESTLAKES ROAD, PORTLAND NORTH VIC 3305 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | Vicfire reported a pole fire caused a grass fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, resulting in a ground fire (Approx. 3m x 5m) on the road reserve. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 42461.4563 | 1 | Small: 10 - 1000 sq.m | 543 | Roadway |  | 20160107PWA_3 | Infrastructure (network-based) | -38.3069 | 141.5843 | 1 | Powercor | Report | 824 | 0.013729 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland North | Pole
Crew isolated supply and undertook repairs | 340 HEALES ROAD, LARA VIC 3212 |  | Working too close to overhead lines | [5 empty] | 2 | A customer reported they contacted the service line with an excavator inside the property at the incident location. On arrival the crew found the customer (Vince Tassone, Ph: 0422 399 998) was operating an excavator and contacted the LV service line to the premises, breaking the line causing it to fall to the ground. There was no ground fire. There were no reported injuries or third party property damages. Following repairs the cable was measured at 2.8m at the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Excavator contacted LV service line | No Go Zone (contact);Damage to network assets | 42401.6188 |  |  | 562 | Residential |  | 20160108PWA_1 | Infrastructure (network-based) | -38.0472 | 144.353 | 1 | Powercor | Report | 2711 | 0.0018519 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Vehicle
CEOT dispatched fault crew to make safe and investigate. BA fuse replaced and supply successfully restored. Broken fuse returned to Traralgon quarantine for inspection. | 55 DRIFFIELD ROAD, DRIFFIELD VIC 3840 | 2622721 |  |  |  | Mechanical breakdown |  |  | 2 | IMS 219918. At Bennett 17 Substation, lis 2622721, hung-up BA fuse, burnt in half. No ground fire present. | Boric acid | 0 | 0 | 0 |  | mwts14 | Burnt Boric Acid fuse tube. Equipment failure. | Other electricity related | 42583.6729 | 1 | Negligible: no ground fire | 567 | Agricultural |  | 20160108SPN_1 | Infrastructure (network-based) | -38.2943 | 146.3184 | 1 | AusNet Services Distribution | Report | 855 | 0.0089294 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Driffield | Fuse
Crew liaised with customers and security and isolated are for repair works. Security firm also increased security of site. | 114 DERRIMUT ROAD, WERRIBEE VIC 3030 |  | Theft | [5 empty] | 2 | A customer reported fluctuating low voltage at the incident location. On arrival the crew found substation doors at an indoor substation had been forced open and the removal and theft of: - Powercor earths on the transformers, HV switchgear, LV switchgear, wall mounted earth bus and other assorted equipment. - Customer LV neutrals from the LV switchgear and other. - Remnant earthing function was that provided by the incoming HV cable screen wires. The crew also found evidence of an electrical flash on one of the Customer LV neutral cables. During the Christmas period, this substation had been within an area fenced off and screened as a construction zone due to expansion works at the Werribee Plaza shopping centre. There were no reported injuries. Incident reported to Police. | Indoor | 0 | 0 | 0 |  |  | Theft | Damage to network assets | 42583.7354 |  |  | 574 | Commercial |  | 20160111PWA_4 | Infrastructure (network-based) | -37.8755 | 144.6828 | 1 | Powercor | Report | 867 | 0.014564 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | Other
An Electrical Network Operator and Work Practice representatives were dispatched to site and SBY11 was isolated and switched around to restore supply to the SBY11 customers. | 1 MITCHELLS LANE, SUNBURY VIC 3429 |  | Working too close to underground cables | [5 empty] | 1 | A contractor conducting works for Telstra which involved excavation caused the 22kV cable (SBY11) feeder to have an unsuccessful reclose and go to lockout. On attending the site, it was observed that there were what appeared to be vertical cuts and a drilled hole in the SBY11 22kV cable. Within the trench there remained a battery operated grinder and drill that along with the adjacent cable, appeared to have sustained flash marks and damage. The emergency services of Victorian Police and Ambulance Victoria attended the site with WorkSafe being notified of the incident by Victorian Police and an injured person was transported to hospital. Corner of Mitchells Land and Horne Street. | Cable | 0 | 0 | 0 |  |  | Telstra work party - cable had been damaged by what appeared to be vertical cuts and a drilled hole. | Medical attention (first aid/doctor/hospital) | 42552.616 |  |  | 582 | Commercial |  | 20160113JEM_1 | Infrastructure (network-based) | -37.5862 | 144.7207 | 1 | Jemena | Report | 1178 | 0.032041 | 22kV AC | Melbourne Airport | 3429 | Sunbury | Dug up
CEOT dispatched fault crew. Isolated supply and made safe. Top of pole cut off (approx. 450mm ) and P bracket and 9 shed clamp top insulator refitted after being cleaned and the line was restored. Check required to ensure clearances are OK for SWER angle and substation pole now that 450mm of pole at top has been removed after being burnt. | 61 TURPINS ROAD, MADALYA VIC 3971 | 2626714 |  | Precipitation;Prone to dust deposition |  | Leakage |  | Phase to earth | 2 | IMS 219982. Pole fire, was out on arrival, CFA did not attend, no ground fire. Pole fire at SWER angle Pole 2626714 McCormick P5 Turpins Rd, Madalya. Top of Pole burnt at P Bracket kingbolt of 9 shed clamp top insulator. Approximately 450mm of top of pole burnt out. Current tracking (leakage) across insulator from drizzle after long dry spell. | Pole (wood) | 0 | 0 | 0 |  | FTR12 | Current leakage (tracking) across HV insulator to wood pole caused by pollution (dust) from drizzle rain after a long dry spell of weather. | Pole-top fire | 42705.6424 | 1 | Negligible: no ground fire | 588 | Agricultural |  | 20160113SPN_2 | Infrastructure (network-based) | -38.5091 | 146.4977 | 1 | AusNet Services Distribution | Report | 887 | 0.014354 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3971 | Madalya | Pole
Crew isolated supply and inspected pole for damage. | 231-233 WOODWARD ROAD, GOLDEN SQUARE VIC 3555 |  |  | Bird |  |  |  |  | 1 | Customer reported a transformer â€œexplodedâ€ at the incident location. On arrival the crew found that two birds had caused a flashover on a 22kV fuse unit on a concrete substation pole, resulting in a ground fire (Approx. 0.5m square) on the road reserve. The fire self-extinguished. Protection operated. There were no reported injuries. | Transformer | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 42705.7708 | 1 | Localised: less than 10 sq.m | 594 | Roadway |  | 20160114PWA_1 | Infrastructure (network-based) | -36.7812 | 144.2653 | 1 | Powercor | Report | 897 | 0.0086377 | 22kV AC | Bendigo Airport | 3555 | Golden Square | Animal
MFB put out fire. | 3 LODDON AVENUE, RESERVOIR VIC 3073 | Pole no: A034555 |  |  |  | Leakage |  |  | 2 | Crossarm fire reported by MFB | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire caused by leakage and weather conditions | Pole-top fire | 14/01/2016 11:03 | 1 | Negligible: no ground fire | 608 | Residential |  | 20160115JEM_1 | Infrastructure (network-based) | -37.7236 | 145.0268 | 1 | Jemena | Report | 917 | 0.02991 | 22kV AC | Essendon Airport | 3073 | Reservoir | Crossarm
Crew isolated supply and undertook repairs | 605 BACCHUS MARSH ROAD, LOVELY BANKS VIC 3213 |  | Working too close to underground cables | [5 empty] | 2 | A contractor reported that they had contacted an underground cable at the incident location. On arrival the crew found that a contractor (Warren Communications, Contact: Paul, Ph: 0408 376 792) was undertaking excavation works and contacted a LV underground public lighting cable resulting in damage to the cable. There were no reported injuries. There was no ground fire. The contractor had undertaken DBYD enquiries for the site. | Services cable | 0 | 0 | 0 |  |  | Excavator contacted UG cable | No Go Zone (contact);Damage to network assets | 42675.4521 |  |  | 612 | Roadway |  | 20160115PWA_3 | Infrastructure (network-based) | -38.0291 | 144.3498 | 1 | Powercor | Report | 921 | 0.02901 | Low voltage AC (<1kV) | Avalon Airport | 3213 | Lovely Banks | Dug up
Crew isolated supply and undertook repairs | 725 INGLISTON ROAD, INGLISTON VIC 3342 | 30116684 |  |  |  | Mechanical breakdown;Unknown technical factor |  |  | 1 | A field crew attending an outage had patrolled the line and found nothing. Following a series of trial recloses and further substation isolations the crew found that a 12.7kV conductor had broken and had fallen to the ground. The crew also found that a ground fire (Approx. 20 sqm) had occurred on private property. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  | BMH003 | Broken SWER conductor | Grassfire | 13/01/2016 23:56 | 1 | Small: 10 - 1000 sq.m | 616 | Agricultural |  | 20160115PWA_5 | Infrastructure (network-based) | -37.6372 | 144.3002 | 1 | Powercor | Report | 12607 | 0.0054965 | 12.7kV AC (SWER) | Avalon Airport | 3342 | Ingliston | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions | 52 STATION STREET, NUNAWADING VIC 3131 | LIS No. 7031287 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Passerby called to report that a road side HV crossarm has a split and its about to fall. Following light drizzly rain the previous day, a HV intermediate crossarm fire occurred at pole No. LIS 7031287 located on the corner of Mount Pleasant Road and Station Street, Nunawading. No high voltage injection or damage was sustained following the red phase HV insulator tracking to the timber crossarm. | Crossarm (wood) | 0 | 0 | 0 |  | NW 33 | Crossarm fire due to probable insulator tracking during light drizzle. | Pole-top fire | 42705.9729 | 1 | Negligible: no ground fire | 604 | Roadway |  | 20160115UTD_3 | Infrastructure (network-based) | -37.8203 | 145.1788 | 1 | United Energy Distribution | Report | 912 | 0.010027 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Crossarm
Emergency high voltage switching was completed and the HV intermediate crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 284 WARRIGAL ROAD, OAKLEIGH SOUTH VIC 3167 | LIS No. 2334974 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Caller reports there is a crossarm fire on a pole in Warrigal Road on the corner of Bossington Street. During light drizzly rain, a pole fire occurred at a HV intermediate crossarm on pole No. LIS 2334973 located outside Bowens Timber Yard in Warrigal Road on the corner of Bossington Street, Oakleigh South. | Crossarm (wood) | 0 | 0 | 0 |  | OR 23 | Insulator tracking occurred following light drizzle. | Pole-top fire | 14/01/2016 10:41 | 1 | Negligible: no ground fire | 610 | Roadway |  | 20160115UTD_7 | Infrastructure (network-based) | -37.9163 | 145.0842 | 1 | United Energy Distribution | Report | 919 | 0.019976 | 11kV AC | Moorabbin Airport | 3167 | Oakleigh South | Crossarm
Crew isolated supply and undertook repairs | 300 HENKES ROAD, MUMBANNAR VIC 3304 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a SWER pole which burnt the top of the pole. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42705.3292 | 1 | Negligible: no ground fire | 633 | Roadway |  | 20160118PWA_05 | Infrastructure (network-based) | -37.9528 | 141.1825 | 1 | Powercor | Report | 961 | 0.034619 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3304 | Mumbannar | Pole
Crew isolated supply and arranged repairs | 15 HILLVIEW ROAD, MERBEIN WEST VIC 3505 |  | Working too close to underground cables | [5 empty] | 2 | A nearby customer reported an excavator dug up an underground cable at the incident location. On arrival the crew found that an excavator (Operated by Rob Anstis Contracting, Ph: 0427101114, PO Box 138, Mildura Plaza Centre, 3501) was trenching water pipes in the road reserve and made contact with a LV underground service cable, causing damage to the cable. There were no reported injuries. The contractor claimed to have made DBYD enquiries. | Services cable | 0 | 0 | 0 |  |  | Excavator contacted LV UG cable | No Go Zone (contact);Damage to network assets | 13/01/2016 13:30 |  |  | 635 | Roadway |  | 20160118PWA_07 | Infrastructure (network-based) | -34.1506 | 141.9986 | 1 | Powercor | Report | 963 | 0.011375 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Merbein West | Dug up
Crew isolated supply and checked for damages | 396 CANNING STREET, CARLTON NORTH VIC 3054 |  |  | Wind |  |  |  |  | 1 | Nearby customers reported that a scaffold had been blown down in strong winds and is contacting wires at the incident location. On arrival the crew found that a scaffold had been blown down in strong winds and was resting on the low voltage overhead conductors. Protection had operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Wind | No Go Zone (contact) | 13/01/2016 18:08 |  |  | 641 | Roadway |  | 20160118PWA_11 | Infrastructure (network-based) | -37.788 | 144.9748 | 1 | CitiPower | Report | 974 | 0.022722 | Low voltage AC (<1kV) | Essendon Airport | 3054 | Carlton North | Other
CEOT dispatched a fault crew to investigate, make safe and repair. The DAO arrived at site at approximately 7.00am (15/01/2016) to find pole 12-10911 had already been repaired. It appears the pole fire started at the top of the pole. The CEOT Dispatcher informed the DAO that the contractors that attended the site on the 14/01/2016 cut the damaged part of the pole off and moved the 66kV & 22kV crossarms down to suit. There were small chunks of burnt wood around the base of the pole. No damage was caused to the nature strip and or surrounding property. All conductor clearances to ESMS requirements. | 1 POWER ROAD, BAYSWATER VIC 3153 | 1210911 |  | Precipitation |  | Leakage |  |  | 2 | IMS 220040. Fire Brigade reported a fire on a pole. CEOT reported that there was a pole fire on the 66/22kV pole. The cause of the incident was current leakage from a 66kV disk insulator to the crossarm eye-bolt causing the pole top to burn. The leakage was due to dust pollution on the insulator. | Pole (wood) | 0 | 0 | 0 |  | bwr22 | 66kV insulator current leakage to crossarm eye bolt. | Pole-top fire | 14/01/2016 9:45 | 1 | Negligible: no ground fire | 630 | Commercial |  | 20160118SPN_06 | Infrastructure (network-based) | -37.8438 | 145.2708 | 1 | AusNet Services Distribution | Report | 1436 | 0.020354 | 22kV AC;66kV AC | Moorabbin Airport | 3153 | Bayswater | Pole
CEOT sent a fault crew to investigate, make safe and repair. Patch of burnt grass at base of pole was observed. The tree was removed by the CFA. The fault crew checked the condition of the conductors for any damage and reported no other damage occurred. Supply was restored. | 815 YARRAGON-SHADY CREEK ROAD, YARRAGON VIC 3823 | 2202181 |  | Wind;Fallen |  |  |  | Phase to earth |  | IMS 220009. CEOT received job from Vic Fire. Wire down. Possible grass fire in vicinity. Final report: A tree clearer subcontractor to Asplundh engaged by AusNet Services was driving along the road in storm conditions when he saw a large tree limb fall onto a 22kV conductor bringing the conductor down near the ground. The tree clearer observed some sparking and burning of branches and a small ground fire. The HV conductor then sprung back up into its position very soon after some branch burning took place. The tree clearer reported the fire to the CFA and CEOT. The fault crew arrived on site and observed a burnt tree branch and a burnt grass area of 6 sq. metres around the base of the pole. A tree had brought down the HV 3/2.75 Sc Az conductor. The tree is located in the public road reserve and was outside the vegetation clearance space. | Conductor (bare) | 0 | 0 | 0 |  | moe22 | Vegetation: Trees Incident | Grassfire | 13/01/2016 19:15 | 1 | Localised: less than 10 sq.m | 636 | Agricultural |  | 20160118SPN_08 | Infrastructure (network-based) | -38.1404 | 146.078 | 1 | AusNet Services Distribution | Report | 966 | 0.0012303 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon | Trees
A Downer construction crew attended and replaced 4 bays of overhead conductors before supply was restored after 3 x 315amp HRC fuses were replaced at "Whitehead-Wilson" substation. | 15 WHITEHEAD STREET, BLAIRGOWRIE VIC 3942 | LIS NO. 1304278 |  | Heat |  | Conductor clashing |  |  | 1 | Caller reports that a sparking pole has caused a fire on the nature strip. The CFA were on site and the fire is out. During very hot and windy conditions, conductors were clashing and molten metal following a LV copper conductor failing to the ground ignited a 10sqm section of the nature strip. The CFA were in attendance and extinguished the grass fire outside 15 Whitehead Street, Blairgowrie near pole No. LIS 1304278. | Conductor (bare);Copper | 0 | 0 | 0 |  |  | During strong winds. conductors were clashing. | Grassfire | 31/12/2015 17:30 | 1 | Localised: less than 10 sq.m | 629 | Roadway |  | 20160118UTD_01 | Infrastructure (network-based) | -38.3646 | 144.7735 | 1 | United Energy Distribution | Report | 951 | 0.013845 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Conductor
Made safe | 7 GORDON STREET, FOOTSCRAY VIC 3011 |  |  | Heat;Cold |  | Leakage |  |  | 1 | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire due to leakage | Pole-top fire | 14/01/2016 15:43 | 1 | Negligible: no ground fire | 648 | Residential |  | 20160119JEM_02 | Infrastructure (network-based) | -37.7881 | 144.8903 | 1 | Jemena | Report | 987 | 0.035877 | 22kV AC | Essendon Airport | 3011 | Footscray | Crossarm
Crew isolated supply and arranged repairs | 18 VINCENT CRESCENT, WERRIBEE VIC 3030 |  | Vehicle | [5 empty] | 2 | VicFire reported that a wire had come down and they have responded to a fire at the incident location. On arrival the crew found that a LV service cable had been contacted by an unknown vehicle causing the cable to break and fall to the ground resulting in a ground fire (Approx. 1.2m by 4.0m) on the nature strip. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | Grassfire | 18/01/2016 12:22 | 1 | Small: 10 - 1000 sq.m | 653 | Roadway |  | 20160119PWA_01 | Infrastructure (network-based) | -37.8903 | 144.6582 | 1 | Powercor | Report | 992 | 0.02436 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
Crew isolated supply and undertook repairs | 86 DOUGLAS LANE, ILLOWA VIC 3282 |  |  |  |  | Fuse failed to eject |  |  | 2 | A customer reported arcing and smoke on a pole at the incident location. On arrival the crew found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse did not drop out | Pole-top fire | 13/01/2016 11:47 | 1 | Negligible: no ground fire | 655 | Agricultural |  | 20160119PWA_03 | Infrastructure (network-based) | -38.3241 | 142.3787 | 1 | Powercor | Report | 994 | 0.039383 | 22kV AC | Warrnambool Airport Ndb | 3282 | Illowa | Fuse
A LEI and faults truck attended and commenced an investigation. The LEI tested between an independent earth and the water taps and measured a voltage rise of up to 8v. The faults crew checked all service connections and no fault could be identified. The LEI left supply on after arranging for the circuit to be balanced or the upgrading of the reticulation which is approximately 10 bays away from the transformer. It was noted the copper conductors were 7/080 and may require a system augmentation. | 83 BEAUNA VISTA DRIVE, RYE VIC 3941 |  |  |  |  | Out of balance load |  | Phase to earth | 2 | REC Jarrod called to report the customer is getting tingles from the taps. He has turned off the main switch and disconnected the MEN after recording 4 to 5 volts between the earth and neutral. The occupier was receiving slight electric shocks between the water taps and the laundry sink and contacted a REC to investigate. The REC measured a voltage on the water pipes and isolated supply before contacting the United Energy faults and emergencies call centre. | No failed asset | 0 | 0 | 0 |  |  | Possible LV circuit re-balancing or overhead reticulation upgrade may be necessary. | Minor shock | 14/01/2016 11:30 |  |  | 649 | Residential |  | 20160119UTD_01 | Infrastructure (network-based) | -38.3791 | 144.8338 | 1 | United Energy Distribution | Report | 986 | 0.040277 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | Rye | Conductor
Crew checked assets for damage - none found | 4484-4550 PORTLAND-CASTERTON ROAD, MERINO VIC 3310 |  |  | Bird |  |  |  |  | 2 | VicFire reported a grass fire at the incident location. On arrival the crew found that a grass fire (Approx. 20m x 50m) had been extinguished by the CFA around the base of a 22kV ACR pole. At first inspection no obvious cause for the fire was found. Supply had not been interrupted and all hardware appeared intact. The attending linesman also noted a number of feathers on the ACR but no bird carcass was found. Later the crew were speaking with one of the CFA personnel who reported seeing a magpie sitting on the ACR when they first arrived on site. The bird appeared stunned and only flew away sometime later. It is likely that the cause was a bird related flashover on the ACR pole. There were no reported injuries. | ACR/OCR | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 19/01/2016 6:54 | 1 | Small: 10 - 1000 sq.m | 658 | Roadway |  | 20160120PWA_01 | Infrastructure (network-based) | -37.6902 | 141.5408 | 1 | Powercor | Report | 998 | 0.0061667 | 22kV AC | Hamilton Airport | 3310 | Merino | Animal
Crew inspected lines and repairs were arranged | LOT 13 HENSHAWS ROAD, ST HELENS VIC 3285 |  |  | Precipitation;Prone to salt deposition |  |  |  |  | 1 | VicFire reported a pole fire at the inciden location. On arrival the crew found a that tracking had occurred across 66kV insulators in misty weather resulting in ground fires in two locations (Approx 60x15m total area) on the road reserve. Protection operated. There were no reported injuries. | Insulators | 0 | 0 | 0 |  |  | Misty weather conditions and salt prone area | Grassfire | 19/01/2016 5:21 | 1 | Small: 10 - 1000 sq.m | 661 | Roadway |  | 20160120PWA_03 | Infrastructure (network-based) | -38.2737 | 142.0316 | 1 | Powercor | Report | 1002 | 0.0047558 | 66kV AC | Warrnambool Airport Ndb | 3285 | St Helens | AF Other
Refer also to UE incident report No. 20160115UTD_8. Following a pole fire that occurred on 14/01/2016 in Singer Avenue, Glen Waverley, LV parallels were installed to restore supply to customers from "Singer-York" substation pending the substation pole replacement. During warm weather with peak energy usage, the LV red phase transformer lead at "Moira-Campbell" substation failed that caused molten metal to fall to the ground and a nature strip fire occurred that was estimated to be 16sqm in size. A nature strip tree was also charred due to the grass fire near pole No. LIS 0605133. A faults truck attended and repaired the LV conductors before the LV red phase 315amp HRC fuse on the north circuit of "Moira-Campbell" substation was replaced that restored supply to customers. The cause was overload with the LV parallels installed. | 4 MOIRA GROVE, GLEN WAVERLEY VIC 3150 | LIS No. 0605133 |  | Heat |  | Electrical overload |  |  | 1 | A small numbers of customers supplied from "Singer-York" and "Moira-Campbell" substations advised of they have lost their electricity supply. During warm conditions with a strong north wind, customers supplied from "Singer-York" and "Moira-Campbell" substations called the United Energy faults and emergencies call centre advising they have an electricity outage. | Conductor (bare);Aluminium;Connector/termination | 0 | 0 | 0 |  | GW 11 | The cause was overload with the LV parallels installed between the two substations. | Grassfire | 18/01/2016 18:15 | 1 | Small: 10 - 1000 sq.m | 660 | Roadway |  | 20160120UTD_01 | Infrastructure (network-based) | -37.8697 | 145.1719 | 1 | United Energy Distribution | Report | 1000 | 0.036781 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Glen Waverley | Conductor
Made safe | 9 EDWARD STREET, MACLEOD VIC 3085 |  |  | Heat;Cold |  | Leakage |  |  |  | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire caused by hot weather followed by drizzle. | Pole-top fire | 20/01/2016 9:14 | 1 | Negligible: no ground fire | 679 | Residential |  | 20160121JEM_01 | Infrastructure (network-based) | -37.7256 | 145.0792 | 1 | Jemena | Report | 1022 | 0.037043 | 22kV AC | Essendon Airport | 3085 | Macleod | Crossarm
Crew isolated supply and arranged repairs | 430 OLD KERANG ROAD, KERANG VIC 3579 |  |  | Bird |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival the crew found that a pelican had contacted a 22kV line and fallen to the ground resulting in a ground fire (Approx. 10m x 5m) on the road reserve. The resulting fault current caused a 22kV bridge, adjacent to the pelican contact site, to fail also resulting in a ground fire (Approx. 10m x 5m) also on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 19/01/2016 16:03 | 1 | Small: 10 - 1000 sq.m | 680 | Roadway |  | 20160121PWA_07 | Infrastructure (network-based) | -35.7785 | 143.8892 | 1 | Powercor | Report | 1024 | 0.0081782 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | Animal
Crew isolated supply | ALL SAINTS, 94-100 FAWTHROP STREET, PORTLAND VIC 3305 |  |  |  |  | Unknown technical factor |  |  | 1 | Vic Fire reported an exploded junction box and fire at the incident location. On arrival the crew found that a customers LV supply pillar had faulted and was fire damaged. Protection operated. There was no ground fire. There were no reported injuries. | Customer installation | 0 | 0 | 0 |  |  | Cause not determined | Plant/equipment | 42136.1146 |  | Negligible: no ground fire | 685 | Commercial |  | 20160121PWA_11 | Infrastructure (network-based) | -38.3588 | 141.5911 | 1 | Powercor | Report | 1029 | 0.0060313 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
Crew isolated supply and undertook repairs. | 38 CRAIG AVENUE, WARRACKNABEAL VIC 3393 | 30086721 |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the top of the pole and cross arm. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. (This incidents was found during OMS checks for additional fire incidents) | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | HSM005 | Pole fire | Pole-top fire | 29/12/2015 9:26 | 1 | Negligible: no ground fire | 695 | Roadway |  | 20160122PWA_08 | Infrastructure (network-based) | -36.2501 | 142.3884 | 1 | Powercor | Report | 1048 | 0.031275 | 22kV AC | Horsham Aerodrome | 3393 | Warracknabeal | Pole
Crew isolated supply and undertook repairs. | 35 PETERING STREET, MINYIP VIC 3392 |  |  |  |  | Mechanical breakdown |  |  | 1 | A customer reported a wire down at the above location. On arrival the crew found that a LV service had broken at the POA end, falling to the ground and resulting in a ground fire (Approx. 0.5m x 0.5m) on private property. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Broken LV service conductor | Grassfire | 30/12/2015 16:33 | 1 | Localised: less than 10 sq.m | 697 | Roadway |  | 20160122PWA_10 | Infrastructure (network-based) | -36.456 | 142.5882 | 1 | Powercor | Report | 1051 | 0.016644 | Low voltage AC (<1kV) | Horsham Aerodrome | 3392 | Minyip | Conductor
Crew isolated supply and undertook repairs. | 76 SOUTH BOUNDARY ROAD, KYABRAM VIC 3620 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the top of the pole and cross arm. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 31/12/2015 12:15 | 1 | Negligible: no ground fire | 700 | Agricultural |  | 20160122PWA_13 | Infrastructure (network-based) | -36.3284 | 145.1022 | 1 | Powercor | Report | 1055 | 0.036894 | 22kV AC | Shepparton Airport | 3620 | Kyabram | Pole
Emergency high voltage switching was completed and the HV strain crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 7 STRACHANS ROAD, MORNINGTON VIC 3931 | LIS No. 1101409 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Report of a broken crossarm in Strachans Road, Mornington. During drizzly rain, a pole fire occurred at a HV strain crossarm on pole No. LIS 1101409 located in Strachans Road, Mornington south of "Strachans-Esplanade" substation. | Crossarm (wood) | 0 | 0 | 0 |  | MTN 34 | HV insulator or disc tracking caused the crossarm fire. The pole is in close proximity to Port Phillip Bay and salt borne contaminants may have been a contributing factor. | Pole-top fire | 20/01/2016 11:57 | 1 | Negligible: no ground fire | 686 | Roadway |  | 20160122UTD_01 | Infrastructure (network-based) | -38.2303 | 145.0272 | 1 | United Energy Distribution | Report | 1033 | 0.010407 | 22kV AC | Moorabbin Airport | 3931 | Mornington | Pole
Fault crew isolated the feeder and made safe. The fault crew attempted to restore the 22kV line, however could not locate the cause of the feeder trip during the night hours. Approximately five hours were spent searching for the fault, to no avail. The search was called off at 4am on the 14.1.16. A helicopter patrol resumed the search later that morning and took aerial photos of the area and confirmed that blackening marks were present on the surge arrestor. A team was put together to replace the surge arrestor on the Thursday Morning of 14.01.16. | 358 ELEVEN MILE CREEK ROAD, GLENROWAN WEST VIC 3675 | 3909514 |  | Lightning |  | Leakage |  | Phase to earth | 1 | IMS220010. CEOT dispatched a fault crew to make safe and investigate. CFA and Police where in attendance. At pole 3909514 evidence of a fire was present in the form of a burnt area surrounding the pole site, approximately 580msq in size. A surge arrestor on the 22kV cable head pole displayed signs of blackening. The ACR tripped. Lightning activity in area at the time of the incident. | Surge diverter | 0 | 0 | 0 |  | WN6 | A surge arrestor on the 22kV cable head pole displayed signs of blackening. Lightning activity in area at the time of the incident. Insulator Pollution. | Grassfire | 13/01/2016 8:55 | 1 | Small: 10 - 1000 sq.m | 705 | Agricultural |  | 20160124SPN_02 | Infrastructure (network-based) | -36.5173 | 146.1519 | 1 | AusNet Services Distribution | Report | 1062 | 0.030102 | 22kV AC | Wangaratta Aero | 3675 | Glenrowan West | Lightning
CEOT dispatched a fault crew to make safe and repair. Faulty FOLCB was replaced with a new 250 Amp Krone Box (FSD) with 160 Amp fuses (upgraded current capacity). | 39 WOODSIDE BEACH ROAD, WOODSIDE VIC 3874 | 2612758 |  |  |  | Electrical overload;Overheated connection |  |  | 2 | IMS 220166. LV pole box burnt out and melted on substation pole. It was observed that approximately 10cm x 10cm of grass was burnt at the base of the pole. The cause of the fault was diagnosed as an Fused Overhead Line Connection Box (FOLCB) with 3 x underground cables and open wire feeding the Caravan Park at full Capacity. Primary fault cause was electrical overload. No LV fuses blew. | Connection box | 0 | 0 | 0 |  | ftr23 | Burnt out FOLCVB at pole end - electrical overload. | Grassfire | 24/01/2016 8:45 | 1 | Localised: less than 10 sq.m | 712 | Residential |  | 20160124SPN_09 | Infrastructure (network-based) | -38.5317 | 146.8817 | 1 | AusNet Services Distribution | Report | 1123 | 0.012931 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3874 | Woodside | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the two affected customers. | 1565 POINT NEPEAN ROAD, ROSEBUD WEST VIC 3940 | LIS No. 13001108 |  | Precipitation |  | HV injection |  |  | 2 | Emergency services report that a car has struck a pole in Point Nepean Road, Rosebud. At 5.14AM during light drizzle, a vehicle driver appeared to have lost control and struck a timber pole outside 1567 Point Nepean Road, Rosebud West - LIS No. 13001108. The timber HV/LV pole with intermediate construction was damaged and required replacement. The occupier from 1565 Point Nepean Road, reported to the faults crew that light globes had exploded when the power went off. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from the red phase conductor at "Nepean-Percival" substation. The LEI confirmed that a high voltage injection occurred (MOR 1602) affecting only the 2 customers from units 3 & 4, 1565 Point Nepean Road that sustained minor damage. | Pole (wood) | 0 | 0 | 0 |  | RBD 14 | A vehicle driver appeared to have lost control and struck a timber pole. | HV injection;Loss of supply | 23/01/2016 5:14 |  |  | 718 | Roadway |  | 20160125UTD_06 | Infrastructure (network-based) | -38.3626 | 144.8809 | 1 | United Energy Distribution | Report | 1080 | 0.003735 | 22kV AC | Moorabbin Airport | 3940 | Rosebud West | Vehicle
Made safe and repaired supply to the pole. | 96-122 RUTHERFORD ROAD, VIEWBANK VIC 3084 |  |  |  |  | Neutral fault |  |  | 2 | Animal (dog) received minor shock from rubbing against pole in Viewbank Reserve (public reserve). | Public infrastructure | 0 | 0 | 0 |  |  | Service connection to pole | Shock to livestock, pet or companion animal | 22/01/2016 19:40 |  |  | 752 | Public space |  | 20160129JEM_03 | Infrastructure (network-based) | -37.7411 | 145.0937 | 1 | Jemena | Report | 1133 | 0.0024375 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Viewbank | AF Other
Isolated and repaired crossarm & pole. | 31 VICTORIA STREET, FLEMINGTON VIC 3031 |  |  | Heat;Cold |  | Leakage |  |  | 2 | Pole fire | Pole top | 0 | 0 | 0 |  |  | Pole top fire | Pole-top fire | 22/01/2016 8:50 | 1 | Negligible: no ground fire | 753 | Residential |  | 20160129JEM_04 | Infrastructure (network-based) | -37.7874 | 144.9337 | 1 | Jemena | Report | 1134 | 0.0050914 | 11kV AC | Essendon Airport | 3031 | Flemington | Pole
Crew arranged replacement of LA units | 1096 WEBB ROAD, TIMMERING VIC 3561 |  |  | Lightning |  |  |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that lightning had struck a 22kV Regulator structure the previous day, causing damage to two 22kV LA units. On the day in question a ground fire occurred around the regulator structure (Approx. 43m X 2m) on the road reserve. The crew were unable to determine the cause of the fire however it is likely that the fire was caused by the lightning damaged LA units. There were no reported injuries. | Surge diverter | 0 | 0 | 0 |  |  | Lightning strike damage LA units | Grassfire | 42371.8194 | 1 | Small: 10 - 1000 sq.m | 765 | Roadway |  | 20160202PWA_02 | Infrastructure (network-based) | -36.3577 | 144.9205 | 1 | Powercor | Report | 1163 | 0.019104 | 22kV AC | Shepparton Airport | 3561 | Timmering | Lightning
Fault crew attended and DAO advised. The fault crew isolated supply and made safe. An underground crew attended and a straight joint and re-terminated the dropper HV ABC segment. | 80 WANDIN CREEK ROAD, WANDIN EAST VIC 3139 | 1005488 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | IMS 220287. At a HV overhead to underground interface pole (hybrid tee-off junction pole) a tree branch fell onto the portion of the overhead HV ABC which is not supported by a catenary at the pole which resulted in a blown 35 sq. mm HV ABC termination elbow. It is believed a phase to earth fault occurred at the HV ABC and a flashover damaged adjacent phases. A fire was observed in the vicinity on the side of the road - 3m x 1.5m in size. No other damage occurred and no fire services were required. Electrical protection operated - Boric Acid fuse operated at LD153 SWCHFUSE, 25E POLE:104764. | Conductor (ABC) | 0 | 0 | 0 |  | wyk12 | Vegetation: Trees Incident | Grassfire | 42371.7951 | 1 | Localised: less than 10 sq.m | 763 | Agricultural |  | 20160202SPN_01 | Infrastructure (network-based) | -37.8001 | 145.469 | 1 | AusNet Services Distribution | Report | 1162 | 0.0119 | 22kV AC | Moorabbin Airport | 3139 | Wandin East | Trees
Emergency high voltage switching was completed and the HV strain crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 2 MILL STREET, ASPENDALE VIC 3195 | LIS No. 3303517 |  | Lightning |  | Electrical breakdown |  |  | 1 | At 1527hrs on 28/01/2016, ACR FS 7714 located in Mount View Street reclosed to lockout affecting 116 customers. A customer called to advise that a pole caught fire on the corner of Mill and Pine Streets and the crossarm exploded and is now on the ground. During stormy conditions, it appears lightning struck a HV strain crossarm outside 2 Mill Street, Aspendale on pole No. LIS 3303517. The footpath side HV conductor remained attached to a burnt section of the timber crossarm, that failed at the crossarm brace causing it to fall onto the LV crossarm. The faults crew requested a LEI to attend and check premises for damage. The LEI attended and confirmed that a HVI did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | MC 02 | Probable lightning struck HV crossarm. | Pole-top fire;Loss of supply | 28/01/2016 15:27 | 1 | Negligible: no ground fire | 769 | Roadway |  | 20160203UTD_01 | Infrastructure (network-based) | -38.0133 | 145.0942 | 1 | United Energy Distribution | Report | 1167 | 0.014539 | 22kV AC | Moorabbin Airport | 3195 | Aspendale | Lightning
A faults crew completed emergency switching and the pole type substation was isolated and LV parallels installed to restore supply to customers in the area. A Downer construction crew was called in to commence repairs and the 200kVA transformer was replaced along with the damaged electrical infrastructure at the pole type substation. A oil spill kit was also installed at the base of the substation in accordance with environmental procedures. Traffic control was required to complete the rectification work safely and the HV bridges on the tee-off pole were broken and an Access Authority issued. Upon completion of the rectification work, the boric acid HV fuses were replaced after they had earlier operated. | 20 CHENIER STREET, RYE VIC 3941 | LIS No. 1318399 |  | Precipitation |  | Corrosion;Overheated connection |  |  | 1 | Per CFA - Transformer is on fire and the power is out to the area. A transformer fire occurred at "Chenier-Belinda" pole type substation located opposite 20 Chenier Street, Rye at concrete pole No. LIS 1318399 following light early morning rain. The CFA were in attendance and extinguished a grass fire that started when hot oil from the 200kVA transformer spilled onto the ground. A small tee-tree also caught fire. | Boric acid;Pole mounted;Transformer | 0 | 1 | 0 |  | STO 21 | The cause is undetermined but could be attributed to sea borne contaminants due to the location to Bass Strait or a loose connection at a transformer bushing. | Pole-top fire;Loss of supply;Grassfire | 29/01/2016 4:03 | 1 | Localised: less than 10 sq.m | 770 | Roadway |  | 20160203UTD_02 | Infrastructure (network-based) | -38.3816 | 144.7913 | 1 | United Energy Distribution | Report | 1168 | 0.011431 | 22kV AC | Avalon Airport | 3941 | Rye | AF Other
MFB put fire out and supply was isolated. | 23-25 LARA WAY, CAMPBELLFIELD VIC 3061 | A132362 | Blown detritus | Wind |  |  |  |  | 1 | Air Conditioner metal tubing contacted the 66KV causing a grass and fence fire. | Conductor (bare) | 0 | 0 | 0 |  | SMTS-SSS | Air Conditioner tubing contacted the 66KV. | Grassfire | 42402.6625 | 1 | Small: 10 - 1000 sq.m | 777 | Industrial |  | 20160204JEM_01 | Infrastructure (network-based) | -37.657 | 144.9676 | 1 | Jemena | Report | 2970 | 0.036832 | 66kV AC | Essendon Airport | 3061 | Campbellfield | Other
The attending Fault Crew replaced the service cable, and also replaced the pole mounted FOLCB to suit the new ABC cable. The installation was tested by the attending L.E.I and zero volts were recorded on the installation neutral bar at the main switchboard and the water piping system, and between the points where the person received the electric shock Voltage tests between an independent earth and various points of the electrical installation, including the M.E.N. and metallic water pipe system and the distribution assets, identified a constant voltage 0 Volts. â€¢ An NST test carried out by LEI indicated a Pass result. â€¢ A clip on amp meter tong test on the water pipe indicated Zero amps flowing in the earthing system. The Installation was left ON supply. | 49 BRANTOME STREET, GISBORNE VIC 3437 |  |  |  |  | Corrosion |  | Phase to earth | 2 | The Plumbing Contractor Mr Harvey was cutting a water pipe when he received an electric shock by making simultaneous contact with his hands on the metallic water pipe on both sides of his pipe cut, whilst kneeling on the floor. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a corroded neutral screen conductor near the reticulation service pole. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 20 Volts on the water piping system. | Neutral screen | 0 | 0 | 0 |  |  | A corroded service neutral screened conductor located near the pole end of the service. | Minor shock | 23/09/2015 16:00 |  |  | 791 | Residential |  | 20160204PWA_10 | Infrastructure (customer connection) | -37.4888 | 144.5896 | 1 | Powercor | Report | 1199 | 0.011616 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | OH Cable
Crew isolated supply for REC to undertake repairs | 76 ARGYLL CIRCUIT, MELTON WEST VIC 3337 |  | Unauthorised work | [5 empty] | 2 | A customer reported no supply andf that there was digging for plumbing works next door to the incident location. On arrival the crew found that a LV UG customer mains cable had been contacted and damaged by a plumbing contractor (MIDNIGHT PLUMBING SERVICES ph. 03 9747 8587). The plunbing contractor had then repaired the damage and backfilled the excavation. The crew also found that the fuse on the LV pillar supplying the cable was removed during the repair work by the plumbing contractor. There were no reported injuries. | Customer installation | 0 | 0 | 0 |  |  | Interference with Supply assets | Damage to network assets | 42431.5389 |  |  | 802 | Residential |  | 20160205PWA_02 | Infrastructure (network-based) | -37.6723 | 144.5544 | 1 | Powercor | Report | 1215 | 0.010123 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Dug up
CEOT dispatched a fault crew to isolate, make safe and repair. The 6k EDO fuse was replaced and all supply restored. No damage to assets. | 192 ROSS LANE, CUDGEWA VIC 3705 | 5236025 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 220321. EDO fuse had hung-up and candled. The top of the EDO fuse holder fell to the ground. No fire on the ground. Green grass around pole. Base of holder remained in bottom jaws of EDO unit. | EDO fuse | 0 | 0 | 0 |  | wots24 | EDO fuse tube candled. Equipment failure. | Other electricity related | 42462.3681 | 1 | Negligible: no ground fire | 800 |  |  | 20160205SPN_06 | Infrastructure (network-based) | -36.1495 | 147.7873 | 1 | AusNet Services Distribution | Report | 1213 | 0.0027535 | 22kV AC | Wangaratta Aero | 3705 | Cudgewa | Fuse
The attending Powercor Fault Crew reterminated the existing O/H Service Neutral conductor and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, following retermination of the O/H Service Neutral conductor confirmed Zero Volts under normal load conditions. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H service cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 74 SHEEDY ROAD, GISBORNE VIC 3437 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Mrs Malanie Lye received an electric shock while operating the rear garden tap when she made simultaneous contact with her hand on the metal tap while standing bare footed on the wet lawn. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H service neutral conductor termination at the clamp at the point of connection to the reticulation conductors, causing a high impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 15 Volts on the water piping system and between the points of contact. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | Corroded O/H service neutral conductor termination at the clamp at the point of connection to the reticulation conductors. | Minor shock | 17/10/2015 19:20 |  |  | 803 | Residential |  | 20160208PWA_01 | Infrastructure (customer connection) | -37.494 | 144.6 | 1 | Powercor | Report | 1216 | 0.0076898 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Connection
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, the distribution assets and between the points of contact, identified Zero Volts following replacement of the O/H Service Cable. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 77 HARVEY ROAD, ST LEONARDS VIC 3223 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Darren King of Programmed Maintenance Services was assisting with the repair of a leak at the Water Main connection located in the Road Reserve outside 50 Harvey Road St Leonards when he received an electric shock as he made simultaneous contact with his hand on the copper water main and his other hand on the ground around the excavation. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Service Neutral Conductor of the O/H Neutral Screen Service Cable as the cause of the high impedance associated with the return path of the neutral current. The corrosion of the O/H Service Neutral Conductor resulted from water entering the outer insulation via a small perforation in the cable sheath, the cause of which was not able to be determined. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 24 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | Corroded Service Neutral Conductor of the O/H Neutral Screen Service Cable. | Minor shock | 42166.4167 |  |  | 818 | Residential |  | 20160208PWA_14 | Infrastructure (network-based) | -38.1666 | 144.7125 | 1 | Powercor | Report | 1233 | 0.012799 | Low voltage AC (<1kV) | Avalon Airport | 3223 | St Leonards | OH Cable
Made safe | 24 STEELE CREEK DRIVE, KEILOR EAST VIC 3033 |  |  |  |  | Mechanical breakdown |  |  | 2 | The red and blue phase tappet wedges failed by separation of the metal contacts and the main wedge housing. This in turn resulted in the tensioning mechanism of the wedge becoming ineffective. As a result the electrical contact integrity of the wedge was compromised resulting initially of an electrical arc, which quickly escalated into a fire within the pillar. | LV Pillar | 0 | 0 | 0 |  |  | The red and blue phase tappet wedges failed by separation of the metal contacts and the main wedge housing. This in turn resulted in the tensioning mechanism of the wedge becoming ineffective. As a result the electrical contact integrity of the wedge was compromised resulting initially of an electrical arc. | Other electricity related | 19/12/2015 14:24 | 1 | Negligible: no ground fire | 822 | Residential |  | 20160209JEM_01 | Infrastructure (network-based) | -37.7395 | 144.8803 | 1 | Jemena | Report | 1239 | 0.021334 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | Connection
Made safe and removed tree branch | 552 BARRY ROAD, COOLAROO VIC 3048 |  |  | Fallen |  |  |  |  | 2 | Private tree branches at rear of property contacted overhead conductors caused branches to burn. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Other vegetation | 24/12/2015 11:42 | 1 | Negligible: no ground fire | 823 | Residential |  | 20160209JEM_02 | Infrastructure (network-based) | -37.6642 | 144.9274 | 1 | Jemena | Report | 1240 | 0.02764 | 22kV AC | Essendon Airport | 3048 | Coolaroo | Trees
Made safe | 29-31 LAKESIDE AVENUE, RESERVOIR VIC 3073 |  |  | Bird |  |  |  |  | 2 | Bird nest on top of distribution transformer caught fire | Pole mounted | 0 | 0 | 0 |  |  | Bird Incident | Other vegetation | 27/08/2015 17:00 | 1 | Negligible: no ground fire | 824 | Industrial |  | 20160209JEM_03 | Infrastructure (network-based) | -37.7096 | 144.9879 | 1 | Jemena | Report | 5514 | 0.0415 | 22kV AC | Essendon Airport | 3073 | Reservoir | Animal
Crew isolated supply and undertook repairs | 51 ARGYLL CIRCUIT, MELTON WEST VIC 3337 |  | Working too close to underground cables | [5 empty] | 2 | A customer reported that he had damaged an underground wire at the incident location. On arrival the crew found that a customer was excavating on his property and contacted a LV underground public lighting cable causing damage to the cable. There were no reported injuries. The customer had undertaken DBYD enquiries. | Services cable | 0 | 0 | 0 |  |  | Contact with underground cable | No Go Zone (contact);Damage to network assets | 23/01/2016 21:28 |  |  | 825 | Residential |  | 20160209PWA_02 | Infrastructure (network-based) | -37.6724 | 144.5577 | 1 | Powercor | Report | 1242 | 0.0067778 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Dug up
Crew isolated supply and undertook repairs | 105 SMITH ROAD, KOROOP VIC 3579 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the top of the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 31/01/2016 14:59 | 1 | Negligible: no ground fire | 840 | Agricultural |  | 20160209PWA_10 | Infrastructure (network-based) | -35.7492 | 144.052 | 1 | Powercor | Report | 1262 | 0.025685 | 22kV AC | Swan Hill Aerodrome | 3579 | Koroop | Pole
Crew isolated supply and undertook repairs | 388 JOHNSON ROAD, LOCKINGTON VIC 3563 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV/LV substation pole. The cross arm was partly burnt through, but remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 31/01/2016 11:02 | 1 | Negligible: no ground fire | 846 | Roadway |  | 20160210PWA_04 | Infrastructure (network-based) | -36.2646 | 144.5088 | 1 | Powercor | Report | 1270 | 0.0064769 | 22kV AC | Bendigo Airport | 3563 | Lockington | Crossarm
Crew isolated supply and arranged repairs | 18 THOMAS STREET, KEW VIC 3101 |  | Working too close to underground cables | [5 empty] | 2 | A Boring Contractor reported that they had contacted underground cables at the incident location. On arrival the crew found that the contractor (Ram Boring, 74 Emerald Road, Beaconsfield Upper, 3808. Ph:0417 015 473, Site contact: Ryan Weekes, Ph: 0403 542 111) was operating an excavator and contacted a low voltage underground service cable causing damage to the cable. There were no reported injuries or third party property damages. The contractor had undertaken a DBYD enquiry for the location. | Services cable | 0 | 0 | 0 |  |  | Contractor contacted LV UG service cable | No Go Zone (contact) | 42523.3896 |  |  | 852 | Roadway |  | 20160211PWA_04 | Infrastructure (network-based) | -37.8108 | 145.0494 | 1 | CitiPower | Report | 1277 | 0.025734 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Dug up
Sent inspection report and contract to action VWDâ€™s (Tiger Tails) to be installed and Inspector informed customer that the service must be isolated when the scaffold is to be removed. Advised customer to attach Ply Hoarding to scaffold as per NGZ guidelines. Cust stated that no more Mobile Plant will be on site. | 28 BLENHEIM STREET, BALACLAVA VIC 3183 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - Prelim worksite inspection for scaffold installation, found scaffold already erected Incident - (3 of) Erection of scaffolding done without approval, Home made visual warning device (VWD) attached to service cable by Electrician and Crane truck operating within 3000mm of overhead service cables, no Spotter in use. Asset type - LV 3 phase and 1 phase 240 volt service cables Clearance to asset - Crane within 3000mm, Home made warning device wrapped around / touching cable Structure in NGZ: Erection of scaffolding done without approval and crane work within NGZ Developer - Chris Makris (Singen Group) 0411 734 542 | Service conductor | 0 | 0 | 0 |  |  | Structure and work in NGZ | No Go Zone (no contact);No Go Zone (contact) | 42645.4167 |  |  | 858 | Roadway |  | 20160211PWA_09 | Infrastructure (network-based) | -37.8675 | 144.9948 | 1 | CitiPower | Report | 1283 | 0.0069572 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | Balaclava | Other
Upon arrival the faults crew carried out a test from the water pipe to an independent earth and found 12-20 Volts on the water pipe. A check of the service connections found a corroded neutral connection on a neutral connection associated with a Krone fused isolator (FSD). The service connections were then re-terminated directly to the overhead conductor and the water pipe voltage disappeared. The installation was tested and all tests passed. | 114 HOTHAM STREET, TRARALGON VIC 3844 | 2614130 |  |  |  | Corrosion;Fault on customer installation |  | Phase to earth | 2 | IMS 219959. Whilst preparing site for new under bore by a different contractor, the Gippsland Water employee received a tingle to the back of his hand when he made contact with the existing water pipe. The employee advised his supervisor who reported it to AusNet Services. The cause of the electric shock was a corroded neutral connection on the Krone fuse box (FSD) on the pole. The water pipe service work was associated with the CWA Hall at Traralgon. | Connector/termination | 0 | 0 | 0 |  | tgn11 | A corroded neutral connection on the Krone fuse box. | Minor shock | 42675.5833 |  |  | 854 | Commercial |  | 20160211SPN_01 | Infrastructure (network-based) | -38.1969 | 146.5343 | 1 | AusNet Services Distribution | Report | 1279 | 0.0093877 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
Crew isolated supply and undertook repairs | 35 UPPER GELLIBRAND ROAD, BARRAMUNGA VIC 3249 |  |  |  |  | Candled fuse |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (Approx. 1000sqm) on the road reserve and private property. There was also minor damage caused to fencing. There were no reported injuries | EDO fuse | 0 | 0 | 0 |  |  | EDO Fuse unit did not drop down | Grassfire | 42676.5576 | 1 | Small: 10 - 1000 sq.m | 863 | Roadway |  | 20160212PWA_01 | Infrastructure (network-based) | -38.572 | 143.6897 | 1 | Powercor | Report | 1288 | 0.0084792 | 22kV AC | Avalon Airport | 3249 | Barramunga | Fuse
Crew isolated supply and undertook repairs | 20 SHORT ROAD, HATTAH VIC 3501 |  | Working too close to overhead lines | [5 empty] | 1 | A customer reported that an excavator had dug up an underground cable at the incident location. On arrival the crew found that a contractor (Pipe Line Contractor, Contact: Steve Barone, Ph: 0419 268 208) was operating an excavator and contacted a 12.7kV SWER line causing three bays of conductor to fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. The line height was measured at 5.55m at the contact location. | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator contacted overhead line | No Go Zone (contact) | 42676.5417 |  |  | 865 | Agricultural |  | 20160212PWA_03 | Infrastructure (network-based) | -34.8052 | 142.4679 | 1 | Powercor | Report | 1290 | 0.024014 | 12.7kV AC (SWER) | Mildura Airport | 3501 | Hattah | Dug up
Initial CEOT report: Sent crew to investigate, isolate & make safe. Final report: The fault crew checked other spreaders in the vicinity and found another one that had started to wear through and they were both repaired by installing a sleeve. | 33 FISHERMANS ROAD, VENUS BAY VIC 3956 | 2806533 |  |  |  | Age;Corrosion |  | Phase to earth | 2 | IMS 220008. Initial CEOT report: Reports of wires on ground, crew arrived and found live LV on ground at LIS#2806533. Final report: Usually for the coastal areas LV spreaders are tied onto the LV conductors, but this particular spreader had a clip on it which had rubbed through the aluminium conductor. Protection settings on LV did not operate due to the high impedance fault - the LV conductor was still alive on arrival of the crew. No burn marks were evident on the ground. A Schedule 1 report was not sent to ESV by our CEOT due to a misunderstanding by a Dispatcher. | Conductor (bare) | 0 | 0 | 0 |  | wgi14 | Asset failure - a clip on LV spreader had rubbed through the aluminium conductor. Assessment is that it would have taken many years for this occur. | Loss of supply | 13/01/2016 15:32 |  |  | 874 | Residential |  | 20160217SPN_01 | Infrastructure (network-based) | -38.6735 | 145.7959 | 1 | AusNet Services Distribution | Report | 8535 | 0.02476 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3956 | Venus Bay | Conductor
Crew checked line for damage - none found | 3 ARCHER ROAD, KIALLA VIC 3631 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A civil contractor reported that an excavator had hit wires at the incident location. On arrival the crew found that a 22kV fuse at the location had operated but no vehicle or any other damage found at the site. There was no ground fire. There were no reported injuries or third party property damages. The contractors details are: One Stop Civil, Contact: Neil, Ph: 0428 348 790, Excavator Driven by David Fitzgerald, Ph:0407 099 744. | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator contacted 22kV line | No Go Zone (contact) | 17/02/2016 15:09 |  |  | 879 | Roadway |  | 20160218PWA_05 | Infrastructure (network-based) | -36.4207 | 145.4098 | 2 | Powercor | Report | 1308 | 0.0382 | 22kV AC | Shepparton Airport | 3631 | Kialla | Vehicle
On the identification of the transposed neutral and blue phase conductors at the pole end, the Line Worker immediately cuts the connections from the blue phase and the neutral, isolating the supply to the premises. The Line Worker returns to the ground and both team members discuss the situation before deciding to rectify the connections and continue with testing. Line worker returned to the pole and using the existing tails connects the blue and neutral phases correctly. Both Line Workers return to the meter board and complete all required testing. All tests pass and the new three phase supply is energised. The incident is not reported. The Line Workers locate the pit for the single phase supply and proceeds to disconnect and remove the cabling. The Line Workers pack up their work areas and leave the site. (As soon as the customersâ€™ neutral was livened up, there was potential for property damage and injury. The incident should have been reported immediately and an inspector contacted on behalf of United Energy to confirm the premises was safe, regardless of how long the system was live for, or the fact the situation was rectified and testing passed prior to the line workers leaving the site). Wayne Kelly (UE) was contacted by the Electrical Inspector at approximately 4.30PM who advised that an injection has occurred and there is damage to the customers wiring. The Electrical Inspector was at the Downer Mornington office but it appeared no one was in attendance or answering their phones. Wayne suggested the Electrical Inspector call the United Energy faults and emergencies call centre (13 20 99) and report the incident. Trouble Event Order 858662 was created at 4.43PM. Later in the evening, a phone call is received by the line worker from the Electrical Inspector to report there was damage at the premises. The line worker contacts his Supervisor and reports the incident to the Duty Officer. Incident Notifications to Downer Managers and UE are completed. The Duty Officer requested a written sequence of events from the Line Workers and they meet at one employeeâ€™s house to prepare their report. The report is submitted to Downer. The investigation commenced on 22 February 2016. The Downer investigation was completed that resulted in the two Line Workers being dismissed. The cause of the incident was a failure to correctly follow the VESI Installation Supply Connection Tests and Procedures. The Line Workers failed to adhere to testing procedures and missed a number of key steps in the process that would have identified the incorrect connections at the pole end. | 29 CALLANANS ROAD, RED HILL SOUTH VIC 3937 |  |  |  |  | Neutral fault | Not followed |  | 2 | On 19 February, 2016 a service order was issued for a meter and servicing crew to complete the connection of a new three phase supply to a new meter position and switchboard at 29 Callanans Road, Red Hill South. The pole to pit dress up had been previously completed at this location on the 1 May 2015, with the supply energised to the pit. (During the dress up works on the 1 May 2015 the connections from the three phase underground Fused Mains Junction Box to the overhead reticulation were transposed (Neutral connected to Blue phase)). Crew arrive on site and complete a Safety Assessment. â€¢ Crew meet with REC (N Theodorakis) and Electrical Inspector (Kevin Toland) and are provided a copy of the Certificate of Electrical Safety, certificate number 4031 0954 6. â€¢ Crew are advised by REC that the existing supply to the site is via a single phase connection to a separate meter board. â€¢ The crew inspected the new pit and confirmed the pit contained the three phase supply, connected and alive and the consumer mains were 35mm sized conductors. No single phase connection to the old meter was present at the new pit. â€¢ The crew reportedly lifted the neutral at the meter board, by pushing it back towards the inside of the board (not bent away) and the actives were secured at the fuse base. Continuity testing on the consumer mains was completed with the NITP completed at the metal meter enclosure. â€¢ Crew confirmed with the REC and Electrical Inspector that it was okay to make the connections at the pit. â€¢ The disconnected neutral conductor had moved and was under the neutral link plate. Note: At this point in time the neutral and earthing system on the property were live. â€¢ The crew proceeded to pack up their tools and equipment at the pit and move the truck to the pole in position ready to isolate the existing single phase supply â€¢ Crew members return to the meter board to complete the testing. â€¢ Line Worker sees the neutral is in position behind the link and automatically moves to the testing mode of completing testing at the meter position and inserts the fuses. Note: The act of inserting the fuses created a situation where the phase to phase was present in the premises and therefore 415Volts at the connected appliances. The Line Worker completing the testing believed the main switch on the switchboard was in the â€œOFFâ€ position (possibly looking at the auto change over switch for the inbuilt generator). However, following the incident it has been recognised the main switch was in the â€œONâ€ position. â€¢ Line Worker identifies only two of the three phases are present at the meter. â€¢ Line Worker uses neon tester and tests voltages between phases, indicating 415V phase to neutral. â€¢ Line Worker removes the neutral from behind the neutral bar and a spark occurs. â€¢ It is assumed the Line Worker also removed the fuses at some point (either before or after the neutral was lifted). Line Worker unable to clearly recall sequence of events to confirm. â€¢ Line Workers return to the pit to confirm correct connections. â€¢ Line workers set up the EWP and Line Worker ascends the pole to inspect the overhead connections where, the transposed blue phase and neutral conductors are identified. The VESI Installation Supply Connection Tests and Procedures weâ€™re not followed in sequence and this resulted in a low voltage injection into the neutral and earth circuits of the customerâ€™s premises. Damage occurred to the sub-switchboard and the air conditioning unit. | Cable;Aluminium twisted (XLPE);Connector/termination | 0 | 0 | 0 |  |  | A connection within the 3 phase underground FOLCB was transposed at the pole end (Neutral connected to Blue phase) resulting in a low voltage (240v) injection into the neutral and earth circuits at the premise. There were a number of risk management and risk control issues identified that directly contributed to the incident; â€¢ SWMS were not followed â€¢ the connections to the overhead conductors were not visually confirmed â€¢ the line workers failed to follow the VESI Installation Supply Connection Tests and Procedures correctly. The phase identification indicators on the service cable are continuous ribbing around the cable for neutral and three ribs for blue. It is possible in poor light conditions and with low voltage gloves on to confuse the indicators on the blue and neutral conductors. | Less than $50k damage | 19/02/2016 13:30 |  |  | 892 | Residential |  | 20160222UTD_02 | Infrastructure (network-based) | -38.3831 | 145.0354 | 1 | United Energy Distribution | Report | 1327 | 0.0039826 | Low voltage AC (<1kV) | Moorabbin Airport | 3937 | Red Hill South | Other
Crew isolated supply and undertook repairs | 104 KINGS ROAD, ST ALBANS VIC 3021 |  | Vehicle | [5 empty] | 2 | A customer reported that a truck has hit the wire from pole to house and the wire is laying on road at the incident location. On arrival the crew found that LV service cable had been contacted by an unknown vehicle causing the cable to break and fall to the ground. There was no vehicle on site when the crew arrived. There were no reported injuries or third party property damage. The cable height was measured following repairs at 5.5m at the kerb. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | No Go Zone (contact) | 42645.7799 |  |  | 898 | Roadway |  | 20160223PWA_03 | Infrastructure (network-based) | -37.7306 | 144.7819 | 1 | Powercor | Report | 1333 | 0.029318 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
Crew isolated supply | 183-225 HIGH STREET, MELTON VIC 3337 |  | Theft | [5 empty] | 2 | A REC reported that wires have been cut at the incident location. On arrival the crew found that a three phase low voltage customers mains service cable between the pit and the meter board on the toilet block been cut and the cable stolen. The customerâ€™s meter board had been vandalised. There were no reported injuries. | Customer installation | 0 | 0 | 0 |  |  | Theft | Less than $50k damage | 17/02/2016 15:41 |  |  | 912 | Public space |  | 20160223PWA_17 | Infrastructure (network-based) | -37.6831 | 144.5917 | 1 | Powercor | Report | 1347 | 0.014992 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Other
Crew isolated supply and undertook repairs | 57 CALLISTER STREET, SHEPPARTON VIC 3630 |  | Vehicle | [5 empty] | 2 | A customer reported that a truck had struck a wire at the incident location. On arrival the crew found that a truck ( which did not stop/not identified) had contacted an LV service cable causing the cable to break away from the house and fall to the ground. There were no reported injuries. Following repairs, the service cable height was measured at 4.7m above the kerb | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle hit LV service cable | No Go Zone (contact);Damage to network assets | 42492.5833 |  |  | 914 | Roadway |  | 20160223PWA_19 | Infrastructure (network-based) | -36.3903 | 145.4159 | 1 | Powercor | Report | 1349 | 0.036561 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
Crew isolated supply and arranged repairs | 630 ELIZABETH STREET, MELBOURNE VIC 3000 |  | Working too close to underground cables | [5 empty] | 2 | A contractor reported that they had contacted wires at the incident location. On arrival the crew found that a contractor (Melbourne Irrigation, 28 Homestead Road, Wonga Park, - working for Melbourne City Council, Contact Tony, Ph: 0412 243 082) was using a directional borer to install irrigation pipes and contacted a low voltage underground service supplying public lighting in the nature reserve, causing damage to the cable and conduit. There were no reported injuries or third party property damages. | Services cable | 0 | 0 | 0 |  |  | Directional bore contacted UG cable | No Go Zone (contact);Damage to network assets | 15/02/2016 11:30 |  |  | 917 | Roadway |  | 20160224PWA_03 | Infrastructure (network-based) | -37.8037 | 144.9588 | 1 | CitiPower | Report | 8006 | 0.019704 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
Crew isolated supply and arranged repairs | 9 DOOLAN STREET, MADDINGLEY VIC 3340 |  | Vehicle | [5 empty] | 1 | Fire Brigade reported an LV pillar on fire at the incident location. On arrival the crew found that a vehicle (Rego: 1DJ 2ME) had contacted a LV pillar and caught fire, resulting in a ground fire (approx. 5m x 8m) on road reserve. Protection operated. There were no reported injuries. | LV Pillar | 0 | 0 | 0 |  |  | Car hit LV pillar | Grassfire | 23/02/2016 12:30 | 2 | Small: 10 - 1000 sq.m | 918 | Roadway |  | 20160224PWA_04 | Infrastructure (network-based) | -37.6912 | 144.4151 | 1 | Powercor | Report | 1353 | 0.030642 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Vehicle
Crew inspected site and found no reason for reported shocks | 35 CAPE NELSON ROAD, PORTLAND VIC 3305 |  | Unknown external/community factor | [5 empty] | 2 | A field crew patrolling following an outage reported that they were flagged down by a man near the incident location. The man claimed that his 15 year old son and his sonâ€™s girlfriend had seen several poles sparking and received a shock at the incident location, and had been taken to the Hospital for observation. The crew investigated and found no evidence of a flashover (sparking) occurring at the site. Further checks and subsequent tests the following day could not show any reason for a flashover (sparking) or shocks to occur. The crew tested the assets involved and no voltages were found. The two young persons who claimed that they received the shocks, were released from Hospital with no apparent injuries. There was no ground fire. There were no reported injuries or third party property damages. Initial reports said that the two young persons had touched a stay wire when they received the shock, however the boy later told crews that he was sitting on the fence of the RSL over the road (at about 10pm), when â€œhe felt a tingling sensationâ€ he said that he went to investigate the pole in question over the road. He claimed that he was standing on the opposite side of the pole to the stay when there were sparks coming from 3 poles in the immediate area, and he said that he received a shock and fell over. At the same time he said that his girlfriend tried to run away and also received a shock and fell over. Information was also provided that there was another boy involved who was reported as standing up at the back of the vacant block adjacent to the pole, at the time the others reportedly received the shocks. Initial reports from the linesmen on site said that they thought the people involved may have been â€œswingingâ€ on the stay wire at the switch pole, which may have caused HV conductor clashing, however none of this could be confirmed with the persons. | Guy wire;Pole (concrete) | 0 | 0 | 0 |  |  | Cause unable to be determined | Medical attention (first aid/doctor/hospital) | 21/02/2016 22:08 |  |  | 919 | Roadway |  | 20160224PWA_05 | Infrastructure (network-based) | -38.3601 | 141.6056 | 2 | Powercor | Report | 3156 | 0.036536 | Other | Portland (Cashmore Airport) | 3305 | Portland | Other
CEOT dispatched a fault crew sent to make safe, isolate and investigate. The crew found burnt out HV leads at the transformer and they noticed small patches of burnt ground at the base of the transformer. | 3 SAVANNAH CRESCENT, EPPING VIC 3076 | 916606 |  |  |  | Corrosion |  |  | 1 | IMS 220650. CEOT received All Supply Failure fault from Substation Savannah Greenbrook. The Centre Phase HV dropper lead was corroded. 3 Phase overhead HV fuses were blown. A fire of size 1m x 1m and 2m from the pole was observed. | Transformer;Dropper/bridge | 0 | 0 | 0 |  | epg34 | Centre Phase HV dropper corroded. | Grassfire | 23/02/2016 17:27 | 1 | Localised: less than 10 sq.m | 923 | Residential |  | 20160224SPN_02 | Infrastructure (network-based) | -37.6471 | 145.0366 | 1 | AusNet Services Distribution | Report | 1360 | 0.012734 | 22kV AC | Essendon Airport | 3076 | Epping | AF Other
CEOT dispatched a fault crew to make safe, isolate and investigate. The crew replaced the LV White Phase D-loop. Supply restored to customers. | 55 ELONERA AVENUE, GREENSBOROUGH VIC 3088 | 901523 |  |  |  | Overheated connection |  |  | 1 | IMS 220648. CEOT received an incident for All Supply Failures. The fault crew found a burnt-off copper to aluminium LV lead at the substation transformer. The crew noticed a burnt area 1 x 1.5 metres in size at the base of the pole 901523. A LV D-loop failed/burnt on the White Phase. Electrical protection operated - 1 x HRC fuse blew. | Connector/termination;Transformer | 0 | 0 | 0 |  | wt15 | LV D-loop burnt through. | Grassfire | 23/02/2016 16:47 | 1 | Localised: less than 10 sq.m | 924 | Residential |  | 20160224SPN_03 | Infrastructure (network-based) | -37.7175 | 145.1044 | 1 | AusNet Services Distribution | Report | 1362 | 0.017608 | 22kV AC | Essendon Airport | 3088 | Greensborough | Connection
Crew isolated supply and undertook repairs | 5 FINN STREET, NORTH BENDIGO VIC 3550 |  |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire at the incident location. On arrival the crew found that a connection had overheated on a 22kV line causing hot debris to fall to the ground resulting in a ground fire (Approx. 1.5m x 1.5m) There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 24/02/2016 14:45 | 1 | Localised: less than 10 sq.m | 927 | Roadway |  | 20160225PWA_01 | Infrastructure (network-based) | -36.7363 | 144.2918 | 1 | Powercor | Report | 1366 | 0.023081 | 22kV AC | Bendigo Airport | 3550 | North Bendigo | Connection
Made safe - isolated substation | 8-10 PAU STREET, COBURG NORTH VIC 3058 |  | Vandalism;Theft;Unauthorised access | [5 empty] | 2 | Vandels have attempted to steal copper from PAU-WILLIAMS distribution substation inside private property | Indoor;Earth/earthing | 0 | 0 | 0 |  |  | Vandels | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/02/2016 15:45 |  |  | 938 | Industrial |  | 20160229JEM_01 | Infrastructure (network-based) | -37.7302 | 144.9611 | 1 | Jemena | Report | 1379 | 0.0096169 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3058 | Coburg North | Other
Crew undertook repairs | UNIT 4 110 LA TROBE STREET, REDAN VIC 3350 |  | Vehicle | [5 empty] | 2 | A customer reported that a removalist truck had struck a wire and the wire was hanging low at the incident location. On arrival the crew found that a unknown removalist truck had contacted an LV service cable causing the cable to become unhooked at the pole end and hang low over the driveway. The customer advised that the service cable had been struck by another truck approximately two weeks beforehand and was hanging low over the driveway. This previous contact was not reported to Powercor at the time. There were no reported injuries or third party property damages. Following repairs, the service cable height was measured at 3.0m above the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Removalist truck contacted LV service cable | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/02/2016 9:44 |  |  | 953 | Residential |  | 20160302PWA_01 | Infrastructure (network-based) | -37.5727 | 143.844 | 1 | Powercor | Report | 1396 | 0.034368 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Redan | Vehicle
Developer (Darren) advised to create a no go zone by hoarding off the scaffold on either side of the service cable. Crew arranged to attach battens to the service. Developer advised that Inspector will attend site to issue a Permit to Work from the scaffold once this work is completed. Scaffold was installed by â€œSafety Scaffâ€ as advised by Developer. | 6 HIGHTON GROVE, DEEPDENE VIC 3103 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - Call centre contacted NGZ desk as per call from building company Incident - Home made visual warning device and timber shroud attached to service cable by Builder where service cable was sitting on Scaffold. Asset type - 1 phase 240 volt service cable Clearance to asset - wrapped around / touching Structure in NGZ: Scaffold Builder - Owner - Name and contact details: Developer - Name and contact details: Darren Purdom 0419 257 973 ( IE constructions PO Box 3118 Cotham Vic 3101) | Service conductor | 0 | 0 | 0 |  |  | NGZ Infringement | No Go Zone (contact) | 16/02/2016 10:00 |  |  | 955 | Roadway |  | 20160302PWA_03 | Infrastructure (network-based) | -37.815 | 145.0685 | 1 | CitiPower | Report | 1398 | 0.0065498 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Other
Crew isolated supply and undertook repairs | 76 HEYERS ROAD, GROVEDALE VIC 3216 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Powercor received reports of a wire down and sparking at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV/LV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 19/02/2016 14:11 | 1 | Negligible: no ground fire | 963 | Roadway |  | 20160303PWA_02 | Infrastructure (network-based) | -38.2073 | 144.3302 | 1 | Powercor | Report | 1406 | 0.021438 | 22kV AC | Avalon Airport | 3216 | Grovedale | Crossarm
Crew isolated supply and undertook repairs | 146 GREIGS ROAD, ROCKBANK VIC 3335 |  | Vandalism;Theft | [5 empty] | 2 | A passer-by reported that a cable covering and the cable on the pole at incident location has been cut. Upon arrival, the crew found that a LV UG service cable had been cut away from the pole up to the pit. The conduit on the pole was also damaged. There were no reported injuries or third party property damages. . | Services cable | 0 | 0 | 0 |  |  | Theft/Vandalism | Damage to network assets | 22/02/2016 16:42 |  |  | 964 | Roadway |  | 20160303PWA_03 | Infrastructure (network-based) | -37.7456 | 144.6781 | 1 | Powercor | Report | 1407 | 0.024934 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Crew checked and tightened earth connections | PEARSE LAKE ROAD, NYAH WEST VIC 3595 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A asset inspector reported a fire at the incident location. On arrival the crew found that a pole fire ahd occurred in the area of the HV earth which caused burning on the pole from just above ground level to about 1.5 mtrs up the pole. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42372.3972 | 1 | Negligible: no ground fire | 971 | Roadway |  | 20160303PWA_10 | Infrastructure (network-based) | -35.1786 | 143.31 | 1 | Powercor | Report | 2861 | 0.014549 | 22kV AC | Swan Hill Aerodrome | 3595 | Nyah West | Pole
The attending LEI and fault crew identified the fault at the O/H neutral reticulation split- bolt connection. The attending fault crew re-terminated the neutral connection. Voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, earthing system and the distribution assets following re-termination of the neutral conductor, identified 1 Volt. A final NST test was performed which passed. The Installation was left ON supply. | 1665 YARRA JUNCTION-NOOJEE ROAD, POWELLTOWN VIC 3797 | 1404875 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 220163. Grace received an electric shock to her right hand when she simultaneously touched her meter panel and the mass of earth. Further tests between an independent earth and various points of the electrical installation, including the point of contact and distribution assets, revealed a detached O/H service neutral at the reticulation split-bolt connection. This condition caused current to flow through installation MEN connection, main earthing conductor, through Grace, and the general mass of earth. The impedance to the flow of current between the general mass of earth and metallic portions was sufficient enough to cause a rise of 90 Volts on the meter panel and associated earthing system. | Service conductor;Aluminium twisted (XLPE);Connector/termination | 0 | 0 | 0 |  | wyk11 | Faulty service neutral split-bolt connection on overhead. | Minor shock | 23/01/2016 10:51 |  |  | 978 | Residential |  | 20160303SPN_02 | Infrastructure (network-based) | -37.8632 | 145.7554 | 1 | AusNet Services Distribution | Report | 1421 | 0.014723 | Low voltage AC (<1kV) | Moorabbin Airport | 3797 | Powelltown | Connection
A LEI and faults truck attended and completed installation tests and a NST failed. The LEI tested between the earthed electrical equipment in the shed to an independent earth and measured 92v. The LEI identified a power board had been wired into the back of a light switch with a 3 core flexible cable with only the active and neutral conductors connected in the shed. Voltage tests between an independent earth and the active conductor with load applied found a decrease in voltage to 204v that caused the dimming of lights. The LEI disconnected the non-compliant power board and the faults crew checked connections at the house and pole ends and identified a loose neutral connection at the pole end. The connection was re-terminated and supply was restored. As the problem was continuing, a faults truck re-attended and replaced the existing grey twisted overhead service a with XLPE type. Lights continued to dim and the faults crew proceeded to check all connections back to "Overton-Nepean" substation. A deteriorated neutral connection was identified at the substation and the faults crew re-terminated the connection that rectified the problem. | 10 OVERTON ROAD, FRANKSTON VIC 3199 | LIS No. 3317979 |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | 25/02/2016 - The occupier advised that a slight electric shock was received whilst using an electric drill in the shed and has noticed that lights have been dimming. 26/02/2016 - Customer advised that lights are continually dimming but there have been no electric shocks received since the crew were in attendance last night. 28/02/2016 - Customer called advising they have intermittent supply with the lights diming slightly and coming back to full brightness. The occupier advised they continually have intermittent supply with the single instance of an electric shock being received from a drill that was being used in the rear shed. | Service conductor;Connector/termination;Transformer | 0 | 0 | 0 |  | FTN 21 | 1. A non-compliant power board and the faults crew checked connections at the house and pole ends and identified a loose neutral connection at the pole end. 2. As the problem was continuing, a faults truck re-attended and replaced the existing grey twisted overhead service a with XLPE type. 3. Lights continued to dim and the faults crew proceeded to check all connections back to "Overton-Nepean" substation. A deteriorated neutral connection was identified at the substation and the faults crew re-terminated the connection that rectified the problem. | Minor shock | 25/02/2016 17:45 |  |  | 986 | Residential |  | 20160303UTD_01 | Infrastructure (network-based) | -38.1292 | 145.1259 | 1 | United Energy Distribution | Report | 1429 | 0.03492 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Crew isolated supply and undertook repairs | 22 WASHINGTON STREET, ST ALBANS VIC 3021 |  |  |  |  | Overheated connection |  |  | 1 | VicFire reported a minor grass fire on nature strip at the incident location. On arrival the crew found that the White phase fused isolator copper to ally t clamp on the load side had burnt off, resulting in a ground fire (approx. 6m x 5m) on the road reserve. There were no reported injuries or third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection. | Loss of supply | 42585.8167 |  |  | 1015 | Roadway |  | 20160309PWA_04 | Infrastructure (network-based) | -37.7453 | 144.7884 | 1 | Powercor | Report | 3092 | 0.022773 | 22kV AC | Melbourne Airport | 3021 | St Albans | Connection
Crew isolated supply and undertook repairs | 16 REIDY RISE, MELTON WEST VIC 3337 |  | Vandalism | [6 empty] | A customer reported a broken UG pit lid and wire exposed at the incident location. Upon arrival, the Powercor crew found that an unknown third party damaged the pit lid. Customer fell on pit lid cover. there was no third party property damages or ground fire. | Services pit | 0 | 0 | 0 |  |  | broken pit lid | Damage to network assets | 42403.4243 |  |  | 1017 | Public space |  | 20160309PWA_06 | Infrastructure (network-based) | -37.6655 | 144.5641 | 1 | Powercor | Report | 3071 | 0.018524 | 22kV AC | Melbourne Airport | 3337 | Melton West | Other
Crew isolated supply and undertook repairs. | 3 DANDARRIGA DRIVE, CLIFTON SPRINGS VIC 3222 |  |  |  |  | Overheated connection |  |  | 2 | Vic fire reported that a pole fire has caused a grass fire at the incident location. On arrival the crew found that a low voltage fuse connection on the pole had overheated, resulting in a small area scorched (0.1 by 0.1 m2) near the pole. There were no reported injuries. There was no ground fire. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 42554.4236 |  | Localised: less than 10 sq.m | 1018 |  |  | 20160309PWA_07 | Infrastructure (network-based) | -38.148 | 144.5762 | 1 | Powercor | Report | 3128 | 0.0071655 | 11kV AC;22kV AC | Avalon Airport | 3222 | Clifton Springs | Connection
Crew isolated supply and undertook repairs. | 5 PARK STREET, BRIDGEWATER ON LODDON VIC 3516 |  |  | Bird |  |  |  |  | 1 | A Fault crew attending following an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | The cause of the fault was a Cockatoo that was chewing on the bottom end of the insulated HV leads on the substation, ultimately causing a flashover and the demise of the Cockatoo. | Loss of supply | 42585.3847 |  |  | 1020 | Roadway |  | 20160309PWA_09 | Infrastructure (network-based) | -36.6045 | 143.9383 | 1 | Powercor | Report | 3095 | 0.01795 | 22kV AC | Bendigo Airport | 3516 | Bridgewater On Loddon | Animal
Crew isolated supply and undertook repairs. | 26 CASTLES CRESCENT, KYNETON VIC 3444 |  | Working too close to underground cables;Caused by REC/contractor | [5 empty] | 2 | A builder reported that the gas contractor on their site hit the LV underground cable with a crowbar at the incident location. On arrival the crew found that a contractor (Downer Gas, Contact: Andrew Wilson, Ph: 0428 387 339) was exposing cables with a crowbar and contacted a LV underground cable causing superficial damage to the cable. There were no reported injuries or third party property damages | Cable | 0 | 0 | 0 |  |  | Contractor made contact with a Low Voltage underground cable. | No Go Zone (contact);Damage to network assets | 42463.516 |  |  | 1021 | Residential |  | 20160309PWA_10 | Infrastructure (network-based) | -37.2546 | 144.4673 | 1 | Powercor | Report | 3076 | 0.0072836 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3444 | Kyneton | Dug up
The attending LEI called for a service truck to replace the street crossing with a new cable. Voltage tests between an independent earth and various points of the electrical installation detected zero volts after cable was replaced. | UNIT 2 121 BRIDGE STREET, BENDIGO VIC 3550 |  |  |  |  | Fault on customer installation |  |  | 2 | Mrs Williamson was having a shower when she received an electric shock from the metallic shower head. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a severely corroded neutral screen of an aluminium neutral screened service cable as the cause of the high impedance associated with the return path of the neutral current. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 35 volts on the water piping system. | Service conductor | 0 | 0 | 0 |  |  | Neutral Screen of service cable | Minor shock | 42432.1042 |  |  | 1022 | Residential |  | 20160309PWA_11 | Infrastructure (network-based) | -36.7483 | 144.2875 | 1 | Powercor | Report | 5301 | 0.011797 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | OH Cable
Emergency high voltage switching was completed on 22kV feeder EB 33 to minimise the number of customers affected and the HV intermediate crossarm was replaced under Access Authority conditions prior to the supply being restored. | 233 BLACKBURN ROAD, BLACKBURN SOUTH VIC 3130 | LIS No. 7027797 |  | Precipitation |  | Corrosion;Electrical breakdown;Insulator;Leakage |  |  | 2 | The MFB reported that a crossarm on a pole outside this address is on fire. Following light drizzly rain, a HV intermediate crossarm fire occurred at pole No. LIS 7027797 located outside 233 Blackburn Road, Doncaster East. The MFB were in attendance. | Crossarm (wood) | 0 | 0 | 0 |  | EB 33 | Probable HV fog type insulator breakdown and fauilure. | Pole-top fire | 20/12/2015 18:02 | 1 | Negligible: no ground fire | 419 | Roadway |  | 20151222UTD_4 | Infrastructure (network-based) | -37.8413 | 145.1556 | 1 | United Energy Distribution | Report | 632 | 0.031243 | 22kV AC | Moorabbin Airport | 3130 | Blackburn South | Crossarm
Crew isolated supply and undertook repairs | 22 WASHINGTON LANE, WOODEND VIC 3442 |  | Working too close to underground cables | [5 empty] | 2 | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location. On arrival the crew found that a contractor (Newmans Earth Moving, contact Michael : Ph: 0467 006 033) was operating an excavator and contacted a LV underground mains cable causing damage to the cable and conduit. A DBYD enquiry had been made for this contractor at this location. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Excavator contacted LV cable | No Go Zone (contact);Damage to network assets | 15/12/2015 10:37 |  |  | 437 | Roadway |  | 20151223PWA_3 | Infrastructure (network-based) | -37.3655 | 144.5312 | 1 | Powercor | Report | 660 | 0.024235 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Dug up
Crew isolated supply and undertook repairs | 241 DUFFIELDS ROAD, JAN JUC VIC 3228 |  |  |  |  | Unknown technical factor |  |  | 2 | CFA reported a fire in a street light at the above location. On arrival the crew found that a fire had started in a LV street lighting lantern. There was no ground fire. There were no reported injuries or third party property damages. | Public lighting | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Other electricity related | 17/11/2015 20:25 | 1 | Negligible: no ground fire | 440 | Roadway |  | 20151223PWA_6 | Infrastructure (network-based) | -38.3415 | 144.3044 | 1 | Powercor | Report | 663 | 0.019856 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the HV intermediate crossarm was replaced under Access Authority conditions. In addition the aluminium HV tee-off conductors required to be sleeved and re-terminated prior to the supply being restored. | 111-115 LONSDALE STREET, DANDENONG VIC 3175 |  |  | Precipitation |  | Leakage |  |  | 1 | At 0849hrs on 20/12/2015, 22kV feeder DN 07 circuit breaker successfully reclosed and held. A short time afterwards at 0917hrs, 22kV feeder DN 07 circuit breaker reclosed to lockout affecting 798 customers. Following light drizzly rain, a HV intermediate crossarm fire occurred at a HV/LV tee off pole located outside 115 Lonsdale Street, Dandenong. This caused the blue phase HV intermediate conductor to contact the HV tee-off conductors below and HV conductors to fall to the ground. No high voltage injection or damage was sustained. | Conductor (bare);Crossarm (wood);Aluminium | 0 | 0 | 0 |  | DN 07 | Following a hot spell, light "dirty" rain fell that left a residue on HV insulators. Following additional light drizzly rain, a HV intermediate crossarm fire occurred on a pole in Dandenong. | Pole-top fire;Loss of supply | 20/12/2015 9:17 | 1 | Negligible: no ground fire | 444 | Commercial |  | 20151223UTD_1 | Infrastructure (network-based) | -37.9946 | 145.216 | 1 | United Energy Distribution | Report | 668 | 0.036875 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Crossarm
Crew isolated supply and undertook repairs | 6861 WIMMERA HIGHWAY, CHARAM VIC 3318 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  |  | Vic Fire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, which burnt the end of the arm causing the crossarm to break and fall to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 20/12/2015 18:50 | 1 | Negligible: no ground fire | 453 | Agricultural |  | 20151224PWA_1 | Infrastructure (network-based) | -36.9096 | 141.4926 | 1 | Powercor | Report | 692 | 0.022307 | 22kV AC | Horsham Aerodrome | 3318 | Charam | Crossarm
Crew isolated supply for REC to undertake repairs | 1 DUNCAN STREET, BIRCHIP VIC 3483 |  | Vehicle | [5 empty] | 2 | Vicfire reported a wire down at the incident location. On arrival the crew found that a LV service cable had been broken and had fallen to the ground. Damage was also caused to house end FMB. Birchip Police advised that a truck (Rego - 481-KCR. Driver- Lyle McInerney, Ph: 0402 597 99) with a car carrier had contacted the service cable. There was no ground fire. There were no reported injuries. As the service was not replaced pending repairs by the REC the service height was not measured. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | No Go Zone (contact);Damage to network assets | 21/12/2015 17:27 |  |  | 458 | Roadway |  | 20151224PWA_6 | Infrastructure (network-based) | -35.9844 | 142.9143 | 1 | Powercor | Report | 8059 | 0.036843 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3483 | Birchip | Vehicle
CEOT dispatched to fault crew to make safe and investigate. DAO also attended. LV isolator replaced. | 101 LOUGHNAN ROAD, RINGWOOD VIC 3134 | 1214263 |  |  |  | Overheated connection |  | Phase to earth | 2 | IMS 219827. Pole arcing outside property caused a small grass fire on nature strip, as per CFA. DAO arrived on site and found a burnt out strip of Road Reserve approximately 5m long x 1m wide. No damage to any AusNet Services' assets, or private assets. Found some burnt metal blobs on site which were part of the Blue Phase LV Isolator on the transformer pole. | Disconnector/isolator | 0 | 0 | 0 |  | rwn24 | Possible faulty electrical connection. | Grassfire | 24/12/2015 15:25 | 1 | Localised: less than 10 sq.m | 461 | Residential |  | 20151228SPN_1 | Infrastructure (network-based) | -37.8092 | 145.2185 | 1 | AusNet Services Distribution | Report | 701 | 0.012694 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Ringwood | Connection
CEOT dispatched fault crew and LEI, Crew isolated supply, made repairs to HV crossarm. Isolated affected LV customers and LEI checked installations for HVI damage. On arrival the crew found HV coss arm had burnt off near straps causing HV conductors to fall into the LV conductors. The crew replaced HV cross arm and re-sleeved HV conductor due to damage caused during contact with LV (HV conductor size 144 ally, LV conductors 186 ally). LEI completed inspection on all associated industry residents off the affected low voltage - all 3 phase meters (6 x 450) and 3 CT meters were replaced. A number of sites sustained damaged equipment - included was spilt system air conditioners and a photocopier and one meter panel needed replacing. 2 x damaged LED street lights damaged were replaced. White and Blue Phase LV fuses blown on Sub Pole Lis No 2614729 - No 14 to 16 loss of supply, multiple phases blown. All other fuses OK. | 18 SWAN ROAD, MORWELL VIC 3840 | 2614729 |  | Industrial or urban pollution |  | Leakage |  | Phase to phase | 1 | IMS 219829. Broken HV conductor, HV lines into LV lines resulting in a HVI. HV crossarm had burnt off near cross arm strap due to current/voltage tracking - HV conductor landed in on White Phase of the low voltage line. Feeder tripped and locked out. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | mwts32 | Burnt HV cross arm caused by current/voltage leakage due to pollution on HV insulators. | HV injection | 26/12/2015 7:15 |  |  | 462 | Industrial |  | 20151228SPN_2 | Infrastructure (network-based) | -38.2413 | 146.4434 | 1 | AusNet Services Distribution | Report | 703 | 0.039551 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Crossarm
Site made safe | 199 GORDON STREET, FOOTSCRAY VIC 3011 |  | Vehicle | [5 empty] | 2 | A truck has reportedly collided with several cars and exploded on the corner of Barkly and Gordon Streets in Footscray. No Jemena involvement, however the explosion has damaged LV assets (pole and conductors) leaving 111 customers off supply. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | A truck has reportedly collided with several cars and exploded causing pole to fall over and LV conductors on ground. | Significant disruption to the community;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/12/2015 11:30 |  |  | 464 | Roadway |  | 20151229JEM_1 | Infrastructure (network-based) | -37.7985 | 144.8882 | 1 | Jemena | Report | 707 | 0.0036539 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
Crew isolated supply and undertook repairs. | 708 LAKE ROAD, NATIMUK VIC 3409 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported wires arcing at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break, however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 3:30 | 0 | Negligible: no ground fire | 468 | Agricultural |  | 20151230PWA_1 | Infrastructure (network-based) | -36.6885 | 141.9345 | 1 | Powercor | Report | 1173 | 0.024172 | 22kV AC | Horsham Aerodrome | 3409 | Natimuk | Crossarm
Crew isolated supply and undertook repairs. | 12-14 SLOANE STREET, STAWELL VIC 3380 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A fault crew attending an outage found that a crossarm fire had occurred on a 22kV/lv pole at the incident location, which caused the crossarm to break and the 22kV conductor to make contact with the low voltage conductor below it. This resulted in a HV injection and minor damage to installations of several premises (including two meters and council lighting). The status of three properties remained unknown at the time the LEIs were investigating due to no access to those premises. The three premises were left isolated from supply until they are checked for HV injection damage. Protection operated. There was no ground fire. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire;HV injection;Less than $50k damage | 26/12/2015 7:05 | 1 | Negligible: no ground fire | 482 | Roadway |  | 20151230PWA_8 | Infrastructure (network-based) | -37.0559 | 142.7826 | 1 | Powercor | Report | 1152 | 0.0075394 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3380 | Stawell | Crossarm
A LEI and faults truck attended and identified the neutral screened service had been damaged by a tree in the nature strip that was attached to a service pole outside the property. NST failed on neutral impedance 1.59ohms, 10v mesured on the neutral bar from an independant earth under a 6.5amp load and 8.6v on the bathroom taps. The faults crew identified the 2 phase aluminium neutral screened service had broken strands and proceeded to replace with a XLPE type. The service was relocated from pole number LIS No. 7067023 to 7067026 away from the large nature strip tree. The LEI re-tested the installation that confirmed the fault had been rectified. | 58 OLD WARRANDYTE ROAD, DONVALE VIC 3111 | LIS No. 7067024 |  | Alive |  | Electrical breakdown |  | Phase to earth | 2 | REC states there is a broken neutral coming into the property after the customer was getting shocks from the the water taps. He measured 120v on the water pipes. The occupiers were receiving slight electric shocks from the water taps and contacted a REC to investigate. The REC measured voltages on the taps and believed there is no neutral connected to the overhead reticulation. | Service conductor;Aluminium;Neutral screen | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Minor shock | 23/12/2015 9:00 |  |  | 480 | Residential |  | 20151230UTD_7 | Infrastructure (network-based) | -37.7822 | 145.1833 | 1 | United Energy Distribution | Report | 726 | 0.036125 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | Trees
Crew isolated supply and undertook repairs. | 559 YATES ROAD, WERRIMULL VIC 3496 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A fault crew patrolling a line following an outage found that a crossarm fire had occurred on a 22kV pole at the incident location, which caused the crossarm to break and resulting in the conductors falling to the ground. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 12:45 | 1 | Negligible: no ground fire | 487 | Roadway |  | 20151231PWA_1 | Infrastructure (network-based) | -34.3873 | 141.5504 | 1 | Powercor | Report | 1150 | 0.013309 | 22kV AC | Mildura Airport | 3496 | Werrimull | Crossarm
Crew isolated supply and undertook repairs. | 345 MURCHISON-TATURA ROAD, DHURRINGILE VIC 3610 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 0 | Customer reported a low wire & fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV/lv pole, which caused the crossarm to break and resulted in the 22kV conductor to fall and come to rest above the ground supported by the crossarm tie. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 26/12/2015 16:15 | 1 | Negligible: no ground fire | 489 | Roadway |  | 20151231PWA_3 | Infrastructure (network-based) | -36.5588 | 145.2227 | 1 | Powercor | Report | 1143 | 0.001544 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3610 | Dhurringile | Crossarm
Crew isolated supply and undertook repairs. | 17 GALTES CRESCENT, BRUNSWICK WEST VIC 3055 |  | Vehicle | [5 empty] | 2 | A passerby reported that a truck had struck a tree and a power pole is down at the incident location. On arrival the crew found that a removalist truck (Rego No: YSL-726, Driver: Nakerz Wegenek, Licence No: 082621944, Expires: 01.09.2016, Address: 1 Dalton Drive, Melton South) had contacted and pulled down a third party communications cable (owned by Optus) that is attached to a LV pole, causing the pole to break at the base and resulting in the pole and the conductors to fall to the ground. The conductors were reported to have been sparking and smoldering on the ground. The MFB were in attendance to secure the site pending the arrival of the fault crew. There was no ground fire. There were no reported injuries. | Pole (wood);Communication cable/equipment | 0 | 0 | 0 |  |  | Truck contacted third party communications cable | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/12/2015 16:26 |  |  | 494 | Roadway |  | 20151231PWA_8 | Infrastructure (network-based) | -37.7529 | 144.9303 | 1 | CitiPower | Report | 1176 | 0.037392 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Vehicle
CEOT dispatched a fault crew to make safe, isolate repair. The candled EDO fuse tube was replaced and supply restored. A request for a work order has been raised to replace the EDO fuse units with Boric Acid fuse units. | 730 WATERLOO ROAD, TRAFALGAR VIC 3824 | 2206061 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 219839. Burnt out EDO fuse found at Trafalgar 70 Substation. No fire on ground or pole. | EDO fuse | 0 | 0 | 0 |  | moe32 | Burnt EDO fuse tube. | Other electricity related | 31/12/2015 7:00 | 1 | Negligible: no ground fire | 496 | Agricultural |  | 20160103SPN_2 | Infrastructure (network-based) | -38.2024 | 146.1826 | 1 | AusNet Services Distribution | Report | 750 | 0.021825 | 22kV AC | Morwell (Latrobe Valley Airport) | 3824 | Trafalgar | Fuse
CEOT dispatched fault crew to make safe and investigate. Fault crew made safe. Construction crew attended and sleeved in approximately 17m Cu Conductor and re-sagged & retied at interpole - resolve approximately 9 pm 2/1/2016. Tree cleared from line. Vegetation Management have been requested to assess the tree and determine if hazardous - Initial assessment provided 6/1/2016 - no hazard - 2nd opinion will be sort from arborist. | 122 CARDIGAN ROAD, MOOROOLBARK VIC 3138 | 1014776 |  | Blown branch/vegetation |  |  |  | Phase to phase | 1 | Fire near asset @ Lis #1014774. Approximately 6:57 pm, 2/1/2016, a private tree branch allegedly sheered of in the wind and fell into overhead High Voltage Open Wire line - branch came to rest on sidewalk/property side conductor and ground & Centre Phase HV Conductor broke and scorched grass approximately 5 m long by 0.15 m wide. AusNet Services' Vegetation Management report states: "Large liquid amber has had a limb tear out and fallen across lines. No fire found but customer stated that sparks emitted when the branch hit line. Tree has overhang on line and may require further inspection to ascertain risk level." The fault was not caused by branches inside the clearance space. Extreme windy conditions. | Pole (wood) | 0 | 0 | 0 |  | ldl24 | Vegetation: Trees Incident | Grassfire | 42401.7882 | 1 | Localised: less than 10 sq.m | 502 | Residential |  | 20160103SPN_8 | Infrastructure (network-based) | -37.7895 | 145.3301 | 1 | AusNet Services Distribution | Report | 762 | 0.018998 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | Trees
CEOT dispatched to Fault Crew, LEIs and DAO to make safe, isolate and investigate. The faults crew repaired the damaged lightning arrestor at the pole. LEIs on site - checked for damaged metering & switchboards from the injection. Damaged & inaccessible properties taken off supply and details provided to CEOT. Notice Of Customer Installation Defects form was issued to the owner of no. 3 Orange Grove to engage a REC for the main switchboard replacement and to check the entire electrical installation. Customer Advice forms issued to affected properties. | 3 ORANGE GROVE, BAYSWATER VIC 3153 | 1211027 |  | Lightning |  |  |  | Phase to earth | 1 | IMS19856. There was a lightning strike to the Red Phase of the 22KV line on pole no.1211027, outside 2 Orange Grove, Bayswater, resulting in a High Voltage Injection. A small fire occurred at the customer's main switchboard at no. 3 Orange Grove. The Fire Brigade were in attendance for 3 Orange Grove switchboard fire. | Conductor (bare);Switchboard;Surge diverter;Customer installation | 0 | 0 | 0 |  | BWR32 | Lightning strike to 22 kV line. | HV injection | 42430.5208 |  |  | 503 | Residential |  | 20160103SPN_9 | Infrastructure (network-based) | -37.8485 | 145.2684 | 1 | AusNet Services Distribution | Report | 764 | 0.0036285 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3153 | Bayswater | Lightning
Crew isolated supply and undertook repairs | 26-28 BROOKLYN ROAD, MELTON SOUTH VIC 3338 |  |  |  |  | Overheated connection |  |  | 1 | CFA reported a pole fire at the incident location. On arrival the crew found that a connection on the HV insulated lead had overheated causing the lead to catch fire. Protection operated. There were no reported injuries or third party property damages. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Plant/equipment | 26/12/2015 4:45 | 1 | Negligible: no ground fire | 513 | Roadway |  | 20160104PWA_1 | Infrastructure (network-based) | -37.7026 | 144.5734 | 1 | Powercor | Report | 778 | 0.0081007 | 22kV AC | Laverton Raaf | 3338 | Melton South | Connection
Crew isolated supply and undertook repairs | 1310 LEAKES ROAD, ROCKBANK VIC 3335 |  |  |  |  | Overheated connection |  |  | 2 | A nearby customer reported smoke and flame coming from a pole at the incident location. On arrival the crew found that a connection had overheated on a pole mounted LV fuse box causing the box to catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Plant/equipment | 26/12/2015 8:04 | 1 | Negligible: no ground fire | 516 | Roadway |  | 20160104PWA_3 | Infrastructure (network-based) | -37.7391 | 144.6512 | 1 | Powercor | Report | 866 | 0.017006 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Connection
CEOT dispatched fault crew. Crew made safe, carried out repairs and report organized. Fence post fire extinguished. Construction crew arranged to sleeve damaged conductor and restore supply. | LOT 4B SIGNBOARD LANE, DUTSON DOWNS VIC 3851 | 2503266 |  | Bird |  |  |  | Phase to phase |  | IMS 219860 INCD-90691-r An Eagle caused a phase to phase fault on 22kV conductors bringing the Centre Phase conductor to the ground. HV fuse down at SW# 810829. Ground fire was observed near assets - 650 sq.m in size. Also a couple of fence posts are burnt. Ground fire was out, fence post fire was extinguished. | Conductor (bare) | 0 | 0 | 0 |  | SLE31 | Bird Incident | Grassfire | 28/12/2015 11:48 | 1 | Medium: 1000 sq.m - 10 ha | 511 | Agricultural |  | 20160104SPN_2 | Infrastructure (network-based) | -38.2214 | 147.2744 | 1 | AusNet Services Distribution | Report | 12591 | 0.023843 | 22kV AC | Bairnsdale Airport | 3851 | Dutson Downs | Animal
Crew isolated supply and undertook repairs | 15 MYALL ROAD, WESTBY VIC 3579 |  |  |  |  | Candled fuse |  |  | 2 | A nearby customer reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a fire to start in the vicinity of the base of the pole. An area of approximately 8000 sqm of grass on private property was burnt. There were no reported injuries. | EDO fuse | 0 | 0 | 0 |  |  | Candled fuse | Grassfire | 42430.8785 | 1 | Medium: 1000 sq.m - 10 ha | 531 | Agricultural |  | 20160105PWA_2 | Infrastructure (network-based) | -35.6495 | 143.96 | 1 | Powercor | Report | 805 | 0.025833 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3579 | Westby | Fuse
Crew isolated supply and undertook repairs | 41 SLADEN STREET, HAMLYN HEIGHTS VIC 3215 |  |  |  |  | Age;Electrical overload |  |  | 2 | Customer reported a service wire "blew up" and sparked on the ground at the incident location. On arrival the crew found that a LV service cable had broken at the house end and fell to the ground resulting in a ground fire (Approx. 10cm x 10cm) on private property. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Broken LV service due to overload/deterioration | Grassfire | 42430.7917 | 1 | Localised: less than 10 sq.m | 533 | Residential |  | 20160105PWA_4 | Infrastructure (network-based) | -38.1241 | 144.3212 | 1 | Powercor | Report | 809 | 0.035991 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | Conductor
Crew isolated supply and undertook repairs | MOOLERRLLEEN, 652 WIMMERA HIGHWAY, MOOLERR VIC 3477 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a crossarm fire had occurred on a 22kV pole, which burnt through the cross arm near the brace causing the outer phase to fall to the ground. There was no ground fire. Protection operated. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | crossarm fire | Pole-top fire | 42491.75 | 1 | Negligible: no ground fire | 556 | Roadway |  | 20160107PWA_16 | Infrastructure (network-based) | -36.6365 | 143.1954 | 1 | Powercor | Report | 839 | 0.040082 | 22kV AC | Horsham Aerodrome | 3477 | Moolerr | Crossarm
Crew isolated supply and undertook repairs | 73 MURRAYVILLE-NHILL ROAD, MURRAYVILLE VIC 3512 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole causing the pole top structure to fall to the ground resulting in a ground fire which self extinguished (Approx. 0.4m x 0.4m) where the pole head sat on the ground. Protection operated. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 42430.9403 | 1 | Localised: less than 10 sq.m | 560 | Agricultural |  | 20160107PWA_18 | Infrastructure (network-based) | -35.2698 | 141.1889 | 1 | Powercor | Report | 845 | 0.011494 | 22kV AC | Mildura Airport | 3512 | Murrayville | Pole
Crew isolated supply and undertook repairs | 171 JARRETTS ROAD, HEATHMERE VIC 3305 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a SWER pole which burnt the top of the pole resulting in a ground fire (Approx. 7500 sqm) on private property. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 42461.3521 | 1 | Medium: 1000 sq.m - 10 ha | 542 | Agricultural |  | 20160107PWA_2 | Infrastructure (network-based) | -38.1981 | 141.5827 | 1 | Powercor | Report | 822 | 0.036162 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3305 | Heathmere | Pole
The faults crew assessed the electrical infrastructure for any damage following the grass fire and replaced the 5amp HV powder filled fuse at "Derril-Eramosa" pole type substation restoring supply to 5 customers supplied from the substation. | 1110 DERRIL ROAD, MOOROODUC VIC 3933 | 1103553 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | Caller reports very large branch has fallen onto the powerlines and a grass fire has started. The road is blocked and the CFA have been called. During strong gusty winds, a council tree branch from outside 1110 Derril Road has broken and contacted the LV conductors. When the branch fell, it avoided making contact with the HV conductors. The CFA were in attendance and extinguished a grass fire that started after the white and blue LV conductors clashed that resulted in molten metal dropping into the dry grass below. The fire was estimated to be 45m x 4m in size and there was a LV spreader attached to the conductors in the middle of the bay (substation bus). The council gum tree was located approximately 30m away from the conductors on the other side of the road. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | MTN 22 | Vegetation: Trees Incident | Loss of supply;Grassfire | 42430.0083 | 1 | Small: 10 - 1000 sq.m | 557 | Roadway |  | 20160107UTD_1 | Infrastructure (network-based) | -38.2179 | 145.1125 | 1 | United Energy Distribution | Report | 840 | 0.0029039 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Trees
Crew isolated supply and undertook repairs | 1164 AYRESFORD ROAD, ECKLIN SOUTH VIC 3265 |  |  |  |  | Unknown technical factor |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that a service cable fault had occurred on a grey twisted service, approx. 5 metres from the POA, which caused hot debris to fall to the ground, resulting in a ground fire (approx. 8m x 3m) on private property. The cause of the service fault could not be determined. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Unknown fault in LV service cable | Grassfire | 42614.9958 | 1 | Small: 10 - 1000 sq.m | 572 | Agricultural |  | 20160111PWA_2 | Infrastructure (network-based) | -38.3616 | 142.8684 | 1 | Powercor | Report | 863 | 0.018628 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Ecklin South | OH Cable
Crew isolated supply and arranged repairs | 34 CLARENDON STREET, SOUTHBANK VIC 3006 |  | Working too close to underground cables | [5 empty] | 1 | A civil contractor reported that they had contacted an underground cable with a jackhammer at the incident location. On arrival the crew found that a contractor (Coleman Rail, 174 Turner St, Port Melbourne, Phone:(03) 9624 4210, Equipment operator-Josh Wong) was digging for a drainage trench and contacted an LV underground mains cable causing damage to the cable. Protection operated. The contractor advised that they had undertaken DBYD enquiries. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Third party dig-in | No Go Zone (contact);Damage to network assets | 42522.5507 |  |  | 575 | Roadway |  | 20160111PWA_5 | Infrastructure (network-based) | -37.8248 | 144.9565 | 1 | CitiPower | Report | 956 | 0.030007 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | Dug up
A faults truck attended and installed 2 new protective covers on the stay wire that supports pole No. LIS 060227 located on the corner of Lawrence Road and Price Avenue, Mount Waverley. Details of the person who sustained a minor cu has been emailed to the UE Customer Resolutions team for follow up. | 233 LAWRENCE ROAD, MOUNT WAVERLEY VIC 3149 | LIS No. 0602247 | Vandalism | [5 empty] | 2 | Customer advised the protective cover over the guy wire that is supporting the pole has cracked and come away. A passerby has been cut when they accidentally hit the guy / stay wire. It was suspected the stay wire cover had been vandalised. | Guy wire | 0 | 0 | 0 |  |  | Damaged stay wire with protective covers removed that left a sharp steel strand to protrude. | Medical attention (first aid/doctor/hospital) | 42552.6042 |  |  | 569 | Roadway |  | 20160111UTD_2 | Infrastructure (network-based) | -37.8749 | 145.1416 | 1 | United Energy Distribution | Report | 857 | 0.039699 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Other
Crew isolated supply and undertook repairs | 29 SOUTHBOURNE ROAD, RIDDELLS CREEK VIC 3431 |  | Theft | [5 empty] | 2 | Pat from Keogh Homes reported damage to meter / switchboard & pit lid off and tampering with UG cables at the incident location. On arrival the crew found that an apparent attempt to pull customers side underground cable out of their conduit had occurred. Unknown third parties attempted to isolate the cable at the pit resulting in a live cable being left out of the pit and neighbouring property having its neutral conductor cut. There were no reported injuries. | Customer installation | 0 | 0 | 0 |  |  | Attempted copper theft | Damage to network assets | 42705.7083 |  |  | 609 | Residential |  | 20160115PWA_2 | Infrastructure (network-based) | -37.4593 | 144.6914 | 1 | Powercor | Report | 918 | 0.0074896 | Low voltage AC (<1kV) | Melbourne Airport | 3431 | Riddells Creek | Other
A construction crew was arranged and the HV termination crossarm was replaced using glove and barrier techniques. | 76 CANTEBURY ROAD, BLACKBURN SOUTH VIC 3130 | LIS No. 0639742 |  | Precipitation |  | Electrical breakdown |  |  | 2 | A passerby called to report there is a broken insulator on the pole and the wire is hanging from the crossarm on the corner of Donald Street and Canterbury Road, Blackburn South. Following light drizzly rain, a HV termination crossarm fire occurred at pole No. LIS 0639742 located on the corner of Canterbury Road and Donald Street, Blackburn South. No high voltage injection or damage was sustained. | Crossarm (wood) | 0 | 0 | 0 |  | BH 11 | Crossarm fire following light rain and probable insulator tracking. | Pole-top fire | 42675.8111 | 1 | Negligible: no ground fire | 603 | Roadway |  | 20160115UTD_2 | Infrastructure (network-based) | -37.8315 | 145.1437 | 1 | United Energy Distribution | Report | 911 | 0.0025694 | 22kV AC | Moorabbin Airport | 3130 | Blackburn South | Crossarm
A Downer construction crew attended and installed LV parallels to maintain supply to customers supplied from the transformer whilst the HV intermediate crossarm was replaced under Access Authority conditions. | 1 GREEN ACRES COURT, LANGWARRIN VIC 3910 | LIS No. 3311334 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Per Select Solutions Asset Inspector - HV crossarm tracking under the footpath side insulator. Following light drizzly rain the previous day, a HV intermediate crossarm fire occurred at "Potts-Cranbourne" substation at pole No. LIS 3311334 located outside 1 Green Acres Court, Langwarrin. No high voltage injection or damage was sustained following the red phase brown fog HV insulator tracking to the timber crossarm. | Crossarm (wood) | 0 | 0 | 0 |  | LWN 21 | During light drizzle, the red phase brown fog HV insulator was tracking to the timber crossarm. | Pole-top fire | 42675.7986 | 1 | Negligible: no ground fire | 605 | Roadway |  | 20160115UTD_4 | Infrastructure (network-based) | -38.1408 | 145.2116 | 1 | United Energy Distribution | Report | 913 | 0.015346 | 22kV AC | Moorabbin Airport | 3910 | Langwarrin | Crossarm
Fault crew dispatched, DAO notified. Made safe & repaired. The faulty transformer was replaced. | 659 HEALESVILLE-YARRA GLEN ROAD, TARRAWARRA VIC 3775 | 1009408 |  | Heat |  | Electrical breakdown |  | Phase to earth | 1 | IMS 220011. During high activity, customer claims there is a small fire at base of pole lis #19408. There was a transformer fault that resulted in a flashover between a HV fuse unit and the earth on the concrete pole. This resulted in the feeder ACR at LD318 to operate. The fire was confined to the short grass at the base of the pole. The ground was dry and very little grass as this is in a cow paddock. The Fire Danger Rating was Extreme on the day and the temperature was 43 C. | Boric acid;Pole mounted;Transformer;Pole (concrete) | 0 | 0 | 0 |  | ldl14 | Faulty transformer - Transformer Failure Electrical Failure. | Grassfire | 14/01/2016 19:30 | 1 | Localised: less than 10 sq.m | 618 | Agricultural |  | 20160117SPN_01 | Infrastructure (network-based) | -37.6546 | 145.4329 | 1 | AusNet Services Distribution | Report | 929 | 0.0069745 | 22kV AC | Moorabbin Airport | 3775 | Tarrawarra | AF Other
Made safe | 645 GEELONG ROAD, BROOKLYN VIC 3012 |  |  |  |  | Conductor clashing |  |  | 2 | Grass fire at property caused by conductor clashing | Conductor (bare) | 0 | 0 | 0 |  |  | Conductor clashing | Grassfire | 17/01/2016 15:10 | 1 | Localised: less than 10 sq.m | 620 | Industrial |  | 20160118JEM_01 | Infrastructure (network-based) | -37.8193 | 144.8416 | 1 | Jemena | Report | 933 | 0.019271 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | Conductor
The attending Powercor Fault Crew replaced the O/H Service Cable, removed the Pole Junction Box and terminated the new O/H Service Cable directly to the reticulation conductors. The Fault Crew also completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, confirmed 0.3 Volts following replacement of the O/H Service Cable. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 87 POWELL STREET, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  |  | 2 | Miss Grace Mowatt received an electric shock while she was washing dishes in the kitchen sink when she made simultaneous contact with one hand on the kitchen tap and her other hand on the kitchen sink. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Junction Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 12 Volts on the water piping system and between the points of contact. | Customer installation | 0 | 0 | 0 |  |  | Corroded connection | Minor shock | 24/11/2015 12:00 |  |  | 621 | Residential |  | 20160118PWA_01 | Infrastructure (customer connection) | -38.2651 | 144.526 | 1 | Powercor | Report | 934 | 0.0045532 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Crew isolated supply and arranged repairs | 75A MCCURDY ROAD, HERNE HILL VIC 3218 |  | Working too close to underground cables;Theft | [5 empty] | 1 | A civil contractor installing optic fibre cable reported that they had drilled through a cable at the incident location. On arrival the crew found that an under road boring unit had struck a 3 phase low voltage underground cable between a pole and the underground pit resulting in damage to the cable. The contractor had undertaken DBYD enquiries. Upon further inspection the crew found that at an earlier (unknown) date, an unrelated theft by unknown third parties, had occurred at the installation being fed from the underground cable. Part of the costumers private mains from ground level to the customers meter box had been stolen, along with the entire contents of the meter box, meter board and the meter itself. One phase of the three phase underground was still alive at ground level below the meter box, the other two phases had blown fuses at the FOLCB believed to be due to being contacted by the boring unit as the contractor reported hearing a noise at the time of contact. There was no ground fire. There were no reported injuries. | Services cable | 0 | 0 | 0 |  |  | Contractor dig-in and theft by unknown third parties | No Go Zone (contact);Damage to network assets | 42675.6062 |  |  | 634 | Roadway |  | 20160118PWA_06 | Infrastructure (network-based) | -38.1389 | 144.3183 | 1 | Powercor | Report | 962 | 0.0051088 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Herne Hill | Dug up
The attending Powercor Fault Crew reterminated the existing O/H Service Neutral connection and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, confirmed Zero Volts under normal load conditions. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H service cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 2 85 WOODEND ROAD, WARRNAMBOOL VIC 3280 |  |  |  |  | Corrosion |  |  | 2 | Ms Tennille Scott was showering when she received an electric shock as she made simultaneous contact between her hands on the metal shower taps and feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Junction Box located on the Reticulation Service Pole, causing a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 5.8 Volts on the water piping system and between the points of contact. | Customer installation | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral Conductor termination at the Junction Box at the Reticulation Service Pole | Minor shock | 42675 |  |  | 638 | Residential |  | 20160118PWA_08 | Infrastructure (network-based) | -38.3592 | 142.4715 | 1 | Powercor | Report | 968 | 0.0099248 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Fault crew made safe and made repairs. Candled fuse was sent to quarantine and the DAO notified. Crews attended site and found one of the 5k EDO fuses had not fully activated and was candling on pole. No evidence of fire or animals at base of pole and suspect lightning causing HV fuses to activate. Crew removed fuse and replaced with another 5k EDO. Crew states that the hinge is too tight causing fuse to hang up which is common for last generation of EDOs. Recommend to replace with BA's. | 15 NOTTS ROAD, CARLYLE VIC 3685 | 5209086 |  |  |  | Age;Corrosion;Electrical breakdown |  |  |  | IMS220039. Fault crew attending INCD 92745-r. Crew reports that the HV fuse had candled. Customer called in all supply failure and fuse down on substation RAU 11. | EDO fuse | 0 | 0 | 0 |  | bwa23 | Crew states that the EDO fuse hinge is too tight causing fuse to hang-up. | Other electricity related | 14/01/2016 20:00 | 1 | Negligible: no ground fire | 628 | Agricultural |  | 20160118SPN_05 | Infrastructure (network-based) | -36.0304 | 146.4692 | 1 | AusNet Services Distribution | Report | 953 | 0.011207 | 22kV AC | Wangaratta Aero | 3685 | Carlyle | Fuse
The incident was attended to by an AusNet Services' fault crew (Downer) to make safe and repair. Line isolated and EAP issued. The crew replaced the PG clamp and the HV conductor. Supply restored. | THOMASTOWN TERMINAL STATION, THOMASTOWN VIC 3074 | 910791 |  |  |  | Corrosion |  | Phase to earth | 1 | A small fire at base of strain pole feeding a substation. Many people on site to make sure fire remains out. The HV bridge on a strain pole became free and produced some arcing due to a poor connection at the PG clamp due to corrosion. There was a ground fire below the pole which burnt approximately one acre of grass paddock / easement which was extinguished by the CFA. Feeder protection operated. | Conductor (bare) | 0 | 0 | 0 |  | TT12 | HV conductor Joint Failure. A poor connection nt out at the PG clamp due to corrosion. A burnt out PG clamp. | Grassfire | 22/12/2015 14:40 | 1 | Medium: 1000 sq.m - 10 ha | 631 | Industrial |  | 20160118SPN_07 | Infrastructure (network-based) | -37.6909 | 145.009 | 1 | AusNet Services Distribution | Report | 964 | 0.017303 | 22kV AC | Essendon Airport | 3074 | Thomastown | Connection
A LEI and faults truck attended and tested the installation to determine the cause. A NST was completed that failed and the LEI measured 67v between an independent earth and the shower rose. The faults crew checked connections and found a corroded neutral connection at the pole end at pole No. LIS 7051105 that caused a high resistance connection. The connection to the line tap was cleaned, greased and re-terminated and a NST was completed after the rectification work that passed. The LEI completed tests that confirmed the fault had been rectified with neutral resistance measured at 0.4ohm and a NST pass. | 21 DIXON GROVE, BLACKBURN VIC 3130 | LIS No. 7051105 |  | Heat |  | Corrosion;Neutral fault |  | Phase to earth | 2 | Caller advised that lights are dimming under load and they received a mild electric shock from the shower on Thursday. The occupier advised that an electric shock was received from the shower tap recently and lights are constantly dimming when the kettle is turned on. | Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | A corroded neutral connection at the pole end that caused a high resistance neutral connection. | Minor shock | 16/01/2016 14:20 |  |  | 657 | Residential |  | 20160119UTD_06 | Infrastructure (network-based) | -37.8123 | 145.1425 | 1 | United Energy Distribution | Report | 996 | 0.035854 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | Connection
Crew checked cable for damages - none found | 1040 LEAKES ROAD, ROCKBANK VIC 3335 |  | Working too close to overhead lines | [5 empty] | 2 | A contractor reported that an underground cable had been hit by excavator at the incident location. On arrival the crew found that a contractor (Matt Salter, Ph: 0417 558 424, Naturform, 11 Production Rd, Melton, Ph: 9746 0099) was undertaking landscaping works and had contacted the conduit of LV public lighting service with an excavator. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Excavator contacted LV assets | No Go Zone (contact) | 15/01/2016 15:55 |  |  | 668 | Commercial |  | 20160120PWA_09 | Infrastructure (network-based) | -37.719 | 144.6544 | 1 | Powercor | Report | 2737 | 0.03567 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected prior to the supply being restored. | 90 HENDERSONS ROAD, BITTERN VIC 3918 | LIS No. 8831124 |  | Heat |  | Fatigue;Electrical breakdown |  |  | 1 | At 1042hrs on 19/01/2016, 22kV feeder ACR MT0447 located in Hendersons Road reclosed to lockout affecting 2981 customers. At the same time, 22kV feeder HGS 23 circuit breaker reclosed to lockout. There was commentary that a customer was putting a fire out after the wires were sparking. HVABC failed midspan in Hendersons Road, Bittern approximately 300m North of Myers Road. This event resulted in the 22kV conductors to arc and a very small grass fire started on the road reserve outside 90 Hendersons Road caused by molten aluminium falling into the dry grass near pole No. LIS 8831124. No major damage was sustained. | Conductor (ABC) | 0 | 0 | 0 |  | HGS 23 | HVABC failing mid-span. | Grassfire | 19/01/2016 10:42 | 1 | Localised: less than 10 sq.m | 662 | Roadway |  | 20160120UTD_02 | Infrastructure (network-based) | -38.3354 | 145.1667 | 1 | United Energy Distribution | Report | 1003 | 0.035894 | 22kV AC | Moorabbin Airport | 3918 | Bittern | OH Cable
CTA/LEI performed voltage test from independent earth spike to neutral bar of main switchboard resulted in a reading of 1 Volt from no load to 90 Volts maximum load. Performed voltage test from independent earth spike to hot water tap at the kitchen sink where Shane felt the slight shock resulted in a reading of 1 Volt no load to 90 Volts maximum load. Performed voltage test from independent earth spike to conductive plumbing fittings throughout premise with maximum 90 Volts. Service crew performed NST test of the Neutral Screen service at POA with fail result recorded. Crew replaced damaged Neutral Screen with a new ABC service. CTA/LEI performed NST test at installation switchboard with a pass result recorded. CTA/LEI Performed voltage test from independent earth spike to the neutral bar of the MSB, conductive plumbing fittings and installation general mass of earth resulting in a reading of 1 Volt at no load, and 1 Volt maximum load. A final NST test was carried out by the CTA / LEI with a pass result again recorded. Installation left ON supply. | 41 TELETA CRESCENT, CORIO VIC 3214 |  |  |  |  | Age |  |  | 2 | Shane was standing at the kitchen sink and received a slight shock to his left hand when he came in contact with the hot water tap. The sheath of the Neutral Screen LV o/h service was deteriorated causing the neutral screen to corrode and break, and deterioration of the active conductor insulation. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 90 Volts on the water piping system. | Service conductor | 0 | 0 | 0 |  |  | Deteriorated LV service cable | Minor shock | 42370.7083 |  |  | 672 | Residential |  | 20160121PWA_02 | Infrastructure (network-based) | -38.072 | 144.361 | 1 | Powercor | Report | 1014 | 0.0055671 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | OH Cable
Crew checked line for damages, none found | 3215 HAMILTON-CHATSWORTH ROAD, WOODHOUSE VIC 3294 |  |  | Bird |  |  |  |  | 1 | A field crew attending an outage found that a swan had contacted a 66kV line and fallen to the ground resulting in a ground fire (Approx. 2000 sqm) on the road reserve. There were no reported injuries. Protection operated. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 15/01/2016 12:33 | 1 | Medium: 1000 sq.m - 10 ha | 677 | Roadway |  | 20160121PWA_06 | Infrastructure (network-based) | -37.7908 | 142.3666 | 2 | Powercor | Report | 1020 | 0.004316 | 66kV AC | Hamilton Airport | 3215 | Woodhouse | Animal
Crew isolated supply and undertook repairs | LOT 46A ELMHURST-GLENPATRICK ROAD, ELMHURST VIC 3469 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole, which burnt through the cross arm causing the conductor to fall and rest on the stay. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 20/01/2016 10:58 | 1 | Negligible: no ground fire | 681 | Agricultural |  | 20160121PWA_08 | Infrastructure (network-based) | -37.1737 | 143.2517 | 1 | Powercor | Report | 1025 | 0.010325 | 22kV AC | Ballarat Aerodrome | 3469 | Elmhurst | Crossarm
Crew checked pole and arranged inspection and repairs | 397 THE ESPLANADE, ST LEONARDS VIC 3223 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | CFA reported a fire at the incident location. On arrival, the crew found a that a pole fire had occurred on a 22kV pole which burnt the top of the pole resulting in a ground fire (Approx. 15m x 20m) near the base of the pole. The pole top structure remained in place. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 21/01/2016 13:32 | 1 | Small: 10 - 1000 sq.m | 683 | Roadway |  | 20160121PWA_10 | Infrastructure (network-based) | -38.1522 | 144.7157 | 1 | Powercor | Report | 1027 | 0.024001 | 22kV AC | Avalon Airport | 3223 | St Leonards | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the HV off-set intermediate crossarm was replaced under Access Authority conditions prior to the supply being restored. | 694 HIGHBURY ROAD, GLEN WAVERLEY VIC 3150 | LIS No. 0604517 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Victoria Police advised of a pole fire near the fire station on the corner of Highbury and Springvale Roads, Glen Waverley. Following light rain after a extended spell of hot weather, a HV crossarm fire occurred on a HV/LV pole with off-set intermediate construction (LIS No. 0604517) located outside 694 Highbury Road, Glen Waverley. The pole fire originated at the HV crossarm near the kingbolt that resulted in the HV conductor hanging approximately 150mm from the LV conductors. A LEI was dispatched to the site as the faults crew suspected that a HVI may have occurred. The LEI inspected properties in the vicinity and confirmed that a HVI did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | EB 32 | Probable insulator tracking following light rain after an extended dry spell. | Pole-top fire | 20/01/2016 12:05 | 1 | Negligible: no ground fire | 678 | Roadway |  | 20160121UTD_02 | Infrastructure (network-based) | -37.8626 | 145.1724 | 1 | United Energy Distribution | Report | 1021 | 0.017867 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Crossarm
The employee stopped work and assessed injuries, retested the GPO status with one tester and found it dead, retested with another tester and found it to be alive. It was then established that the GPO was supplied via the 30v battery bank charger circuit. The employee then isolated the GPO. All other installations were checked to determine if this hazard existed. One site was identified and actions taken to remedy this. To prevent future such incidents, the procedure "Precautions for Work on or Near Secondary LV Electrical Apparatus" has been updated and communicated to Electrical Plant and Test employees. | LOT 1 KERRS ROAD, MADDINGLEY VIC 3340 | [5 empty] | Incorrect electrical isolation and/or permits;Faulty tools/plant/equipment |  | 2 | Whilst working on a project to install infrastructure to support zone sub station control rooms an employee received a minor electrical shock from making contact with a live GPO. | Zone substation | 0 | 0 | 0 |  |  | Circuit was unexpectedly alive and employees tester did not identify circuit was alive. | Minor shock | 18/09/2015 0:00 |  |  | 692 | Commercial |  | 20160122PWA_05 | Infrastructure (network-based) | -37.6995 | 144.4087 | 1 | Powercor | Report | 1041 | 0.0055347 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Other
Crew isolated supply for repairs | 61B FITZROY STREET, ST KILDA VIC 3182 |  | Vehicle | [5 empty] | 2 | A garbage contractor reported that a garbage truck had contacted equipment at the incident location. On arrival the crew found that a garbage truck (operated by City Wide Solutions Pty Ltd, Contact: Nick, Ph: 9261 5000) was driving down a narrow alley and contacted a krone box mounted on the side of the building resulting in damage to the krone box and attached low voltage underground cable and loss of supply to a number of shops. There was no ground fire. There were no reported injuries. | Connection box | 0 | 0 | 0 |  |  | Garbage truck contacted krone box | Damage to network assets | 22/01/2016 5:33 |  |  | 694 | Roadway |  | 20160122PWA_07 | Infrastructure (network-based) | -37.8613 | 144.9754 | 1 | CitiPower | Report | 1045 | 0.015341 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Vehicle
Crew isolated supply and undertook repairs. LEI checked installation for damages. | 152 WADES ROAD, HARROW VIC 3317 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 12.7kV SWER angle pole which burnt the top of the pole causing the SWER conductor to fall into the angle and onto the roof of a shed resulting in a high voltage injection which caused damage to the electrical installation in the shed. Protection operated. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole Fire | Pole-top fire;HV injection | 22/01/2016 4:36 | 1 | Negligible: no ground fire | 696 | Agricultural |  | 20160122PWA_09 | Infrastructure (network-based) | -37.2045 | 141.7053 | 1 | Powercor | Report | 1049 | 0.0027465 | 12.7kV AC (SWER) | Hamilton Airport | 3317 | Harrow | Pole
Crew isolated supply and undertook repairs. | 67 FITZGERALD STREET, PORTLAND VIC 3305 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  |  | A field crew attending an outage found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break and the conductors to fall to the ground, resulting in a ground fire (Approx. 1 sqm) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross-arm fire | Grassfire | 18/12/2015 19:46 | 1 | Localised: less than 10 sq.m | 698 | Roadway |  | 20160122PWA_11 | Infrastructure (network-based) | -38.3346 | 141.5897 | 1 | Powercor | Report | 1053 | 0.022685 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Crossarm
Crew isolated supply and undertook repairs. | LOT 1 TWOMEYS BRIDGE ROAD, GAZETTE VIC 3289 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  |  | A field crew patrolling a line following an outage found that a failed surge arrester had caused a pole fire. There was no ground fire. There were no reported injuries or third party damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 26/12/2015 13:44 | 1 | Negligible: no ground fire | 699 | Agricultural |  | 20160122PWA_12 | Infrastructure (network-based) | -37.8843 | 142.153 | 1 | Powercor | Report | 1054 | 0.032256 | 22kV AC | Hamilton Airport | 3289 | Gazette | AF Other
Fire was out on arrival of the fault crew. The fault crew made safe, fixed fault, supply to customers restored and CEOT organized for a fire report to be completed. Shutdown was arranged to replace the wood crossarm to a steel crossarm and new post type insulators were installed. | 36 STATION ROAD, SEVILLE VIC 3139 | 1004314 |  | Industrial or urban pollution;Prone to dust deposition |  | Leakage |  | Phase to phase | 2 | IMS 220165. Brown fog type 22kV type insulator (road side) on an intermediate crossarm failed due to pollution/dust which caused tracking and burnt the crossarm which caused burning embers resulting in a small grass fire 30cm x 30cm in size. | Pole (wood);Crossarm (wood);Insulators | 0 | 0 | 0 |  | wyk12 | HV insulator failure due to pollution/dust build-up causing current/voltage tracking to wood HV crossarm. | Grassfire | 24/01/2016 12:25 | 1 | Localised: less than 10 sq.m | 704 | Residential |  | 20160124SPN_01 | Infrastructure (network-based) | -37.7722 | 145.4593 | 1 | AusNet Services Distribution | Report | 1060 | 0.0041956 | 22kV AC | Moorabbin Airport | 3139 | Seville | Crossarm
CFA where on site and had found the transformer black and burnt. The CFA advised the fire looks to have been deliberatly lit from the outside. The transformer isolated and made safe. The transformer was changed to a 500kVA and 2 x LV circuits were straight jointed and re-terminated, the HV required two new 400 Amp elbows. The crew worked into the early hours of the morning but couldn't finish it until the next day. | 27 TOPTANI DRIVE, NARRE WARREN SOUTH VIC 3805 |  |  |  |  | Electrical overload |  | Phase to earth | 2 | A fault crew attended a report that a transformer was on fire. The CFA attended a reported fire at our kiosk substation which is called Topani Minton. The CFA had said that the fire was deliberately lit at the base of the kiosk, the day was hot and a total fire ban. The substation was isolated and the fire extinguished. There was 161 customers off supply, 111 of which were put back on under parallel but 50 were left overnight until repairs were completed. The substation fitters upon arrival that evening reported that the fire was not deliberately lit but due to 2 x LV circuits shorting to ground due to overload of the 300kVA transformer. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | cln14 | 2 x LV circuits in kiosk substation burnt out / shorting to earth due to overload of the 300kVA transformer. | Loss of supply;Plant/equipment | 19/01/2016 16:40 | 0 | Negligible: no ground fire | 706 | Residential |  | 20160124SPN_03 | Infrastructure (network-based) | -38.0629 | 145.3158 | 1 | AusNet Services Distribution | Report | 1064 | 0.012566 | Low voltage AC (<1kV) | Moorabbin Airport | 3805 | Narre Warren South | Other
CEOT dispatched fault crew. The HV conductor was immediately de-energised in order to make safe, then isolated in order to allow fire authorities access. The conductor was inspected and found to be OK. The tree was removed and power restored. Before power was restored the poles either side were inspected for damage and were all OK. The local Field Team Manager has requested the Senior Network Representative to follow up with customer, Kevin Coates at 52 Jarvis Road, Gelliondale, to provide an official warning concerning the dangers involved in felling trees in the vicinity of overhead power lines. | 52 JARVIS ROAD, GELLIONDALE VIC 3971 | 2608223 | Working too close to overhead lines |  |  |  |  | Phase to phase | 2 | IMS 220164. A tree had fallen onto the HV conductor. On arrival the fault crew found the tree sparking only by the leaves of the tree touching the conductor. High impedance fault. The tree was being felled by a 3rd party. No visible fire on the ground. | Conductor (bare) | 0 | 0 | 0 |  | ftr23 | Vegetation: Trees Incident | Other vegetation | 23/01/2016 21:15 | 1 | Negligible: no ground fire | 711 | Agricultural |  | 20160124SPN_08 | Infrastructure (network-based) | -38.6258 | 146.5794 | 1 | AusNet Services Distribution | Report | 1124 | 0.019481 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Gelliondale | Trees
A LEI and faults truck attended and completed a NST that passed. The LEI tested between an independent earth and the bathroom taps and measured 3-9volts and isolated supply. The incoming supply voltage indicated significant imbalance between phases in the overhead reticulation from heavily loaded conductors due to high temperatures and air conditioner use. This imbalance resulted in a rise in voltage on the neutral conductor. The faults crew proceeded to check all connections at the POA, pole and back to the transformer. Upon completion of the reticulation tests, the LEI re-tested the installation and measured 3.5v on the neutral and reconnected supply to the premise. Another trouble order was created for a voltage recorder to be installed to determine if any further rectification work is required. | 36 DUNHAM STREET, RYE VIC 3941 |  |  | Heat |  | Out of balance load |  | Phase to earth | 2 | REC called after being called to the property by the customer after they felt electric tingles from the bathroom water tap in the bathroom. The REC checked and could not find any internal problems. The occupiers received a slight electric shock from the bathroom shower taps this morning and contacted a REC (Simon 0488 006 046) to investigate the cause. The REC could not identify any problems and contacted the United Energy faults and emergencies call centre requesting that a faults truck check connections in the overhead conductors. | No failed asset | 0 | 0 | 0 |  |  | Possible imbalance between phases in the overhead reticulation from heavily loaded conductors due to high temperatures and air conditioner use. This imbalance resulted in a rise in voltage on the neutral conductor. | Minor shock | 18/01/2016 14:00 |  |  | 713 | Residential |  | 20160125UTD_01 | Infrastructure (network-based) | -38.3706 | 144.8041 | 1 | United Energy Distribution | Report | 1075 | 0.0019699 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | AF Other
Emergency high voltage switching was completed and the HV intermediate crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 32 NONNA STREET, OAKLEIGH EAST VIC 3166 | LIS No. 2324203 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Customer called to report that part of the power pole with the insulator has fallen off and is hanging in the air. The electricity supply remains on. During drizzly rain, a pole fire occurred at a HV intermediate crossarm on pole No. LIS 2324203 located outside 32 Nonna Street, Clayton. The footpath side HV conductor remained attached to a burnt section of the timber crossarm, that failed at the crossarm brace causing it to fall onto the LV crossarm. The faults crew checked premises in the area and a HVI did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | CDA 11 | Insulator tracking during light drrizzle caused the timber crossarm to fail at the crossarm brace. | Pole-top fire | 22/01/2016 12:13 | 1 | Negligible: no ground fire | 717 | Roadway |  | 20160125UTD_05 | Infrastructure (network-based) | -37.9002 | 145.117 | 1 | United Energy Distribution | Report | 1079 | 0.010514 | 22kV AC | Moorabbin Airport | 3166 | Oakleigh East | Pole
Crew isolated supply and undertook repairs | 99 FOLEYS ROAD, CASHMORE VIC 3305 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break, however the conductors remained aloft. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 22/01/2016 8:29 | 1 | Negligible: no ground fire | 726 |  |  | 20160127PWA_02 | Infrastructure (network-based) | -38.3127 | 141.5253 | 1 | Powercor | Report | 1098 | 0.035163 | 22kV AC | Portland (Cashmore Airport) | 3305 | Cashmore | Crossarm
Crew isolated supply and arranged repairs | 219 PUNT ROAD, RICHMOND VIC 3121 |  | Vehicle | [5 empty] | 2 | Vic Fire reported that a car had collided with a pole at the incident location. On arrival the crew found that a car (registration TYP-817) had collided with a low voltage pole resulting in wooden pole breaking at the ground and falling over where it hung supported by the low voltage conductors approximately 1.4m above the ground. The driver of the vehicle left the incident site. The incident site was secured by the MFB. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Car hit pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 26/01/2016 3:57 |  |  | 725 | Roadway |  | 20160127PWA_01 | Infrastructure (network-based) | -37.819 | 144.9899 | 1 | CitiPower | Report | 1097 | 0.03112 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Vehicle
Fault crew called, isolated and made safe. On arrival at the substation, the Electrical Fitter confirmed the substation had been broken into. After assessing the situation and damage, the Electrical Fitter recommended an emergency outage be taken to make the situation safe. All copper in our substation has been removed. i.e., LV earths, HV earths, LV transformer leads, Earth screens for HV cable and Earthing bars on HV switchgear. The control room (CEOT) was contacted with this advice and it was agreed an emergency outage would be arranged as Live Line Lineworkers (Glovers) could not break the HV cable head in Canterbury Rd as the transformer could not be isolated due to the damaged HV switch. The fault truck arrived on site at about 3:30pm and the emergency outage affecting approximately 70 commercial customers was taken. This allowed the fault crew to disconnect the HV cable head from the overhead conductors in Canterbury Rd and effectively isolate the substation. The Electrical Fitter made temporary repairs to the substation door and closed it. There are currently no active customer requiring supply from the substation, giving our business time to determine the better long term solution. The owner of the site was advised and negotiations have begun on how to make an alternative supply to the site (the site is currently a Warehouse) until a longer term solution to vandalism of indoor substations is address by AusNet Services' Asset Management team. | 80-86 CANTERBURY ROAD, KILSYTH VIC 3137 |  | Vandalism;Theft | [5 empty] | 2 | IMS 220 212. A client Electrician reported to the Design Team Leader that their switchboard adjacent to our indoor substation Cantbury N80 Lpool had been broken into and copper stolen. He said it looked like our substation had also been broken into and recommended someone come and have a look. An AusNet Services' Electrical Fitter was dispatched from the Lilydale depot to assess the situation. | Indoor | 0 | 0 | 0 |  |  | Theft of copper at indoor substation. | Damage to network assets | 28/01/2016 13:25 |  |  | 746 | Commercial |  | 20160128SPN_01 | Infrastructure (network-based) | -37.8176 | 145.3201 | 1 | AusNet Services Distribution | Report | 1122 | 0.032916 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3137 | Kilsyth | Other
A LEI and faults truck attended and tested the installation. Initial testing indicated 26v between an independent earth to the external water tap and customers earthing system. Supply was immediately disconnected with another voltage test indicating 24v and a NST failed. Further investigation of the installation found there are two sets of consumer mains, one for 740 North Road and another for 740A North Road that are supplied from the same fused mains box at the front of the two installations. Once supply was disconnected at the fused mains box, voltage testing indicated 0.2v on the customers' earthing systems and the external water tap. The faults crew proceeded to check all connections and identified a corroded neutral connection at the pole end. They replaced the three phase grey twisted overhead service with a XLPE type and the LEI re-tested the installation that confirmed the fault had been rectified. | 740 NORTH ROAD, ORMOND VIC 3204 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | REC Brendan Harrison (0439 893 154) called to advise the customer is getting electric shocks from the external water taps. He tested and found between 19 - 38v on the taps even with the main switch turned off. The occupier was receiving slight electric shocks from the water taps and contacted a REC to investigate. The REC measured voltages on the water pipes and contacted the United Energy call centre to investigate the cause. | Connector/termination | 0 | 0 | 0 |  |  | A corroded neutral connection at the pole end. | Minor shock | 25/01/2016 17:10 |  |  | 737 | Residential |  | 20160128UTD_02 | Infrastructure (network-based) | -37.9057 | 145.0523 | 1 | United Energy Distribution | Report | 1111 | 0.025632 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Ormond | Connection
Inspector completed the required tests. Service cable replaced. | 34 CHURCH STREET, WEST FOOTSCRAY VIC 3012 |  |  |  |  | Age |  |  | 2 | Customer received shock from all metal fittings at premise | Service conductor | 0 | 0 | 0 |  |  | Failure of the service | Minor shock | 28/01/2016 18:47 |  |  | 750 | Residential |  | 20160129JEM_01 | Infrastructure (network-based) | -37.7931 | 144.8774 | 1 | Jemena | Report | 1131 | 0.036918 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | OH Cable
CEOT dispatched a fault crew. Crew reported tree had been on conductor and fallen to ground leaving stranded conductor. Isolated supply and made safe. Duty Officer dispatched to investigate fire. CFA on site. The 22kV overhead conductors were repaired and supply restored. | UPPER YARRA DAM ROAD, REEFTON VIC 3799 | 1411245 |  | Fallen |  |  |  | Phase to phase | 1 | IMS 220267. Report of a tree on a HV conductor and of a fire. Report of CFA in attendance. A suspected rotting Stringybark tree located on an approximate 3 metre road embankment east of existing pole #1411245 and approximately 17 metres north of 22kV overhead conductors broke and partly fell on the 22kV overhead conductors with the fault current from the branch between two 22kV phases causing the branch to smoulder and ignite and the ACR & Spur fuse protection WYK23 Feeder to operate. The fire was only contained within the smouldering branch and no other fire damage seen. | Conductor (bare) | 0 | 0 | 0 |  | wyk23 | Vegetation: Trees Incident | Other vegetation | 29/01/2016 14:10 | 0 | Negligible: no ground fire | 759 |  |  | 20160201SPN_01 | Infrastructure (network-based) | -37.6721 | 145.8809 | 1 | AusNet Services Distribution | Report | 1155 | 0.00058912 | 22kV AC | Morwell (Latrobe Valley Airport) | 3799 | Reefton | Trees
Crew undertook repairs | 224 SCOTCHMANS LEAD ROAD, SCOTCHMANS LEAD VIC 3352 |  | Theft | [5 empty] | 2 | A passer-by reported to Powercor Fault Centre a pole had been vandalised; copper wire had been stolen, wires cut & earth wire left exposed at the incident location. On arrival the crew found that a 1 metre section of the Substation LV earth had been cut out and stolen from aq pole type substation structure. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Theft of cables | Damage to network assets | 31/01/2016 15:55 |  |  | 764 | Roadway |  | 20160202PWA_01 | Infrastructure (network-based) | -37.6616 | 143.853 | 1 | Powercor | Report | 1161 | 0.010339 | Earthing cable | Ballarat Aerodrome | 3352 | Scotchmans Lead | Other
Crew isolated supply and undertook repairs. | 1763 BALLARAT-MARYBOROUGH ROAD, BLOWHARD VIC 3352 |  |  | Lightning |  |  |  |  | 1 | CFA reported a ground fire at the incident location. On arrival the crew found that a lightning had struck a 22kV conductor causing the conductor to break and fall to the ground resulting in a ground fire (Approx. 2.5 sqm) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Lightning | Grassfire | 29/01/2016 15:58 | 1 | Localised: less than 10 sq.m | 766 | Roadway |  | 20160202PWA_03 | Infrastructure (network-based) | -37.4347 | 143.7958 | 1 | Powercor | Report | 1164 | 0.027425 | 22kV AC | Ballarat Aerodrome | 3352 | Blowhard | Lightning
Emergency high voltage switching was completed on 11kV feeder OR 32 to minimise the number of customers affected and the HV intermediate crossarm was replaced under Access Authority conditions prior to the supply being restored. | 986 NORTH ROAD, BENTLEIGH EAST VIC 3165 |  |  | Precipitation |  | Insulator;Leakage |  |  | 1 | At 1305hrs on 31/01/2016, 11kV feeder OR 32 circuit breaker reclosed to lockout affecting 1615 customers. Following light drizzly rain after a period of hot weather, a HV intermediate crossarm fire occurred at a 66kV anchor pole with a 11kV tee-off located on the corner of North Road and Marlborough Street, Bentleigh East. The 11kV crossarm had brown fog insulators that were most likely tracking to the 11kV crossarm that caused the crossarm to burn and break. | Crossarm (wood) | 0 | 0 | 0 |  | OR 32 | HV brown fog insulators were most likely tracking to the 11kV crossarm causing it to burn following light rain. | Pole-top fire | 31/01/2016 13:05 | 1 | Negligible: no ground fire | 772 | Roadway |  | 20160203UTD_04 | Infrastructure (network-based) | -37.9076 | 145.069 | 1 | United Energy Distribution | Report | 1175 | 0.019559 | 11kV AC | Moorabbin Airport | 3165 | Bentleigh East | Pole
Fault truck removed damaged service cable and installed new service to property. Property tested, all VESI tests passed. | 52 OAKDENE GROVE S, ALTONA MEADOWS VIC 3028 | [5 empty] | Poor workmanship | Phase to earth | 2 | Mario was trimming a hedge at the time, he severed the service cable to the property with a hedge trimmer. No shock was received. | Service conductor | 0 | 0 | 0 |  |  | Service cable cut with hedge trimmer | Loss of supply | 42073.4306 |  |  | 784 | Residential |  | 20160204PWA_03 | Infrastructure (network-based) | -37.8728 | 144.7587 | 1 | Powercor | Report | 1192 | 0.033134 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Other
Crew isolated supply and undertook repairs | 8840 PRINCES HIGHWAY, PANMURE VIC 3265 |  |  |  |  | Overheated connection |  |  | 2 | CFA reported a fire at the incident location. On arrival the crew found that a connection on a 66kV pole had overheated, resulting in a ground fire (approx. 10m x 2.5m) in the road reserve. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 42431.8146 | 1 | Small: 10 - 1000 sq.m | 801 | Roadway |  | 20160205PWA_01 | Infrastructure (network-based) | -38.3357 | 142.7284 | 1 | Powercor | Report | 1214 | 0.006059 | 66kV AC | Warrnambool Airport Ndb | 3265 | Panmure | Connection
Powercor linesman carried out repairs & CTA carried out all tests and including an N.S.T & Voltage tests following the repair and normal results were obtained. | 6 SHIRLEY STREET, ST ALBANS VIC 3021 |  |  |  |  | Corrosion |  |  | 2 | David received an electric shock when he simultaneously contacted the metallic tap with one hand and the metallic waste with his foot A voltage test between the tap and metal waste of the shower recess identified 76 volts. Further testing of the installation identified a corroded service neutral connection at the customers FMJB. The condition described above caused current to flow in the metallic water pipe system via the installation MEN connection, main earth and water pipe bonding conductors. The level of impedance to the flow of current through the metallic water pipe with respect to the general mass of earth was sufficient to cause a voltage rise of 76 volts on the metallic parts of the plumbing system. | Service conductor | 0 | 0 | 0 |  |  | Corroded service neutral at the FMJB | Minor shock | 15/10/2015 18:00 |  |  | 805 | Residential |  | 20160208PWA_02 | Infrastructure (customer connection) | -37.7368 | 144.7925 | 1 | Powercor | Report | 1596 | 0.019962 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Connection
The attending Powercor Fault Crew replaced the corroded connection, reterminated the O/H Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, the distribution assets and between the points of contact, identified 0.5 Volts following repair works. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 36 BREARLEYS LANE, CHARLEMONT VIC 3217 |  |  |  |  | Corrosion |  |  | 2 | Miss Melissa Amin received an electric shock while she was washing dishes in the kitchen sink when she made simultaneous contact with her hands between the kitchen taps and the metal sink. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded service neutral conductor termination of the O/H service cable at the connection on the reticulation pole as the cause of the high impedance associated with the return path of the neutral current. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 0.8 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | A corroded service neutral conductor termination of the O/H service cable at the connection on the reticulation pole. | Minor shock | 20/10/2015 17:30 |  |  | 808 | Residential |  | 20160208PWA_04 | Infrastructure (network-based) | -38.2042 | 144.3804 | 1 | Powercor | Report | 1597 | 0.020587 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Charlemont | Connection
The attending Powercor Fault Crew replaced the damaged Two Core O/H Service Cable and completed a Polarity and NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system and distribution assets, following replacement of the O/H Service Cable confirmed correct Polarity and Zero Volts on the Neutral conductor and the Main Earthing system. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 2 EDMUND COURT, KANGAROO FLAT VIC 3555 | [5 empty] | Ineffective planning/procedures/processes |  |  | Mr Graham Burt was standing on the metallic verandah roof trimming and removing vegetation near the O/H Service Cable located at the Customerâ€™s Point of Attachment when he inadvertently and partially cut through both the Active and Neutral conductors of the O/H Service Cable with a set of metallic insulated handle pruning shears. A visual inspection of the O/H Service Cable at the POA identified evidence of an Arcing Fault that occurred when the metallic shears severed the insulation of the cable cores and simultaneously contacted the active and neutral conductors of the O/H Service Cable causing a â€œshort-circuitâ€ between the conductors which resulted in damage to the pruning shears. Mr Burt advised that he was startled by the resultant Arc and Flash, however did not receive an electric shock as initially reported. | Service conductor | 0 | 0 | 0 |  |  | The O/H Service Cable supplying the property was damaged when Mr Burt inadvertently and partially cut through both the Active and Neutral conductors of the O/H Service Cable while trimming and removing vegetation located at the Customerâ€™s Point of Attachment. | No Go Zone (contact) | 23/10/2015 11:00 |  |  | 814 | Residential |  | 20160208PWA_10 | Infrastructure (network-based) | -36.7883 | 144.2389 | 1 | Powercor | Report | 1227 | 0.038295 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Kangaroo Flat | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the three HV insulators were replaced under Access Authority conditions prior to the supply being restored. | 2 NEPEAN PLACE, PORTSEA VIC 3944 | LIS No. 1307262 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 1625hrs on 27/01/2016, 22kV ACR RB7401 located in Point Nepean Highway reclosed to lockout affecting 583 customers. Caller reports the power pole is on fire outside 2 Nepean Place and the CFA are on site. Following light misty rain, a pole fire occurred due to tracking between the HV and LV crossarms that caused superficial damage to the timber pole. It appeared a brown HV fog type insulator had been struck by lightning and was damaged at pole No. LIS 1307262. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | STO 22 | A brown HV fog type insulator had been struck by lightning. | Pole-top fire | 27/01/2016 16:25 | 1 | Negligible: no ground fire | 806 | Roadway |  | 20160208UTD_02 | Infrastructure (network-based) | -38.3207 | 144.7133 | 1 | United Energy Distribution | Report | 1219 | 0.023184 | 22kV AC | Avalon Airport | 3944 | Portsea | Pole
Replaced crossarm | 58 ROBERTS ROAD, AIRPORT WEST VIC 3042 |  |  |  |  | Leakage |  |  | 2 | Broken high voltage crossarm caused by crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 27/08/2015 17:00 | 1 | Negligible: no ground fire | 833 | Residential |  | 20160209JEM_04 | Infrastructure (network-based) | -37.7255 | 144.8758 | 1 | Jemena | Report | 5515 | 0.026826 | 22kV AC | Essendon Airport | 3042 | Airport West | Crossarm
Replaced crossarm | 90 THE CROSSWAY, KEILOR EAST VIC 3033 |  |  |  |  | Leakage |  |  | 2 | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42006.3479 | 1 | Negligible: no ground fire | 834 | Residential |  | 20160209JEM_05 | Infrastructure (network-based) | -37.7465 | 144.8574 | 1 | Jemena | Report | 5512 | 0.030645 | 22kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
Replaced crossarm | 75 STERLING DRIVE, KEILOR EAST VIC 3033 |  |  |  |  | Leakage |  |  | 1 | Crossarm fire | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42006.5264 | 1 | Negligible: no ground fire | 837 | Residential |  | 20160209JEM_07 | Infrastructure (network-based) | -37.7411 | 144.8532 | 1 | Jemena | Report | 5511 | 0.03575 | 22kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
Crew isolated supply and undertook repairs | 109 CROMER AVENUE, SUNSHINE NORTH VIC 3020 |  |  |  |  | Overheated connection |  |  |  | MFB reported a crossarm fire at the incident location. On arrival the crew found that a connection had overheated in a crossarm mounted LV fuse box resulting in the fuse box melting and falling to the ground. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Pole-top fire | 31/01/2016 4:47 | 1 | Negligible: no ground fire | 842 | Roadway |  | 20160210PWA_01 | Infrastructure (network-based) | -37.7503 | 144.8345 | 1 | Powercor | Report | 1265 | 0.0040926 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Connection
Crew isolated supply for repairs | 2541 FINLAY ROAD, KOYUGA VIC 3622 |  |  |  |  | Unknown technical factor |  |  | 2 | A REC reported a fire at the incident location. On arrival the crew found that a fire had started in the vicinity of the meter panel in the dairy. The meter panel and an area of the surrounding building structure was damaged in the fire. The crew were unable to determine the cause of the fire due to damage caused. There were no reported injuries. | Meter board (including fuses) | 0 | 0 | 0 |  |  | Crew unable to determine cause due to damage to caused | Property;Meter board;More than $50k damage | 42431.6792 |  | Small: 10 - 1000 sq.m | 847 | Agricultural |  | 20160210PWA_05 | Infrastructure (network-based) | -36.2549 | 144.8842 | 1 | Powercor | Report | 1271 | 0.011096 | Low voltage AC (<1kV) | Shepparton Airport | 3622 | Koyuga | AF Other
CEOT dispatched fault crew to make safe and investigate. Fault crew confirmed that no one was hurt and no damage to AusNet Services' assets. DAO advised of incident. Ausnet Services' crew leader and lineworker spoke with the customer and helped to calm him after the event. The DAO conducted an investigation on 10/2/16 and the HV conductors were measured at incident site point of contact to be 5. 3 metres at 9:00 am. Follow-up survey by the Benalla depot survey party was conducted on 15/02/16. Pole 73 to be replaced with a 14-8W pole and conductors to be restrung to increase ground clearance. Follow-on notification 100875458 raised and forwarded to the Planning Team Manager North Region to raise a work order - action item raised. A No Go Zone Rules breach letter and brochures were mailed to the customer on 18/02/16 along with advice of proposed works to increase the HV conductor height. | 2037 CARBOOR-EVERTON ROAD, CARBOOR VIC 3678 | 5100635 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 220409. Farmer Christopher Box of Property 2037 Carboor Everton Rd, whilst moving a tractor to install fence posts the tractor came into contact with overhead 22kV conductors. Christopher stayed on the tractor and reversed it away. The tractor sustained 3 blown tyres where the electricity exited to earth leaving burn marks on the ground. Both Christopher and his helper who was walking beside the tractor when the incident occurred were unhurt but very shaken from the event. Successful Reclose on WN009 at 16:27. No fire service attended. | Conductor (bare) | 0 | 0 | 0 |  | wn5 | A farmer caused a tractor (with fence post drilling rig attachment) to make contact with overhead HV conductors. | No Go Zone (contact) | 42615.6854 |  |  | 844 | Agricultural |  | 20160210SPN_01 | Infrastructure (network-based) | -36.6087 | 146.536 | 1 | AusNet Services Distribution | Report | 1268 | 0.013652 | 22kV AC | Wangaratta Aero | 3678 | Carboor | Vehicle
Crew undertook repairs | 27 CARRINGTON DRIVE, SUNSHINE VIC 3020 |  | Vandalism | [5 empty] | 2 | A passer by reported that copper earths had been stolen from pole at the incident location. On arrival the crew found that the high voltage copper earth from the substation had been severed but not stolen. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Vandalism/attempted theft | Damage to network assets | 42492.5597 |  |  | 851 | Roadway |  | 20160211PWA_03 | Infrastructure (network-based) | -37.771 | 144.8099 | 1 | Powercor | Report | 1276 | 0.021943 | Earthing cable | Laverton Raaf | 3020 | Sunshine | Other
Crew isolated supply and arranged repairs | 115-117 WILLIAM ANGLISS DRIVE, LAVERTON NORTH VIC 3026 |  |  |  |  | Overheated connection |  |  | 1 | A HV customer reported smoke coming from HV box at the incident location. On arrival, the crew found that a connection on a LV fuse at a kiosk substation had overheated casing the LV fuse board to catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Pad mounted equipment/kiosk;Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Other electricity related | 42584.35 | 1 | Negligible: no ground fire | 853 | Industrial |  | 20160211PWA_05 | Infrastructure (network-based) | -37.8162 | 144.7818 | 1 | Powercor | Report | 1278 | 0.029834 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Connection
Crew isolated supply and arranged repairs | 24 WILTSHIRE LANE, DELACOMBE VIC 3356 |  |  |  |  | Unknown technical factor |  |  | 1 | VicFire reported a transformer fire at the incident location. On arrival the crew found that a transformer fire had occurred in a kiosk transformer which burnt the transformer and cable connections. The fire was contained to the kiosk enclosure. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. The crew were unable to determine the cause of the fire. | Pad mounted equipment/kiosk | 0 | 1 | 0 |  |  | Crew unable to determine. | Other electricity related | 42645.4125 | 1 | Negligible: no ground fire | 857 | Industrial |  | 20160211PWA_08 | Infrastructure (network-based) | -37.576 | 143.8089 | 1 | Powercor | Report | 1282 | 0.019275 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3356 | Delacombe | AF Other
Crw isolated supply and undertook repairs | 7286 PRINCES HIGHWAY, TYRENDARRA VIC 3285 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported wires down and a grass fire at the incident location. On arrival the crew found that a pole fire had occurred on a 66kV pole, causing the insulator and conductor to fall away from the pole but remain suspended above the ground, resulting in a ground fire (approx. 100m x 100m) on the road reserve and private property. Protedction operated. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 14/02/2016 17:36 | 1 | Medium: 1000 sq.m - 10 ha | 871 | Agricultural |  | 20160216PWA_01 | Infrastructure (network-based) | -38.2183 | 141.7639 | 1 | Powercor | Report | 1299 | 0.017236 | 66kV AC | Portland (Cashmore Airport) | 3285 | Tyrendarra | Pole
Crew isolated supply and undertook repairs | 206 HIGH STREET, WINDSOR VIC 3181 |  |  |  |  | Overheated connection |  |  | 1 | MFB reported that overhead cables had fallen to the ground at the incident location. On arrival the crew found an IPC connection on the overhead LV mains had overheated causing the LV mains cable to break and fall to the ground, across four parked cars. Protection operated. There was no ground fire. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection | Less than $50k damage | 16/12/2015 20:10 |  |  | 875 | Roadway |  | 20160218PWA_01 | Infrastructure (network-based) | -37.8522 | 144.9948 | 1 | CitiPower | Report | 8005 | 0.019328 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Windsor | Connection
Crew isolated supply and undertook repairs | 416 BARINGHUP ROAD, CARISBROOK VIC 3464 |  |  |  |  | Unknown technical factor |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that a grass fire (Approx. 5m x 30m) had started approximately 10m out from the pole. The crew inspected the pole top and found evidence of burning on the centre phase conductor near the armour rod. The crew were unable to determine a cause for the burn mark. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Unable to be determined | Grassfire | 16/02/2016 12:48 | 1 | Small: 10 - 1000 sq.m | 876 | Roadway |  | 20160218PWA_02 | Infrastructure (network-based) | -36.975 | 143.8824 | 1 | Powercor | Report | 1305 | 0.037029 | 22kV AC | Bendigo Airport | 3464 | Carisbrook | Conductor
Crew isolated supply and undertook repairs | 729 CRESWICK ROAD, WENDOUREE VIC 3355 |  |  |  |  | Overheated connection |  |  | 1 | A nearby customer reported sparking on a pole and a ground fire start at the incident location. On arrival the crew found that a connection had overheated on a 22kV switch causing hot debris to fall to the ground resulting in a ground fire (Approx. 25m x 8m) on the road reserve. Protection operated. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 17/02/2016 13:57 | 1 | Small: 10 - 1000 sq.m | 878 | Roadway |  | 20160218PWA_04 | Infrastructure (network-based) | -37.5375 | 143.849 | 1 | Powercor | Report | 1307 | 0.03302 | 22kV AC | Ballarat Aerodrome | 3355 | Wendouree | Connection
Crew isolated supply and undertook repairs | 1063 LORENZS ROAD, KATUNGA VIC 3640 |  |  |  |  | Overheated connection |  |  | 2 | Vic Fire reported a fire at the incident location. On arrival the crew found that a connection had overheated in a LV FSD causing hot debris to fall to the ground resulting in a ground fire (Approx. 11m x 60m) in the road reserve. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 21/02/2016 9:05 | 1 | Small: 10 - 1000 sq.m | 893 | Roadway |  | 20160222PWA_03 | Infrastructure (network-based) | -36.0211 | 145.5056 | 1 | Powercor | Report | 1325 | 0.03374 | Low voltage AC (<1kV) | Shepparton Airport | 3640 | Katunga | Connection
Crew isolated supply and undertook repairs | 21-25 CHAMBERS ROAD, ALTONA NORTH VIC 3025 |  | Vehicle | [5 empty] | 1 | A nearby customer reported that a high load truck had hit wires and they were hanging very low touching the ground still connected to poles at the incident location. On arrival the crew found that LV conductors had been contacted by an unknown vehicle and had fallen to the ground and across a vehicle parked beneath the cables, causing minor damage to the vehicle. There was no vehicle on site when the crew arrived. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV conductors | No Go Zone (contact) | 42645.8076 |  |  | 897 | Roadway |  | 20160223PWA_02 | Infrastructure (network-based) | -37.8419 | 144.8412 | 1 | Powercor | Report | 1332 | 0.026236 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Vehicle
Crew removed balloons from line | 107 CHARLES STREET, FITZROY VIC 3065 |  | Recreation - Helium (party) balloons | [5 empty] | 2 | A passer-by reported metallic balloons tangling among conductors and sparking at the incident location. Upon arrival, the crew found that helium balloons had contacted LV conductors cayusing sparking of the lines. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Balloons in contact with LV cables | Interference with electrical assets;Other | 42676.5528 |  |  | 899 | Roadway |  | 20160223PWA_04 | Infrastructure (network-based) | -37.8033 | 144.983 | 1 | CitiPower | Report | 1334 | 0.036632 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Other
Police attended, crew made site safe | 147 DERRIMUT ROAD, DERRIMUT VIC 3030 |  | Vandalism;Theft | [5 empty] | 2 | Sectrol Security reported a break in at the incident location (Truganina ZSS construction sit). The offenders, having been disturbed by Security, fled on foot abandoning their vehicle which had become bogged. On arrival the crew found a fence gate padlock broken, also, the fence had been cut. It was subsequently determined nothing was taken during this incident. There were no reported injuries or other third party damage. The site was made secure. Police attended and arranged for the offenders abandoned vehicle to be removed. | Zone substation | 0 | 0 | 0 |  |  | Attempted theft | Damage to network assets | 13/02/2016 23:57 |  |  | 904 | Construction |  | 20160223PWA_09 | Infrastructure (network-based) | -37.806 | 144.7524 | 1 | Powercor | Report | 1339 | 0.005581 | Not applicable | Laverton Raaf | 3030 | Derrimut | Other
Crew inspected pole | 1 PLAYFAIR STREET, EDDINGTON VIC 3472 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A field crew found that a pole fire had occurred on a 22kV pole below the bolt on the cross arm straps. The pole had a burnt strip approx. 300mm down from the bolt. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 16/02/2016 14:49 | 1 | Negligible: no ground fire | 909 | Roadway |  | 20160223PWA_14 | Infrastructure (network-based) | -36.882 | 143.8585 | 2 | Powercor | Report | 1344 | 0.03944 | 22kV AC | Bendigo Airport | 3472 | Eddington | Pole
Crew made safe in Pit | 1005 LEAKES ROAD, TARNEIT VIC 3029 |  | Theft | [5 empty] | 2 | A Powercor field crew reported that the customers mains service cable has been stolen at the incident location. On arrival the crew found that unknown third parties had removed the customers LV service cable by cutting it in the pit and near the meter. There were no reported injuries. There was no ground fire. | Customer installation | 0 | 0 | 0 |  |  | Theft | Less than $50k damage | 17/02/2016 8:52 |  |  | 911 | Residential |  | 20160223PWA_16 | Infrastructure (network-based) | -37.8311 | 144.6631 | 1 | Powercor | Report | 1346 | 0.0055926 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Crew isolated supply and arranged repairs | 59 WESLEY STREET, KANGAROO FLAT VIC 3555 |  | Vehicle | [5 empty] | 1 | CFA reported that a vehicle had struck a power pole at the incident location. On arrival the crew found that a vehicle had struck a 66kV stay wire, the force of the impact broke the fluter insulator in the ground stay and the stay made contact with a phase of the subsidiary 22kV circuit causing hot debris to fall to the ground resulting in a ground fire (Approx. 25m x 50m) in the road reserve. Protection operated. There were no reported injuries. | Guy wire | 0 | 0 | 0 |  |  | Car hit pole | Grassfire | 23/02/2016 15:42 | 1 | Medium: 1000 sq.m - 10 ha | 916 | Roadway |  | 20160224PWA_02 | Infrastructure (network-based) | -36.8017 | 144.2328 | 1 | Powercor | Report | 1351 | 0.0035093 | 22kV AC | Bendigo Airport | 3555 | Kangaroo Flat | Vehicle
Crew isolated supply and undertook repairs. | 57-77 MOON STREET, MOOLAP VIC 3224 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the cross-arm. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Pole-top fire. | Pole-top fire | 13/01/2016 7:22 | 1 | Negligible: no ground fire | 931 |  |  | 20160225PWA_04 | Infrastructure (network-based) | -38.1686 | 144.4133 | 1 | Powercor | Report | 1370 | 0.026103 | 22kV AC | Avalon Airport | 3224 | Moolap | Pole
CEOT dispatched the Corryong fault crew from Wodonga to attend the incident to investigate, make safe, isolate and make any necessary repairs. The spur line was isolated at 19:36 and earthed and an EAP issued to allow the tree to be cut clear of the conductor. There was no damage to the conductor or the line. Supply was restored at 20:22. One customer affected. 25/02/16, 09:00, Site investigation conducted by the DAO: The tree line was at approximately 570m along a single span of 993.5m between poles 1(5214832) and 2(5214833). The tree line was at an approximate perpendicular to the conductor. There had been high wind gusts in the area on the day of the incident. The conductor height at the tree line was 10.0m at 25 degrees C when measured at 09:00am on 25/02/16. The two trees that were cut down were approximately 11.0m tall and their trunks were approximately 9.2m, at ground level, from the centreline of the conductor. The fire affected area was measured at approximately 50m x 20m. Other trees on the tree line had previously been trimmed to approximately 7m each side of the conductor centerline. The calculated conductor sway at the tree line is approximately 24m. It is proposed to install a new pole at the tree line to minimize future conductor sway. A survey request has been issued to the Benalla survey team to determine the correct size pole and pole-top structure. The property owner is agreeable to this work. Information from AusNet Services Vegetation Management group: The span was assessed on the 27/08/2015 as a PT365 and cut on 03/12/2015 and signed off as a C720. Actions we are taking to ensure this doesnâ€™t occur again in other long spans: Vegetation & Easement staff will conduct Quality Cut Audits on all spans over 500m to ensure compliance to Electricity Safety (Electric Line Clearance) Regulations 2015. | 214 GUYS FORREST ROAD, BURROWYE VIC 3709 | 5214832 |  | Wind |  |  |  |  | 2 | IMS 220687. CEOT received a report from the CFA of a fire near a powerline at Beers Lane, Burrowye. The attending AusNet Services' fault crew found the SWER overhead conductor caught in the top of a tree with burnt vegetation and grass in the area beneath the line. The fire had been extinguished before the fault crew arrived and no one was at the site. There was no damage to the conductor or the SWER line. DAO notified to investigate the incident. | Conductor (bare) | 0 | 0 | 0 |  | trc01 | Conductor sway due to wind. | Grassfire | 24/02/2016 18:15 | 1 | Small: 10 - 1000 sq.m | 940 | Agricultural |  | 20160229SPN_01 | Infrastructure (network-based) | -36.0174 | 147.543 | 1 | AusNet Services Distribution | Report | 2998 | 0.0016146 | 12.7kV AC (SWER) | Wangaratta Aero | 3709 | Burrowye | Trees
A faults truck attended and sleeved the white phase LV conductor before replacing the HV blue phase 56 amp powder filled fuse along with 3 x 250amp LV fuses for the north circuit of "Glendale-Foote" substation that restored supply to customers in the vicinity. | 10 GLENDALE AVENUE, TEMPLESTOWE VIC 3106 | LIS No. 7057598 |  | Wind |  | Conductor clashing |  |  | 1 | Customers supplied from "Glendale-Foote" substation advised they have lost their electricity supply. The Templestowe Fire Brigade are on site for a fire outside 13 Glendale Avenue. A private tree branch from a gum tree at 10 Glendale Avenue fell onto the LV conductors that caused the white phase conductor to fall to the ground. Sparks from conductor clashing caused a 6sqm grass fire to start on the dry nature strip grass that was quickly extinguished by the Templestowe Fire Brigade. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Grassfire | 25/02/2016 16:05 | 1 | Localised: less than 10 sq.m | 939 | Residential |  | 20160229UTD_01 | Infrastructure (network-based) | -37.7585 | 145.1316 | 1 | United Energy Distribution | Report | 1380 | 0.011582 | Low voltage AC (<1kV) | Moorabbin Airport | 3106 | Templestowe | Trees
Crew isolated supply and undertook repairs | 74 JAMIESON STREET, WARRNAMBOOL VIC 3280 |  |  |  |  | Overheated connection |  |  | 1 | Nearby customers reported a fire at the incident location. On arrival the crew found that a connection on a 22kV Isolator bridge had overheated causing hot debris to fall to the ground resulting in a ground fire (Approx. 4 sqm) on the road reserve. There were no reported injuries. The fire self-extinguished. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 29/02/2016 10:06 | 1 | Localised: less than 10 sq.m | 944 | Roadway |  | 20160301PWA_01 | Infrastructure (network-based) | -38.3746 | 142.4892 | 1 | Powercor | Report | 1387 | 0.00364 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Crew secured site and reported incident to Police | 54 FELLMONGERS ROAD, BREAKWATER VIC 3219 |  | Vandalism;Theft | [5 empty] | 2 | A Powercor project manager reported that there was a break in at the incident location. On arrival the crew found that the chain on the front gate had been cut and unknown third parties had entered the zone substation. The security lights and two security cameras had been vandalised. A shipping container was also broken into however no items appear to have been stolen. There were no reported injuries or third party property damages. | Zone substation | 0 | 0 | 0 |  |  | Theft/Vandalism | Damage to network assets | 22/02/2016 9:10 |  |  | 951 | Other | Substation | 20160301PWA_08 | Infrastructure (network-based) | -38.1803 | 144.3813 | 1 | Powercor | Report | 1394 | 0.012038 | Not applicable | Avalon Airport | 3219 | Breakwater | Other
Crew undertook repairs | 29 JUDGE STREET, SUNSHINE VIC 3020 |  | Vehicle | [5 empty] | 2 | A local resident reported that a truck had contacted a service wire at the incident location. On arrival the crew found that a truck (Owned by JJ Richards & Sons Pty Ltd. 47-59 Benn Court, Derrimut, Ph: 9794 5722, Registration No ZQK-523) which moves rubbish skips had contacted an LV service cable, resulting in the service hooks dislodging at both ends and the service hanging low (approx. 2m above the ground). There was no ground fire. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/02/2016 13:25 |  |  | 954 | Roadway |  | 20160302PWA_02 | Infrastructure (network-based) | -37.7998 | 144.8401 | 1 | Powercor | Report | 1397 | 0.040624 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Vehicle
Crew isolated supply and undertook repairs | 20 SWEETMAN PARADE, OCEAN GROVE VIC 3226 |  |  |  |  | Overheated connection |  |  | 2 | An unknown person from a Caravan Park reported a fire in a street light at the incident location. On arrival the crew found that a fire had started in a street lighting lantern. There was no ground fire. There were no reported injuries or third party property damages | Public lighting | 0 | 0 | 0 |  |  | Street light fire | Pole-top fire | 23/02/2016 15:25 | 1 | Negligible: no ground fire | 956 | Roadway |  | 20160302PWA_04 | Infrastructure (network-based) | -38.2694 | 144.514 | 1 | Powercor | Report | 1399 | 0.013192 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | AF Other
CEOT sent a fault crew to investigate, isolate and make safe. The crew isolated the spur line at pole 47 6672 and attached an HV earth and short circuit. Issued an Access Permit and then proceeded to remove the tree from the HV conductors. They found no other damage to the line once the tree was removed then restored supply. | 169 HIGH STREET, NAGAMBIE VIC 3608 | 4706003 | Working too close to overhead lines |  |  |  |  | Phase to phase | 1 | Seymour fault crew were sent to High Street, Nagambie, with a report of a tree on conductors. Upon arrival they found that the customer was cutting trees on his own property when a gust of wind caught the tree and caused it to fall across the HV conductors feeding into his property. Electrical protection operated - 2xHV fused blown HV fuses 5679172. Property owner details: Michael McNamara, tel. 0437 796042. | Conductor (bare) | 0 | 0 | 0 |  | smr8 | Vegetation: Trees Incident | No Go Zone (contact);Damage to network assets | 18/01/2016 10:26 |  |  | 952 | Agricultural |  | 20160302SPN_01 | Infrastructure (network-based) | -36.7965 | 145.1508 | 1 | AusNet Services Distribution | Report | 1395 | 0.023547 | 22kV AC | Mangalore Airport | 3608 | Nagambie | Trees
Crew isolated supply and undertook repairs | 400 DHURRINGILE ROAD, TATURA VIC 3616 |  | Vehicle | [5 empty] | 2 | Customer reported a wire down at the incident location. On arrival the crew found that a concrete truck (Boral Concreting, Rego: 1CQ - 9AY) was delivering concrete to the site for building extension works and made contact with a LV service cable while driving on the property. The service was pulled out at the pole end. Following repairs the height of the service cable was measured at 3.55m over an area not normally traversable by a vehicle. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Concrete truck contacted LV service cable | No Go Zone (contact);Damage to network assets | 18/02/2016 12:39 |  |  | 962 | Construction |  | 20160303PWA_01 | Infrastructure (network-based) | -36.4477 | 145.2408 | 1 | Powercor | Report | 1405 | 0.016421 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Tatura | Vehicle
Crew isolated supply and undertook repairs | 1 MERRIVALE DRIVE, WARRNAMBOOL VIC 3280 |  |  |  |  | Overheated connection |  |  | 2 | Vic fire reported arcing and sparking on a pole at the incident location. On arrival the crew found that a street light had overheated and caught fire which burnt the light. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Public lighting | 0 | 0 | 0 |  |  | Street light fire | Pole-top fire | 42372.016 | 1 | Negligible: no ground fire | 967 | Roadway |  | 20160303PWA_06 | Infrastructure (network-based) | -38.3841 | 142.4689 | 1 | Powercor | Report | 3069 | 0.035284 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | AF Other
Crew isolated supply and undertook repairs | 148 ALTON ROAD, MOUNT MACEDON VIC 3441 |  |  | Within clearances |  |  |  |  | 1 | Customer reported a wire down at the incident location. On arrival the crew found that a tree had been cut by private contractors (Tree Masters, Owner: Jim Tua, Ph: 0416 963 717 Contact: Tony, Ph: 0424 646 652) working for the customer and had fallen onto the adjacent 22kV conductors, causing one HV conductor to break. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | No Go Zone (contact);Damage to network assets | 25/02/2016 12:33 |  |  | 969 | Roadway |  | 20160303PWA_08 | Infrastructure (network-based) | -37.3925 | 144.5849 | 1 | Powercor | Report | 3061 | 0.0061424 | 22kV AC | Melbourne Airport | 3441 | Mount Macedon | Other
Crew isolated supply and undertook repairs | 10 MITCHELL STREET, SHEPPARTON VIC 3630 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A asset inspector reported a fire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole, which burnt part way through the cross arm. All equipment was still intact. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42372.4361 | 1 | Negligible: no ground fire | 972 | Roadway |  | 20160303PWA_11 | Infrastructure (network-based) | -36.3788 | 145.4201 | 1 | Powercor | Report | 3068 | 0.016454 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the HV/LV pole was replaced under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 442 LOWER DANDENONG ROAD, BRAESIDE VIC 3195 | LIS No. 9519813 | Vehicle |  |  | HV injection |  |  | 1 | At 0441hrs on 29/02/2016, 22kV feeder NP12 circuit breaker reclosed to lockout affecting 1849 customers. A vehicle travelling west has struck a HV intermediate concrete pole with LVABC located on the corner of Lower Dandenong Road and Woodlands Drive (LIS No. 9519813) and also took out several traffic signal poles. The severity of the crash snapped the concrete pole at its base and caused the red phase HV conductor to come off the HV insulator and contact the steel HV crossarm. It appeared the HV conductor had also briefly contacted the street light attached to the pole which was connected to the LV white phase conductor supplied from "Humes-Lower Dandenong" substation. Apart from the street lights, there were only two installations connected to the street circuit which included the United Petrol Station and a South East Water monitoring station. The faults crew requested a LEI attend as a HVI was suspected to the two customers and street lighting supplied from "Humes-Lower Dandenong" substation. The LEI confirmed a high voltage injection occurred (KEY 1602) that caused minor damage to the two installations appliances and equipment. | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  | NP 12 | A vehicle travelling west along Lower Dandenong Road has struck a HV intermediate concrete pole with LVABC. | HV injection;Loss of supply | 29/02/2016 4:41 |  |  | 990 | Roadway |  | 20160303UTD_03 | Infrastructure (network-based) | -37.9878 | 145.1178 | 1 | United Energy Distribution | Report | 1435 | 0.022933 | 22kV AC | Moorabbin Airport | 3195 | Braeside | Vehicle
Faults crew attended and noticed that there was no access to the POA due to a recently constructed verandah. They then checked the connections on the pole and found the neutral conductor of the grey twisted service cable had corroded out where it had a previous repair. The previous repair was cut out and the connections were re-made. The crew then carried out the required tests at the meter box which passed and left the installation off supply till the AusNet Services' LEI arrived. The LEI carried out some tests and found the neutral impedance to be 0.27 Ohm. Voltage tests to an independent earth revealed only 0.9 Volts on the neutral with about 30 Amps of load. installation was left on supply and the customer was issued with a defect notice (NCID) to shift his POA, at which time the service will be replaced. | 6 GALILEE COURT, TRARALGON VIC 3844 | 2604624 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 220183. Customer was showering when he went to turn the taps off and received strong tingles. He then got out of the shower and used a dry towel to turn the taps off before notifying AusNet Services. The tingles were caused by a corroded neutral conductor on the service cable that had a previous repair. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  | tgn11 | A corroded neutral service conductor connection. | Minor shock | 26/01/2016 17:50 |  |  | 995 | Residential |  | 20160304SPN_02 | Infrastructure (network-based) | -38.1964 | 146.5548 | 1 | AusNet Services Distribution | Report | 1441 | 0.032796 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
A faults crew promptly attended the site and disconnected the 250w HPS lantern with the MFB still attendance. A new job was created for the replacement of the defective lantern. | 47 BAMFIELD STREET, HAMPTON VIC 3188 | LIS No. 1817909 | Unknown external/community factor | Unknown environment factor |  | Defective component | Unknown work practice factor |  | 2 | Per MFB - street light fire. The MFB were in attendance for a street light fire outside 47 Bamfield Street near the corner of Bridge Road, Hampton on pole No. LIS 1817909. | Public lighting | 0 | 0 | 0 |  |  | Defective 250w HPS lantern. | Pole-top fire | 42431.875 | 1 | Negligible: no ground fire | 996 | Roadway |  | 20160304UTD_03 | Infrastructure (network-based) | -37.9456 | 145.0096 | 1 | United Energy Distribution | Report | 1442 | 0.034 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton | AF Other
Crew isolated supply and undertook repairs | 10 JAMES STREET, LAVERTON NORTH VIC 3026 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A passerby reported a fire on a pole at the incident location. On arrival the crew found that a cross-arm fire had occurred on a 22Kv cross arm which burnt the arm only. Protection operated. There were no reported injuries, no shocks, no ground fire, no HVI and no third party damage. | Crossarm (wood) | 0 | 0 | 0 |  |  | cross arm fire | Pole-top fire | 42432.1167 | 1 | Negligible: no ground fire | 999 | Roadway |  | 20160307PWA_02 | Infrastructure (network-based) | -37.8346 | 144.7975 | 1 | Powercor | Report | 3073 | 0.0063032 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Crossarm
Fault crew contacted CEOT and replaced the HV fuse. | 24 MARLO PLAINS ROAD, MARLO VIC 3888 |  |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | Fault crew found a candling HV fuse at LIS 1907552 BEMM RIVER 115. Contacted CEOT and replaced. | EDO fuse | 0 | 0 | 0 |  |  | CEOT didn't specify a cause. The incident is currently under investigation. | Other electricity related | 42403.4097 | 1 | Negligible: no ground fire | 1001 |  |  | 20160307SPN_01 | Infrastructure (network-based) | -37.8012 | 148.6382 | 1 | AusNet Services Distribution | Report | 1452 | 0.026696 | 22kV AC | Bairnsdale Airport | 3888 | Marlo | Fuse
CEOT dispatched a fault crew and the DAO to isolate supply, make safe and investigate. | 142 OLD YARRAGON-LEONGATHA ROAD, YARRAGON SOUTH VIC 3823 | 2203698 |  | Lightning | [5 empty] | Customer report to CEOT of a lightning strike and an alleged small fire in the vicinity of the transformer pole. | Pole mounted | 0 | 0 | 0 |  | moe22 | CEOT didn't specify a cause. The incident is currently under investigation. | Grassfire | 42463.7826 | 1 | Localised: less than 10 sq.m | 1004 |  |  | 20160307SPN_02 | Infrastructure (network-based) | -38.2295 | 146.0641 | 1 | AusNet Services Distribution | Report | 1454 | 0.033554 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon South | Lightning
Made safe | 514 BALLARAT ROAD, ALBION VIC 3020 |  |  |  |  | Leakage |  |  | 2 | Pole fire | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire caused by leakage and weather conditions | Pole-top fire | 42463.8438 | 1 | Negligible: no ground fire | 1011 | Industrial |  | 20160309JEM_01 | Infrastructure (network-based) | -37.7761 | 144.8229 | 1 | Jemena | Report | 1466 | 0.011257 | 22kV AC | Essendon Airport | 3020 | Albion | Pole
Crew isolated supply and undertook repairs. | 75 SWAYNS LANE, DEANS MARSH VIC 3235 |  | Working too close to underground cables | [5 empty] | 1 | A fencing contractor reported that he had exposed a white conduit and orange tape at the incident location. On arrival the crew found that the fencing contractor (A & S Mooney, 90 Norman Road, Murroon Vic 3243. Contact: Simon Mooney) was operating a post hole auger and contacted two HV Underground cables in the same trench. The protection operated. There were no reported shocks or injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Contractor was operating a post hole auger and contacted two HV Underground cables in the same trench. | Loss of supply | 29/02/2016 11:10 |  |  | 1014 | Agricultural |  | 20160309PWA_03 | Infrastructure (network-based) | -38.3963 | 143.9308 | 1 | Powercor | Report | 1469 | 0.017647 | 22kV AC | Avalon Airport | 3235 | Deans Marsh | Dug up
Crew isolated supply and undertook reparis | 571 INKERMAN ROAD, CAULFIELD NORTH VIC 3161 |  |  |  |  | Overheated connection |  |  | 2 | A pedestrian reported that there was a wire sparking at the incident location. On arrival the crew found a melted IPC (most likely due to over-heating) and hot debris from this had reached the ground causing a grass fire approximately 2m2 in area. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 42585.6694 |  | Localised: less than 10 sq.m | 1016 | Roadway |  | 20160309PWA_05 | Infrastructure (network-based) | -37.8683 | 145.0134 | 1 | CitiPower | Report | 8010 | 0.0082037 | 22kV AC | Moorabbin Airport | 3161 | Caulfield North | Connection
Crew isolated supply and undertook repairs. | 150A ODESSA AVENUE, KEILOR DOWNS VIC 3038 |  | Theft | [5 empty] | 2 | A customer reported that an earth wire have been removed by persons unknown from sub ODESSA SWINDON opposite 137 Odessa Avenue Keilor Downs. Upon arrival the crew found that the door earth and LV bonding cables at substation ODESSA-SWINDON 1 had been stolen. There were no reported injuries, ground fire or third party damages. | Outdoor | 0 | 0 | 0 |  |  | theft and damage by persons unknown | Loss of supply | 42554.6528 |  |  | 1019 | Public space |  | 20160309PWA_08 | Infrastructure (network-based) | -37.7154 | 144.8054 | 1 | Powercor | Report | 3089 | 0.014135 | 22kV AC | Melbourne Airport | 3038 | Keilor Downs | Other
Crew isolated supply and undertook repairs | UNIT 4 36 BROOKE STREET, NORTHCOTE VIC 3070 |  |  |  |  | Neutral fault |  |  | 2 | Margaret reports receiving an electric shock while in the shower operating the shower taps. Whislt attending site various other flat owners also reported dimming lights and tingles. Tests were carried out using an independent earth and the customers earthing system and 32V was measured on the customer earthing system and shower taps. A burnt out bullet was found to be the cause of the high impedance neutral connection which resulted in current flow through the MEN and customers earthing system causing a voltage rise on the earthing system and connected customers plumbing (shower taps). | Service conductor | 0 | 0 | 0 |  |  | Fault crew repaired the neutral connection. NST testing passed. Voltage checked at point of contact and customer left on supply. | Minor shock | 42403 |  |  | 1024 | Residential |  | 20160309PWA_13 | Infrastructure (customer connection) | -37.7767 | 145.0045 | 1 | CitiPower | Report | 8012 | 0.02085 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
Crew isolated supply and undertook repairs. | 29 DOUEALS ROAD, COLERAINE VIC 3315 |  |  |  |  | Fuse failed to eject |  |  | 2 | A fault crew attending a report of a fire on a pole found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse operated | Plant/equipment | 42585.6472 |  | Negligible: no ground fire | 1026 | Roadway |  | 20160309PWA_15 | Infrastructure (network-based) | -37.6164 | 141.7009 | 1 | Powercor | Report | 3094 | 0.014933 | 22kV AC | Hamilton Airport | 3315 | Coleraine | Fuse
CEOT dispatched to a fault crew and the DAO. Suspected bird flashover on LV bushings of transformer. | 20 BENGWORDEN ROAD, BAIRNSDALE VIC 3875 |  |  | Bird | [5 empty] | Grass fire reported by CFA affecting AusNet Services' assets. A grass fire of 10m x 10m in size was observed by AusNet Services' fault crew. | Transformer | 0 | 0 | 0 |  |  | Incident is currently under investigation. | Grassfire | 42616.7854 | 1 | Small: 10 - 1000 sq.m | 1033 |  |  | 20160310SPN_01 | Infrastructure (network-based) | -37.8496 | 147.5656 | 1 | AusNet Services Distribution | Report | 1490 | 0.033328 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Bairnsdale | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the HV crossarm was replaced under Access Authority conditions prior to the supply being restored. | 52 EVELYN STREET, CLAYTON VIC 3168 | LIS No. 0613913 |  | Precipitation |  | Electrical breakdown;Insulator |  |  | 2 | During an aerial asset inspection of HV infrastructure, a badly burnt crossarm was identified that required urgent replacement. Following light drizzly rain after a dry spell, a HV crossarm fire occurred that was identified by an aerial inspection. The HV/LV pole was located outside 52 Evelyn Street at pole No. LIS No. 0613913 near Dooga Street and the crossarm was found with the end of the crossarm burnt off. | Crossarm (wood) | 0 | 0 | 0 |  | SVW 54 | Probable insulator tracking after light drizzle following a long dry spell. | Pole-top fire | 42432.7653 | 1 | Negligible: no ground fire | 1039 | Roadway |  | 20160310UTD_06 | Infrastructure (network-based) | -37.922 | 145.1306 | 1 | United Energy Distribution | Report | 1495 | 0.036927 | 22kV AC | Moorabbin Airport | 3168 | Clayton | Crossarm
A ZNX construction crew attended and replaced a single phase 19/3.25 aluminium conductor that required replacement following the clashing. Upon completion of the rectification work, the 22kV feeder VR 126 circuit breaker was closed and successfully held. Vic Rail were advised to perform a phase out and supply will be restored when completed. | 107 NICHOLAS STREET, ASHBURTON VIC 3147 | 8803304 |  |  |  | Conductor clashing |  |  | 1 | At 1415hrs on 06/03/2016, 22kV sub-transmission feeder MTS - VR Gardiner 126 opened to lockout - there is no auto reclose on the feeder. The HV feeder was patrolled with no faults identified. Vic Track also inspected their assets and the Network Control Rooms agreed to attempt restoration of the MTS - VR Gardiner 126 feeder at 4.53PM that is located in Malvern Terminal Station. The 22kV sub-transmission feeder VR126 circuit breaker opened to lockout once again but secondary damage occurred at pole No. LIS 8803304 located in Ryburne Avenue, at the rear of 107 Nicholas Street with conductor clashing occurring mid-span due to probable fault current that caused a HV conductor to fall to the ground. The conductor clashing occurred between the HV strain CHP and Tower T12. Molten metal from the conductor clashing fell into the dry scrub land and started a small 20sqm grass fire that was quickly extinguished. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | MTS-VR Gardiner 126 | HV conductor clashing due to fault current. | Loss of supply;Grassfire | 42524.7035 | 1 | Small: 10 - 1000 sq.m | 1044 | Roadway |  | 20160311UTD_02 | Infrastructure (network-based) | -37.8754 | 145.0731 | 1 | United Energy Distribution | Report | 1500 | 0.01247 | 22kV AC | Moorabbin Airport | 3147 | Ashburton | Conductor
CEOT dispatched a Fault crew to isolate supply and make safe. DAO advised. | 29 HUON PARK ROAD, CRANBOURNE NORTH VIC 3977 |  |  |  |  | Electrical breakdown |  |  |  | CFA report of a street light head on fire. | Public lighting | 0 | 0 | 0 |  |  | CEOT didn't specify a cause. | Other electricity related | 42677.3174 | 1 | Negligible: no ground fire | 1047 |  |  | 20160314SPN_02 | Infrastructure (network-based) | -38.0744 | 145.2747 | 1 | AusNet Services Distribution | Report | 1505 | 0.034994 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne North | AF Other
The faults crew replaced the damaged FOLCB and supply was restored to the single underground supplied customer. | 530 BAXTER-TOORADIN ROAD, PEARCEDALE VIC 3912 | LIS No. 3301596 |  | Heat |  | Overheated connection |  |  | 2 | CFA called and advised there is a power pole on fire. The CFA are on site and have contained the fire to the pole. During warm conditions, a 3 phase FOLCB at pole No. LIS 3301596 located outside 530 Baxter-Tooradin Road, Pearcedale near the corner of West Road caught alight. The cause was unknown but it could be attributed to a possible loose overheated connection. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but it could be attributed to a loose overheated connection. | Pole-top fire | 42585.8785 | 1 | Negligible: no ground fire | 1049 | Roadway |  | 20160315UTD_01 | Infrastructure (network-based) | -38.2001 | 145.2077 | 1 | United Energy Distribution | Report | 1508 | 0.032882 | Low voltage AC (<1kV) | Moorabbin Airport | 3912 | Pearcedale | Connection
Crew isolated supply and undertook repairs. | KINAVALE, 64 JELLBARTS ROAD, WAAIA VIC 3637 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | CFA reported that a pole fire had occurred at the incident location. On arrival the crew found that a t/off cross-arm had burnt off resulting in the conductor bridge pulling out of the live line clamp and falling to the ground, the conductor remained energised until fault crew facilitated isolation of the spur. There were no reported injuries, no ground fire or third party property damage. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross-arm fire | Pole-top fire | 42646.8403 | 1 | Negligible: no ground fire | 1062 | Roadway |  | 20160317PWA_04 | Infrastructure (network-based) | -36.0479 | 145.3004 | 1 | Powercor | Report | 3101 | 0.021958 | 22kV AC | Shepparton Airport | 3637 | Waaia | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was replaced under Access Authority conditions prior to the supply being restored. | 71 EMERALD DRIVE, SPRINGVALE VIC 3171 | LIS No. 0621276 |  | Precipitation |  | Insulator |  |  | 2 | Emergency services advise of a pole fire on the corner of Emerald Drive and Donald Street, Springvale. During light misty drizzle, a crossarm fire occurred on a 66kV crossarm located on the corner of Emerald Drive and Donald Street, Springvale. The pole fire occurred on the pole/HV crossarm behind the king bolt and the centre phase conductor at pole No. LIS 0621276. The "SVTS-SS" 66kV feeder and the 22kV feeder SS 22 required high voltage switching to enable the repairs to be safely completed. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | 66kV feeder SVTS-SS | Probable insulator tracking following light drizzle. | Pole-top fire | 42646.7292 | 1 | Negligible: no ground fire | 1063 | Roadway |  | 20160317UTD_03 | Infrastructure (network-based) | -37.9578 | 145.1422 | 1 | United Energy Distribution | Report | 1524 | 0.0014074 | 66kV AC | Moorabbin Airport | 3171 | Springvale | Crossarm
The existing XLPE overhead services were re-used and supply restored after NST's were completed. | 13 JEFFREY STREET, TEMPLESTOWE LOWER VIC 3107 | Pole No. LIS 7068470 |  |  |  | Overheated connection |  |  | 2 | Pole fire at 8 Jeffery Street per MFB. The MFB were in attendance for a pole fire at service pole No. LIS 7068470 (Telstra joint use pole) after a 2 phase FOLCB burnt out that supplied 13-15 Jeffery Street, Lower Templestowe. The cause was unknown that left a slight charcoal burn on the pole. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but possibly attributed to a lose connection although there were no customer calls for flickering or dimming lights etc. | Pole-top fire | 17/03/2016 8:07 | 1 | Negligible: no ground fire | 1073 | Roadway |  | 20160321UTD_01 | Infrastructure (network-based) | -37.7661 | 145.1045 | 1 | United Energy Distribution | Report | 1538 | 0.023713 | Low voltage AC (<1kV) | Essendon Airport | 3107 | Templestowe Lower | Connection
crew isolated supply and undertook repairs. | 25 CANTERBURY STREET, DEER PARK VIC 3023 |  | Vehicle | [5 empty] | 2 | VicFire reported wires brought down by a truck at the incident location. On arrival the crew found that a Low Voltage service cable brought down and lying on the ground. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Truck, driver details unknown, contacted Low Voltage Service Cable | Loss of supply | 16/03/2016 14:32 |  |  | 1083 | Roadway |  | 20160322PWA_05 | Infrastructure (network-based) | -37.7709 | 144.7717 | 1 | Powercor | Report | 1549 | 0.0028021 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Vehicle
CEOT dispatched a fault crew to investigate, isolate and make safe. DAO advised. Pole and transformer replaced. Oil spill cleaned up. | 71 POUND ROAD W, ALBERTON VIC 3971 | 2621517 |  | Precipitation;Prone to salt deposition |  | Leakage |  | Phase to earth | 1 | IMS 219963. Report of pole fire. Fault crew attended LIS# 2621517, and found a pole top burning. No fire on the ground. CFA on site. Light overnight and morning drizzle coupled with pollution on insulator at asset id 2621517Mcleod P4A (named Mcleod P5 substation) after long dry spell caused tracking on centre phase dropper insulator (5 shed post insulator) igniting where bolted through substation pole. Pole burnt through causing crossarm to drop on top of 100kVA pole mounted transformer breaking transformer HV bushing in turn HV fuse at pole 2621265 (sw818160) operated. Oil spill from transformer covered an area 5m x 4m at base of pole on Eastern side of pole including customer's driveway. | Pole (wood);Crossarm (steel);Insulators | 0 | 0 | 0 |  | ftr23 | Current leakage from HV insulator due to pollution (dust/salt) combined with light drizzle conditions. | Pole-top fire | 42705.309 | 1 | Negligible: no ground fire | 579 | Agricultural |  | 20160112SPN_1 | Infrastructure (network-based) | -38.5791 | 146.6644 | 1 | AusNet Services Distribution | Report | 876 | 0.0035567 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Alberton | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1 PROGRESS AVENUE, CARRUM VIC 3197 | LIS No. 3303240 | Vehicle |  |  | Conductor clashing;HV injection |  |  |  | At 2203hrs on 10/01/2016, 22kV feeder CRM 22 circuit breaker successfully reclosed and held. Communications to ACR FS7791 failed as a command to open was sent. When the operator arrived on site the ACR was open. A vehicle has struck the HV/LV tee-off pole (LIS No. 3303240) located on the corner of Nepean Highway and Progress Avenue, Carrum that caused mid-span conductors to clash and molten metal to fall into the dry grass below resulting in a grass fire estimated to be 5sqm to start that was extinguished by emergency services. The 22kV centre phase conductor snapped due to the force of the vehicle hitting the pole and fell to the ground. Following the conductors clashing, splash marks were identified on the HV conductor after they made contact with the LV conductors. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Progress-Nepean" substation. The LEI confirmed a high voltage injection occurred (MOR 1601) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CRM 22 | Car struck pole. | HV injection;Loss of supply;Grassfire | 42644.9187 | 1 | Localised: less than 10 sq.m | 578 | Roadway |  | 20160112UTD_1 | Infrastructure (network-based) | -38.0797 | 145.1233 | 1 | United Energy Distribution | Report | 872 | 0.025411 | 22kV AC | Moorabbin Airport | 3197 | Carrum | Vehicle
A Downer First Responder attended and made the site safe by temporary repairing the substation access door. Substation Fitters attended the site on 13/01/2016 to repair the doors to ensure the site is secure. A Substation Supervisor has discussed the rectification work with the building owner for the past six months to upgrade the safety rail and ladder for access to the substation but nothing has occurred. | 117-119 MAIN STREET, MORNINGTON VIC 3931 |  | Vandalism |  |  | Fault on customer installation |  |  | 2 | A local resident advised there is a electricity substation opposite the shops with security fencing that children have gained access via a ladder and platform. Vandals have forced the door open into "Coles-Octavia" indoor substation located at the rear of 117-125 Main Street, Mornington but haven't touched anything. Children have obtained access by climbing a ladder to a platform that had the potential for a serious accident to occur as there is a 3-4m drop to ground level. The substation is located in the Coles docking dock in Octavia Street near the corner of Barkley Street. | Indoor | 0 | 0 | 0 |  | MTN 21 | Vandals have forced the door open into "Coles-Octavia" indoor substation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42705.6667 |  |  | 592 | Commercial |  | 20160113UTD_1 | Infrastructure (network-based) | -38.2204 | 145.039 | 1 | United Energy Distribution | Report | 894 | 0.00019444 | 22kV AC | Moorabbin Airport | 3931 | Mornington | Other
Made safe and Fire extingushed by Fire department | 61-63 MICKLEHAM ROAD, TULLAMARINE VIC 3043 |  |  | Heat |  | Electrical overload |  |  | 1 | Minor Grass Fire | Cable | 0 | 0 | 0 |  |  | Over voltage stress on cable due to delayed protection operation from an adjacent feeder. | Grassfire | 13/01/2016 16:20 | 1 | Localised: less than 10 sq.m | 597 | Industrial |  | 20160114JEM_1 | Infrastructure (network-based) | -37.6991 | 144.8802 | 1 | Jemena | Report | 2730 | 0.037304 | 22kV AC | Essendon Airport | 3043 | Tullamarine | AF Other
Crew isolated supply and undertook repairs. | 25 MCCONCHIE AVENUE, KEW EAST VIC 3102 |  |  |  |  | Overheated connection |  |  | 1 | Customer reported a loud bang and a fire at the incident location. On arrival the crew found that a connection on a 22kV isolator had overheated, causing hot debris to fall to the ground and resulting in a ground fire (approx. 0.9m by 0.45m) on the nature strip. Protection operated. There were no reported injuries. | Disconnector/isolator | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 13/01/2016 19:30 | 1 | Localised: less than 10 sq.m | 600 | Residential |  | 20160114PWA_4 | Infrastructure (network-based) | -37.7949 | 145.0437 | 1 | CitiPower | Report | 908 | 0.010068 | 22kV AC | Essendon Airport | 3102 | Kew East | Connection
Crew discussed with Contractor who advised they would re-cover cables | 28-34 CLARENDON STREET, SOUTHBANK VIC 3006 |  | Working too close to underground cables | [5 empty] | 2 | A field crew working onsite to undertake repairs for a cable dig-in (refer incident no. 20160111PWA_5) noticed a pile of cable cover slabs on the other side of the road and went over to investigate. The crew found that underground cables had been uncovered and one cable had been cut back with sections removed. The cable voltages were not determined. The crew spoke to the contractor working in the area (Coleman Rail, 174 Turner St, Port Melbourne VIC 3207 Ph: 9624 4210) who, after they initially denied they had cut the cable back, then said that they werenâ€™t aware and agreed that they shouldnâ€™t have cut the cable. The contractor advised that they had located a cut end of a cable and traced back to this location where the cable was cut. The contractor advised that they would replace the cover and slabs over the cables. There were no reported injuries. Upon checking cable plans for the area, it was noted that there are out of service cables in the area. The contractor had advised in relation to the other dig-in incident that they had DBYD plans for the area (refer incident no. 20160111PWA_5). Refer also to incident dated 29/03/2013, Melbourne â€“ St Kilda Rd (Domain Interchange) involving Coleman Rail where they ignored a direction not to disturb cables. | Cable | 0 | 0 | 0 |  |  | Contractor did not follow correct cable NGZ process | No Go Zone (no contact) | 42583 |  |  | 601 | Roadway |  | 20160115PWA_1 | Infrastructure (network-based) | -37.8249 | 144.9567 | 1 | CitiPower | Report | 909 | 0.033175 | Not applicable | Essendon Airport | 3006 | Southbank | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected and a Downer construction crew replaced the HV tee-off and intermediate crossarms under Access Authority conditions. | 26 HEALEY ROAD, DANDENONG SOUTH VIC 3175 | LIS No. 0621512 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 1 | At 0631hrs on 14/01/2016, 22kV feeder DVY 32 circuit breaker reclosed to lockout affecting 40 customers. Following light drizzly rain after a very hot day, a HV tee-off crossarm fire occurred at pole No. LIS 0621512 located on the corner of Healey and Kitchen Roads, Dandenong. There was evidence of the HV conductors making contact with the LV conductors below and a LEI was dispatched to investigate. The LEI checked installations in the vicinity and confirmed that no high voltage injection or damage was sustained to electrical installations supplied from "Kitchen-Healey" substation. | Crossarm (wood) | 0 | 0 | 0 |  | DVY 32 | Crossarm fire caused by probable insulator tracking. | Pole-top fire;Loss of supply | 15/01/2016 9:51 | 1 | Negligible: no ground fire | 602 | Roadway |  | 20160115UTD_1 | Infrastructure (network-based) | -38.0301 | 145.2223 | 1 | United Energy Distribution | Report | 910 | 0.036998 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Crossarm
Crew attended and DAO advised. Line isolated and repaired and SWER line restored from Glovers Rd ISO 794 Asset ID 2006268. Up to 30 fire trucks with firefighters attended the fire to extinguish it. Hay shed full of hay was destroyed in the fire along with a 4 wheel motorcycle (make and size unknown) along with a 6 x 4 trailer with either a generator or generator pump attached and some fencing was burnt. On follow up investigation on 14-1-16 at 10:30am noticed there was a stranded conductor still in the span and arrangements were made to repair this which occurred early afternoon using G & B techniques. There are now 5 sleeves or repairs in this single span of 3/2.75 steel SWER conductor. The span is approximately 135m long. AusNet Services' Vegetation Management section is investigating the incident. | 80 HORSBURGH ROAD, NYORA VIC 3987 | 2006707 |  | Wind;Fallen;Dead |  |  |  | Phase to earth | 1 | IMS 220033. Report by CFA of wires down and grass fire in the vicinity. Feeder CB tripped to Lockout. The following report is from David Green, Senior Network Representative at Leongatha depot: Broken SWER conductor (3/2.75 ST/GZ HV) between poles 2006706 Lester 2 and 2006707 Lester 3 and fire burning approximately 78,000 square metres including hay shed and numerous hay bales along with 4 wheel motorcycle, fencing and a trailer with either a generator or pump attached. On site investigation suggests dead tree branch outside clearing space but high enough to hit the line broke off tree from huge winds (micro burst around 100kmh) and fell across the SWER line, eventually breaking the line and falling to ground where allegedly a fire started. No stock lost in paddocks. I was on site at around 9.30pm and the chief of the CFA escorted us to where the conductor was broken and it was laying in a position consistent with what was alleged that a tree branch that had fallen across the conductor and broken it. On talking to the person looking after the property the following was said by him "My wife was outside at the time opening the shade shutters on the house because the wind was blowing very hard and the wind would damage them if they were left down and she looked across and saw a tree branch that had fallen over the line and at that moment the power went off for what they thought was 30 seconds, it then came back on for a little bit and then it went back off and then it came back on again where there was a flash or large arc at where the tree had fell and a fire started underneath. He then grabbed a fire extinguisher and rushed over and tried to put the fire out but it got away and out of control". He went further to say "did you know there was a similar incident a month or so back where another tree in the same span fell across the line and broke the conductor? I said no and then he went on "I only wish I had of followed up to get the trees cut and I don't understand why AusNet Services didn't because it seems so simple now". He then left. The chief of the CFA pointed out that there had been several fires in the area started by a fire bug and if I did not say the fire was started by our assets he would get the investigators in for a suspected deliberately lit fire and we would not be allowed to repair the line. I said I can't make that call because I was not here at the time and it would only be a guess. I said I can see a tree branch broken, a powerline down and a fire and he would need to make that call. He then said to go ahead and repair the line. | Conductor (bare) | 0 | 0 | 0 |  | llg12 | Vegetation: Trees Incident | Grassfire | 13/01/2016 18:55 | 1 | Medium: 1000 sq.m - 10 ha | 619 | Agricultural |  | 20160117SPN_02 | Infrastructure (network-based) | -38.3049 | 145.6772 | 1 | AusNet Services Distribution | Report | 931 | 0.016836 | 12.7kV AC (SWER) | Moorabbin Airport | 3987 | Nyora | Trees
Crew checked pole, and referred on for repairs | 152 MOORE STREET, WARRNAMBOOL VIC 3280 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a pole fire had occurred, causing burning of the pole around the area of the centre phase 22kV High Voltage insulator. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | pole fire | Pole-top fire | 13/01/2016 20:57 | 1 | Negligible: no ground fire | 644 | Roadway |  | 20160118PWA_13 | Infrastructure (network-based) | -38.3744 | 142.5021 | 1 | Powercor | Report | 978 | 0.021106 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
Crew isolated supply and undertook repairs | 38 APPLEBY CRESCENT, BRUNSWICK WEST VIC 3055 |  |  |  |  | Overheated connection |  |  | 2 | A passer-by reported that there was a small fire at the incident location. On arrival the crew found that a connection on a transformer isolator had overheated causing hot debris to fall to the ground resulting in a ground fire (Approx. <0.3 sqm) on the road reserve. There were no reported injuries. | Disconnector/isolator | 0 | 0 | 0 |  |  | Overheated connection | Grassfire | 13/01/2016 23:16 | 1 | Localised: less than 10 sq.m | 645 | Roadway |  | 20160118PWA_14 | Infrastructure (network-based) | -37.7559 | 144.9461 | 1 | CitiPower | Report | 980 | 0.025365 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Connection
Crew checked conductors for damage and undertook repairs | 34 FAIRBAIRN ROAD, SUNSHINE WEST VIC 3020 |  |  | Wind |  |  |  |  | 1 | Vic Fire reported a fire at the incident location. On arrival the crew found the white and blue phase LV conductors had clashed causing hot debris to fall starting a ground fire (Approx. 170 sqm) . Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Wind caused conductors to clash | Grassfire | 13/01/2016 18:00 | 1 | Small: 10 - 1000 sq.m | 646 | Roadway |  | 20160118PWA_15 | Infrastructure (network-based) | -37.7979 | 144.8185 | 1 | Powercor | Report | 982 | 0.033175 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Conductor
Crew removed EDO Tube - Replaced EDO Tube and Fuse 5K. Corrective action created to assess and replace with Boric Acid fuse. Sub is single phase. | 37 EARLS ROAD, YARRAGON SOUTH VIC 3823 | 2203369 | [6 empty] | 2 | Initial report was that a EDO fuse had candled/burnt. CEOT sent a Schedule 1 report to ESV via fax/e-mail. Further investigation found that it was just a fuse hang-up only, no burnt/candled fuse tube. Therefore no Schedule 2 report is required for this incident. Accordingly, AusNet Services has classed it as a near-miss electrical incident. | EDO fuse | 0 | 0 | 0 |  | MOE22 |  | Hung-up fuse only | 15/01/2016 10:55 |  |  | 637 | Residential |  | 20160118SPN_09 | Infrastructure (network-based) | -38.2378 | 146.0876 | 1 | AusNet Services Distribution | Report | 972 | 0.020714 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon South | Fuse
CEOT dispatched a fault crew and a DAO to isolate, make safe and investigate. The Linesmen isolated the transformer via the HV fuse to complete repairs. The Linesmen replaced the LV box, transformer LV leads and 1 of the 2 overhead service cables. | 169 BIRDS ROAD S, HEDLEY VIC 3967 | 2609008 |  |  |  | Overheated connection |  |  | 2 | IMS 220061. Customer report of a pole fire. Fire out. Fire in the vicinity of the base of pole. No other damage. Appears the LV fuse failed to blow and caused transformer LV fuse box to melt as well as the LV leads. Some molten material fell to the ground and caused a small grass fire of size 10mx2m which was extinguished at the time the fault was called in at 6:20am. HV fuses didn't blow. | Crossarm (steel);Any other type;Pole mounted;Pole (concrete) | 0 | 0 | 0 |  | ftr23 | Possible poor electrical connection or overload. | Grassfire | 17/01/2016 6:20 | 1 | Small: 10 - 1000 sq.m | 642 | Agricultural |  | 20160118SPN_10 | Infrastructure (network-based) | -38.6516 | 146.523 | 1 | AusNet Services Distribution | Report | 976 | 0.030197 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3967 | Hedley | Fuse
Made safe | 101 LOWER HEIDELBERG ROAD, IVANHOE VIC 3079 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Found evidence of grass fire in area. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 13/01/2016 15:20 | 1 | Localised: less than 10 sq.m | 647 | Residential |  | 20160119JEM_01 | Infrastructure (network-based) | -37.7717 | 145.0479 | 1 | Jemena | Report | 984 | 0.033096 | 11kV AC | Essendon Airport | 3079 | Ivanhoe | Conductor
A LEI and faults truck attended and commenced an investigation. The installation was tested and no faults could be identified with 0.4v measured between the clothes dryer and an independent earth. The customer had towels in the dryer at the time and the LEI suspected static electricity was the cause. The faults crew replaced the LV earth cover strips on pole No. LIS 3301080 that were damaged after the pole had been struck. | 296 CENTRE ROAD, LANGWARRIN VIC 3910 | LIS No. 3301080 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Customer advised the received an electric shock from the clothes dryer after a grader hit the pole outside yesterday that dislodged cables running down the pole. The occupier claimed to have received an electric shock from the clothes dryer yesterday when removing a load of towels. Also advised that a grader has struck the pole yesterday and damaged cables. | No failed asset | 0 | 0 | 0 |  |  | Probable static electricity. | Minor shock | 14/01/2016 13:30 |  |  | 650 | Residential |  | 20160119UTD_02 | Infrastructure (network-based) | -38.1693 | 145.2066 | 1 | United Energy Distribution | Report | 988 | 0.016554 | Low voltage AC (<1kV) | Moorabbin Airport | 3910 | Langwarrin | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. | 705 FERNTREE GULLY ROAD, GLEN WAVERLEY VIC 3150 |  |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | At 1813hrs on 13/01/2016, 22kV feeder ACR DN9651 located in Darnley Road on MGE34 reclosed to lockout affecting 630 customers. During a hot day with strong north winds, a council tree branch contacted HV conductors outside 17 Swift Drive, Wheelers Hill. Secondary damage occurred due to possible conductor clashing or fault current that caused molten metal to fall into dry grass from 3 damaged PG clamps outside 705 Ferntree Gully Road. The small grass fire was estimated to be 10sqm in size that was quickly extinguished. | Conductor (bare);Aluminium;Connector/termination | 0 | 0 | 0 |  | MGE 34 | Vegetation: Trees Incident | Grassfire | 13/01/2016 18:13 | 1 | Localised: less than 10 sq.m | 651 | Roadway |  | 20160119UTD_03 | Infrastructure (network-based) | -37.9043 | 145.171 | 1 | United Energy Distribution | Report | 989 | 0.0015579 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Trees
Made safe | 11 KWINANA COURT, IVANHOE VIC 3079 |  | Vehicle | [5 empty] | 2 | Removalist truck contacted Optus cable causing it to flick into LV conductor, which brought it to the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Removalist truck contacted Optus cable causing it to flick into LV conductor, which brought it to the ground. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/01/2016 8:09 |  |  | 684 | Residential |  | 20160121JEM_02 | Infrastructure (network-based) | -37.7576 | 145.0407 | 1 | Jemena | Report | 1028 | 0.004478 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Vehicle
Crew isolated supply and undertook repairs | 65 WOONTON LANE, NYAH WEST VIC 3595 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | An Asset Inspector reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole, which burnt the crossarm at the brace, the arm remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm Fire | Pole-top fire | 20/01/2016 10:40 | 1 | Negligible: no ground fire | 682 | Roadway |  | 20160121PWA_09 | Infrastructure (network-based) | -35.2027 | 143.3718 | 1 | Powercor | Report | 1026 | 0.018132 | 22kV AC | Swan Hill Aerodrome | 3595 | Nyah West | Crossarm
A faults truck attended and re-terminated the LVABC connections. The LV circuit fuses operated and required replacement before supply was restored to customers in the vicinity. | 1-3 HILLHOUSE ROAD, TEMPLESTOWE VIC 3106 | LIS No. 7065399 |  | Heat |  | Electrical overload |  |  | 1 | Customer reporting the wires on the power pole are sparking and there is a fire at the base of the pole which the customer has put out. During warm conditions with a strong north wind, a LVABC IPC connection (LVABC to LVABC tee-off conductor) failed at "Hillhouse-Porter" substation that caused molten metal and plastic to fall into the dry grass below the pole (LIS No. 7065399) located on the corner of Porter Street and Hillhouse Road. A small grass fire estimated to be 5sqm started on the nature strip that was extinguished by a customer. "Hillhouse-Porter" substation was under LV parallel at the time of the event and the LV connection failure could be attributed to a loose connection during a period of peak electricity usage. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  |  | The LVABC connection failure could be attributed to a loose connection during a period of peak electricity usage with the substation in LV parallel with another substation at the time. | Grassfire | 18/01/2016 18:00 | 1 | Localised: less than 10 sq.m | 674 | Residential |  | 20160121UTD_01 | Infrastructure (network-based) | -37.7559 | 145.1607 | 1 | United Energy Distribution | Report | 1016 | 0.014131 | Low voltage AC (<1kV) | Moorabbin Airport | 3106 | Templestowe | Connection
Crew isolated supply and undertook repairs | 327 MORPUNG AVENUE, IRYMPLE VIC 3498 |  |  |  |  | Age |  |  | 2 | A customer reported a fire at the incident location. On arrival the crew found that a fault had occurred on an LV service cable resulting in a ground fire (less than 0.09 sqm) . There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Deteriorated LV service cable | Grassfire | 21/01/2016 11:00 | 1 | Localised: less than 10 sq.m | 687 | Roadway |  | 20160122PWA_01 | Infrastructure (network-based) | -34.243 | 142.1818 | 1 | Powercor | Report | 1035 | 0.024213 | Low voltage AC (<1kV) | Mildura Airport | 3498 | Irymple | OH Cable
Crew made safe and undertook repairs | 49 HUNTS CROSS WAY, CAROLINE SPRINGS VIC 3023 |  | Vandalism | [5 empty] | 2 | A Powercor employee reported vandalism and that the door of a Kiosk substation was broken open at the incident location. On arrival the crew found that unknown third parties had broken open the door of a Kiosk substation. No equipment was found missing however there was evidence of a flashover inside the LV fuse cabinet of the substation. No cause could be determined for the flashover and no flashover damage was found to any electrical equipment other than a flashover smoke mark on the wall of the kiosk and significant arc spatter at the door of the substation. No cause was found for this flashover smoke and arc spatter. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Vandalism | Singeing or local charring/blackening only;Damage to network assets | 15/01/2016 13:46 |  |  | 688 | Roadway |  | 20160122PWA_02 | Infrastructure (network-based) | -37.7379 | 144.7274 | 1 | Powercor | Report | 2720 | 0.0052894 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Caroline Springs | Other
Crew isolated supply and undertook repairs. LEI checked installations for damages. | 49 EASEY STREET, COLLINGWOOD VIC 3066 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | MFB reported a sparking and fire on a pole at the incident location. On arrival, the crew found that a crossarm fire had occurred on a 11kV pole causing the crossarm to break and fall to the ground. The incident also resulted in a HVI injection affecting a small number of installations. Protection operated. There was no ground fire. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | HV injection | 20/01/2016 9:46 |  |  | 690 | Roadway |  | 20160122PWA_03 | Infrastructure (network-based) | -37.798 | 144.9872 | 1 | CitiPower | Report | 8004 | 0.012916 | 11kV AC | Essendon Airport | 3066 | Collingwood | Crossarm
rew isolated supply and undertook repairs | 378 LORENZS ROAD, STRATHMERTON VIC 3641 |  | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A REC reported wire down at the incident location. On arrival the crew found that a farmer (P & R Gundrill, 352 Lorenz Rd, Strathmerton, Ph: 0408 586 459) was towing an auger in the upright position and contacted a LV service cable , breaking the cable causing it to fall to the ground. There were no reported injuries or third party property damages. The height of the LV service cable was estimated to be greater than 5m. | Service conductor | 0 | 0 | 0 |  |  | Tractor towing auger contacted LV service cable | No Go Zone (contact);Damage to network assets | 21/01/2016 12:21 |  |  | 691 | Agricultural |  | 20160122PWA_04 | Infrastructure (network-based) | -35.9594 | 145.5048 | 1 | Powercor | Report | 1040 | 0.018383 | Low voltage AC (<1kV) | Shepparton Airport | 3641 | Strathmerton | Vehicle
Crew isolated supply and undertook repairs. LEI checked premises for damage. | 1521 STURT STREET, NEWINGTON VIC 3350 |  |  | Bird |  |  |  |  | 1 | A field crew attending an outage found that a crow had caused a flashover on a 22kV pole, breaking two HV ties and also causing a 22kV conductor to break and fall into LV conductors below, resulting in a High Voltage Injection affecting approximately 25 installations. Protection operated. There was no ground fire. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | HV injection | 20/01/2016 16:55 |  |  | 693 | Roadway |  | 20160122PWA_06 | Infrastructure (network-based) | -37.5587 | 143.8271 | 1 | Powercor | Report | 1044 | 0.0079016 | 22kV AC | Ballarat Aerodrome | 3350 | Newington | Animal
Crew isolated supply and undertook repairs. | 740 LILFORD ROAD, MOOROOPNA NORTH WEST VIC 3616 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the cross arm. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole top | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 13/12/2015 15:09 | 1 | Negligible: no ground fire | 701 | Agricultural |  | 20160122PWA_14 | Infrastructure (network-based) | -36.3429 | 145.2306 | 1 | Powercor | Report | 1056 | 0.0017257 | 22kV AC | Shepparton Airport | 3616 | Mooroopna North West | Pole
Crew isolated supply and undertook repairs | 834 WOORINEN-GOSCHEN ROAD, SWAN HILL WEST VIC 3585 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the top of the pole and cross arm. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 26/12/2015 18:57 | 1 | Negligible: no ground fire | 702 | Agricultural |  | 20160122PWA_15 | Infrastructure (network-based) | -35.3686 | 143.4534 | 1 | Powercor | Report | 1057 | 0.0051007 | 22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill West | Pole
CEOT dispatched a fault crew to investigate, isolate & make safe. Local Field Team Manager sent a request to Works Programming to raise a Work Order to change the fuse units to Boric Acid fuses. | 1614 GREAT ALPINE ROAD, SARSFIELD VIC 3875 | 1600270 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 2220113. On arrival, the fault crew found a HV fuse hung-up and the fuse tube burnt in half. there was no fire on the ground or at pole top. Substation DONALDSON PUMP 005 POLE @ SARSFIELD. | EDO fuse | 0 | 0 | 0 |  | bdl8 | Burnt EDO fuse tube. | Other electricity related | 20/01/2016 12:55 | 1 | Negligible: no ground fire | 707 | Agricultural |  | 20160124SPN_04 | Infrastructure (network-based) | -37.7344 | 147.7773 | 1 | AusNet Services Distribution | Report | 1066 | 0.027727 | 22kV AC | Bairnsdale Airport | 3875 | Sarsfield | Fuse
CEOT dispatched fault crew to make safe and investigate. Access Permit issued to change the pole and rebuild the structure. | 3 CAMMS ROAD, CRANBOURNE VIC 3977 | 505538 |  | Precipitation;Industrial or urban pollution |  |  |  | Phase to earth | 2 | IMS 220114. Fire damage observed on HV cross arm. CFA in attendance. Pole fire caused by light rain tracking through the HV Centre Phase bolt supporting the strain insulators causing the pole and the HV crossarm to burn. | Pole (wood);Crossarm (wood);Insulators | 0 | 0 | 0 |  | cre32 | Dust on insulators with light drizzle caused tracking through kingbolt burning pole and crossarm. | Pole-top fire | 20/01/2016 11:55 | 1 | Negligible: no ground fire | 708 |  |  | 20160124SPN_05 | Infrastructure (network-based) | -38.0961 | 145.2682 | 1 | AusNet Services Distribution | Report | 1068 | 0.022289 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne | Crossarm
CEOT dispatched fault crew to investigate. Fault crew attended prior to arrival of AusNet Services' LEI. The fault crew informed the control room (CEOT) of damage sustained to several properties. LEI in attendance to check for property damage - appliance damage was found. Claims advice provided. | 9 MIRRA COURT, BUNDOORA VIC 3083 | 5682456 |  | Lightning |  |  |  |  | 1 | IMS 220119. Customer complaining of appliance damage. Protection reclose on 22 kV line in early hours of the morning. HV injection due to lightning strike at an unknown location. | Conductor (bare) | 0 | 0 | 0 |  | wt13 | Lightning strike. | HV injection | 20/01/2016 6:15 |  |  | 709 | Commercial |  | 20160124SPN_06 | Infrastructure (network-based) | -37.703 | 145.0706 | 1 | AusNet Services Distribution | Report | 1070 | 0.030365 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3083 | Bundoora | Lightning
CEOT dispatched a fault crew. DAO to complete fire report. The line was checked for any damage and no damage was found. The tree was cleared by AusNet Services vegetation contractors. Supply restored. | 479 MONBULK ROAD, MONBULK VIC 3793 | 1321153 |  | Lightning;Dead | Unlikely |  |  | Phase to phase | 1 | IMS 220159. A large dead tree 9 metres from the pole was reportedly struck by lightning and fell from its roots across the HV conductors a third of the way along the span from the pole. The tree caught fire which was extinguished by the CFA. No damage was caused and the tree was cut clear from the line by our contractors. HV fuse operated successfully - line de-energized. | Conductor (bare) | 0 | 0 | 0 |  | bge11 | Vegetation: Trees Incident | Other vegetation | 22/01/2016 9:55 | 1 | Negligible: no ground fire | 710 | Residential |  | 20160124SPN_07 | Infrastructure (network-based) | -37.8681 | 145.4087 | 1 | AusNet Services Distribution | Report | 1072 | 0.012892 | 22kV AC | Moorabbin Airport | 3793 | Monbulk | Trees
Crew isolated supply and undertook repairs | 171 GOODMAN ROAD, WOORINEN VIC 3589 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the cross at the king bolt causing arm to break and fall, remaining held up by cross arm straps, resulting in a ground fire (approx. 5m x 3m) on road reserve. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Grassfire | 22/01/2016 16:26 | 1 | Small: 10 - 1000 sq.m | 719 | Roadway |  | 20160125PWA_01 | Infrastructure (network-based) | -35.247 | 143.4718 | 1 | Powercor | Report | 1082 | 0.026365 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen | Pole
Crew checked line for damages - none found | 26 BULLEEN ROAD, BALWYN NORTH VIC 3104 |  |  | Fallen;Council |  |  |  |  | 2 | Resident reported that a fire had started in trees outside the property at the incident location. On arrival the crew found that a broken tree branch had been resting on 11kV overhead conductors resulting in the branch catching fire and a ground fire on the nature strip. (Approx. 0.2 by 0.1m). The tree is in a declared area. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 23/01/2016 23:35 | 1 | Localised: less than 10 sq.m | 720 | Roadway |  | 20160125PWA_02 | Infrastructure (network-based) | -37.7908 | 145.0724 | 2 | CitiPower | Report | 1084 | 0.034149 | 11kV AC | Essendon Airport | 3104 | Balwyn North | Trees
Crew isolated supply and arranged repairs | 1095 GLENMORE ROAD, ROWSLEY VIC 3340 |  | Vehicle | [5 empty] | 1 | Police reported that a car had hit a pole, conductor down and started grass fire at the incident location and person trapped in car. On arrival the crew found that a single vehicle had collided with 66kV steel tower on Bacchus Marsh- Balliang Rd and had brought down the steel tower and 66kV conductor. The driver and sole occupant of the vehicle airlifted with serious injury after crash. The incident also resulted in a ground fire (Approx. 10m x 5m) was contained to the immediate area surrounding the car. Vic Fire had extinguished the fire prior to the crew arriving. Damage was also caused to the neighbouring property fence. | Tower | 0 | 0 | 0 |  |  | Car hit tower | Grassfire | 24/01/2016 17:26 | 0 | Small: 10 - 1000 sq.m | 728 | Roadway |  | 20160127PWA_04 | Infrastructure (network-based) | -37.7132 | 144.3394 | 1 | Powercor | Report | 1101 | 0.0018021 | 66kV AC | Avalon Airport | 3340 | Rowsley | Vehicle
Crew isolated supply and arranged repairs | 716-738 TROUPS ROAD S, MOUNT COTTRELL VIC 3024 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A customer reported a fire at the above location. On arrival the crew found that a pole fire had occurred on a 22kV pole, resulting in the pole top being burnt. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 24/01/2016 12:09 | 1 | Negligible: no ground fire | 739 | Roadway |  | 20160128PWA_08 | Infrastructure (network-based) | -37.7864 | 144.6612 | 1 | Powercor | Report | 1113 | 0.0033252 | 22kV AC | Laverton Raaf | 3024 | Mount Cottrell | Pole
Crew isolated supply and arranged repairs | 223 MOORE STREET, WARRNAMBOOL VIC 3280 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | An employee reported a damaged crossarm that was a result of a previous crossarm fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole at some time in the past damaging the crossarm which remained intact. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 25/01/2016 16:33 | 1 | Negligible: no ground fire | 740 | Roadway |  | 20160128PWA_09 | Infrastructure (network-based) | -38.3742 | 142.495 | 1 | Powercor | Report | 1114 | 0.020441 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Crossarm
Sent crew to make safe and repair. DAO Carlo Cellante to do fire report. Line checked for damage - OK. The low voltage substation fuse was replaced and supply restored. | 140 DUNNETTS ROAD, YAN YEAN VIC 3755 | 918157 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 220181. A small 3 x 3 metre grass fire was caused by a backhoe operator relocating and lifting an approximately 8 metre fallen tree branch over a farm fence, with the tree branch partly dislodging from his machine and making contact and clashing with low voltage open wire that also caused the low voltage substation fuse to operate on pole #918157. The CFA did not attend the fire, with the fire having been extinguished by an adjoining neighbour. The backhoe excavator machine operator was Gus McMahon of 140 Dunnetts Rd, Yan Yean, Vic, 3755, mobile 0417 307 095. | Conductor (bare) | 0 | 0 | 0 |  | drn22 | 3rd party contact with overhead LV. | Grassfire | 25/01/2016 18:35 | 1 | Localised: less than 10 sq.m | 748 | Agricultural |  | 20160128SPN_03 | Infrastructure (network-based) | -37.5476 | 145.1228 | 1 | AusNet Services Distribution | Report | 1128 | 0.019087 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3755 | Yan Yean | Vehicle
Crew check conductors for damage, Span referred for design review | 2368-2402 HOPKINS HIGHWAY, BALLANGEICH VIC 3279 |  |  |  |  | Conductor clashing |  |  | 1 | CFA reported a pole fire at the above location. On arrival the crew found that 22kV conductors had clashed resulting in a grass fire (Approx. 50m x 50m) on the road reserve. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | 22kV conductor clashing in strong winds | Grassfire | 28/01/2016 16:00 | 1 | Medium: 1000 sq.m - 10 ha | 756 | Roadway |  | 20160129PWA_01 | Infrastructure (network-based) | -38.2299 | 142.6576 | 2 | Powercor | Report | 1156 | 0.018802 | 22kV AC | Warrnambool Airport Ndb | 3279 | Ballangeich | Conductor
Fault crew removed existing service and installed a new service. .CTA re-tested property, all VESI tests passed | 458 CAMBERWELL ROAD, CAMBERWELL VIC 3124 |  |  |  |  | Neutral fault |  |  | 2 | Lucie was turning on the kitchen sink tap at the time, she received an electric shock when she made simultaneous contact between the metallic kitchen tap and the metallic kitchen sink with her hands. Voltage tests between an independent earth, the point of contact and various points of the electrical installation, including distribution assets, revealed a high impedance service cable neutral conductor mid-way along the cable span. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. An impedance to the flow of current between the general mass of earth and the metallic water pipe system was sufficient enough to cause a voltage rise of 30 volts on the water pipe system. | Service conductor | 0 | 0 | 0 |  |  | High impedance neutral in service cable. | Minor shock | 42195.3125 |  |  | 788 | Residential |  | 20160204PWA_07 | Infrastructure (network-based) | -37.8393 | 145.0656 | 1 | CitiPower | Report | 1196 | 0.024844 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | OH Cable
On arrival the fault crew performed an NST test which failed. The neutral screened service was checked and found to be faulty and replaced with a new XPLE type service cable. A final NST test and polarity checks were done and passed. Checks to an independent earth found 2V on the neutral and taps, which is well within acceptance. On arrival crew performed NST test and it failed..The neutral screened service was checked and found to be faulty and replaced.An nst and polarity checks were done and passed. Checks to an independant earth found 2v on neutral and taps, which is well within code | 54 SURF BEACH ROAD, CAPE PATERSON VIC 3995 | 2811121 |  |  |  | Age;Corrosion |  | Phase to earth | 2 | Customer received an electric shock to hand when using tap connected to earthing system caused by a faulty neutral screen service cable. | Service conductor | 0 | 0 | 0 |  | wgi31 | Faulty neutral screen service cable creating a high impedance neutral. | Minor shock | 26/12/2015 12:00 |  |  | 779 | Residential |  | 20160204SPN_01 | Infrastructure (network-based) | -38.6728 | 145.6148 | 1 | AusNet Services Distribution | Report | 1186 | 0.0034826 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | Cape Paterson | Crossarm
The feeder was patrolled and supply restored a short time afterwards. | 55 DUNDAS STREET, RYE VIC 3941 | LIS 1305118 | Working too close to overhead lines;Unauthorised work | Within clearances |  |  |  |  | 1 | At 1401hrs on 02/02/2016, 22kV ACR RB0228 located in Melbourne Road reclosed to lockout affecting 2115 customers. A private tree clearer dropped a branch from a heritage listed cypress tree at 55 Dundas Street, Rye that contacted the HV conductors causing the ACR in Melbourne Road to reclose to lockout. There was no prior contact with United Energy in regard to No Go Zones etc. No damage or injuries were received. Company involved - Southern Peninsula Tree Works Stuart Wells 0408 171 470 PO Box 2337 Rosebud Plaza VIC 3939 | Conductor (bare) | 0 | 0 | 0 |  | STO 14 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 42402.584 |  |  | 778 | Roadway |  | 20160204UTD_01 | Infrastructure (network-based) | -38.3759 | 144.8173 | 1 | United Energy Distribution | Report | 1184 | 0.030587 | 22kV AC | Moorabbin Airport | 3941 | Rye | Trees
CEOT dispatched a fault crew to make safe and arrange repair. Electrix were sent out to investigate and replace with a new 150 Watt HPS street light. | 18 LANDAU DRIVE, WARRANWOOD VIC 3134 | 1203064 |  |  |  | Age;Electrical breakdown |  |  | 2 | IMS 220315. CEOT received a report from the MFB of a street light on fire. The MFB and advised the fire was extinguished. | Public lighting | 0 | 0 | 0 |  | rwt31 | The old burnt out lantern shows signs of igniter getting hot due to trying to restart more times than it is designed for. | Other electricity related | 42431.1111 | 1 | Negligible: no ground fire | 797 | Residential |  | 20160205SPN_03 | Infrastructure (network-based) | -37.7699 | 145.2402 | 1 | AusNet Services Distribution | Report | 1572 | 0.028953 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Warranwood | AF Other
AusNet Services received reports of customer appliance damages. The incident was attended to by an AusNet Services' fault crew and an LEI. The attending fault crew repaired the fault and reconnected supply at approximately 3:00am. The LEI was subsequently called at 10:15am to attend and assess for customer appliance / property damage. The attending LEI found evidence of property damage and directed the fault crew to isolated LV supply from the substation until correct customer isolation procedures could be carried out. The attending LEI inspected affected properties and found evidence of damage. Customer damage reports left with various customers assessed and no access letters left for no access to unattended properties. Control Room (CEOT) notified. | 84 ANNE ROAD, KNOXFIELD VIC 3180 | 1311761 |  | Blown branch/vegetation |  |  |  |  | 2 | A tree branch located on 84 Anne Rd fell onto open bare 400V conductors causing the neutral conductor to be disconnected at the Pole Sub-Anne/Kathryn, in turn creating a high volts situation on the LV reticulation system. The falling tree branch was caused by inclement weather and windy conditions. | Conductor (bare) | 0 | 0 | 0 |  | bra13 | Vegetation: Trees Incident | Damage to network assets | 14/01/2016 1:00 |  |  | 798 | Residential |  | 20160205SPN_04 | Infrastructure (network-based) | -37.8886 | 145.2476 | 1 | AusNet Services Distribution | Report | 1209 | 0.03411 | Low voltage AC (<1kV) | Moorabbin Airport | 3180 | Knoxfield | Conductor
CEOT dispatched a fault crew to isolate supply, make safe and repair. Boric Acids fuse tubes replaced and supply restored. | 141 TAYLOR BAY RIGHT ARM ROAD, TAYLOR BAY VIC 3713 | 4715118 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 220318. CEOT received a customer call saying that a pole was arcing, Fault crew attended and found a hung-up and candled 15 Amp Boric Acid fuse at the substation pole TAYLOR BAY EAST 3. No fire on the pole or the ground. No damage assets. | Boric acid | 0 | 0 | 0 |  | eld01 | Burnt BA fuse tube. | Other electricity related | 42462.191 | 1 | Negligible: no ground fire | 799 | Residential |  | 20160205SPN_05 | Infrastructure (network-based) | -37.2096 | 145.877 | 1 | AusNet Services Distribution | Report | 1211 | 0.04061 | 22kV AC | Mangalore Airport | 3713 | Taylor Bay | Fuse
A Downer construction crew attended and isolated supply to safely replace the broken HV termination crossarm including three HV fuse units at the substation pole No. LIS 1109381. The HV 31.5amp Powder Filled Fuse had operated at ACR MT0986 located in Watts Road that was replaced restoring supply to a small amount of customers in the area. | 33-39 GRAYDENS ROAD, TYABB VIC 3913 | LIS No. 1109381 |  | Precipitation |  | Conductor clashing;Rot |  |  | 1 | The CFA reported there is a wire down in Graydens Road near Frankston-Flinders Road that has started a fire. A HV termination crossarm at "Watts P12-Graydens" substation failed that caused the 22kV red phase HV conductor connection to fail following conductor clashing that caused molten metal to fall to the ground and a 40sqm grass fire started that was extinguished by the CFA. The cause of the HV termination crossarm failure was deterioration and it broke at the crossarm brace bolt. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | HGS 23 | The cause of the HV termination crossarm failure was deterioration. | Grassfire | 42371.6375 | 1 | Small: 10 - 1000 sq.m | 792 | Residential |  | 20160205UTD_01 | Infrastructure (network-based) | -38.2847 | 145.1799 | 1 | United Energy Distribution | Report | 1200 | 0.022226 | 22kV AC | Moorabbin Airport | 3913 | Tyabb | Crossarm
The attending Powercor Fault Crew replaced the service cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, the distribution assets and between the points of contact, identified 0.5 Volts following replacement of the Cable. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 75 FYANS STREET, SOUTH GEELONG VIC 3220 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Russell Mayne (Electrician) received an electric shock while coming in contact with a bare earth conductor of a Socket Outlet while kneeling on the floor. Mr Russell Mayne had separated the bare earthing conductors at the Socket Outlet when he simultaneously contacted the separated conductors with his hands. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded neutral conductor of a two wire aluminium O/H neutral screened service cable as the cause of the high impedance associated with the return path of the neutral current. The corrosion of the O/H service neutral conductor was the result of water entering the insulation via a small perforation in the cable sheath, the cause of which was unable to be determined. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 12 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | Corroded neutral conductor of a two wire aluminium O/H neutral screened service cable. | Minor shock | 42348.4167 |  |  | 810 |  |  | 20160208PWA_06 | Infrastructure (network-based) | -38.1624 | 144.3574 | 1 | Powercor | Report | 1223 | 0.027572 | Low voltage AC (<1kV) | Avalon Airport | 3220 | South Geelong | OH Cable
The attending Powercor Fault Crew replaced the service cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, following replacement of the O/H Service Cable confirmed Zero Volts under normal load conditions. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 134 MCLEAN LANE, VINIFERA VIC 3591 |  |  |  |  | Fatigue |  | Phase to earth | 2 | Mr Gary Clarke received an electric shock while he was standing on the metal water tank stand when he made simultaneous contact with his hand on the metallic roof guttering. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a damaged O/H Service Active conductor located at the Dog Bone securing the service cable at the Customerâ€™s POA. The active conductor of the three wire O/H twisted aluminium (grey) service cable was damaged by the metal core of the O/H Service Dog Bone used to secure the service cable to the structure. The dog bone was broken at the opposite end to hook exposing the metal core, the service conductor had slipped on the dog bone under strain and the metal core of the dog bone had embedded into the active conductor of the O/H service cable. The hook of the dog bone was attached to a metal raiser bracket which was in contact with the metal roof structure and metal guttering. This condition caused voltage to flow through the metal core of the O/H service dog bone through the installations metal raiser bracket, metal roofing and metal guttering. The roofing structure and guttering was not connected to the general mass of earth and therefore gave rise to a potential difference of 242 Volts on the metallic guttering and roof structure to earth and between the points of contact. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | Service dog bone deteriorated | Minor shock | 24/10/2015 15:00 |  |  | 812 | Residential |  | 20160208PWA_08 | Infrastructure (network-based) | -35.2112 | 143.3841 | 1 | Powercor | Report | 1225 | 0.0034178 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3591 | Vinifera | AF Other
The attending Powercor Fault Crew replaced the deteriorated cable connector, reterminated the red phase active conductor and completed a polarity and NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, following replacement of the Cable Connector confirmed Zero Volts under normal load conditions. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 22 FRASER STREET, CLUNES VIC 3370 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Neil Slater of Central Highlands Water was attempting to establish the cause of a water leak in the Water Service supplying 22 Fraser Street Clunes when he noticed water flowing out of the adjacent Electricity Pit. Mr Slater removed the pit lid and while kneeling on the footpath with one hand on the ground he touched the top of the water in the pit with the back of his other hand to see if it was â€˜live.â€™ In doing so he received an electric shock. Voltage tests between an independent earth and the water in the electricity pit and the red phase cable connector identified deteriorated insulation exposing live parts of the red phase cable connector located in the electricity pit. This condition caused current flow from the red phase pit connector through the water that was leaking into the electricity pit, via Mr Slaterâ€™s hand and out his other hand to the wet concrete footpath and returned to the sub - station via the ground. | Services pit | 0 | 0 | 0 |  |  | Deteriorated insulation exposing live parts of the red phase cable connector located in the electricity pit. | Minor shock | 21/10/2015 8:30 |  |  | 813 | Roadway |  | 20160208PWA_09 | Infrastructure (network-based) | -37.293 | 143.7852 | 1 | Powercor | Report | 1226 | 0.034663 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3370 | Clunes | Connection
The public Lighting circuit supplying the pole was isolated and tagged and reported for follow up by underground crew. | FAWKNER PARK, MELBOURNE VIC 3004 |  |  |  |  | Unknown technical factor |  |  | 2 | John was walking his 3 year old bulldog through the park. John's dog yelped around a public light pole and pulled john into the pole (dog on leash) when the exposed skin on John's right forearm came into direct contact with the pole and he received a shock. Voltage tests between an independent earth and the pole showed 240V. The ground around the pole was also probed and found to be live out to a radius of about 2m. John came into direct contact with a live pole receiving the electric shock. It is not clear if the dog came into direct contact with the pole or experienced a voltage gradient whilst walking around the pole. | Public lighting | 0 | 0 | 0 |  |  | Cause not determined | Minor shock;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/01/2016 19:00 |  |  | 827 | Public space |  | 20160209PWA_04 | Infrastructure (network-based) | -37.8414 | 144.9833 | 1 | CitiPower | Report | 1245 | 0.030421 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | AF Other
Crew isolated supply and undertook repairs | 155 SHUTER AVENUE, GREENDALE VIC 3341 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which burnt the crossarm only. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 28/01/2016 11:30 | 1 | Negligible: no ground fire | 839 | Roadway |  | 20160209PWA_09 | Infrastructure (network-based) | -37.5562 | 144.315 | 1 | Powercor | Report | 1260 | 0.019112 | 22kV AC | Avalon Airport | 3341 | Greendale | Crossarm
Removed, made safe, restored cutomers and fuse taken back to depot for investigation. Replaced fuse tube and restored supply. No fire present. Corrective action to have EDO tube replaced. | 16 ANTONIA ROAD, BOOLARRA VIC 3870 | 2627079 | [6 empty] | 2 | IMS 220360. Initial CEOT report was: Candled EDO fuse, no fire, no damage. Final report: "Crew called to All Supply Failure to find hung- up EDO fuse. Replaced fuse tube and restored supply. No fire present. Corrective action to have EDO tube replaced." As a result, the incident category has been changed in IMS form serious to an electrical near-miss incident because there was no candled or burnt fuse tube. This incident will be included in the MEC Quarterly Report as a statistic. A Schedule 2 report is not required for this incident. | EDO fuse | 0 | 0 | 0 |  | mwts14 | Hun-up EDO fuse tube only. | Loss of supply | 42492.8472 | 1 | Negligible: no ground fire | 832 |  |  | 20160209SPN_01 | Infrastructure (network-based) | -38.3743 | 146.3004 | 1 | AusNet Services Distribution | Report | 1252 | 0.028929 | 22kV AC | Morwell (Latrobe Valley Airport) | 3870 | Boolarra | Fuse
CEOT dispatched fault crew and notified the DAO, to isolate, make safe and investigate. Tree cleared. LV re-instated. Line restored at 22:09. The DAO conducted a site visit and consulted AusNet Services' Vegetation Management group for a report. | 11 MONTGOMERY STREET, SALE VIC 3850 | 2507484 |  | Fallen |  |  |  | Phase to earth | 2 | IMS 220363. CFA report a tree has taken a street wire down and a fire is in the vicinity. Gum tree branch broke away from tree and fell onto the 4 wire LV. The LV failed in several places possibly because of the tree branch consisting of multiple branches. A small of 3 sq.m in size fire burnt the vegetation on the road reserve. No damage to private property was present. Report from Ausnet Services' Vegetation Management group: tree branch failure on SLE31, Camm 2507486, Pole No 7E (LV ext L02W). â€¢ The span is in an LBRA Declared area, which means that AusNet Services / Select Solutions are only responsible for pruning private trees. The local Shire's are responsible for their own trees. â€¢ Last inspected on 21/1/16 by Vegetation Management. The LBRA areas are currently being pruned in the East, with completion expected to be prior to end of March. â€¢ The span was coded as a CC for AusNet Services, and as a PT720 for the Shire due to the tree being on their land. This means that there is no pruning for AusNet Services, and no immediate action for the Shire (but likely action within 720 days). â€¢ If the tree showed any obvious signs of being hazardous at the time of inspection, it would have been reported. | Conductor (bare) | 0 | 0 | 0 |  | sle31 | Vegetation: Trees Incident | Grassfire | 42523.8403 | 1 | Localised: less than 10 sq.m | 836 | Residential |  | 20160209SPN_02 | Infrastructure (network-based) | -38.1155 | 147.0819 | 1 | AusNet Services Distribution | Report | 1258 | 0.038697 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | Trees
Fault crew isolated supply, made safe and arranged for the replacement of pole Lis 12-07227. The wood pole was replaced as it was too badly damaged to remain. The wood pole was replaced including the installation of new standard HV insulators which provide greater insulator creepage distances. There was no damage to customer's lawn or property. | 13 WINCHESTER DRIVE, BAYSWATER NORTH VIC 3153 | 1207227 |  | Animal |  |  |  | Phase to earth | 2 | IMS 220367. HV/LV intermediate pole burnt and badly damaged at a Telstra cable installation bracket bolt location on the wood pole due to a possum on HV steel crossarm causing a flashover from the HV conductor and tracking down the pole to the Telstra earth. | Pole (wood);Crossarm (steel);Insulators | 0 | 0 | 0 |  | bwr13 | Animal Incident | Pole-top fire | 42553.9201 | 1 | Negligible: no ground fire | 838 | Residential |  | 20160209SPN_03 | Infrastructure (network-based) | -37.8262 | 145.292 | 1 | AusNet Services Distribution | Report | 1261 | 0.018302 | 22kV AC | Moorabbin Airport | 3153 | Bayswater North | Animal
Crew isolated supply and undertook repairs | 64-66 MCARTHURS ROAD, ALTONA NORTH VIC 3025 |  |  | Lightning |  |  |  |  | 1 | MFB reported sparking and arcing on a pole at the incident location. On arrival the crew found that lightning had struck the structure causing damage to the centre phase 22kV bushing and bushing cover. Protection operated,. There was no ground fire. There were no reported injuries or third party property damages. | Insulators;Transformer | 0 | 1 | 0 |  |  | Lightning | Plant/equipment | 31/01/2016 1:08 |  | Negligible: no ground fire | 843 | Roadway |  | 20160210PWA_02 | Infrastructure (network-based) | -37.8342 | 144.8382 | 1 | Powercor | Report | 1266 | 0.0083403 | 22kV AC | Laverton Raaf | 3025 | Altona North | Lightning
Crew isolated supply and undertook repairs | 580 BELLS ROAD, SMYTHES CREEK VIC 3351 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV term substation pole, which burnt through the crossarm at the EDO bolt position causing the end of the crossarm to break and fall to the ground, resulting in a ground fire (approx. 1m x 1m) on the road reserve. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Grassfire | 42645.1986 | 1 | Localised: less than 10 sq.m | 845 | Roadway |  | 20160210PWA_03 | Infrastructure (network-based) | -37.5917 | 143.752 | 1 | Powercor | Report | 1269 | 0.0014838 | 22kV AC | Ballarat Aerodrome | 3351 | Smythes Creek | Crossarm
Crew isolated supply and undertook repairs | 419 NHILL-MURRAYVILLE ROAD, YANAC VIC 3418 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | An asset inspector reported a fire on a pole at the above location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole. The cross arm remained intact and the conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm Fire | Pole-top fire | 42462.359 | 1 | Negligible: no ground fire | 849 | Roadway |  | 20160211PWA_01 | Infrastructure (network-based) | -36.1165 | 141.4102 | 1 | Powercor | Report | 1274 | 0.013644 | 22kV AC | Horsham Aerodrome | 3418 | Yanac | Crossarm
Crew undertook repairs | 85 BROWNS ROAD, WERRIBEE VIC 3030 |  | Theft | [5 empty] | 2 | An Asset Inspector reported that copper earths had been stolen from a pole type substation at the incident location. On arrival the crew found the copper earths had been stolen by unknown third parties. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Theft | Damage to network assets | 42462.4792 |  |  | 850 | Roadway |  | 20160211PWA_02 | Infrastructure (network-based) | -37.924 | 144.6076 | 1 | Powercor | Report | 1275 | 0.018161 | Earthing cable | Laverton Raaf | 3030 | Werribee | Other
Crew isolated supply and undertook repairs | 63 RESERVE ROAD, WOORINEN VIC 3589 |  |  |  |  | Candled fuse |  |  | 1 | A field crew attending following an outage found that an EDO fuse had operated at the incident location due to a magpie causing a fault, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. The magpie fell to the ground. The incident resulted in a ground fire (Approx. 1 sqm) on the road reserve. There were no reported injuries. | EDO fuse | 0 | 0 | 0 |  |  | Candled fuse | Grassfire | 42553.6042 | 1 | Localised: less than 10 sq.m | 860 | Roadway |  | 20160211PWA_10 | Infrastructure (network-based) | -35.2738 | 143.4601 | 1 | Powercor | Report | 2911 | 0.037953 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen | Animal
Crew inspected pole, superficial damage only | 17-19 GARDEN CRESCENT, ECHUCA VIC 3564 |  | Vandalism | [5 empty] | 2 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a fire had been started on the pole approx. 1m from the ground. The field crew reported that an unknown person had placed a cigarette butt against the pole resulting in the fire damage. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | unknown third party vandalism | Grassfire | 42523.5722 |  | Negligible: no ground fire | 861 | Roadway |  | 20160211PWA_11 | Infrastructure (network-based) | -36.1387 | 144.7442 | 1 | Powercor | Report | 1286 | 0.0069907 | Not applicable | Shepparton Airport | 3564 | Echuca | Other
Crew rehung cable | 265 HIGH STREET, ECHUCA VIC 3564 |  | Vehicle | [5 empty] | 2 | A bus company reported that one of their buses had made contact with a low wire at the incident location. On arrival the crew found that a LV service cable had come off the hook on the service pole and was low over the road. The hook was not damaged and the crew reported that it was likely that an unknown high load had contacted the service at some time previous. The crew restored the service and the height was measured at 5.7m. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Unknown high load contacted LV service cable | Damage to network assets | 42615.3938 |  |  | 862 | Roadway |  | 20160211PWA_12 | Infrastructure (network-based) | -36.1439 | 144.7518 | 1 | Powercor | Report | 2914 | 0.012883 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | Vehicle
Crew isolated supply and undertook repairs | 116 HEPBURN-NEWSTEAD ROAD, ELEVATED PLAINS VIC 3461 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV pole which caused the crossarm to break, however the conductors remained aloft. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 22/01/2016 9:55 | 1 | Negligible: no ground fire | 727 | Roadway |  | 20160127PWA_03 | Infrastructure (network-based) | -37.2935 | 144.1243 | 1 | Powercor | Report | 1099 | 0.039563 | 22kV AC | Ballarat Aerodrome | 3461 | Elevated Plains | Crossarm
Crew sent to investigate. A construction crew were called to attend and they repaired the damage to the conductors. The incident was also investigated by Select Solutions Vegetation Management group. | 1 OLIVER STREET, YARRA GLEN VIC 3775 | 106465 |  | Fallen;Property owner/customer |  |  |  | Phase to phase | 1 | IMS 220080. CEOT received incident report from Fire Brigade for a pole. A mature Cupressus macrocarpa (Monterey Cypress) has snapped out a main leader at ground level which has fallen over the overhead lines breaking the conductors. The tree had a poor structure which is common for this species. There was no sign of decay at the point of entry but the surrounding trees are showing symptoms of early stages of cypress canker which will inevitability result in the death of the trees. The limb that failed was approximately 12m tall & was 400mm in diameter at its widest point. The tee limb brought down the HV and LV conductors at lis106465. A small grass fire in vicinity of size 1m x 1m was observed. The tree was not classed as a hazardous tree and there are no other hazardous trees in the vicinity. The tree/limb was not inside the clearance space. Electrical protection operated - ACR LD228 tripped. | Conductor (bare) | 0 | 0 | 0 |  | cpk12 | Vegetation: Trees Incident | Grassfire | 18/01/2016 23:25 | 1 | Localised: less than 10 sq.m | 747 | Residential |  | 20160128SPN_02 | Infrastructure (network-based) | -37.6602 | 145.3681 | 1 | AusNet Services Distribution | Report | 1127 | 0.039279 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3775 | Yarra Glen | Trees
The fault crew attended and made safe and temporarily fixed the problem. An action item has been placed on the local Design Officer to manage the repair of the underground asset. | 232 MUMMERY ROAD, MYRTLEFORD VIC 3737 | 4500211 | Working too close to underground cables | [5 empty] | 2 | IMS 220176. Report of damage to LV service pit outside of 22 Mummery Lane. Fault Crew arrived and confirmed that the LV service pit has been dug up and damaged. A local Council grader was conducting maintenance works and accidentally exposed the pit. | Services pit | 0 | 0 | 0 |  | myt8 | 3rd party operating a road grader made contact with live service pit. | No Go Zone (contact) | 25/01/2016 14:45 |  |  | 749 | Residential |  | 20160128SPN_04 | Infrastructure (network-based) | -36.5591 | 146.746 | 1 | AusNet Services Distribution | Report | 1130 | 0.034513 | Low voltage AC (<1kV) | Wangaratta Aero | 3737 | Myrtleford | Dug up
As the electricity supply had previously been reconnected, the LEI was to respond to individual customers requests if they advised of damaged electrical equipment following the tree branch contacting the overhead conductors the previous day. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1774 MALVERN ROAD, MALVERN EAST VIC 3145 | LIS No. 2316724 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1713hrs on 26/01/2016, 11kV feeder K 13 circuit breaker successfully reclosed and held. 26/01/2016 - A rotted tree branch from a council tree in Hedgeley Dene Gardens located next to 1774 Malvern Road, contacted the high voltage conductors that caused the HV feeder to successfully reclose and hold. The LV white and blue phase fuses at "Stanley-Malvern" substation were replaced that restored supply to customers after the tree branch contacted the conductors. 27/01/2016 - Customers supplied from the south circuit of "Stanley-Malvern" substation contacted the United Energy faults and emergencies call centre advising that some electrical appliances are not working since the supply outage late yesterday. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Stanley-Malvern" substation. The LEI confirmed that a high voltage injection occurred (BWD 1601) affecting a small number of customers that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | K 13 | Vegetation: Trees Incident | HV injection;Loss of supply | 26/01/2016 17:13 |  |  | 742 | Public space |  | 20160128UTD_03 | Infrastructure (network-based) | -37.8668 | 145.0584 | 1 | United Energy Distribution | Report | 1116 | 0.0024769 | 11kV AC | Moorabbin Airport | 3145 | Malvern East | Trees
Made safe | 42 MAFFRA STREET, COOLAROO VIC 3048 |  |  | Heat;Cold |  | HV injection |  |  | 1 | HVI to one property due to broken crossarm caused by a pole fire | Conductor (bare);Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  |  | Pole fire cause crossarm to break | Pole-top fire;HV injection | 22/01/2016 19:17 | 1 | Negligible: no ground fire | 751 | Industrial |  | 20160129JEM_02 | Infrastructure (network-based) | -37.6604 | 144.9411 | 1 | Jemena | Report | 1132 | 0.040528 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3048 | Coolaroo | Pole
Made safe | 6 NEILSON PLACE, FOOTSCRAY VIC 3011 |  |  | Lightning |  |  |  |  | 1 | HV conductors fell to the ground | Conductor (bare) | 0 | 0 | 0 |  |  | Lightning hit the crossarm on the pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/01/2016 23:15 |  |  | 758 | Residential |  | 20160201JEM_01 | Infrastructure (network-based) | -37.7992 | 144.9078 | 1 | Jemena | Report | 1145 | 0.015034 | 22kV AC | Essendon Airport | 3011 | Footscray | Conductor
A LEI and faults truck attended and the South East Water plumber advised that he didn't receive an electric shock. The occupier advised that lights had been dimming at night. A NST was completed that failed and the LEI tested to an independent earth to the water meter and measured 10v, 17v to the neutral bar and 30v on the neutral with a 4amp load connected. The faults crew identified the neutral screen service had been damaged mid-span by a council tree and corroded the internal neutral screen. The damaged two phase neutral screened service was replaced with a XLPE type and the LEI tested the installation that confirmed the fault had been rectified. The service was connected to a different pole to avoid the council tree. | 15 MITFORD STREET, ST KILDA VIC 3182 | LIS No. 2332760 |  | Alive;Council |  | Neutral fault |  | Phase to earth | 2 | South East Water is on site and measured up to 50v on the water pipe. The worker received a slight zap when he was working on the water pipe. A South East Water plumber received a slight electric shock from the water pipe whilst working on the leaking pipe outside 15 Mitford Street, StKilda. He proceeded to test and measured fluctuating voltages at the water meter and contacted the United Energy faults and emergencies call centre. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Minor shock | 31/01/2016 10:30 |  |  | 771 | Roadway |  | 20160203UTD_03 | Infrastructure (network-based) | -37.8715 | 144.9812 | 1 | United Energy Distribution | Report | 1170 | 0.029816 | Low voltage AC (<1kV) | Moorabbin Airport | 3182 | St Kilda | Trees
Emergency high voltage switching was completed on 22kV feeder NP 16 to minimise the number of customers affected and the 66kV road side 11 shed insulator was replaced with the 22kV conductors re-tied under Access Authority conditions prior to the supply being restored with the LV fuses for the west circuit replaced at "Theodore-Backous" substation. Three 150w HPS public lights were also damaged following the HVI and a further trouble order was created for ACE Energy to replace the damaged lanterns. | 2 ATHOL ROAD, NOBLE PARK VIC 3174 | LIS No. 9859030 | Vehicle |  |  | Conductor clashing |  |  | 1 | At 2210hrs on 30/01/2016, 66kV feeder SVTS-NP circuit breaker locked out. At the same time 22kV feeder NP 16 circuit breaker reclosed to lockout. There was a report of a car into a pole in Corrigan Road, Noble Park. A vehicle struck a 66kV angle type 1 pole (LIS No. 9859030) located in Athol Road 1 pole west of Corrigan Road that caused a 66kV conductor to briefly contact the 22kV HV tee-off conductors and the LV conductors at the corner pole. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the west circuit of "Theodore-Backous" substation. The LEI confirmed a high voltage injection occurred (KEY 1601) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole top;Insulators | 0 | 0 | 0 |  | 66kV feeder SVTS- NP and 22kV feeder NP 16 | A vehicle struck a ttimber 66kV angle type 1 pole that caused a 66kV conductor to briefly contact the 22kV HV tee-off conductors and the LV conductors at the tee-offpole. | HV injection;Loss of supply | 30/01/2016 22:10 |  |  | 775 | Roadway |  | 20160203UTD_05 | Infrastructure (network-based) | -37.9733 | 145.1665 | 1 | United Energy Distribution | Report | 1180 | 0.031946 | 22kV AC;66kV AC | Moorabbin Airport | 3174 | Noble Park | Vehicle
After gaining an exemption from Energy Safe Victoria. No. E/18523. The attending Powercor Fault Crew replaced the section of existing O/H neutral screen cable and completed an NST test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, identified Zero Volts following replacement of the O/H service cable. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H service cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 3874 WARRNAMBOOL-CARAMUT ROAD, MINJAH VIC 3276 |  |  |  |  | Neutral fault |  |  | 2 | Mr. Brad Beaven was showering when he received an electric shock as he made simultaneous contact between his hand on the taps and his feet on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H neutral screen conductor, mid span of the Overhead Private Electric Line which was identified as the cause of the high impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 10 Volts on the water piping system and between the points of contact. | Neutral screen | 0 | 0 | 0 |  |  | Corroded Neutral Conductor, Private Electric Line | Minor shock | 42014.375 |  |  | 785 | Residential |  | 20160204PWA_04 | Infrastructure (network-based) | -38.0586 | 142.4919 | 1 | Powercor | Report | 1193 | 0.04024 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3874 | Minjah | OH Cable
Fault Crew attended and reterminated the loose neutral connection. CTA re-tested pole, all VESI tests passed. | 379 CHAPEL STREET, SOUTH YARRA VIC 3141 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Myhalo received an electric shock when he made simultaneous contact between the metallic street pole with one hand and the metallic pedestrian safety barrier at the kerb with his other hand Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a loose neutral connection at the FOLCB on the pole. This condition caused current to flow through the parking sign MEN connection, main earthing conductor and the steel street pole. An impedance to the flow of current between the general mass of earth and the steel street pole was sufficient enough to cause a voltage rise of 40 volts between the street pole and the metallic pedestrian safety barrier. | Pole (steel) | 0 | 0 | 0 |  |  | Loose neutral connection at FOLCB | Minor shock | 42165.5833 |  |  | 787 | Roadway |  | 20160204PWA_06 | Infrastructure (network-based) | -37.8459 | 144.9941 | 1 | CitiPower | Report | 1195 | 0.021567 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Connection
CEOT dispatched a fault crew to make safe, isolate and investigate the incident. The crew attended , isolated supply and made safe. The fallen tree was removed by the Council and customer's supply was subsequently restored. The HV conductor was checked for correct height by lineworkers. In relation to the backfeed situation: The downstream transformer windings introduce additional impedance to the fault circuit that resulted in low fault current that was not detected by the upstream protection including Sensitive Earth Fault protection. The Sensitive Earth Fault protection on the AusNet Servicesâ€™ network is designed to clear the majority of high impedance faults, the sensitivity of this protection is a balanced compromise between detecting high impedance faults but also operating the network and catering for normal imbalances and transient disturbances. AusNet Services is adopting industry accepted practice in the detection of high impedance faults. To date there are no commercially available protection relay products which will detect high impedance faults with a greater sensitivity without practical operational shortcomings. AusNet Services is however investigating emerging technologies to detect these types of high impedance faults. | 80 OLD KOONWARRA-MEENIYAN ROAD, KOONWARRA VIC 3954 | 2000915 |  | Fallen;Council |  |  |  |  | 1 | IMS 219858. Tree pinning 22 kV load side conductor down, live on ground via back feed through downstream winding of transformers. No fire, no damage. Voltage of line was 22kV Single Phase. Electrical protection operated - HV fuse dropped but did back feed - found via using a Modiwark. There were very windy days preceding this incident and the tree was rotten right through. The Council did not have the tree listed as hazardous. The tree was located on the road reserve and it fell across the road. The fault crew rang the Council to remove the tree once the area was made safe. The conductor did not touch the ground the tree's weight took it down to just a few feet above ground height. No repairs to the conductor were necessary. Report from AusNet Services' Vegetation Management group states: "Trunk on Gum tree (Eucalyptus ovata) has failed one metre from ground level, causing the head of the tree to come in contact with HV overhead conductors. Base of gum tree is located 15 metres from closest overhead conductor. Most of the failed timber has been removed from site; height of tree could not be established. Rot and fungal fruiting body evident at failed section of tree, this would suggest poor tree health has caused tree to fail. Reports done for other hazardous trees in same location. There was no fire start on the ground so this incident is not reportable as a vegetation fire start." | Conductor (bare) | 0 | 0 | 0 |  | lga14 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42461.2569 |  |  | 795 | Roadway |  | 20160205SPN_01 | Infrastructure (network-based) | -38.5484 | 145.9506 | 1 | AusNet Services Distribution | Report | 3739 | 0.007515 | 22kV AC | Morwell (Latrobe Valley Airport) | 3954 | Koonwarra | Trees
Area isolated. Faulted area sectionalized. Grass fire was extinguished. Switch opened, repair work completed and supply restored. Advised Works Practices Advisory personnel and CEOT Manager. Operator involved stood down from operating pending an investigation. ESV notified. | 10 JONES ROAD, DROUIN VIC 3818 | 2703341 |  |  |  |  | Not followed |  | 1 | IMS 220314. A gum tree fell over HV conductors, wires down, ACR operated - tripped out. CEOT advised crew to isolate - open WL158 (NKG gas switch). After the switch was opened by the crew, CEOT closed WL174, faulted area became energized (feeder tripped). A grass fire was subsequently observed where the wires were down. The fire was observed to be 4 to 6 meters from the pole and was 2m x 2m in size. Crew found that switch WL158 was still closed. | Conductor (bare) | 0 | 0 | 0 |  | wgl11 | The HV switch was operated and the operator believed it was Open, however it was Closed. The HV Switch was not correctly confirmed as Open. Operator was rushing and was distracted and did not confirm switch semaphore indicated Open. | Grassfire | 42431.7222 | 1 | Localised: less than 10 sq.m | 796 | Agricultural |  | 20160205SPN_02 | Infrastructure (network-based) | -38.152 | 145.8728 | 1 | AusNet Services Distribution | Report | 2686 | 0.022598 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Drouin | Trees
A LEI and faults truck attended and completed voltage tests between an independent earth and all metal equipment that was bonded to the metallic water system and measured 60v under load. A NST was completed at the main switchboard that failed. Another NST was completed at the POA that failed. The faults crew commenced to check all connections and identified a loose neutral connection at the pole end - LIS No. 3304062. The grey twisted services neutral connection was cleaned, greased and re-terminated and the LEI retested the installation that confirmed the fault had been rectified with 0v measured on the metallic water system. | 20 HAIG AVENUE, EDITHVALE VIC 3196 | LIS No. 3304062 |  | Prone to salt deposition |  | Corrosion;Electrical breakdown |  | Phase to earth | 2 | Customer called to report they received a slight electric shock from the shower taps. The occupier was showering and received an electric shock whilst making contact with the shower taps as he stood on the wet shower base. | Service conductor;Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | A loose corroded neutral connection at the pole end. | Minor shock | 42431.7917 |  |  | 794 | Residential |  | 20160205UTD_03 | Infrastructure (network-based) | -38.0401 | 145.1153 | 1 | United Energy Distribution | Report | 1202 | 0.010065 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Edithvale | Connection
Powercor linesman replaced the service & CTA carried out all tests and including an N.S.T & Voltage tests following the repair and normal results were obtained. | 9 HARLOW COURT, DEER PARK VIC 3023 |  |  |  |  | Corrosion |  |  | 2 | Linda received an electric shock when she simultaneously contacted the metallic tap with one hand and the metallic sink with the other hand. A voltage test between the tap and metal sink identified 57 volts. Further testing of the installation identified a corroded service neutral at the pole end. The condition described above caused current to flow in the metallic water pipe system via the installation MEN connection, main earth and water pipe bonding conductors. The level of impedance to the flow of current through the metallic water pipe with respect to the general mass of earth was sufficient to cause a voltage rise of 57 volts on the metallic parts of the plumbing system. | Service conductor | 0 | 0 | 0 |  |  | Corroded service neutral at the pole end | Minor shock | 13/10/2015 20:00 |  |  | 807 | Residential |  | 20160208PWA_03 | Infrastructure (network-based) | -37.7524 | 144.7683 | 1 | Powercor | Report | 1595 | 0.027073 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Connection
The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact following the replacement of the O/H Service Cable, confirmed 0.9 Volts under normal load conditions. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. Ms Dianne Younis (Parent) was issued with an Electrical Fault on Customerâ€™s Premises Notice, regarding the installation of an Equipotential Bonding Conductor to the shower waste water pipes and the concrete slab to minimise the risk of any existing potential difference between the points of contact. | 5 ILUKA COURT, JAN JUC VIC 3228 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Alex Cordner was showering when he received an electric shock as he made simultaneous contact between his hands on the metallic shower taps and his bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral conductor termination at the Customerâ€™s FOLCB located at the POA, resulting in a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 1.7 Volts on the water piping system and between the points of contact. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral conductor termination at the Customerâ€™s FOLCB located at the POA. | Minor shock | 42046.4167 |  |  | 815 | Residential |  | 20160208PWA_11 | Infrastructure (customer connection) | -38.3517 | 144.2942 | 1 | Powercor | Report | 1228 | 0.005728 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
The HV and LV overhead conductors were isolated and an Access Authority issued to allow the CFA access to extinguish the fire in the VT. VicRoads contractors Fulton Hogan also attended the site to clean up the oil spill. An investigation commenced and the preliminary investigation has identified the VT installed was rated at 11kV. | 37 CHANDLER ROAD, NOBLE PARK VIC 3174 | LIS No. 0619096 |  |  |  | Incorrect design | Inappropriate tools/plant/equipment |  | 1 | At 1107hrs on 04/02/2016, 22kV feeder NP 36 circuit breaker reclosed to lock out. Live Line Sequence had been enabled to install cut out tools using glove and barrier techniques to connect a voltage transformer at the new remote controlled gas switch. 28/01/2016 - A Downer Glove and Barrier work crew had the task to replace the HV crossarm, remove 22kV manual gas switch No. DN8598 and install a new remote controlled gas switch to be known as DN3217 at pole No. LIS 0619096 located in Chandler Road, 1 pole south of Heatherton Road, Noble Park. This switch is the normal open point between 22kV feeders NP25 and NP36. 04/02/2016 - The Downer Glove and Barrier crew were to install the control leads for the remote controlled gas switch (RCGS) following the construction work completed last week. As part of the work the crew were commissioning a Tyree Voltage Transformer (VT) at the RCGS using a cut out tool to energise the VT. After energising the VT, the crew descended to the LV fuse box to undertake further commissioning work. On their ascent up to the HV switch, the VT ruptured and caught fire causing the lid to be blown off and hot oil from inside the VT to be released that contacted a lineworker on the ground. The lineworker received oil burns and was transported to hospital by ambulance for observation and was released without requiring treatment. The employees in the EWP were not affected. In addition, the heated oil splashed onto 5 surrounding vehicles. Members of the CFA, Vic Police, WorkSafe and ESV were also in attendance. United Energy contacted ESV but were advised the event had previously been reported with reference number 4437632 provided. | Transformer | 1 | 1 | 0 |  | NP 36 | Line Worker experienced minor burns from hot oil when voltage transformer failed on energisation releasing hot oil. | Pole-top fire;Loss of supply;Medical attention (first aid/doctor/hospital) | 42462.4632 | 1 | Localised: less than 10 sq.m | 804 | Roadway |  | 20160208UTD_01 | Infrastructure (network-based) | -37.9671 | 145.1872 | 1 | United Energy Distribution | Report | 1217 | 0.01975 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | AF Other
Replaced crossarm | 2-4 ARCADE WAY, AVONDALE HEIGHTS VIC 3034 |  |  |  |  | Leakage |  |  | 1 | Crossarm fire corner Arcade Way and North Road | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 42006.3479 | 1 | Negligible: no ground fire | 835 | Residential |  | 20160209JEM_06 | Infrastructure (network-based) | -37.7567 | 144.8536 | 1 | Jemena | Report | 5513 | 0.033016 | 22kV AC | Essendon Airport | 3034 | Avondale Heights | Crossarm
The attending Powercor Fault Crew replaced the O/H Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system and the distribution assets identified Zero Volts following replacement of the O/H Service Cable. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 137 GARLANDS ROAD, MINERS REST VIC 3352 |  |  |  |  | Corrosion |  |  | 2 | Mr Paul Hoffmann, Plumbing Contractor was removing a Hot Water Service when he received an electric shock when he made simultaneous contact with his hand on the metallic frame of the Hot Water Service and his leg while kneeling on the wet concrete floor of the back veranda. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Aluminium Neutral Screen Conductor of the O/H Neutral Screened Service Cable, located at the Wrap-on Termination Device at the Customerâ€™s POA, which was identified as the cause of the high impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 56.0 Volts on the earthing system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | Corroded Aluminum Neutral Screen Conductor of the O/H Neutral Screened Service Cable, located at the Wrap-on Termination Device at the Customerâ€™s POA. | Minor shock | 42402.4375 |  |  | 820 | Residential |  | 20160209PWA_01 | Infrastructure (network-based) | -37.4877 | 143.8158 | 1 | Powercor | Report | 1237 | 0.0041759 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Miners Rest | OH Cable
The attending Powercor Fault Crew replaced the O/H Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system and the distribution assets identified Zero Volts following replacement of the O/H Service Cable. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 9 BOLDEN AVENUE, WARRNAMBOOL VIC 3280 |  |  |  |  | Corrosion |  |  |  | Mr Brian Murphy was opening the metal Meter/Switchboard Enclosure to check why the lights were dimming when he received an electric shock as he made simultaneous contact between his hands on the metal Meter/Switchboard Enclosure and his bare feet while standing on the damp concrete veranda. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s Fused Overhead Line Connection Box (FOLCB) which was identified as the cause of the high impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 46.2 Volts on the earthing system and between the points of contact. | Customer installation | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB. | Minor shock | 42431 |  |  | 831 | Residential |  | 20160209PWA_08 | Infrastructure (network-based) | -38.3846 | 142.5095 | 1 | Powercor | Report | 1250 | 0.0035278 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | OH Cable
Replaced service conductor | 51 SAUNDERS STREET, COBURG VIC 3058 |  |  |  |  | Neutral fault |  |  | 2 | Plumber received electric shock when disconnecting water pipe | Service conductor | 0 | 0 | 0 |  |  | Broken neutral in service conductor at pole end | Minor shock | 42584.9153 |  |  | 841 | Residential |  | 20160210JEM_01 | Infrastructure (network-based) | -37.7492 | 144.951 | 1 | Jemena | Report | 1263 | 0.015042 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Conductor
Crew isolated supply and undertook repairs | 4150 DARTMOOR-HAMILTON ROAD, GRASSDALE VIC 3302 |  |  |  |  | Mechanical breakdown;Unknown technical factor |  |  | 2 | A line inspector reported a fire on a pole at the incident location. On arrival the crew found that a tie had broken on a SWER pole and the SWER conductor had become dislodged and rested against the pole resulting in a burn mark at the top of the pole, which remained intact. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Broken HV tie wire | Pole-top fire | 42431.5806 | 1 | Negligible: no ground fire | 848 | Agricultural |  | 20160210PWA_06 | Infrastructure (network-based) | -37.7845 | 141.6683 | 1 | Powercor | Report | 1272 | 0.019481 | 12.7kV AC (SWER) | Hamilton Airport | 3302 | Grassdale | Connection
Crew isolated supply and arranged repairs | 54-84 MCSWAIN ROAD, ECHUCA VIC 3564 |  | Working too close to underground cables | [5 empty] | 1 | A boring contractor reported making contact with an underground cable while boring at the incident location. On arrival the crew found that contractor (Comdain Infrastructure, Contact: Ian Wilkie, Ph: 0419 873 513) was operating a borer and contacted a 22kV underground cable while installing a gas service to 56 McSwain Rd, causing damage to the cable. The contractors had dial before you dig plans. Protection operated. There were no reported injuries. | Cable | 0 | 0 | 0 |  |  | Contact with UG cable | No Go Zone (contact) | 42615.5486 |  |  | 855 | Roadway |  | 20160211PWA_06 | Infrastructure (network-based) | -36.142 | 144.7227 | 1 | Powercor | Report | 1280 | 0.007331 | 22kV AC | Bendigo Airport | 3564 | Echuca | Dug up
Initial report: CEOT dispatch a fault crew and the Duty Officer to isolate supply, make safe and investigate. Final report: The Downer fault crew were on site and they isolated and earthed the line. The customer removed the balloon from the line. DAO inspected the line and reported there was no visible damage to the HV conductors. The fault crew re-instated supply. | 10 SPRING LANE, GRUYERE VIC 3770 | 1032877 | Manned balloon |  |  |  |  | Phase to phase | 1 | IMS 220481. Initial report:Report of a hot Air balloon contacting electrical main and the balloon is hanging over the mains, People still in the balloon basket. No report of injury or any other damage. Final report: DAO attended site 0915hrs. Balloon operator "RICHARD" (0412066 666) from "PICTURE THIS BALLOON CO" (03 9429 0277). Richard described coming in to land and seeing the HV line between poles 1008468 and 1008471, however he did not see the line between poles 1032877 and 1033055. According to Richard, the balloon was on the ground skidding along when they stopped more abruptly than usual. When Richard got out of the balloon he saw the balloon hanging over the HV Line. The DAO measured the height of the HV line after the balloon had been removed and this was 28.8m. Speaking with Richard, the balloon and basket setup is 35m tall. The HV was still in the air and there was no visible damage from the DAO's point of view and inspection. Richard advised no person was injured or received any electric shock. None of the passengers were present by the time the DAO arrived at site. Richard requested several times that the DAO ask the fault crew to "hurry up" so he could get the balloon down. The DAO advised RIchard that the crew will do what they can as promptly as possible but that safety is the main concern and that we will wait until they give the go ahead before moving any closer to the balloon and that we need to stay at least 10m away for safety purposes. The wind started picking up and RIchard became more and more agitated as time went on. As the Downer fault crew were driving up the road, Richard ran off to meet them and put himself in a dangerous position as he was grabbing the balloon and ropes, but at this point there was no advice from the Downer fault crew that the line was dead at this point in time. Despite the DAO's concern and words to Richard previously he had no regard for his own safety at this time and the DAO believes it was lucky that the Dower fault crew had isolated and earthed the line, thus making the line "dead" as RIchard assumed this, as the crew were not working on the line anymore. The Downer fault crew did advise that the line was dead and the balloon was removed from the HV Line. Richard proceeded to tie down and fold up the balloon and once this was secured, the Downer fault crew began re-instating supply. A support crew for Richard arrived at approximately 10:30am and the DAO left the site at 11am. Per advice from the Downer fault crew on-site, the 2x outer HV fuses had blown on the spur (confirmed Red and Blue Phases on-site - Switch - LD010) but that the Centre Phase (White) had remained in until they isolated upon their arrival. Advice from "Will" from the winery also that Hot Air Balloons do not have permission to land in this property, but they do for next door. Richard said he thought he was in the other property and was not aware he was in the wrong property here. | Conductor (bare) | 0 | 0 | 0 |  | ldl23 | Hot air balloon contact with overhead HV conductors. | No Go Zone (contact) | 13/02/2016 7:43 |  |  | 868 | Agricultural |  | 20160214SPN_01 | Infrastructure (network-based) | -37.6971 | 145.4278 | 1 | AusNet Services Distribution | Report | 1294 | 0.0012465 | 22kV AC | Moorabbin Airport | 3770 | Gruyere | Other
Crew isolated supply and undertook repairs | 140 MORTLAKE-ARARAT ROAD, MORTLAKE VIC 3272 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a cross arm fire had occurred on a 22kV/LV substation pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 17/02/2016 9:56 | 1 | Negligible: no ground fire | 877 | Roadway |  | 20160218PWA_03 | Infrastructure (network-based) | -38.0652 | 142.817 | 1 | Powercor | Report | 1306 | 0.025799 | 22kV AC | Warrnambool Airport Ndb | 3272 | Mortlake | Crossarm
Supply isolated and made safe | 51 BANYULE ROAD, ROSANNA VIC 3084 |  |  | Fallen;Property owner/customer |  |  |  |  | 1 | High voltage cables on ground caused by customer tree branch | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/02/2016 15:05 |  |  | 886 | Residential |  | 20160222JEM_01 | Infrastructure (network-based) | -37.7422 | 145.0778 | 1 | Jemena | Report | 1317 | 0.021248 | 11kV AC | Essendon Airport | 3084 | Rosanna | Trees
Crew isolated supply | 35A MELTON HIGHWAY, TAYLORS LAKES VIC 3038 |  | Vehicle | [5 empty] | 1 | Jemena contacted Powercor Report Room advising of a car into pole at the above location and possible fatality. Pole was on boundary of Jemena and Powercor assets. On arrival the crew found that a single vehicle had collided with a wooden cable head pole resulting in a fatal injury to the driver of the vehicle. There was no ground fire. | Pole (wood) | 0 | 0 | 0 |  |  | Car hit pole | Not involving electrocution;Damage to network assets | 18/02/2016 20:40 |  |  | 890 | Roadway |  | 20160222PWA_02 | Infrastructure (network-based) | -37.7009 | 144.796 | 1 | Powercor | Report | 2916 | 0.013618 | Not applicable | Melbourne Airport | 3038 | Taylors Lakes | Vehicle
Crew isolated supply and checked assets for damage | 541 GRAHAM STREET, PORT MELBOURNE VIC 3207 |  |  | Bird |  |  |  |  | 1 | A field worker reported a fire at the incident location. On arrival the crew found a crow had caused a flash over on a 66kV cable head pole, causing the crow to fall to the ground resulting in a ground fire (approx. 0.3m x 0.2m) on the road reserve. Protection operated. There were no reported injuries. | Pole top | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 20/02/2016 12:23 | 1 | Localised: less than 10 sq.m | 894 | Roadway |  | 20160222PWA_04 | Infrastructure (network-based) | -37.8292 | 144.9312 | 1 | CitiPower | Report | 1326 | 0.039613 | 66kV AC | Essendon Airport | 3207 | Port Melbourne | Animal
Crew isolated supply and undertook repairs | 29 CLYDE CRESCENT, WARRNAMBOOL VIC 3280 |  |  |  |  | Age |  |  | 2 | A customer reported no supply and the service wire broken at the incident location. On arrival, the crew found that a neutral screen service had broken at the POA, causing it to fall to the ground, resulting in a fire (Approx. 0.3m x 0.1m) on private property. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Broken LV service cable | Grassfire | 22/02/2016 16:59 | 1 | Localised: less than 10 sq.m | 896 | Residential |  | 20160223PWA_01 | Infrastructure (network-based) | -38.3716 | 142.4635 | 1 | Powercor | Report | 1331 | 0.012095 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Conductor
Crew isolated supply and undertook repairs | UNIT 1 109 NORMANBY AVENUE, THORNBURY VIC 3071 |  | Vehicle | [5 empty] | 2 | A nearby resident reported that a truck had made contact with an overhead line at the incident location. On arrival the crew found that a truck (Registration No XSL-449 â€“ No other details obtained) had contacted a LV overhead service cable in the driveway of the property, damaging the insulation and causing it the cable to come to rest approx. 2.7m from the ground. There were no reported injuries or third party property damages. Following repairs the cable was measured at 3.1m at the point of contact. | Service conductor | 0 | 0 | 0 |  |  | Truck contacted LV service cable | No Go Zone (contact) | 13/02/2016 12:53 |  |  | 902 | Residential |  | 20160223PWA_07 | Infrastructure (network-based) | -37.7586 | 144.9902 | 1 | CitiPower | Report | 1337 | 0.0058356 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Vehicle
Crew isolated supply and undertook repairs | 54 MARTIN STREET, HAMILTON VIC 3300 |  | Vehicle | [5 empty] | 2 | The local Council reported a wire down at the incident location. On arrival the crew found that a council road works truck (Hamilton City Council) had made contact with a LV service cable while resurfacing the road. The service broke mid span and fell to the ground. Following repairs the service height was measured at 5.5mtrs at the centre of the road. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Contact with LV service cable | No Go Zone (contact);Damage to network assets | 15/02/2016 15:28 |  |  | 908 | Roadway |  | 20160223PWA_13 | Infrastructure (network-based) | -37.7466 | 142.0273 | 1 | Powercor | Report | 1343 | 0.034512 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Vehicle
Crew isolated supply and undertook repairs | 19 CHESTER STREET, NEWTOWN VIC 3220 |  | Working too close to overhead lines | [5 empty] | 2 | A builder reported that an overhead cable had been hit by a concrete pumping truck and the live cable was hanging approx. 2m above the ground at the incident location. On arrival the crew found that a concrete pumping truck (Operated by Maximum Concrete Pumping Pty Ltd, 15 Freeman Crt, St Albans, Ph: 0418 992 852) had contacted a LV service cable causing the service to hang low (approx. 2m ex ground). There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | LV service contacted by concrete pumping truck | No Go Zone (contact) | 16/02/2016 9:50 |  |  | 910 | Residential |  | 20160223PWA_15 | Infrastructure (network-based) | -38.1409 | 144.3216 | 1 | Powercor | Report | 1345 | 0.0025255 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | Vehicle
Crew isolated supply and undertook repairs | 6 NEPEAN ROAD, BOLWARRA VIC 3305 |  |  |  |  | Unknown technical factor |  |  | 1 | A Powercor fault crew had completed opening a gas switch at the incident location as part of restoration of the 22kV Line. The Powercor Operations Controller then closed the line, at which time one of the supply transformers at the incident location faulted, causing debris and oil to fall to the a ground. A small grassfire occurred as a result (approx. 2m x 2m) on the road reserve. Protection operated. There were no reported injuries. | Transformer | 0 | 1 | 0 |  |  | Fault in supply transformer | Grassfire | 21/02/2016 7:20 | 1 | Localised: less than 10 sq.m | 915 | Roadway |  | 20160224PWA_01 | Infrastructure (network-based) | -38.2999 | 141.6027 | 1 | Powercor | Report | 1350 | 0.041054 | 22kV AC | Portland (Cashmore Airport) | 3305 | Bolwarra | AF Other
AusNet Services' fault crew found 2 fuses had operated at 808218 and opened a Gas Switch. The line was patrolled and the fault crew found an excavator under a stranded conductor. The operator when questioned denied any contact with the HV or that a flashover had occurred. When repairs were being made, grease was found on the HV conductors. The excavator and its operator had left the site. Excavator driver details not known. Height of overhead line where conductor failed was greater than 9.4m (limit of measuring stick) | 409 MOROKA ROAD, VALENCIA CREEK VIC 3860 | 2513125 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 220617. 11:30 Boisdale ACR opened auto (INCD-91730-r) on SEF prot. ACR successfully closed at 12:02. At 12:14 received report of ASF ex HV Fuses 808218. Fault truck dispatched. Fault crew found an excavator under a stranded HV conductor. | Conductor (bare) | 0 | 0 | 0 |  | mfa21 | Excavator contacted overhead HV conductors. Breach of No Go Zone Rules. | No Go Zone (contact) | 22/02/2016 12:14 |  |  | 922 | Agricultural |  | 20160224SPN_01 | Infrastructure (network-based) | -37.7959 | 147.0155 | 1 | AusNet Services Distribution | Report | 1358 | 0.0049803 | 22kV AC | Bairnsdale Airport | 3860 | Valencia Creek | Vehicle
A faults crew attended and removed the three phase overhead service and meter for safety of the demolition workers. A review of UE systems showed that we had not received any abolishment requests for 861A Nepean Highway Moorabbin. UE do however have a de-energisation request due to be completed on 26/02/2015. | 861A NEPEAN HIGHWAY, BENTLEIGH VIC 3204 | LIS No. 1804263 | Crane, excavator or other construction/farming equipment |  |  | Fault on customer installation |  |  | 2 | Caller reports that a demolition crew is knocking down the building and there was a loud bang at the switchboard and it was sparking and smoking and the power has gone out. The building is located in Nepean Highway between Patterson Road and Wolsley Street, Bentleigh. A City Circle Demolition and Excavation team were knocking down a section of building that contained live wiring. During this demolition work, live wiring was damaged that caused the protection to operate at the main switchboard. It was unknown if the service fuse cartridges had operated. No shocks or injuries were sustained. City Circle Demolition - 9489 7600 | Service conductor | 0 | 0 | 0 |  |  | Demolition work whilst the electrical installation remained alive. | Loss of supply | 24/02/2016 10:00 |  |  | 921 | Commercial |  | 20160224UTD_02 | Infrastructure (network-based) | -37.9265 | 145.0286 | 1 | United Energy Distribution | Report | 1356 | 0.016256 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Bentleigh | Other
Crew isolated supply and undertook repairs. | 29 PRINCES STREET, MILDURA VIC 3500 |  |  |  |  | Unknown technical factor |  | Phase to earth | 1 | A field crew attending an outage found that 22kV Cable Head Pole had faulted, resulting in fire damage to the pole and to the cabling on the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (concrete) | 2 | 2 | 2 |  |  | 22kV Cable Head failure causing fire. | Pole-top fire | 42614.2236 | 1 | Negligible: no ground fire | 930 | Roadway |  | 20160225PWA_03 | Infrastructure (network-based) | -34.192 | 142.1492 | 1 | Powercor | Report | 1369 | 0.020854 | 22kV AC | Mildura Airport | 3500 | Mildura | Connection
Crew isolated supply and undertook repairs | 1A MCLELLAN COURT, WYE RIVER VIC 3234 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred on a 22kV pole which burnt the top of the pole. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole top | 0 | 0 | 0 |  |  | Pole-top fire. | Pole-top fire | 42552.4375 | 1 | Negligible: no ground fire | 932 | Roadway |  | 20160225PWA_05 | Infrastructure (network-based) | -38.6333 | 143.891 | 1 | Powercor | Report | 1371 | 0.031551 | 22kV AC | Avalon Airport | 3234 | Wye River | Pole
Crew isolated supply and undertook repairs to conductors. | 1054 WILSON ROAD, TONGALA VIC 3621 |  |  | Bird |  |  |  |  | 1 | A customer reported a conductor down at the above location. On arrival the crew found that a HV conductor had broken (possibly due to bird/animal interference), falling to the ground and resulting in a ground fire (Approx. 1m x 1m) on the road reserve. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 24/01/2016 4:56 | 1 | Localised: less than 10 sq.m | 933 | Agricultural |  | 20160225PWA_06 | Infrastructure (network-based) | -36.2398 | 145.0138 | 1 | Powercor | Report | 1373 | 0.036713 | 22kV AC | Shepparton Airport | 3621 | Tongala | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the HV/LV pole was replaced under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 369 BAY ROAD, CHELTENHAM VIC 3192 | LIS No. 1823037 | Vehicle |  |  | HV injection |  |  | 1 | At 1654hrs on 24/02/2016, 11kV feeder CM 25 circuit breaker reclosed to lockout affecting 1415 customers. A large vehicle has struck a HV intermediate pole with a LV strain located outside 369 Bay Road, Cheltenham (LIS No. 1823037). It appeared the HV conductor had briefly contacted the LV below and the faults crew requested a LEI attend as a HVI was suspected to customers supplied from the south circuit of "Graham-Bay" substation. The LEI confirmed a high voltage injection occurred (CLA 1601) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Pole (wood) | 0 | 0 | 0 |  | CM 25 | A large vehicle has struck a HV intermediate pole with a LV strain. | HV injection;Loss of supply | 24/02/2016 16:54 |  |  | 926 | Roadway |  | 20160225UTD_01 | Infrastructure (network-based) | -37.9562 | 145.0432 | 1 | United Energy Distribution | Report | 1365 | 0.040098 | 11kV AC | Moorabbin Airport | 3192 | Cheltenham | Vehicle
Crew isolated supply and undertook repairs | 530 PHOINES ROAD, WANDO VALE VIC 3312 |  |  |  |  | Unknown technical factor |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 12.7kV SWER pole, which burnt the pole causing the conductors to fall to the ground in a ploughed paddock. There was no ground fire. Protection operated. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 24/02/2016 18:35 | 1 | Negligible: no ground fire | 937 | Agricultural |  | 20160226PWA_02 | Infrastructure (network-based) | -37.5341 | 141.4664 | 1 | Powercor | Report | 1378 | 0.012072 | 12.7kV AC (SWER) | Hamilton Airport | 3312 | Wando Vale | Pole
CEOT dispatched a fault crew to attend the incident, make safe, isolate and repair. Crew made site safe and replaced the 150 Amp 3 Phase fuse box at LIS 4503089. The DAO was informed of the incident. The fault crew removed the existing box and sleeved the cables through as another 160 Amp fuse box was located at the other end of the service. The fuse burnt out fuse box was found to be redundant and was not required. | 63 FORD STREET, BEECHWORTH VIC 3747 | 4503089 |  |  |  |  | Poor workmanship |  | 2 | IMS 220762. Per CFA report of a pole box on fire at cnr Camp St. A 150 Amp 3 Phase fuse box at pole LIS 4503089 caught fire due to a loose connection. | Connection box | 0 | 0 | 0 |  | myt7 | Burnt out pole fuse box due to a loose connection. | Other electricity related | 27/02/2016 12:23 | 1 | Negligible: no ground fire | 941 | Commercial |  | 20160229SPN_02 | Infrastructure (network-based) | -36.3597 | 146.6859 | 1 | AusNet Services Distribution | Report | 1384 | 0.0077847 | Low voltage AC (<1kV) | Wangaratta Aero | 3747 | Beechworth | Connection
Crew isolated supply and undertook repairs | 631 MIRAM SOUTH ROAD, KANIVA VIC 3419 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | An asset inspector reported a low wire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which caused the crossarm to break and the conductor to fall coming to rest approx. 1m from the ground. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Pole-top fire | 25/02/2016 7:46 | 1 | Negligible: no ground fire | 945 | Agricultural |  | 20160301PWA_02 | Infrastructure (network-based) | -36.4498 | 141.3656 | 1 | Powercor | Report | 3063 | 0.033706 | 22kV AC | Horsham Aerodrome | 3419 | Kaniva | Crossarm
Crew attended and secured site | 242 ST ALBANS ROAD, BREAKWATER VIC 3219 |  | Theft | [5 empty] | 2 | An employee reported a forced entry at the incident site. On arrival it was found that entry had been gained to the Zone Substation by unknown third parties by cutting a chain that secured a set of double gates. No items appeared to be missing. No items were reported stolen subsequent to this non-authorised entry. No additional damage or injury was reported. | Zone substation | 0 | 2 | 0 |  |  | Attempted theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42523.3958 |  |  | 957 | Industrial |  | 20160302PWA_05 | Infrastructure (network-based) | -38.1798 | 144.3813 | 1 | Powercor | Report | 1400 | 0.0020498 | Not applicable | Avalon Airport | 3219 | Breakwater | Other
Crew isolated supply and arranged repairs | 4 APOLLO PLACE, ARDEER VIC 3022 |  | Working too close to overhead lines | [5 empty] | 2 | Builder reported that a bobcat had contacted a service and it is now hanging low at the incident location. On arrival the crew found that a bobcat (Operated by Mark Durbin, Ph: 0417 011 065) had contacted a low voltage service cable with its raised bucket resulting in the service being dislodged at the pole end and pulled out of the FOLCB at the house end. There was no ground fire. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  |  | Bobcat contacted LV service cable | No Go Zone (contact) | 24/02/2016 9:33 |  |  | 966 | Residential |  | 20160303PWA_05 | Infrastructure (network-based) | -37.7911 | 144.7917 | 1 | Powercor | Report | 1409 | 0.032257 | Low voltage AC (<1kV) | Laverton Raaf | 3022 | Ardeer | Vehicle
Crew isolated supply and undertook repairs | 168 MIDAS ROAD, MINERS REST VIC 3352 |  | Working too close to underground cables | [5 empty] | 1 | A contractor reported that an excavator on their work site had hit an underground service cable at the incident location. On arrival the crew found that a contractor (Fulton Hogan, 26 Kennedys Dr, Delacombe, Contact: David, Ph.: 0429 014 813) was operating an excavator and contacted a LV underground service cable causing damage to the cable and conduit. There were no reported injuries or third party property damages. | Services cable | 0 | 0 | 0 |  |  | Excavator contacted UG cable | No Go Zone (contact) | 42372.6722 |  |  | 968 | Roadway |  | 20160303PWA_07 | Infrastructure (network-based) | -37.4616 | 143.8096 | 1 | Powercor | Report | 1411 | 0.036667 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Miners Rest | Dug up
Crew isolated supply and undertook repairs | 150 WILLIAMS ROAD, PRAHRAN VIC 3181 |  | Vehicle | [5 empty] | 2 | A customer reported that their service wire had been hit by truck, the hook pulled out and point of attachment hanging at the incident location. On arrival the crew found that an unknown vehicle had contacted a LV service cable causing damage to the customers POA. The crew were advised by a worker onsite that the incident took place approximately two weeks ago. No power outage was reported. There was no ground fire. There were no reported injuries. Following repairs the cable was measured at 5.1m at the kerb. | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted LV service cable | No Go Zone (contact) | 42372.6062 |  |  | 973 | Roadway |  | 20160303PWA_12 | Infrastructure (network-based) | -37.8494 | 145.0032 | 1 | CitiPower | Report | 1416 | 0.022222 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Prahran | Vehicle
The attending Powercor Fault Crew isolated the High Voltage SWER line and replaced the HV Polymeric Insulator with a Porcelain type insulator and re-energised the SWER line on completion. Subsequent Safe to Approach Test and Voltage Tests between an independent earth and various points on the Timber SWER Pole including the metal LIS Identification Plate, conductive Out Building materials and Perimeter Fences in the vicinity of the pole confirmed Zero Volts following replacement of the HV Insulator. The LEI also completed an NST Test at the Customerâ€™s Main Switchboard which confirmed a Pass result. The Installation was left ON supply. | 90 MANNA GUM DRIVE, CAPE OTWAY VIC 3233 |  |  |  |  | Electrical breakdown |  |  | 2 | Mr Michael Sanders (Contract Vegetation Inspector) was recording the Pole LIS number when his hand came in contact with the Name Plate on the wet SWER Pole while standing in wet grass. The prevailing weather conditions were wet and drizzling rain at the time the electric shock was received. The LEI completed a Safe to Approach Test with a â€œModiewarkâ€ and confirmed there was no indication of a voltage at or in the vicinity of the SWER Pole. The weather conditions were fine (not raining) and the pole was dry at the time of the investigation. Additional voltage tests between an independent earth and various points on the Timber SWER Pole including the metal LIS Identification Plate, conductive Out Building materials and Perimeter Fences in the vicinity of the pole also confirmed Zero Volts. A Polymeric HV Insulator supported the HV Conductor on the Intermediate SWER Pole which was replaced as a precautionary measure following signs of deterioration. | Pole (wood) | 0 | 0 | 0 |  |  | Deteriorated insulator | Minor shock | 19/02/2016 10:30 |  |  | 980 | Commercial |  | 20160303PWA_17 | Infrastructure (network-based) | -38.8347 | 143.5132 | 1 | Powercor | Report | 2918 | 0.0097766 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3233 | Cape Otway | Other
Crew undertook erpairs | LOT 12 REROCK DRIVE, DELACOMBE VIC 3356 |  | Vandalism;Terrorism | [5 empty] | 2 | A passer-by reported that copper was removed from a pole at the incident location. On arrival the crew found that about 2m of the HV and 2m of the LV earths had been cut and removed on a 22kV pole, There were no reported injuries. | Earth/earthing | 0 | 0 | 0 |  |  | Theft/Vandalism | Damage to network assets | 28/02/2016 14:20 |  |  | 982 | Roadway |  | 20160303PWA_19 | Infrastructure (network-based) | -37.5758 | 143.8192 | 1 | Powercor | Report | 3065 | 0.019961 | Earthing cable | Ballarat Aerodrome | 3356 | Delacombe | Other
Crew isolated supply | 7-11 SOUTHBANK BOULEVARD, SOUTHBANK VIC 3006 |  |  |  |  | Overheated connection |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found a LV underground service pit, filled with crushed rock and within the path of a loading area for a nearby construction site. The pit connectors within the pit had overheated resulting in a fire, which was contained to the connectors. There were no reported injuries or third party property damages. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection due to foreign materials in UG pit | Other electricity related | 25/02/2016 15:25 | 0 | Negligible: no ground fire | 984 | Roadway |  | 20160303PWA_21 | Infrastructure (network-based) | -37.8215 | 144.9629 | 1 | CitiPower | Report | 8007 | 0.030569 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | AF Other
Made safe | 105 CHAMPION ROAD, NEWPORT VIC 3015 |  |  | Heat;Cold |  | Leakage |  |  | 2 | Pole fire | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42463.2417 | 1 | Negligible: no ground fire | 991 | Residential |  | 20160304JEM_01 | Infrastructure (network-based) | -37.8485 | 144.8734 | 1 | Jemena | Report | 1437 | 0.014388 | 22kV AC | Laverton Raaf | 3015 | Newport | Pole
The inspector has sent a NGZ inspection report to the builder to install barricades from within the site to exclude access to within 3m of the cables. The builder has signed and returned the inspection report. The relocation of assets is planned for 4 April. | 15 YARRA STREET, RICHMOND VIC 3121 |  | Working too close to overhead lines | [5 empty] | 2 | Reason attending site - Permit To Work inspection Incident - Steel framework erected in breach VESI guidelines Asset type - LV Overhead, Clearance to asset - 1000mm from steel frame to bare open wire LV conductors Builder - Rob Thomas Avalon Builders ph 0418372141 rothomoh@bigpond.com Owner - unknown Developer - unknown | Conductor (bare) | 0 | 0 | 0 |  |  | No Go Zone infringement | No Go Zone (no contact) | 42554 |  |  | 1031 | Roadway |  | 20160310PWA_01 | Infrastructure (network-based) | -37.8319 | 144.998 | 1 | CitiPower | Report | 8014 | 0.014182 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Crew isolated supply and undertook repairs | 551 MALAYA ROAD, ROBINVALE IRRIGATION DISTRICT SECTION C VIC 3549 |  |  |  |  | Overheated connection |  |  | 2 | A customer reported black box on pole has melted and started small grass fire. On arrival the crew found that a LV 400 amp Krone fused switch dis-connector had melted dropping hot substance, resulting in a ground fire (approx. 2 sqm) on the road reserve. There were no reported injuries or third party property damages. | Disconnector/isolator | 0 | 0 | 0 |  |  | Overheated Krone Box | Grassfire | 42616.7965 | 1 | Negligible: no ground fire | 1036 | Roadway |  | 20160310PWA_02 | Infrastructure (network-based) | -34.6302 | 142.7311 | 1 | Powercor | Report | 3098 | 0.033321 | Low voltage AC (<1kV) | Mildura Airport | 3549 | Robinvale Irrigation District Section C | Fuse
Crew isolated supply and undertook repairs | 4 PEKIN ROAD, MARYBOROUGH VIC 3465 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | CFA reported a fire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole, with roadside end of cross arm burning off, resulting in a ground fire (approx. 1 sqm) on road reserve. There were no reported injuries. No HV injection, no third party property damage. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross arm fire on 22kV power line | Grassfire | 42616.8736 | 1 | Negligible: no ground fire | 1040 | Roadway |  | 20160310PWA_03 | Infrastructure (network-based) | -37.0407 | 143.7286 | 1 | Powercor | Report | 3097 | 0.0068669 | 22kV AC | Ballarat Aerodrome | 3465 | Maryborough | Crossarm
Crew isolated supply and undertook repairs | 66 SUTTON ROAD, MARYBOROUGH VIC 3465 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A Field crew reported a fire at the incident location. The crew found that a cross arm fire had occurred on a 22kV pole which partially burnt the cross arm only. No Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross arm fire on 22kV line | Pole-top fire | 42646.1625 | 1 | Negligible: no ground fire | 1041 | Roadway |  | 20160310PWA_04 | Infrastructure (network-based) | -37.0489 | 143.7529 | 1 | Powercor | Report | 3105 | 0.01794 | 22kV AC | Ballarat Aerodrome | 3465 | Maryborough | Crossarm
A LEI and faults truck attended and immediately noticed the neutral screened overhead service had been damaged as a result of rubbing on a tree in the customers property. The LEI tested between the shower tap and an independent earth and measured 26v. The faults crew replaced the copper neutral screen overhead service with a XLPE type and the installation was re-tested that confirmed the fault had been rectified. The occupier was concerned about the electric shocks being received from the taps and chose to stay in a motel overnight that was arranged by the Real Estate Agent. | 414 WAVERLEY ROAD, MALVERN EAST VIC 3145 |  |  | Alive |  | Neutral fault |  |  | 2 | The occupier received slight electric shocks from the shower taps and contacted a REC to investigate the cause. The REC also believed that a plumber also received shocks from the water mains. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Minor shock | 42372.8333 |  |  | 1032 | Residential |  | 20160310UTD_01 | Infrastructure (network-based) | -37.8784 | 145.0654 | 1 | United Energy Distribution | Report | 1487 | 0.026512 | Low voltage AC (<1kV) | Moorabbin Airport | 3145 | Malvern East | Trees
A LEI attended and confirmed that a HVI did not occur to premises supplied from "Huisman-King" substation. A street light had also caught on fire at pole No. LIS 1106570 and the lantern was disconnected by the faults crew and a new order created for ACE to attend and to replace the damaged lantern. The neutral conductor was tied back onto the insulator and the HV feeders were patrolled and the concrete pole checked once again in daylight to ensure there was no further damage. Telstra workers were on site completing repairs to the fire damaged Telstra pit. | 259 MARINE PARADE, HASTINGS VIC 3915 | LIS No. 1106570 |  | Animal |  | Neutral fault |  |  | 1 | At 2324hrs on 01/03/2016, 66kV feeder TBTS-HGS No. 2 and 22kV feeder HGS22 circuit breakers successfully reclosed and held. The fire authority advised there was a grass fire at the base of a pole in Marine Parade near the corner of Robertson Street which is now out. According to a local resident, possums were fighting on the concrete HV/LV pole and there was a loud bang that caused the HV feeder protection to auto reclose and hold. It was uncertain what the possum made contact with but there were burn marks on the pole in the vicinity of the neutral conductor that had dislodged from the insulator. The possum caught on fire and fell into the dry grass below that caused a small grass fire to occur that was extinguished by the CFA. A Telstra pit near the base of the concrete pole sustained fire damage and the faults crew suspected that a high voltage injection may have occurred to customers supplied from "Huisman-King" substation and a LEI was dispatched to investigate. | Pole (concrete) | 0 | 0 | 0 |  | 66kV feeder TBTS-HGS No. 2 and 22kV feeder HGS 22 | Animal Incident | Grassfire | 42372.975 | 1 | Localised: less than 10 sq.m | 1034 | Roadway |  | 20160310UTD_02 | Infrastructure (network-based) | -38.2877 | 145.1896 | 1 | United Energy Distribution | Report | 1489 | 0.031994 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3915 | Hastings | Animal
The faults crew attended and assisted the LEI with the inspection of properties in the area. The meter at number 16 Bellavista Road had lost its display and was replaced. | 16 BELLA VISTA ROAD, GLEN IRIS VIC 3146 |  |  | Lightning |  | HV injection;Fault on customer installation |  |  | 2 | Customer contacted the United Energy faults and emergencies call centre advising they have a part supply failure and the switchboard is blackened and burnt. During stormy unsettled conditions, it appeared that lightning struck two properties at 16 and 20 Bellavista Road, Glen Iris that caused damage to customers switchboards and electrical appliances. A LEI attended and checked for any further damage to customers supplied from "Bellavista-High" substation but there were only the two properties affected from the high voltage injection (BWD 1602). | No failed asset | 0 | 0 | 0 |  | EM 08 | Lightning strike | HV injection | 42493.4181 |  |  | 1043 | Residential |  | 20160311UTD_01 | Infrastructure (network-based) | -37.8608 | 145.072 | 1 | United Energy Distribution | Report | 1499 | 0.0047558 | Not applicable | Moorabbin Airport | 3146 | Glen Iris | Lightning
Crew isolated supply and undertook repairs | 535 BOUNDARY ROAD, CHARLEMONT VIC 3217 |  |  | Fallen |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival the Powercor crew found that a tree branch fell on to 22kV conductors resulting in a small grass fire (100m2). Protection operated. There were no reported injuries or other damage | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 15/03/2016 14:06 | 1 | Negligible: no ground fire | 1055 | Roadway |  | 20160316PWA_01 | Infrastructure (network-based) | -38.2219 | 144.3602 | 1 | Powercor | Report | 3108 | 0.037619 | 22kV AC | Avalon Airport | 3217 | Charlemont | Trees
Crew isolated supply and undertook repairs. | 560 ECHUCA ROAD, MOOROOPNA NORTH VIC 3629 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Crew reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 66kV pole which burnt the cross arm only. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross arm fire on 66kV pole | Pole-top fire | 16/03/2016 11:29 | 1 | Negligible: no ground fire | 1056 | Roadway |  | 20160316PWA_02 | Infrastructure (network-based) | -36.3491 | 145.3366 | 1 | Powercor | Report | 3109 | 0.027355 | 66kV AC | Shepparton Airport | 3629 | Mooroopna North | Crossarm
CEOT dispatched a fault crew to attend the site and make safe. DAO was contacted for the fire report. A small fire of approximate size 10m x 30m was observed on the side of the roadway. | 110 FORREST DRIVE, NYORA VIC 3987 |  |  | Fallen | [5 empty] | IMS 221029. CFA advised that a tree had fallen on powerlines and there was a small grass fire in the area. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 15/03/2016 15:40 | 1 | Small: 10 - 1000 sq.m | 1064 |  |  | 20160317SPN_01 | Infrastructure (network-based) | -38.3024 | 145.657 | 1 | AusNet Services Distribution | Report | 1526 | 0.0051597 | 22kV AC | Moorabbin Airport | 3987 | Nyora | Trees
Dispatched fault crew. | UNIT 1 69 UNION STREET, KILMORE VIC 3764 |  |  | Within clearances | [5 empty] | Customer tree branch has rubbed through service line. Fire tab created in iMS. | Services cable | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 16/03/2016 11:17 | 1 | Localised: less than 10 sq.m | 1065 |  |  | 20160317SPN_02 | Infrastructure (network-based) | -37.2895 | 144.9562 | 1 | AusNet Services Distribution | Report | 1528 | 0.012618 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3764 | Kilmore | Trees
CEOT dispatched a fault crew. Supply stayed on and investigation requested. | 253 EDGARS ROAD, LALOR VIC 3075 |  |  | Bird | [5 empty] | Crow on concrete pole caught fire and fell to the ground. A small fire was observed at the site. The incident is being investigated. | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 16/03/2016 17:10 | 1 | Localised: less than 10 sq.m | 1066 |  |  | 20160317SPN_03 | Infrastructure (network-based) | -37.6721 | 145.0016 | 1 | AusNet Services Distribution | Report | 1530 | 0.019802 | 22kV AC | Essendon Airport | 3075 | Lalor | Animal
Fires extinguished by customer. CEOT dispatched a fault crew to make safe and investigate. | 2 SHILO COURT, THOMASTOWN VIC 3074 |  |  | Within clearances | [5 empty] | IMS 221076. Tree hit service cable which caused LV conductors to clash. 2 x small fires on nature strip near this site were observed. | Conductor (bare);Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 16/03/2016 15:30 | 1 | Localised: less than 10 sq.m | 1067 |  |  | 20160317SPN_04 | Infrastructure (network-based) | -37.6849 | 144.9946 | 1 | AusNet Services Distribution | Report | 2999 | 0.024325 | Low voltage AC (<1kV) | Essendon Airport | 3074 | Thomastown | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was replaced under Access Authority conditions. A construction crew replaced a bay of damaged HV conductors and repaired electrical infrastructure on pole No. LIS 1103671. Traffic control was required due to the high volume of traffic in the area at the time of the fault. | 337 RACECOURSE ROAD, MORNINGTON VIC 3931 | LIS No. 1103671 |  | Wind;Alive;Fallen |  | Conductor clashing |  |  | 1 | At 1535hrs on 15/03/2016, 22kV feeder MTN 21 circuit breaker reclosed to lockout affecting 2354 customers. During windy conditions, a large private cypress tree belonging to the Mornington Racecourse, located on the corner of Racecourse and Watt Roads, fell over the HV conductors entering the property causing them to fall to the ground and a grass fire to start that was quickly extinguished. No HV injection or major damage was sustained. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | MTN 21 | Vegetation: Trees Incident | Grassfire | 15/03/2016 15:35 | 1 | Localised: less than 10 sq.m | 1060 | Public space |  | 20160317UTD_02 | Infrastructure (network-based) | -38.2353 | 145.0677 | 1 | United Energy Distribution | Report | 1521 | 0.0018345 | 22kV AC | Moorabbin Airport | 3931 | Mornington | Trees
Made safe | 10 BUCKLEY ROAD, DIGGERS REST VIC 3427 |  |  | Bird |  |  |  |  | 1 | Grass fire caused by a magpie making contacting between earth and white phase conductor | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 21/03/2016 10:56 | 1 | Small: 10 - 1000 sq.m | 1074 | Agricultural |  | 20160321JEM_03 | Infrastructure (network-based) | -37.6165 | 144.7209 | 1 | Jemena | Report | 1539 | 0.040543 | 22kV AC | Melbourne Airport | 3427 | Diggers Rest | Animal
The matter to be discussed with ESV | 1 GRAHAM AVENUE, BUNDALONG VIC 3730 |  | Building too close or within the No Go Zone | [5 empty] | 2 | A Powercor Crew reported a customer interaction with Powercor assets at the incident location. On arrival the crew found that a customer, from the property on the corner of Goughs Lane and Graham Ave (11 Goughs Lane), has used temporary props to lift a Low Voltage service wire to the neighbouring property (1 Graham Ave). The props are in place to lift the service over a newly constructed car port. No request was made for a permit or to reconfigure the service. There were no reported injuries or third party property damages. | Conductor (insulated) | 0 | 0 | 0 |  |  | The owner of a property on the corner of Goughs Lane and Graham Ave (11 Goughs Lane), has used temporary props to lift a service wire to the neighbouring property (1 Graham Ave). | No Go Zone (contact) | 17/03/2016 14:47 |  |  | 1071 | Roadway |  | 20160321PWA_02 | Infrastructure (network-based) | -36.0268 | 146.1603 | 2 | Powercor | Report | 3111 | 0.032019 | Low voltage AC (<1kV) | Wangaratta Aero | 3730 | Bundalong | Other
Crew isolated supply and undertook repairs | 42 CALDER HIGHWAY, NULLAWIL VIC 3529 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  |  | Vic Fire reported a pole and grass fire at the incident location. On arrival the crew found signs of burning on the pole and a grass fire of approximately 2 metres square. There were no injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 18/03/2016 14:41 | 1 | Negligible: no ground fire | 1072 | Roadway |  | 20160321PWA_03 | Infrastructure (network-based) | -35.8515 | 143.1759 | 1 | Powercor | Report | 3115 | 0.011718 | 22kV AC | Swan Hill Aerodrome | 3529 | Nullawil | Pole
CEOT dispatched fault crew to make safe, isolate and repair. Area was made safe. Water and gas was shut down. Emergency services attended. | 240 WOORI YALLOCK ROAD, COCKATOO VIC 3781 |  | Vehicle | [6 empty] | IMS 221132. Truck hit HV/LV Pole LIS# 420422 registration # ZLU788. Pole broken at base, wires on the ground, burst water and gas pipes. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Vehicle collided with HV/LV pole. | Damage to network assets | 18/03/2016 14:22 |  |  | 1075 |  |  | 20160321SPN_01 | Infrastructure (network-based) | -37.9166 | 145.5013 | 1 | AusNet Services Distribution | Report | 1541 | 0.020134 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3781 | Cockatoo | Vehicle
Faults crew and a LEI were dispatched. Initial NST test performed which failed on 6 premises. Voltage from independent earth to shower tap/roller door was measured at 20-40 Volts. Neutral Impedance was measured at 4 Ohms. Voltage was measured at 264-280.5 Volts. Drop of 30 Volts was observed when the HWS boost was engaged. The cause was found to be a faulty neutral connection on pole 2805927. Repairs were made to the neutral connection (new double split-bolt connection onto bridge). After repairs were carried out the test results on all 6 residences passed - NST tests, independent earth to shower and roller door voltages were measured to be 0.7 Volt. Customer's REC (Shaun tel. 0409 539150) also bonded the metal water pipes to the earthing system. | 26 STRADBROKE AVENUE, COWES VIC 3922 | 2805927 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 220668. CEOT received a call from a customer that they had received tingles from a shower tap and a roller door. No one injured, no other damage. Scotch College School Camp (26 Stradbroke Avenue) Year 7 students were showering off using the outdoor showers after sailing when they received a tingle off the shower tap. They also received tingles off the Boat House roller door. Margret Evetts of 30 Stradbroke Avenue also received slight tingles off her back tap while washing her feet off after kayaking. The tingles were caused by a faulty neutral connection at the pole end (single D line tap, split-bolt connection). | Connector/termination | 0 | 0 | 0 |  | phi13 | Faulty neutral connection at spilt-bolt clamp at pole end. | Minor shock | 24/02/2016 11:12 |  |  | 1095 | Residential |  | 20160322SPN_05 | Infrastructure (network-based) | -38.4496 | 145.2534 | 1 | AusNet Services Distribution | Report | 1563 | 0.0043623 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Cowes | Connection
The attending Powercor Fault Crew checked all connections from the Customerâ€™s POA to the terminals of the Transformer and checked various other O/H Services on the West LV Circuit of the McLennan / McLachlan Sub Station. The East LV Circuit of the McLennan / McLachlan Sub Station was subsequently paralleled to the Nelson / Diana Sub Station, wherein the Voltage Rise on the MEN and Main Earthing system at 1 McLennan Street reduced to less than 1 Volt when the McLennan / McLachlan East Circuit Bus Fuses were opened. The Fault Crew returned to 1 McLennan Street and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including between the MEN at the Main Control Switchboard, metallic water pipe system, distribution assets and between the points of contact confirmed 0.75 Volts under normal load conditions. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The installation was left ON supply. The Report Room was advised that further investigation was required by the Supply Quality Group to eliminate the source of the abnormal Network Supply condition. The Owner was also advised to consider the installation of an Equipotential Earth Bonding Conductor to the Reinforcing steel in the Concrete Slab Floor to help reduce the risk of a Potential Difference between the Installation Earthing System and the Concrete Floor. | 1 MCLENNAN STREET, APOLLO BAY VIC 3233 |  |  |  |  | Corrosion |  |  | 2 | 3 separate reports consolidated Ms Abbey Fisher was washing her clothes in the Communal Laundry Sink when she received an electric shock as she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the damp concrete floor. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, installation MEN, main earthing conductor, water pipe earth bond conductor and metallic water pipes, identified a Potential Difference of 17.3 Volts. The rise in voltage on the installation MEN and Main Earthing system is suspected of originating from an external source supplied by the LV Network Assets requiring further investigation. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes resulting in a voltage rise of 17.3 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | High resistance connection in distribution LV neutral | Minor shock | 18/03/2016 16:30 |  |  | 1113 | Residential |  | 20160329PWA_09 | Infrastructure (network-based) | -38.7566 | 143.6635 | 1 | Powercor | Report | 5385 | 0.010726 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Connection
A LEI attended and checked the installation and believed a problem existed in the overhead reticulation and contacted a faults crew to check the connections at the pole end. The LEI tested the installation and measured 30v between the water piping system and an independent earth. A faults crew promptly attended and checked the connections at the pole end and identified a damaged neutral connection at pole No. LIS 1315617. The faults crew replaced the single phase grey twisted overhead service with a XLPE service and the LEI re-tested the installation and confirmed the fault had been rectified. | 81 JETTY ROAD, ROSEBUD VIC 3939 | LIS No. 1315617 |  |  |  | Corrosion |  | Phase to earth | 2 | Caller advised that lights are dimming under load and they received a slight electric tingle but are okay. The occupier contacted the United Energy faults and emergencies after a slight electric shock was received from the kettle and has observed the noticeable dimming of lights. | Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | Corroded neutral connection at pole end. The property is located in close proximity to Port Phillip BAy. | Minor shock | 19/03/2016 8:30 |  |  | 1107 | Residential |  | 20160329UTD_01 | Infrastructure (network-based) | -38.3625 | 144.9091 | 1 | United Energy Distribution | Report | 1578 | 0.022263 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the HV/LV pole was replaced under Access Authority conditions prior to the supply being restored. | 561 NEPEAN HIGHWAY, BONBEACH VIC 3196 | LIS No. 3302939 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Pole has snapped per CFA possibly due to a pole fire. During light drizzly rain, a pole fire occurred at a HV/LV intermediate pole (LIS No. 3302939) located outside 561 Nepean Highway, Chelsea. The pole was damaged and required replacement. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | CRM 22 | Pole fire during light drizzly rain. The pole is located in close proximity to Port Phillip Bay. | Pole-top fire;Loss of supply | 25/03/2016 13:34 | 1 | Negligible: no ground fire | 1110 | Roadway |  | 20160329UTD_02 | Infrastructure (network-based) | -38.0652 | 145.1196 | 1 | United Energy Distribution | Report | 1581 | 0.011579 | 22kV AC | Moorabbin Airport | 3196 | Bonbeach | Pole
Crew isolated supply and undertook repairs. | 326 RODBOROUGH ROAD, JOYCES CREEK VIC 3364 |  |  | Bird |  |  |  |  | 1 | Auto Reclose Target on CMN-MRO 66KV Line required a ground patrol at the incident location. Crew found a Swan had made contact with the 66KV Feeder causing a ground fire of approximately 75x10 metres. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 26/03/2016 9:58 | 1 | Small: 10 - 1000 sq.m | 1122 | Roadway |  | 20160330PWA_09 | Infrastructure (network-based) | -37.1032 | 143.9781 | 1 | Powercor | Report | 1599 | 0.017706 | 66kV AC | Ballarat Aerodrome | 3364 | Joyces Creek | Animal
Construction crew repaired LV conductors. AusNet Services' LEI confirmed damage to customers installation. | 190 HARVIE ROAD, PAKENHAM UPPER VIC 3810 |  |  | Fallen | [5 empty] | IMS 221246. LV conductor down - HV fuse operated. Fault crew attended to make safe. AusNet Services' LEI called to investigate a possible HVI. | Conductor (bare) | 0 | 0 | 2 |  |  | CEOT didn't specify a cause. The incident is currently under investigation. | HV injection | 27/03/2016 12:33 |  |  | 1123 |  |  | 20160330SPN_01 | Infrastructure (network-based) | -38.0085 | 145.5387 | 1 | AusNet Services Distribution | Report | 1602 | 0.018508 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3810 | Pakenham Upper | Conductor
Crew isolated supply and undertook repairs. | 164 VERE STREET, ABBOTSFORD VIC 3067 |  |  |  |  | Corrosion |  |  | 1 | VICFIRE reported that there was a wire sparking and it had come down onto a tree at the incident location. On arrival the crew found a low voltage service cable that had come down onto a tree. There was no personal injuries or any third property damages. | Conductor (insulated) | 0 | 0 | 0 |  |  | Low Voltage service cable failed. | Loss of supply | 31/03/2016 16:05 |  |  | 1130 | Residential |  | 20160404PWA_01 | Infrastructure (network-based) | -37.8026 | 144.9954 | 1 | CitiPower | Report | 7989 | 0.0069433 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | OH Cable
Crew isolated supply and undertook repairs | 84 CENTRAL AVENUE, ALTONA MEADOWS VIC 3028 | 202556 |  |  |  | Leakage |  |  |  | Fault crew attending an outage found a pole fire at the incident location. The crew also found that the cross arm and pole of LIS 202556 partly bunt through around the king bolt There was no ground fire. There were no reported injuries or third party damage. | Crossarm (wood) | 0 | 0 | 0 |  | LV003 | Crossarm fire | Pole-top fire | 42525.2139 | 1 | Negligible: no ground fire | 1173 | Roadway |  | 20160412PWA_04 | Infrastructure (network-based) | -37.8704 | 144.7699 | 1 | Powercor | Report | 2944 | 0.007316 | 22kV AC | Laverton Raaf | 3028 | Altona Meadows | Crossarm
On arrival crews isolated supply and carried out repairs | 951 MOUNT COTTRELL ROAD, ROCKBANK VIC 3335 | 111482 | Vandalism;Theft | [6 empty] | V/line reported that a boom gates are not working at the incident location. Upon arrival, the Powercor crew found that the UG service cable had been cut away from the pole up to the pit. The conduit on the pole also damaged. Some of cables including HV earthing had been stolen. There were no reported injuries or fire. This was the power supply to boom gate control mechanism. Thieves cut the live cable and also HV earthing cable. Power cables, UG pit and other asset vandalised. An axe left at the incident location. | Services cable | 0 | 0 | 0 |  | MLN011 | vandalism, copper theft | Loss of supply;More than $50k damage | 42525.4257 |  |  | 1176 | Roadway |  | 20160412PWA_07 | Infrastructure (network-based) | -37.7177 | 144.6185 | 1 | Powercor | Report | 1668 | 0.011965 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated substation and carried out repairs | 134 WHITES ROAD, CARDIGAN VIC 3352 | 45531 | Theft | [6 empty] | Electrix reported that the Low Voltage earth cable on the Substation pole at the incident location had been stolen. Upon arrival the crew found that approx. 3m of the LV earth cable had been stolen. There were no reported injuries, ground fire or third party damage. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Theft of earth cables | More than $50k damage | 42586.5 |  |  | 2185 | Roadway |  | 20160413PWA_09 | Infrastructure (network-based) | -37.5323 | 143.7402 | 1 | Powercor | Report | 2677 | 0.0028194 | Earthing cable | Ballarat Aerodrome | 3352 | Cardigan | Other
CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 6 Volts no load to 100 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 6 Volt no load to 100 Volts maximum load. CTA/LEI performed NST test at installation main switchboard with a fail result recorded. Service crew performed NST test at the POA with a fail result recorded. Following visual investigation the damaged conductor across the road was replaced. Crew performed NST test of new conductor across the road with a pass result recorded. Crew performed NST test at the POA with a pass result recorded. CTA/LEI performed NST test at installation MSB with pass result recorded. CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 2 Volts no load to 4 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 2 Volts no load to 4 Volts maximum load. A final NST test was carried out by the CTA / LEI with a pass result again recorded. | 24 ALICE ROAD, AIREYS INLET VIC 3231 |  |  | Bird |  | Corrosion |  | Phase to earth |  | Customer was standing at the bathroom sink and received a shock to his hands when he came in contact with the taps and running water whilst standing barefooted on the tiled floor. | Service conductor | 0 | 0 | 0 |  |  | Insulation on the grey twisted 4 wire conductor across the road that supplies the service pole which services this address, 24 Alice Rd, was damaged. Suggest damage caused by a Cockatoo. An active and the neutral conductor were exposed to the elements, causing corrosion and breakdown of the aluminium conductors. | Minor shock | 42373.8646 |  |  | 2195 | Residential |  | 20160414PWA_08 | Infrastructure (network-based) | -38.459 | 144.1096 | 1 | Powercor | Report | 2688 | 0.037359 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Aireys Inlet | OH Cable
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral conductor at the pole end. | 26 JAMES STREET, ST ALBANS VIC 3021 |  |  |  |  | Corrosion |  | Phase to earth |  | Customer received an electric shock when she made simultaneous contact between the metallic taps with one hand and the general mass of earth with wet feet whilst watering the garden | Service conductor | 0 | 0 | 0 |  |  | Corroded neutral conductor at the pole end | Minor shock | 42373.9792 |  |  | 2196 | Residential |  | 20160414PWA_09 | Infrastructure (network-based) | -37.7398 | 144.7911 | 1 | Powercor | Report | 2689 | 0.0036806 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | OH Cable
On arrival crew made site safe and carried out repairs | 14 WIMMERA COURT, WERRIBEE VIC 3030 | 206545 | Vehicle | [5 empty] | 2 | MFB reports truck has brought down wires, lying on road & sparking outside No.1 Wimmera Court Werribee. On arrival the crew found that a truck has hit the Optus Service Cable running from LIS-206546 to House No. 14 Wimmera Court, Werribee, this has resulted in the Optus Service Cable flicking up into the LV Bare Mains in the span Opp. No. 14, Splash marks observed on the red phase & neutral conductors. No Protection operated. There were no reported injuries, no shocks, no HVI and no third party damage. | Conductor (bare) | 0 | 0 | 0 |  | WBE012 | Truck hitting Optus cable | Loss of supply;Damage to network assets | 42647.8174 |  |  | 2199 | Roadway |  | 20160415PWA_02 | Infrastructure (network-based) | -37.8846 | 144.6559 | 1 | Powercor | Report | 8056 | 0.036139 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
Repairs completed | 97 HOPETOUN PARK ROAD, HOPETOUN PARK VIC 3340 | 776693 | Theft | [5 empty] | 2 | An asset inspector reported that an earthing cable on the sub pole at incident location has been cut away. Upon arrival, the Powercor crew found that a part of earthing cable had been stolen from the pole. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | BMH006 | Theft | Loss of supply | 13/04/2016 8:36 |  |  | 2202 | Roadway |  | 20160415PWA_05 | Infrastructure (network-based) | -37.6857 | 144.5024 | 1 | Powercor | Report | 2702 | 0.015051 | Earthing cable | Laverton Raaf | 3340 | Hopetoun Park | Other
Repairs completed | 206 HOPETOUN PARK ROAD, HOPETOUN PARK VIC 3340 | 103179 | Theft | [5 empty] | 2 | A contractor reported that a wooden cable covering and the earthing cable on the sub pole at incident location has been cut away. Upon arrival, the Powercor crew found that the earthing cable had been stolen from the sub pole and some damage done to the its wooden cover. The repairs completed. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | BMH006 | Theft | Loss of supply | 42708.5097 |  |  | 2203 | Roadway |  | 20160415PWA_06 | Infrastructure (network-based) | -37.6957 | 144.5041 | 1 | Powercor | Report | 2703 | 0.022815 | Earthing cable | Laverton Raaf | 3340 | Hopetoun Park | Other
Repairs completed | WEIGHBRIDGE ROAD, CARDIGAN VIC 3352 | 9728 | Theft | [5 empty] | 2 | An contract employee reported missing earth cables. On arrival the crew the low voltage earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Theft | Loss of supply | 13/04/2016 9:17 |  |  | 2205 | Roadway |  | 20160415PWA_07 | Infrastructure (network-based) | -37.5101 | 143.7066 | 1 | Powercor | Report | 2705 | 0.008544 | Earthing cable | Ballarat Aerodrome | 3352 | Cardigan | Other
Repairs completed | 295 WHITES ROAD, CARDIGAN VIC 3352 | 37865 | Theft | [5 empty] | 2 | An contract employee reported missing earth cables. On arrival the crew found that the low voltage earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Theft | Loss of supply | 13/04/2016 9:21 |  |  | 2206 | Roadway |  | 20160415PWA_08 | Infrastructure (network-based) | -37.5506 | 143.7368 | 1 | Powercor | Report | 2706 | 0.010957 | Earthing cable | Ballarat Aerodrome | 3352 | Cardigan | Other
Repairs completed | OLD WESTERN HIGHWAY, LONG FOREST VIC 3340 | 105598 | Copper theft | [5 empty] | 2 | An asset inspector reported an earthing cable theft on sub pole at the incident location. Upon arrival, the Powercor crew found that earthing cables had been stolen from the pole. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | BMH006 | Theft | Loss of supply | 14/04/2016 12:32 |  |  | 2208 | Roadway |  | 20160415PWA_10 | Infrastructure (network-based) | -37.6851 | 144.5144 | 1 | Powercor | Report | 8032 | 0.021999 | Earthing cable | Laverton Raaf | 3340 | Long Forest | Other
On arrival crews made site safe. Section of cable replaced. | 72 HARCOURT ROAD, ALTONA VIC 3018 | 994551 |  |  |  | Electrical breakdown |  |  | 1 | A Powercor fault crew attending an outage found that a HV ABC cable lying on the ground at the incident location resulting small (5m*5m) grass fire. The cable fell onto a fence which has been slightly damaged There were no reported injuries | Conductor (ABC) | 0 | 0 | 0 |  | LVN022 | Electrical discharge to earthed catenary conductor | Grassfire | 20/04/2016 8:49 | 1 | Small: 10 - 1000 sq.m | 2228 | Roadway |  | 20160420PWA_06 | Infrastructure (network-based) | -37.8507 | 144.7814 | 1 | Powercor | Report | 2838 | 0.0093194 | 22kV AC | Laverton Raaf | 3018 | Altona | OH Cable
Fault crew isolated the underground fault and made safe. An Electrical Access Permit (EAP) and a Sanction For Testing (SFT) was issued. Rectification was a HV transition joint to a HV cable head. 15 metres of XLPE 185 sq.mm was installed. The cable was tested by the underground crew and it was declared fit for service. | 46 ELDER STREET, WATSONIA VIC 3087 | 901958 | Working too close to underground cables |  |  |  |  | Phase to phase | 1 | IMS 221579. A private contractor damaged a HV underground feeder cable whilst performing excavation work. The contractor's details were not provided. The Feeder protection operated. No third party details were provided. | Cable | 0 | 0 | 0 |  | wt8 | No Go Zone Rules breach. | No Go Zone (contact) | 20/04/2016 11:28 |  |  | 2244 | Residential |  | 20160426SPN_02 | Infrastructure (network-based) | -37.7133 | 145.0879 | 1 | AusNet Services Distribution | Report | 2793 | 0.019337 | 22kV AC | Essendon Airport | 3087 | Watsonia | Dug up
On arrival crew made site safe and commenced repairs | 125 BO PEEP ROAD, BURRUMBEET VIC 3352 | 9772 | Theft | [5 empty] | 2 | A contract employee reported missing earth cables at incident location. On arrival the crew found that the earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Earth cable theft | Less than $50k damage | 15/04/2016 9:12 |  |  | 2254 | Roadway |  | 20160427PWA_06 | Infrastructure (network-based) | -37.5083 | 143.677 | 1 | Powercor | Report | 2804 | 0.027478 | Earthing cable | Ballarat Aerodrome | 3352 | Burrumbeet | Other
On arrival crew made site safe and commenced repairs | 86 BO PEEP ROAD, BURRUMBEET VIC 3352 | 9769 | Theft | [5 empty] | 2 | A contract employee reported missing earth cables at incident location. On arrival the crew found that all the earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Outdoor | 0 | 0 | 0 |  | BAS011 | Earth cable theft | Less than $50k damage | 15/04/2016 9:23 |  |  | 2256 |  |  | 20160427PWA_08 | Infrastructure (network-based) | -37.5046 | 143.6774 | 1 | Powercor | Report | 2806 | 0.034458 | Earthing cable | Ballarat Aerodrome | 3352 | Burrumbeet | Other
On arrival crew made site safe and commenced repairs | THE PLAITERS POLE, 601 BALLARAT-CARNGHAM ROAD, BUNKERS HILL VIC 3352 | 8402 | Theft | [5 empty] | 2 | A contract employee reported missing earth cables at incident location. On arrival the crew found that all the earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Pole mounted | 0 | 0 | 0 |  | BAS011 | Earth cable theft | Less than $50k damage | 15/04/2016 10:07 |  |  | 2257 | Roadway |  | 20160427PWA_09 | Infrastructure (network-based) | -37.5621 | 143.7428 | 1 | Powercor | Report | 2807 | 0.038549 | Earthing cable | Ballarat Aerodrome | 3352 | Bunkers Hill | Other
On arrival crew made site safe and commenced repairs | 27 SHARPES ROAD, MINERS REST VIC 3352 | 6337 | Theft | [5 empty] | 2 | An contract employee reported missing earth cables at incident location. On arrival the crew found that at both sites the high and low voltage earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper theft | More than $50k damage | 27/04/2016 8:45 |  |  | 2267 | Roadway |  | 20160429PWA_01 | Infrastructure (network-based) | -37.4822 | 143.807 | 1 | Powercor | Report | 2822 | 0.038267 | Earthing cable | Ballarat Aerodrome | 3352 | Miners Rest | Other
On arrival crew made site safe and commenced repairs | PIVOT AGRICULTURE, 44 OLD MIDLAND HIGHWAY, MOUNT ROWAN VIC 3352 | 4896 | Theft | [5 empty] | 2 | An contract employee reported missing earth cables at incident location. On arrival the crew found that at both sites the high and low voltage earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper theft | More than $50k damage | 27/04/2016 13:01 |  |  | 2268 | Roadway |  | 20160429PWA_02 | Infrastructure (network-based) | -37.517 | 143.8472 | 1 | Powercor | Report | 2823 | 0.040512 | Earthing cable | Ballarat Aerodrome | 3352 | Mount Rowan | Other
HV conductor was put back up in the air | 1 MAY STREET, COBURG VIC 3058 |  |  | Lightning | Highly unlikely | Electrical overload |  |  | 1 | HV conductor down. | Conductor (bare) | 0 | 0 | 0 |  | cs12 | Possible lightning strike | Loss of supply | 42374.1514 |  |  | 2286 | Public space |  | 20160503JEM_01 | Infrastructure (network-based) | -37.7336 | 144.9611 | 1 | Jemena | Report | 2845 | 0.015481 | 22kV AC | Essendon Airport | 3058 | Coburg | Lightning
Emergency high voltage switching was completed to minimise the number of customers affected and the 66kV, 22kV and LV intermediate timber pole was replaced under Access Authority conditions. | BRADY ROAD, DANDENONG NORTH VIC 3175 | LIS No. 0625205 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 1313hrs on 22/04/2016, 66kV feeder ERTS-DSK circuit breaker locked out but no customers were affected. At the same time, 22kV feeder LD 33 circuit breaker reclosed to lockout. A 'B'-Double truck backed into pole No. LIS 0625205 located in Brady Road, Dandenong that caused a 22kV conductor to briefly contact the LV conductors below as they clashed. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Brady-Cardinia" substation. The LEI confirmed a high voltage injection occurred (KEY 1604) affecting approximately 15-20 street lights in Stud Road between Police and Brady Roads that require replacement. The pole was broken at the base and required replacement. | Conductor (bare);Pole (wood);Public lighting | 0 | 0 | 0 |  | ERTS-DSH 66kV and LD 33 22kV | A 'B'-Double truck backed into pole No. LIS 0625205. | HV injection | 22/04/2016 13:13 |  |  | 2281 | Roadway |  | 20160503UTD_01 | Infrastructure (network-based) | -37.9557 | 145.2275 | 1 | United Energy Distribution | Report | 3202 | 0.03195 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3175 | Dandenong North | Vehicle
On arrival crew confirmed safety of site, repaired conductor and restored supply | 49 CLARKES CREEK ROAD, MERINO VIC 3310 | 717753 | Working too close to overhead lines | [5 empty] | 1 | Customer reported tree had brought conductor down at the incident location. On arrival the crew found that a tree (from outside the clearance space) had been felled across an adjacent SWER conductor, causing the conductor to break and fall to the ground. Protection operated. There was no ground fire There were no reported injuries or third party property damages. No shock, of fire starts. | Conductor (bare) | 0 | 0 | 0 |  | HTN002 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 42465.6104 |  |  | 2301 | Forest - plantation |  | 20160505PWA_01 | Infrastructure (network-based) | -37.757 | 141.5153 | 1 | Powercor | Report | 2863 | 0.026064 | 12.7kV AC (SWER) | Hamilton Airport | 3310 | Merino | Trees
Made safe | 42 HUMESIDE DRIVE, CAMPBELLFIELD VIC 3061 |  | Vehicle | [5 empty] | 1 | Truck hit a LV pillar and damaged the existing switch in the pillar. Cables have burnt, sparks and smoke came out of pillar caused by burnt cables due to the vehicle impact. | Cable;LV Pillar | 0 | 0 | 0 |  | BD16 | Truck hit pillar caused cables to burn. | Other electricity related | 42586.5514 | 1 | Negligible: no ground fire | 2312 |  |  | 20160509JEM_02 | Infrastructure (network-based) | -37.6718 | 144.9634 | 1 | Jemena | Report | 2982 | 0.040381 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Vehicle
Supply to Cable isolated and repairs made, Inspector attending to test and check that all is okay. | 2 NORMANBY STREET, MOONEE PONDS VIC 3039 |  | Working too close to underground cables;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 2 | Electric Shock received from metal shovel by third party person while performing excavating works. | Cable | 0 | 0 | 0 |  | LV / Feeder number N/A | Mr Sunny Watapotha 39 year old male working for Bosco Civil Received shock from metal shovel while excavating, the customer contacted 95mm2 LV cable trying to confirm location of cable prior to bringing in machinery for excavation purposes. | Minor shock | 42618.3958 |  |  | 2314 | Public space |  | 20160509JEM_03 | Infrastructure (network-based) | -37.7711 | 144.9151 | 1 | Jemena | Report | 2905 | 0.021538 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Dug up
CEOT dispatched fault crew to make safe and repair. Replaced fuse tube and restored supply. The fuse tubes were replaced with new type double action fuse tube holders. | 25 RIVER DRIVE, TARWIN LOWER VIC 3956 | 2804467 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 221643. Found 6K EDO fuse tube burning which blew due to unknown cause. No fire or damage caused. The existing fuse tubes were glowing. | EDO fuse | 0 | 0 | 0 |  | wgi14 | EDO fuse tube candled. | Other electricity related | 27/04/2016 21:20 | 1 | Negligible: no ground fire | 2310 | Commercial |  | 20160509SPN_01 | Infrastructure (network-based) | -38.699 | 145.8667 | 1 | AusNet Services Distribution | Report | 2879 | 0.027531 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Tarwin Lower | Fuse
CEOT dispatched to Fault Crew to make safe and repair. Fault truck attended. No damage to overhead conductors. CEOT operations closed ACR - BG121. Tree branch removed. Supply restored. | 5 COLLIE ROAD, GEMBROOK VIC 3783 | 417051 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 221733. Report of tree fire in vicinity of AusNet Services' assets. During strong winds and heavy rain a large tree limb broke off a wattle tree causing it to land across the HV conductors. A grass fire of 50 sq. metres was observed in the vicinity. ACR - BG121 operated. The following details were extracted from a report carried out by the AusNet Services' Vegetation group: Hazardous tree - yes; Tree - poor structure; Tree - private owner; Responsibility - AusNet Services; Branches inside vegetation clearance space - no; Weather - heavy rain. The following details were extracted from a report carried out by the Vegetation group: Hazardous tree - yes. Tree poor structure. Tree private owner. Responsibility - AusNet Services. Branches inside vegetation clearance space - no. Weather - heavy rain. | Conductor (bare) | 0 | 0 | 2 |  | phm33 | Vegetation: Trees Incident | Grassfire | 42434.4361 | 1 | Small: 10 - 1000 sq.m | 2316 | Residential |  | 20160509SPN_04 | Infrastructure (network-based) | -37.9431 | 145.5553 | 1 | AusNet Services Distribution | Report | 2890 | 0.016426 | 22kV AC | Moorabbin Airport | 3783 | Gembrook | Trees
CEOT dispatched to fault crew to attend to make safe and repair. WT127- ACR 1405244, isolated made safe construction crew t/c tree clearers. Conductors were repaired. | 340 GEMBROOK-LAUNCHING PLACE ROAD, LAUNCHING PLACE VIC 3139 | 145678 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | IMS 221732. A private tree has fallen and appears to have made contact with electrical conductors, fire was reported in vicinity. WT127-ACR 1405244 operated. A gum tree leader failed in strong winds and fell across HV conductors. Mature blue gum with a bifurcation 5 m from ground. Line side bifurcation failed in strong winds and fell across the HV conductors. Limb was approximately 20m long and 500m at its widest point. 2 separate fires, 1 small area of 3 sq.m at the point of impact, and 63 sq. m 40m up hill from point of impact. Tree branches were not inside vegetation clearance space. Extreme windy conditions with heavy rain. | Conductor (bare) | 0 | 0 | 0 |  | wyk11 | Vegetation: Trees Incident | Grassfire | 42434.4799 | 1 | Small: 10 - 1000 sq.m | 2317 | Agricultural |  | 20160509SPN_05 | Infrastructure (network-based) | -37.804 | 145.5869 | 1 | AusNet Services Distribution | Report | 2892 | 0.028412 | 22kV AC | Moorabbin Airport | 3139 | Launching Place | Trees
Fault crew facilitated isolation of the fault at fused switch P20 Breamar. Repairs completed | 1752 MOUNT MACEDON ROAD, WOODEND VIC 3442 | 909474 |  | Precipitation |  | Leakage |  |  | 1 | Vicfire reported that a conductor was down across road & was arcing / sparking at the incident location. On arrival the crew found that a cross arm had broken on P34 of the Breamar spur line resulting in one HV conductor falling to the ground. A localised back-feed occurred through transformer HV windings leaving the downed conductor energised. The fuses operated at P20 Breamar Spur Line. There were no reported injuries, no ground fire, no third party damage. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | WND012 | Crossarm fire | Pole-top fire | 42556.2389 | 1 | Negligible: no ground fire | 2323 | Roadway |  | 20160510PWA_04 | Infrastructure (network-based) | -37.3618 | 144.5569 | 1 | Powercor | Report | 2900 | 0.016166 | 22kV AC | Wallan (Kilmore Gap) | 3442 | Woodend | Crossarm
On arrival Crew removed Service line . Defect notice issued to repair/replace raiser bracket at house end | 21 PRITCHARD AVENUE, BRAYBROOK VIC 3019 | 11838 | Vehicle | [5 empty] | 2 | Passer-by reports that a tow truck has contacted a service at the incident location. On arrival the crew found that a tow truck had contacted a service resulting in damage to the service. There were no reported injuries. There was no fire. | Service conductor | 0 | 0 | 0 |  | SSE034 | Tow Truck (unknown operator) damaged service and raiser bracket | Loss of supply | 42526.4417 |  |  | 2324 | Roadway |  | 20160510PWA_05 | Infrastructure (network-based) | -37.7938 | 144.8482 | 1 | Powercor | Report | 2901 | 0.0062546 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Vehicle
EIO Geoff Jackson attended and discovered corroded neutral on pole and no neutral conductor to premise, there was an imbalance with the neutral - dim lights under the load. Fault crew replaced neutral screen service due to deterioration, tested and left supply on. | 24 PENTLAND PARADE, SEDDON VIC 3011 | 10562229 |  |  | Likely | Corrosion |  | Phase to earth | 1 | Customer received electric tingle/shock in the shower some weeks ago. | Pole top;Neutral screen | 0 | 0 | 0 |  | FE-08 | Deteriorated neutral screen service as identified by EIO. | Minor shock | 42679.3771 |  |  | 2330 | Residential |  | 20160511JEM_04 | Infrastructure (network-based) | -37.8089 | 144.8949 | 1 | Jemena | Report | 2908 | 0.01847 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Seddon | OH Cable
On arrival crew made site safe and commenced repairs | 34A CARAVAN STREET, WENDOUREE VIC 3355 | 17699 | Theft |  | Unlikely |  |  |  | 2 | mployee reported missing earth cable at incident location. Crew attended and found HV earth cable missing at pole. Crew replaced missing cables. No shocks, injuries or third party damage. | Earth/earthing | 0 | 0 | 0 |  | BAN004 | Copper Theft | Less than $50k damage | 42679.4389 |  |  | 2335 | Roadway |  | 20160512PWA_02 | Infrastructure (network-based) | -37.5328 | 143.8113 | 1 | Powercor | Report | 2937 | 0.0226 | Earthing cable | Ballarat Aerodrome | 3355 | Wendouree | Other
On arrival crew made site safe and commenced repairs | 87 MCMEEKIN ROAD, WARRNAMBOOL VIC 3280 | 8825 | Vehicle | [5 empty] | 2 | Vicfire reported that there were â€œwires down at premises, possibly hit by truckâ€ at the incident location. On arrival the crew found that an LV grey twisted service cable had been struck by an unknown vehicle, resulting in damage to the customers POA and their mains cable. The Police onsite said they had been told the service was hit by a truck, but nobody actually saw the truck that did the damage, and the Police had no more information. The service hooks at both ends were straightened, showing that the service was still on the hooks at the time of impact. There were no reported injuries or ground fires. | Service conductor | 0 | 0 | 0 |  | WBL004 | Unknown vehicle (Truck) hit service cable | Loss of supply | 42679.3243 |  |  | 2338 | Roadway |  | 20160512PWA_03 | Infrastructure (network-based) | -38.3756 | 142.4533 | 1 | Powercor | Report | 2924 | 0.014381 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
CEOT dispatched a fault crew and a LEI to make safe, investigate and repair. The damaged cable was repaired and supply restored to 57 St. Georges Rd. NST test result - Passed. Polarity test - Passed. LEI in attendance: The cable was repaired and supply restored to 57 St. Georges Rd. prior to the LEI's arrival. NST test result - Passed. Polarity test - Passed. CEOT (Control Room) was informed of outcome. | 55 ST GEORGES ROAD, BEACONSFIELD UPPER VIC 3808 | 521081 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 221346. Mr. Hayes was completing trench works by hand shovel at the service pit on the boundary of 55 & 57 St. Georges Rd. when the metal handle shovel he was using pierced the insulation of the red phase of the consumer's mains supplying 57 St. Georges Rd, making contact with the copper conductor, causing Mr. Hayes to receive a tingle from both hands to his feet whilst standing on the dirt area adjacent to the service pit. The cable in question protruded out from an existing manufacturer's hole (approx. 100mm diameter) in the side of the concrete service pit. | Services pit;Customer installation | 0 | 0 | 0 |  | bge12 | Electrician using a hand shovel at a shared position service pit the pierced insulation of UG consumer's mains cable to a neighouring property. | Minor shock | 42464.7028 |  |  | 2333 | Residential |  | 20160512SPN_02 | Infrastructure (network-based) | -38.001 | 145.3979 | 1 | AusNet Services Distribution | Report | 2919 | 0.023164 | Low voltage AC (<1kV) | Moorabbin Airport | 3808 | Beaconsfield Upper | Dug up
CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew replaced the EDO fuse tube and fuse link. | 121 EAST WEST ROAD, WARRAGUL SOUTH VIC 3821 | 2703982 |  | Lightning |  | Electrical breakdown |  |  | 2 | IMS 221916. LIS# 2703982 EDO Fuse candled at a substation pole. No other damage. No fire occurred. Fuse was hanging and burning. It is believed the EDO fuse to have been previously damaged during a lightning storm. | EDO fuse | 0 | 0 | 0 |  | wgl15 | Candled EDO fuse tube caused by lightning. | Other electricity related | 13/05/2016 13:40 | 1 | Negligible: no ground fire | 2343 | Agricultural |  | 20160516SPN_01 | Infrastructure (network-based) | -38.1862 | 145.9016 | 1 | AusNet Services Distribution | Report | 2932 | 0.025421 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Warragul South | Fuse
CEOT dispatched fault crew to make safe, investigate and repair. DAO for area sent to investigate. CFA put fire out & then reported. | 103 HOLDSWORTH ROAD, BENALLA VIC 3672 | 3902106 |  | Animal |  |  |  | Phase to earth | 1 | IMS 221933. A possum shorted the front disc insulator to steel crossarm on concrete pole on incoming 22kV centre phase pole strap apparently to bridge, that appears to have adequate clearance. A small area of grass was burned of approximate size 10m x 1.5 m. The possum's body was taken before the AusNet Services investigator got there. The feeder CB tripped. | Pole (concrete) | 0 | 0 | 0 |  | bn3 | Animal Incident | Grassfire | 22/04/2016 16:38 | 1 | Small: 10 - 1000 sq.m | 2345 | Agricultural |  | 20160516SPN_02 | Infrastructure (network-based) | -36.5269 | 145.9665 | 1 | AusNet Services Distribution | Report | 2935 | 0.022694 | 22kV AC | Wangaratta Aero | 3672 | Benalla | Animal
CEOT dispatched a fault crew to make safe and a LEI to investiagate. Meter 4749863. NST Passed on all 3 phases. Red-250volts White-243volts Blue-256 volts. 2v on the M.E.N & tap to an independent earth with no load. 3v on the M.E.N & tap to an independent earth with a 3A load. 4v on the M.E.N & tap to an independent earth with a 8A load. 0.4 Ohm Impedance. 651A PSC. Main earth OK. Water Bond OK. Fault Truck checked connections on Pole and found to be OK. No fault found. Property connected with a new 3 Phase XLPE Overhead Service.(is a new property so didnâ€™t replace service). Located 7 Poles back from Substation near the end of the LV circuit. Connected to Pole 1217551 out the front of property. (Pole is condemned). Substation 100kVA on pole 1217571 located out on Wicklow Ave. First bay has small copper conductors only then aluminium for 6 poles in Glenora Ave. | 17 GLENORA AVENUE, CROYDON VIC 3136 | 1217590 |  |  |  | Unknown technical factor |  | Phase to earth | 2 | IMS 221452. Customer receiving tingles in back yard. Chris Mees went to turn on the tap in the backyard and noticed a tingle to his hand/fingers. Chris had bare feet at the time and the ground below was damp from the tap being used previously. Tests showed 3v on the tap to a independent earth with a 3A load and 4v with a 8A load on the installation. The tap was bonded to the installations earthing system. This voltage on the tap may have been due to possible Impedance on the Reticulation as no other fault was found. | Conductor (bare) | 0 | 0 | 0 |  | cyn12 | Possibly due to long run of LV distribution network. | Minor shock | 42678.5021 |  |  | 2346 | Residential |  | 20160516SPN_03 | Infrastructure (network-based) | -37.7961 | 145.2746 | 1 | AusNet Services Distribution | Report | 2936 | 0.026437 | Low voltage AC (<1kV) | Moorabbin Airport | 3136 | Croydon | AF Other
CEOT dispatched a fault crew to make safe and investigate. Downer were on site preparing to repair the conductor whilst The DAO was on site. | 500 SOLDIERS ROAD, CLYDE NORTH VIC 3978 | 502463 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 221961. An excavator contacted a 22kV overhead line. AusNet Services' investigation officer, (the DAO) spoke with DAVID HOPGOOD from STREETWORKS (tel. 0419 911 727) about this as he was the site supervisor. David advised that the driver (not on site when the DAO was there) was working on one side of the road and was crossing the road to park the excavator on the other side for the next day's work. He said there was no spotter present as he was only driving, not working around the HV line. A traffic controller made noise and attention as he saw sparks coming from the excavator as it crossed under the HV line, thus that's the only way they knew that the excavator had hit the HV line. The outer 2 Phases had been hit (Red & Blue) and had suffered damage to 1 or 2 strands of the conductor. The excavator was a very large SUMITOMO SH300 excavator and there were scorch/weld marks on the top of the boom. This HV span is 105.7m between poles 502462 and 502463 and was hit approx. 40m from pole 502463. The HV line at this site measured at approx. 8.57m from the ground. David made several excuses that the driver wasn't in working mode and they didn't have markers on the line or any spotters or anything as he was only moving the excavator. The HV fuse operated on spur fuse site. | Conductor (bare) | 0 | 0 | 0 |  | cln23 | Excavator caused a No Go Zone Rules breach - contact with overhead HV conductor. | No Go Zone (contact) | 17/05/2016 12:15 |  |  | 2352 | Residential |  | 20160518SPN_01 | Infrastructure (network-based) | -38.0842 | 145.3627 | 1 | AusNet Services Distribution | Report | 2954 | 0.027056 | 22kV AC | Moorabbin Airport | 3978 | Clyde North | Vehicle
on arrival crew made site safe and commenced repairs | NAZARETH HOUSE, 218 MILL STREET, LAKE WENDOUREE VIC 3350 | 22005 |  | Animal |  |  |  |  | 1 | A Powercor customer reported dim lights and electrical appliances not working at the incident location. On arrival the crew found that the roadside bare copper HV conductor had broken at a copper to copper Ampac connection, causing the HV conductor to fall to the ground. There was no ground fire, no reported injuries or third party property damage. | Conductor (bare) | 0 | 0 | 0 |  | BAN005 | Animal Incident | Loss of supply | 17/05/2016 3:45 |  |  | 2358 | Roadway |  | 20160519PWA_02 | Infrastructure (network-based) | -37.5538 | 143.845 | 1 | Powercor | Report | 2960 | 0.019976 | 22kV AC | Ballarat Aerodrome | 3350 | Lake Wendouree | Animal
On arrival crew confirmed site safe. There was no damage to overhead conductors | 571 WALLINGTON-OCEAN GROVE ROAD, WALLINGTON VIC 3222 |  |  | Within clearances |  |  |  |  | 1 | A contractor reported a tree branch fell onto HV conductor while he is tree trimming at the incident location. On arrival the Powercor crew found that the trees had been trimmed but no damage to the conductors. Protection operated. There was no ground fire. There were no reported injuries, HVI or damage to third party property | Conductor (bare) | 0 | 0 | 0 |  | DDL023 | Private contractor trimming vegetation. | Loss of supply | 18/05/2016 12:22 |  |  | 2361 | Roadway |  | 20160519PWA_03 | Infrastructure (network-based) | -38.2207 | 144.5051 | 1 | Powercor | Report | 3206 | 0.025521 | 22kV AC | Avalon Airport | 3222 | Wallington | Trees
On arrival Crew made site safe. Temporary repairs to the ZSS perimeter fencing had been undertaken, permanent fence repairs to be organized. | 68 FOREST STREET, COLAC EAST VIC 3250 | 33039966 | Vehicle | [5 empty] | 2 | Advice from the CFA of a vehicle accident at Colac Zone Substation. On arrival the crews found a car had driven through the ZSS perimeter fencing and collided with ZSS equipment in the yard. The driver had been apprehended by the police and was suspected of driving under the influence. No reports of injuries, shock or ground fires were received. | Equipment | 0 | 0 | 0 |  | CLC004 | Vehicle incident | Damage to network assets | 22/05/2016 0:14 |  |  | 2368 | Other | Substation | 20160523PWA_01 | Infrastructure (network-based) | -38.3409 | 143.6057 | 1 | Powercor | Report | 12407 | 0.038119 | 22kV AC | Ballarat Aerodrome | 3250 | Colac East | Vehicle
A faults truck attended and with the assistance of the police, dismantled the ladders and ensured the site was left safe. United Energy had concerns the customer may consider other creative methods to reconnect his electricity supply and contacted the Department of Human Services in an effort to mitigate any further unsafe connection attempts. | 2B WELLESLEY STREET, MONT ALBERT VIC 3127 | LIS No. 859993 | Unauthorised access | [5 empty] | 2 | Caller advised that a neighbour has rigged up several ladders near the power pole and they have called the police. The customer had been off supply since June 2014 after they were disconnected for non-payment at the pole end. The customer constructed ladders up the pole (LIS No. 859993) in an effort to re-connected himself. Police were in attendance and indicated the customer may be mentally unstable / handicapped and they cannot guarantee that he will not try and reconnect himself again. No electric shocks or injuries were received by the customer. ESV were notified with reference number 4599429 provided. | Pole (wood) | 0 | 0 | 0 |  |  | The customer constructed ladders up the pole in an effort to re-connected the electricity supply to his property. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/02/2016 13:00 |  |  | 993 | Roadway |  | 20160304UTD_02 | Infrastructure (network-based) | -37.8173 | 145.1021 | 1 | United Energy Distribution | Report | 1439 | 0.020003 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Mont Albert | Other
Disconnected street light lantern | 89 ESPLANADE, WILLIAMSTOWN VIC 3016 |  |  |  |  | Overheated connection |  |  | 2 | Street light lantern fire | Public lighting | 0 | 0 | 0 |  |  | It is possible that the lantern failures were the result of moisture ingress. However, a more realistic scenario is that the lighting control gear in the lantern is subject to overheating due to repeated attempts to re-strike an arc in the high pressure sodium lamp of the luminaire. This occurs when lamps start to cycle off then on, generally when lamps are approaching the end of their life. | Other electricity related | 42554.8681 | 1 | Negligible: no ground fire | 1006 | Residential |  | 20160308JEM_01 | Infrastructure (network-based) | -37.8666 | 144.8908 | 1 | Jemena | Report | 1465 | 0.03034 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown | AF Other
CEOT dispatched a fault crew to isolate and make safe. Substation was isolated and made safe. Requested Underground crew sent to investigate and repair the damage or to replace the substation. DAO advised to attend the site. No fire damage to any public property. The fire only affected the kiosk substation. | 62 SNAKE GULLY DRIVE, BUNDOORA VIC 3083 |  |  |  |  | Unknown technical factor |  |  |  | Kiosk substation LV circuits and LV Webber strips melted. Evidence of char marks on kiosk. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | wt9 | CEOT didn't specify a cause. The incident is currently under investigation. | Plant/equipment | 42524.6062 | 1 | Negligible: no ground fire | 1009 |  |  | 20160308SPN_02 | Infrastructure (network-based) | -37.7017 | 145.0489 | 1 | AusNet Services Distribution | Report | 1461 | 0.041436 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Bundoora | OH Cable
Crew isolated supply and undertook repairs | 7089 BENDIGO-PYRAMID ROAD, MITIAMO VIC 3573 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | CFA reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the top of the pole. The dust and light shower caused centre phase polymeric HV insulator to leak to Pole Top Assembly. No protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 42524.9215 | 1 | Negligible: no ground fire | 1013 | Roadway |  | 20160309PWA_02 | Infrastructure (network-based) | -36.1907 | 144.131 | 1 | Powercor | Report | 3088 | 0.012616 | 22kV AC | Bendigo Airport | 3573 | Mitiamo | Pole
Crew isolated supply and undertook repairs. | 402-448 LEAKES ROAD, PLUMPTON VIC 3335 |  | Theft | [5 empty] | 2 | A customer reported that a cable on a pole at the incident location has been stolen. Upon arrival the crew found that the newly laid but not connected 70m long 16mm 4C cable had been stolen. There were no reported injuries, ground fire or third party damage. | Cable | 0 | 0 | 0 |  |  | Theft of cable by persons unknown | Damage to network assets | 42554.5028 |  |  | 1025 | Residential |  | 20160309PWA_14 | Infrastructure (network-based) | -37.6761 | 144.6623 | 1 | Powercor | Report | 3090 | 0.028306 | 22kV AC | Melbourne Airport | 3335 | Plumpton | Other
The faults crew identified that 2 x 5amp HV powder filled fuses had operated and the 25kVA transformer requires replacement. The repairs were completed, including the replacement of the damaged 3 phase and single phase pole mounted FMJB's and the LEI inspected the three properties as they were energised by the faults crew. The LEI confirmed that a HVI did not occur to premises supplied from "Moorooduc- P7 Barak" substation. | 929 MOOROODUC HIGHWAY, MOOROODUC VIC 3933 | LIS No. 11004823 |  | Heat |  | Overheated connection |  |  | 1 | CFA on site near 929 Moorooduc Road at pole No. LIS 11004823 after a grass fire started. During hot conditions, a possible faulty 25kVA transformer at "Moorooduc- P7 Barak" pole type substation appeared to be the cause of a grass fire after the LV transformer leads and two underground FMJB's on the pole caught fire and dropped molten metal into the dry grass below. The grass fire was estimated to be 100sqm (20m x 5m) and was quickly extinguished by the CFA. The faults crew suspected that a high voltage injection may have occurred to the three customers supplied by underground cables from "Moorooduc- P7 Barak" substation and a LEI was dispatched to investigate. Pole No. LIS 11004823. ESV were advised with incident number 4617279 provided. | Services cable;Powder filled;Pole mounted;Connection box;Transformer | 0 | 1 | 0 |  | MTN 24 | During warm conditions, the LV transformer leads and two underground FMJB's on the pole caught fire and dropped molten metal into the dry grass below. The 25kVA transformer required replacement. | Pole-top fire;Loss of supply;Grassfire | 42403.684 | 1 | Small: 10 - 1000 sq.m | 1035 | Roadway |  | 20160310UTD_03 | Infrastructure (network-based) | -38.2482 | 145.0831 | 1 | United Energy Distribution | Report | 1491 | 0.031784 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the HV crossarm was replaced under Access Authority conditions prior to the supply being restored. | 7 SANDHAM STREET, ELSTERNWICK VIC 3185 | LIS No. 2303356 |  | Precipitation |  | Electrical breakdown;Insulator;Leakage |  |  | 2 | Caller reported a pole fire outside 7 Sandham Street, Elsternwick. Following light drizzly rain after a dry spell, a HV crossarm fire occurred on a HV/LV pole (LIS No. 2303356) located outside 7 Sandham Street, Elsternwick. | Crossarm (wood) | 0 | 0 | 0 |  | EL 13 | Probable insulator tracking after morning drizzle following a dry spell of weather. | Pole-top fire | 42432.2799 | 1 | Negligible: no ground fire | 1038 | Roadway |  | 20160310UTD_05 | Infrastructure (network-based) | -37.8817 | 145.0019 | 1 | United Energy Distribution | Report | 1494 | 0.0089954 | 11kV AC | Moorabbin Airport | 3185 | Elsternwick | Crossarm
Jemena CoC dispatched Fault crew to investigate concerns of sparking on street water main. Jemena Faults crew located house fault, isolated supply and contacted JEN Inspector, Work Practices and Police. | 104A NORTHERN ROAD, HEIDELBERG WEST VIC 3018 |  | Unauthorised work;Unauthorised access |  | Highly unlikely |  |  |  | 2 | Electrician was observed connecting the Jemena overhead LV service tails to the Customerâ€™s fused mains box. The electrician had replaced 3 phase fused mains box, upsized the HRC fuses to 80m amps, and was reconnecting the services which were crossed to reach the box terminals when approached to cease works by Jemena Compliance Officer. Electrician removed â€˜liveâ€™ service tails from customers fused mains box without authority. Replaced 3 phase 55 amp customers mains box to 100 amps 3 phase mains box. Swapped service tail phasing to reach mains box connections, upsized HRC 55amp fuses to 80 amp HRC Jemena Inspector and Faults truck contacted to check and test the installation, receive correct Prescribed certficate, replaced overhead service. | Service conductor | 0 | 0 | 0 |  |  | Electrician undertaking unauthorised works on Jemena assets | No Go Zone (contact) | 28/02/2016 14:20 |  |  | 1045 | Commercial |  | 20160311JEM_01 | Infrastructure (network-based) | -37.7301 | 145.0533 | 1 | Jemena | Report | 3388 | 0.014255 | Low voltage AC (<1kV) | Essendon Airport | 3018 | Heidelberg West | Other
Fuse was replaced and supply restored to customers. | 401 SOLDIER SETTLERS ROAD, TALLANGATTA VALLEY VIC 3701 |  |  | Lightning | [5 empty] | Customer called in advising of all supply. Fault crew arrived and advised 6K EDO had operated and there were burn marks on the fuse tube. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse tube burnt. CEOT did not specify a cause. | Other electricity related | 42646.6799 | 1 | Negligible: no ground fire | 1046 |  |  | 20160314SPN_01 | Infrastructure (network-based) | -36.2225 | 147.3296 | 1 | AusNet Services Distribution | Report | 1503 | 0.024888 | 22kV AC | Wangaratta Aero | 3701 | Tallangatta Valley | Fuse
Opened CY002 and CY013 remotely. Closed CY001 restoring supply up to CY013. Patrol arranged and found and CEOT was advised a tipper truck with tripper tray elevated had contacted the HV. No reported injuries. Section was isolated pending repairs. | 8243 MURRAY RIVER ROAD, WALWA VIC 3709 |  | Working too close to overhead lines | [5 empty] | 1 | TRC advised ARC to WALWA had tripped on SEF. | Conductor (bare) | 0 | 0 | 0 |  |  | Tipper truck with raised tray contacted HV line. | No Go Zone (contact) | 42707.5507 |  |  | 1048 |  |  | 20160314SPN_03 | Infrastructure (network-based) | -35.9477 | 147.6697 | 1 | AusNet Services Distribution | Report | 1507 | 0.0072187 | 22kV AC | Wangaratta Aero | 3709 | Walwa | Vehicle
Crew isolated supply and undertook repairs | 189 CAPEL PLACE, NORTH MELBOURNE VIC 3051 |  | Working too close to underground cables | [5 empty] | 2 | An on site worker reported that they have uncovered an underground cable at the incident location. On arrival the crew found that the contractor (BP Plumbing BP Plumbing, 155-157 Wellington Road, Clayton 3168, Cathal Mcloglin, mobile 0433 685 873 ) were installing water taps when their excavator struck and damaged an 11kV underground cable. The damaged cable was later determined to be an out of service, but serviceable. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Contractor made contact with 11kV underground cable | Less than $50k damage | 16/03/2016 13:00 |  |  | 1061 | Commercial |  | 20160317PWA_03 | Infrastructure (network-based) | -37.8041 | 144.9546 | 1 | CitiPower | Report | 8016 | 0.0048032 | 11kV AC | Essendon Airport | 3051 | North Melbourne | Dug up
Made safe and repaired | 402 UPPER HEIDELBERG ROAD, EAGLEMONT VIC 3084 | [5 empty] | Not followed |  | 2 | The crew while manoeuvring the EWP basket into position the White phase LV conductor caught under the Redmond Gary EWP basket and was dragged across making contact with the Neutral conductor causing the White phase conductor fall to ground level. | Conductor (bare) | 0 | 0 | 0 |  |  | Whilst moving the EWP bucket into place, the White phase LV conductor caught under the Redmond Gary EWP basket and was dragged across making contact with the Neutral conductor causing the White phase conductor to fall to ground level. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/03/2016 11:35 |  |  | 1069 | Residential |  | 20160321JEM_02 | Infrastructure (network-based) | -37.7577 | 145.0542 | 1 | Jemena | Report | 1534 | 0.039947 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Eaglemont | Other
Crew isolated supply and undertook repairs | 3 HADDON-WINDERMERE ROAD, HADDON VIC 3351 |  | Working too close to overhead lines | [5 empty] | 1 | A customer reported that an excavator(owned by Pat Kennedy â€“ 0418 508 817 â€“ Dowling Road, Cardigan) had struck a power line and damaged a pole at the above location. On arrival the crew found that an excavator whilst cleaning out a dam had contacted a SWER conductor causing the pole to break 2 metres above the ground. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | An excavator (owned by Pat Kennedy â€“ 0418 508 817 â€“ Dowling Road, Cardigan) had struck a HV SWER conductor and damaged a pole at the above location. | Loss of supply | 17/03/2016 17:10 |  |  | 1070 | Agricultural |  | 20160321PWA_01 | Infrastructure (network-based) | -37.5904 | 143.7188 | 1 | Powercor | Report | 3129 | 0.024514 | 22kV AC | Ballarat Aerodrome | 3351 | Haddon | Vehicle
Crew isolated supply and undertook repairs | NARILLA, 785 SMARTS HILL ROAD, BO PEEP VIC 3351 |  | Theft | [5 empty] | 2 | A faults crew attended an All Supply fail report at the incident location. Upon arrival the crew found that the HV and LV earths on a pole had been stolen by an unknown party. There were no reported injuries, ground fire or third party property damages | Conductor (bare);Earth/earthing | 0 | 0 | 0 |  |  | Theft of earth wires by person/s unknown | Damage to network assets | 18/03/2016 1:49 |  |  | 1080 | Roadway |  | 20160322PWA_04 | Infrastructure (network-based) | -37.531 | 143.6723 | 1 | Powercor | Report | 1546 | 0.02275 | 22kV AC | Ballarat Aerodrome | 3351 | Bo Peep | Other
Crew isolated supply and undertook repairs | 109 COUNTRY CLUB DRIVE, CLIFTON SPRINGS VIC 3222 |  |  |  |  | Neutral fault;Fault on customer installation |  |  | 2 | Ms Donna Copperwaite was operating the shower tap for her son when she received an electric shock as she made simultaneous contact between her hand on the shower tap and her bare feet while standing on the damp bathroom floor. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an â€˜Open Circuitâ€™ O/H Service Neutral Conductor at the Reticulation Pole, which was displaced from its termination to the Reticulation Conductors following contact by a High Load vehicle earlier in the day. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 205 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | The attending Powercor Fault Crew replaced the existing O/H Twisted Aluminium Service Cable and completed an NST test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact following replacement of the overhead service cable, identified 0.7 Volts under normal load conditions. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | Minor shock | 16/03/2016 16:40 |  |  | 1084 | Residential |  | 20160322PWA_06 | Infrastructure (network-based) | -38.1547 | 144.5734 | 1 | Powercor | Report | 1551 | 0.015206 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | Vehicle
Crew isolated supply and undertook repairs | 73 GIRDLESTONE STREET, ARARAT VIC 3377 |  |  |  |  | Fault on customer installation |  |  | 1 | Ms Lynne Shipcott was washing her hands in the kitchen sink when she received an electric shock as she made simultaneous contact between her hand on the kitchen tap and her arm on the metal sink. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor at the â€œWrap-onâ€ located at the Customerâ€™s Point of Attachment, causing a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | REC Jeff Oâ€™Donnell attended site to replace a deteriorated Mains Connection Box, which was undertaken prior to the investigation by the attending LEI. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST Test, which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, confirmed 1.5 Volts following replacement of the O/H Service Cable. A final NST Test was carried out on the installation by the attending LEI, which also confirmed a Pass result. The Installation was left ON supply. | Minor shock | 42616.7292 |  |  | 1087 | Residential |  | 20160322PWA_08 | Infrastructure (network-based) | -37.2797 | 142.9361 | 1 | Powercor | Report | 3099 | 0.020856 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | OH Cable
CEOT dispatched a fault crew to make safe and isolate. The crew Isolated the street lantern in the pit and raised a new job for street light replacement. | 570 BORONIA ROAD, WANTIRNA VIC 3152 |  |  |  |  | Electrical breakdown |  |  |  | IMS 221161. Street light lantern caught fire and burnt out. 250 Watt HPS lantern. | Public lighting | 0 | 0 | 0 |  |  | CEOT didn't specify a cause. Incident is currently under investigation. | Other electricity related | 22/03/2016 5:45 | 1 | Negligible: no ground fire | 1082 |  |  | 20160322SPN_01 | Infrastructure (network-based) | -37.8508 | 145.2366 | 1 | AusNet Services Distribution | Report | 1550 | 0.0044618 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | AF Other
A faults crew attended and installed LV parallels to temporary restore supply to customers supplied from the concrete pole type substation. It was planned to replace the blue phase HV powder filled fuse assembly and melted HV dropper during daylight hours. | 93 NICHOLAS STREET, ASHBURTON VIC 3147 |  |  |  |  | Fatigue |  |  | 2 | Customers who reside in Nicholas Street advised that lights and appliances are flickering. A 11kV HV fuse candled at "Winton-Nicholas" substation that caused a loss of supply to customers who reside in Nicholas Street, Ashburton. | Powder filled | 0 | 0 | 0 |  | EM 05 | Candling fuse | Pole-top fire | 21/03/2016 2:39 | 1 | Negligible: no ground fire | 1076 | Roadway |  | 20160322UTD_01 | Infrastructure (network-based) | -37.8746 | 145.0743 | 1 | United Energy Distribution | Report | 1542 | 0.035659 | 11kV AC | Moorabbin Airport | 3147 | Ashburton | Fuse
Crew isolated supply and undertook repairs | 1020 GIRGARRE EAST ROAD, GIRGARRE EAST VIC 3616 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a cross-arm fire had occurred on a 22kV pole which burnt the cross-arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross-arm fire | Pole-top fire | 17/02/2016 8:37 | 1 | Negligible: no ground fire | 1097 | Agricultural |  | 20160323PWA_02 | Infrastructure (network-based) | -36.4519 | 145.1136 | 1 | Powercor | Report | 1565 | 0.032791 | 22kV AC | Shepparton Airport | 3616 | Girgarre East | Crossarm
Crew isolated supply and undertook repairs | 80 BALDWIN ROAD, TATURA VIC 3616 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a cross-arm fire had occurred on a 22kV pole. There was no ground fire. There were no reported injuries or third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross-arm fire on 22kV pole | Pole-top fire | 18/03/2016 7:53 | 1 | Negligible: no ground fire | 1100 | Roadway |  | 20160323PWA_05 | Infrastructure (network-based) | -36.44 | 145.1945 | 1 | Powercor | Report | 3117 | 0.027553 | 22kV AC;66kV AC | Shepparton Airport | 3616 | Tatura | Crossarm
Crew isolated supply and undertook repairs. | 422 SUTTON STREET, DELACOMBE VIC 3356 |  |  |  |  | Defective component |  |  | 1 | A customer reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, resulting in a ground fire (approx. 2 sqm) on road reserve. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Crew found surge arrestor on cable head pole had failed and flashed over causing pole fire and resulting debris started a ground fire. | Pole-top fire | 23/03/2016 14:40 | 1 | Localised: less than 10 sq.m | 1102 | Roadway |  | 20160324PWA_01 | Infrastructure (network-based) | -37.5787 | 143.8272 | 1 | Powercor | Report | 3137 | 0.037071 | 22kV AC | Ballarat Aerodrome | 3356 | Delacombe | Other
Crew isolated supply and undertook repairs. | 200 TYNTYNDER ROAD, TYNTYNDER VIC 3586 |  | Caused by REC/contractor | Fire |  |  |  |  | 1 | A customer reported pole burnt down wires down due to property fire at the incident location. On arrival the crew found that a 22kV pole had burnt off at the ground level and fell over. Protection operated. The fire involved was due to property owner burn off and not Powercor related. There were no reported injuries or third party property damages. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Fire commenced by farmer burning stubble | Loss of supply | 23/03/2016 15:42 |  |  | 1106 | Agricultural |  | 20160329PWA_04 | Infrastructure (network-based) | -35.2661 | 143.5338 | 1 | Powercor | Report | 3195 | 0.010169 | 22kV AC | Swan Hill Aerodrome | 3586 | Tyntynder | Other
Crew isolated supply and undertook repairs | WEAVER RESERVE, 141-153 ESPLANADE, ALTONA VIC 3018 |  |  |  |  | Overheated connection |  |  | 2 | Fire brigade and Hobsons Bay City Council reported a pole fire at the above location.On arrival, the crew found a fire had occurred within a Fused Overhead Line Connection Box belonging to the Hobsons Bay City Council. There was no ground fire. No reported injuries or third party property damages. | Connection box | 0 | 0 | 0 |  |  | Customers FOLCB overheated and melted | Plant/equipment | 26/03/2016 6:21 | 2 | Negligible: no ground fire | 1108 | Roadway |  | 20160329PWA_05 | Infrastructure (network-based) | -37.8704 | 144.8306 | 1 | Powercor | Report | 2809 | 0.020911 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Connection
Crew isolated supply and undertook repairs | 319 PRINCES HIGHWAY, WERRIBEE VIC 3030 | 30113795 |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 0 | Customer reported a pole fire at the incident location. On arrival, the crew found a fire had occurred at the 22kV cross-arm. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  | WBE013 | Cross arm fire on 22kV power pole | Pole-top fire | 25/03/2016 10:35 | 1 | Negligible: no ground fire | 1111 | Roadway |  | 20160329PWA_07 | Infrastructure (network-based) | -37.8845 | 144.6997 | 1 | Powercor | Report | 5386 | 0.02312 | 22kV AC | Laverton Raaf | 3030 | Werribee | Crossarm
Crew isolated supply and undertook repairs | 2 YORK AVENUE, AVOCA VIC 3467 |  | Working too close to overhead lines | [5 empty] | 2 | An on site worker reported a forklift hit overhead wire at the incident location. On arrival the crew found that a damaged 4 core low voltage service cable, the insulation had been stripped around the midpoint and 3 wires were detached at the pole. The crew measured the service at 4.3 at the POA and 4.4 over the drive. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | forklift made contact with low voltage overhead service wire | No Go Zone (contact) | 30/03/2016 15:48 |  |  | 1124 | Commercial |  | 20160331PWA_01 | Infrastructure (network-based) | -37.0826 | 143.4783 | 1 | Powercor | Report | 1604 | 0.035688 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3467 | Avoca | Vehicle
CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 6 Volts no load to 90 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 6 Volt no load to 90 Volts maximum load. CTA/LEI performed NST test at installation switchboard with a fail result recorded. Service crew investigated connections at the customer FOLCB at the POA and found a poor neutral connection between the PAL o/h service neutral conductor and the consumer mains neutral conductor, due to loose grub screws in the neutral terminal. Service crew performed NST test at the POA with a pass result recorded and re-terminated the PAL o/h service neutral conductor securely in the neutral terminal of the FOLCB. CTA/LEI performed NST test at customer MSB with pass result recorded. CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 1 Volt no load to 2 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 1 Volt no load to 2 Volts maximum load. A final NST test was carried out by the CTA / LEI with a pass result again recorded. Installation left ON supply. | 26 BEALES STREET, TORQUAY VIC 3228 |  |  |  |  | Mechanical breakdown |  |  | 2 | Rahman was standing at the outdoor MSB metal electricity meter enclosure and received a shock to his right hand when he came in contact with the metal latch of the enclosure whilst standing on the bare ground with rubber thongs on his feet. Grub screws that secure the PAL o/h neutral service conductor into the neutral terminal of the customer FOLCB at the POA were loose, which created a poor connection between the PAL o/h service neutral conductor and the customer consumer mains neutral conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 90 Volts on the water piping system and the earthed MSB metal electricity meter enclosure. | Service conductor | 0 | 0 | 0 |  |  | Loose grub screws in neutral terminal of POA FOLCB. | Minor shock | 25/03/2016 14:00 |  |  | 1127 | Residential |  | 20160331PWA_03 | Infrastructure (customer connection) | -38.3342 | 144.3189 | 1 | Powercor | Report | 8026 | 0.020502 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Connection
A LEI and faults truck attended and tested the installation to determine the cause and measured 47v between the water pipes and an independent earth. The faults crew proceeded to check connections at the POA and pole ends and identified the cause to be a corroded neutral block in the three phase FOLCB at pole No. LIS 8830915 that supplied two customers from an underground pit. The faults crew replaced the three phase FOLCB and the LEI re-tested the installation that confirmed the fault had been rectified and supply was left on. | 201A OSBORNE DRIVE, MOUNT MARTHA VIC 3934 | LIS No. 8830915 | Unknown external/community factor | Prone to salt deposition |  | Corrosion;Neutral fault | Unknown work practice factor | Phase to earth | 2 | Customer advised that lights are dimming and his wife received an electric shock at the kitchen sink. The occupier contacted the United Energy faults and emergencies call centre after a slight electric shock was received when she touched the earthed dishwasher and the kitchen taps. They have also noticed the recent dimming of lights for the past two or three nights. | Cable;Connection box | 0 | 0 | 0 |  |  | The cause was due to a corroded neutral block in the three phase FOLCB that supplied two customers from an underground pit. | Minor shock | 22/03/2016 16:00 |  |  | 1125 | Roadway |  | 20160331UTD_01 | Infrastructure (network-based) | -38.2454 | 145.0365 | 1 | United Energy Distribution | Report | 1605 | 0.0063796 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | Connection
Fault follow up raised to replace crossarm | NAKIAS 324 PENTAL ISLAND ROAD, PENTAL ISLAND VIC 3586 | 32162437 |  |  |  | Leakage |  |  | 2 | Crew reported a fire at the incident location. On arrival the crew found burn marks around the king bolt on Pole 22. The fire had occurred at a previous date and had self extinguished. There was no signs of a ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  | SHL005 | Electrical Leakage | Pole-top fire | 42373.766 | 1 | Negligible: no ground fire | 1137 | Agricultural |  | 20160404PWA_05 | Infrastructure (network-based) | -35.3754 | 143.5841 | 1 | Powercor | Report | 1621 | 0.014194 | 22kV AC | Swan Hill Aerodrome | 3586 | Pental Island | Crossarm
CEOT dispatched a fault crew to make safe, isolate and repair. The crew made the site safe, replaced the HV fuse and restored supply to customers. A work order has been raised to replace this EDO fuse with a BA fuse. | 976 EAST WEST ROAD, DARNUM VIC 3822 | 2718603 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 221337. Candled EDO fuse. No damage. No pole or ground fire. Nobody harmed. No evidence of why it candled. | EDO fuse | 0 | 0 | 0 |  | wgl15 | No direct evidence of why it candled. | Other electricity related | 42433.5194 | 1 | Negligible: no ground fire | 1135 | Agricultural |  | 20160404SPN_02 | Infrastructure (network-based) | -38.1952 | 145.9885 | 1 | AusNet Services Distribution | Report | 1618 | 0.020841 | 22kV AC | Morwell (Latrobe Valley Airport) | 3822 | Darnum | Fuse
The crew carried out repairs | 17 FRANK STREET, BALWYN NORTH VIC 3104 | 7592 |  |  |  | Overheated connection |  |  |  | MFB reported that there was a pole fire, at the incident location. On arrival the crew found 3ph fuse mains junction box had caught fire on pole #7592 and was damaged. There was no evidence of ground fire. There was no injuries or any property damage. | Connection box | 0 | 0 | 0 |  | WD013 | Loose connection | Melting or smoking only | 42464.85 |  |  | 1145 | Public space |  | 20160406PWA_02 | Infrastructure (network-based) | -37.7967 | 145.0947 | 1 | CitiPower | Report | 2742 | 0.03787 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Connection
Crew isolated supply and undertook repairs | 1 EAST STREET N, BAKERY HILL VIC 3350 | 976620 |  |  |  | Overheated connection |  |  |  | VicFire reported a fire at the incident location. On arrival the crew found that a krone box fire had occurred on a 315 kVA concrete substation pole (South West side), which caused debris to fall on a vehicle parked nearby. There was no ground fire. There were no reported injuries. | Connection box | 0 | 0 | 0 |  | BAN007 | overheated connection | Loss of supply;Less than $50k damage | 42464.6979 |  |  | 1147 | Roadway |  | 20160406PWA_04 | Infrastructure (network-based) | -37.5617 | 143.8677 | 1 | Powercor | Report | 1635 | 0.023913 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Bakery Hill | Connection
The customer mains were tested and 40 volts was found between the active and the neutral. The crew abolished supply to the property. | 51 KNOX DRIVE, BARWON HEADS VIC 3227 | 3647 | Theft | [6 empty] | A Lendlease (Powercor Contractor) attended the incident location to abolish a low voltage service. On arrival the crew found that the service fuse had been removed by an unknown party and replaced with a piece of garden hose and tape. The meters had been removed and the customers mains were cut and left hanging in the air. Demolition of the house had taken place with part of the facia cut away and supported by a steel pole. The facia contained the POA No injury and no third party damage was reported. | Connection to meter;Customer installation | 0 | 0 | 0 |  | WPD024 | Meters missing and Interference to assets | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42464.5972 |  |  | 1150 | Residential |  | 20160407PWA_02 | Infrastructure (network-based) | -38.2689 | 144.4915 | 1 | Powercor | Report | 1640 | 0.0028403 | Low voltage AC (<1kV) | Avalon Airport | 3227 | Barwon Heads | Other
The contractor had no paperwork on site but ref no given over the phone. Fault Follow up arranged for permanent repairs | 464 WILLIAM STREET, WEST MELBOURNE VIC 3003 | 75434 | Working too close to underground cables | [6 empty] | A Contractor (Steve Ryan, mobile 0421 549 258.) advised that they have hit a cable in footpath at the incident location and nearby businesses have part supply. On arrival the crew found that the contractor had contacted a live low voltage underground service while they manually excavating foot path using a Cro bar for fire service. The insulation was damaged and the low voltage service was still â€œaliveâ€ when the crew arrived. There were no reported injuries. There was no fire. | Services cable | 0 | 0 | 0 |  | VM040 | Failure to identify cable location | Loss of supply | 42494.5056 |  |  | 1155 | Roadway |  | 20160408PWA_02 | Infrastructure (network-based) | -37.8065 | 144.9541 | 1 | CitiPower | Report | 2830 | 0.014 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Dug up
The crew made the place safe and the repairs done | 25 FARRANTS ROAD, WERRIBEE SOUTH VIC 3030 | 203247 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival, the crew found that the cross arm and pole around the King bolt partly bunt through. There was no ground fire. There were no reported injuries or third party damage. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | WBE034 | Pole fire | Pole-top fire | 42525.2354 | 1 | Negligible: no ground fire | 1157 | Agricultural |  | 20160408PWA_04 | Infrastructure (network-based) | -37.96 | 144.6811 | 1 | Powercor | Report | 2943 | 0.036981 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Pole
CEOT DISPATCHED FAULT CREW TO MAKE SAFE, INVESTIGATE AND REPAIR. CREW MADE SAFE AND REPLACED FUSE WITH 6K BORIC ACID FUSE. | 31 DE FREDERICKS ROAD, YARRAMBAT VIC 3091 | 900139 |  |  |  | Electrical breakdown |  |  | 2 | IMS 221422. SUBSTATION BORIC ACID HV FUSE CANDLED ON POLE 900139 [DEFREDRICKS P2 S/S]. | EDO fuse | 0 | 0 | 0 |  | drn013 | Boric Acid fuse candled. | Other electricity related | 42586.65 | 1 | Negligible: no ground fire | 1160 | Residential |  | 20160410SPN_02 | Infrastructure (network-based) | -37.6385 | 145.1406 | 1 | AusNet Services Distribution | Report | 1652 | 0.035525 | 22kV AC | Essendon Airport | 3091 | Yarrambat | Fuse
Made safe | 390 MELROSE DRIVE, TULLAMARINE VIC 3043 |  | Vehicle | [5 empty] | 1 | Truck has collided with pole causing pole to fall onto low voltage conductors resulting in high voltage injection. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  |  | Truck collided into pole | HV injection | 42555.3333 |  |  | 1165 | Industrial |  | 20160411JEM_04 | Infrastructure (network-based) | -37.6873 | 144.8689 | 1 | Jemena | Report | 2736 | 0.026785 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3043 | Tullamarine | Vehicle
Fault crew on site. Damaged neutral repaired on overhead line. Neutral volts test at service line - 1.4V. Overhead line disconnected at FOLCB. AusNet Services' LEI on site: NST result- Pass. Neutral Bar volts- 0.45V- No load, 6.5V- 15A load (Independent earth). Rear water tap- 6.5V (Independent earth). Consumer's mains IR test- 0.2 M Ohm (Fail). Riser bracket- 35V (Independent earth). Network analyser test results: V-N- 239.9V Z-L-N- 0.55 Ohm PSC L-N- 427.4A Z N- 0.03 Ohm. REC on site: Replaced consumer's mains. Replaced FOLCB. Prescribed CES & electrical inspection. Premises reconnected to supply. Control Room (CEOT) informed. | 10 GRAND PANORAMA COURT, LAUNCHING PLACE VIC 3139 | 1406776 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 220951. Mrs Bell was turning on the rear outside water tap with her right hand whilst her feet were simultaneously making contact with the paved area that she was standing on when she received a tingle from the water tap. This was caused by faulty FOLCB and faulty consumer's mains insulation resistance less than 1 Meg Ohm, resulting in higher neutral potential volts to earth. | No failed asset | 0 | 0 | 0 |  | wyk23 | Faulty FOLCB and low IR on consumer mains - 0.2M Ohm. | Minor shock | 42646.5396 |  |  | 1166 | Residential |  | 20160411SPN_01 | Infrastructure (network-based) | -37.7769 | 145.5693 | 1 | AusNet Services Distribution | Report | 1658 | 0.025294 | Low voltage AC (<1kV) | Moorabbin Airport | 3139 | Launching Place | OH Cable
Made safe | JARLEE, 1356 RIDDELL ROAD, RIDDELLS CREEK VIC 3431 |  |  |  |  | Defective component;Candled fuse |  |  | 1 | Burnt HV fuse due to candling | Boric acid | 0 | 0 | 0 |  |  | Candling fuse, the fuse continuous to conduct low level of current and generates significant heat in the contents and the insulating barrel of the fuse element. | Other electricity related | 20/03/2016 9:50 | 1 | Negligible: no ground fire | 1168 | Roadway |  | 20160412JEM_02 | Infrastructure (network-based) | -37.4881 | 144.6802 | 1 | Jemena | Report | 1660 | 0.03947 | 22kV AC | Melbourne Airport | 3431 | Riddells Creek | Fuse
Crew isolated supply and undertook repairs | 484 SHAGGY RIDGE ROAD, ROBINVALE IRRIGATION DISTRICT SECTION E VIC 3549 | 28760 |  |  |  | Leakage |  |  |  | Reports of HV Intermediate crossarm burnt through. On arrival crew found that a crossarm fire had occurred on a 22kv crossarm. There was no ground fire There were no reported injuries or third party property damage. | Crossarm (wood) | 0 | 0 | 0 |  | WMN014 | Excessive leakage current | Pole-top fire | 21/03/2016 17:13 | 1 | Negligible: no ground fire | 1170 | Roadway |  | 20160412PWA_02 | Infrastructure (network-based) | -34.6679 | 142.7543 | 1 | Powercor | Report | 3149 | 0.040612 | 22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section E | Crossarm
Crew isolated supply and undertook repairs | 1342 PRAIRIE-ROCHESTER ROAD, LOCKINGTON VIC 3563 | 32977 |  |  |  | Leakage |  |  | 1 | Customer reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt through the pole and cross arm. The cross arm straps held the equipment up. No ground fire. Protection operated. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  | SHP012 | Pole top fire, top of pole and cross-arm both burnt near king bolt position. | Pole-top fire | 42525.6438 | 1 | Negligible: no ground fire | 1182 | Agricultural |  | 20160413PWA_05 | Infrastructure (network-based) | -36.2989 | 144.5409 | 1 | Powercor | Report | 2938 | 0.016711 | 22kV AC | Bendigo Airport | 3563 | Lockington | Pole
Crew isolated supply and undertook repairs | 7982 MURRAY VALLEY HIGHWAY, BATHUMI VIC 3730 | 12924 |  |  |  | Leakage |  |  |  | Customer reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt the cross through at the cross arm strap, causing the outer phase to fall onto the LV arm. LEI found no evidence of HVI. There were no reported injuries. There was no ground fire | Crossarm (wood) | 0 | 0 | 0 |  | CME016 | Pole fire | Pole-top fire | 42525.866 | 1 | Negligible: no ground fire | 1184 | Roadway |  | 20160413PWA_07 | Infrastructure (network-based) | -36.0245 | 146.1028 | 1 | Powercor | Report | 1676 | 0.034219 | 22kV AC | Wangaratta Aero | 3730 | Bathumi | Pole
Supply isolated and repairs carried out | 12 HEALES STREET, INGLEWOOD VIC 3517 | 411847 | Vehicle | [5 empty] | 2 | Customer reported a vehicle hit pole at the incident location. On arrival the crew found that that a petrol tanker had left the road and made contact with two HV poles in Heales Street near the grant street intersection. The tanker was found on its side and was leaking fuel. The site was closed off by the police and the EPA was called in to manage the site. The power was off at the time of the incident due to a pole fire earlier. The truck driver sustained minor injuries. The supply was not fully restored until 8pm the following day due to the clean up required for the spilled fuel from the tanker. There was approximately 600 customers off in the township of Inglewood for over 24hours due to this accident. | Pole (wood) | 0 | 0 | 0 |  | EHK024 | Vehicle striking two power poles | Loss of supply | 42525.8333 |  |  | 2192 | Roadway |  | 20160414PWA_05 | Infrastructure (network-based) | -36.5764 | 143.8721 | 1 | Powercor | Report | 2684 | 0.014516 | 22kV AC | Bendigo Airport | 3517 | Inglewood | Vehicle
CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 6 Volts no load to 40 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 6 Volt no load to 40 Volts maximum load. CTA/LEI performed NST test at installation main switchboard with a fail result recorded. Service Crew found loose grub screws that secure the customers consumer mains neutral conductor and the PAL o/h neutral service conductor into the neutral terminal of the customer FOLCB at the POA. CTA/LEI performed NST test at installation MSB with fail result recorded. Service crew performed NST test at the POA with a fail result recorded. Following further investigation crew found a loose split bolt connection of the neutral conductor of the 2 wire ABC across road from service pole to bare neutral conductor of the LV reticulation. Crew performed NST test at the POA with a pass result recorded. CTA/LEI performed NST test at installation MSB with pass result recorded. CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of main switchboard resulted in a reading of 1 Volt no load to 3.5 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 1 Volt no load to 3.5 Volts maximum load. A final NST test was carried out by the CTA / LEI with a pass result again recorded. | 5 JEDDA STREET, BELL POST HILL VIC 3215 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Customer was standing at the back door outside garden tap and received a shock to his right hand when he came in contact with the tap whilst standing barefooted on the concrete path. | Connector/termination;Connection box | 0 | 0 | 0 |  |  | Loose connection FOLCB Loose connection service Neutral to LV mains | Minor shock | 42433.6042 |  |  | 2194 | Residential |  | 20160414PWA_07 | Infrastructure (customer connection) | -38.0992 | 144.3328 | 1 | Powercor | Report | 8031 | 0.0091817 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | Connection
Crew isolate supply and undertook repairs | 58A LYNDEN STREET, CAMBERWELL VIC 3124 | 10449 |  |  |  | Overheated connection |  |  |  | Customer reported a fire at the pole outside their property. On arrival the crew found the customers FOLCB had burnt and required replacement. There were no reported injuries, ground fire or property damage. | Connection box | 0 | 0 | 0 |  | RD001 | Attributed to a loose connection | Plant/equipment | 42678.9243 | 0 | Negligible: no ground fire | 2201 | Residential |  | 20160415PWA_04 | Infrastructure (network-based) | -37.8431 | 145.0851 | 1 | CitiPower | Report | 2701 | 0.040219 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Connection
Repairs completed | AYRVALE FARM, 235 SMARTS HILL ROAD, CARDIGAN VIC 3352 | 9470 | Theft | [5 empty] | 2 | An contract employee reported missing earth cables. On arrival the crew found that the low voltage earth cables had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Theft | Loss of supply | 13/04/2016 15:10 |  |  | 2207 | Roadway |  | 20160415PWA_09 | Infrastructure (network-based) | -37.5362 | 143.7333 | 1 | Powercor | Report | 2707 | 0.013293 | Earthing cable | Ballarat Aerodrome | 3352 | Cardigan | Other
Faults crew & LEI dispatched. Initial NST test performed failed. Power isolated before LEIâ€™s arrival. What was rectification? Faulty neutral connection inside pole junction box repaired and neutral bar replaced. After-rectification test results: NST test performed which failed. Neutral impedance fault loop recorded 4.1. What was rectification? Neutral connections all checked and passed. NST Test passed on the line side but not the load side of the FOLCB supplying the underground. Active connections cleaned inside FOLCB. After-rectification test results: Final NST test performed which passed. Neutral impedance fault loop recorded 0.1. Voltage at customer's meter box with 28A load recorded at 1.5V with independent earth. Other results? A voltage irregularity from the broken neutral caused damage to two items of the customer's equipment. One RCD failed to reset, until a pressure pump was removed from the power circuit and a split system air conditioner also failed to work with the circuit breaker on. A Customer Claim form was given to the customer to seek an appliance service contractor to repair the pump flow switch and split system. | 13 TELOPEA DRIVE, SANDY POINT VIC 3959 | 5782955 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 211002. Mr Waldron arrived at his holiday house at approximate 11:30pm 11/03/2016. Upon arrival when he energized the house he noticed the pole across road sparked and arced. He received also received tingles off the metallic meter box/switchboard enclosure. The cause was found to be faulty neutral connection in the junction box on pole (2023180) as well as poor active connection inside the fuse wedge due to corrosion on the FOLCB feeding the u/g mains on pole 2023180. | Any other type;Connection box | 0 | 0 | 0 |  | ftr21 | Pole end fault - pole junction box neutral bar corroded and active fuse prongs corroded at the FOLCB on pole feeding the underground. | Minor shock | 42707.0069 |  |  | 2209 | Residential |  | 20160415SPN_02 | Infrastructure (network-based) | -38.823 | 146.1155 | 1 | AusNet Services Distribution | Report | 2709 | 0.0010428 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3959 | Sandy Point | Fuse
Made safe | 2122 SYDNEY ROAD, CAMPBELLFIELD VIC 3061 |  |  | Bird |  |  |  |  | 1 | On successful reclose of feeder ST23. An operator discovered a crow at base of gas switch and approximately 5msq grass fire at base of pole. | Disconnector/isolator | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 15/04/2016 14:00 | 1 | Localised: less than 10 sq.m | 2212 | Industrial |  | 20160418JEM_01 | Infrastructure (network-based) | -37.6446 | 144.9519 | 1 | Jemena | Report | 2715 | 0.0089687 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, | 27 BOYS STREET, SWAN HILL VIC 3585 |  |  |  |  | Corrosion |  |  |  | A Builder working at the vacant property received and electric shock when he made simultaneous contact with one hand on the front metallic gate and his other hand in contact with the metallic boundary fence at the front of the property. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Consumers Main Neutral Conductor termination at a neighbouring Customerâ€™s FOLCB located at a rear adjacent property situated at 44 Gray Street Swan Hill. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic fence structures. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 30 Volts on the water piping system and fence structures at both properties and between the points of contact at 27 Boys Street, Swan Hill. | Customer installation | 0 | 0 | 0 |  |  | identified a corroded Consumers Main Neutral Conductor termination at a neighboring Customerâ€™s FOLCB located at a rear adjacent property situated at 44 Gray Street Swan Hill. | Minor shock | 42525.7708 |  |  | 2216 | Residential |  | 20160418PWA_02 | Infrastructure (customer connection) | -35.3465 | 143.5532 | 1 | Powercor | Report | 2727 | 0.014178 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a Capacitive Coupling causing an induced voltage on the Metal Downpipe, Guttering and Roof resulting in a Potential Difference of 76.0 Volts between the Points of Contact, which was eliminated when temporarily bonded to the Main Earthing system. A Registered Electrical Contractor attended site and installed an Equipotential Earth Bonding Conductor from the Main Earthing system to the metal Roof and Guttering to eliminate the Capacitive Coupling causing the induced voltage. The attending Powercor Fault Crew also replaced the existing O/H Neutral Screened Service Cable as a precautionary measure and completed an NST Test which confirmed a Pass result. | 12 WYNDHAM STREET, NEWSTEAD VIC 3462 |  |  |  |  | Fault on customer installation |  |  | 2 | Plumbing Contractor Mr Phillip Birwell was removing metallic Downpipes from the Roof Guttering when he received an electric shock as he made simultaneous contact with his hand on the metal Downpipe whilst standing and holding on to an aluminium ladder in contact with the ground located at the rear of the property. | Customer installation | 0 | 0 | 0 |  |  | Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a Capacitive Coupling causing an induced voltage on the Metal Downpipe, Guttering and Roof | Minor shock | 42464.5208 |  |  | 2218 | Residential |  | 20160418PWA_04 | Infrastructure (network-based) | -37.1053 | 144.063 | 1 | Powercor | Report | 8083 | 0.0075012 | Low voltage AC (<1kV) | Bendigo Airport | 3462 | Newstead | OH Cable
Crew completed repairs | 2 DRUMMARTIN STREET, ALBION VIC 3020 | 20799 | Theft | [5 empty] | 2 | A lineworker reported an earthing cable theft on sub pole at the incident location. While attending a report from customers for supply interruptions in the area, the Powercor faults crew found that earthing cables had been stolen from the pole. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | SSE014 | Theft | Loss of supply | 18/04/2016 17:04 |  |  | 2224 | Roadway |  | 20160420PWA_02 | Infrastructure (network-based) | -37.7826 | 144.8216 | 1 | Powercor | Report | 2767 | 0.0050741 | Earthing cable | Laverton Raaf | 3020 | Albion | Other
On arrival the crew found that copper earths had been removed from the substation. Crew replaced about 3 meters of earthing, substation made safe. | 5 GEEHI WAY, RAVENHALL VIC 3023 | 41107686 | Theft | [5 empty] | 2 | Control room received report that copper earths have been stolen at the incident location. On arrival the crew found that copper earths had been removed from the substation. | Pad mounted equipment/kiosk;Earth/earthing | 0 | 0 | 0 |  | SU005 | Theft | Less than $50k damage | 19/03/2016 13:32 |  |  | 2226 | Public space |  | 20160420PWA_04 | Infrastructure (network-based) | -37.7654 | 144.7454 | 1 | Powercor | Report | 3133 | 0.02545 | Earthing cable | Laverton Raaf | 3023 | Ravenhall | Other
On arrival crew made safe and commenced repairs | 15A WESTMINSTER PARKWAY, DERRIMUT VIC 3030 | 41095666 | Theft | [5 empty] | 2 | A Powercor contractor reports that copper straps have been stolen from a kiosk substation in the Sunshine area. On arrival the crew found that thieves are targeting the copper earth door straps on the kiosk substation. . There were no reported injuries. There was no fire. | Earth/earthing | 0 | 0 | 0 |  | SU013 | copper theft | Less than $50k damage | 21/04/2016 12:30 |  |  | 2237 | Public space |  | 20160426PWA_02 | Infrastructure (network-based) | -37.7833 | 144.7578 | 1 | Powercor | Report | 2784 | 0.022316 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply and carried out repairs | 39 TAYLOR STREET, FITZROY NORTH VIC 3068 | 50721 | Unauthorised work;Unauthorised access;Recreation - Fishing;Vehicle | [5 empty] | 2 | Customer in Taylor St reported loss of supply, Another resident reported neighbourâ€™s service line down. On arrival the crew found an overhead copper conductor (red phase) broken & on ground. The pay TV service was detached from the property when the crew arrived. There were no reported injuries or property damage. There was no ground fire | Conductor (bare);Communication cable/equipment | 0 | 0 | 0 |  | CO020 | It is possible that a vehicle made contact with a mid-span overhead pay TV service to 42A Taylor St, as there was evidence of clashing on the damaged conductor. | Loss of supply | 42647.6597 |  |  | 2242 | Roadway |  | 20160426PWA_07 | Infrastructure (network-based) | -37.7744 | 144.9804 | 1 | CitiPower | Report | 2789 | 0.012333 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Vehicle
The attending LEI conducted testing from an independent earth and various parts of the installation and detected 19.8 volts. A broken neutral conductor was determined as the cause. The attending LEI called for a service truck to attend and replace O/H service. The installation was tested by the attending LEI and zero volts were recorded on the installation neutral bar at the main switchboard and the water pipe system. | 48 MARINERS REEF ROAD, MARYBOROUGH VIC 3465 | 809908 |  |  |  | Neutral fault |  | Phase to earth | 2 | Mr Bristol was washing his hands when he made simultaneous contact between the metallic tap and the metallic drain plug. | Service conductor | 0 | 0 | 0 |  | MRO008 | A broken neutral conductor was determined as the cause | Minor shock | 23/04/2016 8:30 |  |  | 2247 | Residential |  | 20160427PWA_01 | Infrastructure (network-based) | -37.0593 | 143.7347 | 1 | Powercor | Report | 2797 | 0.031544 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | OH Cable
Protection (feeder CB) operated as expected Supply isolated to enable crews to undertake repairs | 92-96 PIPE ROAD, LAVERTON NORTH VIC 3026 | 986995 | Vehicle | [5 empty] | 1 | Employee from Nufarm which is located across the road, reported that a car had hit a pole and that wires were on the ground at the incident location. A car had hit pole LIS-986995 resulting in the blue phase HV conductor and blue phase of the LV conductor breaking and coming to ground. The HV crossarm fell into the LV conductor below, however the crossarm was held in place by the HV crossarm brace. There was no ground fire. There were no reported injuries or third party property damages. Protection (feeder CB) operated as expected. Fire brigade, Police and Ambulance were all in attendance. Occupant/s of vehicle taken to hospital. HVI confirmed at 3 properties per the LEI in attendance. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | LVN032 | Vehicle accident | HV injection;Loss of supply | 25/04/2016 5:53 |  |  | 2250 | Roadway |  | 20160427PWA_04 | Infrastructure (network-based) | -37.8242 | 144.801 | 1 | Powercor | Report | 2800 | 0.028109 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
Initial Schedule 1 report: Confirm with Tree Clearers that everyone is OK. Advised ESV of possible HVI. Further information from investigation: The safety observer established that the climber was OK and directed him to safely descend. Once he was on the ground the crew contacted relevant management including the Select Solutions Program Leader and were immediately contacted by CEOT to confirm that that was the cause of the outage. The crew was stood down pending an investigation. The investigation has been completed. The crew have been instructed in a number of operational SWMS and an auditing regime has been put in place by their supervisors. A Safety Gram has been sent to all climbers advising them of the learnings from the incident. | 1694 KANGAROO GROUND-ST ANDREWS ROAD, ST ANDREWS VIC 3761 | 20431 |  | Within clearances |  |  | Not followed | Phase to phase | 1 | IMS 221658. Initial Schedule 1 report: GB717 Auto Reclose was suppressed for tree clearing. GB717 opened and locked out at 12:21. Report of a tree branch clashing with HV & LV conductors at Lis 920431. Possible HVI. Further information from investigation: A vegetation management climbing crew from Active Tree Services were performing vegetation clearance works adjacent a HV/LV line. The climbing party had the Auto Reclose Suppressed as they were working on a tall eucalypt situated parallel to the lines. The climber was aloft working on a laterally growing branch and intended to fell it onto the ground, approximately 14m below. He placed an under cut in the branch then commenced the top part of the step cut, a 130mm diameter x 8.4m long section broke off and twisted as it broke. The resultant twist has caused it to unexpectedly fall into a smaller pine growing in the vicinity, the pine has altered the trajectory of the branch and it has contacted the HV as well as the LV on its decent. No injuries were sustained. Power supply was interrupted. No HVI occurred. | Conductor (bare) | 0 | 0 | 0 |  | drn23 | Vegetation: Trees Incident | Loss of supply | 28/04/2016 12:21 |  |  | 2263 |  |  | 20160428SPN_01 | Infrastructure (network-based) | -37.6115 | 145.2649 | 1 | AusNet Services Distribution | Report | 3002 | 0.012117 | 22kV AC | Essendon Airport | 3761 | St Andrews | Trees
A faults crew attended and disconnected supply to the lantern by a fuse at the base of the pole. The repair work was forwarded to the Downer Public Lighting Department for follow up action. | 9 TEAL COURT, HASTINGS VIC 3915 | LIS No. 9691910 | Unknown external/community factor | Unknown environment factor |  | Electrical breakdown;Overheated connection | Unknown work practice factor |  | 2 | Per CFA - pole and street light on fire and the fire is now out. A 80w MV lantern on a 7m pole (LIS No. 9691910) located in a park at the rear of 9 Teal Court, Hastings caught fire and was extinguished by a CFA crew. The cause of the asset fire was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause of the 80w MV lantern to catch on fire was unknown. | Pole-top fire | 17/03/2016 22:00 | 1 | Negligible: no ground fire | 2259 | Public space |  | 20160428UTD_01 | Infrastructure (network-based) | -38.2979 | 145.1749 | 1 | United Energy Distribution | Report | 2810 | 0.021801 | Low voltage AC (<1kV) | Moorabbin Airport | 3915 | Hastings | AF Other
A faults crew attended, isolated the substation and inserted LV parallels to temporary restore supply to customers. The HV lead and blue phase 11kV HV fuse unit with a 35.5amp powder filled fuse was replaced under Access Authority conditions. The transformer was energised and LV parallels removed to restore normal supply to customers supplied from the substation. | ROSEBERRY GROVE, GLEN HUNTLY VIC 3163 | LIS No. 2328150 | Unknown external/community factor | Wind;Heat |  | Overheated connection | Unknown work practice factor |  | 2 | Customers supplied from "Roseberry-Glenhuntly" substation advised of a loss of supply. The MFB called following reports from customers of a pole fire occurring at the substation. During warm and windy conditions, a HV transformer lead on the blue phase burnt off at the HV fuse unit at "Roseberry-Glenhuntly" pole type substation. | Powder filled;Equipment | 0 | 0 | 0 |  | CFD 24 | HV lead burnt off at the HV fuse unit - probable loose connection. | Pole-top fire;Loss of supply | 18/03/2016 9:05 | 1 | Negligible: no ground fire | 2261 | Roadway |  | 20160428UTD_03 | Infrastructure (network-based) | -37.8887 | 145.0397 | 1 | United Energy Distribution | Report | 2814 | 0.031058 | 11kV AC | Moorabbin Airport | 3163 | Glen Huntly | Connection
CEOT dispatched a fault crew to isolate, make safe and repair. The fault crew replaced the fuse, quarantined the fuse and reported to the DAO. | 805 NEERIM EAST ROAD, NEERIM EAST VIC 3831 | 2700180 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 220483, On arrival to Incd-96679-r for an All Supply Failure call the fault crew found that a EDO fuse had candled. | EDO fuse | 0 | 0 | 0 |  | wgl24 | Candled EDO fuse. | Other electricity related | 42706.4514 | 1 | Negligible: no ground fire | 869 | Agricultural |  | 20160214SPN_02 | Infrastructure (network-based) | -37.9848 | 145.9906 | 1 | AusNet Services Distribution | Report | 1296 | 0.0095266 | 22kV AC | Morwell (Latrobe Valley Airport) | 3831 | Neerim East | Fuse
Made safe | 13 STANLEY STREET, GLENROY VIC 3046 |  | Vehicle | [5 empty] | 2 | LV mains pulled down by garbage truck | Conductor (bare) | 0 | 0 | 0 |  |  | Truck contacted the LV conductors | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42706.2472 |  |  | 870 | Residential |  | 20160215JEM_01 | Infrastructure (network-based) | -37.7115 | 144.9149 | 1 | Jemena | Report | 1297 | 0.0067338 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Vehicle
Crew osilated supply and undertook repairs | 292 HOPKINS HIGHWAY, WARRNAMBOOL VIC 3280 |  |  |  |  | Fuse failed to eject |  |  | 1 | VicFire reported a pole and grass fire at the incident location. On arrival the crew found that a BA fuse had operated, however the barrel of the fuse had stayed in place and caught fire resulting in a ground fire (approx. 10m x 2m) on the road reserve. There was also minor fire damage caused to fencing. There were no reported injuries. | Boric acid | 0 | 0 | 0 |  |  | BA fuse did not drop out | Grassfire | 15/02/2016 19:23 | 1 | Small: 10 - 1000 sq.m | 872 |  |  | 20160216PWA_02 | Infrastructure (network-based) | -38.3486 | 142.507 | 1 | Powercor | Report | 1300 | 0.022721 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Fuse
Crew isolated supply and checked for damages - none found | 1745 STURT STREET, ALFREDTON VIC 3350 |  |  | Animal |  |  |  |  | 1 | A field crew attending an outage found that a possum had caused a flashover on a 22kV pole, bridging between a HV conductor and the BÃ˜ LV Conductor resulting in a High Voltage Injection affecting approximately 9 installations. Protection operated. There was no ground fire. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Animal Incident | HV injection | 15/02/2016 21:51 |  |  | 873 | Roadway |  | 20160216PWA_03 | Infrastructure (network-based) | -37.5514 | 143.8078 | 2 | Powercor | Report | 1315 | 0.028313 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Alfredton | Animal
Crew isolated supply and undertook repairs | LOT 2 DOHERTYS ROAD, TRUGANINA VIC 3029 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A developer reported that there was a pole fire and a ground fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 22kV crossarm causing the fuse mounting bracket to fall away from the crossarm and hang from the overhead line, resulting in a ground fire (Approx. 10sqm) on private property. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire | Grassfire | 18/02/2016 11:34 | 1 | Small: 10 - 1000 sq.m | 889 | Agricultural |  | 20160222PWA_01 | Infrastructure (network-based) | -37.8209 | 144.6997 | 1 | Powercor | Report | 3055 | 0.034649 | 22kV AC | Laverton Raaf | 3029 | Truganina | Crossarm
CEOT dispatched a fault crew to make safe, isolate and arrange for repairs. The PE Cell was burnt out on arrival, no other damage, no burn marks on ground or surrounding area. The PE Cell was replaced and the light was still found to be operational. | KILSYTH OVAL, KILSYTH VIC 3137 | 1005803 |  |  |  | Unknown technical factor |  |  | 2 | IMS 220567. Report of fire on AusNet Services' pole by a member of the public. The fire was actually contained to a faulty10 Amp PE cell on a Watchman type security light attached to a private pole at the Kilsyth football ground. The 10 Amp PE cell failed and melted. There was no apparent cause for the failure. | Public lighting | 0 | 0 | 0 |  | cyn13 | The fire was contained to the PE cell. No apparent cause. | Other electricity related | 18/02/2016 16:09 | 1 | Negligible: no ground fire | 891 | Public space |  | 20160222SPN_01 | Infrastructure (network-based) | -37.803 | 145.308 | 1 | AusNet Services Distribution | Report | 1324 | 0.032126 | Low voltage AC (<1kV) | Moorabbin Airport | 3137 | Kilsyth | AF Other
CEOT dispatched a fault crew to make safe, isolate and make any necessary repairs. The DAO attended on-site after receiving a call from the fault crew. The DAO took a number of photographs showing burn marks on the HV overhead conductors and he also took photographs of a number of machines parked underneath the HV overhead conductors. Upon close inspection of one of the excavators it appeared as though there were burn marks on top of the upper boom of which he also took photographs. The DAO spoke with one of the workers on-site, his name was John, who advised the DAO that on Monday 15/02/2016 a tip truck had dumped its load underneath the HV overhead conductors and made contact with the HV overhead conductors causing a fault which was recorded under SAP work order 110227484. The DAO had a conversation with John and explained to him the No Go Zone Rules and that the he had also taken photographs of the burn marks on the HV overhead conductor and on the boom of the excavator. The DAO asked John for the details of the Site Supervisor which he provided as Chris McMahon, tel. 0437 613726. The DAO then spoke with the Racecourse Manager, Brett Thompson, tel. 0418 388729 and arranged to set up a meeting with Chris on Monday morning at 8:00am to go through the No Go Zone Rules. The DAO also advised Brett that he would like the machinery to be left as it was for the weekend. On Monday 22/02/2016 at 8:00am the DAO met Chris McMahon on-site and went through the No Go Zone Rules of which he already had a copy. The DAI advised Chris that this was a serious incident that would probably be referred to WorkSafe Victoria and that we were lucky that no one was seriously injured or killed to which he agreed. The DAO also advised Chris that he would be receiving an invoice for the fault response on both Monday 15/02/2016 and Saturday 20/02/2016. Chris acknowledged all of the information that the DAO had provided to him. During the meeting The DAO left Chris with five copies of the No Go Zone Rules which he had printed out from the ESV website that morning. The DAO measured the HV conductor ground clearance height to be at 6.35m where the apparent burn marks appear. This ground clearance meets ESMS regulation height. SAP work orders 1100227484 and 110231030 are to be included in the recoverable works costs. Recoverable works charges to be sent to; Chris McMahon - 9 Holland Drive - Melton VIC 3337. Mobile 0437 613726. | 21 KOBYBOYN ROAD, SEYMOUR VIC 3660 | 4721193 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 220596. The DAO received a phone call from the Seymour fault crew advising that they were in attendance of a fault at the Seymour Racecourse where it appeared as though the HV overhead conductors may have been hit by an excavator between poles 4721193 and 4721194. When the DAO arrived on-site and discussed the incident with the fault crew they advised him that the contractors working at the racecourse had previously made contact with the HV overhead conductors on Monday 15/02/2016 when one HV fuse had operated. The DAO spoke with the Racecourse manager Brett Thompson (tel. 0418 388 729) to ensure that it was OK to drive through the racecourse to take photographs and inspect any damage that may have been caused to the overhead HV conductors. Brett advised that this was OK. Electrical protection operated - all three HV fuses operated on 20/2/2016. No injuries were sustained to any persons. | Conductor (bare) | 0 | 0 | 0 |  | smr8 | Overhead No Go Zones Rules breach. | No Go Zone (contact) | 20/02/2016 16:00 |  |  | 895 | Public space |  | 20160222SPN_02 | Infrastructure (network-based) | -37.0365 | 145.1664 | 1 | AusNet Services Distribution | Report | 1330 | 0.00539 | 22kV AC | Mangalore Airport | 3660 | Seymour | Vehicle
Crew isolated supply and undertook repairs | 44 UNION STREET, BRUNSWICK VIC 3056 |  | Working too close to overhead lines | [5 empty] | 2 | A contractor reported that they had contacted wires at the incident location. On arrival the crew found that contractor (Agostino Concrete & Excavations, mobile 0418 513 513) had been working at the site when their excavator contacted a LV service cable, resulting in the service cable being pulled off the pole and falling to the ground. There was no ground fire. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  |  | Excavator contact with LV service cable | No Go Zone (contact) | 15/02/2016 9:30 |  |  | 900 | Roadway |  | 20160223PWA_05 | Infrastructure (network-based) | -37.7737 | 144.9576 | 1 | CitiPower | Report | 1335 | 0.038858 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
Crew undertook repairs to secure site | 61 BOUVERIE STREET, CARLTON VIC 3053 |  | Vandalism;Theft | [5 empty] | 2 | A Building Manager from a nearby building reported that a door to a substation at the incident location has been vandalised. On arrival the crew found that the entrance door to substation had been damaged and that some clamps and connections had been stolen. The crew found some scrap metals and copper fittings inside and beside a car which was parked next to the substation (no registration plates on the vehicle). The incident was reported to Police. There was no interference with live parts of the substation found. There were no reported injuries or third party property damages. | Zone substation | 0 | 0 | 0 |  |  | Vandalism and theft | Damage to network assets | 16/02/2016 9:01 |  |  | 901 | Other | Substation | 20160223PWA_06 | Infrastructure (network-based) | -37.8053 | 144.9613 | 1 | CitiPower | Report | 1336 | 0.014461 | Not applicable | Essendon Airport | 3053 | Carlton | Other
Crew isolated supply and arranged repairs | 24 LICINA ROAD, BROOKFIELD VIC 3338 |  | Theft | [5 empty] | 2 | A customer reported that the customer mains has been damaged and stolen at the incident location. On arrival, the Powercor crew found that the LV customers mains cables had been pulled out from the pit and stolen by unknown third parties. There was also damage caused to the Powercor U/G assets. There were no reported injuries. | Cable;Customer installation | 0 | 0 | 0 |  |  | Theft | Less than $50k damage;Damage to network assets | 42706.4514 |  |  | 903 | Residential |  | 20160223PWA_08 | Infrastructure (network-based) | -37.6895 | 144.5403 | 1 | Powercor | Report | 1338 | 0.00043519 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
CEOT dispatched fault crew to isolate, make safe and repair. Fault crew replaced EDO fuse tube and re-energized substation. A work order is being raised to replace EDO fuse units with Boric Acid fuse units. | 430 MAFFRA-ROSEDALE ROAD, DENISON VIC 3858 | 2509328 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 220668. 6 Amp EDO fuse at substation Rosedale Road 39 burnt in half. No fire on pole, no fire on ground. | EDO fuse | 0 | 0 | 0 |  | mfa22 | EDO fuse burnt in half. | Other electricity related | 24/02/2016 7:26 | 1 | Negligible: no ground fire | 925 | Agricultural |  | 20160224SPN_04 | Infrastructure (network-based) | -38.028 | 146.8795 | 1 | AusNet Services Distribution | Report | 1364 | 0.023988 | 22kV AC | Morwell (Latrobe Valley Airport) | 3858 | Denison | Fuse
Crew isolated supply and undertook repairs | 352 RIVERSIDE EAST ROAD, RIVERSIDE VIC 3401 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 66kV pole, resulting in a ground fire (approx. 1 sqm) on the road reserve. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Grassfire | 25/02/2016 10:11 | 1 | Localised: less than 10 sq.m | 936 | Roadway |  | 20160226PWA_01 | Infrastructure (network-based) | -36.7289 | 142.2492 | 1 | Powercor | Report | 3062 | 0.0083715 | 66kV AC | Horsham Aerodrome | 3401 | Riverside | Pole
A faults truck attended and found LV conductors down on the corner of Hammond and Cahill Roads and all three LV fuses had operated at "Hammond N453-Cahill" substation. In addition, 4 bays of UE fibre optic cable were brought down by a truck with the boom extended. A HVI was suspected as a HV conductor may have clashed with the LV below and the faults crew requested a LEI attend as a HVI was suspected. The LEI attended and tested various electrical installations and confirmed that a high voltage injection did not occur. The faults crew made the site safe and fenced off the area after cutting the LV conductors away from the CHP. A Downer construction crew were dispatched to complete repairs and a Lend Lease crew are also on site to complete repairs to the United Energy optic fibre cable. As a result of the fibre optic cable being damaged, there are no protection alarms for FTN, LWN, CRM and MTN zone substations until the repairs are completed. The repairs were completed and three x LV 400amp HRC fuses at "Hammond N453-Cahill" substation were replaced after the LV conductors were sleeved and re-strained with supply restored upon completion. | 453-455 HAMMOND ROAD, DANDENONG SOUTH VIC 3175 |  | Working too close to overhead lines;Vehicle |  |  | Conductor clashing |  |  | 1 | At 0405hrs on 25/02/2016, wires are down per emergency services and 22kV feeder DVY 14 circuit breaker had successfully reclosed and held. The Victoria Police advised that wires are down outside 455 Hammond Road near Cahill Road, Dandenong South. A rubbish truck with its crane extended contacted the overhead cables that resulted in the neutral and red phase conductors being brought to the ground. Jesse Brien from the Dandenong Police was in attendance and provided details of the driver/operator. Company - Remondis Driver - Mick Day Address - 14 Lisa Place, Coolaroo Phone - 0409 236 085 | Conductor (bare);Communication cable/equipment | 0 | 0 | 0 |  | DVY 14 | A rubbish truck with its crane extended contacted the overhead cables. | Loss of supply | 26/02/2016 4:05 |  |  | 934 | Roadway |  | 20160226UTD_01 | Infrastructure (network-based) | -38.0276 | 145.2035 | 1 | United Energy Distribution | Report | 1374 | 0.030294 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Vehicle
A Downer construction crew attended to replace the damaged electrical infrastructure at the substation pole. it was observed the adjacent HV intermediate pole appeared to have pole fire damage as a detached charred piece of the HV crossarm was hanging down supported by the conductors. Further emergency high voltage switching was completed to minimise the number of customers affected and a Downer construction crew from Mornington proceeded to replace the damaged electrical infrastructure on the substation pole. A Keysborough crew completed the replacement of the HV intermediate pole. 24/02/2016 - The repairs were completed at approximately 2.05AM and the electricity supply was restored. The UE Fire Prevention Planning Manager commenced an investigation to inspect damage and possible causes, but no evidence remained on site. Without being able to inspect the powerline equipment, UE can only suggest two scenarios. 1. Substation Pole LIS No. 3321207 A possum on the substation pole may have navigated between phase and earth, killing the possum and generating sufficient phase to earth leakage current to produce sufficient localised heat to ignite the timber pole material. 2. HV Intermediate Pole LIS No. 3321208 The HV insulators may have failed to adequately insulate the powerline. The phase to earth leakage currents may have generated sufficient localised heat to ignite the timber pole material. | 1011 FRANKSTON-FLINDERS ROAD, SOMERVILLE VIC 3912 | LIS No. 3321207 and 3321208 |  | Wind;Heat |  | Unknown technical factor |  |  | 2 | The CFA issued an emergency warning as a result of a grass fire in Frankston-Flinders Road near Raymond Street, Somerville. 2.42PM - The CFA reported that a fast moving out of control grassfire was travelling in a southerly direction from Frankston-Flinders Road near Raymond Street, Somerville and have requested a section of 22kV HV feeder FSH 23 to be de-energised. A Downer faults crew attended and opened HV switch FS8034 located in Frankston-Flinders Road interrupting supply to 43 customers. The grass fire was extinguished by the CFA. It was estimated the area affected was approximately 5 hectares. 7.15PM - A Downer Duty Manager arrived on site and was met by Victoria Police. The substation pole (â€œFtn Flind P27 Gommsâ€) was cordoned off with police tape. On site at this time were John Kelleher and 3 other people that appeared to be Vic Police investigators along with Simon Oâ€™Leary from ESV. The Downer Duty Manager introduced himself and advised the police they were available to assist with their investigation. A dead possum was identified located at the base of the pole. The police quarantined all â€œfailedâ€ equipment including the deceased possum. | Pole (wood) | 0 | 0 | 0 |  | FSH 23 | No evidence has been made available to UE to conclude that either of the above causes contributed to the ignition of the ground fires. | Grassfire | 23/02/2016 17:15 | 1 | Medium: 1000 sq.m - 10 ha | 935 | Roadway |  | 20160226UTD_02 | Infrastructure (network-based) | -38.2203 | 145.1725 | 1 | United Energy Distribution | Report | 1376 | 0.023916 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Animal
Crew isolated supply and undertook repairs | 26 EGANS ROAD, HUNTLY VIC 3551 |  | Working too close to overhead lines | [5 empty] | 2 | A customer reported a wire down at the incident location. On arrival the crew found that an excavator was trenching for underground services to a sub division on the property and made contact with an LV overhead service cable, causing the cable to break and fall to the ground. There were no reported injuries. The service height was measured at 3.8m over the driveway. | Service conductor | 0 | 0 | 0 |  |  | Excavator contacted LV service cable | No Go Zone (contact);Damage to network assets | 18/02/2016 9:00 |  |  | 946 | Residential |  | 20160301PWA_03 | Infrastructure (network-based) | -36.6482 | 144.3445 | 1 | Powercor | Report | 1389 | 0.041035 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Huntly | Vehicle
Crew isolated supply and undertook repairs | 160 INGLIS ROAD, KATANDRA WEST VIC 3634 |  |  |  |  | Unknown technical factor |  |  | 2 | A customer reported a low conductor and fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a SWER pole due to the SWER conductor dislodging from the insulator, due to a broken insulator. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Broken insulator | Pole-top fire | 19/02/2016 14:00 | 1 | Negligible: no ground fire | 947 | Agricultural |  | 20160301PWA_04 | Infrastructure (network-based) | -36.2802 | 145.5491 | 1 | Powercor | Report | 2928 | 0.036582 | 12.7kV AC (SWER) | Shepparton Airport | 3634 | Katandra West | AF Other
Crew isolated supply and undertook repairs | 31-33 BEVERIDGE STREET, SWAN HILL VIC 3585 |  | Vehicle | [5 empty] | 2 | A customer reported that two trucks had struck a service wire at the incident location. On arrival the crew found that trucks ( which did not stop/not identified) had contacted an LV service cable. Upon inspection, no damage had been incurred to either the overhead service cable or the house point of attachment. There were no reported injuries. The cable height was measured at 4.5m above the kerb upon arrival and following repairs the cable height was measured at 5.5m at the kerb. | Service conductor | 0 | 0 | 0 |  |  | Crew did not determine a cause | No Go Zone (contact) | 18/02/2016 17:03 |  |  | 948 | Roadway |  | 20160301PWA_05 | Infrastructure (network-based) | -35.3351 | 143.5572 | 1 | Powercor | Report | 2917 | 0.040902 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Vehicle
Crew isolated supply and undertook repairs | 818-872 RYANS LANE, MELTON VIC 3337 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Fire Brigade reported a pole fire at the incident location. On arrival, the crew found that a pole fire had occurred on a 66kV/22kV pole which burnt the pole only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  |  | Pole fire | Pole-top fire | 19/02/2016 20:19 | 1 | Negligible: no ground fire | 949 | Roadway |  | 20160301PWA_06 | Infrastructure (network-based) | -37.6506 | 144.6204 | 1 | Powercor | Report | 1392 | 0.0034954 | 22kV AC;66kV AC | Melbourne Airport | 3337 | Melton | Pole
Crew isolated supply and undertook repairs | 51 BOORCAN ROAD, BOORCAN VIC 3265 |  |  |  |  | Mechanical breakdown;Unknown technical factor |  |  | 1 | A field crew reported a ground fire start at the incident location. A crew advise while operating a live line clamp, for a planned outage, a 22kV conductor broke and fell to the ground, resulting in a ground fire (Approx. 60 sqm) on the road reserve. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Broken 22kV conductor | Grassfire | 24/02/2016 9:23 | 1 | Small: 10 - 1000 sq.m | 960 | Roadway |  | 20160302PWA_08 | Infrastructure (network-based) | -38.2097 | 143.0128 | 1 | Powercor | Report | 1403 | 0.017059 | 22kV AC | Warrnambool Airport Ndb | 3265 | Boorcan | Conductor
Crew undertook repairs | 454 SYDNEY ROAD, BRUNSWICK VIC 3056 |  |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire at the incident location. On arrival the crew found that an Low Voltage Insulated Piercing Connectors (IPC) had overheated resulting in burning of the IPC which self-extinguished. There was no ground fire. There were no reported injuries or third party property damages. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Pole-top fire | 24/02/2016 15:12 | 1 | Negligible: no ground fire | 970 | Roadway |  | 20160303PWA_09 | Infrastructure (network-based) | -37.7674 | 144.9623 | 1 | CitiPower | Report | 1413 | 0.011418 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
Crew isolated supply and checked for damages. Third party cable company to undertake repairs | 2 YORK STREET, BALLARAT VIC 3350 |  |  | Bird |  |  |  |  | 1 | Vic Fire reported wires down across the road arcing and sparking at the incident location. On arrival the crew found that a magpie had caused flashover resulting in a a HV Injection on a 22kV pole, which caused the Neighbourhood cable catenary to break and fall to the ground on the nature strip. There was no ground fire. Protection operated. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | HV injection | 42372.8785 |  |  | 975 | Roadway |  | 20160303PWA_13 | Infrastructure (network-based) | -37.5707 | 143.8654 | 1 | Powercor | Report | 1418 | 0.026388 | 22kV AC | Ballarat Aerodrome | 3350 | Ballarat | Animal
Crew isolated supply and undertook repairs | 1 GOROKE-HARROW ROAD, HARROW VIC 3317 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole, which burnt the cross arm causing the blue phase side of the cross arm and the conductor fall to the ground. There was no ground fire. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  |  | crossarm fire | Pole-top fire | 24/02/2016 20:01 | 1 | Negligible: no ground fire | 976 | Roadway |  | 20160303PWA_14 | Infrastructure (network-based) | -37.0951 | 141.5948 | 1 | Powercor | Report | 3058 | 0.029404 | 22kV AC | Horsham Aerodrome | 3317 | Harrow | Crossarm
Crew isolated supply and arranged repairs | 3A THOROUGHBRED AVENUE, WERRIBEE VIC 3030 |  |  |  |  | Unknown technical factor |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a kiosk substation had caught fire, resulting in a fire behind the closed doors of the kiosk substation. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. The cause was unable to be determined. | Pad mounted equipment/kiosk | 0 | 1 | 0 |  |  | Cause unable to be determined | Other electricity related | 26/02/2016 2:46 | 1 | Negligible: no ground fire | 977 | Roadway |  | 20160303PWA_15 | Infrastructure (network-based) | -37.9092 | 144.6328 | 1 | Powercor | Report | 1420 | 0.032701 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | AF Other
Crew isolated supply and undertook repairs | 4 DEHNERTS ROAD, DAISY HILL VIC 3465 |  |  | Within clearances |  |  |  |  | 1 | Customer reported a wire down at the incident location. On arrival the crew found that a tree had been cut by contractors (Brian Dawson â€“ 0439 537 446 â€“ Tree cutter) working for the customers and had fallen onto the adjacent 22kV line causing one of the conductors to break and fall to the ground. The contractors advised a gust of wind caused the tree they were felling to fall towards the conductor. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Damage to network assets | 27/02/2016 10:15 |  |  | 983 | Roadway |  | 20160303PWA_20 | Infrastructure (network-based) | -37.1014 | 143.7258 | 1 | Powercor | Report | 3064 | 0.023728 | 22kV AC | Ballarat Aerodrome | 3465 | Daisy Hill | Trees
The crew isolated supply and undertook repairs. | 113 ARTHURTON ROAD, NORTHCOTE VIC 3070 |  | Working too close to overhead lines | [5 empty] | 2 | A customer advised that a truck had contacted an overhead LV service wire at the above location. Upon arrival the crew found that an LV service had been damaged. The crew made the site safe and undertook repairs. There were no reported injuries or property damage | Service conductor | 0 | 0 | 0 |  |  | An unknown truck contacted overhead LV service wire. | Damage to network assets | 26/02/2016 11:13 |  |  | 985 | Roadway |  | 20160303PWA_22 | Infrastructure (network-based) | -37.7683 | 144.9893 | 1 | CitiPower | Report | 8008 | 0.016898 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
the crew isolated supply and undertook repairs. | 10 HAZEL STREET, LORNE VIC 3232 |  |  |  |  | Fuse failed to eject |  |  | 1 | VicFire reported a pole and grass fire at the incident location. On arrival the crew found that an EDO fuse had operated however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There were no reported injuries or third party property damages. There was no ground fire. | EDO fuse | 0 | 0 | 0 |  |  | EDO fuse barrel did not drop out. | Other electricity related | 29/02/2016 18:03 | 1 | Negligible: no ground fire | 989 | Roadway |  | 20160303PWA_23 | Infrastructure (network-based) | -38.5192 | 143.9886 | 1 | Powercor | Report | 3066 | 0.0029884 | 22kV AC | Avalon Airport | 3232 | Lorne | Fuse
Crew isolated supply and undertook repairs. | 250 FORSYTH ROAD, MURRAYVILLE VIC 3512 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A property owner reported a fire on a pole and wires hanging at incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole causing the cross-arm to break and remain supported by the cross arm straps. There were no ground fire. No reported injuries or third party damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross arm fire | Pole-top fire | 42403.5917 | 1 | Negligible: no ground fire | 1000 | Roadway |  | 20160307PWA_03 | Infrastructure (network-based) | -35.2403 | 141.2233 | 1 | Powercor | Report | 3070 | 0.023344 | 22kV AC | Mildura Airport | 3512 | Murrayville | Crossarm
Crew isolated supply and undertook repairs | 39 GEODETIC ROAD, VECTIS VIC 3401 |  | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | An onsite worker reported that a crane had contacted high voltage conductors at the incident location. On arrival the crew found that a contractor Millers Civil Contractors contact Jay Miller 0417 548 650 was operating a crane being used to extract water out of a dam had hit the roadside conductor and pushed it into the center phase conductor approximately mid span on a 22kV three phase overhead line. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. The height of the high voltage cables was measured at 6.7m at point of contact. | Conductor (bare) | 0 | 0 | 0 |  |  | A crane contacted 22kV conductors. | No Go Zone (contact) | 42463.6417 |  |  | 1002 | Agricultural |  | 20160307PWA_04 | Infrastructure (network-based) | -36.6938 | 142.1685 | 1 | Powercor | Report | 3075 | 0.014752 | 22kV AC | Horsham Aerodrome | 3401 | Vectis | Vehicle
Crew isolated supply and undertook repairs. | 173 MCINTYRE ROAD, SUNSHINE NORTH VIC 3020 |  | Vehicle | [5 empty] | 2 | A passer-by reported wires down across the road at the incident location. On arrival the crew found that a four core low voltage service had fallen down after the service pole was struck by an unknown vehicle. There were no reported injuries or third party damages. | Service conductor | 0 | 0 | 0 |  |  | Unknown truck contacted power pole. | Damage to network assets | 42463.4014 |  |  | 1003 | Roadway |  | 20160307PWA_05 | Infrastructure (network-based) | -37.7601 | 144.8316 | 1 | Powercor | Report | 3087 | 0.0051134 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
Crew isolated supply and undertook repairs | 147 SWAN STREET, RICHMOND VIC 3121 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that an IPC connection had overheated causing the IPC to catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connector/termination | 0 | 0 | 0 |  |  | Overheated connection | Pole-top fire | 42463.4743 | 1 | Negligible: no ground fire | 1005 | Roadway |  | 20160307PWA_06 | Infrastructure (network-based) | -37.8253 | 144.9961 | 1 | CitiPower | Report | 8009 | 0.0085706 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Connection
CEOT dispatched a fault crew to isolate, make safe and repair. The fault crew isolated substation ISLAND RD P15 and organized repairs to be made. A new LV service cable was installed and the LV conductor was spliced. Supply restored. A No Go Zone Rules warning letter is being sent to the excavator operator to warn of the hazards involved in working in the vicinity of overhead wires. | 170 ISLAND ROAD, KOO WEE RUP VIC 3981 | 516403 | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | IMS 220857. An excavator with raised bucket working in the vicinity of a drainage channel on the road reserve contacted an overhead LV XLPE service cable which also brought a LV conductor to the ground. Excavator operator details: Marty Grogan. Address: â€˜The Oaksâ€™ 185 Oakview Lane, Nar Nar Goon. Mobile: 0419 532 224. As it was a LV electrical protection would not have operated due to the high impedance fault. | Service conductor | 0 | 0 | 0 |  | phm12 | 3rd party excavator contacted overhead service cable. | No Go Zone (contact) | 42463.6785 |  |  | 1008 | Agricultural |  | 20160308SPN_01 | Infrastructure (network-based) | -38.1659 | 145.4631 | 1 | AusNet Services Distribution | Report | 1459 | 0.032197 | Low voltage AC (<1kV) | Moorabbin Airport | 3981 | Koo Wee Rup | Vehicle
The damaged 3 phase service was replaced with 35m of XLPE service cable. The installation was tested upon completion and supply was left on. | 294 CLAYTON ROAD, CLAYTON VIC 3168 | LIS No. 0637390 |  | Heat |  | Overheated connection |  |  | 2 | Per MFB - fire from wire attached to building. On a very warm day, a three phase 4 wire service failed after it blew up at the termination below the junction box at the shop frontage above the veranda at 294 Clayton Road near Dunstan Street. The service was attached to pole No. LIS 0637390 and the cause was suspected to be overload. | Conductor (insulated) | 0 | 0 | 0 |  |  | The cause was suspected to be overload. | Other electricity related | 42553.375 | 1 | Negligible: no ground fire | 1010 | Commercial |  | 20160308UTD_01 | Infrastructure (customer connection) | -37.9254 | 145.1199 | 1 | United Energy Distribution | Report | 1462 | 0.022373 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Connection
Crew isolated supply and arranged repairs. Jemena advised that repairs to Jemema assets also required. | 92 NAPIER STREET, GISBORNE SOUTH VIC 3437 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | CFA reported a fire at the incident location. On arrival the crew found that a crossarm fire had occurred on a 66kV/22kV pole causing the arm to break and fall contacting a LV service cable attached to house pulling a barge board off the house. The incident also resulted in a ground fire (Approx. 100 sqm) at the base of the pole. There were no reported injuries. PAL 66kV pole carrying Jemena HV & LV assets. | Crossarm (wood) | 0 | 0 | 1 | Jemena 22kV and LV |  | Crossarm fire | Grassfire | 42554.8028 | 1 | Small: 10 - 1000 sq.m | 1012 | Roadway |  | 20160309PWA_01 | Infrastructure (network-based) | -37.5587 | 144.6628 | 1 | Powercor | Report | 2781 | 0.004662 | 66kV AC | Melbourne Airport | 3437 | Gisborne South | Crossarm
The attending LEI called for a service truck to replace the street crossing with a new cable. Voltage tests between an independent earth and various points of the electrical installation detected zero volts after cable was replaced. | UNIT 2 121 BRIDGE STREET, BENDIGO VIC 3550 |  |  |  |  | Fault on customer installation |  |  | 2 | Mrs Williamson was having a shower when she received an electric shock from the metallic shower head. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a severely corroded neutral screen of an aluminium neutral screened service cable as the cause of the high impedance associated with the return path of the neutral current. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 35 volts on the water piping system. Mrs Williamson was having a shower when she received an electric shock from the metallic shower head. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a severely corroded neutral screen of an aluminium neutral screened service cable as the cause of the high impedance associated with the return path of the neutral current. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 35 volts on the water piping system. | Service conductor | 0 | 0 | 0 |  |  | Neutral Screen of service cable | Minor shock | 42432.1042 |  |  | 1027 | Residential |  | 20160309PWA_16 | Infrastructure (network-based) | -36.7481 | 144.2875 | 1 | Powercor | Report | 3074 | 0.0099965 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | OH Cable
The attending Powercor Fault Crew replaced the existing Four Wire O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Group Meter location, Neutral Bar at the Occupiers Main Switchboard, metallic water pipe system, distribution assets and between the points of contact, confirmed 0.9 Volts following replacement of the O/H Service Cable. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the main earth indicated zero amps in the main earthing system. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 49 MERVYN STREET, NEWTOWN VIC 3220 |  |  |  |  | Corrosion |  |  | 2 | Ms Andrea Tankard was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Junction Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 12.0 Volts on the water piping system and between the points of contact. | Service conductor | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral Conductor termination at the Junction Box located on the Reticulation Pole. | Minor shock | 42403.625 |  |  | 1028 | Residential |  | 20160309PWA_17 | Infrastructure (network-based) | -38.1568 | 144.3405 | 1 | Powercor | Report | 1483 | 0.013406 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | Connection
crew isolated supply and undertook repairs. | BROUGHAM HEIGHTS, 49 BROUGHAM STREET, NORTH MELBOURNE VIC 3051 |  | Working too close to underground cables | [5 empty] | 0 | An onsite worker reported that they have contacted low voltage mains cables during works to install conduits for T.P.G, at the incident location. On arrival the crew found that a Contractor (Elliot Smale, mobile 0418 361 223. CT Civil, 51 Commercial Drive, Thomastown). had contacted a live low voltage underground service while using an excavator to trench in the footpath, resulting in damaged low voltage service and conduit. | Services cable | 0 | 0 | 0 |  |  | Contractor damaged an Low Voltage service cable. | No Go Zone (contact) | 42585.4792 |  |  | 1030 | Residential |  | 20160309PWA_19 | Infrastructure (network-based) | -37.7938 | 144.9437 | 1 | CitiPower | Report | 8013 | 0.025028 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected and the HV and LV crossarms were replaced under Access Authority conditions prior to the supply being restored. | 201 WELLINGTON ROAD, CLAYTON VIC 3168 | LIS No. 0613707 |  | Precipitation |  | Electrical breakdown;Insulator |  |  | 2 | Customer called and advised the pole across the road is sparking and called the fire brigade. The customer mentioned a fire was evident. The MFB attended and patrolled the area but were unable to locate any fires but requested that a further assessment is made in daylight by a faults crew. The faults crew identified that a pole fire had occurred at pole No. LIS 0613707 that is located on the corner of Wellington and Nantilla Roads, Mulgrave. A burnt section of the HV timber crossarm fall onto the LV crossarm and the faults crew requested a LEI to attend and check premises for damage. The LEI attended and confirmed that a HVI did not occur. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | SV 23 | Pole fire after light rain. | Pole-top fire | 42432.2701 | 1 | Negligible: no ground fire | 1037 | Roadway |  | 20160310UTD_04 | Infrastructure (network-based) | -37.9173 | 145.1494 | 1 | United Energy Distribution | Report | 1493 | 0.03511 | 22kV AC | Moorabbin Airport | 3168 | Clayton | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was replaced under Access Authority conditions prior to the supply being restored. | 178 BUCKLEY STREET, NOBLE PARK VIC 3174 | LIS No. 017285 |  | Bird |  | Electrical breakdown;Insulator |  |  | 1 | At 1441hrs on 03/03/2016, 22kV feeder NP 24 circuit breaker reclosed to lockout affecting 1598 customers. Following light drizzle after a long dry spell, the road side HV helical termination (wrap on) failed due to the HV insulator being damaged - cause unknown but possibly caused by a bird but there was no evidence. Molten metal fell into the dry grass below and a small 3sqm fire started that was quickly extinguished. | Conductor (bare);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | NP 24 | Bird Incident | Grassfire | 42432.6951 | 1 | Negligible: no ground fire | 1042 | Roadway |  | 20160310UTD_07 | Infrastructure (network-based) | -37.9796 | 145.1718 | 1 | United Energy Distribution | Report | 1498 | 0.024681 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | AF Other
Crew made site safe and undertook repairs. | 386 FLINDERS LANE, MELBOURNE VIC 3000 |  | Working too close to underground cables | [5 empty] | 2 | An on-siteworker contacted CitiPower to advise a building contractor (Simon Jaques of LinkHill Pty Ltd) had drilled through a live electrical cable at 386 Flinders Lane on the incident date. Mr Jaques received a shock and burns to both hands and was taken to hospital via ambulance. He was discharged the following day. On arrival the crew found an exposed LV cable running from LV switching station 376 FLINDERS ST and the road reserve. The crew isolated supply and undertook repairs. There was no reported third party property damages. | Cable | 0 | 0 | 0 |  | TP003 | Contractor drilled into live low voltage underground cable. | Medical attention (first aid/doctor/hospital) | 42616.6861 |  |  | 1051 | Construction |  | 20160315PWA_01 | Infrastructure (network-based) | -37.818 | 144.9612 | 1 | CitiPower | Report | 1583 | 0.010141 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
Crew isolated supply and undertook repairs. | 135-147 WESTCOTT PARADE, ROCKBANK VIC 3335 |  |  |  |  | Overheated connection |  |  | 1 | VicFire reported wires sparking in Westcott Parade opposite caravan park at the incident location. On arrival the crew found that LV Transformer leads from the LV Bushings to the LV Tx Fuses had overheated and shorted out inside the 40mm conduit running down the pole which had caused hot debris to fall to the ground resulting in a ground fire (approx. 0.5m x 0.5m) on the road reserve at the base of the pole. The fire self-extinguished as there was light drizzle present at the time of the incident. Protection operated. There were no reported injuries, or third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Overheated Transformer leads. | Loss of supply | 13/03/2016 6:45 |  |  | 1052 | Roadway |  | 20160315PWA_02 | Infrastructure (network-based) | -37.7308 | 144.6588 | 1 | Powercor | Report | 3107 | 0.020959 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Connection
Crew isolated supply and undertook repairs. | 13 MOCKRIDGE DRIVE, KANGAROO FLAT VIC 3555 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | A customer reported a fire at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole. No Protection operated. There was no ground fire. There were no reported injuries or third party property damages | Conductor (bare) | 0 | 0 | 0 |  |  | Cross arm fire on 22kV cross arm. | Pole-top fire | 42616.8743 | 1 | Negligible: no ground fire | 1053 | Roadway |  | 20160315PWA_03 | Infrastructure (network-based) | -36.7885 | 144.2318 | 1 | Powercor | Report | 3096 | 0.001772 | 22kV AC | Bendigo Airport | 3555 | Kangaroo Flat | Crossarm
Crew isolated supply and undertook repairs. | 16 LASCELLES STREET, HOPETOUN VIC 3396 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 2 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a Cross-arm fire had occurred on a 22kV intermediate pole at the incident location. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross arm fire on 22kV feeder. | Pole-top fire | 42646.2951 | 1 | Negligible: no ground fire | 1054 | Roadway |  | 20160315PWA_04 | Infrastructure (network-based) | -35.7225 | 142.3619 | 1 | Powercor | Report | 3102 | 0.0086979 | 22kV AC | Horsham Aerodrome | 3396 | Hopetoun | Crossarm
A faults truck attended and isolated supply to complete repairs and the blue phase 400amp single krone switch was replaced. Upon completion, supply was restored to the North Concourse circuit. | 51 RESERVE ROAD, BEAUMARIS VIC 3193 | LIS No. 1811769 |  | Heat |  | Overheated connection |  |  | 2 | The MFB advise there is a ground fire opposite 51 Reserve Road, Beaumaris. The blue phase LV fused 400amp krone switch at "Reserve-North Concourse" substation overheated that caused molten plastic to fall into wood chips at the base of the pole and a small fire to start that was quickly extinguished by the MFB. The krone switch supplied the North Concourse circuit that had a load of 270amps with 315amp Din fuses for protection. The cause was unknown but it could be attributed to a loose overheated connection. Pole No. LIS 1811769. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but it could be attributed to a loose overheated connection. | Pole-top fire | 42707.0139 | 1 | Localised: less than 10 sq.m | 1050 | Roadway |  | 20160315UTD_02 | Infrastructure (network-based) | -37.9864 | 145.0326 | 1 | United Energy Distribution | Report | 1509 | 0.011985 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Beaumaris | Connection
Made safe | 23 OVATA DRIVE, TULLAMARINE VIC 3043 |  |  | Heat;Cold |  | Leakage |  |  | 2 | Pole fire | Pole top | 0 | 0 | 0 |  |  | Leakage and weather conditions | Pole-top fire | 18/03/2016 3:15 | 1 | Negligible: no ground fire | 1068 | Industrial |  | 20160321JEM_01 | Infrastructure (network-based) | -37.7095 | 144.8648 | 1 | Jemena | Report | 1533 | 0.039433 | 22kV AC | Essendon Airport | 3043 | Tullamarine | Pole
Crew isolated supply and undertook repairs. | 15-17 SUTHERLAND STREET, STAWELL VIC 3380 |  | Working too close to underground cables | [5 empty] | 2 | A Shire Council employee rang to advise while digging in Sutherland St, Stawell, near lake oval, they have exposed a Low Voltage underground conduit at the incident location. When the crew arrived they found the conduit damaged but cable intact with supply still on to premises. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  |  | Council workers struck underground conduit. | No Go Zone (contact) | 17/03/2016 10:36 |  |  | 1077 | Roadway |  | 20160322PWA_01 | Infrastructure (network-based) | -37.0668 | 142.7695 | 1 | Powercor | Report | 3113 | 0.0012083 | Low voltage AC (<1kV) | Horsham Aerodrome | 3380 | Stawell | Dug up
Crew isolated supply and undertook repairs. | 29 DERWENT DRIVE, LONG GULLY VIC 3550 |  |  |  |  | Neutral fault |  |  | 0 | Vicfire reported that a fire on POA box had occurred at the incident location. On arrival the crew found that a Neutral screen LV service cable had burnt off at the roller end at the customers point of attachment, the cable remained energised until fault crew facilitated isolation of the service at the pole. There were no reported injuries, no ground fire, no 3rd party property damages. | Service conductor | 0 | 0 | 0 |  |  | Neutral screen LV service cable had burnt off at the roller end at the customers point of attachment | Property | 15/03/2016 22:10 | 2 | Negligible: no ground fire | 1078 |  |  | 20160322PWA_02 | Infrastructure (network-based) | -36.7502 | 144.2565 | 1 | Powercor | Report | 1544 | 0.0071736 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Long Gully | OH Cable
Crew isolated supply and undertook repairs. | 35 FAIRBAIRN ROAD, TOORAK VIC 3142 |  |  | Fallen |  |  |  |  | 0 | Passers-by reported that a large tree has fallen and bought down power lines at the incident location. On arrival the crew found that a large tree had had fallen across power lines, resulting live conductors hanging within reach of the public. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/03/2016 10:58 |  |  | 1079 | Roadway |  | 20160322PWA_03 | Infrastructure (network-based) | -37.8455 | 145.0087 | 1 | CitiPower | Report | 8017 | 0.013137 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the large tree branch was removed. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 7 CAMPBELL COURT, BALNARRING BEACH VIC 3926 |  |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1303hrs on 18/03/2016, 22kV feeder MTN 32 circuit breaker reclosed to lockout affecting 3218 customers. During strong gusty winds, a large private tree branch from a property in Campbell Court, Balnarring Beach contacted the 22kV overhead conductors that resulted in a HV conductor to contact the LV conductors below near the corner of Sidney Street. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Sidney-Campbell" substation. The LEI confirmed a high voltage injection occurred (MOR 1603) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium;Customer installation | 0 | 0 | 0 |  | MTN 32 | Vegetation: Trees Incident | HV injection;Loss of supply | 18/03/2016 13:03 |  |  | 1085 | Residential |  | 20160322UTD_03 | Infrastructure (network-based) | -38.3882 | 145.1219 | 1 | United Energy Distribution | Report | 1552 | 0.018455 | 22kV AC | Moorabbin Airport | 3926 | Balnarring Beach | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the large tree branch was removed. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 475 BALCOMBE ROAD, BEAUMARIS VIC 3193 | LIS No. 1812025 |  | Blown branch/vegetation |  | Conductor clashing;HV injection;Fault on customer installation |  |  | 1 | At 1654hrs on 18/03/2016, 11kV feeder BR 06 circuit breaker reclosed to lockout affecting 1169 customers. During strong gusty winds, a large private tree branch from a property at 475 Balcombe Road contacted the 11kV overhead conductors that caused a HV conductor to contact the LV conductors below near pole No. LIS 1812025. A faults crew attended and requested that a LEI investigate for damage as a HVI was suspected to customers supplied from "Hepburn-Fairleigh" substation. The LEI confirmed a high voltage injection occurred (KEY 1603) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium;Customer installation | 0 | 0 | 0 |  | BR 06 | Vegetation: Trees Incident | HV injection;Loss of supply | 18/03/2016 16:54 |  |  | 1091 | Roadway |  | 20160322UTD_04 | Infrastructure (network-based) | -37.9774 | 145.0303 | 1 | United Energy Distribution | Report | 1558 | 0.0071597 | 11kV AC | Moorabbin Airport | 3193 | Beaumaris | Trees
The faults crew installed a spreader on the LV overhead conductors and ensured the site was made safe. | 22 FORSTER STREET, NOBLE PARK VIC 3174 |  |  | Blown branch/vegetation |  | Conductor clashing |  |  | 2 | The MFB reported that powerlines are clashing outside this property. During gusty winds, LV overhead conductors opposite 22 Forster Street, Noble Park were clashing after branches from a large customers tree was making contact. The clashing caused molten metal to fall into dry grass and fallen leaves below, and a fire that was estimated to be approximately 10m x 15m to start. The fire damaged a customers garden fence and shed. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 15/03/2016 16:45 | 1 | Small: 10 - 1000 sq.m | 1094 | Residential |  | 20160322UTD_05 | Infrastructure (network-based) | -37.9601 | 145.1658 | 1 | United Energy Distribution | Report | 1562 | 0.026984 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Trees
Crew isolated supply and undertook repairs | KALIMNA TEXEL STUD, 2116 WAITCHIE ROAD, WAITCHIE VIC 3544 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A field crew attending an outage found that a cross-arm fire had occurred on a 22kV pole which burnt the crossarm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross-arm fire | Pole-top fire | 42645.5632 | 1 | Negligible: no ground fire | 1096 | Agricultural |  | 20160323PWA_01 | Infrastructure (network-based) | -35.3653 | 143.1096 | 1 | Powercor | Report | 1564 | 0.026756 | 22kV AC | Swan Hill Aerodrome | 3544 | Waitchie | Crossarm
Crew isolated supply and undertook repairs. | 550 BAMAWM HALL ROAD, BAMAWM VIC 3561 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 0 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a cross-arm fire had occurred on a 22kV pole. There was no ground fire. There were no reported injuries and no third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross-arm fire on 22kV power-line | Pole-top fire | 18/03/2016 6:47 | 1 | Negligible: no ground fire | 1099 | Roadway |  | 20160323PWA_04 | Infrastructure (network-based) | -36.2419 | 144.5872 | 1 | Powercor | Report | 3131 | 0.014986 | 22kV AC | Bendigo Airport | 3561 | Bamawm | Crossarm
The attending service crew isolated the supply by removing the service fuses at pole no. 11140. A faults crew were notified to follow up and remove the customer mains in the affected pit. The LEI performed a voltage test to an independent earth and could not confirmed the presence of voltage at the customer's consumer's mains because AusNet Services' workers had disconnected the effected cables before his arrival.Site was left in safe condition. A defect notice was not required as the customer's mains will not be re-instated. Installation left OFF supply. Site was left in a safe condition. Defect notice not required as the customer mains will not be re-instated. Installation left OFF supply. | 100 JEFFERSON ROAD, GARFIELD VIC 3814 | 11140 | Working too close to underground cables |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 220684. A civil works contractor was grading the road and cut through the customer's underground consumer mains supplying 39A Jefferson Rd, Garfield. The mains were thought to be dead and were moved over to the side of the road. A water gun operator stepped on the exposed cable end and received an electric shock to his foot. This condition caused current flow from the active of the consumer's mains, to flow through the wet boot into the general mass of earth and returned to the substation. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, did not reveal any voltage on the severed underground cables because AusNet Services' workers had disconnected the supply at the Mains Fuse Box located at pole no.11140 prior to AusNet Services' LEIâ€™s arrival to site. | Customer installation | 0 | 0 | 0 |  | wgl12 | A civil contractor operating a grader dug up underground consumer's mains cable in road reserve adjacent to property boundary. | Minor shock | 24/02/2016 15:00 |  |  | 1101 | Agricultural |  | 20160323SPN_01 | Infrastructure (network-based) | -38.0849 | 145.684 | 1 | AusNet Services Distribution | Report | 1569 | 0.022525 | Low voltage AC (<1kV) | Moorabbin Airport | 3814 | Garfield | Dug up
Crew isolated supply and undertook repairs | 2-14 DOHERTYS ROAD, ALTONA NORTH VIC 3025 |  | Working too close to overhead lines | [5 empty] | 1 | A fault crew attending a fault found that an excavator working nearby made contact with a 22kV line at the incident location. Protection operated. There were no reported injuries, fire or third party damages. Contractor MultiPro Civil Excavator operator: Howard Rourke 0409 932 320, Manager: Russell Bourke 0400 695 554 (Multi Pro Civil) | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator made contact with HV power line resulting in some damage to a conductor. | No Go Zone (contact) | 24/03/2016 10:41 |  |  | 1103 | Commercial |  | 20160329PWA_01 | Infrastructure (network-based) | -37.831 | 144.8228 | 1 | Powercor | Report | 2865 | 0.019576 | 22kV AC | Laverton Raaf | 3025 | Altona North | Vehicle
Crew isolated supply and undertook repairs. | 5 WALLIS STREET, DELACOMBE VIC 3356 |  | Theft | [5 empty] | 2 | A customer reported that the earth cables on the Substation pole at the incident location had been stolen. Upon arrival the crew found that approx. 1m of the HV earth, and approx. 0.5m of the LV earth cable had been stolen. There were no reported injuries, ground fire or third party damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Theft of earth cables | Damage to network assets | 29/03/2016 10:28 |  |  | 1112 | Roadway |  | 20160329PWA_08 | Infrastructure (network-based) | -37.5723 | 143.8219 | 1 | Powercor | Report | 1584 | 0.039353 | 22kV AC | Ballarat Aerodrome | 3356 | Delacombe | Other
Crew isolated supply and undertook repairs | 196-228 GREIGS ROAD, ROCKBANK VIC 3335 |  | Theft | [5 empty] | 2 | A contractor reported that a cable covering and the cable on the pole at incident location has been cut away. Upon arrival, the Powercor crew found that the UG service cable had been stolen from the pole up to the pit. The conduit on the pole also damaged. There were no reported injuries or third parrty property damages. | Services cable | 0 | 0 | 0 |  |  | Theft of underground cable | Damage to network assets | 29/03/2016 11:07 |  |  | 1114 | Roadway |  | 20160330PWA_01 | Infrastructure (network-based) | -37.7451 | 144.6738 | 1 | Powercor | Report | 1586 | 0.028655 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Crew isolated supply and undertook repairs | 16 ENDEAVOUR DRIVE, TORQUAY VIC 3228 |  | Working too close to underground cables | [5 empty] | 0 | Contractor (Barwon Water, Ph 03 5226 9189, 155 Mercer St, Geelong) reported that they have contacted UG cables during works to install fire hydrant, at the incident location. On arrival the crew found that the contractor had contacted a live street light underground service while excavating, resulting in damaged low voltage service. There were no reported injuries or third party property damages. | Public lighting | 0 | 0 | 0 |  |  | contractor had contacted a live street light underground service while excavating, resulting in damaged low voltage service. The contractor had all paperwork on site but had not interpreted the plans correctly | No Go Zone (contact) | 29/03/2016 10:30 |  |  | 1115 |  |  | 20160330PWA_02 | Infrastructure (network-based) | -38.3186 | 144.3306 | 1 | Powercor | Report | 1587 | 0.039751 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Dug up
Crew isolated supply and undertook repairs | 2140 EURAMBEEN-STREATHAM ROAD, STONELEIGH VIC 3373 |  | Caused by REC/contractor | Fire |  |  |  |  | 1 | A customer reported a neighbour was doing a paddock burn and a pole was burnt to the ground at the incident location. On arrival the crew found that a pole had been burnt at the base of the pole resulting in a 12.7 kV SWER pole falling to the ground. Protection operated. There were no reported injuries or third party damage. | SWER conductor | 0 | 0 | 0 |  |  | fire in paddock commenced by farmer | Loss of supply | 25/03/2016 18:08 |  |  | 1116 | Agricultural |  | 20160330PWA_03 | Infrastructure (network-based) | -37.5541 | 143.1709 | 1 | Powercor | Report | 3196 | 0.0060139 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3373 | Stoneleigh | Other
crew isolated supply and undertook repairss | CHINKAPOOK-NYAH WEST ROAD, CHINKAPOOK VIC 3546 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A customer reported a fire at the incident location. On arrival the crew found that a Cross-arm fire had occurred on a 22kV pole, resulting in a scorched small tree on road reserve. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Cross-arm fire | Pole-top fire | 25/03/2016 9:25 | 1 | Negligible: no ground fire | 1117 | Roadway |  | 20160330PWA_04 | Infrastructure (network-based) | -35.178 | 143.0709 | 1 | Powercor | Report | 3166 | 0.020503 | 22kV AC | Swan Hill Aerodrome | 3546 | Chinkapook | Crossarm
CEOT dispatched a fault crew to make safe, isolate and repair. Fault crew made safe and restored supply. Boric Acid fuse taken back to depot for investigation. Boric Acid fuse replaced, no apparent cause identified. | 12-16 BELFAST ROAD, MONTROSE VIC 3765 | 1001171 |  |  |  | Corrosion;Electrical breakdown |  |  | 2 | IMS 221342. Candling Boric Acid fuse at S/S Belfast Cambridge outside 12 Belfast Rd, Montrose. No fire caused or damage to apparatus. 15e BA at the transformer fuse was candling. | Boric acid | 0 | 0 | 0 |  | cyn33 | Boric Acid fuse candled. No specific failure cause identified. | Other electricity related | 42464.5382 | 1 | Negligible: no ground fire | 1140 | Residential |  | 20160404SPN_04 | Infrastructure (network-based) | -37.8006 | 145.3488 | 1 | AusNet Services Distribution | Report | 1625 | 0.035505 | 22kV AC | Moorabbin Airport | 3765 | Montrose | Fuse
The cables touching the fence were 4 wire 16 sq.mm xlpe cables that had been pulled up out of a concrete service pit located on the Mahers Rd side of the farmer's boundary fence with the concrete pit lid laying upside down beside the pit. The xlpe insulation on the 3 active phases of the cable were deteriorated and a bare section of the red phase cable had arching marks where it had contacted the fence wires. The 3 active cables had enough length to cut off cable back to undamaged insulation and re-terminate them in the pit using IPC connectors. The neutral cable insulation was not deteriorated and was left as found. Supply was restored to all customers off the substation, cables reinstated in the pit and the lid put back on the pit. Mr Carter reported receiving the shock on opening the gate, with one hand on the gate and the other on the chain. He received a second shock on closing the gate, again whilst holding the gate in one hand and the gate chain in the other. Both gate posts are wooden and the fence wire around the gate on the northern side was contacting the metal frame of the gate. Arcing marks were evident between the gate chain and the fencing wire on the southern side of the gate. Mr Carter said that he had been through this gate hundreds of times over the last 5 years and this was the first time he had received a shock. He did not note any symptoms from the shock and did not seek any medical aid. The farmer Gerard McIntosh stated the farm hand entered the paddock to remove a dead calf adjacent to the fence. He stated that he also had two other calves die in the paddock recently. He stated the neighbour across the road at 1381 Mahers Rd, Mr Baldwin, said the cables had been above the ground for at least 15 years. The area on the road side of the fence, including the area surrounding the pit has been grazed by the cattle from the paddock side of the fence. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a defective service conductor causing the fence wire to become alive. The attending service crew checked the condition all conductors and broke and remade all terminations between the distribution system and the Point of Supply of the installation. The installation passed an NST test performed by the attending Service Crew and the attending LEI. Installation left ON supply. | 901 MAHERS ROAD, BONEGILLA VIC 3691 | 5209725 | Unauthorised access |  |  | Age |  | Phase to earth | 2 | IMS 221772. Lines crew were sent to investigate a report of an electric shock in Mahers Rd, Bonegilla. The crew met Colin Carter, the person who the had received the shock and a representative from his employer Gerard McIntosh (0408) 698078, the person who had reported the fault on site to establish the site of the gate where the shock occurred. A voltage test to an independent earth revealed the gate was alive at 240V. The same test to the fence either side of the gate also revealed 240V. The gate was opened and the voltage level fell to 0 V on the southern side of the gate. Gerard McIntosh then directed the line crew to some cables touching the fence approx. 66m on the northern side of the gateway who confirmed they were AusNet Service' underground cables. The cables touching the fence were isolated by opening a low voltage fuse on pole #5209725 "MahersRd 2" substation and the voltage on the fence fell to 0 V. The Lines crew called the AusNet Services' Electrical Inspector travelling to the site and having identified the problem, obtained permission to undertake repairs to the underground cables to get 3 houses back on supply. | Services cable;Services pit | 0 | 0 | 0 |  | wots25 | AusNet Services' underground service cable at the service pit made contact with a wire farm fence. | Minor shock | 42495.6326 |  |  | 2372 | Agricultural |  | 20160524SPN_01 | Infrastructure (network-based) | -36.1857 | 147.0013 | 1 | AusNet Services Distribution | Report | 2979 | 0.0029722 | Low voltage AC (<1kV) | Wangaratta Aero | 3691 | Bonegilla | UG Cable
CEOT dispatched fault crew to make safe and investigate. Protection operated and branch removed. Supply restored. Fuses at HE021 BA 25E TOORA CRES, POLE: 1402770 operated. | 7 TOORA CRESCENT, BADGER CREEK VIC 3777 | 1402779 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 222012. Initial report: Tree branch on 22kV was sparking badly and CFA on site. To be investigated. Please note this report was late due to uncertainty regarding that a tree branch fire actually did occur. Further information: Customer's tree fell over HV causing the tree branch to catch alight but no fire on the ground. Tree branch failed due to poor tree structure and decay. The tree was not classed as hazardous. The tree branch was not inside the vegetation clearance space. Strong windy conditions at the time of incident. The following information is an extract from the vegetation report: Small Blackwood, Acacia melanoxylon (200mm. App 9 mts high) has failed in strong wind gusts and been pushed over line. Directional pruning for lines resulting in majority of growth away from lines. Vegetation has contacted HV causing outage. Evidence of burning on limb at contact point with HV but no evidence of ground fire. Evidence of borers and decay at fail point on tree. | Conductor (bare) | 0 | 0 | 0 |  | wyk24 | Vegetation: Trees Incident | Other vegetation | 19/05/2016 9:15 | 1 | Negligible: no ground fire | 2374 | Residential |  | 20160524SPN_02 | Infrastructure (network-based) | -37.6721 | 145.5352 | 1 | AusNet Services Distribution | Report | 2984 | 0.0063472 | 22kV AC | Moorabbin Airport | 3777 | Badger Creek | Trees
The incident was attended to by AusNet Services' fault crews and an LEI. The cause was found to be a broken neutral connection which had also shorted to the active on the customer's neutral screened mains, in the supply pit. The actual cable connection was made with screw connectors and had both the active and neutral connections within the same cap separated by Bishop tape. This is not to current standards, but are unsure if it met the standards at the time it was installed. The underground network was installed in the court in 1980 and is expected the house would have been connected within the next couple of years. The upside down crutch and cap has let some moisture into the joint as the metal spring in the screw caps are rusty. Procedure 4167-05-01 calls for an NST at attendance to every single customer fault and this was not undertaken by either of the two fault crews who attended to the first report of dim/flickering lights as neither attended the premise. The first crew believed more than one customer was affected and undertook fault investigation based on a multi-customer fault. The second crew that attended on the Friday were unaware a single customer had called as they were just called to inspect connections on "Vails 4" substation. An NST conducted at the customer's premise on the Friday would most likely have failed, requiring further investigation, rectification and prevention of the electric shock. The electricity field procedure 4167-05-01 "NST Testing when attending a Customers Installations for Fault Calls" and "Guidelines for Failed Test Procedures for New Connections/Fault Calls" mentions the requirement to undertake an NST for when attending a fault call at a single customer premises in the "purpose" section but does not mention this in the "scope" section of the document. An action has been created on Works Practices to review the wording on the document to clarify when an NST is required in the fault process. | 10 BRAESIDE COURT, TAWONGA SOUTH VIC 3698 | 5229081 |  |  |  | Moisture ingress |  | Phase to earth | 2 | IMS 221922. A fault call came in for flickering and dim lights from a single premise at 10 Braeside Ct, Tawonga South, on Friday 13/5/16. Prior to arrival of the fault crew a Field Services Representative assessed the AMI meter data on "Vail 4" substation and determined that other customers in the area were also seeing varying voltages. The fault crew visually inspected the connections on pole 5229081 and the overhead line back to the substation and could not see anything obviously wrong. They called a second fault crew to bring an EPV to assess the connections on the substation more closely. The second fault crew attended the substation "Vail 4" and found the Blue Phase isolator partially open. They opened the isolator, regreased the isolator contacts and closed the isolator. On Saturday the 14/5/16, a second fault call came in for the same premise at 10 Braeside Ct, Tawonga South. An REC reported a faulty neutral and a live switchboard. The premise occupant Mr Hodge was checking why he had dimming lights, went to the meter box and had received a tingle. A faults crew and LEI were dispatched to the site and an initial NST test performed which failed. Voltage from an independent earth to meter box and the main neutral bar was measured at 46 Volts. The customer's supply point at an UG pit was located and the neutral UG joint had failed in the pit. The fault crew crutched the neutral screened consumer's mains and re-terminated the mains using IPC's. The installation was re-energized and a voltage test to an independent earth on metal parts as well as the neutral bar, showed zero volts. The installation then passed an NST test. | Services pit;Connector/termination | 0 | 0 | 0 |  | mby11 | Failed neutral connection in service pit. | Minor shock | 14/05/2016 8:38 |  |  | 2382 | Residential |  | 20160525SPN_04 | Infrastructure (network-based) | -36.736 | 147.1561 | 1 | AusNet Services Distribution | Report | 2993 | 1.9676e-05 | Low voltage AC (<1kV) | Wangaratta Aero | 3698 | Tawonga South | Connection
A faults truck attended and replaced the blue phase HV 5amp powder filled fuse at pole No. LIS 1109688 that restored supply to the five customers supplied from the pole type substation. | 1939 FRANKSTON-FLINDERS ROAD, HASTINGS VIC 3915 | 1109688 |  | Precipitation |  | Fatigue |  |  | 2 | Customer advised of the occasional flickering and dimming of lights. Business name is Norton Gates P/L and they will be open until 5.00PM. A HV fuse was found to be candling at "Watts-Haddock" substation following a report of dim lights from a customer who resides at 1939 Frankston-Flinders Road, Hastings. | Powder filled | 0 | 0 | 0 |  | HGS 23 | The cause was probable salt contaminants due to the location near the ocean. | Melting or smoking only | 24/05/2016 14:40 |  |  | 2377 | Roadway |  | 20160525UTD_01 | Infrastructure (network-based) | -38.2944 | 145.1839 | 1 | United Energy Distribution | Report | 3703 | 0.028087 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Fuse
Supply isolated for repairs to conductor. | 23 RONALD STREET, COBURG NORTH VIC 3058 |  |  |  |  | Age;Defective component |  |  | 1 | Jemena received report that Low Voltage red phase conductor was down. Likely causes of this incident may be due to age of the asset and weather conditions. However exact cause unknown due to the failed section of cable being disposed prior to investigation. | Conductor (bare) | 0 | 0 | 0 |  |  | Likely causes of this incident may be due to age of the asset and weather conditions. However exact cause unknown due to the failed section of cable being disposed prior to investigation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/05/2016 6:00 |  |  | 2402 | Public space |  | 20160530JEM_03 | Infrastructure (network-based) | -37.7301 | 144.9797 | 1 | Jemena | Report | 3459 | 0.021242 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg North | Conductor
On arrival crew made safe and commenced repairs | 16 HILL DRIVE, KYNETON VIC 3444 | 907267 |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire on a pole at the incident location. On arrival the crew found that a LV junction box had melted ( no fire on arrival ), the fallen molten material had burnt a small area of grass, approximately 15cm square, ground fire self extinguished. There were no reported injuries, no third party damage. | Any other type;Connector/termination | 0 | 0 | 0 |  | WND024 | Probable Overheated Connection in fused overhead line connector box | Grassfire | 26/05/2016 22:10 | 1 | Localised: less than 10 sq.m | 2395 | Roadway |  | 20160530PWA_02 | Infrastructure (network-based) | -37.2636 | 144.4495 | 1 | Powercor | Report | 3217 | 0.040601 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3444 | Kyneton | Connection
on arrival supply isolated and repairs completed | 8 TOWNSEND STREET, FLORA HILL VIC 3550 | 426288 |  |  |  | Unknown technical factor |  |  | 2 | Vicfire reported a fire on a pole at the incident location. On arrival the crew found that a streetlight had caught on fire. There was no ground fire, reported injuries or third part damage. | Public lighting | 0 | 0 | 0 |  | BGO022 | Insufficient remains to accurately determine cause. | Pole-top fire | 28/05/2016 20:30 | 1 | Negligible: no ground fire | 2398 |  |  | 20160530PWA_03 | Infrastructure (network-based) | -36.7695 | 144.2928 | 1 | Powercor | Report | 8034 | 0.003537 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Flora Hill | AF Other
Crew replaced missing earthing cables | 4476 CRESWICK-NEWSTEAD ROAD, BROOMFIELD VIC 3364 | 25908 | Copper theft | [5 empty] | 2 | Employee reported missing earth cables from pole at incident location. Crew attended and found both the high and low voltage earth cables missing from pole. No shocks, injuries or third party damage. | Earth/earthing | 2 | 2 | 2 |  | BAN009 | Theft | Damage to network assets | 31/05/2016 11:15 |  |  | 2420 | Roadway |  | 20160601PWA_08 | Infrastructure (network-based) | -37.3921 | 143.901 | 1 | Powercor | Report | 8064 | 0.031296 | Earthing cable | Ballarat Aerodrome | 3364 | Broomfield | Other
On arrival the crew found that a low voltage earth cable had been exposed and broken. Earthing Cable repaired. | 73 MILLER STREET, TONGALA VIC 3621 | 27628 | Working too close to underground cables | [5 empty] | 2 | A customer reported finding a cable exposed and broken at the incident location. There was no ground fire. There were no reported injuries or third party property damages. (It is believed a contractor installed the water tapping to this site 3 weeks ago_) | Earth/earthing | 2 | 2 | 2 |  | KYM004 | Damage to earth possible caused by civil contractor up to 3 weeks prior. Contractor has been contacted and awaiting reply. | No Go Zone (contact) | 31/05/2016 13:20 |  |  | 2421 | Roadway |  | 20160601PWA_09 | Infrastructure (network-based) | -36.2495 | 144.9506 | 1 | Powercor | Report | 3041 | 0.011745 | Earthing cable | Shepparton Airport | 3621 | Tongala | Dug up
A LEI and faults truck attended and measured 166v on the 11m steel pole to an independent earth. Supply was isolated in the pit and the LEI and faults crew commenced an investigation to the cause of pole No. LIS 9756405 becoming alive. The investigation revealed the neutral IPC connection in the underground pit was faulty due to possible poor workmanship. Further investigation found the steel public lighting pole was installed in 2001 and there were no defects found at the most recent pole inspection. Repairs were completed at the pit and the lantern was replaced and supply restored to normal. Downer are to provide a detailed investigation report to United Energy by 10/06/2016 including the original higher resolution photos and confirmation of the cause. | FRANKSTON-FLINDERS ROAD, BITTERN VIC 3918 | LIS No. 9756405 | Unknown external/community factor | Precipitation |  | Neutral fault | Unknown work practice factor | Phase to earth | 2 | A Downer employee rang the Resource Coordinator at the United Energy Dispatch team to advise he received a tingle from a steel street light pole located at the intersection of Disney Street and Frankston-Flinders Road when completing a patrol. A Downer lineworker was completing a public lighting patrol and received a slight electric shock to his hand from a steel public lighting pole. A wet tree branch was touching the pole and he received the slight electric shock when he moved the branch to take a photo of the poles LIS number. He wasn't certain that he felt the slight shock and proceeded to use his neon tester to test between the pole & earth and identified the pole was alive. No injuries or medical treatment was required. | Services cable;Public lighting | 0 | 0 | 0 |  | HGS 23 | The initial investigation revealed the neutral IPC connection in the underground pit was faulty due to possible poor workmanship. This will be confirmed in the final investigation report. | Minor shock | 28/05/2016 10:00 |  |  | 2413 | Roadway |  | 20160601UTD_02 | Infrastructure (network-based) | -38.3526 | 145.1571 | 1 | United Energy Distribution | Report | 3033 | 0.011984 | Low voltage AC (<1kV) | Moorabbin Airport | 3918 | Bittern | Connection
Crew isolated supply and commenced repairs | 11 HERON STREET, FRYERSTOWN VIC 3451 | 503561 | Vehicle | [5 empty] | 2 | A member of the public reported that a truck had contacted and bought down a service wire and it was sitting on the truck at the incident location. On arrival the crew found that an LV service had been hit by a truck, resulting in it breaking and coming to rest on the truck. There were no reported injuries or other third part damage. | Service conductor | 2 | 2 | 2 |  | CMN001 | Vehicle contact with service | Loss of supply | 20/05/2016 8:05 |  |  | 2423 | Roadway |  | 20160602PWA_01 | Infrastructure (network-based) | -37.1373 | 144.2494 | 1 | Powercor | Report | 3044 | 0.016086 | Low voltage AC (<1kV) | Bendigo Airport | 3451 | Fryerstown | Vehicle
On arrival crew isolated supply pending repair to damaged cables | 9-17 RAGLAN STREET, SOUTH MELBOURNE VIC 3205 |  | Working too close to underground cables | [5 empty] | 1 | John Bennett reported that demolition equipment used at the incident location has contacted an underground cables at 17 Raglan Street. On arrival the crew found that demolition equipment was being used to pull out foundation material at the above location when it contacted two low voltage underground cables which exit the Thomson-Eastern indoor substation. Dial Before you dig plans were on site. There were no reported injuries, fire or third party property damage. | Cable | 0 | 0 | 0 |  |  | demolition works close to cables | Loss of supply;No Go Zone (contact) | 31/05/2016 10:25 |  |  | 2425 | Roadway |  | 20160602PWA_02 | Infrastructure (network-based) | -37.8365 | 144.9663 | 1 | CitiPower | Report | 3046 | 0.012231 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Dug up
The fault crew isolated supply to the pole, repair works pending. roadster and watchman lanterns and wiring replaced | 120 CLARENDON STREET, SOUTHBANK VIC 3006 | 38684 |  |  |  | Electrical breakdown |  |  | 2 | Report from MFB that a public light pole (metal) is â€œHOTâ€ at the incident location. On arrival the crew found that the public light pole metal work was â€œALIVEâ€ at 240 volts There was no fire or reported injuries. there was no third party damages | Public lighting;Pole (steel) | 0 | 0 | 0 |  | AP9 | Electrical breakdown in Internal control wiring of watchman (eye) lantern and signs of damage to insulated leads of external photo-electric control unit. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42375.4701 |  |  | 2427 | Roadway |  | 20160602PWA_03 | Infrastructure (network-based) | -37.829 | 144.9584 | 1 | CitiPower | Report | 3200 | 0.038689 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | AF Other
On arrival crew carried out repairs | CRYSTAL WATERS, 370 PUNTON ROAD, SHELBOURNE VIC 3515 | 808694 | Working too close to underground cables | [5 empty] | 2 | A customer reported damaging cable at the incident location. On arrival the crew found that a low voltage earth cable had been exposed and broken. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | MRO007 | customer digging close to substation | No Go Zone (no contact) | 42375.4667 |  |  | 2440 | Agricultural |  | 20160608PWA_02 | Infrastructure (network-based) | -36.8789 | 144.015 | 1 | Powercor | Report | 3112 | 0.033142 | Earthing cable | Bendigo Airport | 3515 | Shelbourne | Dug up
Crew isolated supply and commenced repairs | 25 RAILWAY PLACE N, GOORNONG VIC 3557 | 425285 | Working too close to overhead lines | [5 empty] | 2 | CFA reported wire down at the incident location. On arrival the crew found that a truck crane had brought down LV service cable. REC to undertake repairs at customers installation prior to service re-instatement. There were no reported injuries, no ground fire. | Service conductor | 0 | 0 | 0 |  | EHK023 | Crane unloading materials | Loss of supply;No Go Zone (contact) | 42375.5944 |  |  | 2441 |  |  | 20160608PWA_03 | Infrastructure (network-based) | -36.614 | 144.5046 | 1 | Powercor | Report | 3116 | 0.0082963 | Low voltage AC (<1kV) | Bendigo Airport | 3557 | Goornong | Vehicle
Crew isolated supply and commenced repairs | 27 ANDERSON ROAD, THORNBURY VIC 3071 | 812171 |  |  |  | Corrosion |  |  | 2 | A customer reported smoke coming from their POA at the incident location. On arrival the crew found that the POA had caught fire. MFB attended and REC replaced the POA. There was no ground fire. There were no reported injuries. | Connection box | 0 | 0 | 0 |  | NC004 | cause not apparent | Property | 42435.441 | 0 | Negligible: no ground fire | 2442 | Residential |  | 20160608PWA_04 | Infrastructure (customer connection) | -37.7535 | 144.9812 | 1 | CitiPower | Report | 3118 | 0.03015 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Connection
The fault crew inspected the pole top and replaced the HV crossarm and pole top assembly. | 8 GEORGE STREET, SUNSHINE VIC 3020 | 11201 | Vehicle | [5 empty] | 1 | A Customer reported that a â€œbox on pole behind swimming pool has exploded and flames running along power linesâ€ at the incident location. On arrival the crew found evidence that a unknown vehicle may have impacted pole LIS-11201 approx 0.5m above ground level. The center phase HV tie was broken with the 22kv conductor resting on the HV crossarm. There was electrical tracking/flashover between HV crossarm brace, pole, LV crossarm and neutral conductor. LEI did not identify any HVI issues. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare);Crossarm (wood);Insulator tie wires/connections | 0 | 0 | 0 |  | SSE013 | Unknown vehicle struck pole | Loss of supply | 42496.5 |  |  | 2444 | Roadway |  | 20160608PWA_05 | Infrastructure (network-based) | -37.7839 | 144.8347 | 1 | Powercor | Report | 3120 | 0.016411 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine | Vehicle
On arrival crew carried out repairs. | 13 ARUNDEL CRESCENT, SURREY HILLS VIC 3127 | 98679 | Vehicle | [5 empty] | 2 | Owner of the property reported, that when she arrived home the service wire to their house was hanging very low. The house faÃ§ade was slightly damaged . On arrival the crew found that the LV service was still intact and the supply was connected, but the service wire was hanging very low. There was no fire or reported injuries. | Service conductor | 0 | 0 | 0 |  | RD005 | Unknown vehicle | Less than $50k damage | 42588.6986 |  |  | 2451 | Roadway |  | 20160610PWA_02 | Infrastructure (network-based) | -37.8318 | 145.0925 | 1 | CitiPower | Report | 3138 | 0.040383 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | Vehicle
On arrival crew isolated supply and carried out repairs | 122 VICTORIA STREET, NORTH GEELONG VIC 3215 | 61323 | Vehicle | [5 empty] | 2 | Powercor Linesman reported that a conductor is down at the incident location. On arrival the crew found that a vehicle had contacted the neutral conductor , resulting in neutral conductor parting at a midspan sleeve and falling to the ground. There were no reported injuries. There was no fire. | Conductor (bare) | 0 | 0 | 0 |  | GB031 | unknown vehicle struck conductor | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42619.4479 |  |  | 2453 | Roadway |  | 20160610PWA_03 | Infrastructure (network-based) | -38.1227 | 144.3476 | 1 | Powercor | Report | 3141 | 0.0015926 | Low voltage AC (<1kV) | Avalon Airport | 3215 | North Geelong | Vehicle
On arrival crew isolated supply and commenced repairs. | 212 SAILORS GULLY ROAD, SAILORS GULLY VIC 3556 | 407286 | Vehicle | [5 empty] | 2 | Bystanders reported wide load has brought down pole and wires ( no vehicle registration recorded,Vehicle had departed scene before police arrived). Powercor crew attended and found HV/LV pole damaged at ground level and leaning, a span of LV ABC conductor on the ground in at the incident location. There was no ground fire. There were no reported shock or injuries. | Conductor (ABC);Pole (wood) | 0 | 0 | 0 |  | BET001 | Low loader struck pole while turning. | Loss of supply;Damage to network assets | 42588.6771 |  |  | 2454 | Roadway |  | 20160610PWA_04 | Infrastructure (network-based) | -36.7082 | 144.2302 | 1 | Powercor | Report | 8066 | 0.0048345 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Sailors Gully | Vehicle
The neutral conductor was repaired under Access Authority conditions and the LEI investigated the amount of damage that occurred to customers appliances and equipment. In addition, a tap change was completed at the transformer from tap 4 to tap 3. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | OAKLEIGH ROAD, CARNEGIE VIC 3163 |  | Unknown external/community factor | Unknown environment factor |  | Neutral fault;HV injection | Unknown work practice factor |  | 2 | The United Energy AMI Analysts identified smart meters in the Oakleigh Road area are communicating high volts and a faults crew was dispatched to investigate. The neutral conductor was found burnt off the transformer at "Oakleigh-Walden" pole type substation that caused a floating neutral and fluctuating voltages on each phase. Supply was isolated to both circuits and the neutral conductor repaired. Supply was restored and customers claimed to have damaged appliances and the faults crew requested a LEI attend as a injection was suspected to customers supplied from "Oakleigh-Walden" substation. The LEI confirmed a low voltage injection occurred (CLA 1602) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The LEI identified nine properties that had received appliance damage. At one property, a REC had tested the supply voltage before the supply was isolated at the substation and measured - red 280v, white 140v and blue 400v. | Equipment;Pole mounted;Transformer;Customer installation | 0 | 0 | 0 |  |  | Failed neutral connection at "Oakleigh-Walden" pole type substation - cause unknown. | HV injection;Loss of supply | 42527.7431 |  |  | 2452 | Residential |  | 20160610UTD_01 | Infrastructure (network-based) | -37.8998 | 145.0583 | 1 | United Energy Distribution | Report | 3140 | 0.0075544 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | Connection
On arrival crew commenced repairs | 596 BALLARAT ROAD, ARDEER VIC 3022 | 25962 | Copper theft | [5 empty] | 2 | Control room received reports that copper earths have been stolen at the incident location. There were no injuries, fires or third party property damage. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | SU022 | Theft of earth cables | Damage to network assets | 42375.4688 |  |  | 2461 | Roadway |  | 20160614PWA_01 | Infrastructure (network-based) | -37.7739 | 144.8067 | 1 | Powercor | Report | 8067 | 0.012241 | Earthing cable | Laverton Raaf | 3022 | Ardeer | Other
On arrival crew commenced repairs | 14 SYDNEY STREET, ALBION VIC 3020 | 742259 | Copper theft | [5 empty] | 2 | Control room received reports that copper earths have been stolen at the incident location. There was no injuries, fire or third party property damage. | Earth/earthing | 0 | 0 | 0 |  | SSE014 | Theft of earth cables | Damage to network assets | 42649.4688 |  |  | 2462 | Roadway |  | 20160614PWA_02 | Infrastructure (network-based) | -37.7837 | 144.8224 | 1 | Powercor | Report | 8068 | 0.017748 | Earthing cable | Laverton Raaf | 3020 | Albion | Other
On arrival crew commenced repairs | 602 BALLARAT ROAD, ARDEER VIC 3022 | 966627 | Copper theft | [5 empty] | 2 | Control room received reports that copper earths have been stolen at the incident location. There were no injuries, fires or third party property damage. | Earth/earthing | 0 | 0 | 0 |  | SU022 | Theft of earth cables | Damage to network assets | 42649.4688 |  |  | 2463 | Roadway |  | 20160614PWA_03 | Infrastructure (network-based) | -37.7738 | 144.8054 | 1 | Powercor | Report | 8069 | 0.024334 | Earthing cable | Laverton Raaf | 3022 | Ardeer | Other
On arrival crew confirmed isolation of supply and commenced clean up | 585-609 KOROROIT CREEK ROAD, ALTONA VIC 3018 | 2248 | Vandalism;Theft | [5 empty] | 2 | A local REC reported a low voltage supply cabinet in Kororoit Creek Road had lost supply at the incident location. On arrival the crew found that the substation supplying this cabinet had been vandalised. Unknown persons opened the high voltage switch to isolate supply. The 315kVA substation transformer had been pushed over, its lid removed and oil split over the ground. All copper from the open high voltage switch and within the substation has been removed. There was no injuries, fire or third party property damage | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | AC31 | Theft of copper conductor | Loss of supply | 42649.5833 |  |  | 2464 | Industrial |  | 20160614PWA_04 | Infrastructure (network-based) | -37.846 | 144.7984 | 1 | Powercor | Report | 3177 | 0.0099086 | 22kV AC | Laverton Raaf | 3018 | Altona | Other
HV switch 'DN0567 Blackburn Road CHP' was opened and the substation isolated to enable the rectification work to be completed safely. The LV assets in the substation remained isolated and a defect notice issued to the customer as the consumers mains were required to be replaced. | 680-686 BLACKBURN ROAD, NOTTING HILL VIC 3168 |  | Vandalism;Theft;Unauthorised work;Unauthorised access | [5 empty] | 2 | The customer at 680 Blackburn Road advised of a loss of their electricity and the substation outside the building has been opened and the wires exposed. The building is located on the corner of Normanby and Blackburn Roads, Clayton. "Health Comp-Blackburn" Indoor substation has been vandalised and copper stolen by unknown persons. There was evidence of a flashover and the copper conductors from the LV transformer bushings to the LV isolators had been removed along with the copper consumers mains. | Copper;Indoor | 0 | 0 | 0 |  |  | Stolen copper conductors from the Indoor substation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42649.5417 |  |  | 2460 | Commercial |  | 20160614UTD_03 | Infrastructure (network-based) | -37.9072 | 145.1421 | 1 | United Energy Distribution | Report | 3160 | 0.018902 | 22kV AC | Moorabbin Airport | 3168 | Notting Hill | Other
Repair works completed -LV fuse box has been replaced. | 40 MADDISON LANE,GREENDALE,VIC,3341 | 105696 |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire on a pole at the incident location. On arrival the crew found that a LV fuse box had melted and the fallen material had apparently burnt a small area of grass of approximately 0.5 square metres. There were no reported injuries, no third party damage. | Any other type;Connection box | 0 | 0 | 0 |  | BMH003 | Overheated connection | Loss of supply;Grassfire | 15/06/2016 20:11 | 1 | Localised: less than 10 sq.m | 2481 | Roadway |  | 20160617PWA_01 | Infrastructure (network-based) | -37.5586 | 144.3062 | 1 | Powercor | Report | 3213 | 0.037826 | Low voltage AC (<1kV) | Avalon Airport | 3341 |  | Connection
On arrival crews commenced repairs | GOLDEN GROVE, 15 KINGSTON-NEWLYN ROAD, NEWLYN VIC 3364 | 23970 | Theft | [5 empty] | 2 | A citizen reported that copper was removed from a pole at the incident location. On arrival the crew found that about 2m of the LV earth had been cut and removed on a 22kV pole. There were no reported injuries, fires or third party property damage. | Earth/earthing | 0 | 0 | 0 |  | BAS009 | Theft of substation earthing | Less than $50k damage | 17/06/2016 18:10 |  |  | 2495 | Roadway |  | 20160622PWA_01 | Infrastructure (network-based) | -37.4092 | 143.9752 | 1 | Powercor | Report | 3231 | 0.0095683 | Earthing cable | Ballarat Aerodrome | 3364 | Newlyn | Other
Missing earth cable replaced | BALLARAT GENERAL CEMETERYCREMATORIUM, 1250 DOVETON STREET N, INVERMAY PARK VIC 3350 | 32030 | Theft | [5 empty] | 2 | An employee, reported to the control room, a stolen copper earth from the High Voltage switch at the incident location. There were no reported injuries, fires or other third part damage. | Earth | 0 | 0 | 0 |  | BAN011 | copper cable theft | Less than $50k damage | 16/06/2016 10:02 |  |  | 2496 | Roadway |  | 20160622PWA_02 | Infrastructure (network-based) | -37.5366 | 143.8622 | 1 | Powercor | Report | 3232 | 0.0013322 | Earthing cable | Ballarat Aerodrome | 3350 | Invermay Park | Other
Crew commenced repairs FOLCB damaged, defect issued | 47 KIMBERLEY ROAD, WERRIBEE VIC 3030 | 212048 | Working too close to overhead lines |  |  |  | Ineffective planning/procedures/processes |  | 2 | James Logan from neighboring property 49 Kimberley Road was trimming trees and brought down the service wire supplying 47 Kimberley Road resulting in loss of supply. There was no fire or reported injuries | Service conductor | 0 | 0 | 0 |  | WBE031 | Neighbor trimming vegetation near service line | Loss of supply | 19/06/2016 14:56 |  |  | 2497 | Roadway |  | 20160623PWA_01 | Infrastructure (network-based) | -37.8959 | 144.6337 | 1 | Powercor | Report | 3233 | 0.0030266 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Trees
Crew carried out repairs. | 12 THORPE AVENUE, HOPPERS CROSSING VIC 3029 | 208708 | Vehicle | [5 empty] | 2 | A driver reported he has reversed into a service cable, It has broken in the middle at the incident location. On arrival the crew found that the service cable had been damaged and was laying across roadway. There was no ground fire. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  | LV004 | Vehicle reversing | Loss of supply | 20/06/2016 15:27 |  |  | 2499 |  |  | 20160623PWA_03 | Infrastructure (network-based) | -37.8772 | 144.7004 | 1 | Powercor | Report | 3235 | 0.020782 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Vehicle
Crew confirmed isolations | 503 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 112168 | Vandalism;Theft | [5 empty] | 2 | A contractor reported a vandalised pole and UG assets at the incident location. Upon arrival, the Powercor crew found that the UG service cables to two premises had been cut away and some damage done to the switch board across the road. These services had been isolated some time ago as the properties were vacant. There were no reported injuries or other damage. | Services cable;Customer installation | 0 | 0 | 0 |  | MLN022 | cable theft and vandalism | Less than $50k damage | 21/06/2016 9:34 |  |  | 2501 | Roadway |  | 20160623PWA_05 | Infrastructure (network-based) | -37.6889 | 144.5303 | 1 | Powercor | Report | 3328 | 0.030154 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
Isolated supply and undertook repairs. | 177 KOW SWAMP ROAD, LEITCHVILLE VIC 3567 | 704550 |  | Bird |  |  |  |  | 1 | Vic Fire reported a grass fire at the incident location. On arrival the crew found that a conductor was on the ground at the incident location , resulting in a ground fire in the road reserve. Resulting in a small ground fire. The site was made safe and the conductor was repaired. Protection operated. | Conductor (bare) | 0 | 0 | 0 |  | CHA005 | Crew indicated Pelican stuck conductor mid span. | Loss of supply;Grassfire | 23/06/2016 12:23 | 1 | Small: 10 - 1000 sq.m | 2505 | Roadway |  | 20160624PWA_02 | Infrastructure (network-based) | -35.9222 | 144.2816 | 1 | Powercor | Report | 3250 | 0.004934 | 22kV AC | Bendigo Airport | 3567 | Leitchville | Animal
On arrival crew commenced repairs | 3147 MAROONA-GLENTHOMPSON ROAD, STAVELY VIC 3379 | 56069 |  |  |  | Unknown technical factor |  |  | 1 | A property owner reported to Powercor Fault Centre a wire down in a paddock at the incident location. On arrival the crew found the centre phase conductor of a 3 phase HV line had broken and fallen to the ground, resulting in a number of small ground fires. Protection operated as expected. There were no reported injuries | Conductor (bare) | 0 | 0 | 0 |  | ART033 | Conductor ends were not retained by work crew - no cause identified. | Loss of supply;Grassfire | 25/06/2016 20:57 | 1 | Localised: less than 10 sq.m | 2508 | Agricultural |  | 20160627PWA_01 | Infrastructure (network-based) | -37.5868 | 142.5843 | 1 | Powercor | Report | 3276 | 0.023258 | 22kV AC | Hamilton Airport | 3147 | Stavely | Conductor
on arrival crew carried out repairs | 40 WELLINGTON STREET, WARRNAMBOOL VIC 3280 | 17337 |  |  |  | Corrosion |  |  | 2 | Vicfire reported a pole fire and wires sparking at the incident location. On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. There was no ground fire. There were no reported injuries or third party property damage. | Connection box | 0 | 0 | 0 |  | WBL004 | overheated connection | Pole-top fire;Loss of supply | 25/06/2016 18:51 | 1 | Negligible: no ground fire | 2511 | Roadway |  | 20160627PWA_02 | Infrastructure (network-based) | -38.3844 | 142.4694 | 1 | Powercor | Report | 3257 | 0.020568 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew commenced repairs | 225 MEAD ROAD, MEAD VIC 3568 | 701777 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Scott Rutherford, Supervisor for earth moving contractor Ertech reported that an excavator had accidentally reversed into a low voltage service, resulting in damage to FOLCB and service line hanging low across paddock. No protection operation, no reported injuries, fires or third party property damages. | Service conductor | 0 | 0 | 0 |  | CHA006 | Excavator striking service line | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/06/2016 17:28 |  |  | 2512 | Agricultural |  | 20160627PWA_03 | Infrastructure (network-based) | -35.8142 | 144.1242 | 1 | Powercor | Report | 3258 | 0.022049 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3568 | Mead | Vehicle
Jemena crew isolated the low voltage underground cable and made repairs to the cable. | 797 BELL STREET, COBURG VIC 3058 |  | Working too close to underground cables | [5 empty] | 1 | Underground low voltage cable was dug up by Yarra Valley Waters during water works. The low voltage cable was isolated and has been repaired by Jemena crew. | Cable | 0 | 0 | 0 |  |  | Underground cable was dug up by Yarra Valley excavator during water works. | No Go Zone (contact) | 42527.4951 |  |  | 2534 | Commercial |  | 20160704JEM_02 | Infrastructure (network-based) | -37.743 | 144.9798 | 1 | Jemena | Report | 3295 | 0.019429 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Dug up
CEOT dispatched a fault crew to make safe, investigate and repair. Fuse replaced by crew. | 8 RHYLL-NEWHAVEN ROAD, RHYLL VIC 3923 | 2805498 |  |  |  | Electrical breakdown |  |  | 2 | IMS 222751. On arrival at switch 5656325, fault crew found HV fuse damaged due to candling. | Boric acid | 0 | 0 | 0 |  | phi11 | Candled HV fuse. 12 K Boric Acid fuse replaced by crew | Other electricity related | 30/06/2016 15:59 | 1 | Negligible: no ground fire | 2532 | Residential |  | 20160704SPN_01 | Infrastructure (network-based) | -38.4638 | 145.2991 | 1 | AusNet Services Distribution | Report | 3292 | 0.040447 | 22kV AC | Moorabbin Airport | 3923 | Rhyll | Fuse
CEOT notified ESV and AusNet Services' Claims section. Fault crew and DAO to attend. Assuming the line to be still alive wth an antenna still around 100mm from the line, the Fault Linesmen & I asked all persons to remain 6 metres clear of the incident area. Needing to make the area safe and with consultation between CEOT, Fault Linesman & myself it was decided to isolate & earth the affected line at AusNetâ€™s supply point to the Camp. Switch 836031. Talked to Michael M. of ESV (0408 208 838) who was on route, he was asking what is going on. I explained to him the situation as I knew it. Briefed Peter Murphy (0419 927 871) Broadspectumâ€™s Maintenance manager for the camp on the situation, as I knew it on his arrival at the site. Broadspectum wanted to work towards making safe the affected spur line. So that supply could be restored back rest of the Army camp. After consultation with ESV, CEOT & Broadspectum the affected line was made safe. Then supply was restored back to the rest of the camp via switch 836031 then the Armyâ€™s 22kv CB. | DAMASCUS ROAD, PUCKAPUNYUL VIC 3662 |  | Crane, excavator or other construction/farming equipment |  |  |  |  | Three phase | 2 | IMS 222803. Police report serious incident within Army Base at Puckapunyal. CEOT have advised that AusNet Services' assets are not involved. The incident happened on Damascus Rd south of Passchendaele Parade within the Puckapunyal Army Camp. There were a number of services on site Police, Ambulance, Army Fire Rescue & Army personnel etc. The incident involve a portable communication antenna being erect from under, through & contacting an overhead 22kV 3 phase Line [Armyâ€™s Asset]. | Customer installation | 0 | 0 | 0 |  | smr1 | CEOT in AusNet Services believes that an aerial contacted overhead HV and a person was injured. | Medical attention (first aid/doctor/hospital) | 42467.8688 |  |  | 2536 | Roadway |  | 20160705SPN_01 | Infrastructure (network-based) | -37.0018 | 145.0532 | 1 | AusNet Services Distribution | Report | 3298 | 0.026038 | 22kV AC | Mangalore Airport | 3662 | Puckapunyul | Vehicle
On arrival crew isolated supply and commenced repairs | 11 TILLEYS ROAD, MADDINGLEY VIC 3340 | 30291280 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Powecor fault crew attending an outage (BMH06 feeder) found that a conductor down at the incident location. There is evidence of mulch/rubbish being tipped under the conductors where the damage occurred. No vehicles on site. There was no ground fire, injuries or third party property damage. | Conductor (bare) | 0 | 0 | 0 |  | BMH006 | site operations by unknown persons | Loss of supply;No Go Zone (contact) | 42528.3299 |  |  | 2553 | Industrial |  | 20160706PWA_01 | Infrastructure (network-based) | -37.697 | 144.4469 | 1 | Powercor | Report | 3316 | 0.041442 | 22kV AC | Avalon Airport | 3340 | Maddingley | Vehicle
On arrival crew isolated supply and commenced repairs. Asset damage assessed by the LEI. | 24 THOMPSON ROAD, NORTH GEELONG VIC 3215 | 32072771 |  |  |  | Incorrect design |  |  | 1 | Following a lockout of GL024 feeder CB, the crew patrolled the feeder and found a faulted conductor at the incident location. The faulted High Voltage conductor had fallen onto the blue phase of the of the low voltage conductor below. This caused a high voltage injection in the general area of the incident location. There was no fire or injuries. Only minor third party damage was reported. | Conductor (bare) | 0 | 0 | 0 |  | GLE024 | Copper conductor released from Automatic line splice. | HV injection;Loss of supply | 42497.8111 |  |  | 2554 | Roadway |  | 20160706PWA_02 | Infrastructure (network-based) | -38.1226 | 144.3413 | 1 | Powercor | Report | 3329 | 0.029296 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3215 | North Geelong | Conductor
On arrival crew isolated supply and removed the service, supply off. | 135 BARWARRE ROAD, MARSHALL VIC 3216 | 33046839 | Vehicle | [5 empty] | 2 | Customer Brett Dwyer reported one of his employees has hit the LV service line to his house breaking it in half. On arrival Linesmen found the LV service has snapped in half about 3 meters from the pole end. There was no fire or injuries. | Service conductor | 0 | 0 | 0 |  | GLE013 | Vehicle hit service line | Loss of supply | 42467.75 |  |  | 2563 | Roadway |  | 20160708PWA_02 | Infrastructure (network-based) | -38.1988 | 144.3524 | 1 | Powercor | Report | 3334 | 0.034652 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Marshall | Vehicle
Crew isolated the substation and earths were repaired. | 18 HIGH STREET, YARRAVILLE VIC 3013 |  | Copper theft | [5 empty] | 2 | Crew discovered copper earths had been taken away from substation high-Severn. Copper was stolen by unknown persons. | Copper;Earth/earthing | 0 | 0 | 0 |  | Pole no. A051220 | Unknown persons stole copper earths. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/07/2016 12:22 |  |  | 2587 | Residential |  | 20160713JEM_01 | Infrastructure (network-based) | -37.8161 | 144.8805 | 1 | Jemena | Report | 12377 | 0.009081 | Earthing cable | Essendon Airport | 3013 | Yarraville | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 392 BONEO ROAD, BONEO VIC 3939 | 1315805 |  | Wind;Cold;Fallen |  | Conductor clashing;HV injection |  |  | 1 | At 0941hrs on 12/07/2016, 22kV feeder RBD 21 circuit breaker reclosed to lockout affecting 273 customers. During very strong winds, a large tree located outside 392 Boneo Road, Boneo contacted the 66kV, 22kV conductors that resulted in a HV conductor to contact the LV conductors below near pole No. LIS 1315805. The fallen tree caused one pole to break and four bays of HV and LV conductors to fall to the ground. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Boneo-Browns" substation. The LEI confirmed a high voltage injection occurred (MOR 1605) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole (wood);Crossarm (wood);Crossarm (steel) | 0 | 0 | 0 |  | RBD 21 | Vegetation: Trees Incident | HV injection;Loss of supply | 42711.4035 |  |  | 2597 | Roadway |  | 20160715UTD_02 | Infrastructure (network-based) | -38.3956 | 144.888 | 1 | United Energy Distribution | Report | 3561 | 0.026962 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3939 | Boneo | Trees
On arrival crew isolated supply and commenced repairs | 1177 GREENHILLS ROAD, JUNG VIC 3401 | 32090075 |  |  |  | Leakage |  |  | 1 | VicFire reported a pole fire at the incident location. On arrival the crew found that a high voltage wooden SWER s/s pole had burnt through approximately 4m above ground and had fallen to the ground. There was no ground fire. There were no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | HSM001 | Excessive leakage current - Origin not found | Pole-top fire;Loss of supply | 15/07/2016 19:03 | 1 | Negligible: no ground fire | 2603 | Agricultural |  | 20160718PWA_02 | Infrastructure (network-based) | -36.5911 | 142.3887 | 1 | Powercor | Report | 3752 | 0.01838 | 12.7kV AC (SWER) | Horsham Aerodrome | 3401 | Jung | Pole
A full test was conducted on the overhead supply connections to the installation and the only thing found was a dry connection in the mains connection box which was rectified, Further tests on the meters, switchboard and installation found only a few slightly loose terminals on the old federal switchboard and a corroded earth pipe. All tests were carried out and with the installation under load 1.5 volts to an independent earth. All tests passed on arrival and on leaving. | 44 BAYVIEW DRIVE, COWES VIC 3922 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 222496. Customer reported shock from tap, no injury. | Customer installation | 0 | 2 | 0 |  | phi11 | Found a dry connection in the mains connection box which was rectified. Found only a few slightly loose terminals on the old federal switchboard and a corroded earth pipe. | Minor shock | 18/06/2016 9:54 |  |  | 2613 | Residential |  | 20160720SPN_02 | Infrastructure (customer connection) | -38.4597 | 145.2024 | 1 | AusNet Services Distribution | Report | 3392 | 0.03348 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Cowes | Connection
On arrival nst test failed . Connections were checked and a faulty neutral connection was found in the mains box on the pole supplying the underground pit to the property. This connection was relocated to the krone box on the pole; the neutral connection in the pit was also remade. All tests were carried out and no volts were found on the neutral conductors. | 91 BANK STREET, ALBERTON VIC 3971 | 2626611 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 222561. Customer received small tingle when opening metal meter box door. The switchboard/meter box is mounted on north facing wall of shed adjacent to house. The weather at the time was poor and had been raining, the ground around the shed. | Switchboard | 0 | 2 | 0 |  |  | A faulty neutral connection was found in the mains box on the pole supplying the underground pit to the property. | Minor shock | 22/06/2016 17:46 |  |  | 2614 | Residential |  | 20160720SPN_03 | Infrastructure (network-based) | -38.6141 | 146.6714 | 1 | AusNet Services Distribution | Report | 3393 | 0.0014155 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3971 | Alberton | Connection
Replaced fuse. | 125 BEVERIDGE ROAD, BEVERIDGE VIC 3753 | 931594 |  |  |  | Age;Fuse failed to eject |  |  | 0 | IMS 223145. Candled EDO fuse at LIS 931594. | EDO fuse | 0 | 2 | 0 |  | KLO14 | EDO candled. | Pole-top fire | 21/07/2016 13:53 | 1 | Negligible: no ground fire | 2644 | Residential |  | 20160725SPN_03 | Infrastructure (network-based) | -37.4731 | 145.0097 | 1 | AusNet Services Distribution | Report | 3435 | 0.012867 | 22kV AC | Wallan (Kilmore Gap) | 3753 | Beveridge | Fuse
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Distribution Service Pole Connection Box. The attending Powercor Fault Crew reterminated the neutral connection at the Pole Type Connection Box on the Distribution Service Pole and completed an NST Test which confirmed a Pass result. | 519 RAGLAN PARADE, WARRNAMBOOL VIC 3280 | 31028657 |  |  |  | Corrosion |  | Phase to earth | 2 | Various Motel Guests were showering in different Motel Rooms at various times when they received an electric shock as they made simultaneous contact between their hands on the shower taps and their bare feet while standing on the wet shower base. | Connection box | 2 | 2 | 2 |  | WBL010 | Corroded O/H Service Neutral Conductor termination at the Distribution Service Pole Connection Box | Minor shock | 42406 |  |  | 2660 | Commercial |  | 20160726PWA_07 | Infrastructure (network-based) | -38.3819 | 142.4876 | 1 | Powercor | Report | 3462 | 0.022799 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
The excavator contacted the consumers underground cable and caused considerable damage at the pole end as the pole to meter position underground cable was struck with force. The pole mounted FOLCB was damaged and the faults crew contacted their supervisor as they wanted the event reported to ESV as the onsite workers had no considerations for safety when the abolishment work was being undertaken. The underground supply was disconnected from the pole end, meters removed and the REC was instructed to go through the normal processes and apply for an abolishment request. | 3832 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1307203 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | 12.15PM - REC Adam (0421 548 245) states excavators working just near the underground mains and wants a crew to attend and turn off the electricity. They were advised by the United Energy faults and emergencies call centre to stop work. Approximately 1.20PM - Caller states underground cable exposed and an excavator has dug up the underground cable inside the boundary. The previous owner advised the underground cable was on the boundary. REC wants the power turned off for safety. An excavator was on site as part of an home demolishment and dug up the consumers underground mains within the property. REC Adam Tregaskis was on site and wants the supply disconnected. There had been no abolishment request and the underground cable was live. No injuries or damage to plant was sustained. | Services cable;Customer installation | 0 | 0 | 0 |  |  | Excavator contacted the consumers underground cable within the property and caused considerable damage at the pole end as the pole to meter position underground cable was struck with force. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/07/2016 12:15 |  |  | 2664 | Residential |  | 20160727UTD_02 | Infrastructure (network-based) | -38.3191 | 144.7078 | 1 | United Energy Distribution | Report | 3671 | 0.021898 | Low voltage AC (<1kV) | Avalon Airport | 3832 | Portsea | Dug up
A faults truck attended, restored supply and safely secured the distribution pillar. | 12 WHITESIDE ROAD, CLAYTON SOUTH VIC 3169 |  | Vandalism | [5 empty] | 2 | Caller reports the work business has lost the power supply. A meter ping was completed that failed and a faults truck was dispatched to investigate. Vandals had broken into a distribution pillar located outside the group of light industrial factories and removed fuses. It wasn't known if the event was a suspected copper theft or if any electric shocks were received. | Connection box;LV Pillar | 0 | 0 | 0 |  |  | Vandals broke into a distribution pillar. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/07/2016 22:30 |  |  | 2666 | Public space |  | 20160727UTD_04 | Infrastructure (network-based) | -37.9383 | 145.1183 | 1 | United Energy Distribution | Report | 3672 | 0.033584 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Other
Service Crew performed NST test of the service conductor at the POA with a fail result recorded. Crew found that the reticulation N/S conductor across the road to the service pole, that then supplies the installation in question, was damaged at the roller clamp connection to the service pole. Crew replaced the conductor with a 4 wire ABC. They performed an NST test of the new conductor and followed by an NST of the service at the POA, both recorded a pass result. | 103 GARDEN STREET, EAST GEELONG VIC 3219 | 30060747 |  |  |  | Corrosion |  | Phase to earth | 2 | Neil was in the crawl space beneath the building and received a slight tingle in his right hand when he came in contact with a water pipe when investigating a water leak. He was lying on bare earth when this occurred | Service conductor;Neutral screen | 2 | 2 | 2 |  | GCY024 | At the N/S roller clamp the conductor sheath was deteriorated and split exposing the neutral screen. | Minor shock | 42375.6667 |  |  | 2674 | Roadway |  | 20160728PWA_04 | Infrastructure (network-based) | -38.1562 | 144.371 | 1 | Powercor | Report | 3477 | 0.022466 | Low voltage AC (<1kV) | Avalon Airport | 3219 | East Geelong | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 157 HILMA STREET, SUNSHINE WEST VIC 3020 | 32165625 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Vicki Kapodistrias was washing dishes when she received an electric shock as she made simultaneous contact with her hands between the kitchen taps and the metallic sink. | Service conductor;Aluminium;Neutral screen | 2 | 2 | 2 |  | SU035 | The corrosion of the O/H Service Cable was the result of water entering the outer sheath via a small perforation, the cause of which was unable to be determined. | Minor shock | 17/06/2016 8:30 |  |  | 2715 | Residential |  | 20160804PWA_04 | Infrastructure (network-based) | -37.7905 | 144.7921 | 1 | Powercor | Report | 3525 | 0.02572 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | OH Cable
The crew isolated the line at P19 and repaired the broken conductor. | 406 TRAWALLA ROAD, TRAWALLA VIC 3373 | 32013172 |  |  |  | Mechanical breakdown |  |  | 1 | Customers reported low volts and a wire down at the incident location. On arrival the crew found that a HV conductor had broken and was on the ground resulting in the HV fuse blowing. The conductor on the ground was live via back feeds from transformers There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | BAS011 | Wind and storm conditions | Loss of supply | 26/07/2016 10:38 |  |  | 2716 | Agricultural |  | 20160804PWA_05 | Infrastructure (network-based) | -37.468 | 143.4919 | 1 | Powercor | Report | 3526 | 0.000875 | 22kV AC | Ballarat Aerodrome | 3373 | Trawalla | Conductor
Crews isolated supply and made repairs. The electrical inspector attended to investigate the cause and confirm that it resulted in a high voltage injection into customer premises on the red phase circuit. | 77 NEWLANDS ROAD, COBURG NORTH VIC 3058 | A037221 | Vehicle |  |  | HV injection |  |  | 1 | Vehicle impacted into the pole supplying 77 Newlands Road, Coburg North. As a result, the footpath side high voltage conductor fell into the red phase low voltage conductor injecting high voltage into the low voltage supply, causing minimal damage to internal appliances and equipment of some of the properties on the red phase. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CN8 | Vehicle impacted the pole causing high voltage conductor to fall into low voltage conductor. | HV injection | 42437.7056 |  |  | 2722 | Residential |  | 20160805JEM_01 | Infrastructure (network-based) | -37.7281 | 144.9726 | 1 | Jemena | Report | 3542 | 0.00073611 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3058 | Coburg North | Vehicle
Crew isolated supply and undertook repairs | 216 SHEOAK AVENUE, KOORLONG VIC 3501 |  | Working too close to overhead lines | [5 empty] | 1 | Customer reported a wire down at the incident location. On arrival the crew found that a tractor driving under a Low Voltage service wire to the sheds has made contact about mid span, causing the wire to break and fall to the ground. There were no reported injuries or third party damages. | Service conductor | 0 | 0 | 0 |  |  | Tractor made contact with Low Voltage service cable | Loss of supply | 17/03/2016 11:55 |  |  | 1088 | Agricultural |  | 20160322PWA_09 | Infrastructure (network-based) | -34.2436 | 142.0644 | 1 | Powercor | Report | 1555 | 0.026733 | Low voltage AC (<1kV) | Mildura Airport | 3501 | Koorlong | Vehicle
Crew isolated supply and undertook repairs | 381 PICOLA-BARMAH ROAD, PICOLA VIC 3639 |  |  | Bird | [5 empty] | VicFire reported a fire at the incident location. On arrival the crew found that a dead large sized bird had flashed over on Pole 312. The bird fell to the ground and started a grass fire, burning an area of grass approximately 5 by 20mtrs. CFA attended. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 20/03/2016 12:21 | 1 | Small: 10 - 1000 sq.m | 1090 | Agricultural |  | 20160322PWA_10 | Infrastructure (network-based) | -35.9995 | 145.0661 | 1 | Powercor | Report | 1557 | 0.0083808 | 22kV AC | Shepparton Airport | 3639 | Picola | Animal
Crew isolated supply and undertook repairs | ROSTRATA, 1240 DUNOLLY-RHEOLA ROAD, MURPHYS CREEK VIC 3551 |  | Working too close to underground cables | [5 empty] | 2 | Customer reported excavator dug up underground cable at the incident location. On arrival the crew found that an excavation had occurred adjacent to 12.7 kV SWER substation pole, partially severing the HV earth. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  |  | Excavator dug up underground cable at the incident location | No Go Zone (contact) | 22/03/2016 14:59 |  |  | 1098 | Agricultural |  | 20160323PWA_03 | Infrastructure (network-based) | -36.7449 | 143.7739 | 1 | Powercor | Report | 1566 | 0.021249 | 12.7kV AC (SWER) | Bendigo Airport | 3551 | Murphys Creek | Dug up
Crew isolated supply and undertook repairs. | UNIT 2 9-11 KYLE ROAD, ALTONA NORTH VIC 3025 |  | Vandalism | [5 empty] | 1 | A customer reported power outage at their premises at the incident location. Upon arrival, the Powercor crew found that the HV fuses opened by unknown third party using homemade conduit/operating stick. There was a hole in the outer fence of this substation that may have used to enter to the sub. There were no injuries or third party property damages. | Conductor (insulated) | 0 | 0 | 0 |  |  | Interference to Powercor asset by unknown third party | Loss of supply | 29/03/2016 4:53 |  |  | 1119 | Residential |  | 20160330PWA_06 | Infrastructure (network-based) | -37.8309 | 144.8563 | 1 | Powercor | Report | 1591 | 0.0010289 | 22kV AC | Laverton Raaf | 3025 | Altona North | Other
Crew isolated supply and undertook repairs | LOCKHARTS ROAD, STRATEN VIC 3533 |  |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | A customer reported no supply at the incident location. Upon arrival the crew found a Pole/Crossarm fire had occurred on a 22kV pole, resulting in a small ground fire in a stubble paddock. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  |  | pole and cross-arm fire | Pole-top fire | 25/03/2016 15:51 | 1 | Negligible: no ground fire | 1121 | Agricultural |  | 20160330PWA_08 | Infrastructure (network-based) | -35.3882 | 142.6073 | 1 | Powercor | Report | 2860 | 0.00037847 | 22kV AC | Swan Hill Aerodrome | 3533 | Straten | Crossarm
Crew isolated supply and undertook repairs. | 70 SOUTH WHARF DRIVE, DOCKLANDS VIC 3008 | 780993 | Working too close to underground cables | [5 empty] | 2 | An on site worker reported that a contractor (JLM Underground Solutions 1/25 Macquarie Dr Thomastown 3074. Lucas Smith 0413 337 807) had contacted an underground cable while excavating at the incident location. On arrival the crew found that contact had been made to a live low voltage underground service. There were no reported injuries or third party property damages. | Services cable | 0 | 0 | 0 |  | DLF01 | Contractor contacted an undergorund cable while excavating | No Go Zone (contact) | 23/03/2016 7:38 |  |  | 1126 | Roadway |  | 20160331PWA_02 | Infrastructure (network-based) | -37.8222 | 144.9367 | 1 | CitiPower | Report | 3060 | 0.018627 | Low voltage AC (<1kV) | Essendon Airport | 3008 | Docklands | Dug up
Crew isolated supply and undertook repairs. | 191 HAMILTON HIGHWAY, LISMORE VIC 3324 |  |  |  |  | Leakage |  |  | 1 | Customers reported an interruption to supply. On arrival the crew found a HV cross-arm fire had occurred on a low HV conductor span across the Highway. There was no injuries, ground fire or third party property damage reported. | Crossarm (wood) | 0 | 0 | 0 |  |  | Cross-arm fire | Pole-top fire;Loss of supply | 42404.4076 | 1 | Negligible: no ground fire | 1131 | Roadway |  | 20160404PWA_02 | Infrastructure (network-based) | -37.9526 | 143.3221 | 1 | Powercor | Report | 3148 | 0.015508 | 22kV AC | Ballarat Aerodrome | 3324 | Lismore | Crossarm
Tractor bought down low voltage service cable. | 434 HOPKINS FALLS ROAD, CUDGEE VIC 3265 |  | Working too close to overhead lines | [5 empty] | 2 | Customer reported tractor had â€œripped down wire in paddock that goes to houseâ€. On arrival the crew found the Low Voltage overhead service wire from Pole to the house had been pulled down and customer end Point of Attachment damaged. Crews removed damaged service wire and issued defect notice. There were no reported injuries or other third party property damages. | Conductor (insulated) | 0 | 0 | 0 |  |  | Crews isolated supply removed damaged service wire and issued defect notice. | No Go Zone (contact) | 42433.6667 |  |  | 1133 | Agricultural |  | 20160404PWA_04 | Infrastructure (network-based) | -38.3319 | 142.657 | 1 | Powercor | Report | 1614 | 0.039068 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Cudgee | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. CEOT advised the DAO to attend. The fault crew replaced the mains box (FOLCB) and restored supply. The DAO attended on 3/4/16, notes and photos were taken. Scraps of copper with scorching and discolouration were gathered The Immediate area cleaned up. | 70 PHILLIPS ROAD, TOOLANGI VIC 3777 | 1401103 |  |  |  | Corrosion;Overheated connection |  | Phase to phase | 2 | IMS 221336. A three phase LV fused mains box was burnt out on a termination substation pole, LIS 14-01103. Melted plastic fell to ground igniting the bracken fern and burnt the supply mains wires. A small ground fire of approximately 2 m x 10 m in size was observed at the site. The CFA attended. It appears that either a connection within the FOLCB or the LV fuse has caused an excessive amount of heat which has melted the plastic of the FOLCB, dropping hot blobs of melted plastic to the ground at the base of the pole. There was light scorching of the pole but no sustained damage. | Any other type;Connection box | 0 | 0 | 0 |  | klk1 | Either a faulty connection within the FOLCB or the LV fuse has caused an excessive amount of heat which has melted the plastic. | Grassfire | 42404.4208 | 1 | Small: 10 - 1000 sq.m | 1134 | Agricultural |  | 20160404SPN_01 | Infrastructure (customer connection) | -37.5435 | 145.4919 | 1 | AusNet Services Distribution | Report | 1616 | 0.014139 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3777 | Toolangi | Connection
CEOT dispatched a fault crew and the DAO to attend the incident site. The fault crew restored supply to customers. Emergency services on-site. The attending Policeman was (McMillan). The DAO took several photos of the site which looked to be located in between poles 2515091 & 2515092, as they was evidence of flattened crops directly under the HV line. The line is a 3 phase 22kV line with 3/2.75 steel conductor. There were no flash marks on the line that the DAO could see from the ground using the zoom lens on his camera. | 177 UPPER MAFFRA ROAD, NEWRY VIC 3859 | 2515093 | Manned aircraft |  |  |  |  | Phase to phase | 1 | IMS 221338. An ultralight plane has clipped HV overhead lis#2515093, no damage to AusNet Services' assets. No electric shock. Electrical protection operated - Newry ACR reclosed, blew 40E BA @ 805895. Pilot was hurt from the crash. DAO comments: I arrived on site at approximately 3:40PM to find an aircraft had been packed up and on the side of the field. On site were 2 people Dave & Wendy. Dave identified himself as a friend of the pilot. Dave told me the pilot had run into the HV line with his aircraft and was flown via helicopter to the Alfred hospital in Melbourne. They were about to leave to get another vehicle to pick the air craft up. I asked them where the incident happened in which they pointed me in the direction of the field with power lines. | Conductor (bare) | 0 | 0 | 0 |  | mfa22 | An ultra-light plane contacted overhead HV line. | Medical attention (first aid/doctor/hospital) | 42433.5271 |  |  | 1136 | Agricultural |  | 20160404SPN_03 | Infrastructure (network-based) | -37.917 | 146.8747 | 2 | AusNet Services Distribution | Report | 1620 | 0.029023 | 22kV AC | Morwell (Latrobe Valley Airport) | 3859 | Newry | Other
The attending Powercor Fault Crew replaced the O/H Neutral Screened Service Cable between the Reticulation Pole and the Service Pole and the property situated at 59 Orton Street and completed an NST Test at 57 & 59 Orton Street which both confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, Customers metallic Meter Enclosure, distribution assets and between points of contact, confirmed 0.3 Volts following replacement of the O/H Service Cables. The following additional tests were also performed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated zero amps flowing in the earth. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The installation was left ON supply. | 57 ORTON STREET, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr John Trevean received an electric shock while investigating an Electricity Supply Failure at his neighbourâ€™s property when he made simultaneous contact with his hand on the metallic Meter Enclosure and his bare feet whilst standing on the damp concrete. | Service conductor | 0 | 0 | 0 |  |  | Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole Connection Box, resulting in a higher than normal impedance within the O/H Neutral Service Conductor supplying both properties situated at 57 and 59 Orton Street Ocean Grove. | Minor shock | 23/03/2016 17:00 |  |  | 1144 | Residential |  | 20160406PWA_01 | Infrastructure (network-based) | -38.2694 | 144.5206 | 1 | Powercor | Report | 3136 | 0.011 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Repairs completed supply restored | 10-14 VANESSA DRIVE, RAVENHALL VIC 3023 | 824636 |  | Asset covered by growth, deposition or detritus;Other |  |  |  |  | 1 | A customer reported a power outage at the incident location. On arrival, the Powercor crew found that the LV pillar had been damaged by an excavator while the operator was cleaning the vacant ground. There were no reported injuries. There was no fire. | Services pit | 0 | 0 | 0 |  | SU015 | damaged by an excavator while the operator was cleaning the vacant ground | Loss of supply | 42464.4792 |  |  | 1146 | Public space |  | 20160406PWA_03 | Infrastructure (network-based) | -37.7679 | 144.7519 | 1 | Powercor | Report | 1634 | 0.027022 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Ravenhall | Vehicle
Crew isolated supply and undertook repairs | 40 RYANS ROAD, MILLBROOK VIC 3352 | 920684 |  |  |  | Candled fuse |  |  | 2 | A Fault crew attending an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | EDO fuse | 0 | 0 | 0 |  | BAN011 | EDO fuse barrel did not drop out | Other electricity related | 42525.2431 |  |  | 1156 | Roadway |  | 20160408PWA_03 | Infrastructure (network-based) | -37.5827 | 144.0717 | 1 | Powercor | Report | 1646 | 0.030147 | 22kV AC | Ballarat Aerodrome | 3352 | Millbrook | Fuse
Crew Undertook repairs | 102 KURTING-POWLETT ROAD, KURTING VIC 3517 | 408815 |  |  |  | Leakage |  |  | 1 | Crew reported a fire at the incident location. On arrival the crew found that a pole fire had occurred on a 22kV pole, which burnt through the cross arm at the strap, causing the insulator and conductor to fall to the ground. This resulted in a ground fire (approx. 25m x 25m) on private property. Protection operated. There were no reported injuries. | Crossarm (wood) | 0 | 0 | 0 |  | EHK024 | Cross-arm fire | Grassfire | 42525.7083 | 1 | Small: 10 - 1000 sq.m | 1158 | Agricultural |  | 20160408PWA_05 | Infrastructure (network-based) | -36.5343 | 143.8211 | 1 | Powercor | Report | 1648 | 0.030441 | 22kV AC | Bendigo Airport | 3517 | Kurting | Crossarm
CEOT sent crew to investigate, make safe and restore supply. Replaced EDO fuse tube and a 6k EDO fuse. Action assigned to raise notification in SAP for replacement of EDO with BA fuse units. | 3118 PRINCES HIGHWAY, KALIMNA WEST VIC 3909 | 1900249 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 221421. LIS#1900249 - 1 HV EDO Fuse Candled / burnt - No fire. Single phase substation on concrete pole. No evidence of pole fire or ground fire. | EDO fuse | 0 | 0 | 0 |  | bdl6 | Candled EDO fuse. | Other electricity related | 42586.5646 | 1 | Negligible: no ground fire | 1159 | Agricultural |  | 20160410SPN_01 | Infrastructure (network-based) | -37.8644 | 147.9519 | 1 | AusNet Services Distribution | Report | 1650 | 0.028904 | 22kV AC | Bairnsdale Airport | 3118 | Kalimna West | Fuse
Fault crew reconnected the loose neutral conductor. | 13 SYMONS STREET, PRESTON VIC 3072 |  |  |  |  | Neutral fault |  |  | 2 | Customer recieved minor shocks from shower taps | Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Loose service neutral | Minor shock | 42525.6806 |  |  | 1164 | Residential |  | 20160411JEM_03 | Infrastructure (network-based) | -37.7307 | 144.9891 | 1 | Jemena | Report | 1656 | 0.018681 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Connection
Made safe | 13 DAVIS AVENUE, AVONDALE HEIGHTS VIC 3034 |  |  |  |  | Neutral fault |  |  | 2 | Customer received a shock from the kitchen taps | Service conductor | 0 | 0 | 0 |  |  | Faulty neutral screen service | Minor shock | 42708.3972 |  |  | 1172 | Residential |  | 20160412JEM_03 | Infrastructure (network-based) | -37.759 | 144.8589 | 1 | Jemena | Report | 1664 | 0.036331 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | OH Cable
Crew isolated supply and undertook repairs | 1 ROACH DRIVE, ALTONA MEADOWS VIC 3028 | 213606 |  |  |  | Leakage |  |  | 1 | Fault crew attending an outage found a pole fire at the incident location No HV injection reported. There was no ground fire. There were no reported injuries or third party damage. | Crossarm (wood) | 0 | 0 | 0 |  | LVN022 | Excessive leakage current | Pole-top fire | 42525.3229 | 1 | Negligible: no ground fire | 1171 | Roadway |  | 20160412PWA_03 | Infrastructure (network-based) | -37.8843 | 144.7851 | 1 | Powercor | Report | 3150 | 0.037244 | 22kV AC | Laverton Raaf | 3028 | Altona Meadows | Pole
On arrival Repairs done under controlled shut down | LORNE LANDFILL, 370 ERSKINE FALLS ROAD, LORNE VIC 3232 | 29154 |  | Blown branch/vegetation |  |  |  |  | 1 | CFA reported that 22kv conductor down on the road at the incident location On arrival the Powercor crew found that a load side conductor of HV line on the ground There was no ground fire. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  | CLC005 | Vegetation: Trees Incident | Loss of supply | 42525.309 |  |  | 1174 | Roadway |  | 20160412PWA_05 | Infrastructure (network-based) | -38.5307 | 143.9496 | 1 | Powercor | Report | 2941 | 0.006544 | 22kV AC | Avalon Airport | 3232 | Lorne | Trees
On arrival crew made site safe Service to be restored by REC as it was a private service | 1207 SIMMIE ROAD, ECHUCA VIC 3564 | 32812 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Customer reported a wire down at the incident location. On arrival the crew found that private service cable off the substation pole had been hit by a front end loader working in the vicinity. The service to the dairy was live on the ground as it was detached from the dairy end. There were no reported injuries. There was no ground fire | Service conductor | 0 | 0 | 0 |  | ECA005 | Front end Loader striking pole | Loss of supply | 42525.5792 |  |  | 1183 | Agricultural |  | 20160413PWA_06 | Infrastructure (network-based) | -36.2254 | 144.8139 | 1 | Powercor | Report | 1675 | 0.026602 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | Vehicle
On arrival crew isolated supply | 382 SHINNICKS ROAD, KATUNGA VIC 3640 | 3063 | Crane, excavator or other construction/farming equipment |  | Highly unlikely |  |  |  |  | Customer reported an excavator knocked over a pump shed and meter panel at the incident location. On arrival the crew found that an excavator had backed into a pump shed while carrying out channel works. The pump shed and meter panel were knocked over, exposing the private mains at the base of the meter panel. There were no reported injuries. | Customer installation | 0 | 0 | 0 |  | NKA006 | excavator hit pump shed | Loss of supply | 42555.4417 |  |  | 1185 | Agricultural |  | 20160413PWA_08 | Infrastructure (network-based) | -35.9602 | 145.4042 | 1 | Powercor | Report | 8029 | 0.026483 | Low voltage AC (<1kV) | Shepparton Airport | 3640 | Katunga | Vehicle
The site was made safe and existing cable replaced | 1 WESTON STREET, BALWYN VIC 3103 | 13975 | Vehicle | [6 empty] | A customer reported that their service cable brought down by a vehicle at the incident location. On arrival the crew found that the service wire on the ground.There was no ground fire. There were no reported injuries. | Service conductor | 0 | 0 | 0 |  | L004 | Vehicle striking service cable | Loss of supply | 42555.4319 |  |  | 2186 | Roadway |  | 20160414PWA_01 | Infrastructure (network-based) | -37.8117 | 145.0775 | 1 | CitiPower | Report | 2694 | 0.018269 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Vehicle
On arrival crew isolated supply and carried out repair It should be noted that on arrival PAL crew observed CFA personnel walking near the fallen conductor putting out the fire, the CFA crew had not confirmed the electrical condition of the conductor. The PAL crew have reported this activity as potentially dangerous. | ABATTOIRS ROAD, PYRAMID HILL VIC 3575 | 775583 |  |  |  | Overheated connection |  |  | 2 | VicFire reported a fire at the incident location. On arrival the crew found that a conductor had failed at the strain pole and had fallen onto the ground. This caused a number of grass fires to start along where the conductor was laying. These fires were approximately 1 by one meter. Conductor was live via back feed. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  | CHA006 | overheated connection | Grassfire | 13/04/2016 8:19 | 1 | Localised: less than 10 sq.m | 2193 | Agricultural |  | 20160414PWA_06 | Infrastructure (network-based) | -36.0558 | 144.1277 | 1 | Powercor | Report | 2685 | 0.00045023 | 22kV AC | Bendigo Airport | 3575 | Pyramid Hill | Connection
On arrival crew isolated supply and carried out repairs | WALTONS ROAD, WINDEMERE VIC 3352 | 751395 | Theft | [5 empty] | 2 | Electrix reported that the earth cable on the Substation pole at the incident location had been cut. Upon arrival the crew found that approx. 2m of the HV earth cable had been stolen. There were no reported injuries, ground fire or third party damage. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Theft of earthing system | Loss of supply;Damage to network assets | 42678.5326 |  |  | 2198 | Roadway |  | 20160415PWA_01 | Infrastructure (network-based) | -37.4987 | 143.7272 | 1 | Powercor | Report | 8055 | 0.019302 | Earthing cable | Ballarat Aerodrome | 3352 | Windemere | Other
On arrival crew isolated supply and undertook repairs | 434 WENDOUREE PARADE, LAKE WENDOUREE VIC 3350 | 21412 |  |  | Highly likely |  | Not followed |  | 2 | A Powercor customer reported a pole with transformer sparking and banging at the incident location. On arrival the crew found that the HV leads connecting the transformer had caught fire. There was no fire damage to the pole, and no ground fire. No Protection operated. There were no reported injuries. | Pole mounted | 0 | 0 | 0 |  | BAN002 | Cause consistent with insulation breakdown due to proximity of surge diverter lead. No specific investigation conducted. Light misty rain at time of attendance to the incident - temp of approx. 12 Deg C | Melting or smoking only | 42678.059 |  | Negligible: no ground fire | 2200 | Roadway |  | 20160415PWA_03 | Infrastructure (network-based) | -37.5437 | 143.836 | 1 | Powercor | Report | 3320 | 0.0046863 | 22kV AC | Ballarat Aerodrome | 3350 | Lake Wendouree | OH Cable
CEOT dispatched a fault crew to make safe and investigate. Restoration works commenced once traffic control arrived several hours later and was completed about 1730. The height of the conductors at the point of contact was measured at 7.25m. Linesman was on-site to repair & obtained driver's details & truck registration number. The conductor was still in good condition & was sleeved in several places & pulled back up after termination pole x-arm was straightened. | 745 FULLERS ROAD, FOSTER VIC 3960 | 2025278 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 221507. CEOT received a call stating that a tip truck has pulled a power line down across a driveway. The truck stuck on site. Contact Frank 0407343 744. Tip truck entered a paddock to dump sand. The driver was not aware of the overhead HV lines & raised the bucket to dump under single phase HV. With bucket raised he then drove into the line while attempting to empty the bucket. The truck broke one of the steel conductors which then caused the crossarm at termination pole 2025278 to swivel around the pole. Observed 3 burn marks on the grass where the wheels of the truck were at time of contacting the OH line. The contact caused the tee-off fuse 818185 at pole 2026021 to operate. The conductor came down onto Fuller Rd which was temporarily closed until the conductors were cut and removed from the pole. No shock or injury was sustained by the driver. | Conductor (bare) | 0 | 0 | 0 |  | ftr22 | Tip truck contacted overhead HV line. NGZ breach. | No Go Zone (contact) | 14/04/2016 12:59 |  |  | 2197 | Agricultural |  | 20160415SPN_01 | Infrastructure (network-based) | -38.7172 | 146.1877 | 1 | AusNet Services Distribution | Report | 2691 | 0.0096759 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Foster | Vehicle
The crew isolated supply, made area safe and later replaced the pole, re-attached service wires and public light. | 49 WEST ESPLANADE, ST ALBANS VIC 3021 | 30335 | Vehicle | [5 empty] | 2 | Police reported a car hit a power pole at intersection of West Esplanade and Margrave Street, St Albans. On arrival the crew found that a car had collided with a wood pole. The pole broke at ground level causing it to fall over a steel fence on the boundary line of the railway reserve, and 2 live service wires were on the ground over the road. The police informed the crew that the driver of the car had been taken to hospital by ambulance. There was no shock or ground fire reported. | Service conductor;Pole (wood) | 0 | 0 | 0 |  | SSE031 | Vehicle impact | Loss of supply;Damage to network assets | 15/04/2016 23:39 |  |  | 2211 | Roadway |  | 20160418PWA_01 | Infrastructure (network-based) | -37.7374 | 144.7956 | 1 | Powercor | Report | 8057 | 0.038352 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
On arrival crew isolated Circuit at Kiosk substation, underground crew to repair cable later this evening | 53 FRYERS STREET, SHEPPARTON VIC 3630 | 41088280 | Working too close to underground cables | [5 empty] | 2 | A customer reported that a contractor has hit the underground mains cable at the incident location. On arrival the crew found that a contractor was operating an boring machine and contacted a underground LV mains cable causing damage to the cable. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  | SHN014 | Contractor bored into underground cable | Loss of supply | 18/04/2016 13:29 |  |  | 2220 | Commercial |  | 20160419PWA_01 | Infrastructure (network-based) | -36.3789 | 145.4005 | 1 | Powercor | Report | 2740 | 0.03944 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Dug up
On arrival the crew found that the LV service was on the ground, and the crew carried out repairs. | 75 FORTUNA AVENUE, BALWYN NORTH VIC 3104 |  | Working too close to overhead lines | [6 empty] | Owner of the property reported, that the service wire to their house was hit by a crane at the incident location. The crane is owned by a builder working at the incident location. | Service conductor | 0 | 0 | 0 |  |  | Crane activity on property | Loss of supply | 19/04/2016 17:34 |  |  | 2225 | Construction |  | 20160420PWA_03 | Infrastructure (network-based) | -37.7876 | 145.0768 | 1 | CitiPower | Report | 2768 | 0.026073 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | Vehicle
MFB arrived to put out fire. Xarm replaced by crew. | 33 DOUGHARTY ROAD, HEIDELBERG WEST VIC 3081 |  | Vehicle | [5 empty] | 2 | Unknown vehicle had struck the pole causing the High Voltage tie on the centre phase to break and the conductor to fall onto the HV X-Arm. This caused the X-Arm to smoulder. | Crossarm (wood) | 0 | 0 | 0 |  |  | Unknown vehical had struck the pole causing the HV tie on the centre phase to break and the conductor to fall onto the HV X-Arm. This caused the X-Arm to smoulder. | Pole-top fire | 22/04/2016 3:09 | 1 | Negligible: no ground fire | 2235 | Residential |  | 20160422JEM_01 | Infrastructure (network-based) | -37.7352 | 145.0566 | 1 | Jemena | Report | 2794 | 0.016508 | 22kV AC | Essendon Airport | 3081 | Heidelberg West | Vehicle
On arrival Crew made safe and commenced repairs | 6B BENTLEY DRIVE, DEER PARK VIC 3023 | 41088718 | Theft | [5 empty] | 2 | A Powercor contractor reports that copper straps have been stolen from a kiosk substation in the Sunshine area. On arrival the crew found that thieves are targeting the copper earth door straps on the kiosk substation. . There were no reported injuries. There was no fire. | Earth/earthing | 0 | 0 | 0 |  | SU013 | Copper theft | More than $50k damage | 21/04/2016 12:30 |  |  | 2236 | Public space |  | 20160426PWA_01 | Infrastructure (network-based) | -37.7793 | 144.7623 | 1 | Powercor | Report | 2783 | 0.018804 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
Voltage tests between an independent earth and various points of the electrical installation including the distribution assets, revealed a corroded neutral connection on the service pole junction box. The attending LEI called for a service truck, which removed the corroded connection and reconnected the neutral in the service pole junction box. The attending LEI the performed testing between an independent earth and various parts of the installation including the water pipes and detected zero volts | 6 HAGGAR STREET, EAGLEHAWK VIC 3556 | 414477 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Goss was washing the dishes when she made simultaneous contact between the metallic water tap and the metallic sink and received an electric shock. | Connection box | 0 | 0 | 0 |  | EHK031 | corroded neutral connection on the service pole junction box. | Minor shock | 25/04/2016 13:30 |  |  | 2246 | Residential |  | 20160426PWA_08 | Infrastructure (network-based) | -36.7195 | 144.2567 | 1 | Powercor | Report | 2796 | 0.025446 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Eaglehawk | Connection
CEOT dispatched a fault crew to isolate, make safe and investigate. The fault crew replaced fuse and fuse tube. No obvious cause. | 350 LONG GULLY ROAD, PANTON HILL VIC 3759 | 29385 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 221561. Customer report of no power. Fuse down on pole. Fault crew found a candled EDO fuse on the ground. No fire on pole or ground. | EDO fuse | 0 | 0 | 0 |  | drn23 | Candled EDO fuse. | Other electricity related | 19/04/2016 18:36 | 1 | Negligible: no ground fire | 2243 | Agricultural |  | 20160426SPN_01 | Infrastructure (network-based) | -37.6398 | 145.252 | 1 | AusNet Services Distribution | Report | 2791 | 0.011759 | 22kV AC | Essendon Airport | 3759 | Panton Hill | Fuse
On arrival crew made safe and commenced repairs | 19 OBERON STREET, ALFREDTON VIC 3350 | 781953 | Working too close to underground cables | [5 empty] | 2 | An excavation contractor reported that they had just hit an LV underground cable that goes to a streetlight outside the incident location. On arrival the crew found that a contractor was excavating on the road reserve and contacted a LV underground cable to a streetlight, causing damage to the cable. There were no reported injuries or third party property damages. | Cable | 0 | 0 | 0 |  | BAS024 | Contractor carrying out excavation Paul Berriman, Berriman Earthworks PO BOX 1706, Bakery Hill, 3354 Dial Before you Dig enquiry not located in search of our records. No record of permit to work being issued. | No Go Zone (no contact) | 26/04/2016 12:10 |  |  | 2251 | Roadway |  | 20160427PWA_05 | Infrastructure (network-based) | -37.5585 | 143.7894 | 1 | Powercor | Report | 2836 | 0.01428 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Alfredton | Dug up
Downer fault truck already onsite and replaced the overhead Neutral Screen Service cable prior to LEI's arrival onsite. REC was in the process of replacing the Main Switchboard whilst the LEI was onsite and required a Prescribed CES before property can be reconnected. The LEI was not able to perform any tests. NCID issued to REC to have work Inspected before supply can be reconnected. Property Left Off Supply. CEOT (Control Room) notified the LEI required for reconnection. | 28 ROSE AVENUE, BORONIA VIC 3155 | 1219667 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 221031. Penelope Stefanopoulous, an Electrician, (tel 1300 05 06 07) was in the process of replacing the Main Switchboard at 28 Rose Ave, Boronia. All the switchboard's wiring had been removed and when Penelope made contact to one of the un-terminated conductors she felt a tingle to her wrist. Cause of shock is unknown but possibly volts present on the un-terminated neutral conductor at the switchboard due to poor connection at pole end or faulty neutral screen service which was replaced prior to AusNet Services' LEI's arrival. The LEI was unable to perform any tests due to supply not available until REC issues a Prescribed CES for reconnection. | Service conductor | 0 | 0 | 0 |  | bra21 | Appears to be a high neutral impedance fault. | Minor shock | 15/03/2016 2:45 |  |  | 2265 | Residential |  | 20160428SPN_02 | Infrastructure (network-based) | -37.8579 | 145.274 | 1 | AusNet Services Distribution | Report | 2819 | 0.041411 | Low voltage AC (<1kV) | Moorabbin Airport | 3155 | Boronia | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the large tree branch was removed. | 12 LANCASTER STREET, ASHBURTON VIC 3147 | 2317447 | Unknown external/community factor | Wind;Alive |  | Conductor clashing | Unknown work practice factor |  | 1 | At 1337hrs on 18/03/2016, 11kV feeder EM 07 circuit breaker reclosed to lockout affecting 1037 customers. The MFB called to advise that a tree is on fire outside 10 Lancaster Street. During strong gusty winds, a large tree branch from a council tree located outside 12 Lancaster Street, Ashburton contacted the 11kV overhead conductors that caused the HV and LV conductors to clash near pole No. LIS 2317447. Molten metal fell into the dry grass below and a small 5sqm started that was extinguished by the CFA. Secondary damage occurred with ampact connections failing at HV switches OA0059 and OA0751. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | EM 07 | Vegetation: Trees Incident | Grassfire | 18/03/2016 13:37 | 1 | Localised: less than 10 sq.m | 2260 | Roadway |  | 20160428UTD_02 | Infrastructure (network-based) | -37.8689 | 145.0907 | 1 | United Energy Distribution | Report | 2813 | 0.0039479 | 11kV AC | Moorabbin Airport | 3147 | Ashburton | Trees
The glove and barrier crew that were removing the set of HV mid span isolators in Norwood Street, were sent to Trent Street and cut away the tree branches that were in contact with the HV conductor. United Energy requested that ZNX provide a summary investigation report along with preventative measures that will be put in place to avoid a re-occurrence. | TRENT STREET, GLEN IRIS VIC 3146 | LIS No. 2310919 | Unknown external/community factor | Unknown environment factor |  | Out of balance load | Inappropriate tools/plant/equipment |  | 2 | ZNX had a planned job to remove the HV and LV overhead conductors between pole No's LIS 2310919 and 2310920 in Trent Street, Glen Iris. Upon completion their task was to connect new HV and LV underground cables to the poles following the completion of pre-commissioning tests and remove a set of HV mid span isolators in Norwood Street using glove and barrier techniques with the HV feeder RD 04 auto reclose suppressed. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | RD 04 | A new footpath stay appeared to have moved. | Other vegetation | 16/03/2016 13:45 | 1 | Negligible: no ground fire | 2264 | Roadway |  | 20160428UTD_05 | Infrastructure (network-based) | -37.8492 | 145.0806 | 1 | United Energy Distribution | Report | 2817 | 0.04151 | 11kV AC | Moorabbin Airport | 3146 | Glen Iris | Trees
On arrival crew made site safe and commenced repairs | 29 HARVESTER AVENUE, SUNSHINE NORTH VIC 3020 | 21732 | Vehicle | [5 empty] | 1 | Passer-by reported that there was a loud bang at the incident location. On arrival the crew found that a semi-trailer had contacted an Optus cable which broke and contacted the high voltage overhead of the SSE22 feeder resulting in an auto reclose of the feeder and burnt of dropper on gas switch #36718 on the corner of Sussex Street and Northumberland Road. Protection operated. There were no reported injuries. There was no fire. | Conductor (bare);Communication cable/equipment | 0 | 0 | 0 |  | SSE022 | Truck hitting Optus cable which contacted HV overhead conductors | Loss of supply;Less than $50k damage | 29/04/2016 10:20 |  |  | 2277 | Roadway |  | 20160429PWA_07 | Infrastructure (network-based) | -37.7604 | 144.8365 | 1 | Powercor | Report | 2833 | 0.035836 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Vehicle
On arrival CitiPower crew carried out repairs whilst REC was onsite repairing POA | 8 KEMBLA STREET, HAWTHORN VIC 3122 | CLO022 | Vehicle | [5 empty] | 2 | A Double Decker bus made contact with the LV neutral screen aerial service to 8 Kembla St, Hawthorn. The service was came away from the fascia of the house and was resting on the footpath still connected to pole end. | Service conductor | 0 | 0 | 0 |  | 789151 | A Double Decker bus made contact with the LV neutral screen aerial service Bus Operator: Gym Bus rego 1A08574 PH 0429 770 277 | Less than $50k damage | 42374.6771 |  |  | 2282 | Roadway |  | 20160503PWA_01 | Infrastructure (network-based) | -37.8337 | 145.0396 | 1 | CitiPower | Report | 2841 | 0.016288 | Low voltage AC (<1kV) | Moorabbin Airport | 3122 | Hawthorn | Vehicle
CitiPower crew removed tree branches, repaired the conductor and reinstated supply. ESV 02/05/16 @ 09:03hrs â€“ ref 4988947 - Alisa | 229 YORK STREET, SOUTH MELBOURNE VIC 3205 | 40321 |  | Within clearances |  | Conductor clashing |  |  | 1 | A council Palm treeâ€™s branches pushed 2 LV conductors together causing them to clash and blow LV circuit fuses. CFA and Victoria Police attended. There was no ground fire, no reported injuries or third party property damage | Conductor (bare) | 0 | 0 | 0 |  | MG009 | Vegetation: Trees Incident | Loss of supply | 42374.6569 |  |  | 2284 | Roadway |  | 20160503PWA_03 | Infrastructure (network-based) | -37.8327 | 144.9538 | 1 | CitiPower | Report | 2843 | 0.036097 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Junction Box at the Reticulation Pole, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing Pole Junction Box at the Reticulation Pole and completed an NST test which confirmed a Pass result. | NELSON COTTAGES, 22 KELLETT STREET, NELSON VIC 3292 | 905770 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Lomas reported evidence of a voltage on the metallic support post of the Caravan Park Power Outlet Head. Mr Lomas subsequently contacted a Registered Electrical Contractor to investigate the failed television reception at the Caravan Park. The REC identified evidence of a voltage and burn marks on the metallic enclosure of the Television Cable Splitter attached to an earthed metallic support post of the Caravan Park Power Outlet Head. No Electric shock was recieved | Connection box | 0 | 0 | 0 |  | ETSA001 | Corroded O/H Service Neutral Conductor termination at the Pole Junction Box at the Reticulation Pole | Less than $50k damage | 27/04/2016 11:00 |  |  | 2291 | Commercial |  | 20160504PWA_01 | Infrastructure (network-based) | -38.0489 | 141.0086 | 1 | Powercor | Report | 2850 | 0.02741 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3292 | Nelson | Connection
A faults crew attended and disconnected supply to the lantern and a further trouble order was created for ACE to attend and replace the defective 150w HPS lantern. | 15 HIGH STREET, DONCASTER VIC 3108 | LIS No. 7055641 | Unknown external/community factor | Precipitation |  | Moisture ingress;Fatigue | Unknown work practice factor |  | 2 | The MFB called to advise they have put out a street light fire. A 150w HPS lantern on pole No. 7055641 located outside 15 High Street, Doncaster caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown. | Pole-top fire | 26/04/2016 20:45 | 1 | Negligible: no ground fire | 2296 | Roadway |  | 20160504UTD_06 | Infrastructure (network-based) | -37.7869 | 145.105 | 1 | United Energy Distribution | Report | 2855 | 0.001662 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | AF Other
Jemena Work Practices contacted property and excavator owner to advise of the supply loss, splash marks on the overhead High Voltage conductor and No Go Zone requirements | 140 VINEYARD ROAD, SUNBURY VIC 3429 |  | Working too close to overhead lines | [5 empty] | 1 | High voltage feeder SHM11 tripped, ACR # 51635 successfully re-closed. Feeder fault likely to have been caused by excavator contact. | Conductor (bare) | 0 | 0 | 0 |  | SHM11 | Jemena Network Operator patrolled the High Voltage overhead conductors and found splash marks on the conductors. Parked near by was a large excavator with track marks under the conductor near the splash marks. | No Go Zone (contact) | 42434.625 |  |  | 2303 | Agricultural |  | 20160506JEM_01 | Infrastructure (network-based) | -37.6021 | 144.7124 | 1 | Jemena | Report | 12376 | 0.0033264 | 22kV AC | Melbourne Airport | 3429 | Sunbury | Vehicle
CEOT dispatched to a fault crew to make safe and repair. Isolated supply via gas switch pole 1 Olden Spur. Issued EAP repaired conductor and restored supply. | 1060 OUTTRIM-LEONGATHA ROAD, OUTTRIM VIC 3951 | 2005788 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 221734. A tree branch fallen on the 22kV line breaking the HV conductor and a ground shrub fire was observed in the vicinity of the broken conductor. Fire on ground - 90 square metres. Trees alight. Two CFA units attended and put the fire out after supply isolation. The burnt area followed the tree line along the fence and has burnt / damaged approximately 12 wooden fence posts. ACR tripped to lockout. One HV fuse operated. | Conductor (bare) | 0 | 0 | 0 |  | lga23 | Vegetation: Trees Incident | Bushfire | 42434.5299 | 1 | Small: 10 - 1000 sq.m | 2315 | Agricultural |  | 20160509SPN_03 | Infrastructure (network-based) | -38.5069 | 145.7685 | 1 | AusNet Services Distribution | Report | 2888 | 0.0088692 | 22kV AC | Morwell (Latrobe Valley Airport) | 3951 | Outtrim | Trees
Opened wl032 and dispatched fault crew. Reported to vegetation manager, network duty manager and east irt manager. Extracts from Asplundh report; The crew being aware of the potential has then taken measures to secure the scene and notify the AusNet Services' Control Room. Asplundh General Foreman determined there was no injury and he immediately attended the scene given the nature of the event. Suppression requirement: Whilst the crew had obtained suppression for the general feeder WGL15 they had not confirmed and verified suppression was required and activated for the ISO section they were working on. By over cutting the back cut the feller has increased the risk of the hinge breaking away when additional tension was placed on the rope to guide the tree over. By not effectively securing the rope to the tree to be felled in a higher position the crew have created the potential for the tree to overbalance when the scarf broke away. The supervisor had allocated work on the WGL 15 feeder and expected the crew to be working on spans within suppression application NEMS 313298 (WGL15 â€“ Ex z/s/s C/B). Given the weather conditions the crew made the determination to move to a more suitable location on the Mt Worth SWER which is fed by WGL 15. Due to being out of service for the tablet which holds the work, the crew were unable to check the suppression map and incorrectly determined that this section of SWER was covered by NEMS 313298. Had they checked their location, they would have realised that the section they were working on was in fact covered by a different suppressions application - NEMS 313301 (WGL15 ex Mt Worth SWER AR WL032). The investigating team have reviewed all given statements, advice, interviews, facts and reports at hand to find the following as noted: A very basic error on the part of the feller has combined with two other factors and resulted in the tree falling onto the SWER line. The crew by all determinations had been carrying out the works in a professional manner. Due consideration was given to the task at hand and thorough planning, setting up and communication was taking place throughout the works. 1. By overcutting the back cut the feller has significantly reduced any potential for the hinge to be effective when the tension was applied to pull the tree over. 2. Due to the position the rope was secured to the tree, there has been more weight above this point than below. When the tension was applied and the hinge broke away, the butt has come back towards the pulling point and effectively caused the tree to be in a position in which it leaned back beyond vertical towards the line. 3. Whilst the tree has initially began to fall sideways, the proximity to an adjacent acacia tree of similar height has resulted in it rolling against the acacia which has then redirected the direction of fall and gathering momentum directly towards the SWER line. Both workers are appropriately authorised to work on the Select Solutions/AusNet Services 'contract. * The Hazard Assessment Check had been completed satisfactorily. * Thorough communication and set up of process within the work crew. After the incident, Asplundh stood down the two man ground party involved. On receipt and review of the report, the crew members were allowed to return to the network under restricted conditions, including; â€¢ Both crew members will work as EWP operators (until further notice); â€¢ Partner each crew member with an experienced operator (experience in AusNet Services' Network / Suppressions). These conditions remain current pending review and approval of Select-Solutions. | 347 ALLAMBEE ESTATE ROAD, ALLAMBEE VIC 3823 | 2706626 |  | MEC |  |  |  | Phase to earth |  | IMS 221431. Tree clearer Jamie reported a tree on HV at 347 Allambee Estate Rd, Allambee, lis 2706627. Schedule 1 report missed by CEOT. INITIAL SUMMARY OF EVENT: On Sunday 10th April 2016 a two person, sub contract climbing crew, employed by VBL Tree Care were conducting works on behalf of Asplundh on the TGN contract. The work involved both climbing and tree felling activities. The crew was working on a property at 357 Allambee Estate Rd, Allambee. A number of mountain ash trees around 15 metres in height had been identified for removal. The wind was moderate to gusty and the crew had picked this location as the direction of the wind favoured the intended felling line. The crew was using a 3:1 mechanical advantage rigging technique to secure and tension the trees prior and to assist with the felling. The rope was attached approximately 1/3rd up from the base of the tree and secured to larger tree back in the direction of intended fall (700 â€“ 800 away from the SWER line). Three trees had been completed successfully using this method. The crew had comprehensively discussed and agreed on the work method to be undertaken to fell the trees. Once each tree was rigged and secured using the same 3:1 method the rope was tied off and secured using an alpine butterfly knot. Together they would then tension the tree to an agreed point where the tree lay slightly past vertical in the direction away from the SWER line. The feller would then apply the scarf, stop the saw and check with the off-sider. Once confirmed all was ok the feller would indicate he was commencing his back cut while the off-sider monitored the securing line. Once the back cut was complete the feller would return to the securing line and together they would then commence pulling the tree over. The crew have rigged a fourth tree (16m height, 350mm DBH) in the same manner however when the feller has applied the back cut he has cut to deep (overcut) which has resulted in almost all the hinge wood being removed. When he has returned to assist the off-sider to pull the tree over, the resulting force has caused the hinge wood to break clean through. This has caused the tree to overbalance, roll against an adjoining acacia tree and fall in the opposite direction and onto the SWER line. | Conductor (bare) | 0 | 0 | 0 |  | wgl15 | Vegetation: Trees Incident | Loss of supply | 42647.566 |  |  | 2319 | Agricultural |  | 20160510SPN_02 | Infrastructure (network-based) | -38.2841 | 146.0174 | 1 | AusNet Services Distribution | Report | 2896 | 0.011292 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3823 | Allambee | Trees
On arrival crew made site safe and commenced repairs | 179 KEPLER STREET, WARRNAMBOOL VIC 3280 | 16952 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Vicfire reported that there was a pole fire at the incident location. On arrival the crew found that an LV FSD had failed electrically, resulting in molten debris falling on a vehicle parked directly underneath. There were no reported injuries or ground fires. | Connection box | 0 | 0 | 0 |  | WBL010 | possible moisture ingress | Loss of supply;Less than $50k damage | 42618.4056 |  |  | 2327 | Roadway |  | 20160511PWA_02 | Infrastructure (network-based) | -38.3789 | 142.4838 | 1 | Powercor | Report | 2904 | 0.011576 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Fuse
On arrival crew made site safe and commenced repairs | 88 LES DRAFFINS ROAD, CARDIGAN VIC 3352 | 8500 | Theft | [5 empty] | 2 | Contractor reported missing earth cables at incident location. Crew attended and found LV earth cable missing at pole. Crew replaced missing cables. No shocks, injuries or third party damage. | Earth/earthing | 0 | 0 | 0 |  | BAS011 | Copper Theft | Less than $50k damage | 42618.6438 |  |  | 2334 | Roadway |  | 20160512PWA_01 | Infrastructure (network-based) | -37.5523 | 143.6852 | 1 | Powercor | Report | 2920 | 0.016714 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Cardigan | Other
Initial Report: CEOT dispatched a fault crew and an Electrical Inspector (LEI) to make safe, investigate and repair. Final Report: Damaged transformer was changed and tested by the crew. Supply restored. | 505 MILLARS ROAD, POUND CREEK VIC 3996 | 2808752 |  | Lightning | [5 empty] | IMS 221837. Initial Report: Transformer possibly hit by lightning. Replaced on 10/05/16. INCD: 102987-r. Customer has reported internal property damage, possibly related. Final Report: Transformer possibly hit by lightning. No confirmation of a HVI occurring. Due to the fact that apparently no HVI actually occurred then AusNet Services has changed the incident category from serious to a near-miss electrical incident in our IMS. As a result please be advised that a Schedule 2 report is not required and please do not record this incident in ESV's statistics for serious electrical incidents. | Pole mounted | 0 | 0 | 0 |  | wgl14 | It appears that lightning struck a substation transformer. | HV injection | 42679.3229 |  |  | 2332 | Agricultural |  | 20160512SPN_01 | Infrastructure (network-based) | -38.6231 | 145.8224 | 1 | AusNet Services Distribution | Report | 2912 | 0.017704 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3996 | Pound Creek | Lightning
On arrival crew made site safe and commenced repairs | 30 PALMERSTON STREET, MARYBOROUGH VIC 3465 | 807912 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A customer reported that a truck has struck and broke a cable at the incident location. On arrival the crew found that a grader on a low loader ( Operated by: Ballarat Excavations and Transport, 5 Nursery lane, Mitchell Park, Ph: 03 5339 3009) had contacted a LV service cable causing the cable to break and fall to the ground. Following repairs, the service cable height was measured at 5.6m at the point of contact. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  | MRO04 | Grader on back of lowloader striking service line | Loss of supply | 42709.3236 |  |  | 2340 | Roadway |  | 20160513PWA_01 | Infrastructure (network-based) | -37.0458 | 143.7345 | 1 | Powercor | Report | 2926 | 0.039036 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | Vehicle
All works associated with light pole installations stopped on site as advised by AusNet Services until investigation completed. UCS Correction actions/recommendations detailed with report. Discussion to take place with AusNet Services' Land Management group and main contractor on site. Existing permits to be cancelled and new permits applied for , with greater attention to detail on what works are taking place. New Permit to works to be issued based on discussion with contractor on site. | 88 HIGHPARK DRIVE, WOLLERT VIC 3750 | [5 empty] | Not followed |  | 2 | IMS 221560. PTW issued to install 2 poles under 500kV line. Contractor was erecting light poles along new road, not part of PTW or area discussed for the PTW. Contractor employee received shock due to induction. In erecting pole, contractor used synthetic slings however failed to follow their own established SWMS - #2 - Peru / Standing Poles that induction is identified as a risk, and mitigation practice is to earth plant & equipment and poles. The following is a summary from the incident investigation report compiled by Underground Cable Systems: UCS is the electrical contractor for the Lyndarum Estate, Stage 43A. Construction of the electrical works was conducted on the 14th and 15th April 2016. UCS utilised a subcontractor, X-Power, for cable hauling and light column erection on this project. The work included erecting of public light columns in Highpark Drive and along Woodson Drive. Running parallel to Woodson Drive and crossing Highpark Drive is an Electrical Transmission Line. Within the electrical design it had been identified that when installing 2 of 24W FL â€œTSâ€ Greenstreet Lanterns on 5.5m mounting height â€œLincolnâ€ hinged poles in Highpark Drive the works would need to be conducted under permit. A permit was obtained for this location. Work at this location has not yet been undertaken. On 15th April an X-Power crew was undertaking the installation of Public Light Columns along Woodson Drive. No permit was specified nor obtained for the works along Woodson Drive. During the process of erecting the light column at the intersection of Woodson Drive and Wrexham Road (BID PO 2601626817) the light column was suspended from the carne truck with a synthetic sling. Whilst positioning the column the employee guiding the pole dropped the tag-line, and whilst attempting to regain the line made contact with the suspended light column. The worker received a shock from an apparently induced electrical charge on the column. Employee taken to nearest Emergency Department for assessment and treatment. Employee discharged with clearance to resume full duties. X-Power reported incident to Worksafe. UCS reported incident to Energy Safe Victoria. Energy Safe Victoria has informed UCS verbally that their requirements are being met through the process of providing compliance with WorkSafe. | Conductor (bare) | 0 | 0 | 0 |  | SMTS-SYTS No1 & 2 500kV Lines | When the X-Power employee dropped the tag line, and attempted to retrieve it, contact was made with the pole via the back of the employees hand and an induced electrical charge was felt by the X-Power employee. During the process of â€˜riggingâ€™ up the pole, consideration had not been given to the insulation effect of the synthetic slings that had been applied. In this operation the X-Power personnel failed to follow their own established SWMS -#2 â€“ Peru / Standing Poles which states, on page 4, at point 5 that identified hazards included â€˜induction from overhead power linesâ€™ and that the risk control measure(s) were to include â€˜ earthing plant & equipment and polesâ€™. | Minor shock | 15/04/2016 12:00 |  |  | 2347 | Commercial |  | 20160517SPN_01 | Infrastructure (network-based) | -37.6164 | 145.017 | 1 | AusNet Services Transmission | Report | 2939 | 0.021479 | 500kV AC | Essendon Airport | 3750 | Wollert | Other
On arrival crew made safe and restored supply | 17 BALMAIN STREET, CREMORNE VIC 3121 |  |  | Animal |  |  |  |  | 1 | Resident reported a loud bang and smoke coming out from adjacent Indoor Substation at the above incident location. On arrival the crew found that a rat had come across the HV switch within the Indoor Substation which caused the loud band and smoke. There were no reported injuries, No ground fire or Third Party damages. | Indoor | 0 | 0 | 0 |  | RO031 | Rat bridged out switch | Loss of supply | 14/05/2016 22:16 |  |  | 2354 | Residential |  | 20160518PWA_06 | Infrastructure (network-based) | -37.8298 | 144.9914 | 1 | CitiPower | Report | 2956 | 1.6204e-05 | 11kV AC | Essendon Airport | 3121 | Cremorne | Animal
Jemena secured substation access from public. Isolated incoming supply and outgoing no circuits | 50 BAKERS ROAD, COBURG NORTH VIC 3058 |  | Caused by REC/contractor | [5 empty] | 2 | Demolition contractor removed the wall of an indoor 22Kv substation exposing live 22Kv cables and connections to general worksforce | Customer installation | 0 | 0 | 0 |  | CN2 | Demolition Contractor failed to meet NGZ responsabilities | No Go Zone (no contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/05/2016 14:22 |  |  | 2362 | Construction |  | 20160520JEM_01 | Infrastructure (network-based) | -37.7269 | 144.9605 | 1 | Jemena | Report | 2968 | 0.020257 | 22kV AC | Essendon Airport | 3058 | Coburg North | Other
Pole replaced | FRANCISCOS ROAD, WONWONDAH VIC 3401 | 7257 |  | Precipitation |  | Leakage |  |  | 2 | ETSA reported a pole fire at the incident location. On arrival the crew found that a pole fire had damaged a wooden SWER tee off pole eyebolt position. The pole was subsequently replaced. There was no ground fire. There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  | HSM001 | pole fire during drizzly conditions | Pole-top fire | 19/05/2016 21:16 | 1 | Negligible: no ground fire | 2364 | Agricultural |  | 20160520PWA_01 | Infrastructure (network-based) | -36.8801 | 142.2607 | 1 | Powercor | Report | 2969 | 0.026868 | 12.7kV AC (SWER) | Horsham Aerodrome | 3401 | Wonwondah | Pole
site isolated and connection repaired, LEI arranged to inspect for HVI | 63 MITCHELL STREET, NORTHCOTE VIC 3070 | 73169 |  |  |  | Defective component |  |  | 1 | CitiPower crew attending an outage found a lead had detached from 11kV O/H conductor and contacted the LV circuit below at the incident location. Protection operated . HVI found to have impacted on some 30 meters and electrical equipment in installations . There were no reported injuries or fire. | Conductor (bare) | 0 | 0 | 0 |  | NC02 | Damaged connection, possibly due to previous fault | Less than $50k damage | 19/05/2016 2:29 |  |  | 2366 | Residential |  | 20160520PWA_03 | Infrastructure (network-based) | -37.7723 | 145.004 | 1 | CitiPower | Report | 2972 | 0.027907 | 11kV AC | Essendon Airport | 3070 | Northcote | Connection
Feeder protection operated correctly and isolated the fault. A Jemena fault crew attended and found that the contractor had struck and damaged two phases of the underground 66kV oil filled cables. The cables were isolated and earthed. Due to the damage to the cables, the entire WMTS â€“ FE No.1 66kV line has been taken out of service. | LLOYD STREET, WEST MELBOURNE VIC 3003 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | On 23 May 2016 a third party contractor performing civil works (horizontal borer) outside the West Melbourne Terminal Station dug up and damaged two cables on the WMTS â€“ FE No.1 66,000 Volt line exit. There was no injuries and feeder protection operated as planned so no loss of supply occurred. This incident was reported to Jemena Coordination Centre at approximately 11:02. A Jemena fault crew attended the work site and found that the drill had struck two phases of the High Voltage underground cable. There was minor impact to the white phase outer sheath, while the red phase cable sustained major damage, as a result, the WMTS â€“ FE No.1 66kV line could not be repaired at the time of the fault. Currently, Footscray East Zone Substation is running on single contingency supplying approximately 13,900 customers via the WMTS â€“ FE No.2 66kV line. The potential risks for an outage on the WMTS â€“ FE No.2 66kV line has been assessed, and mitigation plans have been developed and are in place. Jemena lacks the specialist resources to perform the necessary repair works to bring the WMTS â€“ FE No.1 66kV line back into commission. All major rectification works are being planned and carried out with assistance from Citipower and a third party specialising in oil filled cable repairs. It is concluded that the failure of the underground cable poses a risk to supply reliability for JEN customers and that the repair of the oil filled cables on WMTS â€“ FE No.1 66kV remains a priority to reduce the potential outages for customers supplied by Footscray East Zone Substation. | Cable | 1 | 1 | 1 | Citipower WMTS-JA No.3 66kV feeder | WMTS-FE No.1 66kV Feeder | Third party contractor performing civil works (horizontal borer) outside the West Melbourne Terminal Station dug up and damaged two cables on the WMTS â€“ FE No.1 66,000 Volt line exit. | Loss of supply;No Go Zone (contact);More than $50k damage | 23/05/2016 11:02 |  |  | 2371 | Public space |  | 20160523JEM_01 | Infrastructure (network-based) | -37.7996 | 144.9348 | 1 | Jemena | Report | 2978 | 0.03002 | 66kV AC | Essendon Airport | 3003 | West Melbourne | Dug up
On arrival crew made site safe and commenced repairs. | 37 CANOPUS CIRCUIT, LONG FOREST VIC 3340 | 101402 | Copper theft | [5 empty] | 2 | A contractor (Karl- Electrix ) reported that an earthing cable on the sub pole at incident location has been cut away. Upon arrival, the Powercor crew found that a 2m of LV earthing cable had been stolen from the pole. There was no reported shock, Ground fire or third party damages. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | BMH006 | Copper theft | Damage to network assets | 20/05/2016 11:17 |  |  | 2369 | Roadway |  | 20160523PWA_02 | Infrastructure (network-based) | -37.6438 | 144.5054 | 1 | Powercor | Report | 8061 | 0.012059 | Earthing cable | Melbourne Airport | 3340 | Long Forest | Other
CEOT dispatched a fault crew and LEI to make safe and investigate. Boric Acid fuses on lis pole 2602581 were replaced. Lis pole 2602573 required a HV bridge / D to be replaced as it was burnt / broken. The LEI completed all required tests and found that there were no defects with the electrical installation's wiring and all tests passed. NST test on installation was 0.36 Ohms after installation tested 0.44 V on neutral with a 30 A load. All the tests conducted by the LEI passed so the reason for the tingle could possibly be due to the fault current at the substation pole. | 10 PATRICIA COURT, TRARALGON VIC 3844 | 2602581 |  | Bird |  |  |  | Phase to earth | 1 | IMS 221691. A fault Crew was dispatched to 10 Patricia Court, Traralgon, for a fault. The customer was in the shower when the power went out and she felt a tingle. The customer was altering the water using the taps when two Boric Acid HV fuses on the substation were blown due to bird activity. The customer reported the electric shock to AusNet Services after turning off the taps where she felt no further tingles. There was also a burnt off D on the Red Phase down the HV line. The customer also said they saw a flash on the substation just before the power went out. The water pipes in the shower were bonded to the electrical installation's earth and the shower has a metal drain in a concrete slab. The installation has copper water pipes bonded to earth on concrete slab. | Boric acid | 0 | 0 | 0 |  | tgn43 | The tingles were possibly due to the fault current at the substation pole. | Minor shock | 30/04/2016 10:09 |  |  | 2378 | Residential |  | 20160525SPN_01 | Infrastructure (network-based) | -38.1861 | 146.5169 | 1 | AusNet Services Distribution | Report | 2988 | 0.035892 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Animal
On arrival crew made site safe and commenced repairs | 91 NICHOLSON STREET, WARRNAMBOOL VIC 3280 | 14062 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | An employee from a demolition company reported they had â€œaccidently pulled the service wireâ€ to a house in Nicholson St, Warrnambool. The overhead service wire from service pole (LIS 14062) to 91 Nicholson St crossed the front yard of the neighbouring property at 93 Nicholson St. and during the demolition works the service wire was damaged by an excavator. There was no shock, injuries, ground fire or other third party property damage reported. | Service conductor | 0 | 0 | 0 |  | WBL008 | Operation of excavator | Loss of supply | 25/05/2016 14:50 |  |  | 2387 | Residential |  | 20160526PWA_02 | Infrastructure (network-based) | -38.3896 | 142.4929 | 1 | Powercor | Report | 3003 | 0.017398 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
Work crew replaced the damaged HV cross arm and repaired the LV neutral conductor. | 14 SECOND AVENUE, MELTON SOUTH VIC 3338 | 109185 |  | Animal |  |  |  |  | 2 | Customer rang to advise they had heard a loud noise from a pole and power had tripped off for a moment but was now back on. Crew attended and found that a possum had made contact between the the HV and the LV neutral conductor. There was no ground fire, No shock, or injuries . LEI attended and indicated some HV injection had occurred | Conductor (bare) | 0 | 0 | 0 |  | MLN011 | Animal Incident | Less than $50k damage | 26/05/2016 22:30 |  |  | 2392 | Roadway |  | 20160527PWA_03 | Infrastructure (network-based) | -37.699 | 144.5741 | 1 | Powercor | Report | 3009 | 0.011836 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3338 | Melton South | Animal
On arrival crew made site safe and commenced repairs | 4 ROSS ROAD, MINERS REST VIC 3352 | 6358 | Copper theft | [5 empty] | 2 | n contract employee reported a missing earth cable at the incident location. On arrival the crew found that the high voltage earth cable had been removed. There was no ground fire. There were no reported injuries or third party property damages. | Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper theft | More than $50k damage | 27/04/2016 14:26 |  |  | 2273 | Roadway |  | 20160429PWA_05 | Infrastructure (network-based) | -37.4791 | 143.8292 | 1 | Powercor | Report | 2828 | 0.038946 | Earthing cable | Ballarat Aerodrome | 3352 | Miners Rest | Other
The faults crew arrived first and commenced preparation work to replace the open wire conductors with a new three phase XLPE overhead service cable. The LEI attended a short time afterwards and investigated the area where the alleged incident had occurred but didn't complete any testing above the shop veranda. The open wire service was replaced from the pole to the faÃ§ade mounted open wire service that was also replaced with a XLPE service cable. Therefore all of the old copper open wire conductors were removed and the site made safe. The LEI completed installation tests at the main switchboard after the faults crew completed their VESI tests. All tests passed and the shop was left on supply. | 48 STATION STREET, MOORABBIN VIC 3189 |  | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | Plumbers were attending the property to repair a leaking roof. They were on the veranda roof and a plumber received a slight electric shock to his shoulder when he made contact with a wire. A plumber who had left the site, received a slight electric shock when he made contact with the open wire service installed between the timber pole to the faÃ§ade mounted open wire service above the shop veranda. The shop was occupied by "George Lake Physio Therapy" in the small shopping strip. | Conductor (covered uninsulated);Service conductor;Copper | 0 | 0 | 0 |  |  | Old open wire service that was slightly frayed was accidentally touched by a plumber fixing a roof leak. | Minor shock | 42555.684 |  |  | 2276 | Commercial |  | 20160429UTD_03 | Infrastructure (network-based) | -37.9338 | 145.0375 | 1 | United Energy Distribution | Report | 3153 | 0.038618 | Low voltage AC (<1kV) | Moorabbin Airport | 3189 | Moorabbin | Conductor
A LEI and faults crew attended and completed installation tests that measured 12v between the water pipes and an independent earth. The faults crew proceeded check all service connections and identified a corroded neutral connection at the pole end at pole No. LIS 1309820. The faults crew replaced the junction box and re-terminated the grey twisted overhead service connections. The LEI completed electrical installation tests once the faults crew had completed their work at the pole end that confirmed the fault had been rectified. | 561 POINT NEPEAN ROAD, MCCRAE VIC 3938 | LIS No. 0309820 |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | REC called to advise there is a neutral fault at the property. REC found current going through the earth wire and the customer mentioned to him they were receiving tingles from some appliances and lights have been dimming the past couple of days. The REC was installing a split system air conditioning unit when he received an electric shock as he made simultaneous contact between his hand on the adjacent water pipes and the wet ground. The occupiers had also received slight electric shocks from metallic appliances and the lights have been dimming. REC: Andca Services 915 Point Nepean Road, Rosebud | Aluminium twisted (grey);Connector/termination;Connection box | 0 | 0 | 0 |  |  | Corroded neutral connection in the pole mounted junction box located near Port Phillip Bay. | Minor shock | 42678.4583 |  |  | 2278 | Residential |  | 20160502UTD_01 | Infrastructure (network-based) | -38.3442 | 144.9386 | 1 | United Energy Distribution | Report | 3154 | 0.032748 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the crane truck was removed. | 16 SOMERS AVENUE, MALVERN VIC 3144 | LIS no. 2300888 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | Unknown environment factor |  | Conductor clashing | Unknown work practice factor |  | 1 | At 1113hrs on 13/04/2016, 11kV feeder K 03 circuit breaker reclosed to lockout affecting 841 customers. A scaffold company was dropping scaffolding off at a large unit development that was being constructed and drove off with the boom in the raised position and contacted the LV overhead conductors and communication cable. No injuries or major damage was sustained although the faults crew suspected that a high voltage injection may have occurred after splash marks were identified on the conductors and a LEI was dispatched to investigate. A LEI investigated electrical installations on the circuit for damage to the customers appliances and equipment and no damage was identified. Worksafe investigated the incident and instructed the truck to remain in position as the Inspector took photos and interviewed the driver/operator of the crane truck. Once the investigation was complete, permission was provided for the truck to be removed to enable repairs to be completed. The Worksafe Inspector issued a improvement notice after the driver/operator failed to comply with No Go Zone clearances. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | K 03 | Crane truck drove off with the boom in the raised position and contacted the LV overhead conductors and communication cable. | Loss of supply;No Go Zone (contact) | 13/04/2016 11:13 |  |  | 2280 | Roadway |  | 20160502UTD_03 | Infrastructure (network-based) | -37.85 | 145.0327 | 1 | United Energy Distribution | Report | 2839 | 0.036823 | 11kV AC | Moorabbin Airport | 3144 | Malvern | Vehicle
On arrival the crew isolated supply | 3 WILLIAM STREET, NETHERBY VIC 3418 | 37898 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A customer reported that a tractor towing a prickle chain cultivator had pulled down the power lines at the above location. On arrival the crew found that an unknown tractor had pulled down the service cable supplying 3 William Street Netherby. The impact with the service cable resulted in extensive damage to the Point of Attachment, front veranda and meter box at the above location. The crew isolated supply to the LV service. There was no shock, injury or fire start. | Service conductor | 0 | 0 | 0 |  | NHL016 | Tractor towing a prickle chain cultivator | Loss of supply;Less than $50k damage | 28/04/2016 19:13 |  |  | 2283 | Roadway |  | 20160503PWA_02 | Infrastructure (network-based) | -36.1085 | 141.6521 | 1 | Powercor | Report | 2842 | 0.027135 | Low voltage AC (<1kV) | Horsham Aerodrome | 3418 | Netherby | Vehicle
The attending Powercor Fault Crew replaced the existing Single Phase O/H Service Cable and completed an NST Test which confirmed a Pass result. | 52 CASSIA STREET, RED CLIFFS VIC 3496 | 18154 |  | Precipitation |  | Corrosion |  | Phase to earth | 2 | Mr Brendan Curtin was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | RCT022 | Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded and burnt Twisted O/H Service Neutral Conductor, which had short circuited to the Active Conductor 300mm from the â€œDog Boneâ€ terminating device at the Reticulation Pole. The insulation of the Twisted O/H Service Cable had deteriorated showing signs of cracks in the Conductor insulation. | Minor shock | 42374.5417 |  |  | 2285 | Residential |  | 20160503PWA_04 | Infrastructure (network-based) | -34.3065 | 142.2159 | 1 | Powercor | Report | 2844 | 0.016368 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | OH Cable
On arrival crew made safe and commenced repairs | 45 OLLIERS ROAD, MOUNT ROWAN VIC 3352 | 923271 | Theft | [5 empty] | 2 | Electrix inspector reported earth cable missing from pole. Crew attended and found that the LV earth cable had been removed from the pole 4 Symons S/L. Crew replaced missing cable No shocks, injuries or third party damage. | Earth/earthing | 0 | 0 | 0 |  | BAN009 | Earth cable theft | Less than $50k damage | 29/04/2016 15:06 |  |  | 2293 | Roadway |  | 20160504PWA_02 | Infrastructure (network-based) | -37.5122 | 143.8411 | 1 | Powercor | Report | 2852 | 0.041344 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Other
The Estate Agent was advised to remove the sign but failed to act on United Energy's request and subsequently the For Sale sign was removed by a underground work crew and the estate agent advised. | 8 MINA COURT, CARRUM DOWNS VIC 3201 |  | Working too close to underground cables;Unauthorised access | Unknown environment factor |  | Unknown technical factor | Not followed |  | 2 | 19/04/2016 - No Go Zone enquiry from O'Brien Real Estate seeking permission to install a "For Sale" board up against the substation. 20/04/2016 - Downer advised the Estate Agent that a "For Sale" board cannot be installed in the kiosk substation reserve as unhindered access is required 24/7 with underground cable in the substation reserve. 20/04/2016 - No Go Zone Encroachment Near Miss. The Real Estate Agent has installed a "For Sale" sign in close proximity to "Mina-Scarlett kiosk substation with star pickets driven deep into the ground that narrowly missed live 22kV underground cables. A First Responder was sent to the site and ensured the site is safe and no underground cable have been damaged and no voltages are on the star pickets. 26/04/2016 - The Estate Agent was advised to remove the sign but failed to act on United Energy's request and subsequently the For Sale sign was removed by a underground work crew and the estate agent advised. 27/04/2016 - It was found the For Sale sign had been re-installed. The United Energy Customer Resolutions Team Leader contacted the Estate Agent and advised the sign has to be removed. Estate Agent - Chris Trickey from O'Brien Real Estate Phone - 0451 536 213 | Cable;Pad mounted equipment/kiosk | 0 | 0 | 0 |  |  | The Real Estate Agent has installed a "For Sale" sign in close proximity to "Mina-Scarlett kiosk substation with star pickets driven deep into the ground that narrowly missed live 22kV underground cables. Photo attached. | No Go Zone (no contact) | 27/04/2016 9:00 |  |  | 2300 | Roadway |  | 20160504UTD_07 | Infrastructure (network-based) | -38.0888 | 145.1978 | 1 | United Energy Distribution | Report | 2859 | 0.0073611 | 22kV AC | Moorabbin Airport | 3201 | Carrum Downs | Other
The ZNX crew completed the 10:00AM truck appointment and supply was left on following the completion of installation tests. | 62 GOODWIN STREET, BLACKBURN VIC 3130 |  | Unauthorised work | Unknown environment factor |  | Unknown technical factor | Not followed |  | 2 | 02/05/2016 - 10.00AM Truck appointment to replace FOLCB and to relocate the meter position and install new single phase meter. Test and leave on with CES. A 10:00AM truck appointment was arranged on 02/05/2016 by the REC to enable a single phase XLPE service to be installed to a new FOLCB at the POA and to relocate the meter position after new consumers mains had been installed. REC No. 11237 Brian Cartwright from Cartwright Electrical P/L 0418 513 491 The ZNX meter and servicing crew attended and found the REC had removed the single phase neutral screen service from the POA and left it laying unsafely live on the ground. The crew took photos and notified their supervisor of the infringement. A LEI (B. Neille) was in attendance and signed off Prescribed CES No. 4030 3203 5. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | REC infringement by removing the single phase neutral screen service and leaving it live on the ground. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42405.4167 |  |  | 2304 | Residential |  | 20160506UTD_02 | Infrastructure (network-based) | -37.8169 | 145.1632 | 1 | United Energy Distribution | Report | 2869 | 0.012786 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | Other
A ZNX faults crew attended and isolated supply at "Egan-Nirvana" supply and the rectification work was completed with repairs to the underground cable red phase and neutral conductors. The red phase fuse had operated at "Egan-Nirvana" substation and supply was restored when the rectification work was completed by a ZNX underground crew. | DERRECK AVENUE, BULLEEN VIC 3105 | LIS No. 7069332 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | Unknown environment factor |  | Unknown technical factor | Followed but inappropriate |  | 1 | Underground cable - Caller from Comdain (Simon 0428 970 132) - Derreck Street close to Manningham Road. Underground cable has been nipped / touched by excavator and line not broken. Comdain were completing excavation work for the water authority and contacted a live LV underground cable in the road reserve. The contractor claimed the cable wasn't covered and it was uncertain if DBYD plans had been sourced. No electric shocks or damage to plant was sustained. | Cable | 0 | 0 | 0 |  |  | Excavation work was being completed and Comdain inadvertently contacted a live LV underground cable. | No Go Zone (contact) | 20/04/2016 14:30 |  |  | 2306 | Roadway |  | 20160506UTD_03 | Infrastructure (network-based) | -37.7663 | 145.0907 | 1 | United Energy Distribution | Report | 2871 | 0.0048565 | Low voltage AC (<1kV) | Essendon Airport | 3105 | Bulleen | Dug up
The NICHOLSON THOMPSON Substation was isolated from the set of Live Line Clamps at lis 919785 and the area was made safe. Preforms on pole were replaced. The attending service crew had isolated the supply due suspect HVI, awaiting support from LEI to asses damage. Attending LEI inspected affected properties on Thompson Cres, Nicholson Close, Reynolds Rd and Howell Ct and found evidence of HV injection on Blue Phase only. AMI meters on all these properties were also affected. 34 customers in total isolated. Recomencement planned for following day due to availability of replacement meters, late night (approaching 1:00 am) and availability of resources. A defect notice (NCID) was issued on 10 and 5 Nicholson ST and 141 Thompson Cres. Control Room notified. | 11 NICHOLSON CLOSE, RESEARCH VIC 3095 | 909785 |  |  |  | Corrosion |  | Phase to phase | 1 | IMS 221684. At approximately 14:15 in Nicholson St, Research, an AusNet Services work crew was restoring supply after planned works App# 312839. A Lineworker was fitting a LLC (Live Line Clamp) at NICHOLSON THOMPSON Substation that was a slack span with HV conductor made off on the insulator. The linesman got the LLC from the HV fuse unit to the â€˜Dâ€™ on the conductor when the wrap-on broke causing the HV conductor to drop into the Blue Phase LV, causing ELM33 feeder CB to trip off. It appears that the damage could have been caused by a lightning strike at pole 919785. No injuries were sustained. The work crew were speaking with CEOT (Control Room), as customers were coming out say they have damaged switchboards - HV injection. | Conductor (bare) | 0 | 0 | 0 |  | elm33 | HV conductor fell into LV conductor when a HV wrap-on broke. | HV injection | 29/04/2016 14:15 |  |  | 2313 | Residential |  | 20160509SPN_02 | Infrastructure (network-based) | -37.7045 | 145.1773 | 1 | AusNet Services Distribution | Report | 2883 | 0.018567 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3095 | Research | Conductor
On arrival crew made site safe and commenced repairs to Cable Head | 419 PRINCES HIGHWAY, CORIO VIC 3214 | 50561 |  |  |  | Unknown technical factor |  |  | 1 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a pole fire had occurred, burning was found around the cable head where it had faulted. There was no ground fire. No injury and no third party damage was reported. | Connector/termination | 0 | 0 | 0 |  | FNS022 | Connection failure | Loss of supply | 42465.7583 |  |  | 2320 | Roadway |  | 20160510PWA_01 | Infrastructure (network-based) | -38.0685 | 144.3765 | 1 | Powercor | Report | 2897 | 0.030124 | 22kV AC | Avalon Airport | 3214 | Corio | Connection
The fire had self-extinguished while the crews were in attendance. The crews replaced the EDO fuses only to find the 315kVA transformer was faulted. A replacement transformer was being arranged for replacement. | 48 FRANCIS STREET, PORTLAND VIC 3305 | 907214 |  |  |  | Mechanical breakdown |  |  | 2 | A customer reported a loss of supply after hearing a loud explosion and seeing a â€œfireâ€ at a transformer at the incident location. On arrival the crew found that an EDO fuse had operated on Substation â€œFrancis- Hogan 5â€ and another EDO fuse carrier had â€œhung up â€œ and caught on fire. No ground fire was started. CFA was not called. There were no reported injuries. | EDO fuse | 0 | 0 | 0 |  | PLD004 | EDO operation following transformer failure | Plant/equipment | 42556.3104 | 1 | Negligible: no ground fire | 2322 | Roadway |  | 20160510PWA_03 | Infrastructure (network-based) | -38.3374 | 141.5941 | 1 | Powercor | Report | 2899 | 0.031257 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Fuse
On arrival crew made site safe and commenced repairs | 47 THE AVENUE, OCEAN GROVE VIC 3226 | 7259 | Vehicle | [5 empty] | 2 | Police report that a car has hit a pole at the incident location. On arrival the crew found that a car had hit pole LIS 7259 on the north east corner of The Ave and Field Street north, resulting in pole shaken and two mains low voltage conductors broken and a service on the ground. Load side conductors (de-energised) fell onto the ground. There were no reported injuries. There was no fire. | Conductor (bare);Service conductor | 0 | 0 | 0 |  | DDL011 | Vehicle striking pole | Loss of supply | 42618.4021 |  |  | 2326 | Roadway |  | 20160511PWA_01 | Infrastructure (network-based) | -38.2654 | 144.5197 | 1 | Powercor | Report | 2903 | 0.024944 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Vehicle
On arrived site made safe supply to the effected meter panel isolated by LEI Meters and board removed and quarantined | 380 TOORAK ROAD, SOUTH YARRA VIC 3141 | 42935 |  |  |  | Overheated connection |  |  | 2 | Vicfire reported a fire at the property indicated below. On arrival the crew found a burnt meter panel, as well as a meter & fuse holder. The fire was extinguished by the buildingâ€™s sprinkler system, which subsequently caused water damage to the meter panel & a number of meters not affected by the fire. The fire appeared to emanate from a fuse holder and is under further investigation by Mark Pilkington. | Meter board (including fuses) | 0 | 0 | 0 |  | TK009 | Overheated connection | Property | 42526.0931 | 1 | Negligible: no ground fire | 2331 | Commercial |  | 20160511PWA_03 | Infrastructure (network-based) | -37.8405 | 145.0027 | 1 | CitiPower | Report | 7991 | 0.023425 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Fuse
The attending AusNet Services' fault crew located the badly corroded neutral connection at the sub-pole #5215356. As the installation was unoccupied, supply was isolated at the sub for replacement of the faulty neutral screened service the following day. The Installation was left OFF supply. Two spans of neutral screen service cable was replaced the next day. NST test completed by crew and installation re-energised by inspector on 13th April. | 277 WATERS LANE, COLAC COLAC VIC 3707 | 5215356 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 221458. REC 4185 reported an electric shock from tap at water pump. REC believes may be a neutral fault. Doug 0427 761529. An unknown worker received an electric shock while he was installing a new water pump when he made simultaneous contact between the external taps and the ground below the rear deck. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 48 Volts on the water piping system. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a defective (broken) service neutral conductor termination at the distribution pole which was identified as the cause of the high impedance within the neutral service conductor. | Service conductor;Neutral screen;Pole mounted | 0 | 0 | 0 |  | wots24 | Broken service neutral at substation pole #5215356. | Minor shock | 42708.641 |  |  | 2337 |  |  | 20160512SPN_04 | Infrastructure (network-based) | -36.233 | 147.8529 | 1 | AusNet Services Distribution | Report | 3000 | 0.012789 | Low voltage AC (<1kV) | Wangaratta Aero | 3707 | Colac Colac | Connection
A faults crew attended and replaced the HV blue phase 10amp EDO fuse and tube at "Kennedy-Aireys" substation and supply was restored to customers in the area. In addition, the faults crew identified the LV white phase fused isolator was damaged and replaced it whilst they were on site with equipment set up. | KENNEDY ROAD, SOMERS VIC 3927 | LIS No. 1107914 | Unknown external/community factor | Precipitation |  | Age;Electrical breakdown | Unknown work practice factor |  | 2 | Customers supplied from "Kennedy-Aireys" substation advised of dim lights and they appear to be cutting in and out. A HV fuse candled at "Kennedy-Aireys" substation that caused the dimming of lights to customers in the area. Pole No. LIS 1107914. | EDO fuse | 0 | 0 | 0 |  | HGS 23 | Corroded EDO fuse and tube. | Pole-top fire | 42679.1181 | 1 | Negligible: no ground fire | 2339 | Roadway |  | 20160512UTD_01 | Infrastructure (network-based) | -38.388 | 145.1732 | 1 | United Energy Distribution | Report | 2925 | 0.020714 | 12.7kV AC (SWER) | Moorabbin Airport | 3927 | Somers | Fuse
On arrival crew made site safe | 66 LOYOLA ROAD, WERRIBEE VIC 3030 | 214109 | Working too close to underground cables | [5 empty] | 2 | A customer reported power outage at their premises at the incident location. On arrival the crew suspected the UG service has been damage so The damage was done by the fencing contractor, while they were installing the fence a year ago. Since then the cable deteriorated. The property owner was contacted but he has no details of the contractor. There was no reported injuries or fire. | Services cable | 0 | 0 | 0 |  | WBE024 | Unknown fencing contractor damaged cable | Loss of supply | 42679.591 |  |  | 2341 | Residential |  | 20160513PWA_02 | Infrastructure (network-based) | -37.9115 | 144.6742 | 1 | Powercor | Report | 2927 | 0.011498 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
Initial Report: CEOT dispatched fault crew to make safe, investigate and repair. Final Report: CEOT dispatched a fault crew to make safe and investigate. The crew attended site and proceeded to cut away HV droppers from the damaged transformer as this was direct connected and not fused. No evidence of a fire at ground level. Suspected lightning strike as the cause of transformer failure. Due to volume of faults, the transformer is still on the pole, waiting for a Work Order to be raised for its replacement. | 1510 NAR NAR GOON-LONGWARRY ROAD, BUNYIP VIC 3815 | 2712820 |  | Lightning |  |  |  |  | 2 | IMS 221864. Initial Report: Control TX to HV Bushing Cap has evidence of fire/burn marks. CEOT didn't enter this incident into IMS until 12 May. Final Report: Etel single phase 16kVA control transformer to HV bushing cap has evidence of fire/burn marks. No signs of fire at ground level but some scorching of the pole was apparent. No physical damage occurred. | Transformer | 0 | 0 | 0 |  | wgl12 | Lightning caused transformer failure. | Other electricity related | 42495.5757 | 1 | Negligible: no ground fire | 2342 | Agricultural |  | 20160513SPN_01 | Infrastructure (network-based) | -38.1005 | 145.7334 | 1 | AusNet Services Distribution | Report | 2930 | 0.0065116 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3815 | Bunyip | Lightning
On arrival crew made site safe and carried out repairs | 232 CIVIC PARADE, ALTONA VIC 3018 | 1580 | Vehicle | [5 empty] | 2 | A customer reported that a truck has struck a cable at the incident location, dislodging from hook and hanging low over roadway. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  | AL006 | High load | Damage to network assets | 42648.3521 |  |  | 2350 | Roadway |  | 20160518PWA_03 | Infrastructure (network-based) | -37.8632 | 144.8171 | 1 | Powercor | Report | 8058 | 0.027068 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Vehicle
Crew isolated supply and undertook repairs | 194 GOLF LINKS ROAD, MAIDEN GULLY VIC 3551 | 40726 |  |  |  | Electrical breakdown;Candled fuse |  |  | 2 | A passer by reported sparking from distribution transformer at the incident location. On arrival the crew found that a HV fuse had candled and another had hung up. There were no reported injuries, no ground fire, or third party damages. | Powder filled;Transformer | 0 | 0 | 0 |  | BET001 | Fuses failed to operate correctly. The transformer had failed internally, cause unknown | Loss of supply;Other electricity related | 14/05/2016 18:18 |  |  | 2353 | Roadway |  | 20160518PWA_05 | Infrastructure (network-based) | -36.7249 | 144.2162 | 1 | Powercor | Report | 3193 | 0.0017917 | 22kV AC | Bendigo Airport | 3551 | Maiden Gully | Fuse
CEOT dispatched a fault crew and the DAO to make safe and investigate. Fuse Savers operated and the incident is being investigated by the DAO / local Electricity Network Representative. A work crew attended and carried out all necessary repairs to the HV line. | 173 MITCHELLS ROAD, NEWMERELLA VIC 3886 | 1906459 | Working too close to overhead lines;Unauthorised work |  |  |  |  | Phase to earth | 1 | IMS 221990. An unknown person operating an excavator whilst building a dam wall caused the excavator to make contact with the overhead Lavell Spur Corringle 22 kV conductor. Results of investigation into conductor damage on Lavell Spur Corringle are as follows: â€¢ Damage â€“ bent hardware and broken tie on pole 1906459. Broken 3/12 steel conductor between poles 1906459 & 1906487. Bent hardware, 2 broken ties and 9 shed insulator on pole 1906487 as well as second conductor dislodged off pole. Bent hardware on pole 1906458. â€¢ Dam being constructed / enlarged between poles 1906459 & 1906487 with dam walls raised considerably. â€¢ Possible machine contacted conductor in this area while operating on dam extensions? â€¢ Bulldozer and Excavator found hidden up bush track with track marks on road leading from dam site. â€¢ No identification found on machines as to ownership. â€¢ Property owner (Theo Mekken) was non-committal with any information in regard to machine operators / owner. Said he was out all day and knew nothing. â€¢ Damage repaired with conductor height of 7.1m above raised dam walls on completion. â€¢ Original conductor height unknown. | Conductor (bare) | 0 | 0 | 0 |  | nla31 | Excavator contact with overhead HV conductor. No Go Zone Rules breach. The work involved would have been in beach of Electricity Safety (Installations) Regulations 2009, regulation 312 Altering Levels and regulation 315 Minimum distances between parts of vehicles, vessels, plant, machinery and aerial lines. | No Go Zone (contact) | 18/05/2016 13:10 |  |  | 2360 | Agricultural |  | 20160519SPN_01 | Infrastructure (network-based) | -37.747 | 148.462 | 1 | AusNet Services Distribution | Report | 3204 | 0.036128 | 22kV AC | Bairnsdale Airport | 3886 | Newmerella | Vehicle
A faults crew attended and disconnected supply to the lantern and replaced the defective 150w HPS lantern. The street light fire was out on arrival. | KEVLAR CLOSE, BRAESIDE VIC 3195 |  |  |  |  | Defective component;Fault on customer installation |  |  | 2 | Pole fire per CFA outside No. 90 Mills Road, Braeside. A 150w HPS lantern located on the first pole into Kevlar Close near 90 Mills Road, Braeside caught fire and required attendance by the CFA. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown. | Melting or smoking only | 24/06/2016 5:05 |  |  | 2355 | Roadway |  | 20160519UTD_01 | Infrastructure (network-based) | -37.9947 | 145.1174 | 1 | United Energy Distribution | Report | 3656 | 0.018449 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Braeside | AF Other
Cable repaired | 437 ST KILDA ROAD, MELBOURNE VIC 3004 | 81543 | Working too close to underground cables | [5 empty] | 1 | CitiPower U/G crew attending an outage found that an 11kV U/G cable damaged by a contractor while they were excavating foot path at the incident location. Protection operated. There were no reported injuries or fire | Cable | 0 | 0 | 0 |  | FR031 | 3rd party works | Loss of supply | 18/05/2016 9:10 |  |  | 2365 | Public space |  | 20160520PWA_02 | Infrastructure (network-based) | -37.8391 | 144.9769 | 1 | CitiPower | Report | 2971 | 0.016668 | 11kV AC | Essendon Airport | 3004 | Melbourne | Dug up
The construction site supervisor was instructed to cease all works at the frontage of the property and the area was taped off. A ZNX crew attended and placed "Capital-Highbury" pole type substation under LV parallel and the HV Live Line clamps were lifted on the tee off pole. Visual aids were attached on the LV ABC along with 'clip on' warning flags on the isolated bay of HV overhead conductors. 20 May - ESV and United Energy representatives attended the site and spoke to the company involved after the company continued with construction work. | 746 HIGHBURY ROAD, GLEN WAVERLEY VIC 3150 |  | Building too close or within the No Go Zone | Unknown environment factor |  | Unknown technical factor | Ineffective planning/procedures/processes |  | 2 | A ZNX No Go Zone Coordinator passed this worksite and found that construction work had been carried out prior to the No Go Zone group's attendance. 16 May - It was identified the building under construction is within 2 metres of the 22kV HV overhead conductors and a ZNX No Go Zone Coordinator took photo's and notified Worksafe of the breach. | Conductor (bare) | 0 | 0 | 0 |  |  | No Go Zone breach. | No Go Zone (no contact) | 16/05/2016 9:30 |  |  | 2367 | Roadway |  | 20160523UTD_01 | Infrastructure (network-based) | -37.8632 | 145.1777 | 1 | United Energy Distribution | Report | 2973 | 0.035642 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Other
The faults crew checked for stray voltages at the pole and less than 3v was measured between the pole and a independent earth. | 25 HYGEIA STREET, RYE VIC 3941 | LIS No. 1300972 | Vandalism | [5 empty] | 2 | Pole fire per CFA. The CFA were leaving the site following an arson attempt at pole No. LIS 1300972 located outside 25 Hygeia Street, Rye. Unknown persons attempted to light a fire at the base of the HV/LV intermediate pole that resulted in superficial damage to the timber pole. The CFA and Police were in attendance. | Pole (wood);No failed asset | 0 | 0 | 0 |  | STO 123 | Unknown persons attempted to light a fire at the base of the HV/LV intermediate pole. | Singeing or local charring/blackening only | 23/05/2016 11:21 |  |  | 2370 | Roadway |  | 20160523UTD_02 | Infrastructure (network-based) | -38.3738 | 144.8305 | 1 | United Energy Distribution | Report | 3239 | 0.027788 | 22kV AC | Moorabbin Airport | 3941 | Rye | Other
Faulted area isolated and earthed to conduct repairs on damaged HV o/head conductor. | 30 SPRINGBANK STREET, TULLAMARINE VIC 3043 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | HV conductor found on ground caused by truck mounted scissor lift making contact with HV Overhead. | Conductor (bare) | 0 | 0 | 0 |  | AW14 | Truck mounted scissor lift came into contact with HV overhead conductor. | No Go Zone (contact) | 25/05/2016 15:18 |  |  | 2383 | Commercial |  | 20160525JEM_01 | Infrastructure (network-based) | -37.6856 | 144.8712 | 1 | Jemena | Report | 3043 | 0.041005 | 22kV AC | Melbourne Airport | 3043 | Tullamarine | Vehicle
Initial Report: CEOT dispatched a fault crew to make safe and investigate. Crew made site safe. No reports of fire. Replaced TX. Final report: Made site safe. No reports of a fire. Replaced single phase 25 kVA transformer, EDO fuse tube and fuse link. | 32 YANNATHAN ROAD, NYORA VIC 3987 | 2025855 |  | Lightning |  |  |  |  | 2 | Initial Report: IMS 222045. @ LIS #2025855 fault crew report 1x 5a EDO fuse hanging down but burnt out. INCD-103714-r. CEOT entered incident in IMS on 20 May but it was not work flowed until 24 May. Schedule 1 Report was sent to ESV by CEOT via a WORD document on 20 May. Final report: At pole LIS #2025855 the fault crew reported 1 x 5 Amp EDO fuse hanging down with a burnt out fuse tube. The substation transformer was possibly weakened / damaged during last weeks storms. | EDO fuse | 0 | 0 | 0 |  | llg12 | Possibly caused by lightning during recent storms. | Other electricity related | 20/05/2016 6:04 | 1 | Negligible: no ground fire | 2379 | Agricultural |  | 20160525SPN_02 | Infrastructure (network-based) | -38.329 | 145.6706 | 1 | AusNet Services Distribution | Report | 2990 | 0.02188 | 22kV AC | Moorabbin Airport | 3987 | Nyora | Lightning
Made safe - Cable repaired and supply restored. | 4 HOLTON COURT, HILLSIDE VIC 3037 | 10420753 |  |  |  | Electrical overload |  |  | 2 | Low voltage underground cable melted in the pit. | Cable | 0 | 0 | 0 |  | LV / Feeder number N/A | Low voltage underground cables melting as a result from high electrical load. | Melting or smoking only | 22/05/2016 16:25 |  |  | 2385 | Residential |  | 20160526JEM_01 | Infrastructure (network-based) | -37.6877 | 144.7515 | 1 | Jemena | Report | 2996 | 0.039363 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Hillside | UG Cable
On arrival crew made site safe and commenced repairs | SETTLEMENT ROAD, ROCHESTER VIC 3561 | 22808 |  |  |  | Leakage |  |  | 2 | A customer reported a pole fire at incident location. There was no ground fire. There was no reported injuries or third party property damage | Pole (wood) | 0 | 0 | 0 |  | SHP012 | Pole top fire | Pole-top fire | 42525.6285 | 1 | Negligible: no ground fire | 2384 | Roadway |  | 20160526PWA_01 | Infrastructure (network-based) | -36.4066 | 144.6516 | 1 | Powercor | Report | 2995 | 0.0020729 | 22kV AC | Bendigo Airport | 3561 | Rochester | Pole
On arrival crew made site safe and commenced repairs | 80 BAYUNGA ROAD, TATURA VIC 3616 | 11996 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A tractor had contacted a guy wire. At the time of contact Peter was doing tillage work at the incident location. The machinery being towed behind the tractor had contacted the guy wire. On arrival the crew found that the pole had snapped in two and the transformer was laying on the ground. The tractor and machinery was not present when the linesmen arrived. There was no ground fire, injuries or third party damages | Pole (wood) | 0 | 0 | 0 |  | MNA014 | farm equipment contacting stay wire | Loss of supply | 19/05/2016 13:49 |  |  | 2388 | Agricultural |  | 20160527PWA_01 | Infrastructure (network-based) | -36.4161 | 145.2592 | 1 | Powercor | Report | 3004 | 0.01888 | 22kV AC | Shepparton Airport | 3616 | Tatura | Vehicle
On arrival crew made site safe and commenced repairs | 9 CHESTERFIELD DRIVE, WYNDHAM VALE VIC 3024 | 790789 | Vehicle | [5 empty] | 2 | A customer reported a smoking LV pillar at the incident location. On arrival crew found that the pillar (N.O.) had been damaged and it had been hit by an unknown vehicle. | LV Pillar | 0 | 0 | 0 |  | WBE023 | Unknown vehicle struck pillar | Melting or smoking only | 26/05/2016 11:56 |  |  | 2389 | Roadway |  | 20160527PWA_02 | Infrastructure (network-based) | -37.8853 | 144.6226 | 1 | Powercor | Report | 3005 | 0.040154 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
CEOT dispatched to the incident an AusNet Services' fault crew to make safe, investigate and repair. A fire in the pole junction box, LIS : 2811961 was observed. The fault crew replaced the 3 phase J-Box on LIS 2811961. No fire damage to the pole. A small bird's nest was observed in the J-box. | 1305 INVERLOCH-KONGWAK ROAD, INVERLOCH VIC 3996 | 2811961 |  | Bird |  |  |  | Phase to phase | 2 | IMS 222141. A customer reported to AusNet Services of a pole fire/junction box fire. The damage was limited to the 3 phase junction box on the pole, no damage to the pole, no confirmation of a ground fire. There was a small bird's nest in J-box. | Connection box | 0 | 0 | 0 |  | wgi14 | Bird Incident | Other electricity related | 26/05/2016 14:38 | 1 | Negligible: no ground fire | 2390 | Agricultural |  | 20160527SPN_01 | Infrastructure (network-based) | -38.6224 | 145.7227 | 1 | AusNet Services Distribution | Report | 3007 | 0.028014 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Animal
Made safe and repairs made and restored once Inspector had completed works. Subsequent field audits found splash marks on a section of OH conductor on ST 23, 300m North of the intersection of Oherns Rd and Hume Hwy between poles A075612 and A075611. Splash mark were also spotted on the section of 66kV span directly above the 22kV span where clashing had occurred confirming the possibility of a 66/22 kV injection between SMTS-ST and ST 23 feeders. Although rare, it is not an uncommon for the rising ionised air from a clashing 22kV feeder below to travel into the 66kV above and set up a conductive path which results in injection. Damage from the HV injection was limited to two sets of surge diverters, three switches and a set of bridges on feeder ST 23 on the Jemena Electricity Network. No other damage has been found. Spreaders have been installed on the span where clashing occurred to prevent a reoccurrence. | 1825 HUME HIGHWAY, SOMERTON VIC 3062 | 10183371 |  | Bird |  | HV injection |  | Three phase | 1 | A bird made contact with fuse units at substation Hume 1825-Somerton #2 supplied off 22kV feeder ST 23, located 300m North West of the intersection of Truck City Drive and Hume Hwy in Campbellfield. At the same time 66kV feeder SMTS-ST successfully reclosed indicating the possibility of a 66/22KV injection. Patrols along the backbone of feeder ST 23 found several failed HV switches and surge diverters upstream of the fault location. | Conductor (bare);Boric acid | 0 | 0 | 0 |  | ST23 | Bird Incident | HV injection | 28/05/2016 13:09 |  |  | 2396 | Industrial |  | 20160530JEM_01 | Infrastructure (network-based) | -37.6425 | 144.9508 | 1 | Jemena | Report | 3321 | 0.020222 | 22kV AC;66kV AC | Essendon Airport | 3062 | Somerton | Animal
On arrival crew isolated supply and commenced repairs | 10 GLOAMING RIDE, KURUNJANG VIC 3337 | 110634 |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire on a pole at the incident location. On arrival the crew found that a LV fuse box had melted. Fallen material burnt a small area of grass at the base of the pole. The ground fire self extinguished. There were no reported injuries, no third party property damage. | Connection box | 0 | 0 | 0 |  | MLN014 | Connection failure | Grassfire | 30/05/2016 19:17 | 1 | Localised: less than 10 sq.m | 2408 | Roadway |  | 20160531PWA_03 | Infrastructure (network-based) | -37.6663 | 144.5739 | 1 | Powercor | Report | 3103 | 0.020867 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Connection
The fault crew arrived and isolated supply. An initial NST test failed. Service neutrals and LV conductor neutral connection were checked and the fault was found to be in the service neutral connection and possible conductor bridge (temporary bridged out). All neutral connections re-made and final NST tests passed. The installation was tested and passed. Voltage to independent earth on 20 Amp customer load was 2V. No leakage to earth was found. | 43 NAPIER STREET, PORT ALBERT VIC 3971 | 2624454 |  |  |  | Corrosion |  |  | 2 | IMS 221811. Mrs Stacy was showering when she received a tingle off the shower tap. The cause was found to be a faulty/broken neutral crimp joint in service line at the POA. | Service conductor;Aluminium twisted (XLPE);Connector/termination | 0 | 0 | 0 |  | ftr23 | A faulty/broken neutral crimp joint in the service line at the POA. | Minor shock | 42618.4028 |  |  | 2407 | Residential |  | 20160531SPN_02 | Infrastructure (customer connection) | -38.6703 | 146.694 | 1 | AusNet Services Distribution | Report | 3027 | 0.03908 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3971 | Port Albert | Connection
The attending Powercor Fault Crew replaced the existing Two Wire O/H Service Cable and completed an NST Test, which confirmed a Pass result. Additional Load Testing at the Sub-station confirmed a load imbalance resulting in a voltage rise on the Reticulation Neutral Conductor and between the points of contact. | 12 KALIMNA COURT, CLIFTON SPRINGS VIC 3222 |  |  |  |  | Out of balance load |  | Phase to earth | 2 | Ms Kay McAuliffe was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Additional Load Testing at the Sub-station confirmed a load imbalance resulting in a voltage rise on the Reticulation Neutral Conductor and between the points of contact. | Minor shock | 19/05/2016 22:00 |  |  | 2412 | Residential |  | 20160601PWA_02 | Infrastructure (network-based) | -38.158 | 144.5522 | 1 | Powercor | Report | 3032 | 0.022176 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | OH Cable
A Registered Electrical Contractor attended site and remounted the FOLCB and re-terminated the Consumers Mains. The Powercor Fault Crew reterminated the existing O/H Service Cable at the FOLCB | 13 CUTHBERTS ROAD, ALFREDTON VIC 3350 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Mr Andrew Fleming was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | The Consumers Mains Neutral Conductor was broken at the FOLCB when the O/H Service Cable dislodged from the Service Hook during a storm. | Minor shock | 42648.2917 |  |  | 2416 |  |  | 20160601PWA_05 | Infrastructure (network-based) | -37.5552 | 143.8109 | 1 | Powercor | Report | 3036 | 0.0092292 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Alfredton | OH Cable
On arrival crew isolated supply and commenced repairs | 12 NORTHUMBERLAND ROAD, SUNSHINE NORTH VIC 3020 | 17304 |  |  |  | Overheated connection |  |  | 2 | MFB reported a fire on a pole at the incident location. On arrival the crew found that a connection had overheated on a LV isolator causing to catch fire (only the red phase LV isolator). There was no ground fire. There were no reported injuries or third party property damages. | Disconnector/isolator | 0 | 0 | 0 |  | SSE032 | Overheated connection | Pole-top fire;Loss of supply | 42375.8542 | 0 | Negligible: no ground fire | 2428 | Residential |  | 20160602PWA_04 | Infrastructure (network-based) | -37.7771 | 144.8409 | 1 | Powercor | Report | 3056 | 0.0040289 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Connection
Substation was isolated and repairs were made. All surge diverters and HV droppers were replaced and substation cleaned and put back in service. | 3 JOYNT STREET, MACLEOD VIC 3085 |  |  |  |  | Age;Not built/maintained to design |  | Phase to phase | 1 | The Blue phase High Voltage dropper on substation Joynt-Grieve has flashed over to the white phase connection the surge diverter and started a small fire. Refer to the attached photo for a better explanation. | Pole mounted | 0 | 0 | 0 |  | NH03 | The blue phase HV dropper flashed over to the top of the white phase surge diverter due to old construction and age. Initially it was thought the incident had occurred due to the failure of the white phase surge diverter but analysis of the affected surge diverter revealed it to be OK. Refer to photo. Old design not to current standard. | Other electricity related | 42527.384 | 1 | Negligible: no ground fire | 2432 | Public space |  | 20160604JEM_01 | Infrastructure (network-based) | -37.7259 | 145.0621 | 1 | Jemena | Report | 3460 | 0.020828 | 22kV AC | Essendon Airport | 3085 | Macleod | AF Other
The fault crew found that a HV fuse failed to operate and had candled. No burn marks at the base of the pole. Switch to be inspected and the line patrolled. The fault crew replaced the Boric Acid fuse. | 112 DALTON STREET, ELTHAM VIC 3095 | 927193 |  |  |  | Electrical breakdown |  |  | 2 | IMS 222284. CEOT dispatched a fault truck to attend to a report of no power and fire at this address. Crew to make safe and investigate. The fault crew found that a HV fuse failed to operate and had candled. No burn marks at the base of the pole. Switch to be inspected and the line patrolled. A HV Boric Acid fuse operated but candled. | Boric acid | 0 | 0 | 0 |  | elm34 | BA fuse candled. | Plant/equipment | 42527.3542 | 1 | Negligible: no ground fire | 2437 | Residential |  | 20160606SPN_01 | Infrastructure (network-based) | -37.7253 | 145.1505 | 1 | AusNet Services Distribution | Report | 3084 | 0.031716 | 22kV AC | Essendon Airport | 3095 | Eltham | Fuse
Initial Report: CEOT Controller waited 15min. Contacted Seymour police who had no calls relating to faults in area. Closed SMR5 CB at 10:59. Craig Velt knew of excavators in area so attended site. Found Excavator operators who admitted contacting HV with boom between LIS 4718204 & LIS 4704309. No PTW on issue. Craig reported that same project had dug up a Telstra cable yesterday. Final Report: The work crew was given contact information for site assessment from Extec (on behalf of AusNet Services) and instructed to make contact to arrange a site inspection for all areas where powerlines are in the vicinity of works. The crew undertook to complete this requirement prior to commencing work near powerlines again. During the discussions the site crew was fully cooperative and appeared to understand the seriousness of the events. Details of Spiecapag Lucas employees: Excavator Operator - Noel Mahon, 0437 829 777 - noelmahon22@yahoo.com. Spotter - Paul Frank. Supervisor - Kieran Mullane - 0447 247 410. APA (Gas pipline owner rep) Senior HSE Specialist- Andrew Cook 0413 271 290, email andrew.cook@apa.com.au. Plant 30T Excavator Rego I8544C - QLD plates. | 400 TELEGRAPH ROAD, SEYMOUR VIC 3660 | 4718204 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 222314. Initial report: SMR5 CB tripped with Live Line Sequence enabled (One shot to lockout). Craig Velt, Adam Hinss and Dean Adams attended site and discussed incident with Spiecapag Lucas staff and supervisor as well as APA (Gas Pipeline owner) HSE Rep. The staff on site advised that a 30T excavator had contacted the line after they had completed laying a new HP gas pipe in the trench directly below the line. No injuries were sustained to personnel and there was no damage to conductor or machinery. Final Report: Controller waited 15min. Contacted Seymour police who had no calls relating to faults in area. Closed SMR5 CB at 10:59. Craig Velt knew of excavators in area so attended site. Found Excavator operators who admitted contacting HV with boom between LIS 4718204 & LIS 4704309. No Permit to Work (PTW) on issue. Craig Velt, Adam Hinss and Dean Adams of AusNet Services, attended site and discussed incident with Spiecapag Lucas staff and supervisor as well as APA (Gas Pipeline owner) HSE Rep. The staff on site advised that a 30T excavator had contacted the line after they had completed laying a new HP gas pipe in the trench directly below the line. The event happened as the machine was exiting the area where the operator lifted and slewed the machine during the exit phase from the work area. At the time the excavator operator had ceased to maintain eye contact with the spotter. No injuries were sustained to personnel and there was no damage to conductor or machinery. Fault current at ZSS was 300A blue phase to ground. When questioned about whether the excavator driver had had a medical check the supervisor advised that the local medical officer (suspect first aider) had discussed the welfare of the operator and sent him home prior to site attendance by AusNet Services' staff. It was strongly recommended that a doctors should be consulted to assess the person. The crew on site were asked about their understanding of the NGZ rule and requirements for PTW from AusNet Services. The crew believed that they had things covered through the use of an industry trained spotter as well as the presence of warning flags in the vicinity of the line. Adam explained the need for PTW due to the machine being large enough to encroach safe approach distances and that extra precautions could have been utilised had a proper process been followed. It was fortunate that AusNet Services had live line sequence enabled on the protection for unrelated works on the same feeder when the event occurred. Therefore the protection operated very quickly and no reclose occurred. The crew were made aware of how fortunate they were that the protection was set this way and this was due to lucky timing rather than good management. Information about project: The joint venture between AJ Lucas and Spiecapag Australia, Spiecapag Lucas, has been awarded the construction contract for loopings 6â€“9 on APA Groupâ€™s Victorian Northern Interconnect Expansion (VNIE) Project. The project, which is part of APA Group's planned upgrade and expansion of its east coast gas grid in response to the transitioning gas market in eastern Australia, will increase the flow of gas from Victoria and New South Wales. Client: APA is Australiaâ€™s largest natural gas infrastructure business, owning and/or operating $12 billion of energy assets. Its gas transmission pipelines span every state and territory on mainland Australia, delivering approximately half of the nationâ€™s gas usage. APA has direct management and operational control over its assets and the majority of its investments. APA also holds minority interests in energy infrastructure enterprises including Envestra, SEA Gas Pipeline, Energy Infrastructure Investments and GDI. | Conductor (bare) | 0 | 0 | 0 |  | smr5 | Excavator with boom contacted overhead HV conductors between LIS 4718204 & LIS 4704309. No Permit to Work (PTW) on issue. | No Go Zone (contact) | 42557.4417 |  |  | 2443 | Construction |  | 20160608SPN_01 | Infrastructure (network-based) | -37.0498 | 145.182 | 1 | AusNet Services Distribution | Report | 3121 | 0.039722 | 22kV AC | Mangalore Airport | 3660 | Seymour | Vehicle
On arrival crew isolated supply and carried out repairs | 41 GORDON STREET, NEWPORT VIC 3015 | 8310 | Vandalism | [5 empty] | 1 | Mr Bardhul Beluli reported a steel bar on LV conductors at the incident location. He stated that someone has thrown it but the personâ€™s identity is not known. On arrival the Powercor crew found the steel bar was bonded to LV phases and resting on the conductors. | Conductor (bare) | 0 | 0 | 0 |  | BLT022 | steel bar across LV | Loss of supply | 42557.4611 |  |  | 2448 | Roadway |  | 20160609PWA_01 | Infrastructure (network-based) | -37.8371 | 144.8669 | 1 | Powercor | Report | 3126 | 0.01234 | Low voltage AC (<1kV) | Laverton Raaf | 3015 | Newport | Other
CEOT dispatched a fault crew to make safe, investigate and repair. Crew replaced the EDO fuse tube and restored supply. | 75 MILLS ROAD, COALVILLE VIC 3825 | 2208109 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 222390. AusNet Services fault crew called to an All Supply Failure to find an EDO fuse tube broken in half due to candling. | EDO fuse | 0 | 0 | 0 |  | moe31 | EDO fuse candled. | Other electricity related | 42649.2868 | 1 | Negligible: no ground fire | 2455 | Agricultural |  | 20160610SPN_01 | Infrastructure (network-based) | -38.2371 | 146.2709 | 1 | AusNet Services Distribution | Report | 3145 | 0.030583 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Coalville | Fuse
On arrival crew isolated supply and carried out repairs | 439 GLENELG HIGHWAY, SMYTHES CREEK VIC 3351 | 15940 |  |  |  | Corrosion |  |  | 2 | Vic Fire reported a power pole on fire. On arrival the crew found that the LV Junction Box connected to a LV Underground cable supplied from the pole had overheated, causing a fire to start at that position on the pole. There was no ground fire, injuries or third party property damage. | Pole mounted;Connection box | 0 | 0 | 0 |  | BAS021 | Overheated connection | Pole-top fire | 42680.7208 | 1 | Negligible: no ground fire | 2472 | Roadway |  | 20160615PWA_01 | Infrastructure (network-based) | -37.5894 | 143.7919 | 1 | Powercor | Report | 3187 | 0.041012 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Smythes Creek | Connection
Crew removed all LV assets and removed HV fuses | 900 RESERVOIR ROAD, SUNBURY VIC 3429 | 11097081 | Copper theft |  | Unlikely |  |  |  | 2 | Member of public called Jemena customer relations team to raise the issue of vandalism. The responding field crew reported that the service cable (copper cables) running from the Krone switch to the underground pit (Calder Fwy-P112) substation had been pulled out and stolen. | Cable;Earth/earthing | 0 | 0 | 0 |  | SBY32 | The cause was vandalism and theft of copper running from the pole mounted substation down to the underground cable pit nearby. Copper cable was stolen. | Damage to network assets | 16/06/2016 15:13 |  |  | 2479 | Public space |  | 20160616JEM_02 | Infrastructure (network-based) | -37.5542 | 144.6591 | 1 | Jemena | Report | 3492 | 0.019359 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
The electrical inspector attended the site, tested and identified severely corroded neutral at the pole mounted connection box. Fault crew attended and repaired corroded neutral. | 105 TYLER STREET, PRESTON VIC 3072 | A031440 |  |  | Likely | Corrosion;Neutral fault |  |  | 2 | The customer received an electric shock while she was washing dishes in the kitchen sink when she made simultaneous contact between the kitchen taps and the kitchen sink. Voltage tests between an independent earth and the water pipe system identified a severely corroded neutral at the pole mounted connection box. Jemena service crews re terminated the neutral conductor at the service pole. | Connection box | 0 | 0 | 0 |  | NH-016 | Severely corroded service neutral at the pole mounted connection box. | Minor shock | 20/06/2016 11:19 |  |  | 2486 |  |  | 20160620JEM_01 | Infrastructure (network-based) | -37.7326 | 145.0272 | 1 | Jemena | Report | 3449 | 0.023516 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Connection
Fault crew isolated the low voltage underground cable pending repairs by daytime underground faults crew. | 301 HAMPSHIRE ROAD, SUNSHINE VIC 3020 | 932619 | Working too close to underground cables | [5 empty] | 2 | Contractor Kane Constructions reported that cables have been dug up at the incident location. On arrival the fault crew found that a four core 16mm2 low voltage underground service supplying some public lights had been damaged, resulting in lights lost supply. Plans on site, no sequence number obtained There was no fire, no reported injuries or third party property damage. | Cable | 0 | 0 | 0 |  | SSE013 | Contractor failing to correctly identify location of cable. | Loss of supply;No Go Zone (contact) | 16/06/2016 20:51 |  |  | 2491 | Roadway |  | 20160621PWA_02 | Infrastructure (network-based) | -37.7833 | 144.8321 | 1 | Powercor | Report | 3226 | 0.029162 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Dug up
On arrival crew carried out repairs | 20-22 QUEENS ROAD, MELBOURNE VIC 3000 | 37265 |  |  |  | Overheated connection |  |  | 2 | A customer reported a fire on a pole (LIS #37265) at the incident location. Upon arrival, the CP crew found that the IPC had melted due to the heat. There were no reported injuries or other third party property damage. | Connector/termination | 0 | 0 | 0 |  | SK004 | connection corrosion | Melting or smoking only | 25/06/2016 0:32 |  |  | 2515 | Roadway |  | 20160628PWA_01 | Infrastructure (network-based) | -37.8407 | 144.975 | 1 | CitiPower | Report | 3408 | 0.0093981 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Connection
On arrival crew commenced repairs | 44 BURNSIDE ROAD, BANNOCKBURN VIC 3331 | 58880 |  |  |  | Overheated connection |  |  | 2 | A nearby Customer reported a pole fire at the incident location. On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. There was no ground fire. There were no reported injuries or third party property damage. | Connection box | 0 | 0 | 0 |  | GL012 | corrossion | Pole-top fire | 25/06/2016 23:39 | 1 | Negligible: no ground fire | 2519 | Public space |  | 20160628PWA_05 | Infrastructure (network-based) | -38.0519 | 144.1717 | 1 | Powercor | Report | 3269 | 0.02301 | Low voltage AC (<1kV) | Avalon Airport | 3331 | Bannockburn | Connection
on arrival crew isolated supply and carried out repairs | 509 BURKE ROAD, CAMBERWELL VIC 3124 | 5384 |  |  |  | Overheated connection |  |  | 2 | A customer reported smoke and flames coming from pole top at the incident location. On arrival the crew found that the one of LV bushings cover bunt out due to overheated connection. There was no ground fire. There were no reported injuries or third party property damage. | Connector/termination | 0 | 0 | 0 |  | K011 | Failed connection, fault report attributed cause as corrosion. Unable to further determine cause. | Pole-top fire | 28/06/2016 8:59 | 1 | Negligible: no ground fire | 2524 | Public space |  | 20160629PWA_01 | Infrastructure (network-based) | -37.8444 | 145.054 | 1 | CitiPower | Report | 3406 | 0.012795 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Connection
Field crew arrived on site and made safe. The substation was isolated, low voltage circuits were placed in parallel to keep customers on supply whilst repairs were conducted on the day. | 77 OFARRELL STREET, YARRAVILLE VIC 3013 |  | Vandalism;Copper theft | [5 empty] | 2 | Jemena field crew was notified by the Coordination Centre of copper theft of High Voltage and Low Voltage Earths at a pole type substation in Yarraville. The substation was isolated and there was no loss of supply to customers as the Low Voltage circuits were put under parallel. Repairs to the earths were completed on the day. | Copper;Pole mounted;Earth/earthing | 0 | 0 | 0 |  | FE9 | The high voltage and low voltage earth conductors were removed from the pole type substation by unknown persons. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42376.5104 |  |  | 2527 | Roadway |  | 20160701JEM_02 | Infrastructure (network-based) | -37.8097 | 144.8843 | 1 | Jemena | Report | 3340 | 0.033264 | Earthing cable | Essendon Airport | 3013 | Yarraville | Other
On arrival crew commenced repairs | 241 KINGSTON ROAD, KINGSTON VIC 3364 | 26587 | Theft | [5 empty] | 2 | Inspectors working on the BAN009 feeder reported the copper earths had been cut and stolen at the incident location. The HV earth was cut and stolen, the LV earth was cut only. There was no fire, injuries or third party property damage. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper cable theft | Less than $50k damage | 30/06/2016 12:57 |  |  | 2537 | Roadway |  | 20160705PWA_01 | Infrastructure (network-based) | -37.3874 | 143.9538 | 1 | Powercor | Report | 3299 | 0.0085602 | Earthing cable | Ballarat Aerodrome | 3364 | Kingston | Other
On arrival crew commenced repairs | 1866 WERONA-KINGSTON ROAD, SMEATON VIC 3364 | 827735 | Theft | [5 empty] | 2 | Inspectors working on the BAN009 feeder reported the copper earths had been cut and stolen at the incident location. The leg of the HV earth was cut and stolen (SWER iso substation) There was no fire, injuries or third party property damage. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper cable theft | Less than $50k damage | 30/06/2016 14:57 |  |  | 2540 | Roadway |  | 20160705PWA_03 | Infrastructure (network-based) | -37.335 | 143.9867 | 1 | Powercor | Report | 3302 | 0.022844 | Earthing cable | Ballarat Aerodrome | 3364 | Smeaton | Other
On arrival nst test passed, 4.5 v on overhead neutral to independent earth which climbs to 6v with hot water load connected, All service connections checked and tightened, all connections back to TX checked and tightened. IPC connection on TX is only single and should be 2. This is a reoccurring problem at this address and seems to occur on peak periods | 97 WOOLAMAI BEACH ROAD, CAPE WOOLAMAI VIC 3925 | 2810616 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 222540. Whilst using outside shower customer received tingles. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | wgi31 | Loose connections on Transformer. | Minor shock | 42710.3854 |  |  | 2543 | Residential |  | 20160705SPN_02 | Infrastructure (network-based) | -38.5294 | 145.3354 | 1 | AusNet Services Distribution | Report | 3305 | 0.017463 | Low voltage AC (<1kV) | Moorabbin Airport | 3925 | Cape Woolamai | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customer. | CLARICE ROAD, BOX HILL SOUTH VIC 3128 | LIS No. 7045008 | Unknown external/community factor | Unknown environment factor |  | Conductor clashing;Fatigue;HV injection;Electrical breakdown | Unknown work practice factor |  | 1 | At 2141hrs on 02/04/2016, 22kV feeder BH22 circuit breaker reclosed to lockout affecting 1108 customers. At the same time, BH34 successfully reclosed and held. The cause of the fault appears to have been an explosion at the HV open point (HV isolators BH 0522) located in Dundee Street. There were splash marks on the HV white and blue phases and a possum was the most likely cause of the fault that caused substantial damage. The HV centre phase conductor fell to the ground on the west side of the HV isolators and three bays of the HV red phase conductor was felled in Clarice Road from the HV CHP to "Mdlboro N313 - Clarice" and "Clarice 31 - Mdlboro" substations. The HV connections appear to have failed where old style crimps were used within the three bays. Secondary damage also occurred as failed HV ampact connections occurred on the blue phase conductor on the north sides of BH0592 and BH0591. The blue phase conductor damage was most likely caused when the red phase HV conductor fell onto the blue phase conductor at the tee-off pole - LIS No. 7045008. The faults crew suspected that a high voltage injection may have occurred and a LEI was dispatched to investigate. A LEI investigated electrical installations on the circuit for damage to the customers appliances and equipment and no damage was identified but there were a number of shops that were left off supply as there was no access to test. 04/04/2016 - Shops re-opened and the LEI returned to test installations where access was not available following the fault. The LEI confirmed a high voltage injection occurred (BWD 1603) at "Alexanders Industrial Laundry" after a damaged dryer was identified. | Conductor (bare);Copper | 0 | 0 | 0 |  | BH 22 | Animal Incident | HV injection;Loss of supply | 42404.9035 |  |  | 1138 | Roadway |  | 20160404UTD_01 | Infrastructure (network-based) | -37.8359 | 145.1341 | 1 | United Energy Distribution | Report | 1622 | 0.012508 | 22kV AC | Moorabbin Airport | 3128 | Box Hill South | Animal
A faults crew attended and found 2 x 20amp HV Powder Filled Fuses on the red and white phases had operated at the spur fuses (FS 1170) along with the HV red and white phase 16amp fuses at "Freemans-Tintajel" pole type substation. The feeder was patrolled and no damage to United Energy infrastructure could be identified. The HV fuses were replaced and supply restored to customers in the area. The cause for the HV fuses to operate was unknown. | FREEMANS ROAD, MOUNT ELIZA VIC 3930 | LIS No. 3315406 | Unknown external/community factor | Unknown environment factor |  | Unknown technical factor | Unknown work practice factor |  | 1 | At 2241hrs on 03/04/2014, 22kV Spur Fusing at FS 1170 located in Daveys Bay Road, Mount Eliza operated affecting 74 customers. Customers that reside in Freemans Road and Old Mornington Road advised of a loud bang and have lost their electricity supply. The CFA are in attendance at the corner of the above Roads for a small vegetation fire, approximately 2sqm in size, that was quickly extinguished. The cause of the small fire appeared to be molten metal falling into the dry vegetation below after the HV fuses operated. | Conductor (bare);Powder filled | 0 | 0 | 0 |  | FSH 13 | Unknown cause. | Other vegetation | 42433.9451 | 1 | Localised: less than 10 sq.m | 1139 | Roadway |  | 20160404UTD_02 | Infrastructure (network-based) | -38.1656 | 145.0884 | 1 | United Energy Distribution | Report | 1623 | 0.019723 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | AF Other
CEOT dispatched a fault crew to make safe, isolate and repair. The faulty surge diverter and blown substation fuse were replaced, 22kV disc insulators cleaned. Supply restored late 8 March. Further notification of a noisy pole at RWN923 required the dispatching of a fault crew to attend early on 10 March and the crew found one BA fuse was candling. BA fuses were manually operated, replaced and supply restored. | 80 WEBB STREET, WARRANDYTE VIC 3113 | 1204854 |  |  |  | Fuse failed to eject |  |  | 1 | IMS 221240. Notification received on 8 March of supply failure at substation â€œWEBB N76 TUNNELâ€ but not attended until approx. 6pm due to higher priority wire down faults. The cause of fault was identified as a faulty surge diverter mounted on the transformer. One of the fuse links on the transformer had operated and opened. The 22kV disc insulators on the substation pole were also noticed to be excessively dirty. The spur was isolated by operating the upstream fuses RW923. The faulty surge diverter and blown substation fuse were replaced, 22kV disc insulators cleaned. Supply restored late on 8 March. On 9th of March, notification received of a â€˜noisy poleâ€™ at RW923. Fault crews attending the site early on 10 March found one BA fuse was candling. Fuses were manually operated, replaced and supply restored. | Boric acid | 0 | 0 | 0 |  | rwn24 | AusNet Services' Lines Section has had discussions with the BA fuse unit manufacturer in relation to a test procedure to investigate the cause of the fuse failure. | Other electricity related | 42616.375 | 1 | Negligible: no ground fire | 1141 | Residential |  | 20160405SPN_01 | Infrastructure (network-based) | -37.7445 | 145.2247 | 1 | AusNet Services Distribution | Report | 1628 | 0.02895 | 22kV AC | Moorabbin Airport | 3113 | Warrandyte | Fuse
CEOT dispatched a fault crew to make safe, investigate and making any necessary repairs. Fault crew isolated sub and line not in use. An Electricity Network Representative / DAO attended site to perform network investigation. When the DAO reach the site, the excavation crew had gone home. The DAO was shown around the site by the Site Supervisor, Berend Van- Daalen - COMDAIN, tel. 0498 332410. After the DAO advised Berend, he contacted the excavator operator with advice to seek medical assessment that no issues with his heart as a result of accidental contact. A No Go Zone Rules breach letter was sent to the offending party. | 130 TUCKERS ROAD, CLYDE VIC 3978 | 508625 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 221344. Live HV overhead conductor to a construction site was struck by an excavator. Excavator was operated by Peadar Quinn of Quinn Excavations. It is alleged that the excavator was moving a silt bin to a silt trap/wash out area when it came into contact with the overhead line. Alleged a Spotter was being used and that he attempted to have excavator stop before coming into contact with the overhead line. The Site Supervisor, Berend Van-Daalen, pointed out excavator was fitted with a electric field sensor/alarm to avoid contact with network assets. No electrical damage/burn marks were observed by AusNet Services' DAO of the excavator or equipment. Electrical protection operated - White phase HV fuse operated. | Conductor (bare) | 0 | 0 | 0 |  | cln22 | Excavator contacted overhead HV line. | No Go Zone (contact) | 42464.5625 |  |  | 1142 | Commercial |  | 20160405SPN_02 | Infrastructure (network-based) | -38.1251 | 145.3454 | 1 | AusNet Services Distribution | Report | 1630 | 0.02635 | 22kV AC | Moorabbin Airport | 3978 | Clyde | Vehicle
A voltage test with reference to an independent earth confirmed an 8 volts rise at the metallic garden water tap. An 8 volt rise was also measured at various points associated with the neutral conductor forming the consumerâ€™s mains and the aerial service line. A Powercor linesman repaired the defective termination. Voltage and NST tests were performed following the repair and normal results were obtained. | 21 MAPLE CRESCENT, HOPPERS CROSSING VIC 3029 |  |  |  |  | Neutral fault |  | Phase to earth |  | Darivs was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his feet on the wet shower base. | Connector/termination | 0 | 0 | 0 |  |  | This voltage rise resulted from a loose neutral service tap clamp termination to the reticulation neutral conductor. The condition described above caused current to flow in the metallic water pipe system via the installation MEN connection, main earth, and water pipe bonding conductors. The level of impedance to the flow of current through the metallic water pipe and the general mass of earth was sufficient to cause a voltage rise of 8 volts on the metallic parts of the plumbing system. | Minor shock | 18/03/2016 11:00 |  |  | 1151 | Residential |  | 20160407PWA_03 | Infrastructure (network-based) | -37.8599 | 144.7092 | 1 | Powercor | Report | 1641 | 0.028664 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
On arrival the crew found that the service wire on the ground and damaged POA. The line disconnected and defect notice issued. | 57 DONNYBROOK ROAD, NORLANE VIC 3214 |  | Working too close to overhead lines | [6 empty] | Mr. Stephan reported that a Bobcat has taken down a service wire and also some damage done to the POA at the incident location. On arrival the crew found that the service wire on the ground and damaged POA. | Service conductor | 0 | 0 | 0 |  |  | Bobcat contacting service cable | No Go Zone (contact) | 42494.6236 |  |  | 1152 | Roadway |  | 20160407PWA_04 | Infrastructure (network-based) | -38.086 | 144.3407 | 1 | Powercor | Report | 8027 | 0.028652 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Vehicle
Crew isolated supply and undertook repairs | KINGSLANGLEY, 3973 STAWELL-WARRACKNABEAL ROAD, RUPANYUP VIC 3388 | 70396 |  |  |  | Leakage |  |  | 2 | Customer rang to advise of pole fire. Crew attended and found 2 way Tee Off cross arm had burnt thru at strap bolt and was hanging from bridge. Crew replaced cross arm. No ground fire start. No shocks or injuries. | Crossarm (wood) | 0 | 0 | 0 |  | STL006 | Excessive leakage current | Pole-top fire | 42525.3042 | 1 | Negligible: no ground fire | 1154 | Agricultural |  | 20160408PWA_01 | Infrastructure (network-based) | -36.6432 | 142.6314 | 1 | Powercor | Report | 3152 | 0.039508 | 22kV AC | Horsham Aerodrome | 3973 | Rupanyup | Crossarm
Made safe | 3A CARSON STREET, RESERVOIR VIC 3073 |  |  |  |  | Leakage |  |  | 2 | Pole top fire causing high voltage injection and high voltage conductor on the ground. | Conductor (bare);Pole top | 0 | 0 | 0 |  |  | Age, weather, leakage | Pole-top fire;HV injection;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42525.3146 | 1 | Negligible: no ground fire | 1162 | Residential |  | 20160411JEM_01 | Infrastructure (network-based) | -37.6984 | 145.0044 | 1 | Jemena | Report | 1654 | 0.0067674 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3073 | Reservoir | Pole
Supply isolated and undertook repairs | 142-218 TOWNSINGS ROAD, DIGGERS REST VIC 3427 | 29408 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location. On arrival crew found that a crossarm fire had occurred on a 66kv crossarm. There was no ground fire. There was no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  | SBY - MLN | Excessive Leakage Current | Pole-top fire | 42646.1049 | 1 | Negligible: no ground fire | 1169 | Roadway |  | 20160412PWA_01 | Infrastructure (network-based) | -37.6065 | 144.6613 | 1 | Powercor | Report | 3106 | 0.030998 | 66kV AC | Melbourne Airport | 3427 | Diggers Rest | Crossarm
Crew isolated supply and undertook repairs | 25 SYLVANDER STREET, BALWYN NORTH VIC 3104 | 9906 | Vehicle | [6 empty] | Owner of the property reported, that the service wire to their house was clipped by truck at the incident location. On arrival the crew found that the LV service was still intact and the supply was ok, but the insulation had shredded and the service wire was hanging lower in tree. The truck left the scene of the incident and they did not see the number plate. There was no ground fire. There were no reported injuries or third party property damages. Height of assets contacted: 3m in the driveway and 4.6m at the kerb | Service conductor | 0 | 0 | 0 |  |  | Unknown vehicle contacted cable | Damage to network assets | 42525.8347 |  |  | 1177 | Residential |  | 20160413PWA_01 | Infrastructure (network-based) | -37.7897 | 145.0937 | 1 | CitiPower | Report | 8019 | 0.027001 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Vehicle
The crew made the place safe and the repairs were done | 18 ST HELIERS STREET, ABBOTSFORD VIC 3067 | 24918 |  |  |  | Overheated connection |  |  |  | MFB reported a pole fire at the incident location. Fault crew attending found a burnt out FSD and the debris from the melted krone box had damaged the roof of the adjacent building. No HV injection reported. There was no ground fire. There were no reported injuries or other third party damage | Connection box | 0 | 0 | 0 |  |  | Overheated connection | Loss of supply;More than $50k damage | 42525.6556 |  |  | 1178 | Roadway |  | 20160413PWA_02 | Infrastructure (network-based) | -37.8021 | 145.0043 | 1 | CitiPower | Report | 2696 | 0.011065 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | Connection
On arrival crew made site safe and organized and completed repairs | 13 HEYINGTON PLACE, TOORAK VIC 3142 | 67149 | Crane, excavator or other construction/farming equipment | [6 empty] | A Contractor (Royale Construction) advised that they have hit a cable at the incident location. On arrival the crew found that the contractor had contacted a live low voltage underground service while they excavating. The insulation was damaged and the low voltage service was still â€œaliveâ€ when the crew arrived. There were no reported injuries. There was no fire. The contractor had no paperwork on site but ref no given over the phone. | Services cable | 0 | 0 | 0 |  | TK025 | excavation works | No Go Zone (contact) | 42525.4424 |  |  | 1180 | Public space |  | 20160413PWA_03 | Infrastructure (network-based) | -37.8398 | 145.0214 | 1 | CitiPower | Report | 8020 | 0.02425 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Dug up
Site made safe - Temporary fencing erected, environmental assessment made | 163 ANDERSON ROAD, SUNSHINE VIC 3020 | 971501 | Vehicle | [5 empty] | 2 | A was car driven into the west side fence of Sunshine East zone substation. The driver indicated that the car was being moved into his truck parking bay when it went out of control passing through two truck bays and collecting a 20 litre drum engine oil (use for truck) then through the bays down the embankment into a through the west timber fence of the ZSS. Inside the yard the car ran alone and stopping when impact with the 66 KV circuit breaker base. The oil drum at that time burst and deposited the oil over the C/B base and into the crushed stone of the switch yard. The driver then turned the car and drove out. There was no Fire or reported injuries Supply was not effected. | Circuit breaker | 0 | 0 | 0 |  | SSE Zone Substation | loss of vehicle control | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);More than $50k damage | 30/03/2016 13:11 |  |  | 1181 | Other | Substation | 20160413PWA_04 | Infrastructure (network-based) | -37.7796 | 144.8281 | 1 | Powercor | Report | 1673 | 0.040766 | 66kV AC | Essendon Airport | 3020 | Sunshine | Vehicle
On arrival crew isolated supply and undertook repairs | 177 KNIGHTS ROAD, CONGUPNA VIC 3633 | 5466 |  |  |  | Leakage |  |  |  | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 0 | 0 | 0 |  | SHN024 | Pole fire | Pole-top fire | 42555.559 | 1 | Negligible: no ground fire | 2187 | Roadway |  | 20160414PWA_02 | Infrastructure (network-based) | -36.3239 | 145.4519 | 1 | Powercor | Report | 2679 | 0.025183 | 22kV AC | Shepparton Airport | 3633 | Congupna | Pole
Crew isolated supply and undertook repairs | 2190 CURR ROAD, TONGALA VIC 3621 | 24089 |  |  |  | Candled fuse |  |  | 2 | On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. No ground fire. There were no reported injuries. No third party property damage. | EDO fuse | 0 | 0 | 0 |  | SHN024 | EDO barrel did not drop out | Other electricity related | 42555.7639 |  |  | 2188 | Roadway |  | 20160414PWA_03 | Infrastructure (network-based) | -36.2408 | 144.9812 | 1 | Powercor | Report | 2680 | 0.00029514 | 22kV AC | Shepparton Airport | 3621 | Tongala | Fuse
Fault crew attended and found in the vicinity of the balloon a 30m x 40m grass fire. The DAO was informed. The DAO was out on-site after the balloon string had been removed. Fire was within vicinity of where the balloon string came in contact with the 66kV line. Fire measured and photos taken. | 2075 OLD SYDNEY ROAD, MICKLEHAM VIC 3064 | 931127 | Recreation - Helium (party) balloons |  |  |  |  | Phase to phase | 1 | IMS 221529. Report at LIS 931127 of a balloon string on SMTS - KMS 66kV line. Feeder CB tripped to lockout. | Conductor (bare) | 0 | 0 | 0 |  | SMTS - KMS 66kv line | A party type helium balloon string made contact with the SMTS - KMS 66kV line. | No Go Zone (contact) | 17/04/2016 17:27 |  |  | 2213 | Agricultural |  | 20160418SPN_01 | Infrastructure (network-based) | -37.5479 | 144.8795 | 1 | AusNet Services Distribution | Report | 3001 | 0.017769 | 66kV AC | Melbourne Airport | 3064 | Mickleham | Other
CEOT dispatched a fault crew to make safe and investigate. The fault crew isolated the overhead service and made safe, removed the meters and service cable from the property. An ESV officer contacted AusNet Services and advised they will speak with Colin Watson, the fault crew leader who attended the site to obtain further details. | 320 WARBURTON HIGHWAY, WANDIN NORTH VIC 3139 | 1002101 | Unauthorised work | [5 empty] | 2 | IMS 221531. Customer call to AusNet Services saying that a service line is down from house end behind the fence. The fault crew leader on arrival at the address found that the house had been demolished, meters removed and the service line was still alive and laying under demolished building material. | Service conductor | 0 | 0 | 0 |  | ldl23 | Demolishment works. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/04/2016 8:49 |  |  | 2215 | Residential |  | 20160418SPN_02 | Infrastructure (network-based) | -37.7763 | 145.4229 | 1 | AusNet Services Distribution | Report | 12592 | 0.038913 | Low voltage AC (<1kV) | Moorabbin Airport | 3139 | Wandin North | Other
On arrive site secured, fence temporary repaired. Drum to be rolled back into yard . | 1321 MURRAY VALLEY HIGHWAY, BOUNDARY BEND VIC 3599 |  | Vandalism | [5 empty] | 2 | Gardening maintenance contractor reported the perimeter fence at the Boundary Bend ZSS had been cut and a drum of cable rolled out of yard. ZSS operator attended and found the perimeter fence had been cut from top to bottom and a large drum of covered aluminium cable had been rolled out of yard and down the hill, coming to rest on a nearby dam bank. No cable was missing. Police attended. No shocks, fire, injuries or third party damage. | No failed asset | 2 | 2 | 2 |  |  | Vandalism | More than $50k damage | 18/04/2016 13:45 |  |  | 2221 | Agricultural |  | 20160419PWA_02 | Infrastructure (network-based) | -34.7127 | 143.0057 | 1 | Powercor | Report | 2764 | 0.032409 | Not applicable | Swan Hill Aerodrome | 3599 | Boundary Bend | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Junction Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. | 12 MAXWELL GROVE, WARRNAMBOOL VIC 3280 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Jayne Mills was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her feet while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  |  | The increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 48.0 Volts on the water piping system and between the points of contact. | Minor shock | 42586.5 |  |  | 2223 | Roadway |  | 20160420PWA_01 | Infrastructure (network-based) | -38.3893 | 142.508 | 1 | Powercor | Report | 2766 | 0.038244 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew made safe and commenced repairs | 54 WESTMINSTER PARKWAY, DERRIMUT VIC 3030 | 41095602 | Theft | [5 empty] | 2 | A Powercor contractor reports that copper straps have been stolen from a kiosk substation in the Sunshine area. On arrival the crew found that thieves are targeting the copper earth door straps. There were no reported injuries. There was no fire. | Earth/earthing | 0 | 0 | 0 |  | SU013 | copper theft | Less than $50k damage | 21/04/2016 12:30 |  |  | 2238 | Roadway |  | 20160426PWA_03 | Infrastructure (network-based) | -37.7857 | 144.7575 | 1 | Powercor | Report | 2785 | 0.026094 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew made site safe and commenced repairs | 16 HOLMEWOOD AVENUE, DEER PARK VIC 3023 | 41094568 | Theft | [5 empty] | 2 | A Powercor contractor reports that copper straps have been stolen from a kiosk substation in the Sunshine area. On arrival the crew found that thieves are targeting the copper earth door straps on the kiosk substation. There were no reported injuries. There was no fire. | Earth/earthing | 0 | 0 | 0 |  | SU015 | Copper Theft | Less than $50k damage | 21/04/2016 12:30 |  |  | 2239 | Public space |  | 20160426PWA_04 | Infrastructure (network-based) | -37.7785 | 144.7577 | 1 | Powercor | Report | 2786 | 0.033616 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
On arrival crew isolated supply and removed service cable, service was replaced later in the day | 755-781 GREIGS ROAD, MOUNT COTTRELL VIC 3024 | 111610 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Louis and Carmen Buhagiar reported a wire sparking at the incident location. On arrival the crew found a 3ph grey overhead twisted service sparking at the dog bone at pole LIS-111610. There was no ground or asset fire. There were no reported injuries or third party property damages. Crew isolated supply and removed the bay of service cable crossing the road. A second fault crew followed up later in the evening to replace the service cable. | Service conductor | 0 | 0 | 0 |  | MLN021 | Insulation failure | Loss of supply | 21/04/2016 16:35 |  |  | 2240 | Roadway |  | 20160426PWA_05 | Infrastructure (network-based) | -37.7456 | 144.6385 | 1 | Powercor | Report | 2837 | 0.018137 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | OH Cable
The gardener immediately secured the area and prevented public access by placement of some witches hats. Citipower fault crew attended and the damaged low voltage service was replaced. | 31 BROUGHAM STREET, RICHMOND VIC 3121 | 6227 | Working too close to overhead lines |  |  |  | Unknown work practice factor |  | 2 | Dallas Gardening services reported that they has severed a low voltage service at the incident location. Resulting in the service falling onto the ground. There were no reported injuries, there was no fire. | Service conductor | 0 | 0 | 0 |  | RTS-NR | Accidental contact with service line by extendable hedge trimmer | No Go Zone (contact) | 22/04/2016 8:50 |  |  | 2241 | Residential |  | 20160426PWA_06 | Infrastructure (network-based) | -37.8216 | 145.0011 | 1 | CitiPower | Report | 2788 | 0.017885 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew disconnected and reterminated the existing O/H Twisted Service Cable at the Customerâ€™s FOLCB and completed an NST Test which confirmed a Pass result. | 9 CHATHAM AVENUE, MOUNT HELEN VIC 3350 | 36766 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Julie White was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet while standing on the wet shower base. | Service conductor;Connection box | 0 | 0 | 0 |  | BAS022 | Corroded connection at FOLCB | Minor shock | 13/04/2016 17:00 |  |  | 2248 | Residential |  | 20160427PWA_02 | Infrastructure (customer connection) | -37.6275 | 143.8734 | 1 | Powercor | Report | 2798 | 0.039891 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Mount Helen | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB located at the POA, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 74 THACKER STREET, OCEAN GROVE VIC 3226 | 955079 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Kevin Downey was removing a gas heater when he made simultaneous contact with his hands between the earthed Gas Heater Casing and the disconnected gas pipe. | Connection box | 0 | 0 | 0 |  | DDL011 | A corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB | Minor shock | 22/04/2016 9:45 |  |  | 2249 | Residential |  | 20160427PWA_03 | Infrastructure (customer connection) | -38.2548 | 144.5106 | 1 | Powercor | Report | 2799 | 0.032705 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
On arrival crew made site safe and commenced repairs | 25 BRIGGS DRIVE, DERRIMUT VIC 3030 | 928395 | Copper theft | [5 empty] | 2 | A Powercor HV operator reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that a part of earthing cable had been cut away from the pole. Conduit on the pole also damaged. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | LVN034 | Copper theft | Less than $50k damage | 27/04/2016 8:34 |  |  | 2271 | Roadway |  | 20160429PWA_03 | Infrastructure (network-based) | -37.8069 | 144.7814 | 1 | Powercor | Report | 2826 | 0.014135 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew made site safe and commenced repairs | 3327 NHILL-YANAC ROAD, YANAC VIC 3418 | 10048 | Vehicle;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A Customer reported a service wire down at the incident location. On arrival the crew found that a 2 wire service had been pulled down by a vehicle from a LV inter pole to a house, resulting in the service being detached from the house end and laying across the road, No Protection operated. There were no reported injuries or Fire. | Service conductor | 0 | 0 | 0 |  | NHL031 | Suspect high farm implement | Loss of supply | 25/04/2016 23:30 |  |  | 2272 | Roadway |  | 20160429PWA_04 | Infrastructure (network-based) | -36.1356 | 141.4372 | 1 | Powercor | Report | 2827 | 0.033159 | Low voltage AC (<1kV) | Horsham Aerodrome | 3327 | Yanac | Vehicle
Crew isolated supply and undertook repairs | 310 BANGERANG ROAD, ECHUCA VILLAGE VIC 3564 | 27135 |  | Fallen |  |  |  |  | 1 | A Powercor crew patrolling following a feeder outage, reported a grass fire at the incident location. On arrival the crew found that a tree from outside the clearance space had rotted and broken off just above ground level, falling on the 22kV High Voltage conductors, causing them to break and fall to the ground, resulting in a grassfire of approx. 500m x 100m (5Ha). There were no reported injuries. Protection operated. Some fences were also damaged, the ownership of these fences could not be determined. | Conductor (bare) | 0 | 0 | 0 |  | ECA003 | Vegetation: Trees Incident | Grassfire | 28/04/2016 11:56 | 1 | Medium: 1000 sq.m - 10 ha | 2275 | Forest - native (not park) |  | 20160429PWA_06 | Infrastructure (network-based) | -36.1249 | 144.8065 | 1 | Powercor | Report | 2831 | 0.019988 | 22kV AC | Shepparton Airport | 3564 | Echuca Village | Trees
Additional emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A SCAP was to be issued by the Rail Authority but took some time to obtain. | 28 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | LIS No. 3302249 | Unknown external/community factor |  |  | Corrosion;Fatigue;Overheated connection |  |  | 1 | At 1853hrs on 04/04/2016, 22kV feeder MC 01 circuit breaker reclosed to lockout affecting 2001 customers. The cause of the HV feeder to lockout was a probable possum at pole No. LIS 8816848 with no damage sustained at this location after the possum got between the red phase HV conductor and earth. Customers on the feeder were also advising of dim lights and further damage was found at the CHP LIS. No. 1824222 and the feeder was sectionalised to minimise the numbers of customers affected. HV ACR FS0172 was closed and the BUEF operated at MC zone substation with the loss of the MC No. 1 bus and 22kV feeder MC 02. The ACR was opened and supply promptly restored. The Downer First Responder patrolled sections of the feeder from CRM zone substation and found a de-energised HV conductor on the ground in Nepean Highway opposite Watkins Street at pole No. LIS 3302249. The ampact connection failed at this location due to probable fault current and the connection was found to be slightly deteriorated due to salt spray from Port Phillip Bay. Molten metal fell to the ground following the fault with small burn marks found in the dry grass below the pole. No high voltage injection occurred or was suspected as a result of the fault. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | MC 01 | The ampact connection failed at this location due to probable fault current and the connection was found to be slightly deteriorated due to salt spray from Port Phillip Bay. | Grassfire | 42464.7868 | 1 | Localised: less than 10 sq.m | 2270 | Roadway |  | 20160429UTD_01 | Infrastructure (network-based) | -38.0137 | 145.0908 | 1 | United Energy Distribution | Report | 2825 | 0.03253 | 22kV AC | Moorabbin Airport | 3195 | Aspendale | Connection
On arrival crew made site safe and commenced repairs | 1100 BELLS ROAD, BARUNAH PARK VIC 3329 | 11605 |  | Lightning |  |  |  |  | 1 | A Powercor crew were patrolling the Mt Rebecca SWER line following the a fuse operation on Mt Rebecca 3 ISO. The crew noticed a fire in the distance and went to the incident location. On arrival the crew found that a transformer had failed (Potentially lightning), the lid of the transformer had dislodged during the fault, and the oil in the transformer had caught alight. There was no ground fire. No injury and no third party damage was reported. | Pole mounted | 1 | 1 | 0 |  | CLC003 | Lightning | Plant/equipment | 42374.2333 | 1 | Negligible: no ground fire | 2294 | Roadway |  | 20160504PWA_03 | Infrastructure (network-based) | -38.0187 | 143.775 | 1 | Powercor | Report | 2853 | 0.038285 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3329 | Barunah Park | Lightning
Crew made site safe and repaired or replaced missing cables. | 81 CUMMINS ROAD, MOUNT ROWAN VIC 3352 | 6198 | Theft | [5 empty] | 2 | Contractor reported damaged and missing earth cables from pole. No shocks, injuries or third party damage. | Pole mounted | 0 | 0 | 0 |  | BAN009 | Cable theft | Less than $50k damage | 42434.3611 |  |  | 2297 | Roadway |  | 20160504PWA_04 | Infrastructure (network-based) | -37.497 | 143.8373 | 1 | Powercor | Report | 2856 | 0.014977 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Other
Crew made site safe and repaired or replaced missing cables. | 35 NOBLE COURT, MOUNT ROWAN VIC 3352 | 6198 | Theft | [5 empty] | 2 | Contractor reported damaged and missing earth cables from pole. Crew attended and found LV earth cable missing or damaged at pole. No shocks, injuries or third party damage. | Pole mounted | 0 | 0 | 0 |  | BAN009 | cable theft | Less than $50k damage | 42434.3646 |  |  | 2298 | Roadway |  | 20160504PWA_05 | Infrastructure (network-based) | -37.5147 | 143.8364 | 1 | Powercor | Report | 2857 | 0.017132 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Other
On arrival crew made site safe and commenced repairs | 90 TAYLORS ROAD, KEILOR DOWNS VIC 3038 | 25265 | Working too close to underground cables | [5 empty] | 2 | A Contractor (Man Civil 1/5b Hamilton St Gisborne) advised that they have hit a cable at the incident location. On arrival the crew found that the contractor had contacted a street light underground service. The cable and conduit have been damaged. There were no reported injuries. There was no fire. he contractor had no paperwork on site but ref no given over the phone. Name of the person who on the site is Terry Custodio | Cable | 0 | 0 | 0 |  | SA003 | Contractor damaging underground lighting cable | No Go Zone (contact) | 42434.4285 |  |  | 2299 | Roadway |  | 20160504PWA_06 | Infrastructure (network-based) | -37.7282 | 144.8049 | 1 | Powercor | Report | 2858 | 0.038662 | Low voltage AC (<1kV) | Melbourne Airport | 3038 | Keilor Downs | Dug up
The copper earthing conductors were replaced at the two pole type substations and protective cover guards firmly fixed in place in an effort to prevent a re-occurrence. | WORSLEY ROAD, BANGHOLME VIC 3175 | LIS NO. 0623739 and 9863503 | Theft;Unauthorised work | Unknown environment factor |  | Earth fault | Unknown work practice factor |  | 2 | A passing Downer crew advised the copper earthing conductor had been removed at "Worsley-4N-Hardwood" pole type substation. An investigation identified that copper earthing conductors had been removed by unknown persons at "Worsley-4N-Hardwood" (LIS No. 9863503) and "Worsley-Hardwood" (LIS No. 0623739) pole type substations. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | DVY 34 | Copper earthing conductors had been stolen by unknown persons. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/04/2016 16:00 |  |  | 2290 | Roadway |  | 20160504UTD_03 | Infrastructure (network-based) | -38.0537 | 145.1843 | 1 | United Energy Distribution | Report | 2849 | 0.037626 | 22kV AC | Moorabbin Airport | 3175 | Bangholme | Other
Emergency high voltage switching was completed and the HV intermediate crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 38 THORNTON CRESCENT, MITCHAM VIC 3132 | LIS No. 7031340 | Unknown external/community factor | Precipitation |  | Electrical breakdown;Insulator;Leakage | Unknown work practice factor |  | 2 | A Select Solutions Asset Inspector identified a burnt HV cross arm with a insulator hanging off the cross arm with the conductor attached. Following light drizzly rain, a pole fire occurred at a HV intermediate crossarm on pole No. LIS 7031340 located outside the Thornton Crescent CafÃ© at the rear of 38 Thornton Crescent, Mitcham. The failed cross arm was identified by a Select Solutions Asset Inspector and the cause was attributed to a HV fog type insulator breaking down. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | RWT 12 | The cause was attributed to a HV fog type insulator breaking down. | Pole-top fire | 42525.8333 | 1 | Negligible: no ground fire | 2295 | Roadway |  | 20160504UTD_05 | Infrastructure (network-based) | -37.8206 | 145.187 | 1 | United Energy Distribution | Report | 2854 | 0.033309 | 22kV AC | Moorabbin Airport | 3132 | Mitcham | AF Other
Emergency high voltage switching was completed and the 15/12kN 66kV intermediate with a 22kV tee-off timber pole was replaced under Access Authority conditions the following day. Traffic control was required and a High Pressure gas transmission pipeline was required to be positively located prior to the commencement of work. The pole was replaced and supply restored at approximately 5.30PM on 05/05/2016. | DANDENONG-HASTINGS ROAD, SOMERVILLE VIC 3912 | LIS No. 3307284 | Vehicle | Precipitation |  | Insulator;Leakage | Unknown work practice factor |  | 2 | Per CFA - there is a fire at the crossarm on a pole located on the corner of Western Port Highway and Queens Road, Somerville. During light drizzly rain, it appears a 66kV (TBTS-FTS) intermediate timber pole (LIS No. 3307284) with a 22kV (HGS 33) tee-off has been struck by an unknown vehicle on the corner of Western Port Highway and Queens Road, Somerville. This resulted in the centre phase 22kV conductor dislodging from the HV insulator onto the steel crossarm and the pole to burn near the 22kV crossarm straps to an extent where the timber pole requires replacement due to the depth of the burnt area. | Conductor (bare);Pole (wood);Crossarm (steel);Insulator tie wires/connections | 0 | 0 | 0 |  | 66kV TBTS-FTS and 22kV HGS 33 | A 66kV (TBTS-FTS) intermediate timber pole (LIS No. 3307284) with a 22kV (HGS 33) tee-off has been struck by an unknown vehicle on the corner of Western Port Highway (AKA - Dandenong-Hastings Road) and Queens Road, Somerville | Pole-top fire | 42465.8903 | 1 | Negligible: no ground fire | 2311 | Roadway |  | 20160509UTD_02 | Infrastructure (network-based) | -38.2151 | 145.2192 | 1 | United Energy Distribution | Report | 2880 | 0.0014109 | 22kV AC;66kV AC | Moorabbin Airport | 3912 | Somerville | Vehicle
On arrival the crew removed the service from the pole . | 42 LEARMONTH CRESCENT, SUNSHINE WEST VIC 3020 | 745194 | Unauthorised work | [5 empty] | 2 | Mark (Powercor employee) reported that a low voltage service has been interfered with at the incident location. On arrival the crew found that a third party (details not obtained) had removed the house end mains junction box leaving the exposed active hanging from the fascia. Resulting in an unsafe situation. There were no reported injuries. There was no fire. | Service conductor | 2 | 2 | 2 |  | SSE034 | Removal of FOLCB from house by unknown party. | Loss of supply | 42495.575 |  |  | 2321 | Residential |  | 20160510PWA_02 | Infrastructure (network-based) | -37.8028 | 144.8319 | 1 | Powercor | Report | 2898 | 0.013801 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Other
On arrival site made safe. The attending Powercor Fault Crew replaced the O/H Service Cables supplying each property and completed an NST Test at both properties which confirmed a Pass result. | 35 GEORGE STREET, HAMILTON VIC 3300 |  |  | Fire |  | Leakage |  | Phase to earth | 2 | Mr Bryan Barrera received an electric shock while he was standing on damp ground when he made simultaneous contact with his hand on the metallic frame of the Meter Enclosure Door and his wet feet wearing thongs on the damp ground. | Service conductor | 0 | 0 | 0 |  |  | The O/H Service Cable supplying the adjacent property was damaged as a result of a stationary vehicle fire which occurred directly below the O/H Service Cable. | Minor shock | 42618.3229 |  |  | 2348 | Roadway |  | 20160518PWA_01 | Infrastructure (network-based) | -37.7468 | 142.0339 | 1 | Powercor | Report | 2949 | 0.013603 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Vehicle
On arrival crew mad site safe . The attending Powercor Fault Crew replaced the Single Phase O/H Twisted Aluminium Service Cable and the Termination Device and completed an NST Test which confirmed a Pass result. | 2 HOLLOWAY GROVE, SWAN HILL VIC 3585 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Mr Daniel Wood (Builder) was replacing the Facia Board adjacent the POA when he received an electric shock as he made simultaneous contact between his hand on the metal roof and his arm in contact with the energised O/H Service Cable Hook attached to the Facia at the POA. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a deteriorated O/H Service Cable Termination Device â€œDog Boneâ€ where the sharp end of the inner metallic rod was exposed at the opposite end to the hook and had made contact with the energised Active Conductor of the O/H Twisted Service Cable. This condition resulted in a potential difference of 241 Volts between the points of contact when the O/H Service Cable Hook attached to the Facia was in contact with the energised metallic hook of the O/H Service Cable Termination Device. | Service conductor | 0 | 0 | 0 |  |  | O/H Service Cable Hook attached to the Facia was in contact with the energised metallic hook of the O/H Service Cable Termination Device. | Minor shock | 26/04/2016 21:30 |  |  | 2349 | Residential |  | 20160518PWA_02 | Infrastructure (network-based) | -35.3323 | 143.5421 | 1 | Powercor | Report | 3175 | 0.038757 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | AF Other
On arrival the crew found that a unknown vehicle had struck 2 LV service cables breaking both off. Site made safe repairs commenced | 2 WILSON STREET, MYSTIC PARK VIC 3579 | 824701 | Vehicle | [5 empty] | 2 | Customer from #2 Wilson Street reported that a high load had struck LV service supplying premises at the incident location. There were no reported injuries, no ground fire. | Service conductor | 0 | 0 | 0 |  | KGT004 | Unknown vehicle struck service lines | Loss of supply | 14/05/2016 18:20 |  |  | 2351 | Roadway |  | 20160518PWA_04 | Infrastructure (network-based) | -35.5579 | 143.7255 | 1 | Powercor | Report | 2951 | 0.040925 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3579 | Mystic Park | Vehicle
On arrival crew made safe and commenced repairs | 9 ST DAVID STREET, NORTHCOTE VIC 3070 | 71877 |  |  |  | Unknown technical factor |  |  | 1 | MFB reported a pole fire at the incident location. On arrival the crew found that a piece of HV Isolator had overheated and fallen to the ground beside the pole. There was no ground fire, No reported injuries and no third party damage | Disconnector/isolator | 0 | 0 | 0 |  | NC015 | HV isolator heating due to fault further downstream | Loss of supply | 14/05/2016 21:54 |  |  | 2357 | Roadway |  | 20160519PWA_01 | Infrastructure (network-based) | -37.7658 | 145.0049 | 1 | CitiPower | Report | 2959 | 0.0172 | 11kV AC | Essendon Airport | 3070 | Northcote | Connection
The faults crew attended and the occupier advised that he received an electric shock from the metal garage lift up door yesterday when it was raining heavily. A LEI was requested to attend to investigate the cause and the faults crew commenced to check connections after a NST failed at the POA. They immediately identified a broken service neutral connection at the pole end at pole No. LIS 1315075. The faults crew replaced the single phase grey twisted service with a XLPE type and installation tests were completed that confirmed the fault had been rectified with 1.2v measured to an independent earth on the neutral bar at the consumers main switchboard and the point of contact. Supply was left on and the occupier advised of the rectification work. | 114 TRUEMANS ROAD, TOOTGAROOK VIC 3941 | LIS No. 1315075 | Unknown external/community factor | Precipitation |  | Corrosion;Neutral fault | Unknown work practice factor | Phase to earth | 2 | AMI meter 0631009 is reporting high voltage events. Please perform NST and check all neutral connections for faults. The United Energy AMI Analysts identified a meter that was communicating high volts and a faults crew were dispatched to investigate. | Service conductor;Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | Broken service neutral connection at the pole end. | Minor shock | 16/05/2016 12:30 |  |  | 2363 | Residential |  | 20160520UTD_01 | Infrastructure (network-based) | -38.3773 | 144.8582 | 1 | United Energy Distribution | Report | 2967 | 0.0090775 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | Tootgarook | Connection
On arrival crew made site safe and commenced repairs | 1104 GNARR ROAD, UNDERBOOL VIC 3509 | 20748 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A field crew attending an outage found that a tractor driver (Andrew Willsmoore, tractor driver and property owner Ph: 0429 946 320) made contact with a 12.7kV SWER pole LIS: 20748 bringing pole & conductor to the ground. There was no Ground fire, shock or third party property damage. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | OYN001 | Tractor striking pole | Loss of supply | 19/04/2016 22:38 |  |  | 2376 | Agricultural |  | 20160525PWA_01 | Infrastructure (network-based) | -35.0899 | 141.8642 | 1 | Powercor | Report | 2986 | 0.021752 | 12.7kV AC (SWER) | Mildura Airport | 3509 | Underbool | Vehicle
A faults crew attended and disconnected supply to the lantern and a further trouble order was created for ACE to attend and replace the defective 150w HPS lantern. | 111 ASLING STREET, BRIGHTON VIC 3186 | LIS No. 2307413 | Unknown external/community factor | Precipitation |  | Moisture ingress;Overheated connection | Unknown work practice factor |  | 2 | Per MFB - burnt out street light and the MFB are now leaving the site. A 150w HPS lantern installed on a 6m outreach bracket on pole No. 2307413 located outside 111 Asling Street, Brighton caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but could be attributed to a possible overheated connection or moisture ingress. | Pole-top fire | 25/05/2016 8:00 | 1 | Negligible: no ground fire | 2386 | Roadway |  | 20160526UTD_01 | Infrastructure (network-based) | -37.8947 | 145.0035 | 1 | United Energy Distribution | Report | 2997 | 0.033922 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | AF Other
Emergency high voltage switching was completed and the timber pole was replaced under Access Authority conditions after traffic control was arranged and set up. An investigation is underway to determine the cause of why the HGS zone substation 66kV circuit breaker C also opened auto with no reclose attempt. The circuit breaker was closed via SCADA by the United Energy Control Room. | ROBINSONS ROAD, LANGWARRIN VIC 3910 | LIS No. 3301887 | Vehicle | Precipitation |  | Conductor clashing;HV injection |  |  | 1 | At 1553hrs on 28/05/2016, 66kV feeder "TBTS-FTS" circuit breaker locked out after a car struck a pole in Robinsons Road, Langwarrin. At the same time, 22kV feeder circuit breaker FSH 33 reclosed to lockout and there were successful circuit breakers recloses on 22kV feeder FSH 21 and ACR FS1069. The HGS zone substation 66kV circuit breaker C also opened auto with no reclose attempt. A vehicle hit and damaged a timber 66kV, 22kV intermediate pole with LV strain construction in Robinsons Road - Pole No. LIS 3301887. The pole was severely damaged and required replacement. There appears to have been a 66kV injection into the 22kV overhead conductors that caused outages and circuit breaker recloses on 22kV FSH zone substation feeders. The faults crew requested a LEI attend as a HVI may have occurred. The LEI attended and confirmed that a high voltage injection did not occur and no damage was sustained to customers electrical installations. Customers supplied from "Murndal-Casurina" substation advised of a loss of supply and the faults crew attended and identified the HV red phase 16amp powder filled fuse had operated following the injection. The faults crew were required to de-energise the whole spur from HV switch FS0264 for a short duration that interrupted customers supplied from 3 substations. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | 66kV feeder "TBTS-FTS" and FSH 21 | Car struck the timber pole. | HV injection;Loss of supply | 28/05/2016 15:53 |  |  | 2404 | Roadway |  | 20160531UTD_01 | Infrastructure (network-based) | -38.183 | 145.2061 | 1 | United Energy Distribution | Report | 3243 | 0.0044294 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3910 | Langwarrin | Vehicle
The attending Powercor Fault Crew replaced the existing O/H Service Cable following installation of a new FOLCB and completed an NST Test which confirmed a Pass result. | 2 TUCKER STREET, BREAKWATER VIC 3219 |  |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Nicola Gordon received an electric shock whilst removing washing from the Washing Machine when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the concrete floor. | Service conductor | 2 | 2 | 2 |  |  | Voltage tests identified a corroded O/H Service Neutral Conductor termination at the Reticulation Service Pole and a corroded Consumers Main Neutral termination at the Customerâ€™s POA. | Minor shock | 16/04/2016 20:00 |  |  | 2414 |  |  | 20160601PWA_03 | Infrastructure (network-based) | -38.1762 | 144.3692 | 1 | Powercor | Report | 3034 | 0.011236 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Breakwater | Connection
High Voltage Overhead assets isolated for work party and the cross-arm was replaced. | 129 RENNIE STREET, COBURG VIC 3058 | 10673174 |  | Industrial or urban pollution |  | Leakage |  |  | 2 | Jemena received a report advising that a high voltage wooden intermediate crossarm had burnt through on the footpath side. | Crossarm (wood) | 0 | 0 | 0 |  | CS09 | The cause was found to be surface tracking on the porcelain insulators, resulting in leakage current between phases and an eventual pole top fire. The presence of pollution on the insulator surface allows leakage current to track over the insulator. This leakage current and the associated voltages developed on the structure have caused the high temperature ionization of air surrounding the wood crossarm kingbolt, resulting in a slow burn between the kingbolt and the pole. Over time this has burnt away the sound wood supporting the crossarm and resulting the pole top fire. | Pole-top fire | 18/05/2016 10:21 | 1 | Negligible: no ground fire | 2436 | Public space |  | 20160606JEM_03 | Infrastructure (network-based) | -37.7516 | 144.9785 | 1 | Jemena | Report | 3280 | 0.030917 | 22kV AC | Essendon Airport | 3058 | Coburg | Crossarm
The crew made the place safe and connections have been temporary repaired. | 3 CURRUNGHI COURT, ST ALBANS VIC 3021 | 844240 | Vehicle | [5 empty] | 2 | MFB reported a car hit LV pillar at the incident location. On arrival Powercor crew found that the (N.O.) pillar had been damaged and wire exposed. No vehicle details available. There were no reported injuries, fire or third party property damage. | LV Pillar | 0 | 0 | 0 |  | SSE012 | Pillar struck by unknown vehicle | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/05/2016 23:22 |  |  | 2446 |  |  | 20160608PWA_06 | Infrastructure (network-based) | -37.7516 | 144.8274 | 1 | Powercor | Report | 3124 | 0.038108 | Low voltage AC (<1kV) | Essendon Airport | 3021 | St Albans | Vehicle
On arrival crew removed all LV service fuses | 530 GOULBURN VALLEY HIGHWAY, SHEPPARTON NORTH VIC 3631 | 2802 | Unauthorised work |  |  |  | Incorrect electrical isolation and/or permits |  | 2 | An employee reported a cable on the ground cable at the incident location. On arrival the crew found that a low voltage service cable had been disconnected from a building and left on ground by a third party. There was no ground fire. There were no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  | SHN011 | demolishment of house | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42557.3951 |  |  | 2447 |  |  | 20160608PWA_07 | Infrastructure (network-based) | -36.3327 | 145.4051 | 1 | Powercor | Report | 3125 | 0.0070417 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Shepparton North | Other
A LEI and faults truck attended and initial voltage testing between an independent earth to the points of contact showed a reading of 15v. The faults crews inspected all connections and suspected the cause to be a faulty connection in the pillar. The faults crew found the connection was loose that caused over heating and arcing. An underground crew attended and had to isolate supply from "Dowell-Jacksons" substation to safely complete the rectification work. The underground crew installed a new neutral bar in the LV pillar and re-terminated connections that were cleaned and greased. Supply was restored after installation tests were completed that confirmed the fault had been rectified. The customer was advised of the investigation findings and rectification work. | 9 BOYD AVENUE, CHELSEA VIC 3196 |  |  |  |  | Neutral fault;Overheated connection |  | Phase to earth | 2 | REC No. 23703 (Trevor) called to advise the customer had been receiving electric shocks from the water taps and shower head since last night. The REC advised there is current at the incoming neutral at the switchboard. The occupier had received slight electric shocks last night to her hand when she touched the shower and contacted a REC to investigate. The REC contacted the United Energy faults and emergencies call centre after he was unable to find any internal problems. | Copper;LV Pillar | 0 | 0 | 0 |  |  | The cause was a faulty neutral connection in the pillar. | Minor shock | 42619.2708 |  |  | 2474 | Residential |  | 20160616UTD_01 | Infrastructure (network-based) | -38.0432 | 145.1266 | 1 | United Energy Distribution | Report | 3199 | 0.0068021 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Connection
A faults crew attended and disconnected supply to the lantern and a further trouble order was created to replace the defective 150w HPS lantern. Traffic control will be required due to the location near the roundabout. | 432 BONEO ROAD, BONEO VIC 3939 | LIS No. 1318653 |  | Precipitation |  | Moisture ingress |  |  | 2 | Per CFA - Street light fire opposite the fire station. A 150w HPS lantern on pole No. 1318653 located outside 432 Boneo Road caught fire and was extinguished by the CFA. The cause was unknown but it had been raining prior to the lantern catching on fire. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but it had been raining prior to the lantern catching on fire. | Pole-top fire | 15/05/2016 19:55 | 1 | Negligible: no ground fire | 2476 | Roadway |  | 20160616UTD_02 | Infrastructure (network-based) | -38.3987 | 144.8878 | 1 | United Energy Distribution | Report | 3205 | 0.036653 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Boneo | AF Other
The HV Operator patrolled the feeder and the United Energy Duty Manager was advised. | 42 BERGINS ROAD, ROWVILLE VIC 3178 | 8809209 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | At 1353hrs on 18/06/2016, 22kV feeder LD33 circuit breaker successfully reclosed and held. Unknown third party contacted the 22kV overhead conductors opposite 42 Bergins Road, Rowville near pole No. LIS 8809209. A HV Operator was dispatched and found there was no crane or witnesses present on arrival however, there were tyre marks and burn marks on ground. There was no damage to United Energy assets and the MFB reported that a crane was removing or delivering a cubby house over rear fence at 35 Salerno Way, Rowville. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | LD 33 | No Go Zone infringement. | No Go Zone (contact) | 18/06/2016 13:53 |  |  | 2484 | Roadway |  | 20160620UTD_01 | Infrastructure (network-based) | -37.9335 | 145.2352 | 1 | United Energy Distribution | Report | 3218 | 0.03534 | 22kV AC | Moorabbin Airport | 3178 | Rowville | Vehicle
On arrival crew commenced repairs | 4A TONGE STREET, ANGLESEA VIC 3230 | 29385 |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire at the incident location. On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. There was no ground fire. There were no reported injuries. | Pole (wood);Connection box | 0 | 0 | 0 |  | WPD021 | corrosion | Pole-top fire;Loss of supply | 26/06/2016 23:39 | 1 | Negligible: no ground fire | 2521 | Roadway |  | 20160628PWA_07 | Infrastructure (network-based) | -38.4126 | 144.1873 | 1 | Powercor | Report | 3271 | 0.035688 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
Crew isolated supply and repairs undertaken. Details of repairs not identified. | 995 RATHDOWNE STREET, CARLTON NORTH VIC 3054 | 88435 | Working too close to underground cables | [5 empty] | 2 | A Contractor (DFG Infrastructure Solutions) advised that their crew have hit a cable at the incident location while they were digging with crowbar for a new gas line. On arrival the crew found that the contractor had damaged a live low voltage underground service. The insulation was damaged and the low voltage service was still â€œaliveâ€ when the crew arrived. There were no reported injuries. There was no fire. | Services cable | 0 | 0 | 0 |  | BQ022 | Contractor installing gas main | No Go Zone (contact) | 24/06/2016 11:32 |  |  | 2523 | Residential |  | 20160628PWA_08 | Infrastructure (network-based) | -37.7803 | 144.9731 | 1 | CitiPower | Report | 3409 | 0.0024734 | Low voltage AC (<1kV) | Essendon Airport | 3054 | Carlton North | Dug up
A faults truck attended and isolated supply to the west LV circuit supplied from "Fernlea-Montreal" substation. A ZNX underground crew were called and proceeded to replace the damaged LV pillar as the casing within the pillar was fire damaged. Supply was restored upon completion after installation tests were completed. | 19 FERNLEA CRESCENT, DONCASTER EAST VIC 3109 |  |  | Precipitation |  | Overheated connection |  |  | 1 | Customers supplied from "Fernlea-Montreal" substation advised of a loss of their electricity supply. It appears an underground cable connection failed in a LV pillar located outside 19 Fernlea Crescent, Doncaster East that caused a 0.5sqm grass fire within and around the pillar. The small grass fire within the pillar self extinguished. | Connector/termination;LV Pillar | 0 | 0 | 0 |  |  | It was suspected that an underground cable connection failed in a LV pillar. | Grassfire | 26/06/2016 4:15 | 1 | Localised: less than 10 sq.m | 2522 | Roadway |  | 20160628UTD_02 | Infrastructure (network-based) | -37.753 | 145.1707 | 1 | United Energy Distribution | Report | 3272 | 0.012219 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Connection
Site was made safe and repairs were made to the damaged sections of conductor. Additionally, the entire tree was removed to prevent further re-occurrence. | 9 WELSH ROAD, GISBORNE VIC 3437 | 10147613 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | A tree which failed at the rootplate fell across HV conductors in Weigall road cnr Welsh road, Gisbourne. This event was due to high winds and caused a HV wire to fall to the ground. Tree branches were outside of the clearance space at the time of the incident. | Conductor (bare);Steel;Boric acid;ACR/OCR | 0 | 0 | 0 |  | SBY32 | Vegetation: Trees Incident | Loss of supply | 42650.8806 |  |  | 2570 | Roadway |  | 20160710JEM_03 | Infrastructure (network-based) | -37.5248 | 144.6171 | 1 | Jemena | Report | 3548 | 0.015373 | 22kV AC | Melbourne Airport | 3437 | Gisborne | Trees
On arrival crew isolated supply and commenced repairs | 50 STAYWOOD ROAD, BUSHFIELD VIC 3281 | 32195606 | Vehicle | [5 empty] | 1 | VIC fire reported â€œpower lines down at the same location as car hit pole. car is on fire, PAL assets badly damaged.â€ On arrival the crew found a motor vehicle had contacted and shattered a wooden HV Substation pole. EDO fusing operated. No evidence of fire was found, however a small amount of oil spillage was identified during repairs. | Pole (wood);Pole mounted | 2 | 2 | 2 |  | WBL005 | Vehicle struck pole | Loss of supply;Less than $50k damage | 42558.8667 |  |  | 2575 | Roadway |  | 20160711PWA_03 | Infrastructure (network-based) | -38.3168 | 142.5332 | 1 | Powercor | Report | 3348 | 0.023391 | 22kV AC | Warrnambool Airport Ndb | 3281 | Bushfield | Vehicle
On arrival crew secured site and arranged fence repairs | 20A STENSON ROAD, KEALBA VIC 3021 | 30254139 | Vandalism | [5 empty] | 2 | Police reported fences damage and yard gate open at the incident location ( St Albans Zone Substation). On arrival, the crew found a break in had occurred and the boundary fences had been cut and the gate left open. Police are investigating. There was no ground fire start. No protection operated. There were no reported injuries. | Zone substation | 2 | 2 | 2 |  | KTS-SA NO1 | Vandalism to enable access to adjacent properties | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42589.5118 |  |  | 2576 | Industrial |  | 20160711PWA_04 | Infrastructure (network-based) | -37.74 | 144.8251 | 1 | Powercor | Report | 12085 | 0.037295 | Not applicable | Melbourne Airport | 3021 | Kealba | Other
Crew attended and replaced missing and damaged cables | 530-544 TROUPS ROAD S, MOUNT COTTRELL VIC 3024 | 33071976 | Vandalism;Theft | [5 empty] | 2 | Employee reports copper earth missing from pole, damage to underground cable and pole leaning at the incident location. . No shocks, injuries or third party damage. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Loss of supply;Less than $50k damage | 42589.4194 |  |  | 2577 | Roadway |  | 20160711PWA_05 | Infrastructure (network-based) | -37.7731 | 144.6632 | 1 | Powercor | Report | 3350 | 0.018706 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
Jemena crew isolated supply to the HV OH conductor and re-terminated and re-sagged the conductor. | UNIT 1 18 SELBOURNE STREET, COBURG VIC 3058 |  |  |  |  | Corrosion |  |  | 1 | Control room was contacted regarding a High Voltage conductor on the ground. Investigation upon arrival by the fault crew discovered a failure of the corroded wrap-on which caused the High Voltage Overhead conductor to fall to the ground. | Conductor (bare);Copper | 0 | 0 | 0 |  | CS5 | The copper conductor had been in service since 1979 and in the absence of any evidence or obvious reason for failure it is presumed that the incident was the result of possible corrosion or deterioration at the wrap-on ties. High Voltage Overhead conductor was possibly due to corrosion or deterioration of the wrap-on ties exacerbated by gusts of wind on the day. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42590.0938 |  |  | 2726 | Residential |  | 20160808JEM_02 | Infrastructure (network-based) | -37.7519 | 144.9521 | 1 | Jemena | Report | 3547 | 0.002169 | 22kV AC | Essendon Airport | 3058 | Coburg | Conductor
An aerial inspection with an EPV was completed on the 66kv, 22kv, intermediate concrete pole and all is ok. No damage. | 2 KENDALL CLOSE, HAMLYN HEIGHTS VIC 3215 | 33045305 | Vehicle | [5 empty] | 1 | Attending linesmen Russell Hawking advised a car has hit pole at incident location. There was a report of one fatality, condition of passenger unknown. There was no fire. | Pole (concrete) | 2 | 2 | 2 |  | GLGCY | Car into pole | Not involving electrocution | 42498.0722 |  |  | 2728 | Roadway |  | 20160808PWA_01 | Infrastructure (network-based) | -38.13 | 144.3416 | 1 | Powercor | Report | 3556 | 0.036793 | 22kV AC;66kV AC | Avalon Airport | 3215 | Hamlyn Heights | Vehicle
Reported breach, awaiting further advise | 135 COPPIN STREET, RICHMOND VIC 3121 | 30191761 | Building too close or within the No Go Zone | [5 empty] | 2 | CitiPower received report that scaffold had been erected in close proximity of distribution service line. Attending CitiPower persons identified that a new building had been constructed contrary to the advice given by CitiPower and the permit to work conditions imposed. It is understood that the scaffolding has subsequently been removed without a permit to work and the service line has been propped up with a temporary wooden support. | Service conductor | 2 | 2 | 2 |  | NR022 | interference to asset | No Go Zone (no contact) | 25/07/2016 0:00 |  |  | 2731 | Residential |  | 20160808PWA_03 | Infrastructure (network-based) | -37.823 | 145.0033 | 1 | CitiPower | Report | 3586 | 0.0079606 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Isolated in pit and made safe. Street light was replaced. | 95 COURTENAY AVENUE, CRANBOURNE NORTH VIC 3977 | 523879 |  |  |  | Age |  |  | 2 | IMS 223502. Street light lantern caught fire and burnt out Lis 523879 | Public lighting | 0 | 0 | 0 |  | cre23 | Faulty street light. | Pole-top fire | 42559.4583 | 1 | Negligible: no ground fire | 2730 | Residential |  | 20160808SPN_02 | Infrastructure (network-based) | -38.0787 | 145.2839 | 1 | AusNet Services Distribution | Report | 11228 | 0.022822 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne North | AF Other
Crew repaired the broken neutral at the pole. | UNIT 4 27 STEPHEN STREET, YARRAVILLE VIC 3013 |  |  |  | Highly unlikely | Corrosion;Neutral fault |  | Phase to neutral | 2 | Jemena customer at the residence of the unit was doing the dishes in the kitchen sink on the night of the 8th of August when she received a strong sensation in her right arm when she made simultaneous contact with her hands between the kitchen sink and the kitchen tap. The customer was not available for interview on the 9th of August. Her partner after learning of incident contacted their REC for investigation who discovered a voltage on the water piping system. | Neutral screen | 0 | 0 | 0 |  |  | Tests using an independent earth to various points of the electrical installation, including the distribution assets, and point of contact revealed a severely corroded neutral conductor at the service pole. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 28 Volts on the water piping system under load. | Minor shock | 42590.5417 |  |  | 2736 | Residential |  | 20160809JEM_01 | Infrastructure (network-based) | -37.8113 | 144.8955 | 1 | Jemena | Report | 3775 | 0.019076 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | OH Cable
Crew attended and repaired conductor | 420 ARDMONA ROAD, ARDMONA VIC 3629 | 33088545 |  | Bird |  |  |  |  | 2 | A customer reported that a wire is hanging low in a tree and there is a small fire at the incident location. On arrival the fault crew found that a 22kV overhead conductor had parted and the conductor was hanging low, contacting some orchard trees. The conductor remained supported by a live line flex The conductor appears to have ruptured as a result of a flashover involving two black ducks (both deceased) | Conductor (bare) | 0 | 0 | 0 |  | MNA014 | Bird Incident | Loss of supply;Other vegetation | 15/08/2016 10:12 | 1 | Small: 10 - 1000 sq.m | 2751 | Agricultural |  | 20160815PWA_03 | Infrastructure (network-based) | -36.366 | 145.2957 | 1 | Powercor | Report | 12064 | 0.016596 | 22kV AC | Shepparton Airport | 3629 | Ardmona | Animal
Area made safe and service joint repaired. | 5 MCIVOR WAY, ATTWOOD VIC 3049 |  |  |  | Highly unlikely | Moisture ingress;Corrosion |  |  | 2 | Customer received a slight electric shock when he made simultaneous contact with his hand on the rear external water tap and the continuous paved surface he was standing on. He was attempting to wash his hands at the time, this was occurring on a regular basis but he is unaware of the cause and took no further action until he saw a service crew working on the pit outside his house and reported it to them. | Services cable | 0 | 0 | 0 |  |  | An NST test using an independent earth performed by the service crew identified a high impedance in the neutral conductor. This condition caused current to flow through the installation MEN connection main earthing conductor, water pipe earth bond conductor and the metallic water pipes via the main earthing conductor and returned to to the sub station via (1) the earth electrode then the general mass of earth or (2) the conductive water pipe bond earth conductor and then the general mass of earth. A severely corroded service tee joint was identified as the cause of the high impedance associated with the return path of the neutral current. The corrosion of the service tee was a result of water entering the insulation or sheath causing the service tee to fail. | Minor shock | 16/08/2016 9:06 |  |  | 2758 | Residential |  | 20160817JEM_03 | Infrastructure (network-based) | -37.6741 | 144.8916 | 1 | Jemena | Report | 3719 | 0.026852 | Low voltage AC (<1kV) | Essendon Airport | 3049 | Attwood | Connection
On arrival crew isolated supply and commenced repairs | MERRYVALE, 568 DOOKIE ROAD, YABBA SOUTH VIC 3646 | 31027909 | Manned aircraft | [5 empty] | 1 | A customer reported that an helicopter had struck and broke a line at the incident location. On arrival the crew found that a helicopter had struck and broke a SWER conductor. Protection operated. There were no reported injuries, shocks, ground fire start or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | STN024 | Helicopter struck conductors | Loss of supply | 17/08/2016 13:37 |  |  | 2759 | Agricultural |  | 20160818PWA_01 | Infrastructure (network-based) | -36.2768 | 145.6902 | 1 | Powercor | Report | 3618 | 0.016816 | 12.7kV AC (SWER) | Shepparton Airport | 3646 | Yabba South | Vehicle
On arrival crew isolated supply and commenced repairs, replacing FSD. | 1180-1196 GISBORNE-MELTON ROAD, TOOLERN VALE VIC 3337 | 33077208 |  |  |  | Corrosion |  |  | 2 | Customer reported fire at substation pole at the incident location. On arrival the crew found that a low voltage FSD had been heat damaged and required replacement. There were no reported injuries. There was no ground fire. | Connection box | 2 | 2 | 2 |  | MLN012 | overheated connection | Pole-top fire | 42377.9688 | 1 | Negligible: no ground fire | 2762 | Roadway |  | 20160818PWA_04 | Infrastructure (network-based) | -37.6092 | 144.5894 | 1 | Powercor | Report | 3678 | 0.035071 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Connection
On arrival crew commenced repairs | 33 ALTAMOUNT DRIVE, TRUGANINA VIC 3029 | 30336797 | Copper theft | [5 empty] | 2 | Powercor employee reported that he had discovered LV service cables cut within an LV pit. He advised that he believed that the exposed cut ends of the cables could be alive. Powercor crew found that a live service cable end in the pit. A piece of cable had been cut away. There were no reported injuries or ground fire start. | Services cable | 2 | 2 | 2 |  | LV003 | cable theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/07/2016 11:38 |  |  | 2764 | Roadway |  | 20160818PWA_06 | Infrastructure (network-based) | -37.8378 | 144.7123 | 1 | Powercor | Report | 3623 | 0.0015312 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Powercor crew attended and repaired earths. | 471A MOUNT COTTRELL ROAD, ROCKBANK VIC 3335 | 30276224 | Copper theft | [5 empty] | 2 | Powercor employee, advised of copper theft on substation pole at corner of Keilor-Melton Rd and Mt Cottrell Rd., Rockbank. The HV & LV substation earths have had above-ground sections cut out and stolen from site. There were no reported injuries or ground fire start. | Earth/earthing | 2 | 2 | 2 |  | MLN012 | cable theft | Damage to network assets | 42408.6222 |  |  | 2765 | Roadway |  | 20160818PWA_07 | Infrastructure (network-based) | -37.6828 | 144.6263 | 1 | Powercor | Report | 3624 | 0.010642 | Earthing cable | Melbourne Airport | 3335 | Rockbank | Other
On arrival crew isolated supply, patrolled line and commenced repairs. Cross-arm replaced. | SUNNYSIDE, 60 BULLOCKY MARY ROAD, BLACK RANGE VIC 3381 | 32115005 |  |  |  | Rot |  |  | 1 | Customer reported power went off and approx 30 min later noticed that the power line on their property is on the ground and sparking. The attending crew found a HV cross arm had broken, 2 HV conductors were on the ground and 2 HV fuses had operated. There were no injuries, third party damage or fires reported | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | STL007 | Broken Crossarm | Loss of supply;Damage to network assets | 42408.7014 |  |  | 2774 | Agricultural |  | 20160819PWA_04 | Infrastructure (network-based) | -37.0976 | 142.744 | 1 | Powercor | Report | 3753 | 0.035918 | 22kV AC | Horsham Aerodrome | 3381 | Black Range | Crossarm
On arrival crew isolated supply and commenced repairs. | 43 WESTBURY TERRACE, HIGHTON VIC 3216 | 34003313 |  |  |  | Mechanical breakdown |  |  | 2 | A customer reported that she was walking her dog on the wet footpath, when the dog let out a yelp as it passed over a small round pit lid. She identified the pit as an electrical pit, and thought there was a possibility that the dog had received an electric shock. She reported this to the Geelong Council, who in turn reported it to Powercor. A Powercor crew attended and confirmed that the heat shrink on the LV joint had deteriorated, exposing the live conductor, which was in contact with the pit lid. This is an old underground area and this method of joining and insulating the cables is no longer used. | Cable;Services pit | 2 | 2 | 2 |  | GL021 | LV joint deteriorated | Minor shock | 42408.5104 |  |  | 2776 | Roadway |  | 20160819PWA_05 | Infrastructure (network-based) | -38.1601 | 144.3138 | 1 | Powercor | Report | 3636 | 0.014799 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
Supply was isolated so repairs could take place. | UNIT 3 803 HUMFFRAY STREET S, MOUNT PLEASANT VIC 3350 | 30015115 | Vandalism | [5 empty] | 2 | While attending a fault a Powercor employee reported vandalism to a customers meter box and the Powercor meter. Vandals had placed paper / cardboard into the meter box and set it alight. This damaged the meter panel and the meter. | Meter board (including fuses) | 2 | 2 | 2 |  | BAS023 | Vandalism | Meter board | 42408.4139 | 0 | Negligible: no ground fire | 2778 | Residential |  | 20160819PWA_06 | Infrastructure (network-based) | -37.5747 | 143.8533 | 1 | Powercor | Report | 3638 | 0.024558 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Mount Pleasant | Other
On arrival crew isolated supply and carried out repairs | 127 CHANNEL ROAD, MERBEIN VIC 3505 | 30099608 | Unknown external/community factor | [5 empty] | 0 | A employee reported a service wire on the ground at the incident location. On arrival the crew found that a service cable had broken and came to the ground alive resulting in burnt a patch of ground approx. 0.5msq. No protection operated. There were no reported injuries, shocks or third party property damages. | Service conductor;Aluminium twisted (grey) | 2 | 2 | 2 |  | MBN021 | No cause found | Grassfire | 19/08/2016 9:53 | 1 | Localised: less than 10 sq.m | 2779 | Agricultural |  | 20160819PWA_07 | Infrastructure (network-based) | -34.1718 | 142.0672 | 1 | Powercor | Report | 3892 | 0.040169 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Merbein | OH Cable
A faults crew attended and isolated supply to units 1, 2 and 3 at 316 Beach Road, Black Rock. The faults crew replaced the damaged three phase FMJB and re-terminated the underground cables before supply was restored. | 316 BEACH ROAD, BLACK ROCK VIC 3193 | 1811878 |  | Prone to salt deposition |  | Electrical breakdown;Overheated connection |  |  | 2 | Caller reports of a pole fire and the MFB are on site reporting that a fuse has burnt out. A three phase FMJB at pole No. LIS 1811878 located outside 317 Beach Road, Black Rock caught on fire and was extinguished prior to the faults crew attending. The FMJB supplied three units via an underground cable to large beachfront occupancies on Beach Road. The cause was a probable loose connection and deteriorated connections due to salt air pollutants. | Cable;Any other type;Connector/termination;Connection box | 0 | 0 | 0 |  |  | The cause was a probable loose connection and deteriorated connections due to salt air pollutants. | Pole-top fire | 42682.6007 | 1 | Negligible: no ground fire | 2773 | Roadway |  | 20160819UTD_04 | Infrastructure (network-based) | -37.9775 | 145.017 | 1 | United Energy Distribution | Report | 3633 | 0.0099456 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Black Rock | Connection
At "Warwick Carpark-Lightwood" Indoor substation in Springvale the door padlock had been cut off. There was no damage to the indoor substation however all of the spare fuses were found smashed on the floor. There was no attempt of copper theft and its suspected young adolescents were involved. | WARWICK AVENUE, SPRINGVALE VIC 3171 |  | Vandalism;Unauthorised access | [5 empty] | 2 | The padlock at "Warwick Carpark-Lightwood" Indoor substation was cut off by unknown persons and the substation entered. The doors to the substation were left wide open. At "Warwick Carpark-Lightwood" Indoor substation in Springvale the door padlock had been cut off. There was no damage to the indoor substation however all of the spare fuses were found smashed on the floor. There was no attempt of copper theft and its suspected young adolescents were involved. | Indoor | 0 | 0 | 0 |  |  | The padlock at "Warwick Carpark-Lightwood" Indoor substation was cut off by unknown persons and the substation entered by vandals. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42621.3958 |  |  | 2775 | Public space |  | 20160819UTD_05 | Infrastructure (network-based) | -37.9501 | 145.1513 | 1 | United Energy Distribution | Report | 3635 | 0.0061042 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Other
Techsafe EIO attended and identified broken neutral in the service. Jemena service crew replaced the over head service line. The service crew conducted an NST test at the customer's meter panel which recorded a pass result. LEI conducted voltage tests using an independent earth to the customers water pipes and metallic surfaces and recorded zero volts. As a final test, the LEI conducted an NST test at the customer's switchboard which recorded a pass result. Supply to the property was left ON. | 15 MURRAY STREET, FAWKNER VIC 3060 |  |  |  |  | Corrosion |  |  | 2 | A Yarra valley water employee was attempting to replace the main stop tap when the he experienced a slight tingling sensation when his hand made contact with the water tap while in kneeling on the damp ground. | Neutral screen | 0 | 0 | 0 |  |  | Voltage tests using an independent earth to various parts of the installation including the distribution assets revealed a severely corroded neutral on the supply service line at pole end. This condition caused current to flow through the installation MEN connection main earthing conductor and water pipe bond and the metallic water pipe system. This increased impedance to the flow of the return current resulted in a voltage rise of 28 volts on the metallic water pipes. | Minor shock | 23/08/2016 15:20 |  |  | 2795 | Residential |  | 20160823JEM_01 | Infrastructure (network-based) | -37.7057 | 144.9656 | 1 | Jemena | Report | 3666 | 0.032438 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | OH Cable
A LEI and faults truck attended and completed installation tests that revealed the public lighting pole and veranda roof were alive at 24volts. NST's were completed at 3 shops and the last shop failed a NST. The investigation by the faults crew identified a faulty aluminium to copper simpi-crimp on the neutral conductor at the POA above the veranda was corroded / burnt out. The connection was re-terminated and the LEI measured 1.3volts at the street light pole and 0 volts on the water main following the rectification work. | 147 ACLAND STREET, ST KILDA VIC 3182 |  |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | The shop trader (Rick 0408 685 050) from First Cut Clothing reported the water workers that were in attendance at the front of his shop advised that an electric shock was received from the water main. Water company workers were completing water main activities out side 147 Acland Street and mentioned to the shop trader that an electric shock was received from the water main. | Conductor (insulated);Connector/termination | 0 | 0 | 0 |  |  | The faults crew identified a faulty aluminium to copper simpi-crimp on the neutral conductor at the POA above the veranda was corroded / burnt out. | Minor shock | 23/08/2016 13:00 |  |  | 2799 | Commercial |  | 20160824UTD_02 | Infrastructure (customer connection) | -37.8691 | 144.9799 | 1 | United Energy Distribution | Report | 3673 | 0.015581 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Connection
26/07/2016 - A site meeting took place with ZNX, Andrew Rippon & another Work Safe employee (unknown) along with Vince Pulitano of Pulitano Construction and Kidd Yu of Kwikserv Formwork & Scaffolding. The site meeting discussion agreed the scaffolding needed to be removed as soon as possible. The United Energy Network Control Centre was contacted to make preliminary arrangements for an emergency shutdown is required to make the site safe. Emergency high voltage switching took place at 1.00PM and a PTW issued after the High & Low Voltage assets were isolated end earthed. | VERMONT AGED CARE, 770 CANTERBURY ROAD, VERMONT VIC 3133 |  | Working too close to overhead lines | [5 empty] | 2 | 21/07/2016 - An email request for a No Go Zone assessment was sent to United Energy. 22/07/2016 - The No Go Zone assessment was issued to Gary Harding from ZNX to investigate. Gary contacted Vince Pulitano of Pulitano Construction and made an appointment to meet on-site at 8.30AM on the following Monday. 25/07/2016 - On attending the site, Gary discovered that scaffold had been installed approximately 600mm away from the 22KV High Voltage transformer on the pole type substation. Gary informed the site supervisor this was a serious breach of the No Go Zone and that all personal should be instructed to stay away from the scaffold and that access ladders should be removed. Gary proceeded to contact Work Safe and his supervisor (Peter McKinnon) who attended the site at approximately 9:30AM. A short time afterwards, Mark Drewry from Work Safe was advised and later this day, advised ZNX the site had been made safe and a Work Safe inspector would attend the following day at 8.30AM. No shocks, injuries or damage to plant was sustained. | Pole mounted | 0 | 0 | 0 |  |  | Scaffolding installed that breached the No Go Zone Framework. | No Go Zone (no contact) | 26/07/2016 9:00 |  |  | 2800 | Construction |  | 20160824UTD_03 | Infrastructure (network-based) | -37.8336 | 145.2094 | 1 | United Energy Distribution | Report | 3680 | 0.018223 | 22kV AC | Moorabbin Airport | 3133 | Vermont | Other
MFB attended premises 24/8/16 following report of fire, Vicpol also attended and request for AusNet Services to attend and isolate supply was made to CEOT (approx. 3.09pm) Service truck attended approx. 4pm and service removed Fire damage to residential premises restricted to area adjacent to POA Inspection within premises revealed Hydroponic setup. David Weston attended approx. 4.30pm, duty officer Carlo Cellante was in attendance and Chris Masson was en route Vicpol sought to obtain warrant and access to the premises was not permitted until 25/08/16. Vicpol placed guard on premises overnight. All AusNet Services personnel left the site as VicPol were preserving the scene until a warrant was obtained. Significant unmetered load, approx. 70 amps, was being used during each 24 hours a day â€“ consisting of 49 x 600 watt lamps and ballasts on 2 x 12 hour cycles for the hydroponic setup. This usage may be contributing cause for damage at POA. | 2 RANDWICK COURT, EPPING VIC 3076 | 2 Randwick Court | Unauthorised work;Unauthorised access |  |  | Fault on customer installation |  |  | 2 | IMS 223896. MFB report fire near service POA. | Service conductor | 0 | 0 | 0 |  | epg12 | David Weston attended with Vicpol on 25/08/16 at approx 8.45am and confirmed 4 hydroponic rooms setup within the premises. Inspection within roof cavity revealed irregular wiring connection to unmetered mains cable above meter position. Irregular wiring removed and given to Vicpol A defect notice was issued and the meter was removed from the premises. The new connection process will apply before any reconnection can occur at this site. | Property | 21/08/2016 15:09 | 2 | Small: 10 - 1000 sq.m | 2801 | Residential |  | 20160825SPN_01 | Infrastructure (network-based) | -37.6419 | 145.0336 | 1 | AusNet Services Distribution | Report | 11274 | 0.0070625 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | Other
Crew attended and replaced service | 251 HUMFFRAY STREET N, BALLARAT EAST VIC 3350 | 32000470 |  | Within clearances |  |  |  |  | 1 | A Customer called to report that her service wire had been pulled out from the house end whilst the customerâ€™s 'builder' was removing a tree, and the tree fell onto the wire. On arrival the crew found that a tree had been cut and had fallen onto the service cable to the customerâ€™s house. The service cable had broken at the pole end resulting in no damage to the customerâ€™s installation. There was no fire, or injuries. | Service conductor | 0 | 0 | 0 |  | BAN015 | Interference | Loss of supply;Damage to network assets | 18/08/2016 13:01 |  |  | 2818 | Residential |  | 20160826PWA_04 | Infrastructure (network-based) | -37.5552 | 143.8797 | 1 | Powercor | Report | 3700 | 0.019757 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat East | Trees
A Downer faults crew attended and disconnected supply to the lantern at the base of the pole and a further trouble order was created to replace the defective 250w HPS lantern. | DAVEY STREET, FRANKSTON VIC 3199 | 8819378 |  | Precipitation |  | Moisture ingress;Electrical breakdown |  |  | 2 | The CFA advised of a street light fire outside the Deck Hotel on the corner of Davey Street and Nepean Highway. A 250w HPS lantern on pole No. 8819378 located on the corner of Davey Street and Nepean Highway in the centre median strip caught fire and was extinguished by the CFA. The cause was attributed to the cover missing with moisture and salt contaminants affecting the lantern that caused corrosion and the lantern to catch on fire. The pole is located in close proximity to Port Phillip Bay. | Public lighting | 0 | 0 | 0 |  |  | The cause was attributed to the cover missing with moisture and salt contaminants affecting the lantern that caused corrosion and the lantern to catch on fire. | Pole-top fire | 25/08/2016 22:20 | 1 | Negligible: no ground fire | 2816 | Roadway |  | 20160826UTD_02 | Infrastructure (network-based) | -38.1452 | 145.1199 | 1 | United Energy Distribution | Report | 3698 | 0.035829 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | AF Other
26/08/2016 - The crew that attended for the initial disconnection for non-payment stopped in Eaton Street to get some lunch and noticed that No. 5 Eaton Street is open, trading and the lights are on. Wayne Kelly (United Energy) contacted REC David (subcontractor for Conway Electrics) who stated that his job was to fix the defect at number 7 and get them back of supply which occurred last night. â€œMate, I know nothing about number 5â€ was his response when I mentioned that ESV were to be advised â€œbut I will give them a call to find out what is going onâ€. I believe â€œthem a callâ€ is Conway Electrics. The United Energy AMI Network Operations ran a consumption report for meter number No. 1231323 (7 Eaton Street) that demonstrated the premise is being used to supply 5 Eaton Street after it was disconnected for non payment. Usage seems quite high and there are concerns about the ramifications of overloading. | 5 EATON MALL, OAKLEIGH VIC 3166 |  |  |  |  | Overheated connection |  |  | 2 | 24/08/2016 - Premise was disconnected for non payment following a request from Momentum Energy. The ZNX crew isolated supply at the under veranda fuse break but when the crew went past the cafÃ© (No. 5) a short time later, they noticed the lights were on and the shop was trading and advised their supervisor. Supply was isolated once again and the fuse carriers were dropped off at the United Energy office pending a re-connection request. A REC was seen at the cafÃ© who appeared to be connecting wiring to the adjacent shop (No. 7). 25/08/2016 at 1542hrs - Per MFB, fire at fuse connection at 11 Eaton Street Mall. A faults crew attended and isolated supply that affected 3 shops including a vacant shop the owner of the cafÃ© stores his expensive classic cars in (No. 7). A defect was issued and numbers 5, 7 and 11 Eaton Street were left off supply as there was potential of another fire start. When questioned of how supply was restored earlier, the cafÃ© trader stated "the power simply come back on a short time after it was turned off earlier". Later this evening, REC No. 11506 (Conway Electrics 0422 402 775) provided Prescribed CES No. 404130549 (LEI Danny Morgan) after the consumers FMJB and the consumers mains were repaired. A faults crew attended and reconnected supply following the completion of repairs to the underground cable by an underground crew. Supply to numbers 7 and 11 Eaton Street was restored and number 5 remained off supply for an outstanding non-payment debt. | Customer installation | 0 | 0 | 0 |  |  | The shop trader continues to restore supply to the cafe in various unsafe manners. | Loss of supply | 25/08/2016 15:42 |  |  | 2819 | Commercial |  | 20160826UTD_03 | Infrastructure (network-based) | -37.8989 | 145.0897 | 1 | United Energy Distribution | Report | 3701 | 0.036104 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh | Other
On arrival crew isolated supply and commenced repairs | 22 ANDREW STREET, SUNSHINE VIC 3020 | 30260581 | Vandalism;Copper theft | [5 empty] | 1 | A customer reported a power outage at the incident location. The crew believe an unknown object was thrown on to the HV leads of the substation. The HV/LV earthing had been cut away and removed from site. There were no reported injuries or fire | Equipment;Earth/earthing | 2 | 2 | 2 |  | SSE032 | Vandalism and cable theft | Loss of supply | 19/08/2016 12:06 |  |  | 2823 | Roadway |  | 20160829PWA_01 | Infrastructure (network-based) | -37.7805 | 144.8416 | 1 | Powercor | Report | 3722 | 0.036979 | 22kV AC;Earthing cable | Essendon Airport | 3020 | Sunshine | Other
On arrival crew isolated supply and commenced repairs | 15 GRACIE STREET, NORTHCOTE VIC 3070 | 30183969 |  |  |  | Overheated connection |  |  | 2 | A few Residents reported sparks falling onto the ground at the above incident location. On arrival, the crew found that the Low Voltage red phase isolator had burnt connections on a transformer pole. There was no ground fire nor third party damaged. There were no reported injuries. | Disconnector/isolator | 2 | 2 | 2 |  | NC009 | corrosion | Loss of supply | 20/08/2016 20:30 |  |  | 2838 | Roadway |  | 20160831PWA_03 | Infrastructure (network-based) | -37.7677 | 144.99 | 1 | CitiPower | Report | 3741 | 0.02133 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
On arrival crew isolated supply and commenced repairs | 520 DIGGERS ROAD, WERRIBEE SOUTH VIC 3030 | 30110409 | Vehicle |  |  | Leakage |  |  | 2 | Customer reported a fire on a pole outside his house. He indicated that the fire was extinguished, but sparking was still occurring at the time of his call. A Powercor crew attended and discovered that a vehicle had collided into pole LIS 203209 in Diggers Rd. The collision impact had caused an outer phase HV conductor to break free from the HV insulator and fall below the HV crossarm making contact with a wet pole surface. The conductor to pole contact duration was sufficient enough to cause charring/burning of the pole section to require replacing the pole. There was no ground fire. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | WBE034 | Vehicle striking pole and dislodging hv conductor | Pole-top fire;Loss of supply | 21/08/2016 18:12 | 1 | Negligible: no ground fire | 2846 | Roadway |  | 20160901PWA_04 | Infrastructure (network-based) | -37.9568 | 144.6868 | 1 | Powercor | Report | 8389 | 0.029446 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Vehicle
A LEI and faults truck attended and measured 204v on the neutral and 170v at the earth to an independent earth. A NST was completed at the three boat sheds that failed. The faults crew commenced to check all connections and identified a corroded neutral connection of boat shed No. 87 at pole number LIS 9588786 was the cause that also supplied sheds No's 82, 85 and 87. The cause was salt corrosion as the pole is located in close proximity to the beach. The connections were cleaned, greased and re-terminated and the LEI tested the three installations that confirmed the fault had been rectified with zero volts measured on the installations neutral and earthing systems. | 3 ROSSERDALE CRESCENT, MOUNT ELIZA VIC 3930 | 9588786 |  | Prone to salt deposition |  | Corrosion |  | Phase to earth | 2 | REC (Ben Beel) is on site and reported that he received an electric shock from the frame of the meter panel. REC suggests there is a problem with the neutral at the pole end as the POA is fine. The REC has isolated supply. A REC was in attendance and received a slight electric shock to the back of his hand from the metal meter enclosure at boat shed No. 85. The REC investigated the cause and advised the United Energy faults and emergencies call centre that the fault is possible located at the pole end. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | The cause was salt corrosion as the pole is located in close proximity to the beach. | Minor shock | 25/08/2016 8:00 |  |  | 2854 | Public space |  | 20160902UTD_02 | Infrastructure (customer connection) | -38.1776 | 145.0801 | 1 | United Energy Distribution | Report | 3761 | 0.014976 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Connection
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service cable and completed an NST test which confirmed a Pass result. | 75 NEWTON AVENUE, BELL POST HILL VIC 3215 | 32077585 |  |  |  | Corrosion |  | Phase to earth | 2 | Programmed Maintenance Services were engaged by Barwon Water to repair a leaking Water Meter at the property, wherein Employee Field Worker Mr Chris Martin attended to execute the repairs. On arrival Mr Martin observed a leak at the output coupling of the Water Meter and attempted to tighten the coupling using a spanner in his right hand, when he made simultaneous contact with the ground with his left hand. Mr Martin experienced a sensation in his right arm which he believes was a slight electric shock. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor of O/H Aluminium Neutral Screened Service Cable at the Reticulation Pole which was identified as the cause of the high impedance within the neutral service conductor. The corrosion of the O/H Neutral Screened Service Cable was the result of water entering the outer sheath via a small perforation, the cause of which was unable to be determined. | Service conductor | 2 | 2 | 2 |  | CRO022 | Corrosion of the O/H Neutral Screened Service Cable was the result of water entering the outer sheath via a small perforation, the cause of which was unable to be determined. | Minor shock | 42437.5833 |  |  | 2866 | Residential |  | 20160906PWA_04 | Infrastructure (network-based) | -38.0945 | 144.3272 | 1 | Powercor | Report | 3773 | 0.040344 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | OH Cable
On arrival crew repaired the damaged cable insulation. | 59-63 MARK STREET, NORTH MELBOURNE VIC 3051 | 30182703 | Working too close to overhead lines | [5 empty] | 2 | Rod Fraser mobile: 0419145928 from Citywide Trees reports that one of his workers has nicked an insulated cable that goes from street light to street light at the incident location. On arrival the fault crew found that a public light supply between pole LIS 75442 and 756822 had been damaged by a chain saw being used to trim trees in its vicinity. There was no ground fire, no injuries or third party property damage. | Conductor (insulated) | 2 | 2 | 2 |  | LS009 | Vegetation: Trees Incident | No Go Zone (contact) | 42530.5417 |  |  | 2891 | Roadway |  | 20160913PWA_01 | Infrastructure (network-based) | -37.7938 | 144.9384 | 1 | CitiPower | Report | 3804 | 0.034231 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Other
On arrival crew isolated supply and replaced EDO fuse tube | 845 ENGLISH ROAD, LETHBRIDGE VIC 3332 | 30068949 |  |  |  | Fuse failed to eject |  |  | 2 | A customer reported a small flame on the middle of cross arm at the incident location. On arrival the crew found that an EDO fuse had operated. And they also found evidence of smouldering, however the barrel of the EDO fuse stayed in position without dropping down There was no ground fire, no injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | GL015 | corrosion | Pole-top fire | 42591.2639 | 1 | Negligible: no ground fire | 2892 | Roadway |  | 20160913PWA_02 | Infrastructure (network-based) | -37.9676 | 144.1308 | 1 | Powercor | Report | 3805 | 0.033282 | 22kV AC | Avalon Airport | 3332 | Lethbridge | Fuse
On arrival crew isolated supply and commenced repairs | 8 ROSE STREET, ECHUCA VIC 3564 | 33083600 |  |  |  | Corrosion |  |  | 2 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. | Connection box | 2 | 2 | 2 |  | ECA012 | Moisture ingress | Pole-top fire;Loss of supply | 42652.7958 | 1 | Negligible: no ground fire | 2903 | Roadway |  | 20160914PWA_02 | Infrastructure (network-based) | -36.1441 | 144.7335 | 1 | Powercor | Report | 3817 | 0.015539 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | Connection
On arrival crew commenced repairs | 15 CHILDE HAROLD ROAD, GISBORNE VIC 3437 | 30287590 | Working too close to underground cables | [5 empty] | 2 | A contractor advised one of the site excavators has hit earthing strap at incident location. On arrival, the fault crew found that the earthing cable of the Kiosk had been damaged. There was no fire , no injuries or third party property damaged. | Earth/earthing | 2 | 2 | 2 |  | GSB013 | Site excavations | Damage to network assets | 42622.5236 |  |  | 2905 | Roadway |  | 20160914PWA_03 | Infrastructure (network-based) | -37.5033 | 144.6046 | 1 | Powercor | Report | 3819 | 0.017981 | Earthing cable | Melbourne Airport | 3437 | Gisborne | Dug up
On arrival crew isolated supply and commenced repairs. Insulator has since been installed in stay | 408-434 QUEENSBERRY STREET, NORTH MELBOURNE VIC 3051 | 30181555 |  | Bird |  |  |  |  | 1 | A bird has flashed over between the 66kv insulator and the stay wire at pole 88 of the VMTS-VM1 66kv line. There are reports of HVI to some equipment near the incident location. There was no ground fire or injuries. | Conductor (bare) | 2 | 2 | 2 |  | WMTS-VVM1 | Bird Incident | HV injection | 19/09/2016 8:41 |  |  | 2925 | Roadway |  | 20160920PWA_01 | Infrastructure (network-based) | -37.8032 | 144.9539 | 1 | CitiPower | Report | 3846 | 0.025641 | 66kV AC | Essendon Airport | 3051 | North Melbourne | Animal
On arrival crew isolated supply and commenced repairs. | UNIT 2 2 SMITH STREET, MELTON VIC 3337 | 30243070 | Working too close to underground cables | [5 empty] | 1 | Powercor fault crew attending a HV feeder outage found that a HV UG cable hit by a bore head at the incident location. DBYD had been obtained # 11162479 No evidence of fire, injuries or any other damage found. Protection operated. | Cable | 2 | 2 | 2 |  | MLN022 | Under road bore struck cable | Loss of supply;No Go Zone (contact) | 19/09/2016 11:51 |  |  | 2926 | Roadway |  | 20160920PWA_02 | Infrastructure (network-based) | -37.6848 | 144.5861 | 1 | Powercor | Report | 3847 | 0.0012639 | 22kV AC | Laverton Raaf | 3337 | Melton | Dug up
The faults crew replaced the LV fuse and repaired the damaged neutral conductor near pole No. LIS 3300882 where the excavator made contact with the LV conductors. | 25 KEIPHA ROAD, CRANBOURNE SOUTH VIC 3977 | 3300882 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  | Conductor clashing |  |  | 1 | Caller reports that a truck has contacted the wires near the corner of Pearcedale and Keipha Roads, Cranbourne South. During construction work, an excavator has contacted the low voltage overhead conductors near pole No. LIS 3300882. This caused an outage to 7 customers supplied from "Pearcedale-Keipha" substation after the 160amp red phase LV fuse operated. Mark Trimboli (0409 450 838) from ICS Industries was managing the site when the incident occurred. No electric shocks or damage to plant was sustained. | Conductor (bare) | 0 | 0 | 0 |  |  | Excavator contacted the LV overhead conductors. | No Go Zone (contact) | 19/09/2016 8:00 |  |  | 2924 | Agricultural |  | 20160920UTD_01 | Infrastructure (network-based) | -38.143 | 145.2429 | 1 | United Energy Distribution | Report | 3843 | 0.034949 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne South | Vehicle
Copper stolen running from pole to pit. Site was Isolated by fuse at the subsation, pit was refitted, damage to pit was repaired and supply was restored to customer premise. | 103 MOMMSENS ROAD, CLARKEFIELD VIC 3430 |  | Vandalism;Copper theft | [5 empty] | 2 | Customer reporting someone has cut cable inside pit, rope is tied around contents of the pit, and tried to pull contents out. vandals have broken the back of the meter and cut the wires at the back of the meter. Broken conduit on opposite side of road. | Services pit;Smart meter | 0 | 0 | 2 |  |  | Vandals have stolen copper from the pole to pit and also damaged customers mains. | Loss of supply;Damage to network assets | 19/09/2016 17:30 |  |  | 2930 | Residential |  | 20160921JEM_02 | Infrastructure (network-based) | -37.5135 | 144.8377 | 1 | Jemena | Report | 3852 | 0.038811 | Low voltage AC (<1kV) | Melbourne Airport | 3430 | Clarkefield | Other
On arrival crew arranged repair of damaged conduit | 43 MURRAY STREET, KERANG VIC 3579 | 32032481 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that the U/G boring machine had struck a conduit at the incident location. On arrival the crew found that a contractor was operating an U/G boring machine and contacted a 63mm conduit of a LV service cable causing damage to the conduit. There were no reported injuries, shocks or third party property damages. | Cable | 2 | 2 | 2 |  | KGT002 | interference | Damage to network assets | 19/09/2016 14:14 |  |  | 2940 | Roadway |  | 20160922PWA_03 | Infrastructure (network-based) | -35.7252 | 143.9148 | 1 | Powercor | Report | 3862 | 0.00085532 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3579 | Kerang | Dug up
A crew attended and replaced missing earth cables. | 112 WHITELAW AVENUE, DELACOMBE VIC 3356 | 32003898 | Copper theft | [5 empty] | 2 | A pole inspector reported copper earth cables missing off substation pole in Whitelaw Ave, Delacombe. 1 of 2 sites. | Earth/earthing | 2 | 2 | 2 |  | BAS021 | Theft | Damage to network assets | 20/09/2016 9:39 |  |  | 2941 | Roadway |  | 20160922PWA_04 | Infrastructure (network-based) | -37.5795 | 143.8176 | 1 | Powercor | Report | 12409 | 0.016133 | Earthing cable | Ballarat Aerodrome | 3356 | Delacombe | Other
A crew attended and replaced missing earth cables | 120 WHITELAW AVENUE, DELACOMBE VIC 3356 | 30004584 | Copper theft | [5 empty] | 2 | A pole inspector reported copper earth cables missing off substation pole in Whitelaw Ave, Delacombe. 2 of 2 incidents. | Earth/earthing | 2 | 2 | 2 |  | BAS021 | Theft | Damage to network assets | 20/09/2016 9:39 |  |  | 2942 | Roadway |  | 20160922PWA_05 | Infrastructure (network-based) | -37.5791 | 143.8141 | 1 | Powercor | Report | 12410 | 0.018256 | Earthing cable | Ballarat Aerodrome | 3356 | Delacombe | Other
CEOT dispatched a fault crew to isolate, investigate and make safe. Both sides of the pillar where confirmed de-energised via blown LV fuses. Fault crew isolated supply to the paralleling pillar, removed the Clipsal 200A LV switch from the pillar and capped both LV cables. The crew replaced 2 x 315A blown fuses in the krone box at pole 5203379 located in Ethel Street, 3x 250A blown fuses in the LV isolators at pole 5205310 located in Lawrence Street and restored supply to all customers. The switch failure is believed to have been caused by moisture ingress. | 2 ETHEL LANE, WODONGA VIC 3690 | 5808844 |  |  |  | Moisture ingress;Electrical breakdown |  | Phase to phase | 1 | IMS 224298. A report was received of a small grass fire outside of a LV pillar in Ethel Lane. An AusNet Services' fault crew attended and found an LV paralleling pillar outside number 2 Ethel Lane on the road reserve that had caught fire. The size of the fire was 1m x 1 m. A small area of grass was burnt surrounding the pillar due to the flames/arc coming out of the base of the pillar. | LV Pillar | 0 | 0 | 0 |  | WO32 | The switch failure is believed to have been caused by moisture ingress. | Grassfire;Plant/equipment | 15/09/2016 12:30 | 1 | Localised: less than 10 sq.m | 2946 | Roadway |  | 20160922SPN_02 | Infrastructure (network-based) | -36.1242 | 146.8917 | 1 | AusNet Services Distribution | Report | 11234 | 0.013119 | Low voltage AC (<1kV) | Wangaratta Aero | 3690 | Wodonga | Pole
CEOT dispatched a fault crew to investigate and make safe. DAO notified. Repairs carried out. | 20 PARK AVENUE, BEECHWORTH VIC 3747 | 4502656 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | IMS 224340. A bulldozer hit a stay wire on pole resulting in the pole & HV conductors hitting the ground causing ACR MY001 to trip (INCD-116918-r). No injuries sustained. No electric shock occurred. | Conductor (bare);Guy wire;Pole (wood) | 0 | 0 | 0 |  | myt7 | Bulldozer hit pole stay wire. | Loss of supply;No Go Zone (no contact) | 17/09/2016 13:00 |  |  | 2948 | Agricultural |  | 20160922SPN_04 | Infrastructure (network-based) | -36.369 | 146.6982 | 1 | AusNet Services Distribution | Report | 3874 | 0.021656 | 22kV AC | Wangaratta Aero | 3747 | Beechworth | Vehicle
on arrival crew carried out repairs | 7 GEORGE STREET, HAMILTON VIC 3300 | 33057949 | Vehicle | [5 empty] | 2 | Vicfire reported a service wire down and sparking at the incident location. On arrival the crew found that a 4 wire grey twisted service had been struck by an unknown vehicle, causing it to break and fall to the ground. The fused mains box on the premises was damaged and required an REC to replace. There was minor scorching of the green grass on the nature strip caused by the arcing service, but there was no fire or injuries. | Service conductor | 2 | 2 | 2 |  | HTN003 | vehicle impact | Loss of supply | 21/09/2016 13:38 |  |  | 2956 | Roadway |  | 20160923PWA_02 | Infrastructure (network-based) | -37.7487 | 142.0336 | 1 | Powercor | Report | 3882 | 0.022781 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Vehicle
On arrival crew commenced repairs | 847-1071 BLACK HILL ROAD, TOOLERN VALE VIC 3337 | 32173540 | Copper theft | [5 empty] | 2 | A Powercor Employee, discovered that the LV copper earth cable was cut away and stolen at incident location from Ground Level to a height of 3.0m above ground. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN012 | theft | Damage to network assets | 24/09/2016 10:08 |  |  | 2959 | Roadway |  | 20160926PWA_02 | Infrastructure (network-based) | -37.6126 | 144.6465 | 1 | Powercor | Report | 3885 | 0.032884 | Earthing cable | Melbourne Airport | 3337 | Toolern Vale | Other
The Greater City of Bendigo have been advised to cease all works until supply is isolated and alternative supply arrangement are made. | 77-79 RETREAT ROAD, SPRING GULLY VIC 3550 | 32052966 | Working too close to underground cables | [5 empty] | 2 | An Powercor employee reported council drainage works in Retreat Rd have exposed U/G mains, conduits and pit. The council did not consult Powercor at any stage. Supply was still on during these works. There were no reported injuries, shocks or third party property damages. | Cable;Services cable;Services pit | 2 | 2 | 2 |  | BET007 | Council drainage works around Underground cables | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/09/2016 9:32 |  |  | 2960 | Public space |  | 20160926PWA_03 | Infrastructure (network-based) | -36.7861 | 144.2883 | 1 | Powercor | Report | 3886 | 0.03769 | 22kV AC | Bendigo Airport | 3550 | Spring Gully | Other
CEOT dispatched a Fault Crew to isolate supply and make safe. CEOT requested the Duty Officer to investigate. Supply isolated at pole base. There was no pole fire, CFA attended. A request has been sent to maintenance to replace the street light head. | 1417 FERNTREE GULLY ROAD, SCORESBY VIC 3179 | 1309556 |  |  |  | Electrical breakdown |  |  | 2 | IMS 224480. VicRoads advised a street light head on fire 200 metres east of Stud Road in Ferntree Gully Road Scoresby. Lis number 1309623. No fire on pole or ground. | Public lighting | 0 | 0 | 0 |  | BRA21 | Uncertain of actual cause but previous incidents are related to the ignitors not being of the timed type and the capacitors casing constructed of plastic. To prevent similar incidents from reoccurring the revised street lantern specification has been changed to require timed ignitors and metal clad capacitors. | Other electricity related | 24/09/2016 21:16 | 1 | Negligible: no ground fire | 2961 | Roadway |  | 20160926SPN_01 | Infrastructure (network-based) | -37.8984 | 145.2353 | 1 | AusNet Services Distribution | Report | 11235 | 0.032517 | Low voltage AC (<1kV) | Moorabbin Airport | 3179 | Scoresby | AF Other
An Electrical inspector was dispatched from Melbourne and a fault crew from Wodonga. On arrival at site the AusNet Services fault crew conducted an NST test at the main switchboard (located at the shed) and it passed. They then completed an NST test at the sub board (located at the house approx. 30m from shed) and it failed. They turned the solar inverter off and re-conducted an NST test at the sub-board (located at the house) and it failed due to low volts. A voltage test on the active to an independent earth revealed 195v. The fuse was pulled at the meter board and in the FOLCB at the substation pole. On inspecting the single phase junction box on the pole the crew found 2 dead bats bridging active to neutral. The single phase junction box was replaced with a 3 phase junction box (no single phase junction box on the truck). Supply was restored conducting a check test, polarity test and a NST test which passed. A voltage test from active to an independent earth measured 230V and this value was also displayed on the meter. A Licensed Electrical Inspector travelling from Melbourne was turned around when problem was found and resolved. A local electrical inspector visited the site on the 5/9/16 to confirm the issues with the customer's installation had been resolved. A voltage test from MEN point to an independent earth measured 0.01 volt. The bats have entered the Junction Box through the gaps between the cables and the cable entry hole. This gap on the new 3 phase Junction box has been sealed up around the cable entry hole with Silastic to prevent future access by bats. | 356 SANATORIUM ROAD, ALLANS FLAT VIC 3691 | 5203892 |  | Bird |  |  |  | Phase to earth | 2 | IMS 223974. On Sunday morning 28/8 the customer noticed brown out conditions and said her freezer was running like a compressor so she turned the freezer off. On Sunday evening her son went for a shower and he said to her that he got a tingle off the taps. They turned the power off to the house by switching off the main switch on the sub-board at the house. The customer called an electrician on Monday morning 29/8 to come and inspect the house. REC (Andrew ph (0499)551422) attended the house. He checked an RCD was installed (Clipsal 30ma 63A CAT 4EL 63/2/30) was installed and had not tripped. Andrew measured 229v active to an independent earth and a small voltage (he did not record the value) on the neutral to independent earth, so reported the matter to AusNet Services. | Connection box | 0 | 0 | 0 |  | wots11 | Bird Incident | Minor shock | 29/08/2016 1:58 |  |  | 2972 | Residential |  | 20160928SPN_02 | Infrastructure (network-based) | -36.286 | 146.9068 | 1 | AusNet Services Distribution | Report | 3914 | 0.031973 | Low voltage AC (<1kV) | Wangaratta Aero | 3691 | Allans Flat | Animal
A LEI and faults truck attended and found another crew were on site completing planned work who had replaced a junction box at the pole end. The LEI tested the installation and confirmed the fault must have been rectified by the on site crew. A NST passed and supply was left on. | 17 GLENVUE ROAD, RYE VIC 3941 |  |  |  |  | Electrical breakdown |  | Phase to earth | 2 | REC advised the customer has been getting electric shocks from the shower taps and has turned the main switch off. The occupier had received electric shocks when touching the shower taps and contacted a REC to investigate the cause. The REC contacted the United Energy faults and emergencies call centre. | Connection box | 0 | 0 | 0 |  |  | Defective connection in a pole mounted junction box. | Minor shock | 26/09/2016 11:00 |  |  | 2980 | Residential |  | 20161003UTD_01 | Infrastructure (network-based) | -38.3892 | 144.8149 | 1 | United Energy Distribution | Report | 3923 | 0.030655 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Pole
A faults crew attended and disconnected supply to the lantern and a further trouble order was created to replace the defective 150w HPS lantern. | 216 STONY POINT ROAD, CRIB POINT VIC 3919 | 8826905 |  |  |  | Overheated connection |  |  | 2 | Light pole on fire as per emergency services. The CFA advised they were on the way to a street light fire outside 216 Stony Point Road after a 150w HPS lantern on pole No. 8826905 caught on fire. The minor fire was extinguished by the CFA and the cause was unknown but most likely an overheated connection. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but most likely an overheated connection. | Pole-top fire | 21/09/2016 5:30 | 1 | Negligible: no ground fire | 2993 | Roadway |  | 20161006UTD_01 | Infrastructure (network-based) | -38.3649 | 145.2039 | 1 | United Energy Distribution | Report | 3943 | 0.0057523 | Low voltage AC (<1kV) | Moorabbin Airport | 3919 | Crib Point | Connection
22/09/2016 - A faults crew attended and isolated supply at the base of the street light pole. 27/09/2016 - A public lighting crew removed the non-standard lantern and installed a standard lantern and re-wired the short pole. | 12 WOODHALL WYND, DONVALE VIC 3111 | 9279455 |  |  |  | Fatigue |  |  | 2 | Street light fire per the MFB at pole number 9279455. A non-standard lantern installed on a short steel pole outside 12 Woodhall Wynd, Donvale caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but the non-standard lantern appeared to be a old Doncaster City Council type and old age may have been a contributing factor. | Pole-top fire | 22/09/2016 19:30 | 1 | Negligible: no ground fire | 2994 | Roadway |  | 20161006UTD_02 | Infrastructure (network-based) | -37.7972 | 145.1826 | 1 | United Energy Distribution | Report | 3944 | 0.023953 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | AF Other
crew isolated and replaced lantern | 1 BARAK ROAD, PORT MELBOURNE VIC 3207 | 30204667 |  |  |  | Overheated connection |  |  | 2 | Nearby resident advise that a street light pole was on fire. On arrival the attending crew identified that a luminaire had melted. No property damage or injuries reported | Public lighting | 0 | 0 | 0 |  | PM005 | loose connection | Melting or smoking only | 42652.5757 |  |  | 2998 | Residential |  | 20161007PWA_01 | Infrastructure (network-based) | -37.8388 | 144.9231 | 1 | CitiPower | Report | 12084 | 0.014262 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | AF Other
crew attended, isolated line and tree cleared | 470 OLD YEO ROAD, YEO VIC 3249 | 30053541 |  | Wind;MEC |  |  |  | Phase to earth | 1 | Feeder circuit breaker operated to lock out. Attending crew patrolled line and found that a large eucalypt had snapped approximately 1 metre above ground and brought down 22kV conductor. Protection operated. There was no fire, injuries or third property damage. | Conductor (bare) | 0 | 0 | 0 |  | CLC007 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 42410.5028 |  |  | 2999 | Agricultural |  | 20161007PWA_02 | Infrastructure (network-based) | -38.3882 | 143.6345 | 1 | Powercor | Report | 3949 | 0.02437 | 22kV AC | Ballarat Aerodrome | 3249 | Yeo | Trees
crew attended, isolated line and removed tree | 400 SETTLEMENT ROAD, SWAN MARSH VIC 3249 | 32065076 |  | Wind |  |  |  |  | 1 | Customer advised wire hit by tree and down resting on shed. Attending crew found large Cyprus tree at rear of shed has uprooted into HV line bringing down one conductor. The tree came to rest on a shed roof with one conductor entangled . Protection operated. There was no fire, injuries or third property damage. | Conductor (bare) | 0 | 0 | 0 |  | CLC006 | Vegetation: Trees Incident | Loss of supply | 42410.4854 |  |  | 3000 | Agricultural |  | 20161007PWA_03 | Infrastructure (network-based) | -38.3525 | 143.3519 | 1 | Powercor | Report | 3950 | 0.0036331 | 22kV AC | Warrnambool Airport Ndb | 3249 | Swan Marsh | Trees
A faults crew attended and installed a LV spreader in the slack termination span at the end of the circuit near pole number LIS 2311940 supplied from "Cressy-Milton" substation. | 116 MILTON PARADE, GLEN IRIS VIC 3146 | 2311940 |  |  |  | Conductor clashing |  |  | 2 | Customer advises that low voltage lines are clashing between poles causing momentary sparking and arcing that caused the nature strip to catch on fire. Caller said emergency services have not been called as he put the fire out. During strong winds, the white and blue phase LV conductors were clashing that caused molten metal to fall into the nature strip shrubs below and a small fire started that was extinguished by a customer who resides at 116 Milton Parade, Glen Iris. | Conductor (bare);Aluminium | 0 | 0 | 0 |  |  | Conductors clashing during strong winds. | Other vegetation | 42410.6528 | 1 | Localised: less than 10 sq.m | 2995 | Roadway |  | 20161007UTD_01 | Infrastructure (network-based) | -37.8507 | 145.0433 | 1 | United Energy Distribution | Report | 3945 | 0.037454 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Conductor
A faults crew attended and placed the substation under LV parallel and proceeded to replace the damaged krone switch. Supply was restored upon completion. | UNIT 3 29 CRANBOURNE ROAD, FRANKSTON VIC 3199 | 8819096 |  | Cold |  | Electrical breakdown;Overheated connection |  |  | 2 | Caller reports pole is on fire and the CFA are on their way. A pole fire was reported at "Melvin-Leslie" pole type substation at pole No. LIS 8819096 outside 3/29 Cranbourne Road where a LV krone switch was found to be burnt out and heat damaged and requires replacement. The cause appeared to be a burnt out white phase connection and the CFA had attended and extinguished the fire. A loose connection was the probable attributing cause. | Disconnector/isolator | 0 | 0 | 0 |  |  | A loose connection was the probable cause. | Pole-top fire | 42410.9722 | 1 | Negligible: no ground fire | 2996 | Roadway |  | 20161007UTD_02 | Infrastructure (network-based) | -38.1463 | 145.1291 | 1 | United Energy Distribution | Report | 3946 | 0.027593 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
The supply was isolated, tree branch was removed, repairs to the conductors were completed and supply restored. | 5 DAWSON STREET, TULLAMARINE VIC 3043 |  |  | Blown branch/vegetation |  | HV injection |  |  | 2 | Due to the high winds a tree branch made contact with high voltage conductors (HV). The HV conductors made contact with the low voltage conductors which caused a high voltage Injection. REC inspected, tested and repaired damages to the impacted properties. | Conductor (bare) | 0 | 0 | 0 |  | AW - 09 | Vegetation: Trees Incident | HV injection | 42623.4889 |  |  | 3005 | Residential |  | 20161010JEM_03 | Infrastructure (network-based) | -37.7011 | 144.8792 | 1 | Jemena | Report | 5001 | 0.022737 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3043 | Tullamarine | Trees
Section of conductor was isolated and made safe. The low voltage conductors were replaced. | 2 SIMS STREET, BRAYBROOK VIC 3019 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Due to storm, tree branch broke and fell onto the low voltage conductor. Low voltage conductor was broken on footpath phase resulting in it falling to the ground. Crew attended and repaired the broken low voltage conductors. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42623.8826 |  |  | 3008 | Residential |  | 20161010JEM_04 | Infrastructure (network-based) | -37.7938 | 144.8536 | 1 | Jemena | Report | 5171 | 0.0050961 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Trees
CEOT dispatched a fault crew to isolate supply and make safe and a LEI to investigate. Traffic management on-site and road closed. Downer fault crew on-site completing repairs. Customer Advice forms were issued to customers with damaged installations or appliances. | 28 MCKILLOP ROAD, MOUNT EVELYN VIC 3796 |  |  | Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 224662. A tree located on the road reserve out the front of 1-3 Lily Ave, Mt Evelyn, fell over onto open bare 22kV â€“ 415V conductors causing a HVI. Feeder protection tripped, blown substation bus fuses and blown service fuses. Metering was also damaged. AusNet Services' attending LEI confirmed that a HVI had occurred from the incident. All of the metering on the circuit was required to be replaced. Customers affected were: 11 McKillop Rd, Mt Evelyn, and 28 McKillop Rd, Mt Evelyn for both the house and shed installations. | Conductor (bare) | 0 | 0 | 0 |  | ldl23 | Vegetation: Trees Incident | HV injection | 42561.575 |  |  | 3015 | Roadway |  | 20161010SPN_01 | Infrastructure (network-based) | -37.794 | 145.4011 | 1 | AusNet Services Distribution | Report | 3966 | 0.0006713 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3796 | Mount Evelyn | Trees
crew attended and removed service wire. REC to submit request for abolishment through retailler | 1543 PRAIRIE-ROCHESTER ROAD, LOCKINGTON VIC 3563 | 33080644 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | An REC reported that a wire had been hit with a tractor, service wire hanging and still attached to the pole. Crew attended and found that the owner had hit the wire with his tractor and brought down the service wire. Crew disconnected service wire. Customer no longer requires service so no reconnection of service wire carried out. Customer to arrange abolishment with his REC. | Service conductor | 0 | 0 | 0 |  | SHP012 | Traffic incident (tractor) | Damage to network assets | 29/09/2016 15:05 |  |  | 3030 | Roadway |  | 20161012PWA_03 | Infrastructure (network-based) | -36.2991 | 144.5185 | 1 | Powercor | Report | 3989 | 0.026662 | Low voltage AC (<1kV) | Bendigo Airport | 3563 | Lockington | Vehicle
Crew isolated supply for LEI attendance and REC repairs the following day. | 3 MALIBU DRIVE, CABARITA VIC 3505 | 34004195 | Working too close to underground cables | [5 empty] | 2 | Customer reported that a handyman was digging drainage and had hit an underground service cable. Minor shock but ok. Crew attended and found that a cable had been hit but were unsure if a Telstra line or consumer mains due to area being waterlogged. Handyman said felt â€œtinglesâ€ when hit it and was ok and was not needing medical treatment. Crew isolated overnight for repair following day. Following day LEI attended and crew re-attended. Had found that the consumer mains cable had been knicked with a saw. | Customer installation | 0 | 0 | 0 |  | MBN022 | Accidental contact | Minor shock;Loss of supply | 30/09/2016 21:30 |  |  | 3031 | Residential |  | 20161012PWA_04 | Infrastructure (network-based) | -34.198 | 142.0856 | 1 | Powercor | Report | 12110 | 0.0039769 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Cabarita | Dug up
crews attended and repaired earthing | 700 DAVIS ROAD, TARNEIT VIC 3029 | 31025271 | Theft | [5 empty] | 2 | passing employee found earths stolen at the incident location, while on route to another work location. A crew attended, made safe and repaired the earths at two substations in this area. | Earth | 0 | 0 | 0 |  | LV002 | interference | Damage to network assets | 42561.5514 |  |  | 4041 | Residential |  | 20161013PWA_05 | Infrastructure (network-based) | -37.8034 | 144.6592 | 1 | Powercor | Report | 5008 | 0.038559 | 22kV AC | Laverton Raaf | 3029 | Tarneit | Other
The ZNX No Go Zone Co-ordinator attended and found scaffolding had been installed around the pole within 4.6m of the lighting assets. (photo attached) The No Go Zone breach was reported to Worksafe this day. | 317-319 CLAYTON ROAD, CLAYTON VIC 3168 |  | Working too close to overhead lines | Unknown environment factor |  | Unknown technical factor | Unknown work practice factor |  | 2 | No Go Zone inquiry. "Unico P/L" sent an email to United Energy regarding a No Go Zone assessment as they were to complete scaffolding work at the property. | Conductor (insulated);Surge diverter | 0 | 0 | 0 |  |  | No Go Zone breach. | No Go Zone (no contact) | 27/05/2016 9:00 |  |  | 2391 | Roadway |  | 20160527UTD_01 | Infrastructure (network-based) | -37.9245 | 145.1196 | 2 | United Energy Distribution | Report | 3008 | 0.026586 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Other
Crew isolated supply and undertook repairs | 9 KING STREET, BELMONT VIC 3216 | 21191 |  |  |  | Overheated connection |  |  | 2 | The CFA reported a fire on a pole near this address. On arrival the attending crews found that a fuse switch disconnector had malfunctioned. There was no ground fire. There were no reported injuries or third party property damages. | Disconnector/isolator | 0 | 0 | 0 |  | GCY023 | Connection failure | Pole-top fire | 30/05/2016 19:11 | 0 | Negligible: no ground fire | 2406 | Roadway |  | 20160531PWA_02 | Infrastructure (network-based) | -38.1776 | 144.3383 | 1 | Powercor | Report | 3216 | 0.012035 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
Pole Substation was initially De-energised and eventually relocated on the 26th of May. | 154 FERGUSON STREET, WILLIAMSTOWN VIC 3016 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Customer constructed canopy close to Jemena pole substation. | Conductor (ABC);Pole mounted | 0 | 0 | 0 |  | NT 11 | Customer did not contact Jemena prior to constructing canopy, there was misunderstanding between Jemena PM and customer. | No Go Zone (no contact) | 42554.466 |  |  | 2409 | Residential |  | 20160601JEM_01 | Infrastructure (network-based) | -37.858 | 144.8921 | 1 | Jemena | Report | 3029 | 0.028697 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Other
The attending Powercor Fault Crew reterminated the existing O/H Twisted Service Cable following installation of a new FOLCB and completed an NST Test which confirmed a Pass result. | 15 MOWAT STREET, GEELONG WEST VIC 3218 |  |  |  |  | Corrosion |  | Phase to phase | 2 | Ms Kerry Macdonald received an electric shock whilst washing dishes when she made simultaneous contact between her hands on the Kitchen Tap and the metal Sink. | Connection box | 2 | 2 | 2 |  |  | Corroded O/H Service Neutral Conductor termination at the Customerâ€™s POA / Two Point Connection Box. | Minor shock | 42618.8333 |  |  | 2415 | Residential |  | 20160601PWA_04 | Infrastructure (customer connection) | -38.1348 | 144.3421 | 1 | Powercor | Report | 3035 | 0.023108 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Connection
The circuit/s was isolated. ESV ( Michael Misulkin) attended site. Investigations undertaken. | 187 MOLLISON STREET, KYNETON VIC 3444 | 904969 |  |  |  |  | Not followed;Incorrect electrical isolation and/or permits |  | 2 | REC reported an electrical worker received an electric shock at the incident location. A Licenced Electrical Inspector (LEI) was attending an appointment on behalf of Powercor to complete the testing and connection of a new multiple occupancy cubicle and associated installations at Kyneton showgrounds and sporting complex. Prior to the receipt of the Certificate of Electrical Safety, the LEI instructed the attending Powercor Metering and Servicing crew to connect supply to the installation. During subsequent testing by the LEI, one of the current transformer (CT) metered installations was energised resulting in an electrical shock to an electrician working at one switchboard. This switchboard was located approximately 300 metres away from the main cubicle. The main cubicle had three (3) CT and seven (7) direct connected supplies. Crew attended and isolated circuit/s for investigation by ESV. Electrical worker attended local hospital for precautionary checks. | Connection to meter;Customer installation | 0 | 0 | 0 |  | WND014 | Wiring was connected and energised prior to the completion of works | Minor shock | 42406.5618 |  |  | 2429 | Public space |  | 20160602PWA_05 | Infrastructure (network-based) | -37.2436 | 144.4545 | 1 | Powercor | Report | 3051 | 0.0041968 | Low voltage AC (<1kV) | Bendigo Airport | 3444 | Kyneton | Other
REPLACED 2x 3 PHASE POLE BOXES AT A049789 opposite 8 FORD CRT. Intersection of Linda and Ford Court. | 8 FORD STREET, FOOTSCRAY VIC 3011 | A049789 |  |  |  | Age |  |  | 2 | MFB reported an asset fire. A 2x 3 PHASE POLE BOXES AT A049789 opposite 8 FORD St was found and required replacement. The molten material fell to the ground without any ignition of material on the ground. The ground around the base of the pole consisted of asphalt footpath and road separated by blue-stone guttering. Consequently the only impact was loss of supply to customers on the affected circuit. | Connection box | 0 | 0 | 0 |  | LV fed from Feeder FE-08 | Elements - Aged & Deteriorated asset. The aged elements in the 3 phase pole box severely overheated to the extent that the unit burnt. Parts of the plastic housing fell to the ground causing minor charring at the base of the pole. | Pole-top fire;Loss of supply | 28/05/2016 19:18 | 1 | Negligible: no ground fire | 2435 | Residential |  | 20160606JEM_02 | Infrastructure (network-based) | -37.7974 | 144.8992 | 1 | Jemena | Report | 3281 | 0.029307 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | AF Other
Crew isolated supply and undertook repairs | 127 FERGUSONS ROAD, ALLESTREE VIC 3305 | 904506 |  |  |  | Leakage |  |  | 1 | Crew were in the area attending a report pole top fire event. Upon commencing restoration activities the crew identified a second pole top fire on P13. The line was isolated once again and repairs undertaken. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 0 | 0 | 0 |  | PLD001 | Excessive leakage current | Pole-top fire | 42461.9563 | 1 | Negligible: no ground fire | 2433 | Roadway |  | 20160606PWA_01 | Infrastructure (network-based) | -38.2834 | 141.6508 | 1 | Powercor | Report | 3079 | 0.032646 | 22kV AC | Portland (Cashmore Airport) | 3305 | Allestree | Pole
Initial Report: All customers were restored approximately at 19:36. Final report: The on-shift controller immediately assessed what had occurred and notified CitiPower and United Energy (the affected distribution businesses) and the Australian Energy Market Operator (AEMO). The on-shift controller requested the distribution businesses strip the busbars at the affected stations to allow the restoration of the sub-transmission loop. Once this was completed, the distribution businesses were advised to restore the load. The on-shift controller also reversed the steps of the switching log and returned RTS to normal. Approximately 55MW of load was interrupted for a period of 9 minutes 36 seconds (9.6 mins). The Shift Manager was briefed by the on-shift controller, the Shift Manager commenced notification through the remainder of the business and ESV. A Whispr message was issued at 20:48 to issue a broad notification. Since the event, a number of improvements have made that would have prevented the outcome of the incident. A broader investigation has also been completed and recommendations from this report are in the process of implementation to further reduce the risk of a similar incident. | 347 MARY STREET, RICHMOND VIC 3121 | not applicable |  |  |  | System false alarm;Other |  |  | 0 | IMS 222257. Initial Report: At 1925, OSSCA Operation at Richmond Terminal Station (RTS) shed Substation Camberwell (CL) & Substation Gardener (K), equating to approximately 50MW. Final Report: On 2 June, 2016, switching was undertaken at Richmond Terminal Station (RTS) to isolate the Number 1 220kV busbar, which was required out of service due to the proximity of testing associated with the new 220kV Gas Insulated Switchgear (GIS). During this switching, at 19:25, OSSCA incorrectly identified an overload of the B6 Transformer, alarmed and then operated to open two 66kV circuit breakers on the 1-2 66KV bus group. This resulted in interrupting supply from RTS to the CitiPower owned Camberwell Zone Substation (CL) and United Energy owned Gardener Zone Substation (K), resulting in the loss of all load at those substations. The significant contributing factors identified are: o The B6 Transformer OSSCA was inadvertently armed by the controller in response to OSSCA alarms alerting overloading of the B6 Transformer during planned switching; o The SCADA data source used for OSSCA B6 Transformer loading calculation was found to be inaccurate due to a pre-existing calculation error; o At the time of the event, the OSSCA display used a different approach to displaying the status and operating controls than normally used in SCADA. This has now been changed in response to this event; o The OSSCA function is armed and disarmed using a single action from the controller. The normal control function requires a two-step confirmation process; o At RTS, 66kV current readings are available in SCADA from the two B6 transformer circuit breakers. No current readings are available in SCADA from the 66kV transformer. The 66kV current in the B6 Transformer is based on a calculation is made in SCADA which summates the absolute values of the current in the two CBs and not the vector quantities. When the B6 transformer 220KV CB is open and the B6 transformer 66kV CBs are being used as a tie between the bus groups, the calculation will give a false reading of double the individual CB current when it should give a result of almost zero Amps. o This false reading is what OSSCA used to determine the transformer loading and consequently generated alarms indicating an overload of the B6 Transformer. The controller then selected the OSSCA display to ensure that OSSCA was disarmed and inadvertently armed the OSSCA B6 model resulting in OSSCA load shedding. | Terminal substation | 0 | 0 | 0 |  | not applicable | Protection operation / load shedding incident. | Loss of supply;Significant disruption to the community | 42406.809 |  |  | 2438 | Other | Substation | 20160606SPN_02 | Infrastructure (network-based) | -37.831 | 145.0004 | 2 | AusNet Services Transmission | Report | 8537 | 0.0061794 | 66kV AC | Essendon Airport | 3121 | Richmond | AF Other
On arrival crew isolated supply and carried out repairs | 15 CARLTON STREET, LAKE WENDOUREE VIC 3350 | 21322 |  | Precipitation |  | Leakage |  |  | 2 | A customer reported a light fitting on fire at incident location | Public lighting | 0 | 0 | 0 |  | BAN001 | Pollution | Other electricity related | 42526.8125 | 1 | Negligible: no ground fire | 2439 | Roadway |  | 20160608PWA_01 | Infrastructure (network-based) | -37.5536 | 143.8198 | 1 | Powercor | Report | 3104 | 0.0083843 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Lake Wendouree | AF Other
Initial report: No one injured - Site vacated - IRT manned - Currently under investigation. John Paul Annal appointed recovery manager. ESV, AEMO, Media notified. Final report: A hazard assessment was undertaken and due to the presence of a further three sets of CTs (9 units) of the same make and type, a safety exclusion zone was placed around the entire 220kV switchyard. The switchyard was scanned for RF, corona and thermograph and found to be clear. The condition of the remaining suspect CTs was checked by taking oil samples under outage conditions for dissolved gas analysis. The DGA results confirmed no untoward behaviour within the CTs and the exclusion zone was rescinded on the afternoon of 10th June. A detailed forensic investigation is underway to determine the root cause of the failure. Following forensic inspection of the failed unit which found the presence of water ingress from the CT head, the exclusion zone was re-established. The suspect CTs are being replaced as a matter of urgency. Two sets have been replaced. The No. 1 220kV Bus CTs were replaced on 24th June, and the 2B-4 220kV Bus Tie CB CTs were replaced on 26 June. The 1-2A 220kV Bus Tie CB and the No. 4 220kV Bus CTs are due to be replaced by the 1st and 5th July respectively. These were the only sets of these types of CTs remaining on the Transmission network. Furthermore, the following note (via an e-mail) was sent to Brett Fox and Ed Micaleff at ESV on 4/7/2016 by Phil Bryant, AusNet Services' Network Safety Manager: Brett/Ed, Just to let ESV know the CTs in question have all been replaced. The last set was completed over the weekend. Regards Phil. | 347 MARY STREET, RICHMOND VIC 3121 |  |  |  |  | Moisture ingress |  | Phase to earth | 1 | IMS 222328. RTS 2B-4 BT CB CT Fail - Significant fire & explosion - Level 3 declared. The No 2 & No 4 220kV Buses tripped at approximately 16:10 hours from Bus protection due to the catastrophic failure of the Blue phase 220kV current transformer (CT) associated with the 2B-4 220kV Bus Tie CB. All site personnel immediately vacated site. There were no injuries and no loss of customer supplies. A level 3 emergency was declared at 16:45 hours. The Metropolitan Fire Brigade (MFB) attended and following the electrical isolation of the affected plant extinguished the fire shortly after 17:10 hours. Energy Safe Victoria (ESV) was advised and representatives inspected the affected plant the following day. All site works were suspended. | Circuit breaker;Terminal substation;Transformer | 1 | 1 | 0 |  | not applicable | Refer to section 5 of the attached report for a list of causal factors. | Plant/equipment | 42557.6736 | 2 | Localised: less than 10 sq.m | 2445 | Other | Substation | 20160608SPN_02 | Infrastructure (network-based) | -37.831 | 145.0004 | 1 | AusNet Services Transmission | Report | 3451 | 0.016708 | 220kV AC | Essendon Airport | 3121 | Richmond | AF Other
On arrival crew isolated supply and commenced repairs | 19 BARBARA STREET, WOODEND VIC 3442 | 916725 |  |  |  | Overheated connection |  |  | 2 | Vic Fire reported pole fire at incident location. On arrival the crew found that a low voltage fused switch disconnector box smoking and burnt out. There was no ground fire. There were no reported shock, injuries or third party property damages. | Disconnector/isolator | 0 | 0 | 0 |  | WND012 | overheated connection | Melting or smoking only | 42527.959 |  |  | 2449 | Roadway |  | 20160609PWA_02 | Infrastructure (network-based) | -37.3396 | 144.5355 | 1 | Powercor | Report | 3127 | 0.035497 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Connection
Supply isolated, meter removed. A defect notice was issued. | 54 WOLLAHRA RISE, WYNDHAM VALE VIC 3024 | 211270 | Vandalism;Unauthorised access | [5 empty] | 2 | A Powercor employee reported a vandalised meter board and sparking wires at the incident location. On arrival the Powercor crew found that the customerâ€™s meter board has been damaged. The live connections exposed and few flash over marks on the board. There were no injuries or fire. | Customer installation | 0 | 0 | 0 |  | WBE014 | Vandalism to customers installation by unknown person | Loss of supply | 42557.559 |  |  | 2450 | Residential |  | 20160610PWA_01 | Infrastructure (network-based) | -37.8732 | 144.6224 | 1 | Powercor | Report | 8037 | 0.0052419 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
A faults truck attended and isolated supply by turning off the circuit breaker in the next public lighting column that isolated another section of footpath lighting. They identified evidence that control wiring was showing signs of possible failure as demonstrated in pics 306 & 307. The faults crew were uncertain if this type of low voltage equipment is suitable to be mounted in the public lighting column as the columns can be susceptible to high levels of condensation that caused the failure of the low voltage lighting equipment. Also attached is a photo of the footpath lighting prior to isolating supply (pic 302). A ZNX Project Planner will be contacting the council as the footpath lighting including the wiring and controllers mounted in the light columns are council assets. There are potentially more of these council assets located in the area and the council will be contacted to determine if they will be isolated due to the potential risk they present. | 13 HAMILTON STREET, MONT ALBERT VIC 3127 | LIS No. 9829505 |  |  |  | Moisture ingress |  |  | 2 | MFB onsite - reports of sparking power lines outside the Churchill CafÃ©. Street lighting wiring caught fire outside 13 Hamilton Street, Mont Albert after it had been arching and the MFB were in attendance and extinguished the fire. The public lighting pole is a council owned decorative pole with a low voltage footpath lighting control transformer and associated wiring that caught fire in the public lighting column with United Energy LIS No. 9829505 attached. No electric were sustained. | Public lighting;Customer installation | 0 | 0 | 0 |  |  | Control wiring within the public light column was showing signs of failure. | Melting or smoking only | 24/06/2016 10:00 |  |  | 2459 | Roadway |  | 20160614UTD_02 | Infrastructure (network-based) | -37.8202 | 145.105 | 1 | United Energy Distribution | Report | 3654 | 0.036346 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Mont Albert | AF Other
Jemena operator isolated the substation and the surrounding area to make it electrically safe. Oil leak was contained locally on site around the pole substation. Substation was replaced on the day. | 76 SYDNEY STREET, FOOTSCRAY VIC 3011 | 10123907 | Vandalism | [5 empty] | 2 | Customer reported oil leaking from pole substation Sydney-Barkly (500kVA) outside her property. When crew arrived on site they advised copper earth had been removed from the substation. I.e. copper was cut clear at base of the pole and the transformer was damaged. | Pole mounted;Earth/earthing | 0 | 1 | 0 |  | FE9 | Unknown third party vandalised distribution pole substation. Third party removed copper earth. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/06/2016 9:29 |  |  | 2475 | Public space |  | 20160616JEM_01 | Infrastructure (network-based) | -37.7981 | 144.8875 | 1 | Jemena | Report | 3251 | 0.041377 | 22kV AC | Essendon Airport | 3011 | Footscray | Other
On arrival crew isolated supply and commenced repairs | 62 ARTHUR STREET, SOUTH YARRA VIC 3141 | 35142 |  |  |  | Corrosion |  |  | 2 | MFB reported a pole fire at the incident location. On arrival the crew found a Krone box on the pole had overheated, causing a fire. There was no ground fire, injuries or third party property damage. | Connection box | 0 | 0 | 0 |  | PR023 | Overheated connection in FSD | Pole-top fire;Loss of supply | 15/06/2016 9:35 | 1 | Negligible: no ground fire | 2488 | Roadway |  | 20160620PWA_01 | Infrastructure (network-based) | -37.8419 | 144.9945 | 1 | CitiPower | Report | 3222 | 0.038786 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Connection
The site was made safe and temporary repairs were made to the fencing. | 242-254 ST ALBANS ROAD, BREAKWATER VIC 3219 |  | Theft | [5 empty] | 2 | A security guard while patrolling GLE Zone Substation, reported to the control room, forced entry to this facility. On arrival the operator found that the zone substation fence had been cut and two drums of control wiring had been removed from GLE Zone Substation. There were no reported injuries or other third part damage. | Zone substation | 0 | 0 | 0 |  | GLE | Criminal activity | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);More than $50k damage | 14/06/2016 21:00 |  |  | 2490 | Industrial |  | 20160621PWA_01 | Infrastructure (network-based) | -38.1796 | 144.3817 | 1 | Powercor | Report | 3225 | 0.02625 | Not applicable | Avalon Airport | 3219 | Breakwater | Other
Crew replaced service cable | 12 KING EDWARD STREET, COHUNA VIC 3568 | 702348 | Vehicle | [5 empty] | 2 | Customer reported cable on ground at incident location. On arrival the crew found service cable broken in half and laying on ground. There was no ground fire,no reported injuries or third party property damages. | Service conductor | 0 | 0 | 0 |  | CHA003 | Believe to be high load, although no vehicle on site | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/06/2016 8:14 |  |  | 2492 | Roadway |  | 20160621PWA_03 | Infrastructure (network-based) | -35.8109 | 144.2225 | 1 | Powercor | Report | 3227 | 0.038612 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3568 | Cohuna | Vehicle
A faults crew attended and disconnected supply to the lantern and a further trouble order was created to replace the defective 150w HPS lantern. | JOSEPH STREET, TEMPLESTOWE LOWER VIC 3107 | 7058602 |  | Precipitation |  | Fault on customer installation |  |  | 2 | Per MFB - Street light fire has been extinguished. A 150w HPS lantern on pole No. 7058602 located on the corner of High and Joseph Street caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting;Customer installation | 0 | 0 | 0 |  |  | The cause was unknown but it had been raining beforehand. | Melting or smoking only | 24/06/2016 1:00 |  |  | 2493 | Roadway |  | 20160622UTD_01 | Infrastructure (network-based) | -37.7719 | 145.1156 | 1 | United Energy Distribution | Report | 3655 | 0.039617 | Low voltage AC (<1kV) | Moorabbin Airport | 3107 | Templestowe Lower | AF Other
On arrival crew commenced repairs | 55 LITTLE LA TROBE STREET, MELBOURNE VIC 3000 |  | Working too close to underground cables | [5 empty] | 2 | Worker reported a cable had been dug up in footpath. On arrival the crew found that an excavator had contacted a low voltage cable whilst working to replace a concrete footpath. No Protection expected. There were no reported injuries, fire or property damage. | Cable | 0 | 0 | 0 |  | MP005 | Cable Sheath damaged by excavator | No Go Zone (contact) | 24/03/2016 8:57 |  |  | 2498 | Public space |  | 20160623PWA_02 | Infrastructure (network-based) | -37.8098 | 144.9626 | 1 | CitiPower | Report | 7992 | 0.036003 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
Upon arrival the crew replaced the stolen earth cables. | 2A LENNON PARKWAY, DERRIMUT VIC 3030 | 972596 | Theft | [5 empty] | 2 | A contractor reported a Kiosk door lock cut away and missing copper earthing cables at the incident location. There were no reported injuries or other damage. | Pad mounted equipment/kiosk;Earth/earthing | 0 | 0 | 0 |  | SU013 | Theft of earth cables | Less than $50k damage | 21/06/2016 9:35 |  |  | 2500 | Public space |  | 20160623PWA_04 | Infrastructure (network-based) | -37.7906 | 144.7632 | 1 | Powercor | Report | 3236 | 0.013771 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
Crew replaced earth cable | 6 PERCY STREET, BRUNSWICK VIC 3056 | 50709 | Theft | [5 empty] | 2 | A passer-by reported that wires appear to be cut at the incident location. On arrival the crew found that thieves had cut and removed the earth from the substation. There was no fire, reported injuries or third party property damage. | Earth/earthing | 0 | 0 | 0 |  | WB009 | cable theft | Less than $50k damage | 23/06/2016 9:30 |  |  | 2504 | Public space |  | 20160624PWA_01 | Infrastructure (network-based) | -37.7658 | 144.9588 | 1 | CitiPower | Report | 3249 | 0.007184 | Earthing cable | Essendon Airport | 3056 | Brunswick | Other
Crew isolated supply to the service cable for repairs. | 59 PARAWEENA DRIVE, TRUGANINA VIC 3029 | 821397 | Theft | [5 empty] | 2 | Aaron Parsons from 52 Paraweena Drive advised he had found bolt cutters on an underground cable at a pit opposite his location at the end of the court. The bolt cutters were still connected to the cable. Crew attended and found bolt cutters had been used in an attempt to cut a low voltage service cable from a pit. Police advised. No shock or injuries reported. No fire or third party damage. | Cable;Services cable | 0 | 0 | 0 |  | LVN024 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/06/2016 11:08 |  |  | 2516 | Industrial |  | 20160628PWA_02 | Infrastructure (network-based) | -37.8141 | 144.7583 | 1 | Powercor | Report | 3263 | 0.040303 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
On arrival crew carried out repairs | 12 WHALLEY STREET, NORTHCOTE VIC 3070 | 73132 | Vehicle | [5 empty] | 2 | A passer-by reported a service cable down and smoking at the incident location. On arrival the crew found that the service cable had been brought down by an unknown vehicle. There was no ground fire. There were no reported injuries or third party property damage. | Service conductor | 0 | 0 | 0 |  | NC006 | Unknown vehicle struck service line | Loss of supply | 27/06/2016 9:23 |  |  | 2518 | Roadway |  | 20160628PWA_04 | Infrastructure (network-based) | -37.7719 | 145.0067 | 1 | CitiPower | Report | 3267 | 0.0069965 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
The attending crew isolated supply and carried out repairs | 1B PARKER STREET, TORQUAY VIC 3228 | 33984 | Vehicle | [5 empty] | 2 | A nearby Customer reported wires down at the incident location. On arrival the crew found that an unknown vehicle had struck a low voltage pole, resulting in the LV conductors falling to the ground. The driver and the vehicle had both decamped the scene by the time the crew arrived, and their identity is unknown. There was no ground fire. There were no reported injuries. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | WPD032 | Unknown vehicle struck pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/06/2016 1:37 |  |  | 2520 | Roadway |  | 20160628PWA_06 | Infrastructure (network-based) | -38.3368 | 144.321 | 1 | Powercor | Report | 3270 | 0.020741 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Vehicle
On arrival confirmed condition of conductor | 26-28 COLLINS ROAD, MELTON VIC 3337 | 29372 | Working too close to overhead lines;Vehicle | [5 empty] | 1 | Powecor fault crew attending an outage found that a tip truck contacted 22kV O/H conductor at the incident location. The truck had left the incident location, no vehicle details available. Flash marks were observed on the conductor . There was no fire or reported injuries. | Conductor (bare) | 0 | 0 | 0 |  | MNL013 | Unknown tip truck struck overhead conductor | No Go Zone (contact) | 29/06/2016 14:08 |  |  | 2525 | Industrial |  | 20160630PWA_01 | Infrastructure (network-based) | -37.6894 | 144.597 | 1 | Powercor | Report | 3277 | 0.0024641 | 22kV AC | Laverton Raaf | 3337 | Melton | Vehicle
The supply to the substation was isolated and the crews replaced the earths. | 169 HENTY STREET, RESERVOIR VIC 3073 |  | Theft | [5 empty] | 2 | Crews discovered that copper earths were stolen from Henty-Kurnai distribution pole substation. The copper was removed by unknown persons. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown person stole the copper earths from the substation. | no person affected;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42407.4257 |  |  | 2528 | Roadway |  | 20160702JEM_01 | Infrastructure (network-based) | -37.7178 | 144.9845 | 1 | Jemena | Report | 3530 | 0.0086574 | Low voltage AC (<1kV);Earthing cable | Essendon Airport | 3073 | Reservoir | Other
Field crews inspected the damage and ensure the site had been made safe. | 83-89 FREIGHT DRIVE, SOMERTON VIC 3062 |  | Vandalism |  |  |  |  | Phase to phase | 1 | Wire found thrown over high voltage overhead conductors at Freight 55-Fleet distribution substation. Burn marks were discovered on 2 phases of the overhead conductors. It was suspected vandals threw the wire but they had left the location before field crews arrived on site. | Conductor (bare) | 0 | 0 | 0 |  |  | It was suspected that vandals threw wire across high voltage conductors. Suspected accidental human wilful vandalism | Loss of supply | 19/06/2016 0:50 |  |  | 2531 | Industrial |  | 20160704JEM_01 | Infrastructure (network-based) | -37.6378 | 144.9618 | 1 | Jemena | Report | 3338 | 0.04014 | 22kV AC | Essendon Airport | 3062 | Somerton | Other
CEOT dispatched a fault crew to make safe, investigate and repair. Isolated transformer, checked fire was extinguished and arranged replacement of LV crossarm. | 65 MOUNT SHAMROCK ROAD, PAKENHAM VIC 3810 | 501136 |  |  |  | Overheated connection |  |  | 1 | IMS 222754. LV crossarm burnt in half on Substation pole. | Crossarm (wood) | 0 | 0 | 0 |  | ofr23 | Unknown cause of fault / fire - CEOT believe loose lv connections caused fire. â€¢ Melted insulation on the neutral wire from the TX down to the LV cross arm (approx. 2mtr) â€¢ Melted insulation on the customers u/g service at the cross arm â€¢ Burnt scorch marks on the pole and on the cross-arm (approx. 1/2mtr on either side of the LV cross arm) â€¢ Cross arm slightly burnt, possible charring when the cable caught fire (Note: signs of cross arm deterioration ) â€¢ HV fuses (6K â€“ BAâ€™s) dropped out. â€¢ No other signs of burnt material / grass in or around the pole | Pole-top fire | 42376.3542 | 1 | Negligible: no ground fire | 2533 |  |  | 20160704SPN_02 | Infrastructure (network-based) | -38.0348 | 145.4828 | 1 | AusNet Services Distribution | Report | 3529 | 0.0057488 | Low voltage AC (<1kV) | Moorabbin Airport | 3810 | Pakenham | Crossarm
The site was isolated and the crew reinstalled the earths. | 5 CALA STREET, WEST FOOTSCRAY VIC 3012 |  | Theft | [5 empty] | 2 | Crews discovered that copper was stolen from Cara-Beaumont substation. Unknown persons stole copper earths. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown persons stole copper earths from the distribution substation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42497.6403 |  |  | 2547 | Roadway |  | 20160705JEM_02 | Infrastructure (network-based) | -37.8072 | 144.8659 | 1 | Jemena | Report | 3531 | 0.016834 | Extra low voltage AC (<50V);Earthing cable | Essendon Airport | 3012 | West Footscray | Other
The switch was isolated and the crew reinstalled the earths. | CURRAJONG STREET, WEST FOOTSCRAY VIC 3012 |  | Theft | [5 empty] | 2 | Crews discovered copper theft from an air break switch which was located on a pole. Unknown persons had stolen the copper earths. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown person stole copper from a switch pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42497.6403 |  |  | 2549 | Roadway |  | 20160705JEM_04 | Infrastructure (network-based) | -37.8018 | 144.8761 | 1 | Jemena | Report | 3533 | 0.014266 | Extra low voltage AC (<50V);Earthing cable | Essendon Airport | 3012 | West Footscray | Other
On arrival crew commenced repairs | 85 NEWLYN RESERVOIR ROAD, NEWLYN NORTH VIC 3364 | 27076 | Theft | [5 empty] | 2 | Inspectors working on the BAN009 feeder reported the copper earths had been cut and stolen at the incident location . The LV earth was cut and stolen. There was no fire, injuries or third party property damage. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper cable theft | Less than $50k damage | 30/06/2016 14:04 |  |  | 2538 | Roadway |  | 20160705PWA_02 | Infrastructure (network-based) | -37.4028 | 144.0088 | 1 | Powercor | Report | 3300 | 0.017668 | Earthing cable | Ballarat Aerodrome | 3364 | Newlyn North | Other
On arrival crew commenced repairs | 73 CHURCH PARADE, KINGSTON VIC 3364 | 32003208 | Theft | [5 empty] | 2 | An Electrix inspector working on the BAN009 feeder reported a copper earth cable had been cut and removed at P272 Creswick line. Approx. 1mtr of cable missing at base of pole. There was no fire, injuries or third party damages. | Earth | 0 | 0 | 0 |  | BAN009 | Copper cable theft | Less than $50k damage | 42376.5868 |  |  | 2541 | Roadway |  | 20160705PWA_04 | Infrastructure (network-based) | -37.3728 | 143.9626 | 1 | Powercor | Report | 3303 | 0.028154 | Earthing cable | Ballarat Aerodrome | 3364 | Kingston | Other
The substation was isolated and crews reinstalled earths. | 4 TURIN PLACE, KEILOR LODGE VIC 3038 |  | Theft | [5 empty] | 2 | Unknown persons stole copper earths from Turin-Messina kiosk substation. | Copper;Earth/earthing | 0 | 0 | 0 |  | shm12 | Unknown persons stole copper earths from substation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42528.3819 |  |  | 2552 | Public space |  | 20160706JEM_02 | Infrastructure (network-based) | -37.7007 | 144.799 | 1 | Jemena | Report | 3534 | 0.0031366 | Extra low voltage AC (<50V);Earthing cable | Melbourne Airport | 3038 | Keilor Lodge | Other
CEOT dispatched a fault crew and a LEI to investigate the incident and carry out any necessary repairs. The fault crew attended the site conducted an initial voltage test from the neutral to an independent earth which recorded between 8-13V. An initial NST test was carried out at various premises and a problem was detected at the neutral connection in the service pit shared between property numbers 116 and 120 Hickox St. A new underground IPC was installed in the service pit and all tests carried out at 104 Hickox St - all tests passed with 1.2 Volts on the neutral. | 116 HICKOX STREET, TRARALGON VIC 3844 | 2577236 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 222481. A plumber was changing a gas hot water service when he felt a slight tingle. Matt the REC, tel. 0422 136162, advised CEOT that the plumber who installed the HWS felt a tingle. The REC conducted tests but couldn't find anything wrong with the installation. The tingle was caused by a faulty neutral service connection in an underground service pit. | Service conductor;Services pit | 0 | 0 | 0 |  | tgn11 | Faulty neutral service connection in an underground service pit. | Minor shock | 17/06/2016 10:59 |  |  | 2557 | Residential |  | 20160707SPN_02 | Infrastructure (network-based) | -38.21 | 146.5314 | 1 | AusNet Services Distribution | Report | 3326 | 0.033039 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
On arrival site assessed and replacement of cable organised | 319-391 LEAKES ROAD, PLUMPTON VIC 3335 | 30138502 | Theft | [5 empty] | 2 | REC attended site to dig trench and pit has been removed. Crew attended site and advised that vandals had stolen the LV UG Service Cable running from Pole LIS-923934 to LV Service Pit across the road at 319-391 Leakes Rd, Plumpton. Melton Police has been advised of incident. â€¢ Please Note:- The LV UG Service Cable was NOT Alive and had only just been recently installed via a 63mm road bore by a PCA approved Contractor and had not yet been connected or energized No shock or injuries reported. No fire or third party damage. | Cable | 0 | 0 | 0 |  | MLN021 | Theft of underground service cable | Less than $50k damage | 42407.4167 |  |  | 2562 | Roadway |  | 20160708PWA_01 | Infrastructure (network-based) | -37.6722 | 144.6635 | 1 | Powercor | Report | 3333 | 0.013933 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Other
On arrival crew isolated supply and commenced repairs | 6 ALEC COURT, TARNEIT VIC 3029 | 34021505 | Working too close to underground cables | [5 empty] | 2 | A Contractor advised that their crew have hit an UG cable at the incident location while they were excavating in the area. On arrival the crew found that the contractor had damaged a live low voltage underground service main. The conduit and insulation were damaged and the low voltage service was still â€œaliveâ€ when the crew arrived. There were no reported injuries. There was no fire. | Services cable | 0 | 0 | 0 |  | WBE012 | Excavator damaged cable | No Go Zone (contact) | 42467.4806 |  |  | 2564 | Roadway |  | 20160708PWA_03 | Infrastructure (network-based) | -37.8703 | 144.6593 | 1 | Powercor | Report | 3410 | 0.016832 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Dug up
On the day of the incident the site was made safe, both low voltage circuit conductors were repaired with conductor crimps to join the sections back together. This site will continue to be monitored, as there will be actions in place to prevent this from re-occurring such as spreaders in the short term and potential long term rectification is necessary as the span does require actions to address sagging. | 48 BARKLY STREET, SUNBURY VIC 3429 | 10955212 |  | Wind |  | Conductor clashing |  | Phase to phase | 1 | Low voltage conductors from two low voltage circuits came into contact due conductor sag and windy conditions. The top circuit is copper conductor, due to its weight and long span, the upper circuit sagged. Due to the windy conditions the bottom circuit (aluminium) blue phase clashed with the white phase of the upper circuit. The resultant fault current at the point of contact lead to the two low voltage conductors to break and fall to the ground. | Conductor (bare);Aluminium;Copper | 0 | 0 | 0 |  | SBY31 | Combination of high winds and the actual condition of the circuits at the time of the incident i.e. conductor sag on the upper circuit. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42711.3701 |  |  | 2581 | Public space |  | 20160712JEM_01 | Infrastructure (network-based) | -37.5831 | 144.7304 | 1 | Jemena | Report | 5524 | 0.034088 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Conductor
One arrival the crew carried out repairs. | 25 LAIDLAW DRIVE, DELACOMBE VIC 3356 | 30150943 | Theft | [5 empty] | 2 | Employee reports copper earth missing from pole at incident location. A crew attended and found that approx. 0.5m of earth cable missing off the pole. There was no fire, injuries or third property damage. | Earth/earthing | 2 | 2 | 2 |  | BAS021 | Copper theft | Less than $50k damage | 42589.491 |  |  | 2579 | Roadway |  | 20160712PWA_01 | Infrastructure (network-based) | -37.5771 | 143.823 | 1 | Powercor | Report | 3352 | 0.010395 | Earthing cable | Ballarat Aerodrome | 3356 | Delacombe | Other
On arrival crew isolated supply and carried out repairs. | 7 SPRINGBANK WAY, BROOKFIELD VIC 3338 | 31024010 |  | Bird |  |  |  |  | 2 | Report of crossarm fire at incident location. On arrival Crew found birds nest in a Fuse Mains Box had caught fire. There was no ground fire, injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | MLN013 | Bird Incident | Pole-top fire | 17/06/2016 20:58 | 1 | Negligible: no ground fire | 2582 | Roadway |  | 20160712PWA_03 | Infrastructure (network-based) | -37.703 | 144.5534 | 1 | Powercor | Report | 3355 | 0.01598 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Animal
On arrival crew arranged for isolation of the feeders, Tree was cut clear of lines. | 54 MCEWEN ROAD, KYABRAM VIC 3620 | 33088654 |  | Wind;Fallen |  |  |  |  | 1 | Customers report a tree over the lines at Incident Location. Reports of smoke/fire, CFA attended site. A Powercor crew attended and found a tree from outside clearance space had fallen across 66kV/22kV/LV conductors of the SHTS KYM 2 line. No conductors had broken. The 66kV protection operated, The 22kV was still alive when crew arrived. No shocks, injuries or ground fire starts. There was no third party property damage | Conductor (bare) | 0 | 0 | 0 |  | SHTS KYM 2 Line | Strong Winds | Other vegetation | 42711.5514 | 1 | Negligible: no ground fire | 2586 | Roadway |  | 20160713PWA_02 | Infrastructure (network-based) | -36.3082 | 145.0325 | 1 | Powercor | Report | 3359 | 0.032951 | Low voltage AC (<1kV);22kV AC;66kV AC | Shepparton Airport | 3620 | Kyabram | Trees
On arrival crew isolated supply and carried out repairs | UNIT 5 38 HOUSTON STREET, STAWELL VIC 3380 | 30252068 |  |  |  | Overheated connection |  |  | 2 | The CFA reported the fuse box smoldering at the above location. When our crew arrived they found that the connections into an LV Service Fuse Base on the meter board had overheated and caused a small fire. The fire was contained to a small area of the meter board (4cm diameter hole). There was no ground fire, reported injuries or third party property damage. | Meter board (including fuses) | 2 | 2 | 2 |  | STL004 | Corrosion | Loss of supply;Meter board | 13/07/2016 23:06 | 1 | Negligible: no ground fire | 2593 | Residential |  | 20160715PWA_02 | Infrastructure (customer connection) | -37.0536 | 142.7766 | 1 | Powercor | Report | 3368 | 0.025441 | Low voltage AC (<1kV) | Horsham Aerodrome | 3380 | Stawell | Connection
Crew attended and replaced missing earth cable. | 18 FORBES ROAD, LEIGH CREEK VIC 3352 | 30000674 | Theft | [5 empty] | 2 | Employee reports copper earth missing from pole at the incident location. There was no fire, injuries or third party damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | Copper cable theft | Less than $50k damage | 14/07/2016 9:08 |  |  | 2594 | Roadway |  | 20160715PWA_03 | Infrastructure (network-based) | -37.5598 | 143.9577 | 1 | Powercor | Report | 12583 | 0.01242 | Earthing cable | Ballarat Aerodrome | 3352 | Leigh Creek | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 2 LOCKE STREET, RYE VIC 3941 | 1303422, 1303421 and 1303420 |  | Wind;Fallen |  | Conductor clashing;HV injection |  |  | 1 | At 1001hrs on 12/07/2016, 22kV feeder STO 14 circuit breaker reclosed to lockout affecting 612 customers. During very strong winds, a large cypress tree located near the corner of Flinders and Locke Streets, Rye contacted the 22kV conductors that resulted in a HV conductor contacting the LV conductors below. The fallen tree caused "Flinders-Locke" substation pole (LIS No. 1303422), HV termination pole (LIS No. 1303421) and LV tee-off pole (LIS No. 1303420) to break and six bays of HV and LV conductors to fall to the ground. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Flinders Locke" substation. The LEI confirmed a high voltage injection occurred (MOR 1604) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (insulated);Pole (wood);Pole mounted | 0 | 1 | 0 |  | STO 14 | Vegetation: Trees Incident | HV injection;Loss of supply | 42711.4174 |  |  | 2598 |  |  | 20160715UTD_03 | Infrastructure (network-based) | -38.3751 | 144.7978 | 1 | United Energy Distribution | Report | 3560 | 0.01815 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3941 | Rye | Trees
Dispatched fault crew Tim Whiting TMR 595 and Inspector Raff Kastenberger to isolate, make safe and investigate. | 71 TWELFTH AVENUE, RAYMOND ISLAND VIC 3880 | 1609362 |  |  |  |  | Followed but inappropriate;Ineffective planning/procedures/processes |  | 2 | IMS 222850. Report from customer that his wife got a shock from pole out front of 24 pole very hot and steam coming of pole per customer , customer ok , no other damage . | Pole (concrete) | 0 | 0 | 0 |  | bdl4 | Initial fault investigation completed and the findings are that an earth from the concrete pole was inadvertently connected to the white phase located directly above. | Minor shock | 24/06/2016 7:42 |  |  | 2612 | Residential |  | 20160720SPN_01 | Infrastructure (network-based) | -37.9199 | 147.7322 | 1 | AusNet Services Distribution | Report | 3391 | 0.034259 | Low voltage AC (<1kV) | Bairnsdale Airport | 3880 | Raymond Island | Connection
MADE SAFE, CONFIRMED NO DANGER TO PUBLIC. REPLACED FITTING | 382 WILLIAMSTOWN ROAD, YARRAVILLE VIC 3013 | A051689 |  |  |  | Defective component |  |  |  | MFB reported fire on pole number A051689 opposite the premise on 382 Williamstown Road, Yarraville. Turned out to be a sodium head street light. No fire was found when crew arrived. Melted black plastic found on street light. Trouble Event Number: 135961 | Public lighting | 0 | 0 | 0 |  | FE 05 | Failure of faulty streetlight fitting. | Melting or smoking only | 21/07/2016 1:27 |  |  | 2615 | Residential |  | 20160721JEM_01 | Infrastructure (network-based) | -37.8224 | 144.8814 | 1 | Jemena | Report | 3601 | 0.021728 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | AF Other
Attended site, representative discussed with builder who advised his electrician had installed the tiger tails. | 66 GEORGE STREET, FITZROY VIC 3065 | 30306115 | Working too close to overhead lines | [5 empty] | 2 | CitiPower representative attended site in response to request for a permit to work. On arrival representative identified that "tiger tails" had already been installed on an insulated aerial service cable. Work being undertaken in laneway at rear of property. | Service conductor | 0 | 0 | 0 |  | B002 | Interference with MEC assets | No Go Zone (contact) | 20/07/2016 11:00 |  |  | 2632 | Residential |  | 20160722PWA_07 | Infrastructure (network-based) | -37.8067 | 144.9811 | 1 | CitiPower | Report | 12075 | 0.025378 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole | 31 CASHMORE ROAD, PORTLAND VIC 3305 | 32132385 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Debbie Annett received an electric shock while she was showering in the bathroom, when she made simultaneous contact between her hand on the metal tap and her bare feet on the wet shower base. | Connection box | 2 | 2 | 2 |  | PLD004 | corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole | Minor shock | 13/06/2016 10:00 |  |  | 2641 | Roadway |  | 20160725PWA_03 | Infrastructure (network-based) | -38.3217 | 141.5931 | 1 | Powercor | Report | 3428 | 0.016615 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
Disconnected service | 17 WILLIAM STREET, CREMORNE VIC 3121 | 30188730 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 1 | Contractor advised scaffold had been erected in close proximity of distribution pole and low voltage wiring compromising No Go Zone | Service conductor;Pole (concrete) | 0 | 0 | 0 |  | R024 | Breach of No Go Zone | No Go Zone (no contact) | 21/07/2016 14:30 |  |  | 2649 | Commercial |  | 20160725PWA_08 | Infrastructure (network-based) | -37.8282 | 144.9965 | 1 | CitiPower | Report | 3452 | 0.021744 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Cremorne | Other
A faults truck promptly attended and found the blue phase 5amp Boric Acid fuse had operated at "Coolart-Hodgins" substation. The crew replaced the 95mm LVABC droppers, re-attached the krone switch at pole No. LIS 1110545 and replaced the HV fuse to restore supply to customers in the area. The underground cable to 173 and 108 Coolart Road was repaired and supply restored after NST tests passed. | 108 COOLART ROAD, TUERONG VIC 3915 | 1110545 |  | Precipitation;Cold |  | Electrical breakdown;Not built/maintained to design |  |  | 1 | Customers supplied from "Coolart-Hodgins" substation advised they have no electricity supply and the CFA advised of a pole on fire and sparking near the corner of Coolart Road and Wonderland Avenue, Hastings. 95mm LVABC was dressed down a concrete pole to a krone switch that supplied an underground cable to 173 and 108 Coolart Road. It appears that a tight bandit tape compressed the LVABC inside a conduit and shorted out to the concrete pole following a downpour of rain. Naked flames were witnessed on the pole and no ground fire started. | Conductor (ABC);Cable;Aluminium;Pole (concrete) | 0 | 0 | 0 |  | HGS 22 | It appears that a tight bandit tape compressed the LVABC inside a conduit and shorted out to the concrete pole following a downpour of rain. This type of connection is used as a general practice on concrete poles but it was unknown if any protective material was used between the steel bandit and the conduit to prevent pinching of the cable. This event is considered a "one off" as its a rare event for this to occur. | Pole-top fire | 22/07/2016 16:45 | 1 | Negligible: no ground fire | 2651 | Roadway |  | 20160725UTD_02 | Infrastructure (network-based) | -38.3087 | 145.1454 | 1 | United Energy Distribution | Report | 3573 | 0.039516 | Low voltage AC (<1kV) | Moorabbin Airport | 3915 | Tuerong | Pole
A faults crew attended and disconnected supply to the lantern and a further trouble order was created to replace the defective 150w HPS lantern. | 40 PARK ROAD, DONVALE VIC 3111 | 7067507 |  | Precipitation |  | Overheated connection |  |  | 2 | MFB advises street light on fire. A 150w HPS lantern on pole No. LIS 7067507 located near the corner of Park Street and Eastlink caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown. | Pole-top fire | 26/07/2016 6:00 | 1 | Negligible: no ground fire | 2665 | Roadway |  | 20160727UTD_03 | Infrastructure (network-based) | -37.801 | 145.1923 | 1 | United Energy Distribution | Report | 3468 | 0.017917 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the FOLCB on the Reticulation Service Pole. The attending Powercor Fault Crew replaced the existing FOLCB on the Reticulation Service Pole and reterminated the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. | 243 ORRVALE ROAD, ORRVALE VIC 3631 | 30131332 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Enrica Rosato was washing clothes in the Laundry when she received an electric shock as she made simultaneous contact between her hands on the metal Taps and the metallic Laundry Trough. | Connection box | 2 | 2 | 2 |  | STN011 | O/H Service Neutral Conductor termination at the FOLCB on the Reticulation Service Pole. | Minor shock | 21/06/2016 19:00 |  |  | 2673 | Roadway |  | 20160728PWA_03 | Infrastructure (network-based) | -36.4144 | 145.4469 | 1 | Powercor | Report | 3476 | 0.012264 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Orrvale | Connection
Emergency high voltage switching took place with all three HV fuses opened on the capacitor bank at pole No. LIS 9360948 and the live line clamps were lifted. | 181-183 FRANKSTON-DANDENONG ROAD, DANDENONG SOUTH VIC 3175 | 9360948 |  |  |  | Electrical breakdown |  |  | 2 | Customer advised that one of the HV lines outside the premise is arcing and on fire. They said it appears to be the insulator / arrestor is on fire at the moment. The CFA advised of a powerline fire also. A boric acid fuse at a capacitor bank located outside 181 Frankston-Dandenong Road, Dandenong candled and there was no fire when the faults truck attended but the HV fuse appeared burnt. It was suspected the HV fuse may not have been secured in the HV fuse cradle. | Boric acid | 0 | 0 | 0 |  | DSH 31 | It was suspected the HV fuse may not have been secured in the HV fuse cradle. | Pole-top fire | 27/07/2016 7:58 | 1 | Negligible: no ground fire | 2670 | Roadway |  | 20160728UTD_02 | Infrastructure (network-based) | -38.0169 | 145.2152 | 1 | United Energy Distribution | Report | 3675 | 0.010716 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Fuse
A LEI and faults truck attended and with the underground tester were unable to obtain a NST pass on the underground service cable. The LEI completed installation tests at the premise and measured 17v rising to 26v with load applied. A underground faults crew were called to investigate and re-terminated connections in the pit but the fault still existed. Further investigation took place and the neutral service tee-joint was also re-terminated and installation tests at the premise measured 0.3v between the metallic water piping system and a independent earth that confirmed the fault had been rectified. | 2 SCOTSBURN COURT, MORNINGTON VIC 3931 |  |  | Precipitation |  | Corrosion;Neutral fault |  | Phase to earth | 2 | AMI meter No. 0825500 at 21 Ellinbank Crescent is reporting under voltage events. Please perform NST and check all neutral connections for faults. The United Energy AMI Analysts identified a meter was communicating under voltage variations and a faults crew were dispatched to investigate. While attending to a voltage investigation 21 Ellinbank Crescent, the attending crew reported that a customer received an electric shock whilst showering at 2 Scotsburn Court Mornington. The address was reported as 2 Scotsburn Court but in United Energy systems the address is known as 19 Ellinbank Crescent with meter number 0825500. The crew identified neutral impedance issues in Ellinbank Crescent and Scotsburn Court and requested that a LEI and an underground cable tester to attend. | Cable;Services cable | 0 | 0 | 0 |  |  | Deteriorated neutral service tee-joint connection was the cause that was re-terminated. | Minor shock | 20/07/2016 9:00 |  |  | 2684 | Residential |  | 20160729UTD_06 | Infrastructure (network-based) | -38.2391 | 145.0624 | 1 | United Energy Distribution | Report | 3487 | 0.01119 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Connection
On arrival crew isolated supply and commenced repairs to MEC assets LEI assessed damage to customers installations believed to be HVI through distribution neutral | 211 MCINTYRE ROAD, SUNSHINE NORTH VIC 3020 | 30103083 | Vehicle | [5 empty] | 1 | A vehicle carrier travelling north along McIntyre Road struck an Optus Overhead Service cable crossing of McIntyre Rd. The communication cable was flicked into HV and LV conductors resulting in a flashover between HV and LV circuits. High Voltage Injection into the LV circuit occurred. The vehicle carrier continued onwards and managed to strike an LV service pole outside No. 211 McIntyre Rd. | Conductor (bare);Pole (wood);Communication cable/equipment | 0 | 0 | 0 |  | SSE012 | high Vehicle / load stuck optus cable. | HV injection;Loss of supply;Damage to network assets | 29/07/2016 13:15 |  |  | 2690 | Roadway |  | 20160801PWA_01 | Infrastructure (network-based) | -37.7569 | 144.8322 | 1 | Powercor | Report | 3591 | 0.023906 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Vehicle
The Powercor crew disconnected the low voltage consumer mains in the electrical service pit and issued a defect notice. REC will do repairs. | 32 COTTESLOE PARADE, TAYLORS HILL VIC 3037 | 30303977 | Working too close to underground cables | [5 empty] | 2 | Registered Electrical contractor Dean Gill reported that customer has dug up the mains cable at the above location and he requires isolation to do repairs. On arrival, the Powercor crew found that the owner was doing some digging on his new house, still under construction, and made contact with the low voltage consumer mains resulting in damage to the conduit and cable. There was no ground fire. There were no reported injuries or other party property damages. | Customer installation | 2 | 2 | 2 |  | SA011 | digging near u/g service | No Go Zone (contact) | 23/07/2016 13:11 |  |  | 2703 | Residential |  | 20160802PWA_07 | Infrastructure (network-based) | -37.7184 | 144.74 | 1 | Powercor | Report | 3512 | 0.019184 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Taylors Hill | Dug up
On arrival crew isolated supply and commenced repairs | 19 MOONAH STREET, RED CLIFFS VIC 3496 | 33109198 |  | Lightning |  |  |  |  | 1 | Vic Fire Comms reports a transformer on fire at intersection of Avocat Avenue and Moonah St Red Cliffs. Crew attended and found ACR Transformer on fire. CFA assisted in extinguishing fire. No shock, injuries or third party damage. No ground fire. | ACR/OCR;Transformer | 2 | 1 | 2 |  | RCT023 | Storm conditions, ACR supply transformer ignited after lightning activity. Fire contained to oil within small transformer tank | Plant/equipment | 25/07/2016 20:40 | 1 | Negligible: no ground fire | 2711 | Agricultural |  | 20160804PWA_01 | Infrastructure (network-based) | -34.2908 | 142.1854 | 1 | Powercor | Report | 8072 | 0.038231 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | AF Other
on arrival crew isolated supply and commenced repairs | 1695 COLAC-LAVERS HILL ROAD, KAWARREN VIC 3249 | 30054670 |  | Alive;Fallen;MEC |  |  |  |  | 1 | Customers reported tree had brought a conductor down at the incident location. On arrival the crew found that a tree (from outside the clearance space) had fallen across an adjacent HV conductor, causing the conductor to come into contact with the LV conductors below, resulting in a High Voltage Injection affecting approximately 5 installations. Protection operated. There was no ground fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | wind storm | HV injection;Loss of supply | 23/07/2016 6:47 |  |  | 2712 | Agricultural |  | 20160804PWA_02 | Infrastructure (network-based) | -38.4903 | 143.5695 | 1 | Powercor | Report | 3522 | 0.025108 | 22kV AC | Ballarat Aerodrome | 3249 | Kawarren | Trees
X-arm and insulators replaced under EAP. | 440 STATION STREET, LALOR VIC 3075 | 911897 |  |  |  | Leakage |  |  | 2 | IMS 223367. Replaced HV X-arm which burnt due to tracking of conductor to X-arm. Fire restricted to end insulator and X-arm. No other damage. | Crossarm (wood) | 0 | 2 | 0 |  | epg31 | Tracking of conductor to crossarm. | Pole-top fire | 42408.7083 | 1 | Negligible: no ground fire | 2720 | Residential |  | 20160805SPN_01 | Infrastructure (network-based) | -37.6656 | 145.018 | 1 | AusNet Services Distribution | Report | 3538 | 0.031606 | 22kV AC | Essendon Airport | 3075 | Lalor | Crossarm
The service has been disconnected from the pole and removed by the faults crew. | 7 ANGUS AVENUE, ALTONA NORTH VIC 3025 | 31023902 | Unauthorised work |  |  |  |  | Phase to earth | 2 | A contractor for UAG assets reported that he received an electric shock from a cover guard installed on the pole outside the incident location. It has been determined that persons working for a demolition company demolished the house cut the service and left the service rolled up near the cover guard on the pole which has public access. Emmanuel Paris (UAG Assets) has contacted the live cover guard with his hand and received an electric shock. | Service conductor | 2 | 2 | 2 |  | BLT030 | Demolition company demolished the house cut the service and left the service rolled up near the cover guard on the pole which has public access. | Minor shock | 42498.3861 |  |  | 2729 | Roadway |  | 20160808PWA_02 | Infrastructure (network-based) | -37.8376 | 144.8563 | 1 | Powercor | Report | 3562 | 0.017117 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
Fault crew attended, tree branch over HV conductors, HV injection in residents in Heathwood street, meters changed to affected residents. | 39 HEATHWOOD STREET, RINGWOOD EAST VIC 3135 |  |  | Fallen | [5 empty] | IMS 223503. Tree Branch on HV Conductors at this location. HVI on CCT Lynwood Heathwood Substation caused DFA to operate opening RW092. | Conductor (bare) | 0 | 0 | 0 |  | rwt22 | Vegetation: Trees Incident | HV injection | 42559.4479 |  |  | 2727 | Residential |  | 20160808SPN_01 | Infrastructure (network-based) | -37.8211 | 145.2577 | 1 | AusNet Services Distribution | Report | 3551 | 0.031664 | 22kV AC | Moorabbin Airport | 3135 | Ringwood East | Trees
Reported to ESV and requested officer to attend. No immediate safety risk at time. Advice received and arrangements subsequently made to have unauthorized objects removed | 90 ST ALBANS ROAD, THOMSON VIC 3219 | 30309740 | Building too close or within the No Go Zone | [5 empty] | 2 | MEC crew identified orange conduit and bunting fitted to low voltage service cable abutting building site. This had been installed without MEC's knowledge. | Service conductor | 0 | 0 | 0 |  | GTSGLE1 | Interference with Network assets | No Go Zone (contact) | 42621 |  |  | 2749 | Construction |  | 20160815PWA_02 | Infrastructure (network-based) | -38.1668 | 144.3746 | 1 | Powercor | Report | 12076 | 0.034556 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Thomson | Other
On 27 July 2016, supply was disconnected to assist police with their activities. | 6 KALIMNA COURT, CLIFTON SPRINGS VIC 3222 |  | Unauthorised work | [5 empty] | 2 | Powercor undertook some investigation of a report that people in unmarked vehicles and in plain clothes had performed work on the pole and property. It was identified that persons unknown had attached a two wire aerial service line around an existing two wire aerial service line to form a 4 wire supply and connected this to a new point of supply. There was no fire, injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  |  | Illegal wiring by persons unknown | Damage to network assets | 21/07/2016 0:00 |  |  | 2760 | Residential |  | 20160818PWA_02 | Infrastructure (network-based) | -38.1581 | 144.5516 | 1 | Powercor | Report | 3721 | 0.017946 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | Other
On arrival crew isolated supply and commenced repairs | DEPOT ROAD, KOROIT VIC 3282 | 30143188 | Vehicle | [5 empty] | 1 | A representative of the Moyne Shire reported that one of their trucks had pulled down a wire, on arrival the crew found that a large tipper truck had been dumping gravel on a road surface in the fully raised position, when the top of the tipper contacted a 22kV HV conductor. The truck was moving at the time of contact, and had travelled approx. 20 metres before the driver realized he had contacted the conductor, and the conductor had broken and fallen to the ground. There were visible scorch marks on the gravel road surface, however there was no fire. There were no injuries, and the protection operated. | Conductor (bare) | 2 | 2 | 2 |  | KRT013 | Tip truck struck conductor | Loss of supply;No Go Zone (contact) | 17/08/2016 13:18 |  |  | 2768 | Roadway |  | 20160819PWA_01 | Infrastructure (network-based) | -38.2675 | 142.3718 | 1 | Powercor | Report | 3627 | 0.012181 | 22kV AC | Warrnambool Airport Ndb | 3282 | Koroit | Vehicle
Supply was disconnected by the crew and the service was removed. | 55 MCDOUGALL STREET, GEELONG WEST VIC 3218 | 32080717 |  |  |  | Rot;Fault on customer installation |  |  | 2 | A Registered Electrical Contractor (Steven Wates 0408 800 221) called to say a painter had removed the Fuse Mains Junction Box from the fascia at the incident location. The crew attended and confirmed that the Fuse Mains Junction Box had been removed from the fascia and was being held in the air by the consumer mains. | Connection box | 2 | 2 | 2 |  | GL022 | Mounting screws failed to hold junction box onto deteriorated fascia, when bumped during sanding of fascia. | Loss of supply | 29/07/2016 14:52 |  |  | 2772 | Residential |  | 20160819PWA_03 | Infrastructure (network-based) | -38.1374 | 144.3381 | 1 | Powercor | Report | 8041 | 0.031856 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Other
CEOT dispatched a fault crew to make safe, investigate and repair. Officer Attended site on the 7/7/16 and took photos of burnt out lantern on pole 1221996. As per photos the lantern is burnt out completely. Aside for the lantern, no damage has been caused to any property or the nature strip below. | 138 RAILWAY AVENUE, RINGWOOD EAST VIC 3135 | 1221996 |  |  |  | Unknown technical factor |  |  | 2 | IMS 222834. Customer reported that a street light globe located outside their house was burning/smouldering. | Public lighting | 0 | 0 | 0 |  | rwt32 | Photos captured but no cause identified. | Other electricity related | 42528.9451 | 1 | Negligible: no ground fire | 2556 | Public space |  | 20160707SPN_01 | Infrastructure (network-based) | -37.8109 | 145.2549 | 1 | AusNet Services Distribution | Report | 3557 | 0.025841 | Low voltage AC (<1kV) | Moorabbin Airport | 3135 | Ringwood East | AF Other
On arrival crew commenced repairs | 281 KINGSTON-NEWLYN ROAD, NEWLYN VIC 3364 | 30002575 | Theft | [5 empty] | 2 | Employees reported missing earth cable at the incident location. There was no fire, injuries or third party property damage | Earth/earthing | 0 | 0 | 0 |  | BAN009 | Copper cable theft | Less than $50k damage | 42467.5153 |  |  | 2567 | Roadway |  | 20160708PWA_04 | Infrastructure (network-based) | -37.3867 | 143.9798 | 1 | Powercor | Report | 3339 | 0.016763 | Earthing cable | Ballarat Aerodrome | 3364 | Newlyn | Other
On arrival crew undertook repairs | 100-102 THACKER STREET, OCEAN GROVE VIC 3226 | 30153472 |  | Within clearances |  |  |  |  | 2 | A tree cutter brought down a service cable at the incident location. On arrival the Powercor crew found that the cable lying on the ground and also damaged to the customerâ€™s fuse board. There was no fire or injuries. | Service conductor | 0 | 0 | 0 |  | DDL011 | Vegetation: Trees Incident | Loss of supply | 42467.5611 |  |  | 2573 | Residential |  | 20160711PWA_01 | Infrastructure (network-based) | -38.2552 | 144.5143 | 1 | Powercor | Report | 3346 | 0.0054433 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Other
On arrival crew isolated supply. Repairs were made to the damaged conductor and supply was restored. | 149 LAMBERT STREET, ARARAT VIC 3377 | 33051807 |  | Wind;Fallen |  |  |  |  | 1 | During extremely strong winds a large tree fell and contacted the road side HV conductors at incident location. The impact broke the Copper HV conductor causing it to come to rest on the ground and against the LV conductors below. Protection operated as expected. The other end of the broken HV conductor remained alive via back-feed through down-stream transformers. An LEI was called to inspected several premises adjacent to the incident site to check for a possible HVI, no damage was found. There was no ground fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | ART034 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42650.9021 |  |  | 2580 | Roadway |  | 20160712PWA_02 | Infrastructure (network-based) | -37.2681 | 142.9192 | 1 | Powercor | Report | 3353 | 0.0091759 | 22kV AC | Ballarat Aerodrome | 3377 | Ararat | Trees
On arrival crew isolated supply and carried out repairs | 866 CHALLICUM ROAD, BUANGOR VIC 3375 | 30005619 |  |  |  | Corrosion;Overheated connection |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a low voltage junction box mounted on Challicum 1 wooden SWER s/s pole had burnt through and required replacement. There was no ground fire or reported injuries. There was no third party property damage. | Pole (wood);Connection box | 2 | 2 | 2 |  | BAS011 | corrosion | Pole-top fire;Loss of supply | 15/07/2016 4:39 | 1 | Negligible: no ground fire | 2596 | Agricultural |  | 20160715PWA_04 | Infrastructure (network-based) | -37.4139 | 143.1291 | 1 | Powercor | Report | 3371 | 0.026904 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3375 | Buangor | Pole
A faults crew attended and the MFB were not in attendance with traffic control arranged due to the location. Supply was disconnected to the lantern and a further trouble order was created to replace the defective 150w HPS lantern. | 196 TENNYSON STREET, ELWOOD VIC 3184 | 2305522 |  |  |  | Overheated connection |  |  | 2 | MFB reports street light on fire. A 150w HPS lantern on pole No. 2305522 located outside 196 Tennyson Street, Elwood caught fire and was extinguished by the MFB. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown. | Pole-top fire | 42466.5208 | 1 | Negligible: no ground fire | 2595 | Roadway |  | 20160715UTD_01 | Infrastructure (network-based) | -37.882 | 144.9923 | 1 | United Energy Distribution | Report | 3370 | 0.01156 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | AF Other
The crew made the flex safe by removing the live line clamp from the top circuit and notified the United Energy Control Centre, ZNX and their supervisor. An investigation commenced. | 50 CENTRAL PARK ROAD, MALVERN EAST VIC 3145 | [5 empty] | Poor workmanship |  | 2 | A ZNX subcontractor (Prasinus) G&B crew were to replace a HV intermediate crossarm by Glove and Barrier method over a HV tee-off. A Prasinus live line work crew were working outside 50 Central Park Road, Malvern on 11kV feeder CFD16 near "Nott-Central Park" substation and inadvertently dropped a HV conductor. They had disconnected the blue phase (footpath side) HV tee-off flex and installed a bridging hopper to maintain supply. They proceeded to lift the conductor into position on the G&B 'Y' arm and secured it in the trap. The crew then moved to the red phase (road side top circuit) conductor to relocate it to the 'Y' arm. They thought the tee-off flex might be long enough to move the top conductor without disconnecting the tee-off or using a hopper. As they lifted the red phase conductor, the tee-off flex slipped out of the 'D' type split bolt connectors and hung uncontrolled. There were no injuries and the only customers impacted were approximately 59 customers supplied from "Nott-Central Park" substation with reports of dim lights. | Conductor (bare) | 0 | 0 | 0 |  | CFD 16 | As the G&B crew lifted the red phase HV conductor, the tee-off flex slipped out of the 'D' type split bolt connectors and hung uncontrolled. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/07/2016 10:12 |  |  | 2600 |  |  | 20160718UTD_01 | Infrastructure (network-based) | -37.8687 | 145.046 | 1 | United Energy Distribution | Report | 3568 | 0.0067674 | 11kV AC | Moorabbin Airport | 3145 | Malvern East | Other
On arrival crew confirmed electrical isolations. | 123 GARSED STREET, BENDIGO VIC 3550 | 32053963 | Unauthorised work | [5 empty] | 2 | A crew attended a disused factory site found that the indoor transformer, associated switchgear and wiring has been removed from site by persons unknown. The supply to the transformer had been isolated when the factory closed down. There was no ground fire start. No protection operated. There were no reported injuries or ground fire start. | Equipment | 2 | 2 | 2 |  | BGO011 | unauthorised removal of electrical equipment | Interference with electrical assets;Other | 15/07/2016 12:22 |  |  | 2617 | Industrial |  | 20160721PWA_01 | Infrastructure (network-based) | -36.7666 | 144.2777 | 1 | Powercor | Report | 3396 | 0.032168 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3550 | Bendigo | Other
On arrival crew isolated supply and carried out repairs | 55 DEVONSHIRE ROAD, SUNSHINE VIC 3020 | 31025021 |  |  |  | Corrosion |  |  | 2 | A customer reported that a service has caught fire and the fire self-extinguished at the incident location. On Investigation it has been established that there was no fire (arcing only), the service having faulted at a point half a meter from the building. There was no ground fire, injuries or third party property damage. There was no fire, | Service conductor;Neutral screen | 2 | 2 | 2 |  | SSE013 | Service line failure | Loss of supply | 21/07/2016 9:16 |  |  | 2619 | Residential |  | 20160721PWA_03 | Infrastructure (network-based) | -37.7851 | 144.8355 | 1 | Powercor | Report | 3413 | 0.008441 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the Pole Top Connection Box and the O/Head Service Cable and completed an NST test which confirmed a Pass result. | 3 BALMORAL STREET, PORTLAND VIC 3305 | 30094936 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Dawn Orchard received an electric shock while she was showering in the bathroom, when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. | Connection box | 2 | 2 | 2 |  | PLD006 | Corroded connection in pole top connection box | Minor shock | 23/06/2016 7:30 |  |  | 2623 | Roadway |  | 20160721PWA_06 | Infrastructure (network-based) | -38.3606 | 141.5991 | 1 | Powercor | Report | 3402 | 0.022919 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | UNIT 10 70 QUEEN STREET, ALTONA VIC 3018 | 30103614 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Agnieska Nowak was showering when she received an electric shock as she made simultaneous contact with her hands between the shower taps and the wet shower base. | Service conductor;Neutral screen | 2 | 2 | 2 |  | AL014 | The corrosion of the O/H Service Cable was the result of water entering the outer sheath via a small perforation, the cause of which was unable to be determined. | Minor shock | 16/06/2016 14:30 |  |  | 2656 | Residential |  | 20160726PWA_04 | Infrastructure (network-based) | -37.8706 | 144.8357 | 1 | Powercor | Report | 3450 | 0.0282 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | OH Cable
Jemena crew attended, made the site safe by removing the chain from the overhead conductors and restored supply. | 21 RESERVE STREET, PRESTON VIC 3072 | 930630 | Vandalism | [5 empty] | 1 | There was a reported supply interruption on Reserve St Preston, 10 Customers were off supply. Jemena crews found chain over the Low Voltage conductors. | Conductor (bare) | 0 | 0 | 0 |  |  | Incident was due to Vandalism by third party. Wilful act by unknown person, a chain was thrown onto the Low Voltage conductor. | Loss of supply | 28/07/2016 5:47 |  |  | 2669 | Industrial |  | 20160728JEM_02 | Infrastructure (network-based) | -37.7534 | 145.0259 | 1 | Jemena | Report | 3652 | 0.030214 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
On arrival crew isolated supply and commenced repairs | 183 MOUTRAYS ROAD, CODRINGTON VIC 3285 | 32131614 |  | Lightning |  |  |  |  | 1 | A field crew attending an outage found that a lightning strike had caused a flashover on a 12.7kV pole, causing a 12.7kV conductor to break and fall to ground and damaging the transformer, resulting in a High Voltage Injection affecting 2 installations. Protection operated. There was no ground fire. There were no reported injuries | SWER conductor;Pole mounted | 2 | 1 | 2 |  | PLD001 | Lightning strike | HV injection;Loss of supply;Damage to network assets | 22/07/2016 0:10 |  |  | 2702 | Agricultural |  | 20160802PWA_06 | Infrastructure (network-based) | -38.2397 | 141.9248 | 1 | Powercor | Report | 3520 | 0.0085532 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3285 | Codrington | Lightning
On arrival crew carried out repairs, which included carrying out bird mitigation works on the structure. | 20 FLOCKHART STREET, MOUNT PLEASANT VIC 3350 | 33005053 |  | Bird |  |  |  |  | 1 | A field crew attending an outage found that a crow had caused a flashover on a 22kV pole, resulting in a High Voltage Injection affecting approximately 3 installations. Protection operated. There was no ground fire. There were no reported injuries. | Boric acid;Pole (concrete) | 2 | 2 | 2 |  | BAS013 | Bird Incident | HV injection;Loss of supply | 29/07/2016 17:32 |  |  | 2704 | Roadway |  | 20160802PWA_08 | Infrastructure (network-based) | -37.5856 | 143.8538 | 1 | Powercor | Report | 3592 | 0.029186 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Mount Pleasant | Animal
On arrival crew isolated supply and issued a defect notice. | 12 SEVENTH AVENUE, ALTONA NORTH VIC 3025 | 32167747 |  |  |  | Overheated connection |  |  | 2 | The MFB reported a fuse box fire at the incident location. On arrival the Powercor crew found that apparently the connections into an LV Service Fuse Base, inside the customerâ€™s switchboard, had overheated and caused a small fire. The fire was contained to a small area in the switchboard, damaging the fuses and connections. The crew isolated supply and issued a defect notice for repair. | Switchboard;Customer installation | 2 | 2 | 2 |  | BLT030 | overheating at switchboard | Property | 24/07/2016 16:58 | 0 | Negligible: no ground fire | 2705 | Residential |  | 20160803PWA_01 | Infrastructure (network-based) | -37.8442 | 144.8473 | 1 | Powercor | Report | 3514 | 0.02474 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Fuse
On arrival crew isolated supply and commenced repairs. pole subsequently changed | DARTMOOR STATE SCHOOL, 76 GREENHAM STREET, DARTMOOR VIC 3304 | 30089503 |  | Precipitation |  | Leakage;Not built/maintained to design |  |  | 2 | A customer reported a small fire at the top of a pole. On arrival the attending crew found that a fire had burnt and significantly damaged substation pole Dartmoor town 18. There was no evidence of ground fire identifiable. There were no reported injuries. | Pole (wood);Outdoor | 2 | 2 | 2 |  | PLD003 | Poor clearance between cable termination and pole step iron | Pole-top fire | 24/07/2016 18:32 | 1 | Negligible: no ground fire | 2706 | Roadway |  | 20160803PWA_02 | Infrastructure (network-based) | -37.9228 | 141.2765 | 1 | Powercor | Report | 3584 | 0.0088229 | 22kV AC | Portland (Cashmore Airport) | 3304 | Dartmoor | Pole
On arrival crew isolated supply and commenced repairs | 500 COLAC-LAVERS HILL ROAD, BARONGAROOK WEST VIC 3249 | 30055437 |  | Wind;Alive;Fallen |  |  |  |  | 1 | Vicfire reported a wire down across the road at this location. On arrival the attending crew found that a SWER conductor had been contacted by a tree and subsequently entangled in a passing truck. Protection operated. There was no fire or injuries reported. The SWER line was left isolated overnight until repairs could be undertaken. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | Vegetation: Trees Incident | Loss of supply | 25/07/2016 16:24 |  |  | 2714 | Roadway |  | 20160804PWA_03 | Infrastructure (network-based) | -38.4108 | 143.5837 | 1 | Powercor | Report | 3524 | 0.037863 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3249 | Barongarook West | Trees
The site was made safe, and electrical inspector was sent out onsite and testing of the premise was conducted, customers were reconnected to supply once damage was repaired. | 297 PASCOE VALE ROAD, ESSENDON VIC 3040 | a143232 | Vehicle |  |  | HV injection |  | Phase to phase | 1 | A car and a light truck travelling along Pascoe Vale Road were involved in a collision causing the truck to collide with a Jemena owned power pole. As a result the pole suffered extensive damage and dislodged the overhead 11kV conductors which made contact with the 415V Low Voltage conductors. The resultant High Voltage injection caused minor property damage to four properties. | Conductor (bare) | 0 | 0 | 0 |  | NS8 | Due to the collision between a car and a light truck, the truck veered out of control and slammed into a Jemena owned power pole. | HV injection;Loss of supply | 42529.9639 |  |  | 2724 | Residential |  | 20160807JEM_01 | Infrastructure (network-based) | -37.7463 | 144.9255 | 1 | Jemena | Report | 3572 | 0.0015289 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3040 | Essendon | Vehicle
11/08/2016 - Downer actioned a Work Order to install a â€œTemporary in Permanentâ€ Meter Installation and to abolish the supply to a builders supply pole. 12/08/2016 - The builder was removing the temporary single phase builders supply pole after the supply to the residential premise was connected yesterday. The builders supply pole was removed and placed on the ground via a backhoe and the builder tried to recover the consumers mains by pulling them up from the ground, but they didn't come out. The builder did not know that the cables were still connected in the pit and assumed they were jammed so he proceeded to cut the cables. The builder cut the neutral cable first without incident and then attempted to cut the active cable, but as soon as he cut through the insulation and the cutters contacted the copper wire, he received a minor shock and dropped the cutters. He received an electric shock to his hand as he was cutting the supply cables whilst squatting on the wet ground. The builder went to the local medical centre for a precautionary ECG which proved clear. | 82 MARINE DRIVE, SAFETY BEACH VIC 3936 | [5 empty] | Not followed;Incorrect electrical isolation and/or permits | Phase to earth | 2 | Caller advised the premise has a builders supply pole and the builder was trying to remove it and received an electric shock when he cut the cable. They believe the builders pole must not have been disconnected properly yesterday by the crew. | Services cable;Customer installation | 0 | 0 | 0 |  |  | A faults truck and LEI attended and commenced an investigation to the cause. Initial voltage tests to an independent earth revealed the supply to the builders supply pole had not been disconnected from the pit with 230v measured. It was quickly discovered the meter had been removed and the service fuse left in. The faults crew disconnected the consumers mains from the pit and removed the conductors from the pit to make the installation safe. Downer management was advised, attended the site and an investigation commenced. The investigation found the following sequence of events led to the builder receiving the electric shock: â€¢ The electrical supply is underground and supplied from an electrical pit in the footpath on the property boundary â€¢ The single phase cable from the pit to the builders supply pole and the three phase consumers mains cable from the pit to the 'Temporary in Permanent' meter location were installed by the builders REC â€¢ The Downer crew attending the site were an Qualified Line Worker and a 3rd Year Apprentice â€¢ The crew firstly undertook confirmation checks on the three phase consumers mains cable between the meter location and the pit to ensure the consumers mains had been installed correctly by the REC and were continuous â€¢ The Qualified Line Worker was at the meter location â€“ the Apprentice was at the pit â€“ and the cable was confirmed as being correct â€¢ The Qualified Line Worker then walked back to the pit to supervise the Apprentice in making the 4 connections (3 x phase + neutral) to the pit connectors â€¢ The Qualified Line Worker looked over the Apprentice as he made the connections whilst at the same time providing pedestrian traffic control as the underground pit was in a busy location â€¢ The Apprentice completed the work as instructed â€¢ The Qualified Line Worker failed to undertake a final check of the Apprentices work The practice at this point would be for the crew to disconnect the single phase and neutral cables (Builders Supply Pole cables) that were installed in 2 of the 4 pit connectors. Whilst this is not written on the Work Order for the project, a residential premise can only have the single point of supply connected â€“ a fact known by the Qualified Line Worker and not expected to be known by the Apprentice (and was not directed by the Qualified Line Worker to be completed). Had the Qualified Line Worker physically checked the Apprentices work he would have seen that two cables were still connected. â€¢ The crew then went to the new three phase meter location and undertook final tests â€¢ The cables were confirmed as correct and the crew installed the fuses and sealed the meter â€¢ The Qualified Line Worker then directed the Apprentice to remove the meter from the temporary builders supply pole â€¢ The Apprentice removed the fuses and therefore isolated everything â€œupstreamâ€ from such to safely remove the meter and tested at the meter to confirm isolation â€¢ The Apprentice then removed the meter â€¢ The Qualified Line Worker tested the conductors in the meter enclosure after the Apprentice had removed the meter and confirmed the metering conductors as dead â€¢ However, the Qualified Line Worker failed to test the supply side of the fuse base in the meter enclosure The crew packed up the site and went on to the next job. | Minor shock;Medical attention (first aid/doctor/hospital) | 42712.3229 |  |  | 2747 | Residential |  | 20160814UTD_01 | Infrastructure (network-based) | -38.3197 | 144.9864 | 1 | United Energy Distribution | Report | 3789 | 0.013938 | Low voltage AC (<1kV) | Moorabbin Airport | 3936 | Safety Beach | Other
Reported to ESV and requested officer to attend. No immediate safety risk at time. Advice received and arrangements subsequently made to have unauthorized objects removed | 6 PERTH STREET, BELMONT VIC 3216 | 30068576 | Building too close or within the No Go Zone | [5 empty] | 2 | MEC crew identified orange conduit and bunting fitted to low voltage service cable abutting building site. This had been installed without MEC's knowledge. | Service conductor | 0 | 0 | 0 |  | GCY023 | Interference with Network assets | No Go Zone (contact) | 42621.4167 |  |  | 2748 | Construction |  | 20160815PWA_01 | Infrastructure (network-based) | -38.1775 | 144.3468 | 1 | Powercor | Report | 12066 | 0.030384 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Other
Isolated section and made safe. | 84-90 JONES ROAD, BROOKLYN VIC 3012 | A089155 | Blown detritus |  |  | Leakage |  |  | 2 | Pole top fire on tee off pole to Jones Rd, it appears a plastic bag has got around an insulator and the cross arm strap and aerial guy wire and then proceeded to track to the Optus catenary wire on the same pole. A portion of the pole has burnt through and will require a pole change. | Pole (wood) | 0 | 0 | 0 |  | TH22 | Airborne debris caused tracking which in turn caused the pole to catch fire. | Pole-top fire | 19/08/2016 4:10 | 1 | Negligible: no ground fire | 2781 | Industrial |  | 20160819JEM_02 | Infrastructure (network-based) | -37.8151 | 144.8331 | 1 | Jemena | Report | 8275 | 0.028472 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | Other
On arrival crew isolated supply and commenced repairs. | CARNGHAM, 2121 DARLINGTON-CARRANBALLAC ROAD, PURA PURA VIC 3271 | 30045678 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A customer reported that he had struck a service cable with his tractor and the wire had broken and was laying on the ground at the incident location. On arrival the crew found that a tractor had contacted and broken the service cable between the substation and the house. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | CDN006 | Tractor hit service line | Loss of supply | 42408.5292 |  |  | 2770 | Agricultural |  | 20160819PWA_02 | Infrastructure (network-based) | -37.822 | 143.0807 | 1 | Powercor | Report | 3630 | 0.013839 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3271 | Pura Pura | Vehicle
A faults crew attended removed the melted wiring and installed new cabling to the 150w HPS lantern. | 114 BAY ROAD, SANDRINGHAM VIC 3191 | 1822914 |  |  |  | Overheated connection |  |  | 2 | Caller is reporting that across the road a pole has a fire on it but its now stopped. Looks like a wire has melted up the pole but they have full power. The conductors to a 150w HPS lantern on pole No. LIS 1822914 located outside 114 Bay Road caught fire and self extinguished. The cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown. | Pole-top fire | 42681.7014 | 1 | Negligible: no ground fire | 2766 | Roadway |  | 20160819UTD_01 | Infrastructure (network-based) | -37.9529 | 145.0117 | 1 | United Energy Distribution | Report | 3625 | 0.034773 | Low voltage AC (<1kV) | Moorabbin Airport | 3191 | Sandringham | AF Other
Jemena fault crew arrived and cut away the old service and made safe. | 40 PEARSON CRESCENT, COOLAROO VIC 3048 |  | Unauthorised work | [5 empty] | 2 | Fault crew found an live service had been wrapped around the base of pole# A065223 by persons unknown some time ago (grass had grown over the service). A Yarra Valley water crew assumed this wire was a Telstra wire and the excavator has clipped the service with bucket causing a flash, no shock, no injury, no fire | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Excavator clipped the service with bucket of a live service that had been wrapped around the base of pole by unknown person/s. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/08/2016 3:08 |  |  | 2785 |  |  | 20160821JEM_02 | Infrastructure (network-based) | -37.6577 | 144.9311 | 1 | Jemena | Report | 3660 | 0.00024884 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Coolaroo | Other
crew attended and replaced connection. | 96 HIGH STREET, TERANG VIC 3264 | 30042402 |  |  |  | Overheated connection |  |  | 1 | CFA reported pole fire at the incident location. On arrival the crew found that a low voltage connection had overheated and caught fire resulting in damage to the connector. There was no ground fire. There were no reported injuries. | Connector/termination | 0 | 0 | 0 |  | TRG004 | Overheated LVIPC connector | Pole-top fire;Loss of supply | 42590.3896 | 1 | Negligible: no ground fire | 2788 | Commercial |  | 20160822PWA_02 | Infrastructure (network-based) | -38.2406 | 142.9157 | 1 | Powercor | Report | 12071 | 0.00062153 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3264 | Terang | Connection
Supply was isolated, repairs were carried out and the site was made safe. Customer was reconnected and supply was restored. | 17 NORTH CRESCENT, HEIDELBERG WEST VIC 3081 |  |  |  |  | Overheated connection |  |  | 1 | MFB reported fire at fuse box. Appears fuse has heated up causing the tubing to catch fire and in-turn causing fascia to catch fire. Crew and inspector advised asset failure. | Connector/termination | 0 | 0 | 0 |  |  | Investigations found that the incoming service active conductor had over heated and caught fire causing localised damage to the customer's two point connection box and weather boards. The fire appeared to be the result of a loose connection in the mains box on the incoming service active. The attending LEI tested the consumer mains which were clear. The linesman fitted a new porcelain fuse mains box and re-terminated the service after cleaning the customer's junction box, removing the carbonisation caused by the fire. The installation passed all required tests performed by the linesmen and supply was restored to the installation. | Property | 23/08/2016 21:22 | 1 | Negligible: no ground fire | 2796 | Residential |  | 20160824JEM_01 | Infrastructure (customer connection) | -37.7401 | 145.0443 | 1 | Jemena | Report | 8276 | 0.0078507 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg West | Connection
The crew replaced the stolen earths with new earths | 1587 DOHERTYS ROAD, MOUNT COTTRELL VIC 3024 | 30118075 | Copper theft | [5 empty] | 2 | Powercor contact centre received a report of stolen copper earths at the incident location. On arrival the fault crew found that the low and high voltage earths had been stolen from the pole type substation. There was no ground fire and no injury as a result of this incident. | Pole mounted | 0 | 0 | 0 |  | WBE032 | interference - theft | Damage to network assets | 42682.4167 |  |  | 2804 | Roadway |  | 20160825PWA_01 | Infrastructure (network-based) | -37.8122 | 144.624 | 1 | Powercor | Report | 3686 | 0.014575 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
Switching undertaken to leave damaged section isolated and restore customers. Excavation and cable repairs programmed | 26 RIVERVIEW DRIVE, KIALLA VIC 3631 | 30230262 | Working too close to underground cables | [5 empty] | 1 | A customer rang to advise that they had struck a U/G cable while boring to install a water tapping in Honeysuckle Dr off Riverview Dr, Kialla. A crew attended but was unable to repair the cable. Switching undertaken to leave damaged section isolated and restore customers. There were no reported injuries, fire or third party damage. | Cable | 0 | 0 | 0 |  | MNA024 | Interference - underground cable struck by horizontal bore | Loss of supply | 25/08/2016 10:13 |  |  | 2809 | Residential |  | 20160825PWA_06 | Infrastructure (network-based) | -36.4088 | 145.3903 | 1 | Powercor | Report | 3717 | 0.014059 | 22kV AC | Shepparton Airport | 3631 | Kialla | Dug up
Crew attended and made safe, New service cable to be installed | 240 NORMANBY ROAD, SOUTH MELBOURNE VIC 3205 | 30167002 | Vehicle | [5 empty] | 2 | Fire Brigade (MFB) reported that a truck hit a pole and wire hanging low at the incident location. Upon arrival, the attending crew found that a lighting service hit by the truck and the service hanging low. There were no reported injuries, third party property damage or fire. | Service conductor | 0 | 0 | 0 |  | MG009 | Vehicle impact | Loss of supply;Damage to network assets | 18/08/2016 10:58 |  |  | 2814 | Commercial |  | 20160826PWA_02 | Infrastructure (network-based) | -37.8289 | 144.948 | 1 | CitiPower | Report | 3696 | 0.024096 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Vehicle
Power supply to effected area was isolated and made safe, a temporary fence was set-up and permanent repairs to fix the indoor substation is to follow. | 1 LYTTON STREET, GLENROY VIC 3046 |  | Vehicle | [5 empty] | 1 | Around 3:30pm on Monday 29th of August a 52 year old man drove his car into a Jemena owned indoor substation, the man is believed to have been intoxicated at the time of the incident. The incident temporarily impacted 100 customers and supply has now been restored. | Indoor | 0 | 0 | 0 |  | PV 31 | 52 year old man drove his vehicle into Jemena owned substation. It is believed the man was intoxicated and mistook the accelerator for the break. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/08/2016 15:30 |  |  | 2826 | Public space |  | 20160829JEM_01 | Infrastructure (network-based) | -37.7052 | 144.9152 | 1 | Jemena | Report | 3725 | 0.039593 | 11kV AC | Essendon Airport | 3046 | Glenroy | Vehicle
Fault isolated, fault truck dispatched, fire brigade on site, fire extinguished, under investigation. Joint replaced. | 11 ALPINE STREET, WARBURTON VIC 3799 |  |  |  |  | Electrical breakdown |  | Phase to earth | 1 | IMS 223925. HVABC joint failed in Alpine St, Warburton. Report received of fire on the ground. DAO advised. Failure occurred during REFCL testing. Note to Greg Sieburn: Report attached as per request. | Conductor (ABC) | 0 | 0 | 0 |  | wyk023 | HV electrical connection deterioration failed under REFCL testing. | Grassfire | 25/08/2016 15:03 | 1 | Small: 10 - 1000 sq.m | 2820 | National/state park |  | 20160829SPN_01 | Infrastructure (network-based) | -37.757 | 145.6842 | 1 | AusNet Services Distribution | Report | 3903 | 0.021272 | 22kV AC | Moorabbin Airport | 3799 | Warburton | OH Cable
On arrival crew isolated supply and commenced repairs | 47-69 SWANN DRIVE, DERRIMUT VIC 3030 | 30152797 | Copper theft | [5 empty] | 2 | An Employee found an earth stolen from the substation at the incident location. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | SU013 | cable theft | Damage to network assets | 26/08/2016 12:34 |  |  | 2835 | Roadway |  | 20160830PWA_04 | Infrastructure (network-based) | -37.8019 | 144.7762 | 1 | Powercor | Report | 3735 | 0.03712 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply | 172 FYANS STREET, SOUTH GEELONG VIC 3220 | 30061327 | Unauthorised work | [5 empty] | 2 | A customer, advised a meter box attached to building at the incident location was relocated approximately two weeks ago. People working from next door have advised him they have seen sparks coming from where the building was previously located. Upon arrival it was discovered the customerâ€™s meter board and meter had been removed. The incoming customers service cable was found to be alive. No protection operated There was no ground fire, injuries or third party property damage. | Customer installation | 2 | 2 | 2 |  | GLE033 | Removal of meter position and meter by persons unknown | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/08/2016 7:24 |  |  | 2861 | Residential |  | 20160905PWA_03 | Infrastructure (network-based) | -38.1654 | 144.3663 | 1 | Powercor | Report | 3768 | 0.034241 | Low voltage AC (<1kV) | Avalon Airport | 3220 | South Geelong | Other
Site Supervisor informed that the scaffold was in vicinity of HV/LV. As Visual Warning Devices are installed a PTW #47110 was issued. Advised shutdown will be required to remove scaffold. | 188 WHITEHORSE ROAD, BALWYN VIC 3103 | 30175201 | Building too close or within the No Go Zone | [5 empty] | 2 | At incident site (Jersey st frontage) a scaffold ( Stairwell) was erected approximately 3000mm from HV/LV, there was no Permit To Work Issued. A Permit To Work had been on issue for approximately 12 months prior for mobile plant use. Site supervisor advised scaffold was in the vicinity of HV/LV and that a shutdown will be required to dismantle the scaffold. As of 1/9/16 scaffold was observed to have been removed there was no shutdown or Permit To Work Issued. | Conductor (bare) | 2 | 2 | 2 |  | L010 | Scaffold erected and removed with no PTW issued or shutdown applied for | No Go Zone (no contact) | 42409.3528 |  |  | 2862 | Construction |  | 20160905PWA_04 | Infrastructure (network-based) | -37.8124 | 145.0759 | 1 | CitiPower | Report | 3769 | 0.040094 | 11kV AC | Moorabbin Airport | 3103 | Balwyn | Other
Crew attended, excavated and resealed cable | 388-396 ELIZABETH STREET, MELBOURNE VIC 3000 | 118464030 | Building too close or within the No Go Zone;Working too close to underground cables | [5 empty] | 2 | A contractor installing a new telecommunications connection to 388 Elizabeth St reported a loud bang while non destructive digging (NDD) was being undertaken. On arrival the crew found that a section of cable that previously serviced the subject address (capped & sealed) had been damaged. A section of one core had melted indicating some arcing. | Services cable | 0 | 0 | 0 |  | MP066 | Excavation in vicinity of cabling | Damage to network assets | 13/08/2016 12:30 |  |  | 2870 | Commercial |  | 20160906PWA_06 | Infrastructure (network-based) | -37.8096 | 144.9613 | 1 | CitiPower | Report | 3780 | 0.031661 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
CEOT dispatched a fault crew to attend and the crew found a HV fuse hung up and candled fuse tube. The fuse and fuse tube were replaced and the incident resolved in Fusion with the following comments: Candling 6a PF, 1ph sub, conc pole, no animal proofing, lis 5217235.Fault Crew made safe. Customer's supply restored. | 15 OLD BARNAWARTHA ROAD, WEST WODONGA VIC 3690 | 5217235 |  |  |  | Age;Corrosion;Electrical breakdown;Fuse failed to eject |  |  | 2 | IMS 224089. Fault crew advised of Candling HV PF fuse at COCHRANES ROAD s/s Lis 5217235. Data Management Team raised an incident with the following remarks: "Meters 4420657 (#15 OLD BARNY RD), 4746388 (APT MANAGEMENT - COCHRANES RD) & 4628428 (RAIL) have volts dropping to 130V since 2/9/16. Remake all connections that are common to all properties. NST Req. Note that Street Lighting does not appear affected." | EDO fuse | 0 | 0 | 0 |  | wo13 | Candled Powder Filled HV Fuse. | Pole-top fire | 42499.2743 | 1 | Negligible: no ground fire | 2869 | Residential |  | 20160906SPN_02 | Infrastructure (network-based) | -36.1011 | 146.8256 | 1 | AusNet Services Distribution | Report | 7921 | 0.040117 | 22kV AC | Wangaratta Aero | 3690 | West Wodonga | Fuse
Area isolated and earths replaced. | 18 BLANDFORD STREET, WEST FOOTSCRAY VIC 3012 |  | Copper theft | [5 empty] | 2 | Six metres of 70m2 Bare copper was stolen by unknown parties from Transformer 'Blandford â€“ Essex' Substation. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown party stole 6m of bare copper cable from Jemena Pole substation. | Damage to network assets | 42560.6951 |  |  | 2881 | Public space |  | 20160907JEM_02 | Infrastructure (network-based) | -37.7938 | 144.8775 | 1 | Jemena | Report | 3793 | 0.0058391 | Earthing cable | Essendon Airport | 3012 | West Footscray | Other
On arrival crew isolated supply. REC repaired customers underground service cable | 180 SEVENTH STREET, MILDURA VIC 3500 | 32143513 | Working too close to underground cables | [5 empty] | 2 | A customer reported that a bobcat had struck an underground cable. Crew attended and found that a bobcat had excavated and struck a neighbours consumer mains cable and it had been exposed. There was no fire, no shock or injuries. | Customer installation | 2 | 2 | 2 |  | MBN022 | excavation on customers property | No Go Zone (contact) | 30/08/2016 18:30 |  |  | 2875 | Residential |  | 20160907PWA_02 | Infrastructure (network-based) | -34.179 | 142.1593 | 1 | Powercor | Report | 3785 | 0.029554 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Dug up
On arrival crew confirmed isolations and initiated environmental cleanup. | 285 AVALON ROAD, AVALON VIC 3212 | 32068690 | Vandalism;Copper theft | [5 empty] | 2 | A customer reported someone stole a transformer from pole and oil soaked in ground at the incident location. Upon arrival, the Powercor fault crew found the leads had been cut and the transformer was knocked off of its platform, dismantled on the ground and the copper windings were taken. The HV was still alive with one fuse blown at the tee off. Corio Police have taken a report and some hand tools found at the site for analysis. No reported injuries or fire | Transformer | 2 | 1 | 2 |  | FNS032 | criminal activity | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42469.7167 |  |  | 2877 | Agricultural |  | 20160907PWA_04 | Infrastructure (network-based) | -38.07 | 144.4252 | 1 | Powercor | Report | 3787 | 0.01067 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3212 | Avalon | Other
A faults crew attended and isolated supply to the three occupancies and they proceeded to replace the damaged three phase FMJB. All underground cable connections were re-terminated before supply was restored. | 330 CENTRE ROAD, LANGWARRIN VIC 3910 | 3301085 |  |  |  | Overheated connection |  |  | 2 | Customer at 330 Centre Road, Langwarrin reports of a fire on the pole outside the property. A three phase FMJB at service pole No. LIS 3301085 located outside 330 Centre Road, Langwarrin caught on fire and self extinguished prior to the faults crew attending. The FMJB supplied three customers via an underground cable and the cause was a probable loose connection. | Cable;Connection box | 0 | 0 | 0 |  |  | The cause was a probable loose connection. | Pole-top fire | 42499.9583 | 1 | Negligible: no ground fire | 2873 | Roadway |  | 20160907UTD_01 | Infrastructure (network-based) | -38.1695 | 145.2048 | 1 | United Energy Distribution | Report | 3783 | 0.040218 | Low voltage AC (<1kV) | Moorabbin Airport | 3910 | Langwarrin | Pole
Crew attended and reinstated service cable, fitted visual warning devices to cabling. Photographs taken and requested site attendance by ESV | 29 LITTLE CRUIKSHANK STREET, PORT MELBOURNE VIC 3207 | 30203321 | Building too close or within the No Go Zone;Unauthorised work | [5 empty] | 2 | A customer reported no supply. On arrival, the attending CitiPower crew found that an aerial service line supplying 29 Lt Cruickshank st and 3 street lights had been removed. A building was under construction in close vicinity to where this service line was. | Service conductor | 0 | 0 | 0 |  | AP014 | Interference by unknown third party | Loss of supply;No Go Zone (contact) | 42530.7917 |  |  | 2886 | Residential |  | 20160909PWA_01 | Infrastructure (network-based) | -37.8398 | 144.9462 | 1 | CitiPower | Report | 12585 | 0.026743 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 1.5 Volts no load to 34 Volts maximum load. Service Crew performed NST test of the service conductor at the POA with a fail result recorded. Service crew replaced the existing N/S service, found to be damaged, with a new ABC aerial service, and performed NST with pass result recorded. | 27 MERLIN CRESCENT, CORIO VIC 3214 | 32083315 |  |  |  | Corrosion |  | Phase to earth | 2 | Peter was standing at the bathroom basin when he received a minor shock through his hands, whilst touching the tap with his right hand and left hand under the running water. N/S service was damaged at the attachment to the Powercor pole. Sheath was damaged exposing neutral screen to the elements. No obvious cause for damage to sheath. | Service conductor;Neutral screen | 2 | 2 | 2 |  | FNS011 | Damaged service cable insulation allowing neutral screen to corrode. | Minor shock | 13/08/2016 15:00 |  |  | 2897 | Residential |  | 20160913PWA_05 | Infrastructure (network-based) | -38.0681 | 144.3575 | 1 | Powercor | Report | 3810 | 0.0050116 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | OH Cable
On arrival crew confirmed safety of the site and arranged temporary locking and security of the site. | 1-15 RATHDOWNE STREET, CARLTON VIC 3053 | CP0011219 | Copper theft | [5 empty] | 2 | A customer reported a copper theft at the incident location. Upon arrival, the fault crew found that the damaged two substationsâ€™ door locks and also approx. 5m of abandoned main service cable from each substation had been stolen. There were no witnesses to the incident. There were no reported injuries or fire. | Customer installation | 2 | 2 | 2 |  | WA023 | Theft of customers mains cables | Less than $50k damage | 42622.4944 |  |  | 2907 | Commercial |  | 20160914PWA_04 | Infrastructure (network-based) | -37.8069 | 144.9686 | 1 | CitiPower | Report | 3821 | 0.023225 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Other
On arrival crew isolated supply and carried out repairs | 23 GAWLER STREET, PORTLAND VIC 3305 | 31017540 |  | Within clearances |  |  |  |  | 2 | A tree cutting crew called to say that they were cutting trees for the council and had clipped a service line. On arrival the crew found that the tree cutting crew had contacted the 2 wire neutral screen service with a saw, causing the service to break and fall. As the service is only short, neither end of the service reached the ground. No third party damage, fire or injuries. | Service conductor | 2 | 2 | 2 |  | PLD004 | Vegetation: Trees Incident | Loss of supply | 42713.3604 |  |  | 2912 | Roadway |  | 20160915PWA_03 | Infrastructure (network-based) | -38.3507 | 141.6042 | 1 | Powercor | Report | 3826 | 0.011755 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Other
On arrival crew isolated supply and carried out repairs | 17 ARCADIA DOWNS DRIVE, KIALLA VIC 3631 | 33096154 |  |  |  | Corrosion |  |  | 2 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. | Connection box | 2 | 2 | 2 |  | MNA024 | connection failure | Pole-top fire | 42683.0444 | 1 | Negligible: no ground fire | 2915 | Roadway |  | 20160916PWA_01 | Infrastructure (network-based) | -36.4415 | 145.3626 | 1 | Powercor | Report | 3830 | 0.026752 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Kialla | Pole
Site was made safe and substation earths were replaced. | 213 GEELONG ROAD, KINGSVILLE VIC 3012 | A051880 | Copper theft | [5 empty] | 2 | Unknown person(s) stole approximately 6 metres of Copper from pole substation Geelong-Queensville pole number A051880. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown person(s) stole approximately 6m of copper from Jemena substation Geelong-Queensville. | Damage to network assets | 18/09/2016 6:15 |  |  | 2920 |  |  | 20160919JEM_01 | Infrastructure (network-based) | -37.8038 | 144.8839 | 1 | Jemena | Report | 5010 | 0.022301 | 22kV AC | Essendon Airport | 3012 | Kingsville | Other
On arrival crew carried out repairs. | 20 GRANVIA CIRCUIT, BURNSIDE VIC 3023 | 30336447 | Working too close to underground cables | [5 empty] | 2 | A contractor reported an auger had disturbed UG cable at the incident location. Upon arrival, the Powercor crew noticed an excavator auger had drilled several holes over the UG LV cable path. The cable conduit was damaged and the concrete slab exposed. There was no outage reported. There was no evidence of injuries or fire. | Cable | 2 | 2 | 2 |  | SU022 | contractor using auger about LV cable | No Go Zone (contact);Damage to network assets | 15/09/2016 8:56 |  |  | 2928 | Roadway |  | 20160921PWA_01 | Infrastructure (network-based) | -37.7468 | 144.7509 | 1 | Powercor | Report | 3849 | 0.022416 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Burnside | Dug up
On Arrival crew confirmed condition of cable and re-instated site | 402-448 LEAKES ROAD, PLUMPTON VIC 3335 | 32173386 | Vandalism | [5 empty] | 2 | A customer advised an underground pit opened and the cable pulled out at the incident location. Upon arrival, The Powercor fault crew found that the pit lid had been opened and the live service cable pulled out by using a rope. No damage to the cable or pit found. | Services cable | 2 | 2 | 2 |  | MLN021 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/09/2016 15:01 |  |  | 2944 | Roadway |  | 20160922PWA_07 | Infrastructure (network-based) | -37.6756 | 144.6624 | 1 | Powercor | Report | 3866 | 0.0014155 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | MELALEUCA DRIVE, CLARINDA VIC 3169 | 8804614 |  | Animal |  | HV injection |  |  | 1 | At 0116hrs on 26/09/2016, 22kV feeder CDA 23 circuit breaker reclosed to lockout affecting 4798 customers. A possum at "Melaleuca-Centre" pole type substation caused the HV conductors to fall to the ground from the HV/LV tee-off pole and a high voltage injection was suspected to customers supplied from the north circuit of "Melaleuca-Centre" substation. It appeared that fault current caused an ampact connection to fail on the tee-off pole and a construction crew were required to replace a bay of aluminium conductor. A LEI attended and confirmed that a high voltage injection occurred (CLA 1603) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium;Pole mounted | 0 | 0 | 0 |  | CDA23 | Highly likely that fault current caused an HV connection to fail on the tee-off pole to teh pole type substation. | HV injection;Loss of supply | 26/09/2016 1:16 |  |  | 2958 | Roadway |  | 20160926UTD_01 | Infrastructure (network-based) | -37.9271 | 145.1067 | 1 | United Energy Distribution | Report | 3884 | 0.019708 | 22kV AC | Moorabbin Airport | 3169 | Clarinda | Animal
On arrival crew isolated supply and carried out repairs. | 96 TUCKER STREET, BREAKWATER VIC 3219 | 33040421 |  |  |  | Unknown technical factor |  |  | 2 | A customer reported a pole fire at the incident location. Upon arrival, the Powercor crew found that a FSD had ignited, the fire self-extinguished. There were no injuries or ground fire. | Connection box | 2 | 2 | 2 |  | GLE012 | Unable to determine direct cause due to damage | Pole-top fire | 23/09/2016 9:07 | 1 | Negligible: no ground fire | 2965 | Roadway |  | 20160927PWA_01 | Infrastructure (network-based) | -38.1843 | 144.3663 | 1 | Powercor | Report | 3897 | 0.0174 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Breakwater | Pole
CEOT dispatched a fault crew to make safe and investigate. The HV conductors showed no signs of damage. The fault crew had to replace a 25E Boric Acid Fuse at WL 436. | 166 RHODES ROAD, DARNUM VIC 3822 | 2706009 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | Whilst undertaking road upgrade works, a tip truck, operated by Downer Roads, came close to a 22kV overhead conductor which caused a flashover. An AusNet Services' fault crew attended and was advised that the Downer truck driver had his tipper parallel to the line and that caused the flashover. The closest pole is CAMM 2706009, with the HV conductors measuring 6.8m to ground at the point of contact being outside 166 Rhodes Road, Darnum. The site contact was Cain O'Neill from Downer Roads, his mobile phone number is 0427 289284.Electrical protection operated - 25E Boric Acid Fuse at WL 436. There were no injuries to any persons. | Conductor (bare) | 0 | 0 | 0 |  | wgl24 | Tipper truck tray came too close overhead HV conductor. | No Go Zone (contact) | 26/09/2016 11:38 |  |  | 2966 | Roadway |  | 20160927SPN_01 | Infrastructure (network-based) | -38.1738 | 145.9879 | 1 | AusNet Services Distribution | Report | 3899 | 0.036671 | 22kV AC | Morwell (Latrobe Valley Airport) | 3822 | Darnum | Other
The faults crew made the site safe and replaced the three phase overhead service that went over the Road along with the three phase FOLCB that supplied the underground cable. In addition, the wiring to a 250w HPS and 80w MV lantern was damaged and both were required to be re-wired. The faults crew took photos of the damaged infrastructure following the pole fire. | 3080 FRANKSTON-FLINDERS ROAD, BALNARRING VIC 3926 | 1108209 |  |  |  | Overheated connection |  |  | 2 | The CFA report lines are sparking on a pole in Frankston-Flinders Road on the Flinders side of the shopping centre. The CFA were in attendance at a service pole (LIS No. 1108209) located opposite 3080 Frankston-Flinders Road, Balnarring. The three phase FOLCB and single and three phase overhead services were damaged following a pole fire starting that damaged a pole mounted junction box and underground service cable that supplied 3080 Frankston-Flinders Road. | Service conductor;Services cable;Aluminium twisted (grey);Connection box;Public lighting | 0 | 0 | 0 |  |  | The cause was a probable loose, overheated connection. | Pole-top fire | 25/09/2016 19:45 | 1 | Localised: less than 10 sq.m | 2964 | Roadway |  | 20160927UTD_01 | Infrastructure (network-based) | -38.3737 | 145.1214 | 1 | United Energy Distribution | Report | 3896 | 0.00072338 | Low voltage AC (<1kV) | Moorabbin Airport | 3080 | Balnarring | Pole
The crew disconnected and replaced the damaged service cable. | 34 LEVENIA STREET, ST ALBANS VIC 3021 | 30106825 | Working too close to overhead lines | Within clearances |  |  |  |  | 2 | A Customer, reported that the the service wire was cut in half with a chain saw at the incident location. Upon arrival the crew had discovered that the neutral screened service cable at the incident location was cut in half by a hand held hedge trimmer whilst undertaking tree trimming works. There were no reported shockâ€™s, injuries, fire or third party damage. | Service conductor | 2 | 2 | 2 |  | SU012 | Customer clearing vegetation | Loss of supply;No Go Zone (contact) | 25/09/2016 16:37 |  |  | 2976 | Residential |  | 20160929PWA_01 | Infrastructure (network-based) | -37.7556 | 144.801 | 1 | Powercor | Report | 3918 | 0.0047326 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Other
CEOT dispatched a Fault crew and an investigation officer (LEI) to isolate, make safe and investigate. The attending service crew had isolated the supply due to the tree still over power lines and suspect HVI, awaiting support from LEI to asses damage. Waited for attendance of tree clearers to remove tree. Attending LEI inspected affected properties on Mt Dandenong Rd, Liverpool Rd and Church St and found evidence of HV injection on Blue Phase. No-Access letters left for unattended installations and report of damage report left with re-connected owners. CEOT, Lend Lease and Select Solutions notified of meter changes required and premises still left off supply. | 14 LIVERPOOL ROAD, KILSYTH VIC 3137 | 1004485 |  | Fallen |  |  |  |  | 1 | IMS 224592. A tree located on the road reserve fell onto open bare 22kV/415V conductors out the front of 14 Liverpool Rd, Kilsyth. Feeder CB tripped. | Conductor (bare) | 0 | 0 | 0 |  | cpk22 | Vegetation: Trees Incident | HV injection | 42410.4528 |  |  | 2983 | Roadway |  | 20161003SPN_04 | Infrastructure (network-based) | -37.8039 | 145.3145 | 1 | AusNet Services Distribution | Report | 3930 | 0.023854 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3137 | Kilsyth | Trees
Crew attended, isolated and replaced earthing | 4 IRAMOO CIRCUIT, ROCKBANK VIC 3335 | 30107812 | Copper theft | [5 empty] | 2 | A customer reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that the earthing cable on the substation pole had been stolen. There were no reported injuries or fire. | Earth/earthing | 0 | 0 | 0 |  | MLN011 | interference | Damage to network assets | 29/09/2016 9:57 |  |  | 3001 | Residential |  | 20161007PWA_04 | Infrastructure (network-based) | -37.7329 | 144.6277 | 1 | Powercor | Report | 3951 | 0.027841 | 22kV AC | Laverton Raaf | 3335 | Rockbank | Other
Site made safe, repaired HV O/H conductor and connection. | 25-49 CRAIG STREET, SPOTSWOOD VIC 3015 |  |  | Bird |  |  |  |  | 1 | Bird managed to get accross the high voltage fuse units which caused a fault on the high voltage conductor. Due to the high voltage voltage fault, caused the ampact connector to fail which resulted in conductor falling on the ground. Conductor was de-energised. | Conductor (bare) | 0 | 0 | 0 |  | NT 10 | Bird Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42592.2757 |  |  | 3002 | Roadway |  | 20161008JEM_01 | Infrastructure (network-based) | -37.8323 | 144.8909 | 1 | Jemena | Report | 5115 | 0.030866 | 22kV AC | Essendon Airport | 3015 | Spotswood | Animal
Site isolated, tree branch removed and supply restored. | 104 VIEW STREET, GLENROY VIC 3046 |  |  | Wind |  | HV injection |  |  | 2 | Due to storms and high winds,a large tree fell, severing all 3 phase HV conductors which inturn contacted the LV conductors causing a HVI. No major damages were reported and supply was restored. | Conductor (bare) | 0 | 0 | 0 |  | PV13 | Vegetation: Trees Incident | HV injection | 42592.6729 |  |  | 3004 | Residential |  | 20161010JEM_02 | Infrastructure (network-based) | -37.6959 | 144.9268 | 1 | Jemena | Report | 5098 | 0.018109 | 11kV AC | Essendon Airport | 3046 | Glenroy | Trees
Crew patrolled line removed tree and undertook repairs to conductor. LEI attended and identified premises with appliance damage | 5 DOODTS ROAD, BLACK HILL VIC 3350 | 30001526 |  | Wind;Fallen |  |  |  |  | 1 | A customer reported a tree had fallen onto power lines at the incident location. On arrival the crew found that a tree (from outside the clearance space) had fallen across an adjacent 22kV conductor causing a 22kV conductor to come into contact with an LV conductor below, resulting in a High Voltage Injection affecting 3 installations. Protection operated. There was no ground fire. There were no reported injuries or shocks. | Conductor (bare) | 0 | 0 | 0 |  | BAN015 | Vegetation: Trees Incident | HV injection;Loss of supply | 42439.4889 |  |  | 3006 | Residential |  | 20161010PWA_01 | Infrastructure (network-based) | -37.5448 | 143.878 | 1 | Powercor | Report | 3956 | 0.03858 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Black Hill | Trees
CEOT dispatched a fault crew to isolate supply and make safe. CEOT also dispatched a LEI to investigate and check for HVI damage. Traffic Management on-site and the road was closed. The LEI confirmed HV Injection had occurred to customers' installations. Once the Fault crew complete repairs, the LEIs were required to reconnect customers and issue Customer Advice Forms to those customers who had damage sustained to their property from the incident. | 11 OAKTREE ROAD, CROYDON NORTH VIC 3136 | 1214601 |  | Wind;Fallen |  | HV injection |  | Phase to phase | 1 | IMS 224668. A large tree located on the Road Reserve on the intersection of Hawthorne Way & Oaktree Rd, Croydon North, fell over onto open bare 22kV/400V conductors. This caused: the Feeder protection to trip, HV & LV Lines were damaged, poles & crossarms were damaged, and metering was damaged. The tree fell due to high wind gusts at the time and the ground being very wet from recent rain. | Smart meter;Customer installation | 0 | 0 | 0 |  | cpk21 | Vegetation: Trees Incident | HV injection | 42623.5903 |  |  | 3016 | Residential |  | 20161010SPN_02 | Infrastructure (network-based) | -37.7819 | 145.2827 | 1 | AusNet Services Distribution | Report | 5175 | 0.0059502 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3136 | Croydon North | Trees
CEOT dispatched a fault crew to isolate supply and make safe. CEOT dispatched an AusNet Services' LEI to investigate the incident. The LEI also found there had been a fire at the Fused Mains Box at pole LIS 921845. The LEI confirmed that a HV Injection had occurred to customers' installations. Once the fault crew complete repairs, the LEIs were required to reconnect customers and issue Customer Advice Forms to those customers who had sustained damage to their property from the incident. | 700 MAIN ROAD, ELTHAM VIC 3095 |  |  | Precipitation;Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 224666. CEOT received INCD for "all supply failures" to GB1847. Large tree located on parkland opposite 674 Main Rd, Eltham, fell over onto open bare 22kV/400V conductors. This caused the feeder protection to trip. The tree fell due to high wind gusts at the time and the ground being very wet from recent rain. SES had closed off the footpath in the parkland where the tree fell. In addition, a FOLCB caught fire at pole LIS 921845 but it was extinguished and no ground fire occurred. | Conductor (bare);Any other type | 0 | 0 | 0 |  | elm34 | Vegetation: Trees Incident | HV injection;Other electricity related | 42623.6215 | 1 | Negligible: no ground fire | 3019 | Roadway |  | 20161010SPN_04 | Infrastructure (network-based) | -37.7244 | 145.1465 | 1 | AusNet Services Distribution | Report | 3973 | 0.031186 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3095 | Eltham | Trees
The EWP and hydraulic saw were tagged out of service and sent to EPV for testing. The Taylors employee sought medical treatment and a clearance to resume normal duties. United Energy has no records of this event in the outage system and therefore assume that Taylors Tree Services hasnâ€™t notified UE of the electric shock event. If United Energy had been advised, due process would have occurred with an Inspector sent to complete an investigation report and ESV advised. | 5 ROSEMORE ROAD, ROSEBUD VIC 3939 |  |  | Council |  |  |  | Phase to earth | 2 | Taylors Tree and Stump Removal employee received an electric shock whilst tree cutting for unknown persons / authorities. Whilst pruning vegetation in close proximity of the LV overhead conductors from a EWP, a Taylors employee received an electric shock to his left hand as he was using an insulated pole saw handle. Apparently the pole saw become energised when it contacted LV conductors as he was cutting branches that were entangled in the conductors. ESV were advised of a work place incident by Taylors Tree and Stump Removal that occurred on 19/05/2016 involving vegetation clearing contractors and no report had been received from United Energy. United Energy were advised of the event by ESV on 10/10/2016. | Conductor (bare) | 0 | 0 | 0 |  |  | The employee received an electric shock to his left hand as he was using an insulated pole saw handle when the pole saw contacted LV conductors. | Minor shock;Medical attention (first aid/doctor/hospital) | 19/08/2016 9:45 |  |  | 3021 | Roadway |  | 20161011UTD_01 | Infrastructure (network-based) | -38.3538 | 144.9199 | 2 | United Energy Distribution | Report | 3975 | 0.035159 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Other
Crew attended, isolated and undertook repairs. LEI attended and did not find any evidence of HV injection damage. | 90 REFINERY ROAD, CORIO VIC 3214 | 30268929 | Vehicle |  |  | Leakage |  |  | 2 | CFA reported wire crossing roadway on fire. Upon arrival, the Powercor fault crew found a car had hit the pole and left the scene. The centre phase HV conductor tie had broken and the HV was resting on the x-arm. The LV x-arm had burnt through at the neutral pin and broken off. No reported injuries or ground fire. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | FNS021 | Traffic accident dislodged HV conductor | Pole-top fire;Loss of supply;Damage to network assets | 42531.8368 | 1 | Negligible: no ground fire | 3032 | Roadway |  | 20161012PWA_05 | Infrastructure (network-based) | -38.0708 | 144.3897 | 1 | Powercor | Report | 8391 | 0.016878 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3214 | Corio | Vehicle
CEOT dispatched a fault crew to isolate, make safe and repair. Replaced Krone LV fuse box. | 101 WONGA ROAD, MILLGROVE VIC 3799 |  |  |  |  | Corrosion |  |  | 2 | IMS 224695. Small fire in vicinity at base of pole, Krone LV fuse box melted on substation pole caused by a loose LV connection on LV leads to Krone fuse box. | Connection box | 0 | 0 | 0 |  |  | Loose connection / corrosion on line side of LV Krone fuse box on pole. | Grassfire | 42714.1424 | 1 | Localised: less than 10 sq.m | 3023 | Residential |  | 20161012SPN_01 | Infrastructure (network-based) | -37.7461 | 145.6536 | 1 | AusNet Services Distribution | Report | 7951 | 0.019233 | Low voltage AC (<1kV) | Moorabbin Airport | 3799 | Millgrove | Connection
Crew attended and repaired conductor. | 12 SHADBUSH COURT, TRUGANINA VIC 3029 | 30275707 |  |  |  | Unknown technical factor |  |  | 1 | A customer reported a detached conductor sitting on the roof of their house at the incident location. The crew attended and confirmed that a High Voltage conductor had broken and was resting on the roof of the house. Minor damage to the fascia and a down pipe was evident following the incident. An electrical inspector inspected the area around the incident location and could not find evidence of High Voltage Injection to installations. | Conductor (bare) | 0 | 0 | 0 |  | LV003 | Not found, probable downstream fault | Less than $50k damage | 42653.4868 |  |  | 4038 | Residential |  | 20161013PWA_04 | Infrastructure (network-based) | -37.8371 | 144.7173 | 1 | Powercor | Report | 5278 | 0.0032477 | 22kV AC | Laverton Raaf | 3029 | Truganina | Conductor
The faults crew assessed the electrical infrastructure for any damage following the fault and completed a patrol of the feeder for any further faults with the supply outage lasting for a duration of 1 hour and 3 minutes. A follow up email was sent to arrange for animal proofing of the pole type substation structure. | 25 VIRGINIA STREET, SPRINGVALE VIC 3171 | 635790 |  | Bird |  |  |  |  | 1 | At 1623hrs on 09/07/2016, 22kV ACR DN8232 located in Springvale Road on feeder SV32 reclosed to lockout affecting 270 customers. Magpies had been constructing a birds nest made of bits of wire on the dressing down crossarm at "Virginia-Wales pole type substation at pole number LIS 0635790 located opposite 25 Virginia Street. It appears the wires in the birds nest flashed over that caused the local ACR to reclose to lockout and a small fire to start in rubbish at the base of the substation pole. The pole is located outside the Springvale Special Development School and the small grass fire had been extinguished prior to the faults crew arrival. | Pole top;Equipment | 0 | 0 | 0 |  | SV 32 | Bird Incident | Loss of supply;Grassfire | 42620.6826 | 1 | Localised: less than 10 sq.m | 2572 | Residential |  | 20160711UTD_01 | Infrastructure (network-based) | -37.9474 | 145.1562 | 1 | United Energy Distribution | Report | 3559 | 0.029517 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Animal
The crew reported the incident to their supervisor and a faults crew were dispatched to disconnect the LV supply at the Indoor substation. They tested the pillar to ensure it was de-energised and covered the LV pillar and made the site safe. They completed a hazard report and provided a copy to their supervisor including a photo (attached). | 40 PRINCES HIGHWAY, EUMEMMERRING VIC 3177 |  | Theft | [5 empty] | 2 | A Downer crew were dispatched to an abolishment of supply to an old McDonalds store at the rear of the Caltex Petrol Station. The crew was not able to locate the meter and it was suspected it had been removed by a Meter Provider or had been stolen. They checked at the rear of the premise and found a live LV pillar that was left exposed/uncovered after a suspected copper theft by unknown persons at the vacant premise. | LV Pillar;Customer installation | 0 | 0 | 0 |  |  | Possible copper theft attempt. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42558.7083 |  |  | 2583 | Commercial |  | 20160713UTD_01 | Infrastructure (network-based) | -38.0017 | 145.2385 | 1 | United Energy Distribution | Report | 3356 | 0.0086042 | Low voltage AC (<1kV) | Moorabbin Airport | 3177 | Eumemmerring | Other
On Arrival Crew isolated supply | 255 PHALPS ROAD, LARPENT VIC 3249 | 30233475 | Vehicle | [5 empty] | 2 | On arrival the crews found a truck had been struck by a diesel passenger train at a level crossing. The side tarpaulins of the truck had struck and remained attached to an overhead HV line. The overhead conductors remained aloft and isolation of the line / tarpaulin was required prior to emergency services being able to attend to approximately 100 persons trapped in the train. There was no ground fire or electrical related injuries. | Conductor (bare) | 0 | 0 | 0 |  | CLC004 | Truck struck by a diesel passenger train | Loss of supply | 13/07/2016 15:48 |  |  | 2588 | Roadway |  | 20160714PWA_01 | Infrastructure (network-based) | -38.3654 | 143.4717 | 1 | Powercor | Report | 3363 | 0.025421 | 22kV AC | Ballarat Aerodrome | 3249 | Larpent | Vehicle
On arrival crew isolated supply and replaced all three fuses. | 2575 MURRAY VALLEY HIGHWAY, COBRAM EAST VIC 3644 | 32182471 |  |  |  | Moisture ingress |  |  | 2 | Customer reported sparking transformer at the incident location (50m West of Dairy Paddock Lane). On arrival the crew found that a Boric Acid HV fuse had candled, the fuse remained in the carrier intact. There was no ground fire, reported injuries or damage to third party property. | Boric acid | 2 | 2 | 2 |  | CME014 | Candling fuse | Loss of supply;Plant/equipment | 15/07/2016 20:00 | 1 | Negligible: no ground fire | 2605 | Roadway |  | 20160719PWA_01 | Infrastructure (network-based) | -35.9782 | 145.741 | 1 | Powercor | Report | 8388 | 0.00038657 | 22kV AC | Shepparton Airport | 3644 | Cobram East | Fuse
On arrival crew checked service connections and carried out repairs | 1 NIGRETTA COURT, POINT LONSDALE VIC 3225 | 32080139 |  |  |  | Neutral fault |  | Phase to earth | 2 | Customer was standing in the shower and received tingles to her right hand when she turned the cold shower tap on and off. | Service conductor;Connection box | 2 | 2 | 2 |  | DDL012 | Loose neutral connections in POA FOLCB | Minor shock | 42710.375 |  |  | 2618 | Residential |  | 20160721PWA_02 | Infrastructure (customer connection) | -38.271 | 144.62 | 1 | Powercor | Report | 3397 | 0.02665 | Low voltage AC (<1kV) | Avalon Airport | 3225 | Point Lonsdale | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, did not identify any defective electrical wiring or equipment within the installation. The attending Powercor Fault Crew checked the condition of all connections between the Distribution Transformer and the Point of Attachment (POA) of the installation. | 1 RUSSELL STREET, GORDON VIC 3345 | 31001760 |  |  |  | Out of balance load |  | Phase to phase | 2 | Mr Andrew Parke was showering when he received an electric shock as he made simultaneous contact between his hand on the metal shower taps and his bare feet while standing on the wet shower base. | Customer installation | 2 | 2 | 2 |  | BAN011 | Potential load imbalance at the Transformer requiring referral to the Supply Quality Group for further investigation. | Minor shock | 30/05/2016 17:30 |  |  | 2620 | Residential |  | 20160721PWA_04 | Infrastructure (network-based) | -37.586 | 144.1013 | 1 | Powercor | Report | 3399 | 0.034218 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3345 | Gordon | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the customers FOLCB, causing a higher than normal impedance within the neutral circuit. | 5 WANWIN STREET N, DARTMOOR VIC 3304 | 33058657 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Heather Prior received an electric shock while she was showering in the bathroom, when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. | Service conductor;Connector/termination | 2 | 2 | 2 |  | PLD003 | Corroded O/H Service Neutral Conductor termination at the customers FOLCB. | Minor shock | 42711.3958 |  |  | 2627 | Residential |  | 20160722PWA_03 | Infrastructure (customer connection) | -37.9228 | 141.2709 | 1 | Powercor | Report | 12111 | 0.028705 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3304 | Dartmoor | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole. | 9 JUBILEE STREET, INVERLEIGH VIC 3321 | 33040217 |  |  |  | Corrosion |  | Phase to earth | 2 | Miss Victoria Zakelj was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet while standing on the wet shower base. | Service conductor;Aluminium twisted (grey) | 2 | 2 | 2 |  | WIN013 | Corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole. | Minor shock | 15/05/2016 20:00 |  |  | 2628 | Roadway |  | 20160722PWA_04 | Infrastructure (network-based) | -38.1065 | 144.057 | 1 | Powercor | Report | 3415 | 0.0358 | Low voltage AC (<1kV) | Avalon Airport | 3321 | Inverleigh | Connection
AusNet Services crew began patrol approximately 8:30am. Report came through that a truck had made contact with conductors in Church Street. The Crew arrived to find the truck parked on the north side of the road, away from conductors and the driver on the phone, attempting to call the faults number again. An assessment of the situation found no injuries to persons, distribution assets or the truck. The truck driver was interviewed and details were exchanged. Once safe to restore supply at 9:06am, HV network was restored to normal by CEOT via remote control. At 9:55 3 x 315 Amp LV fuses were replaced in the high school indoor type sub station. | MILLER HOMES, UNIT 1 76-80 CHURCH STREET, BENALLA VIC 3672 | 3900297 | Vehicle |  |  |  |  | Phase to phase | 1 | IMS 222979. Truck travelling west along Church Street with truck bin lid in the upright position made contact with the live low voltage conductors between poles 3900296 and 3900297 in church street. The force of the contact caused the poles to shake. Due to the shaking, both the low voltage and high voltage conductors clashed - resulting in a prolonged loss of supply to a section of the BN004 Feeder within the bridge, Smith Church and Barkley street area of Benalla. | Conductor (bare) | 0 | 2 | 0 |  | BN4 | Garbage truck was travelling with bin lid in upright position which made contact with the Live LV conductors. | HV injection;Loss of supply | 15/07/2016 8:30 |  |  | 2640 | Commercial |  | 20160725SPN_01 | Infrastructure (network-based) | -36.5484 | 145.9896 | 1 | AusNet Services Distribution | Report | 3569 | 0.016214 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3672 | Benalla | Vehicle
Fire brigade extinguished the fire. Fault crew dispatched. No apparent damage to assets. | UNIT 1 83 MARSHALLS ROAD, TRARALGON VIC 3844 | 2607388 |  | Bird | Highly unlikely |  |  |  | 2 | IMS 222995. Burnt grass are identified at the base of switch TN212 in road reserve. Danny Reid said that they removed wire from the top of the switch which it seemed a bird has used to make a nest. | Disconnector/isolator | 0 | 2 | 0 |  | TGN11 | Bird Incident | Grassfire | 16/07/2016 16:23 | 1 | Small: 10 - 1000 sq.m | 2643 | Industrial |  | 20160725SPN_02 | Infrastructure (network-based) | -38.1795 | 146.5535 | 1 | AusNet Services Distribution | Report | 11227 | 0.033157 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Animal
Isolated HV and LV S/S on arrival. Then rectified the fault by removing the tree and resagging LV cable. | 3 FERRIERS ROAD, LOCH VIC 3945 | 2006199 |  | Fallen |  |  |  |  | 0 | IMS 223195. Under INCD-112498-r tree on ground on top of LV between LIS #2006199 & #2006198. No LV fuses blown @ TX. ie LV was still alive. | Conductor (bare) | 0 | 0 | 0 |  | llg12 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/07/2016 14:38 |  |  | 2663 | Agricultural |  | 20160727SPN_01 | Infrastructure (network-based) | -38.364 | 145.7105 | 1 | AusNet Services Distribution | Report | 3466 | 0.0031597 | Low voltage AC (<1kV) | Moorabbin Airport | 3945 | Loch | Trees
Jemena crew attended, made the site safe by removing the chain from the overhead conductors and restored supply. | 2 REX STREET, PRESTON VIC 3072 |  | Vandalism |  |  |  |  | Three phase | 1 | There was a reported supply interruption on Rex St Preston, 19 Customers were off supply. Jemena crews found chain over the Low Voltage conductors. | Conductor (bare) | 0 | 0 | 0 |  | EP41 | Incident was due to Vandalism by third party. Wilful act by unknown person, a chain was thrown onto the Low Voltage conductor. | Loss of supply | 28/07/2016 7:10 |  |  | 2667 | Industrial |  | 20160728JEM_01 | Infrastructure (network-based) | -37.7493 | 145.0292 | 1 | Jemena | Report | 3470 | 0.016338 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the â€œburnt outâ€ Pole Type Connection Box and reterminated the existing Twisted O/H Service Cable and completed an NST Test, which confirmed a Pass result. | 356 LESTERS ROAD, ASCOT VIC 3364 | 32005154 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Colleen Gilles received an electric shock while she was washing dishes in the kitchen sink when she made simultaneous contact with her hands between the kitchen taps and the metallic kitchen sink. | Connection box | 2 | 2 | 2 |  | BAN006 | Corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole | Minor shock | 42557.3438 |  |  | 2671 | Roadway |  | 20160728PWA_01 | Infrastructure (network-based) | -37.3805 | 143.7855 | 1 | Powercor | Report | 3474 | 0.023328 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3364 | Ascot | Connection
Operator was dispatched to the incident site and the high voltage fuse units at 'T' off pole supplying property was isolated. | BUNTING ROAD, BROOKLYN VIC 3012 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | Excavator made contact with the overhead aerial earth, on attempting to dislodge the cable the excavator arm made contact with the high voltage overhead conductor, jamming the conductor onto the excavator arm. | Conductor (bare) | 2 | 0 | 0 |  | TH22 | Property operates as a Waste Management Industrial business. The roadway under high voltage overhead conductors has been raised to gain access to adjoining property. The plant being utilised onsite was operating at heights greater than registered roadway vehicles. Causing it to contact overhead conductor. | No Go Zone (contact) | 42377.475 |  |  | 2696 | Industrial |  | 20160801JEM_02 | Infrastructure (network-based) | -37.8112 | 144.8404 | 1 | Jemena | Report | 3508 | 0.0031609 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | Vehicle
A LEI attended and no fault was found with 0.7v measured between the earthing system to an independent earth. The LEI suspected the electric shock event was caused by phase imbalance at the installation after the blue phase HV fuse operated due to the fallen tree. The phase imbalance resulted in a rise in voltage on the neutral conductor in the installations two phase supply. A NST passed and the customer was advised of findings and left on supply. | 85 FAVORITE HILL ROAD, PEARCEDALE VIC 3912 |  |  | Wind;Fallen |  | Neutral fault |  | Phase to earth | 2 | A customer called to advise that a large tree has fallen over and taken out the power lines over the road. The customer has a part supply failure and stated that an electric shock was received in the shower earlier in the morning. During strong winds, a tree fall over the HV/LV overhead conductors that caused a HV fuse to operate at the HV spur fusing at FS0726 located in Oakhill Road. A faults crew attended and cleared the council tree from the overhead conductors and sleeved in a new copper conductor to pole No. LIS 3300489. The blue phase 15amp Boric Acid HV fuse was replaced restoring supply to customers in the area and a LEI was dispatched to 85 Favourite Hill Road following a report of an electric shock when the initial fault occurred. | Conductor (bare) | 0 | 0 | 0 |  |  | Probable phase imbalance a LEI was the cause of the electric shock when the initial fault occurred. | Minor shock | 26/07/2016 5:55 |  |  | 2688 | Residential |  | 20160801UTD_01 | Infrastructure (network-based) | -38.179 | 145.2281 | 1 | United Energy Distribution | Report | 3674 | 0.023961 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3912 | Pearcedale | Trees
A LEI attended and met with (S&Z Australia) the company owner and employees who explained what had happened. They advised the LEI they'd contacted dial before dig prior to commencing work and all procedures were followed. Initial voltage testing between an independent earth to the frame of the machine and the truck it was connected to via hydraulic hosing indicated a voltage of 213v. The LEI stayed on site and ensured no one entered the area while waiting for the ZNX faults truck. The underground was isolated by the ZNX fault crew from a fuse mains box located on a timber pole outside 42 Elizabeth Street. The fault occurred between the LV blue phase and earth. The affected block of four units at 16 Browns Road were informed of the situation and told that power would remain off until rectification works had been completed. Supply was isolated at pole No. LIS 1802585 and a ZNX underground crew repaired the underground cable. Later that evening, the LEI returned and tested the installation that confirmed the fault had been rectified. | 16 BROWNS ROAD, BENTLEIGH EAST VIC 3165 | 1802585 | Working too close to underground cables;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 2 | A worker completing directional boring work for Telstra received an electric shock to his hand when the bore struck an underground powerline outside 16 Browns Road, Bentleigh East. The labourer from S&Z Australia was boring underground conduits and installing Telstra infrastructure when the machine they were using came into contact and penetrated a LV underground service cable below the nature strip outside 16 Browns Road, Bentleigh East. A warning came up on the machine and the operator received a minor tingle to his hands before ceasing work. The area was then barricaded off and the United Energy faults and emergencies call centre was contacted. | Services cable;Copper | 0 | 0 | 0 |  |  | A worker completing directional boring work for Telstra struck a possible shallow LV underground cable outside 16 Browns Road, Bentleigh East. | Minor shock;No Go Zone (contact) | 28/07/2016 15:00 |  |  | 2689 | Roadway |  | 20160801UTD_02 | Infrastructure (network-based) | -37.9228 | 145.0561 | 1 | United Energy Distribution | Report | 3676 | 0.016206 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Dug up
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Consumers Main Neutral Conductor termination at the Neutral Bar located in the Distribution Network Service Pillar, which was identified as the cause of the high impedance within the main neutral conductor. The attending Powercor Fault Crew cleaned the corrosion from the Neutral Bar in the Distribution Network Service Pillar and reterminated the Consumers Main Neutral Conductor and completed an NST Test which confirmed a Pass result. | 8 ALLENBY COURT, MOUNT CLEAR VIC 3350 | 34000865 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Marita Thomson was standing at the metallic Meter Enclosure investigating an intermittent power failure when she received an electric shock as she made simultaneous contact with her hand on the metal Meter Enclosure while standing on wet grass. | LV Pillar | 2 | 2 | 2 |  | BAS013 | Corroded Consumers Main Neutral Conductor termination at the Neutral Bar located in the Distribution Network Service Pillar. | Minor shock | 24/06/2016 18:00 |  |  | 2699 | Roadway |  | 20160802PWA_03 | Infrastructure (network-based) | -37.598 | 143.8638 | 1 | Powercor | Report | 3506 | 0.01999 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Mount Clear | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an â€œOpen Circuitâ€ Neutral Screened Conductor at the â€œWrap Onâ€ supporting the O/H Service Cable at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing Single Phase O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. | 11 ROACHE STREET, KANIVA VIC 3419 | 32097227 |  |  |  | Neutral fault;Mechanical breakdown |  | Phase to earth | 2 | Mr Steven Oâ€™Connor received an electric shock while he was washing his hands in the laundry sink when he made simultaneous contact with his hands between the laundry taps and the metallic laundry sink. | Service conductor | 2 | 2 | 2 |  | NHL031 | The O/H Neutral Screened Cable insulation at pole end failed at the "wrap on" due to over tension. The O/H Neutral Screened Service Conductor downstream of the â€œOpen Circuitâ€ was energised at 230 Volts to earth following contact with the Active Conductor | Minor shock | 16/06/2016 9:30 |  |  | 2700 | Residential |  | 20160802PWA_04 | Infrastructure (network-based) | -36.3813 | 141.2467 | 1 | Powercor | Report | 3507 | 0.029588 | Low voltage AC (<1kV) | Horsham Aerodrome | 3419 | Kaniva | OH Cable
On arrival crew isolated supply and commenced repairs | 510 PENSHURST-PORT FAIRY ROAD, KIRKSTALL VIC 3283 | 33102370 |  |  |  | Fuse failed to eject |  |  | 2 | A Fault crew attending an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | EDO fuse | 2 | 2 | 2 |  | KRT013 | EDO fuse barrel did not drop out | Pole-top fire;Other electricity related | 22/07/2016 10:52 | 1 | Negligible: no ground fire | 2701 | Agricultural |  | 20160802PWA_05 | Infrastructure (network-based) | -38.3024 | 142.3073 | 1 | Powercor | Report | 3574 | 0.0088275 | 22kV AC | Warrnambool Airport Ndb | 3283 | Kirkstall | Fuse
Supply disconnected and overhead service removed, site made safe, The LEI informed the Jemena Report Room to arrange a LEI attend at the same time to investigate the electric shock once the illegal wiring was rectified and supply available. | 3 WOODBURN CRESCENT, MEADOW HEIGHTS VIC 3048 |  | Unauthorised work |  |  | Fault on customer installation |  |  | 2 | Jemena faults crew disconnected overhead service line after Jemena field crew found a service fuse had been bridged out. The meter was also found to be illegally bridged out. Customer advised the field crew they received an electric shock. Licensed Electrical Inspector (LEI) from TechSafe was requested to investigate an electric shock. Upon arrival, the person who received shock wasn't home and there was no supply to the premise. The attended LEI couldn't perform the required tests or investigation without supply and presence of the victim. | Any other type;Smart meter | 0 | 0 | 0 |  |  | Techsafe Inspector was unable to investigate the cause of the incident due to customer not present at the premise at the time of visit and the service had been removed by Jemena field crew. | Minor shock | 42437.4007 |  |  | 2707 | Residential |  | 20160803JEM_01 | Infrastructure (network-based) | -37.6593 | 144.914 | 1 | Jemena | Report | 3516 | 0.035575 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Meadow Heights | Other
On arrival crew isolated supply and commenced repairs | 60 BEACON POINT ROAD, CLIFTON SPRINGS VIC 3222 | 32072076 |  | Wind |  | Corrosion |  |  | 1 | Passer by advised that there was a wire down at this location. On arrival the attending crew found that a high voltage conductor had parted at a helical termination on tee off. Conductor fell away from live side, however would have been back-fed through other substations connected. Protection operated. There was no fire, injuries or third property damage. | Conductor (bare) | 2 | 2 | 2 |  | DDL022 | Conductor parted at termination | Loss of supply | 23/07/2016 1:50 |  |  | 2708 | Roadway |  | 20160803PWA_03 | Infrastructure (network-based) | -38.1484 | 144.5754 | 1 | Powercor | Report | 3583 | 0.0083183 | 22kV AC | Avalon Airport | 3222 | Clifton Springs | Conductor
On arrival crew carried out repairs | 322A MT DERRIMUT ROAD, DERRIMUT VIC 3030 | 30228815 | Copper theft | [5 empty] | 2 | A company employer reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that 8m of HV/LV copper cables had been stolen. No other damage identified. The site made safe and repairs done. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | SU013 | copper theft | Damage to network assets | 25/07/2016 13:00 |  |  | 2710 | Roadway |  | 20160803PWA_05 | Infrastructure (network-based) | -37.803 | 144.77 | 1 | Powercor | Report | 3588 | 0.019995 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply and commenced repairs. | 16 HILLARY STREET, HORSHAM VIC 3400 | 30079454 |  |  |  | Incorrect design;Mechanical breakdown |  |  | 0 | A customer reported a wire on the ground at the incident location. On arrival the crew found that an lv conductor had broken resulting in the wire falling to the ground and remained alive. There was no ground fire. There were no reported injuries or third party property damages. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | HSM006 | Mains cable broke after rubbing through insulation of service cable . | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/07/2016 14:23 |  |  | 2718 | Roadway |  | 20160804PWA_07 | Infrastructure (network-based) | -36.7184 | 142.1811 | 1 | Powercor | Report | 3532 | 0.0068333 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Conductor
Fault crew confirm no other damage on site. | 1475 HIGHLANDS ROAD, WHITEHEADS CREEK VIC 3660 | 4705147 |  |  |  | Fuse failed to eject |  |  |  | IMS 223470. Fault crew arrived on site and advised HV Fuse at lis 4705147 had candled. | EDO fuse | 0 | 0 | 0 |  | smr5 | Boric Acid fuse found to be candling. | Pole-top fire | 42498.3132 | 1 | Negligible: no ground fire | 2721 | Residential |  | 20160805SPN_02 | Infrastructure (network-based) | -37.0468 | 145.3 | 1 | AusNet Services Distribution | Report | 7917 | 0.036765 | 12.7kV AC (SWER) | Mangalore Airport | 3660 | Whiteheads Creek | Fuse
Employee reported discovery to their manager on Monday 1/8 and it was decided that they would request the survey team attend site and measure the height of the conductor. Survey has been completed 5th August and measured the height of the HV conductors mid span at 3.9m. IMS raised on Select Solutions to re-sag conductors to achieve min required ground clearance. A lines crew attended the site on Sunday (7/8/16) to raise the height of the conductors. | 710 CLARKES ROAD, HAZELWOOD NORTH VIC 3840 | 2606091 |  |  |  | Unknown technical factor |  |  | 2 | IMS 223489. Whilst out and about near home (off duty), I came across a span of O/H HV (Pole 2606090 - Pole 2606091) that looked a little low. I couldn't be sure at the time due to the land sloping upwards away from the road. | Conductor (bare) | 0 | 0 | 0 |  |  | Survey completed to establish that conductors were low. Cause not determined. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42377.5 |  |  | 2723 | Commercial |  | 20160805SPN_03 | Infrastructure (network-based) | -38.285 | 146.5116 | 1 | AusNet Services Distribution | Report | 3544 | 0.031638 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | Conductor
On Arrival crew isolated and earthed conductors. Truck removed and conductor repaired | 29-49 VERNEY ROAD, SHEPPARTON VIC 3630 | 32187279 | Working too close to overhead lines |  |  |  | Ineffective planning/procedures/processes |  | 1 | Call received from site supervisor to advise tip truck has struck an O/H conductor in Verney Rd, Shepparton. A crew attended and found a tip truck had contacted an O/H HV conductor when tipping off a load during road works. There was a spotter onsite at the time of the incident. The hydraulic ram of the truck failed, lowering the tipper while still connected to the conductor. This resulted in the conductor breaking and falling to ground, striking a passing car. The driver of the truck remained in the truck til the crew arrived. The crew earthed the conductor and removed it from the truck. A numbers of tyres had blown on the truck following the contact. There were no reported injuries, shocks or ground fire start. | Conductor (bare) | 2 | 2 | 2 |  | SHN023 | Tipping operations under live 22kv | Loss of supply;No Go Zone (contact) | 42590.5153 |  |  | 2732 | Roadway |  | 20160809PWA_01 | Infrastructure (network-based) | -36.3611 | 145.416 | 1 | Powercor | Report | 3575 | 0.028106 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Vehicle
On arrival crew carried out repairs | 191-195 BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30333346 | Copper theft | [5 empty] | 2 | A company employee reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that a part of the HV/LV copper cables from the substation pole had been stolen. No other damage identified. . There were no reported injuries or fire. | Pole mounted | 2 | 2 | 2 |  | SU034 | Copper cable theft | Damage to network assets | 26/07/2016 13:07 |  |  | 2733 | Roadway |  | 20160809PWA_02 | Infrastructure (network-based) | -37.8136 | 144.7831 | 1 | Powercor | Report | 3576 | 0.030848 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
On arrival crew commenced repairs | 185-189 BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30333344 | Copper theft | [5 empty] | 2 | A company employee reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that a part of the HV/LV copper earth cables from the substation pole had been stolen. No other damage identified. The sites made safe and repairs done. There were no reported injuries or fire. | Pole mounted | 2 | 2 | 2 |  | SU034 | copper cable theft | Damage to network assets | 26/07/2016 13:07 |  |  | 2734 | Roadway |  | 20160809PWA_03 | Infrastructure (network-based) | -37.8137 | 144.7844 | 1 | Powercor | Report | 3577 | 0.0079664 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
On arrival crew commenced repairs | 181-183 BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30333343 | Copper theft | [5 empty] | 2 | A company employee reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that a part of the of the HV/LV copper earth cables from the substation pole had been stolen. No other damage identified. There were no reported injuries or fire. | Pole mounted | 2 | 2 | 2 |  | SU034 | copper cable theft | Damage to network assets | 26/07/2016 13:07 |  |  | 2735 | Roadway |  | 20160809PWA_04 | Infrastructure (network-based) | -37.8138 | 144.7854 | 1 | Powercor | Report | 3578 | 0.012567 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
The attending Jemena fault crew replaced the O/H corroded service cable. The installation passed an NST test which was performed by the attending fault crew. The attending LEI performed voltage tests between an independent earth and neutral bar at main switchboard, metallic water system and the point where customer received the electric shock, which recorded a constant voltage 0.4 Volts. A final NST test was carried out at the installation switchboard by the attending LEI that indicated a PASS result. The installation was left ON supply. | 69 GENTLES AVENUE, CAMPBELLFIELD VIC 3061 |  |  |  |  | Corrosion |  |  | 2 | Customer was having a shower when she received an electric shock after making simultaneous contact with her hand on the shower tap whilst standing with her bare feet in a wet area with the metallic drain. Voltage tests between an independent earth and various points of the electrical installation (shower tap) identified 24 volts. | Service conductor | 0 | 0 | 0 |  |  | Jemena crew identified a severely corroded service neutral conductor termination of the O/H service cable on the reticulation pole. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage (24 volts) on the water piping system. | Minor shock | 42712.6813 |  |  | 2746 | Residential |  | 20160812JEM_01 | Infrastructure (network-based) | -37.6721 | 144.9497 | 1 | Jemena | Report | 3597 | 0.012046 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Connection
Fuse and barrel replaced, supply restored | 2130 WESTERNPORT ROAD, RIPPLEBROOK VIC 3818 | 2718897 |  |  |  | Age |  |  | 0 | IMS 223599. HV fuse had candled/burnt | EDO fuse | 0 | 0 | 0 |  | wgl13 | EDO Fuse candled. | Pole-top fire | 42682.4056 | 1 | Negligible: no ground fire | 2744 | Agricultural |  | 20160812SPN_01 | Infrastructure (network-based) | -38.2098 | 145.753 | 1 | AusNet Services Distribution | Report | 3595 | 0.034103 | 22kV AC | Moorabbin Airport | 3818 | Ripplebrook | Fuse
Crew attended and replaced service. REC completed repairs to installation. | 26 FRENCH STREET, PENSHURST VIC 3289 | 33056688 |  |  |  | Overheated connection |  |  | 1 | Fire Brigade reports that the customer POA is on fire. Attending Crew advised a customers connection box has caught fire and was contained to the POA area, no ground fire. Minor damage to the house. | Connector/termination | 0 | 0 | 0 |  | HTN003 | Electrical breakdown of connection box | Property | 14/08/2016 0:16 | 0 | Negligible: no ground fire | 2752 | Residential |  | 20160815PWA_04 | Infrastructure (customer connection) | -37.8757 | 142.2937 | 1 | Powercor | Report | 12073 | 0.028662 | Low voltage AC (<1kV) | Hamilton Airport | 3289 | Penshurst | Connection
S/S isolated and all supply restored. Repair and containment organised. | 401 SOUTH GIPPSLAND HIGHWAY, CRANBOURNE NORTH VIC 3977 | 505476 |  |  |  | Age |  |  | 0 | IMS 223700. 3 blown fuses found at Sth Gipp Thompson S/S, lis 505476, Centre phase fuse found hung up and burnt out. Transformer found unserviceable with large oil leak. | EDO fuse | 0 | 0 | 0 |  | CRE23 | EDO fuse hang up | Pole-top fire | 17/08/2016 6:48 | 1 | Negligible: no ground fire | 2755 | Commercial |  | 20160817SPN_01 | Infrastructure (network-based) | -38.0766 | 145.2722 | 1 | AusNet Services Distribution | Report | 11229 | 0.011234 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne North | Fuse
As requested by Michael Miskulin (ESV), LEI requested attending truck crew to open fuses at substation (85 Northcorp - lakeside) and lift incoming neutral at mains switch board. Attending truck crew issued defect notice. CES required for re-connection. The installation was left OFF supply. | 75 NORTHCORP BOULEVARD, BROADMEADOWS VIC 3047 |  |  |  |  | Fault on customer installation |  |  | 2 | Licensed electrician with spotter present, was clipping probes of a temporary power analysis meter onto exposed live bus bar of MSB at 85 Northcorp Blvd when he inadvertently caused a phase to phase fault resulting in an explosion causing a flashover and burns to his face and neck, and the face and neck of his spotter. Incident was immediately reported to work safe who reported the incident to ESV who reported the incident to Jemena. Investigation into the incident was completed by ESV compliance officer Micheal Miskulin prior to Jemena electrical inspector attending site. | Customer installation | 0 | 0 | 0 |  |  | Person working on a live switchboard. | Medical attention (first aid/doctor/hospital) | 19/08/2016 13:29 |  |  | 2782 | Industrial |  | 20160819JEM_03 | Infrastructure (network-based) | -37.6842 | 144.9491 | 1 | Jemena | Report | 3844 | 0.030293 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Other
Krone switch was replaced and supply was restored. | 1 STATION STREET, RESERVOIR VIC 3073 | A074514 |  |  |  | Overheated connection |  |  | 1 | MFB called due to pole fire outside of house number 1 Station St Reservoir. Krone switch melted to pieces at the bottom of pole, apart from pole being scorched no evidence of fire at bottom of pole was found. | Disconnector/isolator | 0 | 0 | 0 |  |  | Melting of LV Krone switch due to overheating of connections. The heat may have resulted from high electrical load, or local overloading. | Melting or smoking only | 21/08/2016 15:08 |  |  | 2786 | Public space |  | 20160821JEM_03 | Infrastructure (network-based) | -37.7297 | 145.0049 | 1 | Jemena | Report | 3837 | 0.024475 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Connection
Crew attended and replaced service. | 12 EUSTON AVENUE, IRYMPLE VIC 3498 | 32142138 | Working too close to overhead lines | [5 empty] | 1 | A customer reported that the excavator on their site hit the service cable at the incident location. On arrival the crew found that a contractor (Leed Engineering) was operating an excavator and contacted a LV service cable causing the cable to break and fall to the ground. No protection operated. There were no reported injuries, shocks, ground fire start or third party property damages. | Service conductor | 0 | 0 | 0 |  | RCT021 | Excavator contacted service line | Loss of supply | 42621.6264 |  |  | 2789 | Agricultural |  | 20160822PWA_03 | Infrastructure (network-based) | -34.2504 | 142.1547 | 1 | Powercor | Report | 12065 | 0.017046 | Low voltage AC (<1kV) | Mildura Airport | 3498 | Irymple | Vehicle
Replaced Krone box and restored supply | Lot 1 Signboard Lane, Dunston |  |  |  |  | Unknown technical factor |  |  | 2 | IMS 223842. Ground fire reported at base of pole.Fire area of 1 Metre square. Found burnt out Krone Box. Address is actually Lot 1 Signboard lane. | Connection box | 0 | 2 | 0 |  | sle31 | Spoke to fault crew and there was no apparent cause found, the attached photo's show that the contacts of one of the krone boxes was melted. | Grassfire | 22/08/2016 2:40 | 1 | Localised: less than 10 sq.m | 2793 |  |  | 20160823SPN_01 | Infrastructure (network-based) | -38.2212 | 147.2745 | 1 | AusNet Services Distribution | Report | 3832 | 0.014851 | Low voltage AC (<1kV) | Bairnsdale Airport |  |  | Connection
Email sent to Adam Duffield to initiate discussion with OHMS about incorrect use of metallic tape measure when working under green book requirements section 1.1.11 | 8 ARMSTRONG ROAD, HEATHMONT VIC 3135 | [5 empty] | Not followed |  | 2 | IMS 223798. Email received from External Project Manager with construction query on design change for correct clearance required with photo attached. In photo is metallic tape measure being used near top of an existing HV pole alive. | Pole top | 0 | 2 | 0 |  |  | Human error. Incorrect use of metallic tape measure. | No Go Zone (no contact) | 18/08/2016 0:00 |  |  | 2794 | Residential |  | 20160823SPN_02 | Infrastructure (network-based) | -37.8277 | 145.2562 | 1 | AusNet Services Distribution | Report | 3665 | 0.032998 | 22kV AC | Moorabbin Airport | 3135 | Heathmont | Other
CEOT dispatched a Fault and the Duty Availability Officer to isolate supply, make safe and investigate. Repairs carried out. | 4 FLOUNDER ROAD, LAKE TYERS BEACH VIC 3909 | 1902844 |  | Animal |  |  |  | Phase to neutral | 2 | IMS 223960. Per CFA Pole Fire - A three phase mains box pole box caught fire and melted on a wood pole, scorching the pole. Melting plastic fell to the ground., No fire started on the ground. Cause unknown but the crew advised there where a lot of ants up the pole which may have contributed if there was a ants nest in mains box. very small fire in vicinity of pole base . no other damage. | Pole (wood);Connection box | 0 | 0 | 0 |  | nla34 | Possible ants nest inside mains box on pole. | Pole-top fire | 27/08/2016 11:18 | 1 | Negligible: no ground fire | 2821 | Residential |  | 20160829SPN_02 | Infrastructure (network-based) | -37.8603 | 148.0802 | 1 | AusNet Services Distribution | Report | 7919 | 0.025589 | Low voltage AC (<1kV) | Bairnsdale Airport | 3909 | Lake Tyers Beach | Animal
The HV line was de energised in order to make safe. The MWTS-MPS#3 66kV line was isolated and earthed and an Access Permit was issued. The crew replaced the 66kV intermediate pole 7700634 with a new 15.5/12 concrete pole. | 412 COMMERCIAL ROAD, MORWELL VIC 3840 | 7700634 | Vehicle | [5 empty] | 2 | IMS 223959. The driver of a large front end-loader caused the vehicle to come in contact with a HV concrete pole causing the pole to break near ground level. The pole was supported by the overhead HV conductors. Steve Evans advised his vehicle ran into a 66kV pole on the MWTS-MPS#3 66kv line. No injuries to Steve or to any persons. No live conductors on ground or below 4.3 metres to ground. NOTE: This incident has been re-categorised from serious to near-miss definition and will be included in the 3rd MEC Quarterly Report to ESV under "Number of reported instances where vehicles have struck MEC poles. Please not class this incident as a serious electrical incident". | Pole (concrete) | 0 | 0 | 0 |  | mwts35 | A front end-loader came in contact with a HV concrete pole. | Loss of supply | 27/08/2016 8:39 |  |  | 2822 | Commercial |  | 20160829SPN_03 | Infrastructure (network-based) | -38.2558 | 146.4169 | 1 | AusNet Services Distribution | Report | 3716 | 0.029859 | 66kV AC | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Vehicle
On arrival crew isolated supply. Customers REC repairing underground cable. Repairs to LV isolators on substation to be completed. | 1498 MELTON HIGHWAY, PLUMPTON VIC 3335 | 33075166 | Working too close to underground cables | [5 empty] | 1 | A customer reported that an excavator has contacted their low voltage underground mains and they have lost power to equipment at the incident location. The contact caused damage to the underground cable resulting in a three phase short circuit near the transformer, the high voltage fuses at the transformer operated to isolate the fault. The low voltage isolators on the transformer were damaged as the underground cable was pulled thru the conduits. There was no fire or injuries. | Pole mounted;Customer installation | 2 | 2 | 2 |  | MLN021 | Excavation works in Quarry | Loss of supply;No Go Zone (contact) | 22/08/2016 10:05 |  |  | 2834 | Commercial |  | 20160830PWA_03 | Infrastructure (network-based) | -37.681 | 144.6731 | 1 | Powercor | Report | 3734 | 0.0052025 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Dug up
On arrival crew isolated supply and commenced repairs | 350 KAWARREN EAST ROAD, KAWARREN VIC 3249 | 32065064 |  | Within clearances |  |  |  |  | 1 | A Customer called to report a tree branch had fallen onto the powerline and broke the wire. ANC Forestry Group (Terry Magnuson) was clearing trees close to where this occurred. On arrival the crew found that a tree branch had been dropped on the SWER line by tree clearers breaking the conductor between REDENBACH P8 & DAWES P1. This caused KAWARREN P2A ACR to trip, de-energising the SWER system. There was no fire, there were no injuries. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 42378.5479 |  |  | 2852 | Agricultural |  | 20160902PWA_03 | Infrastructure (network-based) | -38.5047 | 143.5883 | 1 | Powercor | Report | 3759 | 0.0059236 | 12.7kV AC (SWER) | Avalon Airport | 3249 | Kawarren | Other
On arrival crew disconnected supply and recovered meters | 7 TERINGA PLACE, TOORAK VIC 3142 | 30195921 | Unauthorised work;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Mr. Chris Steele, SFO Construction, advised an excavator accidently knock down a house wall with live meter at the incident location. Upon arrival, The Citipower fault crew found that the meter board including the meter had been knocked down The Fuses at meter position had been removed by an unknown third party. There were no injuries or fire. | Services cable;Meter board (including fuses) | 2 | 2 | 2 |  | TK006 | House demolition activities | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/08/2016 12:41 |  |  | 2856 | Residential |  | 20160902PWA_04 | Infrastructure (network-based) | -37.8398 | 145.0195 | 1 | CitiPower | Report | 3763 | 0.0030671 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Vehicle
employee documented situation and submitted report | 245 ROSLYN ROAD, HIGHTON VIC 3216 | 30063437 | Unauthorised work | [5 empty] | 2 | A powercor employee detected an service line raised by use of a wooden prop at the incident location. | Service conductor | 2 | 2 | 2 |  | WPD013 | Service line propped up by wooden support | No Go Zone (contact) | 25/08/2016 13:32 |  |  | 2859 | Construction |  | 20160905PWA_01 | Infrastructure (network-based) | -38.1731 | 144.3217 | 2 | Powercor | Report | 3766 | 0.014288 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | AF Other
A LEI and faults truck attended and completed installation tests and no faults could be identified. The LEI inspected the light fittings and found one light with a blown globe that tested and inspected okay and the LEI advised the customer that cheap globes can blow prematurely. The council trees at the front of the property had grown close to the reticulation conductors and may have caused the large blue flash the customer witnessed. A new trouble order was created to trim the trees outside 231 Cranbourne Road, Frankston. | 229 CRANBOURNE ROAD, FRANKSTON VIC 3199 |  |  |  |  | Conductor clashing |  | Phase to earth | 2 | The caller advised there was arcing last night but unsure where it was from. She has been experiencing tingles when touching the television and lights have been constantly flickering. The customer explained that she saw a large blue flash occur the previous night outside the property and has experienced dimming of lights constantly. She advised the LEI that no electric shocks had been received. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Minor shock | 29/08/2016 1:00 |  |  | 2858 | Residential |  | 20160905UTD_02 | Infrastructure (network-based) | -38.1521 | 145.1535 | 2 | United Energy Distribution | Report | 3765 | 0.00033102 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Trees
The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the Reticulation Pole Top Connection Box and completed an NST test which confirmed a Pass result. | 119 HURD STREET, PORTLAND VIC 3305 | 32131507 |  |  |  | Corrosion |  | Phase to phase | 2 | Mr Trevor Sherwell was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. | Connection box | 2 | 2 | 2 |  | PLD004 | Corrosion in Pole top Junction box | Minor shock | 42377.0417 |  |  | 2863 | Residential |  | 20160906PWA_01 | Infrastructure (network-based) | -38.3373 | 141.6013 | 1 | Powercor | Report | 3770 | 0.029959 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
The attending Powercor Fault Crew replaced the Pole Top Connection Box and reterminated the existing O/Head Service Conductors and completed an NST test which confirmed a Pass result. | 298 LAVERS HILL-COBDEN ROAD, COBDEN VIC 3266 | 33036609 |  |  |  | Corrosion |  |  | 2 | Mrs Sue Twynstra received an electric shock while she was washing dishes at the kitchen sink, when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the conductive Kitchen floor. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. | Connection box | 2 | 2 | 2 |  | CDN001 | Corrosion in pole top connection box | Minor shock | 16/08/2016 7:30 |  |  | 2864 | Residential |  | 20160906PWA_02 | Infrastructure (network-based) | -38.3476 | 143.0986 | 1 | Powercor | Report | 3910 | 0.037838 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3266 | Cobden | Connection
Citipower linesman replaced the service & CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 69 GEORGE STREET, FITZROY VIC 3065 | 30169620 |  |  |  | Corrosion |  | Phase to earth | 2 | Cherubina received an electric shock when she simultaneously contacted the metallic tap with one hand and the metallic trough with her forearm. A voltage test between the tap and the metallic trough resulted with 123Volts and various points of the installation with reference to an independent earth including the distribution assets revealed the service neutral conductor was damaged. | Service conductor | 2 | 2 | 2 |  | B012 | Service line Neutral damaged | Minor shock | 16/08/2016 15:30 |  |  | 2865 | Residential |  | 20160906PWA_03 | Infrastructure (network-based) | -37.8064 | 144.9804 | 1 | CitiPower | Report | 3772 | 0.0095995 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | OH Cable
Supply was isolated and damages were repaired, once site was made safe supply was restored. | 228-230 BALLARAT ROAD, BRAYBROOK VIC 3019 | A121037 | Vehicle | [5 empty] | 1 | Emergency services reported to Jemena that a vehicle made contact with pole which in turn brought down live conductor on the ground. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | BY 15 | Unknown vehicle hit Jemena Pole (A121037) which in turn brought down the overhead conductors. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42560.5833 |  |  | 2880 | Roadway |  | 20160907JEM_01 | Infrastructure (network-based) | -37.7809 | 144.8647 | 1 | Jemena | Report | 3792 | 0.0056088 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Vehicle
The attending Powercor Fault Crew replaced the Single Phase O/Head Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 6 GEORGE STREET, ANGLESEA VIC 3230 | 30066573 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Deb Chapman received an electric shock while she was washing dishes in the kitchen sink when she made simultaneous contact between the kitchen taps and the metallic kitchen sink. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor, which was the cause of the high impedance associated with the return path of the neutral current. The corrosion of the O/H Service Neutral Conductor was the result of water entering the outer sheath of the O/H Neutral Screened Service via a small perforation in the cable sheath, the cause of which was unable to be determined. | Service conductor;Neutral screen | 2 | 2 | 2 |  | WPD021 | Corroded O/H Service Neutral Conductor, the result of water entering the outer sheath of the O/H Neutral Screened Service via a small perforation in the cable sheath, the cause of which was unable to be determined. | Minor shock | 42559.3333 |  |  | 2898 | Residential |  | 20160913PWA_06 | Infrastructure (network-based) | -38.4115 | 144.1778 | 1 | Powercor | Report | 3811 | 0.037422 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | OH Cable
The attending Powercor Fault Crew repaired the Pole Top Connection Box and reterminated the existing O/Head Service Cable and completed an NST test which confirmed a Pass result. | 39 BELMORE ROAD, WARRNAMBOOL VIC 3280 | 30134276 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Christy Purcell received an electric shock while she was showering in the bathroom, when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. | Connection box | 2 | 2 | 2 |  | WBL012 | corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box | Minor shock | 19/08/2016 0:00 |  |  | 2899 | Residential |  | 20160913PWA_07 | Infrastructure (network-based) | -38.392 | 142.5008 | 1 | Powercor | Report | 3812 | 0.0051481 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew isolated supply and commenced repairs. | 52 EDWARDS DRIVE, ALTONA MEADOWS VIC 3028 | 30116788 |  |  |  | Corrosion |  |  | 2 | A customer reported sparking from pole outside No. 52 Edwards Drive, - significant amount of sparks, sparks reaching ground, a car parked underneath, and intermittent/flickering supply at property. A Powercor crew attended and discovered that at pole LIS 213533 outside No 52 Edwards Drive, an LV conductor line bridge was burning at a substation LV bus fuse termination. There was no ground fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | LVN022 | corrosion at LV isolator connection | Loss of supply | 42683.8021 |  |  | 2908 | Roadway |  | 20160914PWA_05 | Infrastructure (network-based) | -37.8862 | 144.7769 | 1 | Powercor | Report | 3822 | 0.035424 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Pole
A faults crew attended and identified the HV fuse unit requires replacement. The substation was isolated HV and LV and LV parallels installed to restore supply to customers with repairs to be completed in daylight. | 7 SUMMIT DRIVE, BULLEEN VIC 3105 |  |  |  |  | Electrical breakdown |  |  | 2 | Customers supplied from "Westminster-Summit" substation advised of a loss of their electricity supply. A HV EDO fuse candled at "Westminster-Summit" substation that caused a loss of supply to a small number of customers in Summit Drive, Bulleen. | EDO fuse | 0 | 0 | 0 |  | WD 36 | A HV EDO fuse candled at "Westminster-Summit" substation. | Pole-top fire | 13/09/2016 3:50 | 0 | Negligible: no ground fire | 2901 | Residential |  | 20160914UTD_01 | Infrastructure (network-based) | -37.7669 | 145.085 | 1 | United Energy Distribution | Report | 3814 | 0.0074259 | 22kV AC | Essendon Airport | 3105 | Bulleen | Fuse
On arrival following restoration of supply a meter caught fire, supply was immediately disconnected. LEI called and tests revealed a burnt off neutral connection in a junction box. Repairs completed | 441 CONNS LANE, YANGERY VIC 3283 | 33100239 |  | Bird |  | HV injection |  |  | 1 | The customer at the incident location called to report they had no supply. On arrival the crew found a blown HV fuse on the substation caused by a bird, upon restoration of supply, a meter at the dairy caught fire, supply was quickly isolated. Minor damage was caused to the meter board, however the board remained serviceable. An LEI was called, and further tests revealed a burnt off neutral connection in a junction box. No third party damage, no injuries. | Boric acid;Smart meter | 2 | 2 | 2 |  | KRT031 | Bird Incident | Loss of supply;Meter board | 42622.6201 | 1 | Negligible: no ground fire | 2910 | Roadway |  | 20160915PWA_01 | Infrastructure (network-based) | -38.3112 | 142.4292 | 1 | Powercor | Report | 8390 | 0.015955 | Low voltage AC (<1kV);22kV AC | Warrnambool Airport Ndb | 3283 | Yangery | Animal
On arrival crew isolated supply and carried out repairs | 64 GRAYLEA AVENUE, HERNE HILL VIC 3218 | 30076710 |  | Within clearances |  |  |  |  | 1 | A customer called to report that they were cutting a tree, and a branch has hit the wire and caused it to come down at the incident location. On arrival the crew found that part of a tree had been cut and fallen onto the white & blue phases of the LV overhead open wire conductors, causing them to break and fall to the ground. No third party damage, fire or injuries. | Conductor (bare) | 2 | 2 | 2 |  | GL014 | Vegetation: Trees Incident | Loss of supply | 42652.6 |  |  | 2911 | Roadway |  | 20160915PWA_02 | Infrastructure (network-based) | -38.1327 | 144.317 | 1 | Powercor | Report | 3825 | 0.033671 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Herne Hill | Trees
On arrival crew isolated supply and issued a defect notice for damaged POA. | 1241 RYAN ROAD, LANCASTER VIC 3620 | 30131603 | Vehicle | [5 empty] | 2 | A customer informed a service cable low and it could have been hit by a vehicle. Upon arrival the crew found the cable hanging in the mid-air and the POA damaged. There were no reported injuries, third party damage or fire. | Service conductor;Customer installation | 2 | 2 | 2 |  | KYM003 | Unknown vehicle struck service line | Less than $50k damage;Damage to network assets | 13/09/2016 13:49 |  |  | 2913 | Roadway |  | 20160915PWA_04 | Infrastructure (network-based) | -36.3066 | 145.1501 | 1 | Powercor | Report | 3828 | 0.0090197 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Lancaster | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded PG Clamp at a Neutral Bridge Conductor termination at an adjacent Reticulation Pole. Connection replace by field crew. | 84 STRACHAN STREET, BIRREGURRA VIC 3242 | 30051740 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr David Strachan was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | CLC007 | Corroded PG on neutral connection at pole end. | Minor shock | 17/08/2016 18:00 |  |  | 2931 | Roadway |  | 20160921PWA_03 | Infrastructure (network-based) | -38.3439 | 143.7819 | 1 | Powercor | Report | 3912 | 0.001272 | Low voltage AC (<1kV) | Avalon Airport | 3242 | Birregurra | Connection
On arrival crew carried out repairs | 62 ANDREW STREET, MELTON SOUTH VIC 3338 | 30224657 | Copper theft | [5 empty] | 2 | An employee reports pole with copper earth cables missing. There was no fire, no reported injuries, shocks or third party property damages. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | criminal activity | Damage to network assets | 16/09/2016 11:10 |  |  | 2934 | Roadway |  | 20160921PWA_05 | Infrastructure (network-based) | -37.6936 | 144.5798 | 1 | Powercor | Report | 3856 | 0.01406 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
On arrival crew carried out repairs | 19 PHILLIP STREET, MELTON SOUTH VIC 3338 | 30114970 | Copper theft | [5 empty] | 2 | An employee reported pole with copper earth cables missing. There was no fire, no reported injuries, shocks or third party property damages. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Criminal activity | Damage to network assets | 16/09/2016 11:12 |  |  | 2935 | Roadway |  | 20160921PWA_06 | Infrastructure (network-based) | -37.6932 | 144.5774 | 1 | Powercor | Report | 3857 | 0.016122 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Fault crew attended and isolated supply from pit. Follow up of records did not reveal any prior disconnection requests | 28 GORDON CRESCENT, ROMSEY VIC 3434 | 31031529 | Unauthorised work | [5 empty] | 2 | Powercor worker was investigating nil consumption on a meter and found that the house had been removed and was being replaced with 6 units (under construction). Further investigation found that there had been no requests for abolishment or disconnection, the consumers underground unmetered mains were still energized from the service pit. The remote end of these mains was not located. Metering equipment not recovered. | Other meter;Customer installation | 0 | 0 | 0 |  | WND012 | Interference | Damage to network assets | 26/07/2016 0:00 |  |  | 2952 | Construction |  | 20160922PWA_10 | Infrastructure (network-based) | -37.3583 | 144.7381 | 1 | Powercor | Report | 12077 | 0.022623 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3434 | Romsey | Other
On arrival crew carried out repairs | 105 DERBY ROAD, SUNSHINE VIC 3020 | 32178125 | Copper theft | [5 empty] | 2 | A fault crew attending a fault found a copper earthing was stolen at the incident location. There were no other damages or fire reported. The Sunshine police informed. | Earth/earthing | 2 | 2 | 2 |  | SSE034 | Criminal activity | Damage to network assets | 27/09/2016 9:30 |  |  | 2973 | Roadway |  | 20160928PWA_01 | Infrastructure (network-based) | -37.7907 | 144.832 | 1 | Powercor | Report | 3915 | 0.00037037 | Earthing cable | Essendon Airport | 3020 | Sunshine | Other
Site isolated, tree branch removed, repairs completed and supply restored. | 99 BANYULE ROAD, ROSANNA VIC 3084 | Sussex Banyule Substation |  | Blown branch/vegetation |  | HV injection |  |  | 1 | Due to the high winds a tree branch made contact with High Voltage conductors. The HV conductors made contact with the LV conductors which caused a High Voltage Injection. REC inspected, tested and repaired damages to the impacted properties. | Conductor (bare);Customer installation | 0 | 0 | 0 |  | HB 23 | Vegetation: Trees Incident | HV injection | 42410.6104 |  |  | 2987 | Commercial |  | 20161003JEM_02 | Infrastructure (network-based) | -37.7429 | 145.0819 | 1 | Jemena | Report | 3936 | 0.015551 | 11kV AC | Essendon Airport | 3084 | Rosanna | Trees
CEOT dispatched a fault crew to make safe, repair and investigate. The HV Boric Acid fuse was immediately opened and the area was made safe. The transformer and associated apparatus was inspected for any additional damage before replacing the fuse. | 1870 SNOW ROAD, MILAWA VIC 3678 | 5740818 |  |  |  | Electrical breakdown |  |  | 2 | IMS 224584. AusNet Services' fault crew attended reports of dim lights by customers. Found a candling HV Boric Acid fuse on the transformer pole 5740818. No fire evident. | EDO fuse | 0 | 0 | 0 |  | wn5 | Candled BA HV fuse. | Other electricity related | 29/09/2016 18:25 | 1 | Negligible: no ground fire | 2979 | Agricultural |  | 20161003SPN_01 | Infrastructure (network-based) | -36.4532 | 146.4607 | 1 | AusNet Services Distribution | Report | 3924 | 0.033639 | 22kV AC | Wangaratta Aero | 3678 | Milawa | Fuse
CEOT dispatched a fault crew to make safe, investigate and carry out any repairs. All personnel were OK with no injuries or damage to plant or AusNet Services' equipment. The 15E Boric Acid line fuse was replaced at Pole 138, asset number 818214, that restored supply to the line. The HV conductor has been measured on site at 6.21m high where the excavator was alleged to have made contact. AusNet Services' survey has been sent to site to determine the sag and possible issue and how to rectify the conductor height. Height requirement for this track/terrain is 5.5m re "ground traversable by vehicles" but AusNet Services build HV lines to 6.7m ground clearances thus the involvement of our survey section for rectification. Evidently the ground beneath the HV line has been built up over time which has impacted on our standard ground clearance of 6.7m. | 3895 MEENIYAN-PROMONTORY ROAD, YANAKIE VIC 3960 | 2027895 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | IMS 224610. An excavator was reforming a private track under the HV line when it came into proximity to the HV line causing a flash and HV Boric Acid line fuse to operate. | Conductor (bare) | 0 | 0 | 0 |  | ftr22 | An excavator contacted an overhead HV line. | No Go Zone (contact) | 42439.484 |  |  | 2984 | Agricultural |  | 20161003SPN_05 | Infrastructure (network-based) | -38.823 | 146.2325 | 1 | AusNet Services Distribution | Report | 3933 | 0.034051 | 22kV AC | Morwell (Latrobe Valley Airport) | 3895 | Yanakie | Vehicle
CEOT dispatched a fault crew to make safe and repair lines. CEOT also dispatched a LEI to investigate the incident. Traffic Management onsite and Mangans Road was closed off. Tree clearers were on-site to remove the fallen tree. Downer fault crew were on-site repairing the HV & LV lines. The LEI confirmed HV injection had occurred and customer's service fuses were then removed. CEOT was subsequently notified that a HVI had occurred. LEIs required to reconnect all properties on the circuit and assess damage. Several properties were issued defect notices (NCIDs) to have RECs replace damaged FMBs and switchboards from the HV injection. | 9 MANGANS ROAD, LILYDALE VIC 3140 | 1001763 |  | Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 224623. A tree located on the road reserve out the front of 9 Mangans Rd, Lilydale, fell over onto open bare 22kV/415V conductors. The tree fell due to the ground being very wet, high winds and the large pine tree was also located in the road reserve's ditch in which the ground at the base of the tree may have been inadequate. The feeder protection tipped and there were blown substation bus fuses. Ausnet Services' LEI confirmed that a HV injection had occurred to several customers' properties. In addition a large number of meters were required to be replaced. | Conductor (bare) | 0 | 0 | 0 |  | ldl23 | Vegetation: Trees Incident | HV injection | 42470.5472 |  |  | 2990 | Roadway |  | 20161005SPN_01 | Infrastructure (network-based) | -37.7622 | 145.3712 | 1 | AusNet Services Distribution | Report | 3940 | 0.00087963 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Trees
on arrival crew isolated supply and commenced repairs, Cross-arm replaced and conductor repaired | 1185 BLACKGATE ROAD, FRESHWATER CREEK VIC 3217 | 32078631 |  |  |  | Corrosion |  |  | 1 | A REC reported that there appears to be a low conductor at the incident location. On arrival the fault crew found a broken HV crossarm and conductor on the ground. There was no ground fire, no injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | WPD014 | Deterioration ( unable to positively determine if broken conductor initiated cross-arm breakage or vice versa.) | Loss of supply | 42498.4097 |  |  | 2780 | Agricultural |  | 20160819PWA_08 | Infrastructure (network-based) | -38.2796 | 144.2671 | 1 | Powercor | Report | 3641 | 0.0262 | 22kV AC | Avalon Airport | 3217 | Freshwater Creek | Crossarm
Made safe & replaced fuse. | 85 ROADKNIGHT STREET, LAKES ENTRANCE VIC 3909 | 1902429 |  |  |  | Age |  |  | 0 | IMS 223771. Field crews arrived at LIS 1902429 to find a fuse tube burnt in half. | EDO fuse | 0 | 0 | 0 |  | BDL41 | Fuse tube burnt in half. | Pole-top fire | 18/08/2016 20:21 | 1 | Negligible: no ground fire | 2769 | Residential |  | 20160819SPN_01 | Infrastructure (network-based) | -37.8749 | 148.0048 | 1 | AusNet Services Distribution | Report | 11230 | 0.033252 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | Fuse
A faults crew attended and cut the three lightning arrestors clear and supply was restored. | 1270 FERNTREE GULLY ROAD, SCORESBY VIC 3179 | 8808747 |  |  |  | Moisture ingress;Fatigue |  |  | 1 | At 1830hrs on 13/07/2016, 22kV feeder MGE 21 circuit breaker reclosed to lockout affecting 661 customers. A customer called to report a pole on the corner of Ferntree Gully Road and Borg Crescent with a transformer on top seems to be on fire. Customer heard a bang and have lost their power. The blue phase lightning arrestor at "Ferntree Gully-Borg" capacitor bank on pole No. 8808747 located on the corner of Ferntree Gully Road and Borg Crescent was found to have been blown clear. A fire was witnessed at the time of the fault and the cause was unknown. | Surge diverter | 0 | 0 | 0 |  | MGE 21 | The incident cause was unknown but it was damp at thetime of the fault. | Pole-top fire | 13/07/2016 18:30 | 1 | Negligible: no ground fire | 2767 | Roadway |  | 20160819UTD_02 | Infrastructure (network-based) | -37.8997 | 145.2224 | 1 | United Energy Distribution | Report | 3668 | 0.03839 | 22kV AC | Moorabbin Airport | 3179 | Scoresby | Pole
A LEI and faults truck attended and tested at the main switchboard and a NST failed on neutral impedance. Voltage tests indicating 8v at the two shock points and the customers earthing system and the installation was immediately isolated while further inspection and testing was carried out. The overhead service failed a NST that indicated a faulty single phase copper neutral screened service. The fault crew replaced the deteriorated neutral screened service with a XLPE type and the installation was re-tested with a NST passing. Voltage testing indicated 0.2V at shock points and customer earthing system with and without an applied load and network analyses showed positive results. Supply was left on and the customer advised of the rectification work. | 152 BLACKBURN ROAD, GLEN WAVERLEY VIC 3150 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Electric shock was received by the occupier and REC Tristan has attended following a call from the Estate Agent. The occupier received slight electric shocks from the kitchen and shower taps and notified the Estate Agent who contacted a REC to investigate the cause. The REC ran an independent earth and is still measuring 3-4volts and contacted the United Energy faults and emergencies call centre as he was unable to identify the cause. The occupier advised the LEI that he'd been receiving tingles from the taps on a regular basis over the past 6-8 months. | Customer installation | 0 | 0 | 0 |  |  | The cause was a faulty single phase copper neutral screened service. | Minor shock | 42712.4583 |  |  | 2792 | Residential |  | 20160822UTD_01 | Infrastructure (network-based) | -37.8678 | 145.1495 | 1 | United Energy Distribution | Report | 3657 | 0.016309 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Glen Waverley | OH Cable
The Geiger Group lineworkers isolated the single phase XLPE overhead service and removed the service from the pole. They notified their supervisor and a Hazard Alert was created. | 5 LOUIS STREET, GLEN IRIS VIC 3146 |  | Unauthorised work | [5 empty] | 2 | During a Geiger Group site hazard assessment at 5 Louis Street, Glen Iris, they discovered a overhead XLPE service hanging from the end of the LV crossarm. The service had been secured to the top of underground cable guard approximately 2.0m from ground level. Tests on the service found the XLPE overhead service remained alive at 240v. Unknown persons have removed a single phase XLPE overhead service from a property at 5 Louis Street, Glen Iris that was being demolished and left it alive secured on the pole attached to the underground cable guard. The location of the meter is unknown. A review of our records shows that a new underground pit was requested by Carter Grange Homes Mulgrave as follows: From: Paul Quinn mailto:paul@molitor.com.au Sent: Thursday, 23 June 2016 10:08 AM To: ueconnections Subject: 5 Louis Street, Glen Iris 3146 "Hi, We are demolishing our single dwelling at 5 Louis Street Glen Iris 3146. Please find attached an application form for your Under Ground Power Pit with United Energy. Also attached is a site plan with the pit location marked with a green dot. Let me know if more information is required, Regards, Paul Quinn Ph 0418315296" A plan of the new development was also attached from Carter Grange Homes Pty Ltd. 03 8544 4913 15 Compark Circuit, Mulgrave VIC 3170 P.O. Box 5328, Brandon Park VIC 3150 www.cartergrange.com.au | Conductor (insulated);Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Overhead service removed for a home demolition with no contact made with United Energy for an abolishment request. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/08/2016 11:00 |  |  | 2798 | Roadway |  | 20160824UTD_01 | Infrastructure (network-based) | -37.8627 | 145.0477 | 1 | United Energy Distribution | Report | 3670 | 0.0039537 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Other
Repaired the defective cable on PE cell control . Voltage and NST tests were performed following the repair and normal results were obtained | 194-210 KINGS WAY, SOUTH MELBOURNE VIC 3205 | 30160701 |  |  |  | Electrical breakdown |  |  | 2 | Andrew received an electric shock when he contacted the metallic tram pole with one hand whilst making simultaneous contact with the metallic safe rail other hand . Further Tests between an independent earth and various points of the electrical installation, including the point of contact and distribution assets, revealed a damaged cable to Photoelectric /cell light sensitive switch on install on pole | Public lighting;Pole (steel) | 0 | 0 | 0 |  | SB015 | Deteriorated insulation | Minor shock | 42621.625 |  |  | 2812 | Public space |  | 20160825PWA_09 | Infrastructure (network-based) | -37.8301 | 144.964 | 1 | CitiPower | Report | 3694 | 0.019969 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | AF Other
The vehicle stopped some 200 metres up the road. The fault crew made the site safe by lifting the LLC's and attaching an E/S/C. A section of the HV conductor that was hit by the vehicle was replaced. | 329 DARNUM-ALLAMBEE ROAD, CLOVERLEA VIC 3822 | 2705972 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 223899. A HV conductor broke at the tie on an intermediate pole dropping the conductor low across a road that a vehicle was travelling along. The intermediate was approximately 200m into a paddock with the Tee Off pole on the opposite side of the road. Because the conductor broke and the tee off pole was on the other side of the road the car came into contact with the conductor hanging low as it was travelling along. The morning was foggy and making visibility difficult to see the low conductor. The conductor had rusted through at the tie causing it to come back at the tee off. The pole is beside a row of Cyprus trees and looks to be the only location where the rust had appeared. The conductor was steel 3/2.75 SC/GZ. | Conductor (bare) | 0 | 0 | 0 |  | wgl15 | The HV conductor had rusted through at the tie causing it to come back at the tee off. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/08/2016 6:15 |  |  | 2802 | Agricultural |  | 20160825SPN_02 | Infrastructure (network-based) | -38.2164 | 146.0008 | 1 | AusNet Services Distribution | Report | 3904 | 0.025544 | 22kV AC | Morwell (Latrobe Valley Airport) | 3822 | Cloverlea | Conductor
The crew made the place safe and the transformer taken to the depot. Site left off LV supply | 130 GILLESPIES LANE, BALLAN VIC 3342 | 33072430 | Copper theft | [5 empty] | 2 | Bacchus Marsh Police and also a Powercor employee reported vandalised pole sub at the incident location. Upon arrival, the Powercor fault crew found that the transformer was on the ground and pole top assets vandalised. The crew made the site safe and the transformer taken to the depot. There was no fire or injuries. | Pole mounted;Transformer | 0 | 0 | 0 |  | BMH003 | interference - copper theft | Damage to network assets | 16/08/2016 6:45 |  |  | 2813 | Industrial |  | 20160826PWA_01 | Infrastructure (network-based) | -37.6079 | 144.2254 | 1 | Powercor | Report | 3695 | 0.039443 | 22kV AC | Ballarat Aerodrome | 3342 | Ballan | Other
A LEI and faults truck attended and installation tests revealed a deteriorated neutral block/connection in the pillar following 32v being measured to the water tap to an independent earth. A NST was completed that failed. A Downer underground crew were dispatched to complete repairs in the pillar and they replaced the neutral block and re-terminated the neutral conductor. Four customers (10, 11, 12 & 13 McBride) were also off supply whilst the repair work was completed. The LEI re-tested the installation and supply was restored after tests confirmed the fault had been repaired. | 13 MCBRIDE CRESCENT, SEAFORD VIC 3198 |  |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | Caller reports that lights are dimming under load and the customer received a shock from the steel sliding door. This has been occurring since yesterday. The occupier advised that he's noticed the recent dimming of lights and received an electric shock from the bathroom tap as he washed his hands. He proceeded to contact the United Energy faults and emergencies call centre to report the fault. | Cable;LV Pillar | 0 | 0 | 0 |  |  | Installation tests revealed a deteriorated neutral block/connection in the pillar located in the road reserve. | Minor shock | 21/08/2016 12:30 |  |  | 2815 | Residential |  | 20160826UTD_01 | Infrastructure (network-based) | -38.1043 | 145.1495 | 1 | United Energy Distribution | Report | 3697 | 0.0075752 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
On arrival crew isolated supply and commenced repairs | 501 DANDENONG ROAD, ARMADALE VIC 3143 | 30198370 |  |  |  | Overheated connection |  |  |  | rams control room reported a light fitting on Tramway Pole was on fire at the above incident location. On arrival, the crew found that a light fitting cap on a PTC Tramway Pole (located on the Tramway medium strip) had caught on fire, which melted the cap and burnt the light electrical components. There was no ground fire nor third party damaged. There were no reported injuries. | Public lighting | 2 | 2 | 2 |  | AR007 | Overheated connection in lamp | Pole-top fire | 20/08/2016 18:06 | 1 | Negligible: no ground fire | 2832 |  |  | 20160830PWA_01 | Infrastructure (network-based) | -37.8628 | 145.0196 | 1 | CitiPower | Report | 8382 | 0.00023958 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | Connection
CEOT sent fault truck to check site was safe and no damage to assets. The grass fire was extinguished on arrival with the CFA on site. | 2 EDWARD PLACE, TRARALGON VIC 3844 | 2604178 |  | Bird |  |  |  | Phase to earth | 1 | IMS 223979. Fault crew called to fire at base of concrete pole 2604178 on the Traralgon Maffra Road, Traralgon. Fire on ground and 2 dead birds (crows) found at the base of the pole. Grass fire area burnt was approximately 25 x 15 metres in size. 66kV feeder had 1 reclose, on supply when the crew arrived. | Conductor (bare) | 0 | 0 | 0 |  | TGN-MFA | Bird Incident | Grassfire | 29/08/2016 15:30 | 1 | Small: 10 - 1000 sq.m | 2827 | Roadway |  | 20160830SPN_01 | Infrastructure (network-based) | -38.1844 | 146.5619 | 1 | AusNet Services Distribution | Report | 11231 | 0.031824 | 66kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Animal
A water board employee received an electric shock whilst in the process of applying a bonder to a water meter he was in the process of changing, He stopped work immediately and informed his supervisor who called the fault in to Ausnet. On arrival the faults truck conducted an nst test which failed registering 1.5 ohms on the neutral, and 2.2volts to an independent earth | 60 DALY STREET, DALYSTON VIC 3992 | 2811749 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 223481. Water board employee replacing water meter and received shock from pipe. | Customer installation | 0 | 2 | 0 |  | wgl23 | The fault was tracked down to a corrosive joint in a junction box on pole 2811749 and a faulty grey overhead service. Tests conducted at numbers 6064/66// 68 Daly st Dalyston showed 0.2 ohms on the neutral and 0v to an independent earth. | Minor shock | 42498.5417 |  |  | 2829 | Residential |  | 20160830SPN_03 | Infrastructure (network-based) | -38.5619 | 145.546 | 1 | AusNet Services Distribution | Report | 3729 | 0.0069896 | Low voltage AC (<1kV) | Moorabbin Airport | 3992 | Dalyston | Connection
On arrival crew isolated supply at the service pit to enable REC to repair. | 7424 NORTHERN HIGHWAY, STRATHALLAN VIC 3622 | 30299607 | Working too close to underground cables | [5 empty] | 1 | An REC reported a digger hit an consumer mains cable, approx. 300m from the pit at the incident location Crew attended and found LV supply service fuse at pole substation was blown. There was no ground fire or injuries reported. | Customer installation | 2 | 2 | 2 |  | ECA012 | Digging above service cable | Loss of supply;No Go Zone (contact) | 18/08/2016 17:27 |  |  | 2845 | Roadway |  | 20160901PWA_03 | Infrastructure (network-based) | -36.2687 | 144.7052 | 1 | Powercor | Report | 3751 | 0.014818 | Low voltage AC (<1kV) | Bendigo Airport | 3622 | Strathallan | Dug up
Employee documented incident and submitted report | 127 BALLARAT ROAD, BELL PARK VIC 3215 | 32076069 | Unauthorised work | [5 empty] | 2 | An Employee driving past noticed an illegally raised service line. service line was raised usually a wooden support, | Service conductor | 2 | 2 | 2 |  | GL015 | Illegal raising height of service line using temporary support by unknown persons | No Go Zone (contact) | 25/08/2016 11:28 |  |  | 2860 | Residential |  | 20160905PWA_02 | Infrastructure (network-based) | -38.1174 | 144.3319 | 1 | Powercor | Report | 3767 | 0.0099421 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Park | Other
On arrival crew completed repairs | 47-69 SWANN DRIVE, DERRIMUT VIC 3030 | 33107381 | Copper theft | [5 empty] | 2 | An Employee (Matthew Shiberras) found earths stolen at the incident location, while on route to another work location. A crew attended, made safe and repaired the earths. | Earth/earthing | 2 | 2 | 2 |  | SU013 | Theft of earthing cables | Damage to network assets | 26/08/2016 12:29 |  |  | 2867 | Roadway |  | 20160906PWA_05 | Infrastructure (network-based) | -37.8025 | 144.7726 | 1 | Powercor | Report | 3774 | 0.018972 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply to allow repairs to POEL. | 321 BATEY ROAD, INVERGORDON VIC 3636 | 33091566 |  |  |  | Fault on customer installation |  |  | 2 | Vic Fire reports top of pole sparking and arcing at incident location. Crew attended and found service wire hook detached from private pole arm and junction box arcing/sparking. While the crew were at site, the cross-arm of the customerâ€™s first private pole broke. There was no ground fire or injuries. | Private overhead electric line (POEL) | 2 | 2 | 2 |  | SHN011 | POEL crossarm deteriation | Loss of supply | 31/08/2016 0:21 |  |  | 2872 | Agricultural |  | 20160906PWA_08 | Infrastructure (network-based) | -36.189 | 145.6165 | 1 | Powercor | Report | 3782 | 0.033672 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Invergordon | Crossarm
CEOT dispatched a fault crew to make safe, investigate and repair. CEOT also requested the DAO to attend. The fault crew replaced the burnt 3 phase fuse box (FOLCB) at pole LIS 513602. | 170 SOLDIERS ROAD, CALDERMEADE VIC 3984 | 513602 |  |  |  | Corrosion;Electrical breakdown |  |  | 2 | IMS 224049. Emergency Authorities reported an alleged pole fire. When AusNet Services' fault crew arrived the CFA were on site. Allegedly only the LV leads and 3 phase fuse box (Fused Over Line Connector Box) was burnt. The pole was a HV/LV wood substation pole. The DAO attended site and observed no evidence of a grass fire but there were signs of burn marks on the pole. Alleged black burnt plastic was on the ground in the vicinity. | Connection box | 0 | 0 | 0 |  | llg11 | Cause not identified but most likely a high impedance fault due to loose connection / corrosion. | Pole-top fire | 42409.0965 | 1 | Negligible: no ground fire | 2868 | Agricultural |  | 20160906SPN_01 | Infrastructure (network-based) | -38.2463 | 145.5671 | 1 | AusNet Services Distribution | Report | 3777 | 0.029299 | Low voltage AC (<1kV) | Moorabbin Airport | 3984 | Caldermeade | Connection
On arrival crew commenced repairs | 7 HAMMOND CIRCUIT, HOPETOUN PARK VIC 3340 | 34025052 | Vehicle | [5 empty] | 2 | A Moorabool Shire council officer advised one of their vehicles ran over an UG pillar at the incident location. No protection operated. There was no ground fire or injuries and no third party property damage. | LV Pillar | 2 | 2 | 2 |  | BMH006 | Pillar struck by vehicle | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/08/2016 13:04 |  |  | 2876 | Roadway |  | 20160907PWA_03 | Infrastructure (network-based) | -37.6974 | 144.4947 | 1 | Powercor | Report | 3786 | 0.02931 | Low voltage AC (<1kV) | Laverton Raaf | 3340 | Hopetoun Park | Vehicle
Tiger tails installed on service Rang and advised Laurie Crowley that: - PTW 45582 on issue was for access via Elevating Work Platform only and not for Scaffold. - Scaffold not to be accessed by persons as hazard exists where Aerial Service Cable exists thru Scaffold. - Scaffold erected in breach of Citipower NGZ advice. - CP/Pal to forward to ESV for investigation | 41 EILDON ROAD, ST KILDA VIC 3182 | 30212183 | Building too close or within the No Go Zone | [5 empty] | 2 | CitiPower crew attended site to check progress where a permit to work for mobile plant was due to expire. On arrival the crew identified that a scaffold had been erected in contact with a service cable. the permit to work was for an EWP only. | Conductor (insulated);Service conductor | 0 | 0 | 0 |  | SK013 | Interference - works in breach of permit to work issued | No Go Zone (no contact) | 42378.375 |  |  | 2887 | Residential |  | 20160909PWA_02 | Infrastructure (network-based) | -37.8612 | 144.9784 | 1 | CitiPower | Report | 12067 | 0.0078472 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3182 | St Kilda | Other
A faults crew attended and replaced the damaged single phase overhead service with a XLPE type. The United Energy Duty Officer was advised of the event. | 198 BARKLY STREET, ST KILDA VIC 3182 | 2305982 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Caller states while they were doing demolition work at the Smith Street intersection, they clipped the overhead service with an excavator near the pole. The service line is not down but appears damaged at the pole. An excavator was involved with demolition work on the corner of Barkley and Smith Streets and contacted a single phase overhead service that supplied a street light. The service is located between pole No's LIS 9176339 and 2305982. No shocks or damage to plant was sustained. Site contact: Dave 0419 513 621 | Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | An excavator was involved with demolition work and contacted a single phase overhead service that supplied a street light in the road reserve. | No Go Zone (contact) | 42652.3056 |  |  | 2895 | Roadway |  | 20160913UTD_02 | Infrastructure (network-based) | -37.8694 | 144.981 | 1 | United Energy Distribution | Report | 3808 | 0.023333 | Low voltage AC (<1kV) | Moorabbin Airport | 3182 | St Kilda | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. There were no signs of any fire. The crew replaced the fuse and supply was successfully restored. | 901 WANGARATTA-YARRAWONGA ROAD, KILLAWARRA VIC 3678 | 5696900 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 224271. On patrolling the line to locate a fault the crew found a HV fuse had hung up and candled. | EDO fuse | 0 | 0 | 0 |  | WN2 | EDO fuse tube candled. | Other electricity related | 14/09/2016 3:03 | 1 | Negligible: no ground fire | 2902 | Roadway |  | 20160914SPN_01 | Infrastructure (network-based) | -36.2967 | 146.2665 | 1 | AusNet Services Distribution | Report | 11232 | 0.038774 | 22kV AC | Wangaratta Aero | 3678 | Killawarra | Fuse
The LV intermediate crossarm was broken and required replacement along with the blue phase 250amp HRC fuse that operated from the north circuit of "Pepperell-Coleman" substation. The HV ties were also broken and were to be replaced using glove and barrier methods in daylight. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | COLEMAN PARADE, GLEN WAVERLEY VIC 3150 | 197913 | Vehicle | Precipitation |  | Conductor clashing;HV injection |  |  | 1 | At 0133hrs on 14/09/2016, 22kV feeders GW01 and GW08 circuit breakers successfully reclosed and held. Emergency services advised of a car into a pole near the corner of Coleman Parade and Dunscombe Street, Glen Waverley. A vehicle has struck a staked HV/LV intermediate pole (LIS No. 0602431) located in Coleman Parade, 1 pole west of Dunscombe Street that caused mid-span conductors to clash. Following the conductors clashing, splash marks were identified on a HV conductor after they made contact with the LV conductors and the faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Pepperell-Coleman" substation. The LEI confirmed a high voltage injection occurred (BWD 1604) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Crossarm (wood);Insulator tie wires/connections | 0 | 0 | 0 |  | GW08 and GW08 | A car into a pole near the corner of Coleman Parade and Dunscombe Street, Glen Waverley. | HV injection | 14/09/2016 1:33 |  |  | 2904 | Roadway |  | 20160914UTD_02 | Infrastructure (network-based) | -37.877 | 145.1506 | 1 | United Energy Distribution | Report | 3818 | 0.027844 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Vehicle
HV supply in section isolated and made safe to enable replacement of pole. Once replacement work was completed supply was restored to customer. | 1 HARDIE ROAD, YARRAVILLE VIC 3013 | A030063 | Vehicle | [5 empty] | 1 | Third party struck Jemena Tee-Off Pole (A030063) with vehicle on 1 Hardie Road Yarraville inturn reducing clearance of High Voltage (HV) overhead lines to approximetely 2m. The Hv overhead was supplying a dedicated Kiosk substation to a single customer who lost supply. Pole was replaced and supply was restored to premise. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | FW13 | Pole leaning over due to impact by unknown vehicle inturn causing the Tee-off conductors to be reduced to 2m over Hardie road. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/09/2016 11:02 |  |  | 2917 | Commercial |  | 20160916JEM_01 | Infrastructure (network-based) | -37.819 | 144.8594 | 1 | Jemena | Report | 3834 | 0.029711 | 22kV AC | Essendon Airport | 3013 | Yarraville | Vehicle
Doors temporarily repaired by Jemena and supply restored to customer. | 99 OLYMPIA STREET, TOTTENHAM VIC 3012 | OLYMPIA-SUNSHINE Substation | Vandalism | [5 empty] | 2 | Unknown third party vandalism to Jemena substation doors. No Copper was stolen from Jemena assets. | Indoor | 0 | 0 | 0 |  |  | Thieves broke into Indoor substation Olympia-Sunshine, nothing was stolen from Jemena assets, however copper was stolen from customer installation. | Less than $50k damage | 18/09/2016 14:00 |  |  | 2921 | Industrial |  | 20160919JEM_02 | Infrastructure (network-based) | -37.8033 | 144.8574 | 1 | Jemena | Report | 3840 | 0.031356 | 22kV AC | Essendon Airport | 3012 | Tottenham | Other
On arrival crew isolated supply, repair of conductors undertaken after ESV attendance. | 20 CALARCO DRIVE, DERRIMUT VIC 3030 | 30251726 | Working too close to overhead lines | [5 empty] | 1 | Powercor received a call of a crane contacting overhead wires, On arrival the attending crew found that HV conductors had been struck and brought to ground. Powercor advised the crane driver and one other person were taken for precautionary medical check. No evidence of fire found, Contact marks on crane. Feeder protection operated. Repair works undertaken after site attendance by ESV and Worksafe. | Conductor (bare) | 2 | 2 | 2 |  | LVN024 | Interference | No Go Zone (contact);Damage to network assets | 20/09/2016 10:40 |  |  | 2929 | Roadway |  | 20160921PWA_02 | Infrastructure (network-based) | -37.7997 | 144.7542 | 1 | Powercor | Report | 3851 | 0.016654 | 22kV AC | Laverton Raaf | 3030 | Derrimut | Vehicle
On arrival crew carried out repairs | 1232-1290 BEATTYS ROAD, ROCKBANK VIC 3335 | 32170918 | Copper theft | [5 empty] | 2 | An employee reports pole with copper earth cables missing. There was no fire, no reported injuries, shocks or third party property damages. | Earth/earthing | 2 | 2 | 2 |  | KTSMLN | Criminal activity | Damage to network assets | 16/09/2016 11:14 |  |  | 2936 | Roadway |  | 20160921PWA_07 | Infrastructure (network-based) | -37.7037 | 144.6305 | 1 | Powercor | Report | 3858 | 0.01853 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
The attending Powercor Fault Crew replaced the Pole Top Connection Box and reterminated the existing U/G Service Cable and completed an NST test which confirmed a Pass result. | 961 MURCHISON-VIOLET TOWN ROAD, ARCADIA SOUTH VIC 3631 | 33092935 |  |  |  | Corrosion |  |  | 2 | Ms Alice Austin received an electric shock while she was showering in the bathroom, when she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded U/G Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Sub-station Pole, | Services cable;Connection box | 2 | 2 | 2 |  | MNA034 | Corroded neutral in connection box | Minor shock | 29/08/2016 8:00 |  |  | 2937 | Agricultural |  | 20160922PWA_01 | Infrastructure (network-based) | -36.6119 | 145.3255 | 1 | Powercor | Report | 3859 | 0.0029479 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Arcadia South | Connection
CEOT dispatched a fault crew to isolate supply, make safe, investigate and repair. INCD-34337-x - LV circuit isolated and made safe at lis 916761. LV conductor .144 Aluminium damaged, 2 metres of conductor required and needs to be sleeved in. L51 crossarm, 2 LV ties burnt out, neutral screen service cable to number 7 needs to be replaced. Minor traffic control required. | 1 KAOLIN CLOSE, EPPING VIC 3076 | 916761 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 0 | IMS 224289. Police report live conductor on ground and sparking. An excavator hit an Optus cable and flicked up the LV. LV conductor .144 Aluminium damaged. | Conductor (bare) | 0 | 0 | 0 |  | epg12 | 3rd party excavator contacted Optus cable. | No Go Zone (no contact) | 14/09/2016 17:58 |  |  | 2945 | Construction |  | 20160922SPN_01 | Infrastructure (network-based) | -37.6456 | 145.0325 | 1 | AusNet Services Distribution | Report | 3868 | 0.025127 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | Vehicle
CEOT dispatched a fault crew and an electrical inspector (LEI). The fallen tree was suspected of causing a high voltage injection so inspectors were called to site to asses the damage. Line crews repaired the damaged conductors and also replaced blown fuses and meters. Attending inspectors confirmed that there was a high voltage injection that resulted in several properties having damage to their appliances. Customer advice forms were issued to the affected customers. | 71-73 ENNISMORE CRESCENT, PARK ORCHARDS VIC 3114 |  |  | Wind;Fallen |  |  |  | Phase to phase | 2 | IMS 224341. Tree branch has come down into HV and LV conductors causing a HV Injection. Tree located 74-76 Ennismore Crescent fell onto open bare 22kV/415v conductors. | Conductor (bare) | 0 | 0 | 0 |  | rwn26 | Vegetation: Trees Incident | HV injection | 17/09/2016 14:11 |  |  | 2947 | Residential |  | 20160922SPN_03 | Infrastructure (network-based) | -37.784 | 145.2136 | 1 | AusNet Services Distribution | Report | 3872 | 0.016729 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3114 | Park Orchards | Trees
On arrival repairs to the conductor were undertaken. | 275 PALMERS ROAD, TRUGANINA VIC 3029 | 30332332 | Working too close to overhead lines | [5 empty] | 1 | A company (J&L Earthmoving) reported their excavator had made contact with an overhead conductor at the incident location. The crew attended and confirmed that contact to a HV conductor. There was no fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | LV003 | excavator struck conductor | Loss of supply;No Go Zone (contact) | 23/09/2016 12:56 |  |  | 2962 | Construction |  | 20160926PWA_04 | Infrastructure (network-based) | -37.8314 | 144.7473 | 1 | Powercor | Report | 3889 | 0.035203 | 22kV AC | Laverton Raaf | 3029 | Truganina | Vehicle
On arrival crew isolated supply, a defect notice issued for repairs. | 14 ESSEX STREET, PRAHRAN VIC 3181 | 30216897 |  | Within clearances |  |  |  |  | 2 | An REC reported a service cable damaged while a contractor was clearing trees at the incident location. Upon arrival the crew found the service cable and the POA damaged. There were no reported injuries, third party damage or fire. | Service conductor;Connection box | 2 | 2 | 2 |  | TK004 | Vegetation: Trees Incident | Loss of supply | 26/09/2016 13:27 |  |  | 2967 | Residential |  | 20160927PWA_02 | Infrastructure (network-based) | -37.8483 | 144.9967 | 1 | CitiPower | Report | 3901 | 0.0050914 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Prahran | Other
Linesman dispatched to site. illegal connection removed | 4 SOUTHAMPTON CRESCENT, ABBOTSFORD VIC 3067 | 30171299 | Unauthorised work;Unauthorised access | [5 empty] | 2 | Corp affairs & Revenue Protection Martin Hermans (0419 350 585) report union protest have tapped illegally onto overhead mains at incident location. | Service conductor | 2 | 2 | 2 |  | NR003 | Illegal connection to Low voltage | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42622.7326 |  |  | 2977 | Roadway |  | 20160929PWA_02 | Infrastructure (network-based) | -37.8089 | 145.0054 | 1 | CitiPower | Report | 3920 | 0.01702 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | Other
CEOT dispatched a fault crew to check and make safe - DAO advised. Work party arranged for repairs and restoration of supply. | 41 SPILLERS ROAD, MACCLESFIELD VIC 3782 | 408364 |  | Wind;Fallen;MEC |  |  |  | Phase to earth | 1 | IMS 224591. Storm winds and rains caused an approx. 25 metre tall skinny stringy bark tree to fall onto 3/12 steel 12.7 kV S.W.E.R overhead conductor causing it to break and the fault current was suspected to have caused sparks and hot molten metal to ignite and start a small grass fire. ACR tripped to lockout. | Conductor (bare) | 0 | 0 | 0 |  | BGE22 | Vegetation: Trees Incident | Grassfire | 42410.6632 | 1 | Small: 10 - 1000 sq.m | 2982 | Agricultural |  | 20161003SPN_03 | Infrastructure (network-based) | -37.8835 | 145.5055 | 1 | AusNet Services Distribution | Report | 11236 | 0.018063 | 12.7kV AC (SWER) | Moorabbin Airport | 3782 | Macclesfield | Trees
Supply was isolated, iron roofing was removed and all repairs were made to assets. | 240 PASCOE VALE ROAD, ESSENDON VIC 3040 |  | Blown detritus | Wind |  | HV injection |  |  | 2 | Iron roofing from unknown premise blown onto overhead conductors breaking high voltage and low voltage crossarms and damaging conductors. As a result it caused a high voltage injection. No live conductors on the ground. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | NS18 | Iron roofing contacting the high voltage conductors which damaged the conductors and crossarms due to a storm (high winds) - refer to the attached photo. High voltage injection was confirmed. | HV injection | 42623.5354 |  |  | 3003 | Residential |  | 20161010JEM_01 | Infrastructure (network-based) | -37.752 | 144.9257 | 1 | Jemena | Report | 5179 | 0.0001088 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3040 | Essendon | Other
Crew attended and undertook repairs,. LEI attended to assess damage to installations. | 76 RAGLAN STREET, SOUTH MELBOURNE VIC 3205 | 30172293 |  | Wind;Alive;Fallen |  |  |  |  | 1 | A customer tree fell from the front of yard at the See Yup Temple. The tree contacted and brought down LV conductors and also caused the LV conductors to contact HV conductor. This resulted in HV injection damage to installation wiring. Molten conductor material also caused some damage to cars parked in the vicinity. There was no fire. | Conductor (bare) | 0 | 0 | 0 |  | AP018 | Vegetation: Trees Incident | Loss of supply;Less than $50k damage;Damage to network assets | 42410.6174 |  |  | 3007 | Residential |  | 20161010PWA_02 | Infrastructure (network-based) | -37.8368 | 144.9631 | 1 | CitiPower | Report | 3957 | 0.0020995 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3205 | South Melbourne | Trees
Crew attended isolated and replaced service | 33 HIGH STREET, ARARAT VIC 3377 | 30082584 | Working too close to overhead lines | [5 empty] | 2 | A customer reported that a front end loader had broken a service wire and the service was on the ground at the incident location. On arrival the crew found that a 3 wire neutral screen service had been struck by a tractor with a front end loader being used to remove debris from the back yard of the premises, causing it to break and fall to the ground. The tractor (rego 46433-F) was being driven by the customerâ€™s father. There was no fire or injuries. | Neutral screen | 0 | 0 | 0 |  | ART034 | interference | Loss of supply;Damage to network assets | 42561.4917 |  |  | 3033 | Residential |  | 20161012PWA_06 | Infrastructure (network-based) | -37.2836 | 142.9249 | 1 | Powercor | Report | 3992 | 0.0226 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Vehicle
The site was made safe and the service repaired. New service erected at 6.2 meters over the kerb | 37 HARVESTER AVENUE, SUNSHINE NORTH VIC 3020 | 30118142 | Vehicle | [5 empty] | 2 | A member of the public reported that a truck had contacted and bought down a service wire and it was laying on the ground at the incident location. On arrival the crew found that an LV service had been hit by a truck, resulting in it breaking and coming to ground. There were no reported injuries or other third party damage. The site was made safe and the service repaired. | Service conductor | 0 | 0 | 0 |  | SSE032 | Interference, suspect waste truck | Loss of supply | 42561.2576 |  |  | 3034 | Industrial |  | 20161013PWA_01 | Infrastructure (network-based) | -37.7605 | 144.8376 | 1 | Powercor | Report | 3993 | 0.011569 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. The Boric Acid fuse was replaced by the fault crew. | 2269 SNOW ROAD, MARKWOOD VIC 3678 | 5110573 |  |  |  | Electrical breakdown |  |  |  | IMS 224710. Fault crew attended premises after the customer reported crackling/buzzing sound from the pole transformer in front of the property. A 6 Amp Boric Acid fuse on the roadside was hung-up and candled. | Boric acid | 0 | 0 | 0 |  | wn5 | Boric Acid fuse candled. | Other electricity related | 42714.6493 | 1 | Negligible: no ground fire | 4049 | Residential |  | 20161014SPN_02 | Infrastructure (network-based) | -36.4603 | 146.5047 | 1 | AusNet Services Distribution | Report | 5021 | 0.0059722 | 22kV AC | Wangaratta Aero | 3678 | Markwood | Fuse
A ZNX faults crew attended and replaced the three phase FOLCB and supply was restored to the customer. | 28-30 KINGSLEY CLOSE, ROWVILLE VIC 3178 | 8808792 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Business name: Astrotec. Caller reports pole was on fire and the MFB and the police attended the site earlier in the day. A three phase Fused Overhead Line Connector Box (FOLCB) on pole No. LIS 8808792 located outside 28-30 Kingsley Close, Rowville caught on fire and was extinguished by the MFB. The cause was attributed to deterioration and the FOLCB that contained an underground cable was required to be replaced. | Cable;Connection box | 0 | 0 | 0 |  |  | The cause was attributed to deterioration. | Pole-top fire | 42684.6875 | 1 | Negligible: no ground fire | 4042 | Roadway |  | 20161014UTD_01 | Infrastructure (network-based) | -37.9094 | 145.2343 | 1 | United Energy Distribution | Report | 5012 | 0.040132 | Low voltage AC (<1kV) | Moorabbin Airport | 3178 | Rowville | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the tree was removed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 397 KOOYONG ROAD, ELSTERNWICK VIC 3185 | 2307333 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | At 1627hrs on 09/10/2016, 11kV feeder EL 06 circuit breaker reclosed to lockout affecting 1398 customers. During windy conditions, a council tree located near the corner of Kooyong Road and Trevelyan Street fell over the HV overhead conductors that caused a HV conductor to make contact with the LV conductors below near pole No. LIS 2307333. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the north circuit of "Sycamore-Kooyong" substation. The LEI confirmed a high voltage injection occurred (BWD 1605) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | EL 06 | Vegetation: Trees Incident | HV injection;Loss of supply | 42623.6854 |  |  | 4044 | Residential |  | 20161014UTD_03 | Infrastructure (network-based) | -37.8914 | 145.0137 | 1 | United Energy Distribution | Report | 5014 | 0.023289 | 11kV AC | Moorabbin Airport | 3185 | Elsternwick | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 787 DONCASTER ROAD, DONCASTER VIC 3108 | 7061771 |  | Wind |  | Fatigue;HV injection |  |  | 1 | At 1458hrs on 09/10/2016, 22kV feeder DC 01 circuit breaker reclosed to lockout affecting 594 customers. During extreme windy conditions, the road side high voltage conductor tie broke off from the insulator and fell onto public lighting steel catenary stay wire at pole No. 7061771. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied on the red phase from "Church-Doncaster" substation. The LEI confirmed a high voltage injection occurred (BWD 1605) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The 315amp LV fuse operated at "Church-Doncaster" substation and the public lights in the area were damaged. | Conductor (bare);Insulator tie wires/connections | 0 | 0 | 0 |  | DC 01 | The road side high voltage conductor tie broke off from the insulator. | HV injection;Loss of supply;Damage to network assets | 42623.6236 |  |  | 4046 | Roadway |  | 20161014UTD_05 | Infrastructure (network-based) | -37.7862 | 145.1375 | 1 | United Energy Distribution | Report | 5133 | 0.037161 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3108 | Doncaster | Trees
On arrival crew carried out repairs | 262-288 TARLETONS ROAD, PLUMPTON VIC 3335 | 33073880 | Copper theft | [5 empty] | 2 | A Powercor employee) reported a stolen LV earth at the incident location. On arrival the fault crew found that a 3m section of the LV earth had been cut away. There were no reported injuries or third party property damages. | Earth/earthing | 2 | 2 | 2 |  | KTS-MLN | cable theft | Damage to network assets | 42561.6889 |  |  | 4058 | Roadway |  | 20161018PWA_02 | Infrastructure (network-based) | -37.699 | 144.6717 | 1 | Powercor | Report | 5036 | 0.011662 | Earthing cable | Melbourne Airport | 3335 | Plumpton | Other
On arrival crew carried out repairs | 223 COATES ROAD, SNAKE VALLEY VIC 3351 | 30000848 |  |  |  | Overheated connection |  |  | 2 | Vic fire reported a pole fire at the incident location. On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. There was a small ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS011 | connection failure in FOLCB | Loss of supply;Grassfire | 18/10/2016 20:57 | 1 | Localised: less than 10 sq.m | 4060 | Agricultural |  | 20161019PWA_01 | Infrastructure (network-based) | -37.6341 | 143.5735 | 1 | Powercor | Report | 5038 | 0.028072 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Snake Valley | Connection
20/10/2016 - The owner of the factory contacted United Energy and advised the fence has been cut and there are exposed cables. Also mentioned the switchboard had been stripped and they have no power. The owner (Sam 0409 085 555) was contacted by the Downer supervisor who explained what had occurred. They will work together and arrange to reinstate the electricity supply to the factory. | 7-9 CAHILL STREET, DANDENONG SOUTH VIC 3175 |  | Vandalism;Unauthorised access;Copper theft | [5 empty] | 2 | During routine maintenance work, it was identified that copper conductors had been stolen from a ground type substation at 7-9 Cahill Street, Dandenong. 19/10/2016 - A Downer substation supervisor identified that a copper theft occurred at "Einsiedel-Cahill" ground type substation and the site was required to be made safe and de-commissioned for safety. The following copper conductors were stolen. - approximately 20m of 500mm copper cable (LV transformer cables) - approximately 35m 630mm copper cable (customer cables) - 2m of 35mm cables had been cut and were left on site The transformer was isolated and the HV tee-off bridges removed using live line techniques. A substation crew proceeded to decommission the ground type substation and the 22kV transformer and crossarms were removed. The police were also in attendance, took statements and commenced an investigation. | Conductor (insulated);Copper;Equipment | 0 | 0 | 0 |  | DSH 33 | Vandalism and copper theft. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/10/2016 10:00 |  |  | 4071 | Industrial |  | 20161021UTD_02 | Infrastructure (network-based) | -38.0267 | 145.2014 | 1 | United Energy Distribution | Report | 5053 | 0.026531 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Other
CEOT dispatched a fault crew to isolate, make safe and repair. The replaced the HV fuse and restored supply. | 38 SANDERS ROAD, SILVERLEAVES VIC 3922 | 2805771 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 224867. HV fuse at substation has hung-up/candled. The substation fuse was a 6A Boric Acid fuse that had candled, no fire, but well on the way to burning out. The hang-up was the tee off fuse that caused the phase down was a 25A Boric Acid fuse where the fuse pin had triggered but not enough to trigger the fuse to drop. The area is a salt affected coastal area and subject to equipment corroding and not working to design. | Boric acid | 0 | 0 | 0 |  | PHI13 | Candled BA fuse. Coastal environment. | Other electricity related | 21/10/2016 8:10 | 1 | Negligible: no ground fire | 4077 | Residential |  | 20161024SPN_02 | Infrastructure (network-based) | -38.4533 | 145.2615 | 1 | AusNet Services Distribution | Report | 11237 | 0.021366 | 22kV AC | Moorabbin Airport | 3922 | Silverleaves | Fuse
CEOT dispatched field crew and a LEI to make safe, investigate and repair. Fault crew repaired line damage and re-energised LV services. Customer Advice forms were issued to customers with damaged installations or appliances. | 170 GEMBROOK-TONIMBUK ROAD, GEMBROOK VIC 3783 | 5695833 |  | Precipitation;Wind;Fallen |  |  |  | Phase to phase | 0 | IMS 224882. Tree down in HV/LV has caused a HVI. Strong winds and recent rain conditions cause tree to fall into overhead HV conductors. Tree fell from property no 195 Gembrook-Toninbuc Rd, dragging HV cables onto LV cables. Damage sustained: House no. 210 - blown surge diverter and a blown light on fish tank; House no. 185 - air conditioner split unit condenser is not running; and Two properties with no access. All properties left on supply. Passed voltage and NST tests. | Conductor (bare) | 0 | 0 | 0 |  | ofr23 | Vegetation: Trees Incident | HV injection | 22/10/2016 17:35 |  |  | 4080 | Agricultural |  | 20161024SPN_04 | Infrastructure (network-based) | -37.9695 | 145.568 | 1 | AusNet Services Distribution | Report | 5068 | 0.034179 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3783 | Gembrook | Trees
On arrival crew carried out repairs | 431-533 TROUPS ROAD S, MOUNT COTTRELL VIC 3024 | 33071976 | Copper theft | [5 empty] | 2 | When responding to a no supply report a Powercor employee advised of part theft of underground service cable between the substation and lv pit at the incident location. There was no fire, injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN021 | Theft of service cable | Loss of supply;Damage to network assets | 21/10/2016 17:03 |  |  | 4090 | Roadway |  | 20161026PWA_03 | Infrastructure (network-based) | -37.7689 | 144.6645 | 1 | Powercor | Report | 5082 | 0.029234 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
A faults truck attended and found a hanging pole box that had been on fire previously. The cause was unknown and the unused pole box was removed. In addition, the red phase LVABC IPC connection was replaced on pole number LIS 1819500. | HIGHETT ROAD, HIGHETT VIC 3190 | 1819291 |  | Precipitation |  | Moisture ingress |  |  | 2 | Caller reports of a pole fire near the railway station in Highett Road next to the Hawker Bar around the corner from Graham Road. Caller contacted the United Energy faults and emergencies call centre advising of a pole fire near the Highett Railway Station at pole number LIS 1819291. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but he pole box had been hanging upside down. | Pole-top fire | 42410.4792 | 1 | Negligible: no ground fire | 4087 | Roadway |  | 20161026UTD_02 | Infrastructure (network-based) | -37.9486 | 145.0417 | 1 | United Energy Distribution | Report | 5075 | 0.021282 | Low voltage AC (<1kV) | Moorabbin Airport | 3190 | Highett | Pole
The crew made safe by removing all the high voltage fuses. One bay of high voltage overhead line has been removed. The substation has also been removed and will not be replaced. | 270 BULBAN ROAD, WERRIBEE VIC 3030 | 30117723 | Vandalism;Copper theft | [5 empty] | 1 | The report room received reports of a pole down at the incident location. On arrival the fault crew found that some-one had used a chainsaw to cut down the substation pole which services the abandoned property at the incident location. The attending crew heard noises coming from the abandoned house and investigated and were confronted by a man who began yelling. The crew backed away and the police were called. Police (Werribee depot) arrived and the felon was arrested, later a quantity of copper and parts of the substation were found in the offenderâ€™s car which has been impounded. Two high voltage fuses were found to have blown, however the third phase was still â€œALIVEâ€. Due to damage sustained to the transformer (3phase 63kVA) a quantity of oil has escaped into the ground and requires environmental clean-up. There was no fire, injuries or third party property damage. | Conductor (bare);Transformer | 2 | 1 | 2 |  | WBE023 | vandalism and theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/10/2016 9:57 |  |  | 4102 | Agricultural |  | 20161028PWA_02 | Infrastructure (network-based) | -37.9172 | 144.6135 | 1 | Powercor | Report | 5096 | 0.034363 | 22kV AC | Laverton Raaf | 3030 | Werribee | Other
The fallen 3 phase overhead service that was contacted by the crane truck was isolated and made safe. The faults crew installed a new three phase overhead service and supply was restored. | 26 COLCHESTER ROAD, ROSEBUD WEST VIC 3940 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Wire Down - Customer advised that a crane has brought down the powerlines from the pole to factory 2 and the wire is still attached to the top of the pole. There was some sparking but it's stopped now and the customer has no power. A crane was completing work at the property and contacted the 35mm 3 phase overhead service bringing it down to the ground. No injuries or damage was sustained. NPS Crane Hire Owner - Mark 5977 8999 Operator - Ken 0427 686 231 | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | A crane truck contacted the overhead service. | Loss of supply;No Go Zone (contact) | 28/10/2016 13:15 |  |  | 4115 | Roadway |  | 20161031UTD_06 | Infrastructure (network-based) | -38.3797 | 144.8829 | 1 | United Energy Distribution | Report | 5335 | 0.020903 | Low voltage AC (<1kV) | Moorabbin Airport | 3940 | Rosebud West | Vehicle
The faults crew replaced the LV white phase fuse at the east circuit of "Bayview-Long Island" substation that supplied the single customer and replaced the badly burnt pole box on pole No. LIS 1106903. The LEI checked premises in the vicinity but the only damage occurred at number 28 where the service fuse was also badly burnt on the meter panel. It was suspected the cause was possibly lightning and the damaged single phase meter was replaced. A defect notice was left with the customer as the main switchboard and meter panel are damaged and requires repairs and/or replacement. Internally the Commander phone system was severely damaged and supply has been left off until a REC completes the necessary repairs. Procedures as indicated in the work instruction for HV injections has been followed with a claim form left for the single customer. | 28 BAYVIEW ROAD, HASTINGS VIC 3915 | 1106903 |  | Lightning |  | HV injection |  |  | 1 | Business name: Mission to Seamen, Hastings. Customer advised they have no power and checked the meter and found evidence of burning with a small hole in the meter panel. The customer at 28 Bayview Road lost their electricity supply and identified burning around their meter in the enclosure when checking for the cause of the outage. A faults crew attended and suspected that a HVI had occurred and requested that a LEI attend. The LEI confirmed a high voltage injection occurred (MOR 1607) affecting the single customer that sustained damage to appliances and equipment. It was suspected that street lights were also affected but an investigation revealed no damage. | Smart meter;Connection box | 0 | 0 | 0 |  | HGS 21 | It was suspected the cause was possibly a lightning strike. | HV injection;Loss of supply | 29/10/2016 9:30 |  |  | 4118 | Residential |  | 20161102UTD_01 | Infrastructure (network-based) | -38.2904 | 145.2105 | 1 | United Energy Distribution | Report | 5118 | 0.039156 | Low voltage AC (<1kV) | Moorabbin Airport | 3915 | Hastings | Lightning
A faults truck attended to reconnect the property following the rectification of the customer installation faults by a REC and found the REC has completed the work without having supply isolated to complete the work safely. The live overhead service remained connected to the FMJB and the REC installed the new single phase consumers mains with the active terminal remaining alive. The REC also removed two meters from the meter board to carry out the work. The hair dressing business at the front is affected but the supply to the rear domestic occupancy remained alive. The faults crew requested that ESV are advised as they felt the work was completed unsafely by the REC. 02/11/2016 - A faults truck attended, installed a new single phase meter and reconnected the property after installation tests passsed. | 60 ESSEX ROAD, MOUNT WAVERLEY VIC 3149 |  | Caused by REC/contractor | [5 empty] | 2 | REC No. 3824 (Darren Cross 0403 248 153) has installed new consumers mains, meter panel, main switch board, main earthing system and provided Prescribed CES No. 15822673. REC has completed the work after the customer lost power as the service fuse had blown. The REC completed fault rectification work at the premise and contacted the United Energy faults and emergencies call centre as the property is ready for re-connection. A copy of the CES has been left in the meter panel. | Aluminium twisted (grey);Connection box;Customer installation | 0 | 0 | 0 |  |  | Interference with MEC's assets that resulted in a reduction of electrical safety. | Loss of supply | 31/10/2016 17:00 |  |  | 4127 | Residential |  | 20161103UTD_01 | Infrastructure (network-based) | -37.8635 | 145.1191 | 2 | United Energy Distribution | Report | 5345 | 0.026838 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Other
CEOT dispatched a fault crew to isolate supply, make safe and arrange for repair. The street light pole was isolated at an underground supply pit. Passed onto public lighting crew to complete repairs to the 250 Watt HP Sodium Vapour street light. The fire at the street light head was extinguished when fault crew arrived on site. | 93 PRINCE STREET, ROSEDALE VIC 3847 | 5643747 |  |  | Highly unlikely | Electrical breakdown |  |  | 2 | IMS 225046. Streetlight head was reported on fire out the front of 93 Princes St, Rosedale. | Services pit;Public lighting | 0 | 0 | 0 |  | tgn41 | Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors. | Other electricity related | 42532.9549 | 1 | Negligible: no ground fire | 4137 | Roadway |  | 20161107SPN_02 | Infrastructure (network-based) | -38.151 | 146.7825 | 1 | AusNet Services Distribution | Report | 5152 | 0.0058449 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3847 | Rosedale | AF Other
On arrival Crew isolated supply for the REC to carry out the repair. | 27 ORCHID COURT, BEAUFORT VIC 3373 | 30308098 | Working too close to underground cables | [5 empty] | 2 | A customers REC reported that the customer has dug up the underground cable with the digger. On arrival the crew found that the digger had pulled up the low voltage underground service cable while removing a tree stump resulting in damage to the conduit of the customerâ€™s underground mains. There was no ground fire. There was no reported shock or injuries. | Customer installation | 2 | 2 | 2 |  | BAS011 | Excavation on private property | No Go Zone (contact) | 31/10/2016 17:25 |  |  | 4142 | Residential |  | 20161108PWA_02 | Infrastructure (network-based) | -37.4292 | 143.3685 | 1 | Powercor | Report | 5157 | 0.0007037 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3373 | Beaufort | Dug up
On arrival crew isolated supply and commenced repairs | 637 CORAGULAC-BEEAC ROAD, WARRION VIC 3249 | 30052015 |  | Wind |  |  |  |  | 1 | The Customer reported a garage roof had blown off and hit power lines at the incident location. On arrival the crew found that a large section of roof had blown off a nearby garage, landing on the 3 phase LV copper mains, causing them to break and fall to the ground. There were no ground fires or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | CLC003 | roofing blown across line | Loss of supply | 30/10/2016 14:15 |  |  | 4145 | Roadway |  | 20161108PWA_04 | Infrastructure (network-based) | -38.2223 | 143.5719 | 1 | Powercor | Report | 5161 | 0.01831 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3249 | Warrion | Other
On arrival crew commenced repairs | 760 BLACKGATE ROAD, MOUNT DUNEED VIC 3217 | 33106443 |  |  |  | Unknown technical factor |  |  | 2 | A customer reported loss of power to their residence near the incident location. On arrival the fault crew found that the FMJB mounted on the concrete pole had caught fire and burnt out at the incident location. The fire had self-extinguished. There was no ground fire and no injury as a result of this incident. | Connection box | 2 | 2 | 2 |  | WPD022 | Insufficient remains to accurately determine cause. | Pole-top fire | 16/11/2016 11:00 | 1 | Negligible: no ground fire | 4175 | Agricultural |  | 20161116PWA_04 | Infrastructure (network-based) | -38.283 | 144.3152 | 1 | Powercor | Report | 5212 | 0.041579 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Mount Duneed | Pole
Emergency high voltage switching was completed to remove the tree branch using glove and barrier methods from the aluminium overhead conductors prior to supply being restored. | 733 HAMPTON STREET, BRIGHTON VIC 3186 | 1804512 |  | Blown branch/vegetation |  |  |  |  | 2 | Per MFB - Pole fire and emergency service are on site. During strong winds and rain, a large cypress tree branch located in the front yard of 733 Hampton Street near pole No. LIS 1804512 contacted the 11kV overhead conductors and caught fire. It was estimated that a tree canopy fire of approximately 2sqm was started that was extinguished by the MFB. | Conductor (bare) | 0 | 0 | 0 |  | NB12 | Vegetation: Trees Incident | Other vegetation | 22/10/2016 17:45 | 1 | Negligible: no ground fire | 4172 | Residential |  | 20161116UTD_01 | Infrastructure (network-based) | -37.9218 | 145.0053 | 1 | United Energy Distribution | Report | 5208 | 0.040553 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Trees
On arrival crew commenced repairs | 1569-1593 DIGGERS REST-COIMADAI ROAD, TOOLERN VALE VIC 3337 | 30103381 | Copper theft | [5 empty] | 2 | A customer reported a copper theft at the incident location. The Powercor fault crew subsequently found a section of an un-commissioned supply had been stolen by persons unknown. There were no reported injuries or fire. | Services cable | 2 | 2 | 2 |  | MLN012 | Interference - copper theft | Damage to network assets | 42471.375 |  |  | 4184 | Roadway |  | 20161121PWA_01 | Infrastructure (network-based) | -37.609 | 144.6026 | 1 | Powercor | Report | 5358 | 0.039968 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
On arrival crew isolated supply and carried out repairs | 860 BERRIMAL-WEDDERBURN ROAD, BERRIMAL VIC 3518 | 32029053 | Manned aircraft | [5 empty] | 1 | Pilot of fixed wing light aircraft reported making contact with SWER and breaking cable off between 2 poles. Crew attended and found cable across the road broken. Pilot was not injured was able to land his aircraft successfully. There was no ground fire or injuries. | Conductor (bare) | 2 | 2 | 2 |  | CTN002 | Aircraft struck line | Loss of supply | 19/11/2016 11:44 |  |  | 4193 | Agricultural |  | 20161121PWA_08 | Infrastructure (network-based) | -36.4924 | 143.4793 | 1 | Powercor | Report | 5235 | 0.037137 | 12.7kV AC (SWER) | Bendigo Airport | 3518 | Berrimal | Other
CEOT dispatched a fault crew to isolate, make safe and investigate. The HV line was isolated and the conductor was sleeved and repaired. It appears the conductor was corroded. | 250 VENTNOR BEACH ROAD, VENTNOR VIC 3922 | 2807007 |  |  |  | Corrosion |  | Phase to earth | 1 | IMS 225339. HV overhead conductor broke and fell to the ground. A 5m x 10m shrub fire occurred. The CFA was called to extinguish the fire. HV fuse operated. It appeared to be a conductor fail between poles 2807007 Harbison P27 and Harbison Rd P28 where the conductor fell to ground in the road reserve where a small fire had ignited in shrub. | Conductor (bare) | 0 | 0 | 0 |  | phi12 | HV overhead conductor breakage. | Other vegetation | 21/11/2016 10:20 | 1 | Small: 10 - 1000 sq.m | 4189 | Agricultural |  | 20161121SPN_01 | Infrastructure (network-based) | -38.4819 | 145.2103 | 1 | AusNet Services Distribution | Report | 5231 | 0.015308 | 22kV AC | Moorabbin Airport | 3922 | Ventnor | Conductor
Emergency high voltage switching was completed and the capacitor bank was isolated by opening the vacuum switches and the HV fuses. A construction crew attended later that afternoon and completed repairs to the Capacitor Bank. | 33 LEONARD AVENUE, NOBLE PARK VIC 3174 | 618397 |  | Cold |  | Electrical breakdown |  |  | 2 | Per MFB - Pole fire. During cool early morning conditions, Capacitor Bank "LeonardHellyer" located at pole No. LIS 0618397 outside 33 Leonard Avenue, Noble Park failed due to the centre phase HV dropper burning off at the vacuum switch. The fault apparently caused a brief explosion at the pole top but there was no fire damage to the pole. | Capacitor bank;Pole top;Other | 0 | 0 | 0 |  | NP25 | The centre phase HV dropper burnt off at the vacuum switch at the capacitor bank. | Pole-top fire | 17/11/2016 5:54 | 1 | Negligible: no ground fire | 4183 | Roadway |  | 20161121UTD_01 | Infrastructure (network-based) | -37.9709 | 145.1756 | 1 | United Energy Distribution | Report | 5222 | 0.022954 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | AF Other
The ZNX No Go Zone Co-ordinator attended the site following advice from a meter and servicing crew that scaffolding had blown into the No Go Zone after a photo was provided - attached. The scaffold had been repositioned outside the No Go Zone area and the Co-ordinator proceeded to contact Worksafe (Cam Drane) as the conditions of the Permit to Work had not been abided to. There was no damage to United Energy assets in this instance and they will continue to monitor the site for any further breaches. | 730A CENTRE ROAD, BENTLEIGH EAST VIC 3165 |  | Working too close to overhead lines | Wind |  |  |  |  | 2 | The ZNX No Go Zone (NGZ) Co-ordinator attended a construction site that had been issued a Permit to Work prior to strong winds blowing some scaffold and hoarding into the NGZ area. Following strong winds, scaffolding had fallen into the No Go Zone area that breached the conditions of the Permit to Work that had been issued on 20/09/2016. ZNX had been monitoring the construction site very closely and a Permit to Work was issued with very strict restrictions due to the close proximity of the 66kV, 11kV and LV conductors that had been off-setted specifically for this project. | Conductor (bare) | 0 | 0 | 0 |  |  | Scaffolding had fallen into the No Go Zone area that breached the conditions of the Permit to Work that had been issued. The scaffold had been repositioned outside the No Go Zone area and the Co-ordinator proceeded to contact Worksafe. | No Go Zone (no contact) | 42561.2708 |  |  | 4040 | Construction |  | 20161013UTD_04 | Infrastructure (network-based) | -37.9214 | 145.0594 | 1 | United Energy Distribution | Report | 5007 | 0.034914 | Low voltage AC (<1kV);11kV AC;66kV AC | Moorabbin Airport | 3165 | Bentleigh East | Other
CEOT dispatched a fault crew to isolate and make safe. CEOT also advised the DAO to attend to investigate. The fire was put out by the CFA. AusNet Services' line crew were on-site and were completing splice works to HV conductors. HV conductors were measured at >8.0m from the ground. | 271 ARMY ROAD, PAKENHAM VIC 3810 | 503441 |  | Precipitation;Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 711. Tree fire attended by CFA. A large tree approximately 15m away from the power line was >20m tall and fell across HV steel conductors. Fire and burn damage to tree in immediate area, but no significant damage to the ground or any property or livestock. HV substation fuse operated at BD163. | Conductor (bare) | 0 | 0 | 0 |  | phm33 | Vegetation: Trees Incident | Grassfire | 42714.691 | 1 | Localised: less than 10 sq.m | 4048 | Agricultural |  | 20161014SPN_01 | Infrastructure (network-based) | -38.0448 | 145.5009 | 1 | AusNet Services Distribution | Report | 5019 | 0.029841 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the large tree was removed. The LV fuses for the north circuit of "Terrara-Hawthorn" substation operated and required replacement. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | TERRARA ROAD, VERMONT VIC 3133 | 7020341 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1521 hrs on 09/10/2016, 22kV feeder RWT 34 circuit breaker reclosed to lockout affecting 1868 customers. During strong gusty winds, a large council tree uprooted and contacted the 22kV overhead conductors that caused a HV conductor to briefly contact the LV conductors below, near the corner of Terrara and Hawthorn Roads between pole No's 7020341 and 7023539. A faults crew attended and requested that a LEI investigate for damage as a HVI was suspected to customers supplied from "Terrara-Hawthorn" substation. The LEI confirmed a high voltage injection occurred (BWD 1606) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. There were initial suspicions that customers supplied from the east circuit of "Jolimont-Terrara" may have sustained damage but no damage was found. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | RWT 34 | Vegetation: Trees Incident | HV injection;Loss of supply | 42623.6396 |  |  | 4043 | Roadway |  | 20161014UTD_02 | Infrastructure (network-based) | -37.8477 | 145.189 | 1 | United Energy Distribution | Report | 5013 | 0.0012303 | 22kV AC | Moorabbin Airport | 3133 | Vermont | Trees
On arrival crew carried out repairs | 474 BLACKWOOD ROAD, MACEDON VIC 3440 | 32045417 |  | Wind;Fallen;MEC |  |  |  |  | 1 | Customer reported a fire at the incident location. On arrival the crew found that a HV conductor had been brought down by a tree, a ground fire of 1500m square resulted where the HV conductor broke and came to the ground. The tree was 10 metres from the conductors and outside the clearance space. There were no injuries. | Conductor (bare) | 2 | 2 | 2 |  | WND011 | Vegetation: Trees Incident | Grassfire | 15/10/2016 11:50 | 1 | Medium: 1000 sq.m - 10 ha | 4053 | Forest - native (not park) |  | 20161017PWA_02 | Infrastructure (network-based) | -37.4207 | 144.5184 | 1 | Powercor | Report | 5030 | 0.020534 | 22kV AC | Melbourne Airport | 3440 | Macedon | Trees
CEOT dispatched a fault crew to isolate supply and make safe. The crew arrived at the scene and isolated supply and made safe, opened BW1409. CEOT organised for a LEI to also attend due to a possible HVI. The crew made repairs to the overhead lines. The crew removed all service fuses on the affected circuit and energised the LV line. The attending LEIs checked for signs of HV injection damage and there was no evidence showing. The LEIs progressed to test and switch residences on as they were available. All premises passed tests and remained on supply. | 19 DUNKINSON STREET, NARRE WARREN VIC 3805 | 504819 |  |  |  | Defective component |  |  | 1 | IMS 224761. CEOT received a report from the CFA of a fire on LV crossarm @ LIS #504819 intermediate structure. The HV crossarm was found broken and the HV overhead conductor fell into LV conductor. HV fuse operated, BW3356. No ground fire occurred. No HVI damage occurred to customers' properties. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | nrn14 | A broken HV crossarm. | Pole-top fire | 16/10/2016 18:35 | 1 | Negligible: no ground fire | 4056 | Residential |  | 20161017SPN_02 | Infrastructure (network-based) | -38.0299 | 145.3153 | 1 | AusNet Services Distribution | Report | 5034 | 0.015955 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3805 | Narre Warren | Crossarm
On arrival crew commenced repairs | 860 KOROROIT CREEK ROAD, ALTONA NORTH VIC 3025 | 30116817 | Vehicle | [5 empty] | 1 | The fire brigade reported that a car has collided with a pole at the incident location. On arrival the fault crew found a vehicle had struck a pole causing conductor clashing and hardware damage. The feeder circuit breaker operated to lockout. While rendering assistance to the driver, a passer-by was subsequently struck by a conductor as it fell to ground. The passer-by was checked out by attending ambulance crew, he doesn't believe he received a shock and subsequently stated he has some bruises and a headache. There was no fire or shocks. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | AC024 | Vehicle struck pole | Loss of supply;Damage to network assets | 17/10/2016 6:56 |  |  | 4057 | Roadway |  | 20161018PWA_01 | Infrastructure (network-based) | -37.8448 | 144.7912 | 1 | Powercor | Report | 5035 | 0.0024722 | 11kV AC;66kV AC | Laverton Raaf | 3025 | Altona North | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. | 248 ERAMOSA ROAD W, MOOROODUC VIC 3933 | 1122093 |  | Wind |  | Fatigue;Leakage |  |  | 1 | At 1416hrs on 15/10/2016, 22kV feeder MTN 22 circuit breaker reclosed to lockout affecting 3203 customers. During strong winds on 15/10/2016, HVABC failed mid-span in Eromosa Road, Moorooduc at switch pole LIS No. 1122093 opposite house number 248. There was evidence of a small grass fire that was found by the faults crew and it was suspected that molten metal fell towards the ground, but the strong north winds blew the embers across the road into a dry grassed area where a small 3m x 5m fire started. The fire had self extinguished when the faults crew arrived at the site. | Conductor (ABC) | 0 | 0 | 0 |  | MTN 22 | HVABC failed mid-span. | Grassfire | 15/10/2016 14:16 | 1 | Small: 10 - 1000 sq.m | 4061 | Roadway |  | 20161019UTD_01 | Infrastructure (network-based) | -38.2156 | 145.1225 | 1 | United Energy Distribution | Report | 5039 | 0.0059479 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Trees
Crew made safe & repaired low voltage conductors. | 12 PEARCE STREET, YARRAVILLE VIC 3013 |  |  | Blown branch/vegetation |  |  |  |  | 2 | It was reported that live low voltage conductors (2 bays) were on the ground. Tree branch fell into the conductors in high winds causing the conductors to fall to the ground. | Conductor (bare) | 0 | 0 | 0 |  | FE5 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/10/2016 3:06 |  |  | 4068 | Residential |  | 20161021JEM_02 | Infrastructure (network-based) | -37.8195 | 144.8836 | 1 | Jemena | Report | 5323 | 0.015637 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A further trouble order was created for 19 x 150w HPS lanterns to be replaced following the high voltage injection. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | CENTRE DANDENONG ROAD, DINGLEY VILLAGE VIC 3172 | 208971 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 2143hrs on 17/10/2016, 22kV feeder NP 12 circuit breaker successfully reclosed and held. A car has contacted a stay wire attached to pole No. LIS 0630113 located in Centre Dandenong Road, 1 pole north of Lower Dandenong Road, Dingley Village. The LV bus fuses at "Centre Dnong-Lwr Dng" substation had operated and there was evidence of the HV LV conductors clashing at this location. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Centre Dnong-Lwr Dng" substation. The LEI confirmed a high voltage injection occurred (KEY 1605) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Guy wire;Public lighting | 0 | 0 | 0 |  | NP 12 | A car has contacted a stay wire attached to pole No. LIS 0630113 located in Centre Dandenong Road, Dingley Village. | HV injection | 17/10/2016 21:43 |  |  | 4069 | Roadway |  | 20161021UTD_01 | Infrastructure (network-based) | -37.9894 | 145.1415 | 1 | United Energy Distribution | Report | 5135 | 0.028191 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3172 | Dingley Village | Vehicle
On arrival crew commenced repairs. The effected circuit was isolated and each premise inspected by a team of L.E.I.s. High voltage injection damage was found at one premise and another four were isolated (unable to test, no one at home). | 56 BROADWAY, CAMBERWELL VIC 3124 | 30166844 | Vehicle | [5 empty] | 1 | A customer reported that a tree had fallen across the power-lines after being struck by a large truck carrying a container and power has been lost at the incident location. On arrival the fault crew found that a large branch had fallen across the power-lines striking the11kV conductors then fallen onto the low voltage conductors then onto the ground. Clashing of conductors has occurred and the low voltage switch wire was found wrapped around the 11kV conductors. Protection operated to clear the faulted equipment from the CitiPower network. High voltage injection to the east low voltage circuit of the Broadway-Stanhope substation occurred. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | CL038 | Vegetation: Trees Incident | HV injection;Loss of supply | 21/10/2016 13:26 |  |  | 4079 | Roadway |  | 20161024PWA_01 | Infrastructure (network-based) | -37.8255 | 145.0669 | 1 | CitiPower | Report | 5066 | 0.010873 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3124 | Camberwell | Trees
The employee who received the shock informed the project Leader and work ceased. The employee was taken for a precautionary medical assessment and subsequently issued with a certificate of capacity and returned to work to complete the days work. | 7 HAMILTON ROAD, HORSHAM VIC 3400 | [5 empty] | Incorrect electrical isolation and/or permits | Phase to earth | 2 | During planned works at the incident location a Powercor employee brushed against a set of terminals within a transformer control box and received a slight electrical shock. There was no fire or third party property damage. | Zone substation;Transformer | 2 | 2 | 2 |  | HSM | Secondary isolation of tap changer control was not adequate. | Minor shock | 42531.6042 |  |  | 4089 | Other | Substation | 20161026PWA_02 | Infrastructure (network-based) | -36.7348 | 142.2058 | 1 | Powercor | Report | 5102 | 0.023387 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Other
Citipower representative attended site. Advise given to builder that works may not proceed until assets relocated. Builder appears to be disputing initial no go zone inspection report. | 76 LANG STREET, SOUTH YARRA VIC 3141 | 30216032 | Building too close or within the No Go Zone | [5 empty] | 2 | Residential building being constructed in vicinity Citipower High Voltage (11000 volt) and Low Voltage (240 volt) Overhead power lines on Powell St frontage. Building being constructed appears to not comply with Table 313 minimum clearances between Buildings/Structures and Overhead Power Lines derived from Electricity Safety (Installations) Regulations 2009. There was no injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | PR023 | Building activities | No Go Zone (no contact) | 26/10/2016 11:15 |  |  | 4098 | Construction |  | 20161028PWA_01 | Infrastructure (network-based) | -37.8415 | 144.9891 | 2 | CitiPower | Report | 5092 | 0.0094873 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3141 | South Yarra | Other
The crew isolated supply two both of the services and these will be re-instated once the customers RECâ€™s have made the required repairs. Both customers were advised to engage an REC to carry out the necessary repairs. | 48 WAWUNNA ROAD, HORSHAM VIC 3400 | 32101946 | Vehicle | [5 empty] | 2 | Multiple reports were received that a truck had hit wires outside the above location. On arrival the crew found that an unknown truck had made contact with the services to 48 & 50 Wawunna Road Horsham. The impact of the trucked pulled the two services away from their points of attachment at the customerâ€™s premises. Damage was sustained to the fascia of both premises.There was no shock or fire start. | Service conductor | 2 | 2 | 2 |  | HSM010 | Truck struck service lines | Loss of supply | 26/10/2016 22:01 |  |  | 4106 | Residential |  | 20161028PWA_03 | Infrastructure (network-based) | -36.703 | 142.1964 | 1 | Powercor | Report | 5198 | 0.026472 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Vehicle
The crew attended and confirmed contact with a HV conductor had been made. Repairs to conductor completed. | 51 REGAN STREET, ST ALBANS VIC 3021 | 30107569 | Working too close to overhead lines | [5 empty] | 1 | Jim Spence working on the â€œLevel Crossing Removal Authorityâ€ project reported an excavator had made contact with an overhead conductor at the incident location. Damage to excavator unable to be determined. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | SA009 | Excavator contacted overhead line | No Go Zone (contact);Damage to network assets | 29/10/2016 10:46 |  |  | 4112 | Public space |  | 20161031PWA_01 | Infrastructure (network-based) | -37.7351 | 144.7914 | 1 | Powercor | Report | 5109 | 0.00046412 | 22kV AC | Melbourne Airport | 3021 | St Albans | Vehicle
The substation pole was replaced and supply restored on 24/10/2016 after the tee-off bridges were restored under Access Authority conditions and supply restored to normal. | BAY ROAD, HIGHETT VIC 3190 | 1822972 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | A Downer faults crew identified a pole fire had occurred at "Bay-Lansell" ground type substation. Following an extended period of strong rain and winds, a pole fire had occurred at ground type substation pole No. LIS 1822972 with the centre phase eye bolt and HV crossarm kingbolt burned out that required the HV/LV pole to be replaced. The crew lifted the HV tee-off bridges on the corner of Bay Road and Lansell Avenue after "Bay-Lansell" ground type substation was placed under LV parallel to maintain supply to the two street circuits. No high voltage injection occurred to customers in the vicinity supplied from 11kV feeder SR 12. | Pole (wood);Pole top;Crossarm (wood);Outdoor;Dropper/bridge | 0 | 0 | 0 |  | SR 12 | A pole fire had occurred at the ground type substation pole following rain and the cause was suspected to be tracking in the light industrial / bayside area. | Pole-top fire;Loss of supply | 22/10/2016 19:51 | 1 | Negligible: no ground fire | 4110 | Industrial |  | 20161031UTD_03 | Infrastructure (network-based) | -37.954 | 145.0231 | 1 | United Energy Distribution | Report | 5107 | 0.028185 | 11kV AC | Moorabbin Airport | 3190 | Highett | Pole
A faults crew promptly attended and proceeded to isolate and remove the melted 150w HPS lantern. A new order was created for the replacement of the defective lantern. | 1 DISCOVERY ROAD, DANDENONG SOUTH VIC 3175 | 9953514 |  | Precipitation |  | Defective component;Overheated connection |  |  | 2 | The CFA advised of a pole fire with melting and dripping plastic falling onto the road. A 150w HPS lantern on pole No. LIS 9953514 located outside 1 Discovery Road, Dandenong South caught fire and self extinguished. The cause was unknown but most likely a loose connection that overheated may have been the cause. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated may have been the cause. | Pole-top fire | 28/10/2016 6:15 | 1 | Negligible: no ground fire | 4114 | Roadway |  | 20161031UTD_05 | Infrastructure (network-based) | -38.0406 | 145.219 | 1 | United Energy Distribution | Report | 5112 | 0.005103 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Connection
On arrival crew carried out repairs to conductor | 1435 MT NAPIER ROAD, BUCKLEY SWAMP VIC 3301 | 30093590 | Working too close to overhead lines | [5 empty] | 1 | A customer reported an excavator had made contact with an overhead conductor at the incident location. The crew attended and confirmed that contact to a HV conductor had been made between LIS 713408 (Kirkwood P18) & LIS 713409 (Kirkwood P18). There was no fire or injuries. | Conductor (bare) | 2 | 2 | 2 |  | HTN003 | Excavator contacted conductor | Loss of supply;No Go Zone (contact) | 31/10/2016 12:52 |  |  | 4119 | Agricultural |  | 20161102PWA_02 | Infrastructure (network-based) | -37.864 | 142.0802 | 1 | Powercor | Report | 5129 | 0.018353 | 12.7kV AC (SWER) | Hamilton Airport | 3301 | Buckley Swamp | Vehicle
On arrival crew carried out repairs | 511 HAMMOND ROAD, MURCHISON VIC 3610 | 33095223 |  |  |  | Unknown technical factor |  |  | 1 | Vic Fire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. | Connection box | 2 | 2 | 2 |  | MNA034 | Could not be determined due to damage to FOLCB | Pole-top fire | 31/10/2016 17:29 | 1 | Negligible: no ground fire | 4122 | Roadway |  | 20161102PWA_04 | Infrastructure (network-based) | -36.5825 | 145.2287 | 1 | Powercor | Report | 8393 | 0.015365 | Low voltage AC (<1kV) | Shepparton Airport | 3610 | Murchison | Pole
Emergency switching was completed to minimise the number of customers affected and the neutral conductor was replaced/upgraded between the transformer and the reticulation under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | BARRY STREET, SEAFORD VIC 3198 |  |  |  |  | Neutral fault;HV injection |  |  | 2 | A customer who is a REC states they've had intermittent supply for the past 30 minutes. He has tested the voltage to the premise and found it's fluctuating. Customers supplied from "Barry-Fellows" pole type substation in Seaford, advised of fluctuating supply and a faults crew were dispatched. The faults crew identified the neutral connection at the 22kV 315kVA transformer had burnt off and supply was isolated. The faults crew requested that a LEI attend as a LVI was suspected to customers supplied from "Barry-Fellows" substation. The LEI confirmed a low voltage injection occurred (MOR 1608) affecting customers supplied from the transformer who sustained minor damage to appliances and equipment. | Conductor (insulated);Pole mounted;Connector/termination;Transformer | 0 | 0 | 0 |  | FTN24 | The neutral connection at the 22kV 315kVA transformer had failed. | HV injection;Loss of supply | 30/10/2016 18:50 |  |  | 4120 | Residential |  | 20161102UTD_02 | Infrastructure (network-based) | -38.1143 | 145.1478 | 1 | United Energy Distribution | Report | 5120 | 0.034328 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
On arrival crew could find no evidence of damage to assets | 785 GOULBURN VALLEY HIGHWAY, CONGUPNA VIC 3633 | 33091042 |  |  |  | Unknown technical factor |  |  | 2 | A customer reported a fire at the incident location ( SHTSNKA No 1 66kv line). On arrival the crew found that a ground fire had started at the base of a pole (approx. 1m sq) on road reserve. This incident was reported to have occurred at same time as a flashover on SHTSNKA No 2 66kv line. There were no reported injuries, shocks or third party damage. | Pole (concrete) | 2 | 2 | 2 |  | SHTSNKA1 | No direct cause at site was identified by crew | Grassfire | 42411.5958 | 1 | Localised: less than 10 sq.m | 4134 | Roadway |  | 20161104PWA_02 | Infrastructure (network-based) | -36.3144 | 145.421 | 1 | Powercor | Report | 5145 | 0.026865 | 66kV AC | Shepparton Airport | 3633 | Congupna | Pole
A Field Team Leader visited the site to assess immediate safety. At that stage it was considered it was unlikely that the boom and the conductor would clash. This non-conformance has been referred to the No Go Zone group for further assessment and follow-up. | 1200 GREAT OCEAN ROAD, BELLBRAE VIC 3228 | 33042393 | Building too close or within the No Go Zone | [5 empty] | 2 | A concerned member of the public called to say a recently installed boom gate was approximately 1.5 metres away from our assets at the incident address. The boom extends above the high voltage conductors. As the boom is in the middle of the bay (Between LIS 30270 & 30269) the sway of the conductors may encroach on the allowable clearance of 1.5 metres ( Table 225.1 of the service and installation rules). | Conductor (bare) | 2 | 2 | 2 |  | WPD021 | Customer Installing Boom Gate to close to overhead conductors | No Go Zone (no contact) | 31/10/2016 11:18 |  |  | 4144 | Commercial |  | 20161108PWA_03 | Infrastructure (network-based) | -38.3754 | 144.2148 | 1 | Powercor | Report | 5160 | 0.020381 | 22kV AC | Avalon Airport | 3228 | Bellbrae | Other
On arrival crew isolated supply and completed repairs | 653 QUEENSBERRY STREET, NORTH MELBOURNE VIC 3051 | 30198811 |  |  |  | Corrosion |  |  | 2 | MSY Technology Pty Ltd staff reported a light fitting on Public Lighting Pole was on fire at the above incident location. On arrival, the crew found that a light fitting cap on a Public Lighting Pole had caught on fire, which melted the cap and burnt the light electrical components. There was no ground fire nor third party damaged. There were no reported injuries. | Public lighting | 2 | 2 | 2 |  | VM014 | Loose connection | Pole-top fire | 28/10/2016 18:15 | 1 | Negligible: no ground fire | 4146 | Roadway |  | 20161108PWA_05 | Infrastructure (network-based) | -37.8028 | 144.9457 | 1 | CitiPower | Report | 5162 | 0.0026528 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. The HV tee-off bridges to "Cap Dng-Hastings" were lifted to enable the repairs to be safely completed. | 1120 DANDENONG-HASTINGS ROAD, CRANBOURNE SOUTH VIC 3977 | 9657245 | Vehicle | Precipitation;Wind;Cold |  | Mechanical breakdown |  |  | 1 | At 2.31AM on 10/10/2016, 22kV feeder LWN 21 circuit breaker reclosed to lockout affecting 1190 customers after a car hit pole No. LIS 3312572 and broke the stay wire. The necessary rectification work was completed and high voltage switching commenced to restore the HV feeder configuration back to normal. At approximately 3.50AM following the completion of the high voltage switching, the CFA advised of a pole fire in Dandenong-Hastings Road, Cranbourne where they promptly attended to extinguish the pole fire. At the completion of high voltage fault switching, a pole fire occurred at HV Capacitor Bank "Cap Dng-Hastings" and the CFA attended to extinguish the fire on pole No. LIS 9657245. The Capacitor Bank fuse units failed following the restoration of supply after a fault. A flash over occurred and the HV conductor fell to the ground and the pole caught fire adjacent to the 22kV fuse units. | Capacitor bank;Conductor (bare);Pole (wood);Other;Dropper/bridge | 0 | 0 | 0 |  | LWN 21 | The fault occurred at the Capacitor Bank structure following the high voltage switching restoration of the earlier event where a vehicle contacted a pole stay wire during a period of strong winds and rain. | Pole-top fire | 42653.1583 | 1 | Negligible: no ground fire | 4143 | Roadway |  | 20161108UTD_01 | Infrastructure (network-based) | -38.1347 | 145.2282 | 1 | United Energy Distribution | Report | 5182 | 0.01706 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne South | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was replaced under Access Authority conditions prior to the supply being restored. | FLAT 2 589 SOUTH ROAD, BENTLEIGH EAST VIC 3165 | 1824862 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | The MFB advised of a fire at the top of the pole outside 489 South Road, Moorabbin. It was found the double circuit sub-transmission pole was actually located outside 589 South Road, Moorabbin. During light misty drizzle, a crossarm fire occurred on a 66kV pole at the HV crossarm behind the king bolt and the centre phase conductor at pole No. LIS 1824862. The 66kV feeders "HTS-MR" & "HTS-SR" were switched out as the pole was severely damaged and required replacement. | Pole (wood);Pole top | 0 | 0 | 0 |  | HTS-MR and HTS-SR | The pole fire occurred during light drizzle and the probable cause was tracking. | Pole-top fire | 42532.1236 | 1 | Negligible: no ground fire | 4154 | Roadway |  | 20161109UTD_03 | Infrastructure (network-based) | -37.9343 | 145.0497 | 1 | United Energy Distribution | Report | 5180 | 0.0060023 | 66kV AC | Moorabbin Airport | 3165 | Bentleigh East | Pole
CEOT dispatched a fault crew to isolate, make safe and repair. Fault crew found a 16 amp EDO 22kV line fuse blown on T-pole to Veevers S/L 4708837 [switch number 601536]. Crew patrolled the line found no causes & replaced the fuse. For the substation HV fuse that had candled, the fault crew replaced the HV fuse and fuse tube and supply was subsequently restored. | THE SHELING, 485 SCHOOLHOUSE LANE, TALLAROOK VIC 3659 | 578208 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 225159. Fuse on pole had burnt/candled, grass fire in vicinity. 10:41: Customer called to report, part supply failure at 485 School House Lane supplied via Veevers 1 Substation. Fault crew found a 16 amp EDO 22kV fuse blown on T-pole to Veevers S/L 4708837 [switch number 601536]. Crew patrolled the line found no causes & replaced the fuse. This HV line fuse operated correctly. 13:17: Customer called to report that the substation transformer was sparking on the pole, causing a spot fire, no power at property for water. The fault crew found hung-up EDO fuse that had possibly candled and cause a spark to hit the ground. The customer extinguished the fire. Total area burnt was approximately 86 sq. metres. Conditions were 20 degrees C, 20 km/h winds. | EDO fuse | 0 | 0 | 0 |  | SMR1 | Candled EDO fuse tube at substation location. | Other electricity related | 42654.5556 | 1 | Small: 10 - 1000 sq.m | 4156 | Agricultural |  | 20161110SPN_01 | Infrastructure (network-based) | -37.0564 | 145.1101 | 1 | AusNet Services Distribution | Report | 11240 | 0.036231 | 22kV AC | Mangalore Airport | 3659 | Tallarook | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was replaced under Access Authority conditions prior to the supply being restored. | NEW STREET, FRANKSTON VIC 3199 | 3308414 |  | Cold |  | Electrical breakdown;Leakage |  |  | 1 | At 0602hrs on 06/11/2016, 22kV feeder FTN 21 circuit breaker reclosed to lockout affecting 301 customers. During cooler early morning conditions, a crossarm fire occurred on at "New-Tooyal" substation. The pole fire occurred on the HV intermediate crossarm strap and the cause was probable tracking at pole No. LIS 3308414. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "New-Tooyal" substation but no damage was identified. | Conductor (bare);Crossarm (wood);Insulators | 0 | 0 | 0 |  | FTN 21 | The cause was probable tracking at pole No. LIS 3308414. | Pole-top fire | 42532.2514 | 1 | Negligible: no ground fire | 4158 | Roadway |  | 20161111UTD_01 | Infrastructure (network-based) | -38.1335 | 145.1276 | 1 | United Energy Distribution | Report | 5187 | 0.017734 | 22kV AC | Moorabbin Airport | 3199 | Frankston | Pole
Fault Crew isolated supply to Street light A144430 in pit to make safe, and moved pole off road. | 110 JAMES MIRAMS DRIVE, ROXBURGH PARK VIC 3064 | A144430 |  | Wind |  | Fatigue;Mechanical breakdown |  |  | 2 | Police report Street Light Pole down across road. The incident occurred in a new residential development on Aitken Blvd, 850 metres South of intersection of James Mirams Drive, Roxburgh Park. | Pole (steel) | 0 | 0 | 0 |  | COO14 | There were no signs of vehicle impact on the pole. An investigation into the event concluded that the pole had fallen over due to loose mounting hardware at the slip base contributed by strong gusts of wind on the day. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/11/2016 8:39 |  |  | 4161 | Residential |  | 20161113JEM_01 | Infrastructure (network-based) | -37.6238 | 144.915 | 1 | Jemena | Report | 5355 | 0.020395 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Roxburgh Park | AF Other
CEOT dispatched a fault crew to make safe. The supply was isolated and the street light removed and connections made safe. Arranged for public lighting crew to replace the street light. | RIVERHILL MOTOR INN, 45 MAIN STREET, BAIRNSDALE VIC 3875 |  |  |  |  | Unknown technical factor |  |  | 2 | IMS 225215. A street light caught fire per CFA. The street light had a black plastic cover on the back of the light and there was a fault in the wiring that caused this plastic to combust, melting the plastic and causing smoke. No flames where visible when the AusNet Services' fault crew arrive on-site. No visible reason for the short circuit fault was found. | Public lighting | 0 | 0 | 0 |  |  | The internal wiring inside the street light shorted out causing a fault. | Other electricity related | 14/11/2016 23:30 | 1 | Negligible: no ground fire | 4167 |  |  | 20161115SPN_02 | Infrastructure (network-based) | -37.8259 | 147.636 | 1 | AusNet Services Distribution | Report | 5203 | 0.0079769 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Bairnsdale | AF Other
The faults crew promptly isolated supply and replaced the 100amp meter panel fuses to units 1 and 2 Coorigil Road. The installations were tested and supply was left on. | FLAT 1 21-23 COORIGIL ROAD, CARNEGIE VIC 3163 |  |  |  |  | Overheated connection |  |  | 2 | The occupier advised of an all supply failure. A meter ping was completed that failed and a faults truck was dispatched to investigate. A meter panel fuse base had commenced to melt due to a probable loose connection before catching fire. Superficial damage occurred to the meter panel. | Meter board (including fuses) | 0 | 0 | 0 |  |  | The cause was due to a probable loose overheated connection. | Meter board | 42562.9375 | 1 | Negligible: no ground fire | 4173 | Residential |  | 20161116UTD_02 | Infrastructure (network-based) | -37.8955 | 145.0582 | 1 | United Energy Distribution | Report | 5209 | 0.03247 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | Fuse
Site assessed for repairs, reinstalled earths. | 132 BENSON ROAD, GISBORNE SOUTH VIC 3437 |  | Copper theft | [5 empty] | 2 | High voltage and low voltage earths stolen (copper) from a distribution substation (Benson Rd-P8). | Copper | 2 | 2 | 2 |  |  | Unknown person has stolen the copper (HV & LV)) copper earths from the distribution substation. | Damage to network assets | 17/11/2016 15:59 |  |  | 4180 |  |  | 20161117JEM_01 | Infrastructure (network-based) | -37.5513 | 144.6017 | 1 | Jemena | Report | 5218 | 0.0087535 | Earthing cable | Melbourne Airport | 3437 | Gisborne South | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs completed under Access Authority conditions prior to supply being restored after the blue phase LV fused isolator was replaced on the north circuit of "Halley-Lake" substation. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | LAKE ROAD, BLACKBURN VIC 3130 | 7019515 |  | Precipitation;Council;Dead |  | HV injection |  |  | 1 | At 1708hrs on 14/11/2016, 22kV ACR BH7287 located in Central Road reclosed to lockout affecting 392 customers. Following heavy overnight rain, a dead council gum tree from within the Blackburn Lake Sanctuary fell onto the HV and LV conductors in Lake Road between pole numbers LIS 7019515 and 8800263. This caused the blue phase HV conductor to briefly make contact with the blue phase LV conductor below. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Halley-Lake" substation. The LEI confirmed a high voltage injection occurred (BWD 1607) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The dead council tree was estimated to be 12m in length and tree clearers were called to make the area safe along with traffic control. The white and blue phase LV conductors also clashed at the time of the fault that caused the blue phase fuse to operate on the north circuit of "Halley-Lake" substation. | Conductor (bare) | 0 | 0 | 0 |  | NW 11 | Vegetation: Trees Incident | HV injection;Loss of supply | 14/11/2016 17:08 |  |  | 4181 | Public space |  | 20161118UTD_01 | Infrastructure (network-based) | -37.8281 | 145.1606 | 1 | United Energy Distribution | Report | 5219 | 0.023998 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3130 | Blackburn | Trees
As supply had not connected, repairs to conduit undertaken. | 1569-1593 DIGGERS REST-COIMADAI ROAD, TOOLERN VALE VIC 3337 | 30103381 | Working too close to underground cables | [5 empty] | 2 | A customer reported a copper theft at the incident location ( refer report 20161121pwa_01). Crew attended and found that a section of underground conduit had been damaged by the installation of roadside safety railings. The road barriers were installed over the cable path. No other damage identified. There were no reported injuries or fire. Note: This conduit cable was installed 8 years ago and has not been connected to the network | Services cable | 2 | 2 | 2 |  | MLN012 | Interference , roadside barriers installed over cable route | Damage to network assets | 16/09/2016 9:00 |  |  | 4185 | Roadway |  | 20161121PWA_02 | Infrastructure (network-based) | -37.609 | 144.6026 | 1 | Powercor | Report | 5349 | 0.040669 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
On arrival crew isolated supply and sleeved cable and replaced HV Intermediate crossarm to restore supply. | 222 BRIDGEWATER-SERPENTINE ROAD, BRIDGEWATER VIC 3516 | 32033600 |  | Blown branch/vegetation |  |  |  |  | 1 | CFA reported a broken tree branch has fallen across the HV cables at 222 Bridgewater â€“ Serpentine Road BRIDGEWATER and is burning. When crew arrived the cable had burnt through and a small grass fire had been contained by the attending CFA crew. There were no injuries | Conductor (bare) | 2 | 2 | 2 |  | EHK024 | wind storm caused limb to fall into conductors | Grassfire;Damage to network assets | 21/11/2016 16:51 | 1 | Small: 10 - 1000 sq.m | 4197 | Roadway |  | 20161122PWA_04 | Infrastructure (network-based) | -36.5796 | 143.9384 | 1 | Powercor | Report | 5525 | 0.03136 | 22kV AC | Bendigo Airport | 3516 | Bridgewater | Trees
On arrival crew commenced repairs, LEI dispatched to investigate HVI's | 4 ALFRED STREET S, NEWINGTON VIC 3350 | 33007473 |  | Bird |  |  |  |  | 1 | A field crew attending an outage found that a crow had caused a flashover on a 22kV pole, resulting in a High Voltage Injection affecting approximately 11 installations. Protection operated. There was no ground fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BAS014 | Bird Incident | HV injection;Loss of supply | 18/11/2016 8:37 |  |  | 4200 | Residential |  | 20161122PWA_07 | Infrastructure (network-based) | -37.5595 | 143.8294 | 1 | Powercor | Report | 5311 | 0.031266 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Newington | Animal
On arrival crew carried out repairs. | 55 COLES ROAD, CANIAMBO VIC 3630 | 30130885 |  | Bird |  |  |  |  | 2 | Customers reported loss of supply near the incident location. On arrival the fault crew found that an old disused crane had been left under a SWER line. A bird (pigeon) perched on top of this crane has caused a flashover between line and the old disused crane. The flashover caused a small fire to be ignited at the base of the crane of approximately 1m by 1m. The crane has been moved away from the line. There was no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | STN011 | Bird Incident | Loss of supply;Grassfire | 21/11/2016 14:30 | 1 | Localised: less than 10 sq.m | 4203 | Agricultural |  | 20161123PWA_01 | Infrastructure (network-based) | -36.4698 | 145.6261 | 1 | Powercor | Report | 5253 | 0.031407 | 12.7kV AC (SWER) | Shepparton Airport | 3630 | Caniambo | Animal
Gas company and emergency services attended, local area evacuated Electricity supply to area disconnected | 37 ROBERTS STREET, BRUNSWICK EAST VIC 3057 | 30239121 |  |  |  |  | Inappropriate tools/plant/equipment |  | 2 | Whilst replacing a power pole, a gas main was damaged. Gas company and emergency services attended | Pole (wood);Public infrastructure | 0 | 0 | 0 |  | BTS-NS176 | Use of rock auger on loose rock | Significant disruption to the community | 24/11/2016 15:20 |  |  | 4214 | Residential |  | 20161125PWA_04 | Infrastructure (network-based) | -37.7662 | 144.9821 | 1 | CitiPower | Report | 5267 | 0.018649 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3057 | Brunswick East | Other
On arrival crew initiated repairs | 770 TURNBULL ROAD, ARDMONA VIC 3629 | 33088557 |  | Bird |  |  |  |  | 1 | VicFire reported a transformer â€œexplosionâ€ and ground fire at the incident location. On arrival the crew found that a bird had flashed over between a surge diverter and the HV regulator tank body, the remains of the bird was found on the foundation pad at the base of the regulator. A small ground fire resulted approximately 10M X 4M in area of grass burnt. Some minor damage to one of the HV bushings resulted, the surge diverter will also require replacement. There were no reported injuries or 3rd party damage. | Voltage regulator | 2 | 2 | 2 |  | MNA021 | Bird Incident | Grassfire;Damage to network assets | 27/11/2016 10:02 | 1 | Small: 10 - 1000 sq.m | 4222 | Agricultural |  | 20161128PWA_02 | Infrastructure (network-based) | -36.4024 | 145.3134 | 1 | Powercor | Report | 5276 | 0.031663 | 22kV AC | Shepparton Airport | 3629 | Ardmona | Animal
On arrival crew isolated supply and commenced repairs | BERRIWILLOCK NORTH ROAD, BERRIWILLOCK VIC 3531 | 32156207 |  | Lightning |  |  |  |  | 1 | Powercor started to receive calls from customers in the Sea Lake area, reporting a pole fire. Crews were dispatched to the area and found a lightning strike had occurred at the incident location. There were no ground fires, injuries or 3rd party property damage reported. | Pole (wood) | 2 | 2 | 2 |  | CTN003 | lightning strike on pole | Pole-top fire | 42715.3319 | 1 | Negligible: no ground fire | 4236 | Agricultural |  | 20161130PWA_03 | Infrastructure (network-based) | -35.5213 | 142.9845 | 1 | Powercor | Report | 5297 | 0.0070058 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3531 | Berriwillock | Lightning
Isolated supply to replace the damaged transformer and underground cables. | 60 BUCKLAND WAY, SUNBURY VIC 3429 | A004056 - Buckland Way-P8 50kVA substation | Vandalism;Copper theft | [5 empty] | 2 | It was reported that unknown persons had attempted to remove copper earths resulting in damage to the 50kVA transformer (Buckland Way-P8 substation) and loss of supply to the customers. | Conductor (insulated);Copper;Pole mounted | 0 | 2 | 0 |  |  | Vandalism - attempted copper theft. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/11/2016 8:12 |  |  | 4241 | Roadway |  | 20161201JEM_02 | Infrastructure (network-based) | -37.6069 | 144.7238 | 1 | Jemena | Report | 5307 | 0.03719 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3429 | Sunbury | Other
Crew attended and rectified defective service neutral | 44 KENNY STREET, HAMILTON VIC 3300 | 33059732 |  |  |  | Corrosion |  | Phase to earth | 2 | Customer advised shock had been received from shower fitting. Attending crew undertook NST test, gained a failed result and subsequently found corroded neutral connection at junction box. LEI identified a voltage rise of 18 volts on the shower fitting. The defective connection was rectified and NST subsequently passed. | Customer installation | 0 | 0 | 0 |  | HTN004 | deteriorated neutral connection | Minor shock | 42591.375 |  |  | 4247 | Residential |  | 20161202PWA_01 | Infrastructure (customer connection) | -37.7356 | 142.0091 | 1 | Powercor | Report | 5318 | 0.0070104 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Connection
Area isolated and conducted repairs. | 54 MYRTLE STREET, IVANHOE VIC 3079 |  |  |  |  | Age |  |  | 1 | Two phases of high voltage conductors down, roadside & centre phase, the operator noted many bats flying around in the area at the time. No high voltage injection. Crew could not find cause and the conductor was broken in middle. No trees or animals nearby. | Conductor (bare) | 0 | 0 | 0 |  | NH17 | Vegetation: Trees Incident | Loss of supply | 42441.1326 |  |  | 4248 | Residential |  | 20161203JEM_01 | Infrastructure (network-based) | -37.7546 | 145.0528 | 1 | Jemena | Report | 5394 | 0.025059 | 22kV AC | Essendon Airport | 3079 | Ivanhoe | Conductor
AEMO and APD were advised. First responders were sent to HYTS, TRTS and MLTS. APD staff were requested to inspect and report targets from protection relays at the APD site. In conjunction with APD and AEMO, the HYTS-APD No 2 500kV Line and the MOPS No 2 Line No 2 Bus 500kV CB at HYTS were recalled to service. Power supply to APD was made available at 04:30 hours and interconnection to South Australia was restored at 05:41 hours on the same morning The MLTS-TRTS No 1 500kV Line was patrolled in the vicinity of T238, based on the distance to fault location given by the protection relays, i.e. approximately 103km from the MLTS end. The line patrol in this vicinity did not identify a possible cause. The MLTS-TRTS No 1 500kV Line was re-energised at 07:46 hours and again tripped. A further line patrol was initiated. At 10:23 hours, a report was received from the line patrol helicopter of a broken conductor found in the quad conductor bundle on the blue phase between T284 and T285. The conductor failure was located at the No. 4 spacer position i.e. the 4th spacer from T284 (out of 11 spacers in the span). This was approximately 174m from T284 and 291m from T285. A section of conductor was cut out and replaced. The spacer at the conductor break and also a spacer each side of the break were replaced. The line was restored to service at 22:32hrs. Following the repair and replacement of the spacers at the failure site, the following has been carried out: â€¢ Lines involved in the incident, as well as associated lines have been subjected to a routine thermal inspection. â€¢ All records in SAP for the failed conductor span of the MLTS-TRTS No 1 500kV Line have been reviewed. AusNet Services will review the condition and state of assets on the MLTS-TRTS No 1 500 kV Line and other lines in that geographic area with similar characteristics to develop investment plans where necessary. Investigations to establish the cause of the conductor failure are continuing. | 3868 HAMILTON HIGHWAY, MORTLAKE VIC 3272 |  |  |  |  | Unknown technical factor |  | Phase to earth | 1 | IMS 225570. (Towers 284-285, Mortlake) On 01/12/16 at 01:16 hours (AEDT) a fault on the MLTS-TRTS No 1 500kV Line resulted in the line tripping from its protection, reclosing and then tripping to lockout. When the MLTS-TRTS No 1 500kV Line tripped, the AEMO Emergency APD Potline Tripping Scheme (EAPTS) at Heywood Terminal Station (HYTS) operated. The EAPTS control scheme disconnected all supply to APD from HYTS and resulted in the separation of the Victorian and South Australian transmission networks. At the time of this incident, The HYTS-APD No 2 500kV Line was de-energised and a VSCAP (Verbal Statement of Condition of Apparatus) was issued to Alcoa Portland (APD) at their request to undertake maintenance work at APD. Also at this time the No 2 500kV busbar at HYTS was out of service for interrupter head replacement work on the MOPS No 2 Line No 2 Bus 500kV CB at HYTS. Information obtained from the associated protection and control system relays indicated that there was a blue phase to earth fault on the MLTS-TRTS No 1 500kV line. During the incident, the associated protection and control systems operated as designed. | Conductor (bare) | 0 | 0 | 0 |  | MLTS-TRTS No 1 500kV Line | Broken conductor. | Loss of supply | 42381.0521 |  |  | 4250 | Agricultural |  | 20161205SPN_01 | Infrastructure (network-based) | -38.0306 | 142.9282 | 1 | AusNet Services Transmission | Report | 5326 | 0.004956 | 500kV AC | Warrnambool Airport Ndb | 3868 | Mortlake | Conductor
CEOT dispatched a fault crew to isolate, make safe and repair. Street light was disconnected by the fault crew and follow up was required by the public lighting contractor to replace the street light. | 4 MEMORIAL DRIVE, NARRE WARREN NORTH VIC 3804 | 519671 | Vehicle | [5 empty] | 2 | IMS 225575. Street light head fire. The public light is a 100W HPS. Advice from Downer is that the street light was hit by an unknown party which caused the light head to catch fire. | Public lighting | 0 | 0 | 0 |  | lyd013 | Street light head caught fire. Advice from the attending Downer fault crew was that the light had been hit by an unknown vehicle. | Other electricity related | 42412.0521 | 1 | Negligible: no ground fire | 4251 | Roadway |  | 20161205SPN_02 | Infrastructure (network-based) | -37.9875 | 145.3149 | 1 | AusNet Services Distribution | Report | 12336 | 0.012655 | Low voltage AC (<1kV) | Moorabbin Airport | 3804 | Narre Warren North | Vehicle
CEOT dispatched a fault crew to make safe, isolate and repair. Supply was isolated and situation made safe. CEOT advised the DAO to attend to investigate the incident. The damaged section of the NMS (older type) HV ABC cable was replaced with a new 3 metre section of NMS HV ABC cable. The cable was tested before it went back into service. is one of the NMS Replacement Stage 2 sites. For further information: this site is currently being designed for installation of new type LDMS HV ABC cable. Itâ€™s a stage 2E site so itâ€™s due for completion by 30/09/2018. | 115-177 YARRA ROAD, CROYDON HILLS VIC 3136 | 1216269 |  |  |  | Electrical breakdown |  | Phase to earth | 1 | IMS 225589. Non-Metallic Screen (NMS) HV ABC cable had been found burnt between poles 1216269 and 1216271 after protection had tripped off. No evidence of any fire damage was found, only the HV ABC appeared to be damaged. DAO attended site and found burnt HV ABC still in the air. No damage to ground, or pole, or property. Looked like very slight scorching to the Catenary and ABC Insulation only. | Conductor (ABC) | 0 | 0 | 0 |  | cpk11 | Internal HV ABC failure. | Other electricity related | 42472.6736 | 1 | Negligible: no ground fire | 4253 | Roadway |  | 20161205SPN_04 | Infrastructure (network-based) | -37.7726 | 145.2757 | 1 | AusNet Services Distribution | Report | 12337 | 0.026973 | 22kV AC | Moorabbin Airport | 3136 | Croydon Hills | OH Cable
On arrival crew carried out repairs | 166 PUMPS ROAD, RED CLIFFS VIC 3496 | 33064221 |  | Bird |  |  |  |  | 1 | Upon arrival the crew found that a bird had flashed over between a HV dropper and the line side of a BA fuse unit, the remains of the bird was found on the ground at the base of the pole, a small ground fire resulted approximately 4m radius in area of grass burnt. Some minor damage to HV BA fuse unit was evident due to flashover and was changed as a result. The HV dropper was in good condition upon closer inspection using the EPV therefore was left in service. There were no reported injuries or 3rd party damage. | Boric acid;Dropper/bridge | 2 | 2 | 2 |  | RCTS22 | Bird Incident | Grassfire | 42472.3979 | 1 | Localised: less than 10 sq.m | 4258 | Roadway |  | 20161206PWA_04 | Infrastructure (network-based) | -34.2992 | 142.2212 | 1 | Powercor | Report | 5341 | 0.021066 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Animal
On arrival crew commenced repairs | 2-82 SHOGAKI DRIVE, MELTON SOUTH VIC 3338 | 30148970 | Working too close to underground cables | [5 empty] | 1 | Powercor fault crew attending an outage (MLN013 feeder) found an UG HV cable damage at the incident location by an excavator.. Protection operated. The crew found that the SW# 23432 at CHP and customer end HV RMU switch have been damaged. No fire or injuries reported. | Cable | 2 | 2 | 2 |  | MLN013 | Excavator contacted underground cable | Loss of supply;No Go Zone (contact);Damage to network assets | 42563.066 |  |  | 4263 | Industrial |  | 20161208PWA_01 | Infrastructure (network-based) | -37.7069 | 144.6089 | 1 | Powercor | Report | 5375 | 0.031097 | 22kV AC | Laverton Raaf | 3338 | Melton South | Dug up
The HV 63amp blue phase fuse was replaced and supply restored to customers in the area. | 600 SOUTH ROAD, MOORABBIN VIC 3189 |  |  |  |  | Candled fuse |  |  | 2 | Customer from a factory located at 600 South Road, Moorabbin advised one phase in the substation has blown up. He says there's no arcing or sparking and the fuse has turned black. A 22kV 63amp Powder Filled Fuse candled at "South-Deutsher" substation that caused a loss of supply to light industrial customers in the vicinity. | Powder filled | 0 | 0 | 0 |  | HT 08 | HV fuse candled and the cause was unknown. | Loss of supply | 42563.5104 |  |  | 4285 | Industrial |  | 20161214UTD_04 | Infrastructure (network-based) | -37.9369 | 145.0628 | 1 | United Energy Distribution | Report | 5382 | 0.0041273 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Fuse
An underground crew attended the site and commenced rectification work within the ground type substation before supply was restored at approximately 11.00AM. | 111 WOODLANDS DRIVE, BRAESIDE VIC 3195 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Light industrial customers supplied from "Phoenix-Woodlands" substation advised of a loss of their electricity supply when they arrived at work early this morning. Unknown persons broke into "Phoenix-Woodlands" ground type substation after cutting the fence and stole 5m x 240mm covered copper conductors. All active cables were cut at ground level and the neutral conductor had been removed with damage occurring to the low voltage transformer cables. Low voltage fuses had been removed and were left inside the substation fencing. 21 industrial customers were off supply whilst the damaged cabling was replaced. There was no evidence that electric shocks were received. | Copper;Equipment;Outdoor | 0 | 0 | 0 |  | MC 04 | Unknown persons broke into "Phoenix-Woodlands" ground type substation and stole copper conductors. | Loss of supply;Damage to network assets | 42563.2083 |  |  | 4290 | Industrial |  | 20161216UTD_01 | Infrastructure (network-based) | -37.9965 | 145.1196 | 1 | United Energy Distribution | Report | 5398 | 0.0038507 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Braeside | Other
Supply was restored and the faults crew provided close out details to the Resource Coordinator. | 2 BUCHER PLACE, ROSEBUD VIC 3939 | 1309365 | Unauthorised work | [5 empty] | 2 | A substation fault was created following three AMI meters communicating an outage. The incident wasn't a substation fault and it appears street light contractors (Healey Excavations) working on behalf of the local council, disconnected a 3 phase service that supplied three premises in Bucher Place, Rosebud. The contractor advised the faults crew they were isolating supply to a toilet block as part of non - Distributor contestable work for the council. The overhead service went through a large tree and the crew suspected the service supplied street lights and the toilet block only. Healey Excavations have been inducted onto the United Energy network but should not interfere with electrical assets when not working for United Energy and its Service Provider representatives. No electric shocks or damage was sustained. | Service conductor | 0 | 0 | 0 |  |  | Healey Excavations should not interfere with electrical assets when not working for United Energy and its Service Provider representatives. | Loss of supply | 42563.4271 |  |  | 4292 | Residential |  | 20161216UTD_02 | Infrastructure (network-based) | -38.3541 | 144.9076 | 1 | United Energy Distribution | Report | 5401 | 0.022156 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Other
On arrival crew commenced repairs | 489-555 ROBINSONS ROAD, TRUGANINA VIC 3029 | 30334554 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A company employee, Lachlan Bowen, reported a road expansion in progress at the incident location. Upon arrival, the crew found UG pit dug up and live cable exposed, this UG pit supplies a P/L pole that was found lying on the ground . there were no fires, injuries or third party property damage. | Services cable;Services pit;Pole (steel) | 2 | 2 | 2 |  | SU034 | Road making activities in area, pole possibly knocked down by vehicle. All disputed by site contractor. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/11/2016 11:13 |  |  | 4300 | Roadway |  | 20161219PWA_05 | Infrastructure (network-based) | -37.7954 | 144.7431 | 1 | Powercor | Report | 5413 | 0.0010463 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Vehicle
On arrival the crew isolated the service and replaced the service cable, supply was then reconnected. | 239 ARCHER STREET, SHEPPARTON VIC 3630 | 33088678 | Vehicle | [5 empty] | 2 | Vicfire reported a wire down and laying on truck at the above address. Police also attending. The attending crew found a truck had pulled down and broken a service cable to the premises and was lying across the truck. No protection operated. No damage to customer installation No shocks, injuries or fire starts. | Service conductor | 2 | 2 | 2 |  | STN012 | Vehicle struck service cable. | Loss of supply | 42594.3924 |  |  | 4302 | Roadway |  | 20161219PWA_06 | Infrastructure (network-based) | -36.3966 | 145.4103 | 1 | Powercor | Report | 5416 | 0.026764 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 114 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | 3302312 | Vehicle | Wind |  | Leakage |  |  | 1 | At 1632hrs on 08/12/2016, 22kV feeder ACR FS7552 located in Nepean Highway reclosed to lockout affecting 945 customers. Emergency services advised of a pole fire in Nepean Highway, Aspendale. During strong winds, a pole fire started at pole No. LIS 3302312 located opposite 114 Nepean Highway, Aspendale. It appears an unknown vehicle has struck the pole at a prior date and broke the HV ties. The HV conductors were tied on an angle and the centre phase conductor has fallen from the insulator during the strong winds and fallen to the top of the pole resting on the pole cap. Over an unknown period of time, the conductor has tracked through the pole cap and timber pole that caused a pole fire at the LV crossam kingbolt. No HVI occurred. | Conductor (bare);Pole top;Insulator tie wires/connections | 0 | 0 | 0 |  | MC 01 | An unknown vehicle has struck the HV/LV pole at a prior date and broke the HV ties. Over an unknown period of time, the conductor has tracked through the pole cap and timber pole and caused a pole fire at the LV crossam kingbolt. | Pole-top fire | 42594.6889 | 1 | Negligible: no ground fire | 4309 | Residential |  | 20161220UTD_01 | Infrastructure (network-based) | -38.025 | 145.0995 | 1 | United Energy Distribution | Report | 5423 | 0.025512 | 22kV AC | Moorabbin Airport | 3195 | Aspendale | Vehicle
Jemena crew replaced the pole and rectified the HV and LV reticulation. Site was made safe and Power was restored. | 75 SHAFTSBURY STREET, COBURG VIC 3058 | A037883 |  |  |  | HV injection;Leakage |  |  | 1 | Pole top fire outside 75 Shaftsbury St, Coburg on Pole A037883 resulted in the overhead HV lines falling onto the LV line below, this in-turn caused a power outage to approximately 120 customers. LEI inspected all customer properties impacted by the incident and there was no damage to customer property. | Conductor (ABC);Pole (wood) | 2 | 0 | 2 |  | CS5 | The tracking on the centre phase insulator caused a fire start at the top of the pole. It also resulted in the high voltage cross-arm breaking and it was reported to have caused high voltage injection however with no re-portable property damage. | Pole-top fire;Loss of supply | 20/12/2016 16:08 | 1 | Negligible: no ground fire | 4319 | Residential |  | 20161221JEM_01 | Infrastructure (network-based) | -37.7487 | 144.9549 | 1 | Jemena | Report | 5438 | 0.0022373 | 22kV AC | Essendon Airport | 3058 | Coburg | Pole
On arrival crew commenced repairs. | 553 JUNG NORTH ROAD, JUNG VIC 3401 | 30077099 |  | Lightning |  |  |  |  | 1 | Whilst responding to a fault, a Powercor fault crew reported that lightning had struck a HV SWER line, resulting in a transformer tank rupturing and spraying oil on the ground and on a nearby shed. The lightning strike also damaged the next pole along the line, resulting in a small grassfire of less than 1 square metre in size. There were no injuries, and the protection operated as expected. | Conductor (bare);Pole (wood);Pole mounted | 1 | 1 | 2 |  | HSM001 | Lightning strike | Grassfire | 20/12/2016 3:00 | 1 | Localised: less than 10 sq.m | 4318 | Agricultural |  | 20161221PWA_01 | Infrastructure (network-based) | -36.5729 | 142.3596 | 1 | Powercor | Report | 8395 | 0.024404 | 12.7kV AC (SWER) | Horsham Aerodrome | 3401 | Jung | Lightning
On arrival crew isolated supply and carried out repairs. | 274 WILLOWVALE ROAD, WILLOWVALE VIC 3360 | 32008602 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | The CFA reported a machine has struck Power lines at the incident location. On arrival the crew found that a farm sprayer unit had contacted the SWER line when lowering the arms of the sprayer resulting in a strand of the conductor to break and a ground fire to occur. No protection operated. No reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | BAS021 | Operating spray equipment near line | Grassfire | 20/12/2016 14:24 | 1 | Medium: 1000 sq.m - 10 ha | 4321 | Agricultural |  | 20161221PWA_03 | Infrastructure (network-based) | -37.8717 | 143.4597 | 1 | Powercor | Report | 5440 | 0.022155 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3360 | Willowvale | Vehicle
CEOT dispatched a fault crew to isolate supply, make safe and carry out necessary repairs. The fault crew isolated the supply by removing the HV fuses and removing the LL clamps and issued an EAP to make the repairs required. | 1510 LINDENOW-GLENALADALE ROAD, WUK WUK VIC 3875 | 1606515 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | IMS 225481. A farmer was working in his paddock using the forks on his tractor to move hay bales. The fork hit the pole causing the outside phase HV conductor to dislodge from the insulator pin and fall to the ground between LIS poles: 1606515 - 5679221. Electrical protection for this tee-off was 3 x DOF located at the tee-off. The HV fuse for the line side conductor phase on the ground operated but the remaining fuses stayed in. As a result, the load side conductor on the ground remained alive as it was back fed from a downstream distribution transformer on the spur line. No one was injured. Driver details are: David Hurley,133 High Plains Rd, Dargo, vehicle registration QZL871. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | bdl4 | A farmer driving a tractor made contact with a HV pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/11/2016 9:40 |  |  | 4323 | Agricultural |  | 20161222SPN_01 | Infrastructure (network-based) | -37.7691 | 147.4094 | 1 | AusNet Services Distribution | Report | 5442 | 0.034356 | 22kV AC | Bairnsdale Airport | 3875 | Wuk Wuk | Vehicle
CEOT dispatched a fault crew to isolate supply, make safe and carry out repairs. CEOT also dispatched a LEI to investigate and check for HVI damage.The Downer fault crew completed repairs and backfed LV circuit as the substation needed to be replaced. Attending LEI confirmed that a HVI had occurred as a result of the incident. A number if meters on the circuit were required to be replaced. Customer Advice Forms were issued to customers with damaged installations or appliances. | 103 EDINBURGH ROAD, LILYDALE VIC 3140 |  |  | Wind;Fallen |  | HV injection |  | Phase to phase | 1 | IMS 224713. CEOT received many calls for all supply failure on TX Edinburgh Thomas. Upon inspection of this call the fault crew found a HVI had occurred. A tree located on council land was blown over in a storm, resulting in 22kV coming into contact with the LV conductors resulting in a HV injection in customers' properties. Customers left off supply until LEI can attend in the morning to replace meters and disconnect customers from supply. | Conductor (bare) | 0 | 0 | 0 |  | ldl21 | Vegetation: Trees Incident | HV injection | 42623.7188 |  |  | 4050 | Residential |  | 20161014SPN_03 | Infrastructure (network-based) | -37.7939 | 145.3536 | 1 | AusNet Services Distribution | Report | 5023 | 0.014259 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the tree branch was removed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 36 WAVE STREET, ELWOOD VIC 3184 | 2308215 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1445hrs on 09/10/2016, 11kV feeder EW 02 circuit breaker reclosed to lockout affecting 1133 customers. During windy conditions, a tree branch from a council gum tree located outside 36 Wave Street, Elwood fell over the HV overhead conductors that caused a HV conductor to make contact with the LV conductors below near pole No. LIS 2308215. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Foam-Glenhuntly" substation. The LEI confirmed a high voltage injection occurred (CLA 1604) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | EW 02 | Vegetation: Trees Incident | HV injection;Loss of supply | 42623.6146 |  |  | 4045 | Roadway |  | 20161014UTD_04 | Infrastructure (network-based) | -37.8836 | 144.9885 | 1 | United Energy Distribution | Report | 5134 | 0.036431 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3184 | Elwood | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions after the large tree was removed. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 3 MEREWEATHER AVENUE, FRANKSTON VIC 3199 | 3308832 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | At 1517 hrs on 09/10/2016, 22kV feeder FTN 14 circuit breaker reclosed to lockout affecting 1801 customers. During very windy conditions, a tree branch from a gum tree located in the front yard of 35 Mereweather Street fell over the HV overhead conductors and caused a HV conductor to make contact with the LV conductors below. The HV and LV crossarms were broken at pole No. LIS 3308832. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Bragge-Mereweather" substation. The LEI confirmed a high voltage injection occurred (MOR 1606) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | FTN 14 | Vegetation: Trees Incident | HV injection;Loss of supply | 42623.6368 |  |  | 4047 | Roadway |  | 20161014UTD_06 | Infrastructure (network-based) | -38.1356 | 145.1288 | 1 | United Energy Distribution | Report | 5017 | 0.02281 | 22kV AC | Moorabbin Airport | 3199 | Frankston | Trees
CEOT dispatched a fault crew to isolate supply and make safe. CEOT notified the DAO to investigate. The fault crew isolated supply and made safe. DAO obtained a fault investigation report from the Vegetation Management group describing the incident details. A fallen tree was found nearby on the opposite side of the road. The crew repaired the broken conductor using a HV splice. There was light scorching of the ground underneath the tree. Also there were scorch marks on ground in line with the fallen HV conductor. | 540 VICTORIA ROAD, SEVILLE VIC 3139 | 1014014 |  | Wind;Fallen;MEC |  |  |  | Phase to phase | 1 | IMS 224759. An AusNet Services' fault crew attended an incident and advised CEOT that a small ground fire was observed around AusNet Services' assets ex HV Switch LD463. The fire size was less than 10m x 1m in size. A tall gum tree fell onto the HV overhead line and caused a HV conductor to break and fall to the ground. Root failure occurred in a gum tree approximately 23 metres from the conductors. Decay causing structural degradation in broken main roots below ground level was evident. No above ground indicators that would alert an Arborist to the presence of root defects or suspect root rot were observed. Saturated soils and strong winds were also contributors to the tree failure. The tree was not classed as a hazardous tree. 122 customers were off supply. | Conductor (bare) | 0 | 0 | 0 |  | wyk12 | Vegetation: Trees Incident | Loss of supply;Grassfire | 17/10/2016 0:20 | 1 | Localised: less than 10 sq.m | 4054 | Residential |  | 20161017SPN_01 | Infrastructure (network-based) | -37.7679 | 145.4709 | 1 | AusNet Services Distribution | Report | 5042 | 0.030384 | 22kV AC | Moorabbin Airport | 3139 | Seville | Trees
On arrival crew carried out repairs | 116-136 CECIL STREET, SOUTH MELBOURNE VIC 3205 | 30170659 |  |  |  | Overheated connection |  |  | 2 | CitiPower report room received advise from the MFB about a fire at the incident location. On arrival the fault crew found that a krone box had overheated and caught fire, resulting in molten plastic falling onto a car below it, causing damage to the cars paint. The MFB extinguished the fire. There was no ground fire or injuries sustained. | Connection box | 2 | 2 | 2 |  | AP011 | connection failure, unable to further examine box due to damage caused by incident. | Pole-top fire;Loss of supply | 19/10/2016 11:47 | 1 | Negligible: no ground fire | 4063 | Roadway |  | 20161019PWA_02 | Infrastructure (network-based) | -37.8325 | 144.9572 | 1 | CitiPower | Report | 5044 | 0.017795 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Connection
CEOT dispatched a fault crew to isolate supply, make safe and repair. Duty Availability Officer advised to investigate for the fire report. The DAO attended site and took photos and found no evidence of grass burnt or leaf litter on ground, top of tree/some juvenile new growth had signs of being singed and appear to have smouldered. Report from the fault crew that no HV fuse had operated, checked with CEOT and the Network Performance Coordinator - no protection had operated. According to SCADA, the incident occurred on 22/10/16 04:45. Alarms were received from WYK indicating BUEF went above min op for about 330ms. HE019 â€“ sectionaliser upstream reported EF L2. WYK24 had a neutral current limit alarm of 2.2A. The fault was on a fused spur (40E BA) ex HE077 which is downstream of HE112. Further information from Electrical Protection section: Based on WYK24 feeder CB device event download, at 04:45:43 the device picked up on SEF and EF (among other) prot elements on phase to ground type fault averaging about 550A (max 582A) for about 310msec. For such fault level the set of fuses at switch HE077 (currently not showing on SDME) would've operate in about 310msec if they were of BA 40E size. Conclusion: Protection operated as designed (fuse at HE077 on faulted phase operated). No changes to existing setting of WYK24 feeder CB required or to fuse size. A Vegetation & Easements field officer attended site and confirmed that a tree on the opposite side of the road has failed at the root plate and fallen over conductors. The tree was > 6 metres from the line before it failed. | 49 ROMEO ROAD, HEALESVILLE VIC 3777 | 1441138 |  | Precipitation;Wind;Fallen;MEC |  |  |  | Phase to phase | 1 | IMS 224879. Initial report: CFA report received of a tree hitting a pole and wires down and a report of a small fire in the vicinity of pole base. An AusNet Services' fault crew found a HV conductor alive one metre from the ground. Appears HV fuses had not operated. Final report: A Swamp gum tree on opposite side of the road failed at its root plate and contacted overhead HV conductors. Some charring was evident where tree contact was made with HV conductor, but no ground fire occurred. The tree was not classed as a hazardous tree. At the time of the incident there were strong winds and heavy rain conditions. The tree branches were outside of the vegetation clearance space. The incident caused damage to the overhead HV conductors. Tree contact and fault current has burnt through the HV conductor. | Conductor (bare) | 0 | 0 | 0 |  | wyk24 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Singeing or local charring/blackening only | 22/10/2016 5:05 |  |  | 4078 | Agricultural |  | 20161024SPN_03 | Infrastructure (network-based) | -37.6708 | 145.5493 | 1 | AusNet Services Distribution | Report | 5064 | 0.038249 | 22kV AC | Moorabbin Airport | 3777 | Healesville | Trees
A LEI and faults truck attended and tested pole No. LIS 8828297 to an independent earth and measured 0v. At the time of the investigation, no fault was identified that would account for the unknown person receiving the electric shock. However, the terminal cover was found to be missing from the base of the pole and the PVC junction box was broken away from the metal support. Rain may have entered the base of the pole and caused a fault between the unearthed metallic pole and the live terminals of the junction box. The faults truck disconnected supply to the public lighting poles within the car park and made the site safe. The local municipal council was advised to have the pole repaired before supply can be restored. The installation was left off supply. | POINT NEPEAN ROAD, RYE VIC 3941 | 8828297 |  | Precipitation |  | Defective component |  | Phase to earth | 2 | Caller advised they received an electric shock from a pole last Friday. The pole is located at the end of the car park near the Rye Pier on the right hand side. A customer called the United Energy faults and emergencies call centre that a slight electric shock was received from a steel pole in the car park near the Rye Pier during the heavy rain on Friday whilst standing on the wet grass. | Public lighting;Customer installation | 0 | 0 | 0 |  |  | Rain may have entered the base of the steel public lighting pole and caused a fault between the unearthed metallic pole and the live terminals of the junction box. | Minor shock | 18/10/2016 11:00 |  |  | 4086 | Public space |  | 20161026UTD_01 | Infrastructure (network-based) | -38.3691 | 144.8224 | 1 | United Energy Distribution | Report | 5074 | 0.040448 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | Rye | Other
On arrival crew carried out repairs | MENKARA, 2692 CASTLE CAREY ROAD, MORTLAKE VIC 3272 | 32060489 |  | Fallen;Dead |  |  |  |  | 0 | A customer reported that she had heard a loud bang and had seen sparks from across the road at the incident location. On arrival the crew found that a large dead pine tree had fallen onto the 12.7kV SWER conductor and eventually caused the conductor to break and fall to the ground. The barrel of the SWER HV fuse on the ISO pole burnt through and part of it fell to the ground. There was no ground fire or injuries. | Conductor (bare);EDO fuse | 2 | 2 | 2 |  | TRG002 | Vegetation: Trees Incident | Pole-top fire;Loss of supply;Hung-up fuse only;Damage to network assets | 25/10/2016 13:48 | 1 | Negligible: no ground fire | 4097 | Agricultural |  | 20161027PWA_03 | Infrastructure (network-based) | -38.0767 | 142.8719 | 1 | Powercor | Report | 8392 | 0.012399 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3272 | Mortlake | Trees
There was evidence of the HV and LV conductors clashing but no repairs were required. A number of LEI's investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. The occupier at 655 Blackburn Road wasn't in attendance and a card was left as the LEI had to check for internal damage prior to supply being restored. When the customer was in attendance and supply was restored, the switchboard caught fire and the LEI immediately isolated supply. The faults crew removed the service cables from the FMJB at the POA to enable the rectification work thatâ€™s required by a REC to be completed safely. A defect notice was issued to the occupier and meter No. 0627218 was also removed. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | BLACKBURN ROAD, CLAYTON VIC 3168 | 202824 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 1027hrs on 20/10/2016, 22kV feeder SVW 41 circuit breaker successfully reclosed and held. A large truck was turning left from Blackburn Road into Connam Road, Clayton and drove over the stay wire attached to pole No. LIS 0614110. This caused the corner pole to lean when the trucks wheels contacted the stay and the HV and LV conductors clashed in the bay over Blackburn Road when the pole returned to its normal position. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the east and west circuits of "Connam-Cambro" substation connected to the red and white phases. The LEI confirmed a high voltage injection occurred (CLA 1606) affecting customers in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | SVW 41 | A large truck drove over the stay wire causing the conductors to clash. | HV injection;Loss of supply | 20/10/2016 10:27 |  |  | 4092 | Roadway |  | 20161027UTD_01 | Infrastructure (network-based) | -37.9197 | 145.1397 | 1 | United Energy Distribution | Report | 5085 | 0.023576 | 22kV AC | Moorabbin Airport | 3168 | Clayton | Vehicle
CEOT dispatched a fault crew and an Underground crew to isolate the faulted area, locate the fault and carry out repairs. The crew located the fault and two straight underground joints were performed by the Underground Crew to place the underground HV cable back into service. | 4 STONELEIGH ROAD, CRANBOURNE NORTH VIC 3977 | 5709491 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 224515. An underground HV cable was struck by a 3rd party borer (cnr Stoneleigh Rd & Thompsons Rd). Boring was being conducted at 2.2m to avoid the cable depth on MOCS, however, MOCs only highlight depths at cable entry and exit. 3rd party contractor believed boring at depth of 2.2m was sufficient to avoid the cable. The 3rd party had no Permit To Work issued by AusNet Services. UG boring machine operator was Matt Harris of Fulton Hogan, telephone 0411514991. | Cable | 0 | 0 | 0 |  | cln21 | 3rd party contact with underground HV cable. | Loss of supply;No Go Zone (contact) | 26/09/2016 15:25 |  |  | 4104 | Roadway |  | 20161028SPN_04 | Infrastructure (network-based) | -38.0886 | 145.3274 | 1 | AusNet Services Distribution | Report | 5099 | 0.0062697 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne North | Dug up
A faults truck attended and replaced the stolen earth cables and installed new timber protective cover guards. | 38 CAHILL STREET, DANDENONG SOUTH VIC 3175 |  | Copper theft |  |  | Earth fault |  |  | 2 | A Downer Project Manager was out on site and identified that two copper HV earths have been cut and removed by unknown persons on two HV cable head poles outside 38 & 42 Cahill Street, Dandenong. The HV CHP poles were outside the Dandenong Iron Foundry P/L and the earths were for HV switches DN2936 and DN2817. The Project Manager suspected the copper thefts occurred some time go. | Earth | 0 | 0 | 0 |  | DSH 33 | Two copper HV earths have been cut and removed by unknown persons on two HV cable head poles. | Damage to network assets | 27/10/2016 13:00 |  |  | 4099 | Roadway |  | 20161028UTD_01 | Infrastructure (network-based) | -38.0263 | 145.1954 | 1 | United Energy Distribution | Report | 5093 | 0.00085185 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Other
CEOT dispatched to a LEI and a fault crew to make safe and investigate. The overhead line was patrolled by the crew and there was no damage identified on network assets. Could have been an animal but there is no evidence of this. The LV runs beneath the 66kV line. Attending LEI inspected properties along Beauty Gully Rd and Harris Gully Rd Warrandyte and found evidence of HV injection at only 2 properties. The affected properties were 10 and 25 Beauty Gully Rd, Warrandyte, but the LEI was unable to ascertain location of the incident that caused the damage. Customer's installations were isolated and defect notices (NCID) left. CEOT were notified of this action. | 10 BEAUTY GULLY ROAD, WARRANDYTE VIC 3113 |  |  |  |  | Unknown technical factor |  | Phase to phase | 1 | IMS 225005. CEOT advised of reclose of 66kV at 0345hrs, but no evidence could be located to identify what cause the fault. The Templestowe - Sugarloaf line 66kV CB opened on initial fault current then successfully reclosed and held in. Corresponding to this there was an identified HVI affecting 2 houses. | Yet to be determined | 0 | 0 | 0 |  | rwn26 | No cause was identified. The overhead line was patrolled and there was no evidence of nay network asset damage. | HV injection | 42380.184 |  |  | 4124 | Residential |  | 20161102SPN_02 | Infrastructure (network-based) | -37.7565 | 145.2082 | 1 | AusNet Services Distribution | Report | 5126 | 0.022025 | Low voltage AC (<1kV) | Moorabbin Airport | 3113 | Warrandyte | AF Other
CEOT dispatched a fault crew to isolate, make safe and check for any damage to network assets. The area was isolated. The concrete pumping truck had packed up prior to the fault crew arriving. The necessary repairs to the line were undertaken by the crew. | 47 TOOTLE STREET, KILMORE VIC 3764 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | IMS 225008. A concrete pump unit truck pouring a concrete slab for a new building construction contacted a high voltage conductor between poles 4718663 and 4732204 which caused the footpath side phase conductor to break. Feeder protection operated. No injuries to any persons. The ground clearance of the line was well above AusNet Services' ESMS regulation height. The pump operator's details are: Joe Pisano, 3 Tracey Rise, Lalor. Company Lion Pumping, PO Box 1228, Lalor, Vic. 3075, phone 0449929359. Vehicle Registration UVN510. . | Conductor (bare) | 0 | 0 | 0 |  | kms1 | A concrete pump truck contacted overhead HV conductors. | Loss of supply;No Go Zone (contact) | 42411.3507 |  |  | 4125 | Roadway |  | 20161102SPN_03 | Infrastructure (network-based) | -37.3113 | 144.9584 | 1 | AusNet Services Distribution | Report | 5128 | 0.028113 | 22kV AC | Wallan (Kilmore Gap) | 3764 | Kilmore | Vehicle
High voltage supply isolated, Earth and Short Circuit attached, Access Permit issued to Jemena Faults crew, removed branch and cut back overhanging tree branches, network supply restored. | 66 HUGHES PARADE, RESERVOIR VIC 3073 |  | Working too close to overhead lines | Within clearances |  |  |  |  | 2 | A private tree clearer contractor cutting a private tree above high voltage conductors caused the tree branch to make contact with footpath side high voltage conductor. | Conductor (bare) | 0 | 0 | 0 |  | TT8 | Vegetation: Trees Incident | Loss of supply | 42411.3826 |  |  | 4126 | Roadway |  | 20161103JEM_01 | Infrastructure (network-based) | -37.6996 | 145.0006 | 1 | Jemena | Report | 5195 | 0.0019606 | 22kV AC | Essendon Airport | 3073 | Reservoir | Trees
CEOT dispatched a fault crew to attend and make safe. CEOT also dispatched the DAO to attend the site to investigate. The Downer OH fault crew attended site and isolated the supply. The fault crew confirmed that a 315 Amp HRC fuse on the White Phase blew on kiosk substation VIEW PARK ELLEN and 3 fuses (unknown size) blew on kiosk substation KIPPENROSS WOOLSHED. Pillar and cables replaced. | 1 THE ESPLANADE, NARRE WARREN SOUTH VIC 3805 | 5639730 | Vehicle |  |  |  |  | Phase to earth | 1 | IMS 225013. VicPol reported that a car had run into an electrical pillar. The car (Registration number UUA186, the driver was Ben Hadad) lost control of his Holden Commodore ute and hit the LV paralleling pillar 5664082 and the car caught fire as a result. The car caught fire because one of the phases came in contact with the metal frame of the car. The driver did a runner from the scene and was later picked up by Police and taken to Narre Police Station. Paul Hardy was the incident controller for the fire brigade. He and his crew extinguished the car fire. The car was completed destroyed, along with the LV Paralleling Pillar ,which was completed melted. The car fire caused an area of 18 sq. metres of grass nature strip to catch fire. | LV Pillar | 0 | 0 | 0 |  | HPK14 | A car ran off the road and collided with a LV Paralleling Pillar. | Vehicle;Damage to network assets | 42411.4688 | 0 | Negligible: no ground fire | 4132 | Roadway |  | 20161104SPN_02 | Infrastructure (network-based) | -38.0613 | 145.3221 | 1 | AusNet Services Distribution | Report | 11238 | 0.022263 | Low voltage AC (<1kV) | Moorabbin Airport | 3805 | Narre Warren South | Vehicle
CEOT dispatched a fault crew to isolate and make safe and organise repair. The HV ABC mid-span has been repaired with new joints. | 1069 PLENTY ROAD, SOUTH MORANG VIC 3752 | 917429 |  |  |  | Electrical breakdown |  | Phase to phase | 1 | IMS 225045. HV ABC blown mid-span. A small fire approximate size of 1 sq. metre was observed on the ground underneath the cable. Fault caused by HV ABC failing mid-span. | Conductor (ABC) | 0 | 0 | 0 |  | DRN11 | HV ABC blown mid-span. | Other vegetation | 42471.7333 | 1 | Localised: less than 10 sq.m | 4136 | Roadway |  | 20161107SPN_01 | Infrastructure (network-based) | -37.6319 | 145.0957 | 1 | AusNet Services Distribution | Report | 11239 | 0.033002 | 22kV AC | Essendon Airport | 3752 | South Morang | OH Cable
On arrival completed repairs | 8 ODONOHUE ROAD, ANGLESEA VIC 3230 | 30061324 |  |  |  | Unknown technical factor |  |  | 2 | The fire brigade reported a pole fire at the incident location. On arrival the crew found that a 3 phase fused mains box controlling two underground services had overheated and caught fire. There was no ground fire or injuries. | Connection box | 2 | 2 | 2 |  | WPD014 | Could not be established due to damage to box | Pole-top fire | 27/10/2016 11:35 | 1 | Negligible: no ground fire | 4140 | Roadway |  | 20161108PWA_01 | Infrastructure (network-based) | -38.4181 | 144.1702 | 1 | Powercor | Report | 5155 | 0.018771 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Fuse
CEOT dispatched a fault crew to attend and make safe. CEOT also advised the DAO of the fire in the area for investigation. Traffic Control & Tree Clearers were called in to remove the tree. The tree was removed off the HV conductor and the line was re-sagged. | 260 COOK ROAD, LONGWARRY VIC 3816 | 2709203 |  | Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 225057. CFA reported trees on power lines and grass fire in area. The tree was between pole asset numbers 2709203 and 2709206 and was located in the road reserve. The fire was out and the CFA had left by the time of fault crew attendance. The Police had the road blocked until traffic control arrived and set up. Feeder protection operated. | Conductor (bare) | 0 | 0 | 0 |  | wgl12 | Vegetation: Trees Incident | Grassfire | 42562.4583 | 1 | Small: 10 - 1000 sq.m | 4141 |  |  | 20161108SPN_01 | Infrastructure (network-based) | -38.1003 | 145.7423 | 1 | AusNet Services Distribution | Report | 5158 | 0.036968 | 22kV AC | Moorabbin Airport | 3816 | Longwarry | Trees
On arrival crew isolated supply and commenced repairs | WREATH DRIVE, TARNEIT VIC 3029 | 32178555 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Trevor reported an excavator had made contact with an overhead conductor at the incident location. The crew attended and confirmed contact with a HV conductor had been made between LIS 21827 and Dohertys Rd P170E3. No damage to conductor just grease on cable from excavator. There was no ground fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | LV002 | Excavator contacted line | Loss of supply;No Go Zone (contact) | 42685.7083 |  |  | 4162 | Construction |  | 20161114PWA_01 | Infrastructure (network-based) | -37.8209 | 144.6997 | 1 | Powercor | Report | 5192 | 0.0037766 | 22kV AC | Laverton Raaf | 3029 | Tarneit | Vehicle
The crew have isolated the cable pending arrival of an underground crew to restore supply. | 1 ATLANTIS DRIVE, POINT COOK VIC 3030 | 30301256 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that they have dug up an underground cable at the incident location. On arrival the fault crew found that a four core low voltage underground cable installed in orange conduit had been contacted by a back hoe and pulled out of a low voltage pit, the cable was still â€œALIVEâ€. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | LV004 | Excavating too close to cable | Loss of supply;No Go Zone (contact) | 42411.5417 |  |  | 4168 | Roadway |  | 20161115PWA_01 | Infrastructure (network-based) | -37.9109 | 144.7514 | 1 | Powercor | Report | 5217 | 0.018796 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
On arrival crew isolated supply and commenced repairs | 29-31 FRITH STREET, BRUNSWICK VIC 3056 | 30334649 | Vehicle | [5 empty] | 2 | A contractor reported that he has pulled down a service with his truck at the incident location. On arrival the fault crew found that a sucker truck had been moved with its boom in the raised position. The boom has contacted and broken a 4 core XLPE insulated service between the pole and the BTS to 29 Firth Street There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | WB005 | Enviro cleanup truck relocated with boom raised. | Loss of supply;Damage to network assets | 42411.5326 |  |  | 4171 | Roadway |  | 20161116PWA_02 | Infrastructure (network-based) | -37.7673 | 144.9632 | 1 | CitiPower | Report | 5207 | 0.035021 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
On arrival crew isolated supply and commenced repairs | 1235 DORODONG ROAD, DORODONG VIC 3312 | 32130701 |  |  |  | Leakage |  |  | 1 | Following calls from customers in the Dorodong area, reporting dim lights, Crews were dispatched to the area. They found a HV fuse had operated on P1 Dorodong line. Crews patrolled the area found a HV conductor on the ground and evidence of a cross arm fire at angle pole P66. There were no ground fires, injuries or 3rd party property damage reported. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | HTN002 | Pole top fire | Pole-top fire;Loss of supply | 42501.2444 | 1 | Negligible: no ground fire | 4174 | Agricultural |  | 20161116PWA_03 | Infrastructure (network-based) | -37.3465 | 141.0804 | 1 | Powercor | Report | 5210 | 0.025823 | 22kV AC | Hamilton Airport | 3312 | Dorodong | Pole
On arrival crew commenced repairs | 38 HIGH VIEW CRESCENT, GISBORNE VIC 3437 | 32048456 | Copper theft | [5 empty] | 2 | Customer reported that they found a white cover lying on the ground underneath the power pole out the front of the property and that FOLCB had exposed wiring underneath it. Crew attended and found 4c 16mm service cable, running to 53 Highview Cres, was missing. Supply was not interrupted as it was a new installation that had not been connected to the LV mains. Contacted civil contractor who advised they had installed the cable on 14/07/2016. There was no fire or injuries. | Services cable | 2 | 2 | 2 |  | GSB013 | cable theft | Damage to network assets | 42471.3806 |  |  | 4186 | Roadway |  | 20161121PWA_03 | Infrastructure (network-based) | -37.491 | 144.6198 | 1 | Powercor | Report | 5225 | 0.018965 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
The crew have replaced and reinstated wiring to the damaged pit. The supply to units 5 and 6 have been isolated and defect notices issued. | 14 MINGAY CLOSE, TRUGANINA VIC 3029 | 30287248 | Working too close to underground cables | [5 empty] | 2 | A carpenter (Steve) working at this location reported that some-one has used a Bob cat and underground electrical assets have been damaged at the incident location. On arrival the fault crew found that a low voltage pit had been pulled out of the ground, wires exposed and the lid removed damage appears to have been caused by a back hoe or excavator at the incident location. The crew were unable to find any one on site and no details have been confirmed regarding the person/s who caused the damage. There was no ground fire and no injury as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | LV002 | Excavation by unknown person | No Go Zone (contact) | 42624.6222 |  |  | 4187 | Residential |  | 20161121PWA_04 | Infrastructure (network-based) | -37.8446 | 144.7247 | 1 | Powercor | Report | 5226 | 0.0095694 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Dug up
On arrival crew carried out repairs | 420 ARDMONA ROAD, ARDMONA VIC 3629 | 33089756 |  | Bird |  |  |  |  | 1 | A customer reported a fire at the incident location. On arrival the crew found that a crow had created a flash over on the concrete pole and fire had burnt along the Channel Reserve. There were no reported injuries, shocks or third party damage. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | MNA014 | Bird Incident | Grassfire | 19/11/2016 16:23 | 1 | Small: 10 - 1000 sq.m | 4190 | Agricultural |  | 20161121PWA_05 | Infrastructure (network-based) | -36.366 | 145.2957 | 1 | Powercor | Report | 5312 | 0.0053113 | 22kV AC | Shepparton Airport | 3629 | Ardmona | Animal
On arrival crew inspected assets and conducted repairs | 575-635 HAMILTON HIGHWAY, FYANSFORD VIC 3218 | 32084337 |  | Lightning;Wind |  |  |  |  | 1 | A Powercor employee called to report a fire start at the base of our pole after noticing CFA activity at the incident location. A reclose was recorded on the feeder prior to this and may have been a lightning strike in the vicinity of the switch pole. Upon inspection the switch was black and the fire (1m x 10m) appears to have originated at or close to the switch earth. A fuse was also down on the substation 1 pole to the east but no other visible damage. There were no injuries or third party property damage | Disconnector/isolator | 2 | 2 | 2 |  | GL012 | Lightning flashover on switch | Grassfire | 21/11/2016 16:56 | 1 | Small: 10 - 1000 sq.m | 4194 | Roadway |  | 20161122PWA_01 | Infrastructure (network-based) | -38.1326 | 144.2684 | 1 | Powercor | Report | 8394 | 0.030902 | 22kV AC | Avalon Airport | 3218 | Fyansford | Lightning
On arrival crew isolated line and commenced repairs | 95 BLUESTONE SCHOOL ROAD, CONNEWARRE VIC 3227 | 30063270 |  | Blown branch/vegetation |  |  |  |  | 1 | A customer called to report tree branch on line sparking and on fire at the incident location. Powercor crew found multiple small burnt patches on ground, self-extinguished caused by branch falling on line and small pieces falling to the ground alight (largest approx.. 10cmÂ²). | Conductor (bare) | 2 | 2 | 2 |  | WPD024 | Vegetation: Trees Incident | Grassfire;Damage to network assets | 21/11/2016 18:32 | 1 | Localised: less than 10 sq.m | 4195 | Roadway |  | 20161122PWA_02 | Infrastructure (network-based) | -38.2631 | 144.3982 | 1 | Powercor | Report | 5239 | 0.015144 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3227 | Connewarre | Trees
On arrival crew commenced repairs | 231-233 THOMPSON ROAD, BELL PARK VIC 3215 | 30063260 | Vehicle | [5 empty] | 2 | A customer informed a service cable tangled by a truck at the incident location. Upon arrival the crew found the cable pulled from the POA and detached. There were no reported injuries or fire. | Service conductor | 2 | 2 | 2 |  | CRO022 | Rubbish truck contacted service | Loss of supply;Damage to network assets | 14/11/2016 12:18 |  |  | 4211 | Roadway |  | 20161125PWA_01 | Infrastructure (network-based) | -38.1089 | 144.3436 | 1 | Powercor | Report | 5263 | 0.031515 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Park | Vehicle
The GFB was opened and the fire then extinguished. | 39 SHAFTESBURY PARADE, THORNBURY VIC 3071 | 30186544 |  |  |  | Leakage |  |  | 2 | A passer-by called to advise pole on the corner of Stott & Woolton Avenue is sparking and making an arcing noise the MFB are in attendance at the incident location. On arrival the fault crew found that the a GFB switch was candling of the arc shute on roadside phase (HVSW #1008) was on fire at the incident location. There was no ground fire and no injury as a result of this incident. | Disconnector/isolator | 2 | 2 | 2 |  | NC013 | Arc shute degredation | Pole-top fire | 15/11/2016 10:00 | 1 | Negligible: no ground fire | 4212 | Roadway |  | 20161125PWA_02 | Infrastructure (network-based) | -37.7603 | 144.9977 | 1 | CitiPower | Report | 5264 | 0.023454 | 11kV AC | Essendon Airport | 3071 | Thornbury | AF Other
On arrival crew carried out repairs | 22 FISKEN STREET, MADDINGLEY VIC 3340 | 30114393 | Vehicle | [5 empty] | 1 | Powercor fault crew attending an outage found a truck hit O/H LV neutral and it wrapped HV conductors at the incident location. Protection operated. No HVI reported. No fire, injuries or third party damage found. | Conductor (bare) | 2 | 2 | 2 |  | BMH004 | Garbage truck struck neutral cable | Loss of supply;Damage to network assets | 17/11/2016 9:50 |  |  | 4215 | Roadway |  | 20161125PWA_05 | Infrastructure (network-based) | -37.6866 | 144.4429 | 1 | Powercor | Report | 5268 | 0.028797 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3340 | Maddingley | Vehicle
Jemena dispatched faults crew to make site safe and isolate supply to substation. | 7-9 MEPHAN STREET, FOOTSCRAY VIC 3011 |  | Unauthorised access | Within clearances |  |  |  |  | 2 | Property owner contractor tree cutter caused tree limb to fall onto transformer high voltage bushing of a ground type transformer (Mephan 9 - Gordon ground type substation) causing a fire to the branch. Contractor decided to extinguish the flames by cutting the substation gate lock and using a foam type fire extinguisher. Substation was still energised. | Outdoor | 0 | 1 | 0 |  | BY12 | Vegetation: Trees Incident | No Go Zone (no contact);Other vegetation | 26/11/2016 12:47 | 1 | Negligible: no ground fire | 4217 | Industrial |  | 20161126JEM_01 | Infrastructure (network-based) | -37.7869 | 144.8872 | 1 | Jemena | Report | 5412 | 0.0089167 | 22kV AC | Essendon Airport | 3011 | Footscray | Other
Site made safe. The injured worker received on site first aid treatment for minor swelling & abrasion injuries to the right side of his head and shoulder. The injured worker was transported to hospital by a crew member for precautionary medical assessment, following this assessment the worker was released from hospital without requiring any medical treatment. Internal investigation commenced. | 4 DICKENS STREET, HEIDELBERG HEIGHTS VIC 3081 | [5 empty] | Ineffective planning/procedures/processes |  | 2 | A Jemena Electrical Maintenance crew attended a site to conduct the task of replacing an overhead crossarm on a pole. The crew arrived on site and established the work area, which included installing a chain-link barrier around an area designated as a â€œdrop zoneâ€ (restricted area). During work on the crossarm, a Lineworker working aloft in an Elevated Work Platform (EWP), requested equipment from a ground based Jemena worker. This request authorised the ground based worker to enter the drop zone. The worker on the ground proceeded to tie the equipment to a handline lowered by the Lineworker in the EWP basket. While the ground based worker attached the equipment to the handline, a High Voltage Insulator (7.8 kg) which had been unsecured in preparation for the cross arm replacement fell from the crossarm, striking the ground worker on the hard hat and shoulder. Refer to the safety gram. | Insulators | 2 | 2 | 2 |  |  | A Jemena Electrical Maintenance crew attended a site to conduct the task of replacing an overhead crossarm on a pole. The crew arrived on site and established the work area, which included installing a chain-link barrier around an area designated as a â€œdrop zoneâ€ (restricted area). During work on the crossarm, a Lineworker working aloft in an Elevated Work Platform (EWP), requested equipment from a ground based Jemena worker. This request authorised the ground based worker to enter the drop zone. The worker on the ground proceeded to tie the equipment to a handline lowered by the Lineworker in the EWP basket. While the ground based worker attached the equipment to the handline, a High Voltage Insulator (7.8 kg) which had been unsecured in preparation for the cross arm replacement fell from the crossarm, striking the ground worker on the hard hat and shoulder. | Medical attention (first aid/doctor/hospital) | 23/11/2016 14:38 |  |  | 4218 | Residential |  | 20161128JEM_01 | Infrastructure (network-based) | -37.7357 | 145.053 | 1 | Jemena | Report | 5392 | 0.005934 | Not applicable | Essendon Airport | 3081 | Heidelberg Heights | Other
CEOT dispatched a fault crew to isolate, make safe and repair. The crew isolated supply, made safe, replaced the BA fuse tube and fuse and then restored supply to the customer. | 125 BASS LANDING ROAD, BASS VIC 3991 | 2803741 |  |  |  | Corrosion;Electrical breakdown |  |  | 2 | IMS 225484. Operator advised upon arriving @ INCD-21401-s that he found a candled & hung-up Boric Acid fuse. It was a 6A Boric Acid fuse and there was a light drizzle and mist at the time. The area is a high salt area which may have been a contributing factor for this incident. | Boric acid | 0 | 0 | 0 |  | WGI23 | Candled Boric Acid fuse. | Other electricity related | 28/11/2016 4:00 | 1 | Negligible: no ground fire | 4225 | Agricultural |  | 20161128SPN_01 | Infrastructure (network-based) | -38.4987 | 145.4487 | 1 | AusNet Services Distribution | Report | 11242 | 0.023943 | 22kV AC | Moorabbin Airport | 3991 | Bass | Fuse
On arrival crew commenced repairs | 412 EYRE STREET, BALLARAT CENTRAL VIC 3350 | 30005934 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Customer called to advise a concrete pumper had torn down a line to the house and the line was laying on the road. When a crew arrived police where onsite directing traffic. The crew isolated the service from supply at the pole end and the customer engaged a REC to replace the point of attachment, fuse box and inspect mains. No shocks, injuries or fire starts. | Service conductor;Customer installation | 2 | 2 | 2 |  | BAS014 | Concrete pump boom raised when raveling from site | Loss of supply | 29/11/2016 10:22 |  |  | 4259 | Roadway |  | 20161207PWA_01 | Infrastructure (network-based) | -37.5651 | 143.8487 | 1 | Powercor | Report | 5342 | 0.0335 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat Central | Vehicle
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed corroded neutral conductor at the POA end of the service cable to the property. fault truck disconnected existing service cable and replaced with new one. | 1 HAMBLETON STREET, ALBERT PARK VIC 3206 | 30213517 |  |  |  | Corrosion |  | Phase to earth | 2 | Leanne reported to have received an electric shock when she made simultaneous contact between the metallic Front yard tap with one hand whilst standing with bare feet in the front yard. | Service conductor | 2 | 2 | 2 |  | AP003 | Corroded neutral connection at POA | Minor shock | 42562.4167 |  |  | 4260 | Residential |  | 20161207PWA_02 | Infrastructure (customer connection) | -37.8451 | 144.9567 | 1 | CitiPower | Report | 5343 | 0.0061516 | Low voltage AC (<1kV) | Essendon Airport | 3206 | Albert Park | Connection
On arrival The work party had cordoned off the area to prevent public access. Work party completed repairs | 2 TATE STREET, THOMSON VIC 3219 | 32071129 | Working too close to overhead lines | [5 empty] | 2 | A neighbour reports an excavator has contacted and damaged a service at the incident location. On arrival the fault crew found that an excavator working on the construction site at 2 Tate Street had contacted and severed an XLPE service. The service was found lying on the ground with bare conductors alive at the incident location. There was no ground fire or injuries. | Service conductor | 2 | 2 | 2 |  | GLE032 | Excavator working near service line | Loss of supply;No Go Zone (contact) | 42412.3819 |  |  | 4266 | Residential |  | 20161208PWA_03 | Infrastructure (network-based) | -38.1658 | 144.3807 | 1 | Powercor | Report | 5353 | 0.03656 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Thomson | Vehicle
Advised Customer Works not to proceed. | 19 DRYBURGH STREET, WEST MELBOURNE VIC 3003 | 30257569 | Working too close to overhead lines | [5 empty] | 2 | Building site constructed gantry and elevated site sheds on top of gantry below and around 66000 volt OH line. Site metalwork associated with gantry in contact with metal lighting pole. Advised Customer Works not to proceed. | Conductor (bare);Pole (wood);Pole (steel) | 2 | 2 | 2 |  | WMTS-VM2 | Builder carrying out works outside permit to work requirements | No Go Zone (no contact) | 42563.3542 |  |  | 4268 | Construction |  | 20161209PWA_01 | Infrastructure (network-based) | -37.8068 | 144.9426 | 2 | CitiPower | Report | 5357 | 0.0021447 | Low voltage AC (<1kV);66kV AC | Essendon Airport | 3003 | West Melbourne | Other
Crew attended, isolated supply and undertook repairs to replace centre phase attachment! | 1490 ROLLOS ROAD, NULLAWARRE VIC 3268 | 30136883 |  | Wind;Prone to salt deposition |  | Age;Corrosion |  | Phase to earth | 0 | A customer reported that there was a wire down and contacting the electric fence on his farm at the incident location. On arrival the crew found that a SWER insulator and pole cap, with the SWER conductor attached had become dislodged from the pole top and fallen. The conductor came to rest on an electric fence. The electric fence unit was apparently damaged. There was no ground fire or injury. | Pole top;Steel | 0 | 0 | 0 |  | WBL012 | Pole top assembly dislodged | Less than $50k damage | 42594.7639 |  |  | 4271 | Agricultural |  | 20161209PWA_02 | Infrastructure (network-based) | -38.4818 | 142.7047 | 1 | Powercor | Report | 12586 | 0.0074225 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3268 | Nullawarre | AF Other
On arrival crew commenced repairs. String of HV disc insulators on road side phase replaced and integrity of conductor termination confirmed. LV fused isolator blade replaced. | 21 HOMESTEAD DRIVE, KEILOR DOWNS VIC 3038 | 30111711 | Blown detritus | Wind |  |  |  |  | 1 | Mr Geoffrey James, of 28 Homestead Drive Keilor Downs called at 16.11hrs to report an electrical outage after a wind squall blew a marquis/canopy across the street and into overhead lines. Powercor crew attended site and identified plant damage, and HV to LV contact. The remnants of what appeared to be a light, tubular-framed car canopy/marquee were found near LIS 8251 Protection operated. There were no reported injuries or ground fire start. | Conductor (bare) | 2 | 2 | 2 |  | SA006 | Wind blew canopy onto line | Loss of supply | 42563.6743 |  |  | 4272 | Roadway |  | 20161209PWA_03 | Infrastructure (network-based) | -37.7261 | 144.8162 | 1 | Powercor | Report | 12413 | 0.026422 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3038 | Keilor Downs | Other
On arrival On arrival the crew found that the HV cross-arm had broken, HV conductors were dislodged and LV conductors were on the ground. LEI carried out checks for HVI Crew carried out repairs | 767 STRATHFIELDSAYE ROAD, STRATHFIELDSAYE VIC 3551 | 30041489 | Vehicle | [5 empty] | 1 | Vic Fire reported car hit a pole at 767 Strathfieldsaye Rd Strathfieldsaye. They also reported a damaged cross-arm, wires down on road and footpath, burn marks on houses and a small grass fire. There were no reported injuries, the car had driven off. | Conductor (bare);Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BGO013 | Car struck pole | HV injection;Loss of supply;Significant disruption to the community;Grassfire | 42686.625 | 1 | Small: 10 - 1000 sq.m | 4275 | Roadway |  | 20161212PWA_03 | Infrastructure (network-based) | -36.7974 | 144.3434 | 1 | Powercor | Report | 5368 | 0.010638 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3551 | Strathfieldsaye | Vehicle
on arrival l crew isolated line and commenced repairs. | 4674 PRINCES HIGHWAY, SKIBO VIC 3260 | 32059508 |  | Within clearances |  |  |  |  | 2 | A customer reported that he had cut a tree, and it had fallen on the power line at the incident location. On arrival the crew found that a large cypress tree had been cut on the North (side away from line) side by the customer, then the remainder of tree fell onto the 22kV High Voltage conductors on the South side of the tree line. The crew reported that the conductors remained aloft, and an emergency outage was required to remove the tree from the conductors. There were no injuries, and no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | TGTS-CDN | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 42655.5035 |  |  | 4276 | Agricultural |  | 20161212PWA_04 | Infrastructure (network-based) | -38.2171 | 143.1229 | 1 | Powercor | Report | 5371 | 0.0031898 | 22kV AC | Warrnambool Airport Ndb | 3260 | Skibo | Trees
On arrival crew replaced fuse unit | 2024 BENDIGO-TENNYSON ROAD, KAMAROOKA VIC 3570 | 30237533 |  |  |  | Candled fuse |  |  | 2 | Vic Fire reported a pole fire at 2024 BENDIGO-TENNYSON ROAD, KAMAROOKA. On arrival the crew found one of the two BA fuses was candling and had caused a fire underneath the pole. No shock, No injuries, Small ground fire 10m x 100m. Third party damage to customer canola crop. | Boric acid | 2 | 2 | 2 |  | EHK024 | leakage current | Grassfire | 42686.7153 | 1 | Small: 10 - 1000 sq.m | 4277 | Agricultural |  | 20161212PWA_05 | Infrastructure (network-based) | -36.4728 | 144.3806 | 1 | Powercor | Report | 5396 | 0.034611 | 22kV AC | Bendigo Airport | 3570 | Kamarooka | Fuse
On arrival crew carried out repairs | 20 AYTON STREET, SUNSHINE NORTH VIC 3020 | 30118234 | Vehicle | [5 empty] | 1 | The MFB reported that a truck has hit (side swiped) a pole and started a fire at the incident location. On arrival the fault crew found a truck had collided with pole LIS 21762 adjacent 20 Ayton Road . The collision resulted in the low voltage wooden cross-arm on this pole breaking in half and the cross-arm and tee-off conductors fell onto the low voltage conductors below. Contact between the low voltage conductors has caused low voltage bus fuses to operate on the pole three poles north of the incident location . Operation of the low voltage fuses caused hot debris to fall on the ground in a small grass fire. There was no injury as a result of this incident. | Conductor (bare);Any other type | 2 | 2 | 2 |  | SSE012 | Vehicle hitting pole | Loss of supply;Grassfire | 42716.4583 | 1 | Localised: less than 10 sq.m | 4279 | Roadway |  | 20161212PWA_06 | Infrastructure (network-based) | -37.7626 | 144.834 | 1 | Powercor | Report | 5374 | 0.03556 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
A EIV LEI (Frank Zahra) attended and commenced to assess the generator setup and the Coates Hire REC's work. The EIV LEI noted that Coates Hire had fitted locks and tags to most of his isolations but not completed any CES's and had not requested a LVIBS. After a discussion as a group, LEI Doug Hourigan stated that he had not finished the setup when the EIV LEI arrived even though the generators were running and the shops were on supply. At approximately 11.30AM a LVIBS was issued to the REC and the Coates Hire LEI left the site and did not return. Frank Zahra completed all changes to the generator isolation/installation setup and helped the REC complete their CES's as they only managed to find 4 certificates on site and a total of 9 were required. Reports were provided from ZNX (Ben Schmidt - HV Technical Officer) and Frank Zahra (EIV LEI). | CARINISH ROAD, CLAYTON VIC 3168 |  | Caused by REC/contractor | [5 empty] | 2 | As part of the Metro trains level crossing removal project, a ZNX construction crew had the task to relocate HV/LV poles and install 8 bays of overhead conductors in Carnish Road, Clayton near Centre Road. In summary, the HV/LV assets were being relocated from the south side to the north side of Carnish Road. As a result of the work, a large number of customers were affected during the planned shutdown between 8.00AM and 1.00PM. The ZNX construction crew received an Access Authority at 8.00AM for the work party to commence work on the HV/LV overhead and underground cables in Carnish Road. At approximately 9.00AM, a ZNX tester noticed that multiple shops were on supply in Carnish Road within the shutdown area. Upon investigation he found there was 5 generators connected to multiple premises. The Coates Hire REC was spoken to and he advised that his LEI (Doug Hourigan) had completed the installation of the generators to supply customers in the shut down area although this hadn't been brought to the attention of the ZNX workers. The ZNX construction work was immediately ceased and they began to investigate the generator setup. The LEI was questioned who stated to the HV Technical Officer that: - had not spoken to the ZNX work crew and no Low Voltage Isolation and Bonding Statement) LVIBS) had been issued - said that work crew members tell him to go to the next person so he decided to not engage in any conversation with ZNX employees on site - no CES's had been completed - the isolations were standard and did what he needed to do. (No lock or tags were installed at isolation points and no neutrals removed) - claimed there was no chance of back-feed into the network - if the crew have an issue, call Scott from Coates Hire as they were working for him. The HV Technical Officer contacted the United Energy control room and requested a ZNX LEI representative as they werenâ€™t happy with the quality of work from the Coates Hire LEI. The ZNX HV Operator changed the isolations on the Electrical Access permit and the construction crew continued with their planned work. The HV Technical Officer advised United Energy that "While the Job was able to proceed, and we were able to switch around the hazardous generator set up. The simple fact is that this posed and real hazard to our work force. At no point in the morning did anyone approach ZNX employees and hand over any documentation. I estimate that the work party were unable to proceed with their works in the morning for approximately 1.5h due to this incident". | Generator | 0 | 0 | 0 |  |  | Probable unsafe installation of generators to customer installations during a planned outage to complete overhead and underground MEC work. | Serious risk to MEC workers;Other | 42686.375 |  |  | 4282 | Commercial |  | 20161214UTD_01 | Infrastructure (network-based) | -37.9237 | 145.1198 | 1 | United Energy Distribution | Report | 5379 | 0.0092326 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Other
The north circuit of "Chapman-Station" substation was isolated and the faults crew requested a construction crew to attend and replace the damaged 95mm LVABC along with the attached 35mm and 25mm three phase overhead services that supplied the Railway Station and Scout Hall. The rectification work was completed and supply restored. | STATION STREET, SEAFORD VIC 3198 | 3305954 |  |  |  | Fatigue;Overheated connection |  |  | 2 | CFA advised of wires on fire outside the Seaford Station next to the RSL. Pole No. LIS 3305954 located in Station Street, Seaford has 150mm and 95mm LVABC with various services cables attached and it appears that IPC connections failed and caused a pole top fire. The cause was a probable loose connection or deterioration. | Service conductor;Aluminium;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | The cause was a probable loose connection or deterioration. | Pole-top fire | 42412.4583 | 1 | Negligible: no ground fire | 4283 | Roadway |  | 20161214UTD_02 | Infrastructure (network-based) | -38.1035 | 145.126 | 1 | United Energy Distribution | Report | 5380 | 0.035567 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
On arrival crew carried out repairs | 1 VICTORIA STREET, ROCHESTER VIC 3561 | 33084294 | Vehicle | [5 empty] | 2 | A customer rang to advise an truck had struck the overhead line at the incident location. On arrival the crew found a truck had struck the service cable to the house. The service had broken and was laying on the truck and driveway. The pole end of the broken service cable was still alive on the roadway. There were no reported fire, shocks or injuries. | Service conductor | 2 | 2 | 2 |  | SHP012 | Vehicle hit service cable | Loss of supply | 42502.4611 |  |  | 4293 | Residential |  | 20161219PWA_01 | Infrastructure (network-based) | -36.3605 | 144.6977 | 1 | Powercor | Report | 5402 | 0.011895 | Low voltage AC (<1kV) | Bendigo Airport | 3561 | Rochester | Vehicle
crew attended and made safe | 10 KINGSLEY STREET, ST ALBANS VIC 3021 | 32167390 |  | Precipitation | Highly unlikely | Leakage |  |  | 1 | Powercor fault crew attending an outage (SSE031 feeder) found a pole-top fire at the incident location. The crew isolated the faulty section and restored the feeder. No evidence of ground fire found. Protection operated as expected. There was suspected HVI however no damage was found. | Crossarm (wood) | 0 | 0 | 0 |  | SSE031 | excessive leakage current | Pole-top fire | 20/12/2016 6:14 | 1 | Negligible: no ground fire | 4313 | Residential |  | 20161220PWA_02 | Infrastructure (network-based) | -37.7539 | 144.8048 | 1 | Powercor | Report | 12415 | 0.039277 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3021 | St Albans | Pole
Analysis: â€¢ Subsequent investigations have revealed the following: â€¢ The Y4 Trip Coil on Q102 CB was completely burnt out. â€¢ The Emergency Stop scheme within AAGS sends a signal to this Coil for opening. â€¢ The SCADA and Local Commands send a signal to the Y1 Trip Coil. This is the coil we could hear energising and de-energising when manual commands were being issued. This coil is OK. No damage. â€¢ The ABB HV Switchgear Fitter who was on site for the annual maintenance investigated. He said the mechanism for Q012 CB was a bit dry, but was not willing to say that this stickiness was the reason for the CB failure to open. â€¢ Subsequent investigations into the Emergency Stop scheme shows that when you press the E-Stop P/B it stays in until you manually twist it and allow it to release. â€¢ By the P/B staying in and the CB not opening this keeps the Trip Current flowing on the Y4 Trip Coil. Hence the reason it got very hot and eventually burst into flames. Noting that Trip Coils are not meant to be continuously rated. â€¢ It is thought that Protection Trip signals from the Protection Relay are pulsed (1 sec) and hence if this request to open was via the Protection Relay whilst the CB would not have opened at least the Y4 Coil would not have cooked. â€¢ The Emergency Stop does not utilise the Protection Relay to issue the open signal, and this is a valid situation, because the reason you may want to issue an E-Stop could be because the Protection Relay has failed in some way. So going external to the relay is a reasonable application. But of course if the CB fails to open (jammed mechanism etc) then the situation we encountered is a real possibility. â€¢ Therefore some further consideration needs to be taken to assess if we need to modify this Emergency Stop Scheme. â€¢ It is noted that Q102 CB along with the other HV CBâ€™s at AAGS do not operate in anger very often. However it is operated more often than Q101 andQ103 which when asked to open on this day did so without any hesitation. Subsequent Actions: â€¢ Fortunately there was no wiring loom or other equipment immediately above the Y4 Trip Coil and hence no other obvious damage. â€¢ A spare Y4 Coil and assembly was located and installed. â€¢ The ABB Fitter serviced the CB and cleared it for service. â€¢ The Station Fire Extinguisher has since been replaced. â€¢ Report is pending from ABB. | 68 COMMERCIAL DRIVE, THOMASTOWN VIC 3074 |  |  |  | Highly unlikely | Electrical overload |  |  | 2 | IMS 225384. Report on Burnt Trip Coil at AAGS for Q102 HV CB Monday 21st Nov, 2016 No persons were hurt or in immediate danger due to this incident, however if this same thing happened when the station was un-attended the flames may have caused more damage. Background: On Monday 21st Nov as part of the Annual maintenance at AAGS an EAP was to be issued. To facilitate testing of the Emergency Stop the plan was to activate the E-Stop push-button to perform the initial de-energisation of the station. Then the Operator would continue isolations and earthing as per normal. As per NEMS 325406. Sequence of Events: â€¢ At 10:16 AM E-Stop was pressed, all equipment performed as per the schedule except that Q102 HV CB did not trip. â€¢ Several more attempts were made from other E-Stop pushbuttons. â€¢ Investigations were launched into why this did not happen. Schematics consulted etc. â€¢ After about 8 minutes it was decided to manually Open Q102. CEOT attempted via SCADA and no result. â€¢ Q102 was placed into Local Control and an Open was attempted from the Control Panel, no result. Note a solenoid (coil) could be heard to be picking up and dropping out behind the CB mechanism panel. â€¢ It was decided to de-energise the transformer by opening Q0101 and Q103 HV CBâ€™s, by continuing with the NEMS instructions. â€¢ After approx. another 10 minutes the Operator said there were flames coming from behind the CB mechanism panel. â€¢ A Fire Extinguisher was placed against the gap between the two panels and activated. The flames went out. â€¢ The DC Supply MCBâ€™s were located for the controls to the CBâ€™s and turned off. | Circuit breaker | 0 | 0 | 0 |  |  | Trip coil on Q102 CB was burnt out. Emergency Stop scheme modification may be required. | Plant/equipment | 21/11/2016 10:00 | 1 | Negligible: no ground fire | 4312 | Other | Energy storage facility | 20161220SPN_02 | Infrastructure (network-based) | -37.6903 | 145.0427 | 1 | AusNet Services Distribution | Report | 5529 | 0.0094398 | Extra low voltage DC (<120V ripple free) | Essendon Airport | 3074 | Thomastown | AF Other
On arrival crew checked site for damage LEI organised to check for HVI. | 2 VALEWOOD DRIVE, KEALBA VIC 3021 | 30110872 | Vehicle | [5 empty] | 1 | Mr John Condon phoned in to advise of a wire down and a small grass fire at the incident location. Upon arrival the crew had found that an unknown truck had come into contact with the CATV at the intersection of Calverton Road/Driscolls Rd (southern side of No. 2 Valewood Drive, Kealba 3021) and flicked the Foxtel into the LV above which caused sparks to fall to the ground. There was subsequently reports of HV injection . The resultant sparks from this caused 2 x minor grass fires and scorch marks on the nature strip There was no injury or shocks as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | SA002 | Unknown vehicle flicked cable TV wire into LV | HV injection;Loss of supply;Grassfire | 20/12/2016 19:04 | 1 | Localised: less than 10 sq.m | 4322 | Roadway |  | 20161222PWA_01 | Infrastructure (network-based) | -37.7326 | 144.824 | 1 | Powercor | Report | 5507 | 0.016264 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kealba | Vehicle
On arrival crew checked conductors and restored supply. | 156 MCCONNELLS ROAD, TAROON VIC 3265 | 32058903 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A Powercor Customer reported that a tractor with a machine on it had hit the overhead wire at the incident location. On arrival the fault crew reported that a muck auger being used for cleaning a dairy effluent dam, was being moved in the raised position, when the front wheels of the tractor reportedly fell into a hole, this in turn caused the muck auger to contact the overhead HV SWER conductor. There was no reported damage to the overhead line or the muck auger, however the two front tires of the tractor blew out, and the ground was slightly scorched. There were no injuries, no grassfire. | Conductor (bare) | 2 | 2 | 2 |  | TRG004 | farm equipment being relocated | Loss of supply | 21/12/2016 15:08 |  |  | 4326 | Agricultural |  | 20161222PWA_03 | Infrastructure (network-based) | -38.3464 | 142.8536 | 1 | Powercor | Report | 5445 | 0.0021933 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3265 | Taroon | Vehicle
The incident led to a minor fire which was extinguished by MFB. Addtionally, Jemena fault crew attended site to conduct repairs, all three active connections on the LV have been brought up to the current standards. | 39 BIRCH AVENUE, TULLAMARINE VIC 3043 |  |  |  |  | Overheated connection |  | Phase to earth | 1 | The red phase (footpath side) LV connector lead between the Birch-Broadmeadows substation LV isolators and LV mains electrically failed due to burnt out contacts. Sparking from failure caused a grass fire to a vacant lot and also impacted a property fence surrounding the lot. | Aluminium;Dropper/bridge | 0 | 0 | 0 |  | AW11 | LV connection failure was possibly due to overload on hot weather day. It appears that this has caused conductor insulation to melt. | Grassfire | 25/12/2016 17:00 | 1 | Small: 10 - 1000 sq.m | 4340 | Residential |  | 20161226JEM_01 | Infrastructure (network-based) | -37.7054 | 144.8799 | 1 | Jemena | Report | 5464 | 0.012464 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Connection
On arrival crew commenced repairs | 287 TWELFTH STREET, MILDURA VIC 3500 | 33064891 |  | Bird |  | Fuse failed to eject |  |  | 0 | A customer reports grass smoking at base of a pole at the incident location. A crew attended and found a bird at the base of SW/P1 MDA Golf S/L and 2 HV fuses had operated on the SW pole. One of the fuses had hung up and burnt, dropping debris to the ground. There was a grass fire of approx. 1sqm at the base of the pole. CFA did not attend and the fire had self-extinguished before the crew arrived. | EDO fuse | 2 | 2 | 2 |  | MDA033 | Bird Incident | Grassfire | 18/11/2016 9:56 | 1 | Localised: less than 10 sq.m | 4198 | Public space |  | 20161122PWA_05 | Infrastructure (network-based) | -34.1793 | 142.1413 | 1 | Powercor | Report | 5245 | 0.0091933 | 22kV AC | Mildura Airport | 3500 | Mildura | Animal
CEOT dispatched a fault crew to isolate, make safe and repair. Crew made safe, repaired and restored supply. Replaced fuse holder (fuse tube) and fuse link. | 45 GERARD ROAD, SUGARLOAF CREEK VIC 3658 | 4701254 |  |  |  | Defective component |  |  | 2 | IMS 225404. On arrival to SMR BFD 205 substation, one EDO HV fuse had candled and there was an earth lead tail hanging from the lightning arrestor, but unable to determine if this had caused the fault. There were no deceased bird life or animals in vicinity. Summary: * When the crew arrived onsite they found the earthed tail on the lightning arrestor had operated and the EDO fuse tube had candled, there was no evidence of any animal or bird that may have caused the fault. It is not known if the lightning arrestor had operated as part of this fault or at a previous time. * The lightning arrester was not replaced, only the fuse tube on the EDO was replaced. * No fire occurred. * Weather conditions were fine. Further information: * The failure rates of Surge Diverters are managed in accordance with AusNet Servicesâ€™ strategy for Line Surge Diverters. Four modes of failure are common for medium-voltage surge arresters: 1. Leakage currents trigger disconnection; 2. Seal failure allows moisture ingress; 3 External arcing fault; 4. Amplitude of lightning strike exceeds surge arrester ratings. | EDO fuse;Surge diverter | 0 | 0 | 0 |  | SMR3 | It appears a Lightning Arrestor was involved. | Other electricity related | 23/11/2016 18:40 | 1 | Negligible: no ground fire | 4209 | Agricultural |  | 20161124SPN_02 | Infrastructure (network-based) | -37.1247 | 145.0265 | 1 | AusNet Services Distribution | Report | 11241 | 0.016381 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Sugarloaf Creek | Fuse
The faults crew made the site safe and replaced the three phase FOLCB that supplied the underground cable to the commercial development. Installation tests were completed and supply was left on. | 23-25 OVERTON ROAD, SEAFORD VIC 3198 | 3308361 |  |  |  | Electrical overload;Overheated connection |  |  | 2 | Pole fire per CFA outside "Energym" - Business name. The CFA were in attendance at pole (LIS No. 3308361) located outside 25 Overton Road. The three phase FOLCB was damaged following a pole fire that started at the red phase LV terminals that burnt out the junction box on the pole that supplied an underground supply to "Frankston 4x4 and Light Commercial". Overload was the probable cause for the FOLCB to fail. | Cable;Connection box | 0 | 0 | 0 |  |  | Overload was the probable cause for the three phase FOLCB to fail. | Pole-top fire | 22/11/2016 11:05 | 1 | Negligible: no ground fire | 4208 | Commercial |  | 20161124UTD_01 | Infrastructure (network-based) | -38.1294 | 145.1297 | 1 | United Energy Distribution | Report | 5259 | 0.0020914 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Pole
A faults truck attended and found no damage was sustained to the timber pole but identified the HV earth had been stolen from the substation pole. The crew replaced the 3m of cable that was stolen and ensured the substation pole was safe. The copper theft and car fire were unrelated. | GLASSCOCKS ROAD, DANDENONG SOUTH VIC 3175 | 206770 | Copper theft |  |  | Earth fault |  |  | 2 | CFA report of a car fire near a pole in Glasscocks Road, Dandenong South 1 pole west of Taylors Road. Please check the pole for safety. A car fire occurred near "Glasscocks-Taylors" pole type substation (pole No. LIS 0623662) and the CFA were in attendance to extinguish the fire. They contacted the United Energy faults and emergencies call centre suggesting the pole is checked for any damage following the fire. | Copper | 0 | 0 | 0 |  |  | The CFA requested United Energy to check their assets after a car fire in close proximity to a substation pole. | Damage to network assets | 25/11/2016 23:30 |  |  | 4231 | Agricultural |  | 20161129UTD_02 | Infrastructure (network-based) | -38.0607 | 145.2251 | 1 | United Energy Distribution | Report | 5397 | 0.025784 | Earthing cable | Moorabbin Airport | 3175 | Dandenong South | Other
On arrival crew isolated line and carried out repairs | 73 PICKERING ROAD, LAKE MERAN VIC 3579 | 32032402 |  |  |  | Leakage |  |  | 1 | Powercor started to receive calls from customers in the Lake Meran area, reporting a pole fire. Crews were dispatched to the area and found a crossarm fire on P130 Boort line. There were no ground fires, injuries or 3rd party property damage reported. | Crossarm (wood) | 2 | 2 | 2 |  | KGT004 | Excessive leakage current, no further details known | Pole-top fire | 42685.9986 | 1 | Negligible: no ground fire | 4234 | Roadway |  | 20161130PWA_02 | Infrastructure (network-based) | -35.8654 | 143.8037 | 1 | Powercor | Report | 5310 | 0.022964 | 22kV AC | Swan Hill Aerodrome | 3579 | Lake Meran | Pole
CEOT dispatched a fault crew to isolate supply, make safe and investigate. CEOT also dispatched the DAO to attend to investigate the incident. No one was allowed on the site until an investigation had taken place by the relevant aeronautical industry authority. The work crew had to join and re-sag the broken two steel conductors. | 1395 MEENIYAN-MIRBOO NORTH ROAD, DUMBALK VIC 3956 | 2002159 | Working too close to overhead lines;Manned aircraft |  |  |  |  | Three phase | 1 | IMS 225526. Police reported to AusNet Services that a helicopter has made contact with a AusNet Services' pole. Details from the attending DAO was that the helicopter contacted three phase HV conductors between poles 2002159 and 2002160 bring them to the ground. This incident also resulted in damage to other adjacent conductor spans. The pilot was spraying chemicals at the time. The DAO advised that the pilot was taken to hospital for minor injuries. Electrical protection operated. | Conductor (bare) | 0 | 0 | 0 |  | lga13 | A helicopter contacted overhead 22kV conductors. | Loss of supply;Medical attention (first aid/doctor/hospital);No Go Zone (contact) | 29/11/2016 17:55 |  |  | 4232 | Agricultural |  | 20161130SPN_01 | Infrastructure (network-based) | -38.5011 | 146.1215 | 1 | AusNet Services Distribution | Report | 5294 | 0.03948 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Dumbalk | Other
On arrival crew isolated supply and carried out repairs | 431 BARINGHUP-HAVELOCK ROAD, BARINGHUP WEST VIC 3463 | 33011872 |  |  |  | Overheated connection |  |  | 1 | Customer reported a transformer on fire and associated ground fire at the incident location. On arrival the crew found that a LV fused isolator connection was loose and overheated, dropping molten material to the ground, a small ground fire resulted. There were no reported injuries or 3rd party damage. | Disconnector/isolator | 2 | 2 | 2 |  | MRO007 | Loose connection | Pole-top fire | 30/11/2016 17:40 | 1 | Small: 10 - 1000 sq.m | 4238 | Roadway |  | 20161201PWA_01 | Infrastructure (network-based) | -36.979 | 143.9032 | 1 | Powercor | Report | 5304 | 0.026233 | Low voltage AC (<1kV) | Bendigo Airport | 3463 | Baringhup West | Connection
The single large tree branch was cut back by the faults crew and supply restored to customers supplied from 22kV feeder RBD 11. | 8 ALLAMBI AVENUE, ROSEBUD WEST VIC 3940 | 1311762 |  | Wind;Alive;Council |  |  |  |  | 1 | At 1220hrs on 22/11/2016, 22kV feeder RBD 11 circuit breaker reclosed to lockout affecting 1123 customers. The CFA advised that a tree has caught fire after coming into contact with powerlines. During strong winds, a tree branch from a nature strip gum tree located outside 8 Allambi Avenue adjacent to pole No. LIS 1311762 caught fire after making contact with the 22kV overhead conductors. The large gum tree was located on the other side of the road to the HV/LV conductors and the CFA were in attendance. | Conductor (bare) | 0 | 0 | 0 |  | RBD 11 | Vegetation: Trees Incident | Other vegetation | 22/11/2016 12:20 | 1 | Negligible: no ground fire | 4244 | Roadway |  | 20161201UTD_01 | Infrastructure (network-based) | -38.3719 | 144.8874 | 1 | United Energy Distribution | Report | 5390 | 0.035606 | 22kV AC | Moorabbin Airport | 3940 | Rosebud West | Trees
Jemena employee from underground crew attended the site and the underground cable was inspected for damage and reinstated the covers and warning tape. No damage was done to Jemena assets. | 331-333 ASCOT VALE ROAD, MOONEE PONDS VIC 3039 |  | Working too close to underground cables;Unauthorised work | [5 empty] | 2 | External plumbing contractor was excavating adjacent to HV underground cable on feeder NS18 without No Go Zone permit. | Cable | 0 | 0 | 0 |  | NS18 | External plumbing contractor excavating without No Go Zone permit. | No Go Zone (no contact) | 42412.4132 |  |  | 4246 | Construction |  | 20161202JEM_01 | Infrastructure (network-based) | -37.7683 | 144.9244 | 1 | Jemena | Report | 12378 | 0.040916 | 11kV AC | Essendon Airport | 3039 | Moonee Ponds | Other
On arrival crew organised repairs | 2 GRAMMAR COURT, SHEPPARTON NORTH VIC 3631 | 33096736 |  | Bird |  |  |  |  | 1 | SCADA reported protection operations on SHTS-NKA 66KV NO.2 and SHN11 22kV feeders. Crew patrolled between pole 1 and pole 50 of the SHTS-NKA 66KV NO.2 line. On arrival at P22 the crew found that a bird (corella), had flashed over between the centre phase 22kV stand of insulator and the outer phase. The remains of the bird were found at the base of the pole appearing to be the catalyst of the small grass fire which had extinguished itself prior to the crew attending which was approximately 1m X 1m in area of grass burnt. | Conductor (bare) | 2 | 2 | 2 |  | SHTSNKA2 SHN011 | Bird Incident | Grassfire | 42441.3812 | 1 | Localised: less than 10 sq.m | 4257 | Roadway |  | 20161206PWA_03 | Infrastructure (network-based) | -36.3295 | 145.415 | 1 | Powercor | Report | 5340 | 0.0083808 | 22kV AC;66kV AC | Shepparton Airport | 3631 | Shepparton North | Animal
On arrival crew commenced repairs. REC engaged to replace the customers CB. | 4854 HAMILTON-CHATSWORTH ROAD, NAREEB VIC 3293 | 30043100 |  |  |  | Overheated connection |  |  | 2 | The property owner reported a pole fire at the incident location. On arrival the crew found that a connection in a pole mounted circuit breaker had overheated causing the circuit breaker to catch fire resulting in minor damage to the pole. There was no ground fire. There were no reported injuries. | Connection box;Customer installation | 2 | 2 | 2 |  | TRG002 | Connection failure | Pole-top fire | 24/11/2016 12:00 | 1 | Negligible: no ground fire | 4265 | Agricultural |  | 20161208PWA_02 | Infrastructure (network-based) | -37.8592 | 142.5666 | 1 | Powercor | Report | 5352 | 0.029625 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3293 | Nareeb | Connection
The faults crew sleeved and re-sagged the LV white and blue phase conductors and supply was restored after 3 LV fuses were replaced at "Ingram-Svale" substation. | 1 VICTORIA AVENUE, GLEN WAVERLEY VIC 3150 | 604872 |  | Within clearances |  | Conductor clashing |  |  | 1 | At 1802hrs on 30/11/2016, customers supplied from "Ingram-Svale" substation advised of a loss of their electricity supply. The occupier at 1 Mount Street, Glen Waverley was cutting a private tree branch when it twisted and blew in the wind towards the LV overhead conductors. The tree branch contacted the LV conductors causing two LV conductors to fall to the ground (not live) and interrupt the electricity supply to approximately 78 customers. The property is located on the corner of Mount Street and Victoria Avenue near pole number LIS 0604872. The customer did not appear to receive an electric shock but did sustain a minor injury to his ribs whilst trying to control the falling branch. The faults crew were quickly on site making the site safe and broke a set of LV bridges and installed a LV parallel to restore supply to all but 10 customers as the repairs commenced. It was found that all 3 LV circuit fuses had operated at "Ingram-Svale" substation. | Conductor (bare);Copper | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply | 30/11/2016 18:02 |  |  | 4264 | Residential |  | 20161208UTD_01 | Infrastructure (network-based) | -37.8847 | 145.1666 | 1 | United Energy Distribution | Report | 5415 | 0.030192 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Glen Waverley | Trees
On arrival crew carried out repairs | 3689 GLENELG HIGHWAY, PITTONG VIC 3360 | 32002839 |  |  |  | Leakage |  |  | 1 | A person driving past a pole noticed the cross arm was on fire at the address below. On arrival the work crew found a cross arm had burnt off and the conductor was still alive in the air. There was no ground fire. No third party damage or injury was reported. | Crossarm (wood) | 2 | 2 | 2 |  | BAS021 | Crossarm fire due to excessive leakage current | Pole-top fire | 42502.2292 | 1 | Negligible: no ground fire | 4274 | Roadway |  | 20161212PWA_02 | Infrastructure (network-based) | -37.6726 | 143.4515 | 1 | Powercor | Report | 12280 | 0.038413 | 22kV AC | Ballarat Aerodrome | 3689 | Pittong | Crossarm
Site made safe , supply isolated and repairs made | 9 PORT PATRICK COURT, GREENVALE VIC 3059 |  | Working too close to underground cables |  | Highly unlikely |  |  |  | 1 | Directional borer damaged mains underground cable. | Cable | 0 | 0 | 0 |  | COO14 | Third party directional boring | Loss of supply | 14/12/2016 13:20 |  |  | 4287 | Roadway |  | 20161214JEM_01 | Infrastructure (network-based) | -37.6456 | 144.9072 | 1 | Jemena | Report | 12379 | 0.022536 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Dug up
On arrival crew commenced repairs | 4 GLOVER STREET, SOUTH MELBOURNE VIC 3205 | 30170187 |  | Alive |  |  |  |  | 2 | Two passers-by reported a wire down at the incident location. On arrival the fault crew found that the road side low voltage conductor had failed mid span due to rubbing against a large tree branch at the incident location. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | AP014 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42533.3535 |  |  | 4289 | Roadway |  | 20161215PWA_01 | Infrastructure (network-based) | -37.84 | 144.9497 | 1 | CitiPower | Report | 5388 | 0.022223 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Conductor
On arrival crew arranged for repairs to be carried out | 379-393 ALBERT STREET, BRUNSWICK VIC 3056 | 30160338 | Copper theft | [5 empty] | 2 | A CitiPower operator, Roland Power, attending a fault and reported 2m of earthing cables on LIS 46071 (SW#2342) had been stolen and the earthing cable on LIS 46124 (SW#2341) cut at the incident location. T here were no injuries, other damages or fire | Earth/earthing | 2 | 2 | 2 |  | WB006 | cable theft | Damage to network assets | 42594.4639 |  |  | 4304 | Roadway |  | 20161219PWA_07 | Infrastructure (network-based) | -37.7678 | 144.9546 | 1 | CitiPower | Report | 5418 | 0.040424 | Earthing cable | Essendon Airport | 3056 | Brunswick | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1310 MORNINGTON-FLINDERS ROAD, MAIN RIDGE VIC 3928 | 1313929 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | Customer reports that a wire is down at waist height between the pole to pole. Customers downstream of RB0045 located in Mornington-Flinders Road advised of a loss of their electricity supply. A tree branch from a council tree located in Mornington-Flinders Road near Orchard Street contacted the 22kV conductors that resulted in a HV conductor to briefly contact the LV white phase and neutral conductors near pole No. LIS 1313929. The tree branch falling onto the HV conductors caused 3 x 40amp Boric Acid fuses to operate at RB0045 located in Mornington-Flinders Road. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Mtn Flind-P2AA Tucks" substation. The LEI confirmed a high voltage injection occurred (MOR 1610) affecting 4 customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Boric acid | 0 | 0 | 0 |  | DMA 23 | Vegetation: Trees Incident | HV injection;Loss of supply | 42594.4417 |  |  | 4303 | Roadway |  | 20161219UTD_02 | Infrastructure (network-based) | -38.3931 | 144.9928 | 1 | United Energy Distribution | Report | 5417 | 0.0008125 | 22kV AC | Moorabbin Airport | 3928 | Main Ridge | Trees
CEOT dispatched a fault crew to isolate, make safe and repair. CEOT also dispatched the local DAO to investigate the incident. The fault crew replaced the White Phase Ampact connector at top of ACR line side isolator. | 539 PHILLIP ISLAND ROAD, SAN REMO VIC 3925 | 2812439 |  |  |  | Electrical breakdown |  |  | 0 | IMS 225855. CEOT received a CFA report of a small 4m x 6m grass fire in the vicinity of pole LIS 2812439, Switch WG026. AusNet Services' fault crew attended the site and discovered a small 6m x 4m fire had burnt out in relatively short green grass at the base of the concrete pole. The White Phase Ampact connector had failed at the top of the ACR line side isolator. No damage to property. Additional information regarding electrical protection not operating: There was no phase to phase or phase to earth fault. As a result electrical protection would not have operated. It was just a bad (failed) joint which would have caused sparking with sparks then igniting a small grass fire. | Connector/termination | 0 | 0 | 0 |  | wgi31 | Failed Ampact connector on a non-tension joint. | Grassfire | 19/12/2016 17:55 | 1 | Small: 10 - 1000 sq.m | 4308 | Roadway |  | 20161220SPN_01 | Infrastructure (network-based) | -38.522 | 145.3873 | 1 | AusNet Services Distribution | Report | 12338 | 0.030778 | 22kV AC | Moorabbin Airport | 3925 | San Remo | Connection
On arrival crew commenced repairs. Defect issued for fascia and mains box repair Left off supply. | 104 PAYNES LANE, LANCASTER VIC 3620 | 32188133 | Vehicle | [5 empty] | 2 | Customer reported that they had no supply and that the service cable was on the ground. Neighbour had extinguished a small grass fire. A high load vehicle had made contact with multiphase service mains cable from substation pole direct to house damaging the customers facia board and breaking the service mains cable. Crew attended and the Police were onsite. Vehicle details unknown by Police in attendance. Small grass fire, Property damage to facia board and customers mains, | Service conductor | 2 | 2 | 2 |  | KYM003 | Unknown vehicle struck service line | Loss of supply;Grassfire | 20/12/2016 18:43 | 1 | Localised: less than 10 sq.m | 4320 | Roadway |  | 20161221PWA_02 | Infrastructure (network-based) | -36.3211 | 145.1151 | 1 | Powercor | Report | 5439 | 0.014135 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Lancaster | Vehicle
The fault crew requested that a substation crew attend to assist the REC and to make repairs to the lock. The United Energy duty manager was advised of the break-in and the stolen consumers copper cables. | FERNTREE GULLY ROAD, WHEELERS HILL VIC 3150 |  | Unauthorised access;Copper theft | [6 empty] | REC advised the substation on the corner of Ferntree Gully and Jells Roads has the doors open and wires are exposed. The REC believes the substation has been broken into. Business name is Lifestyle. Thieves have broken into "Community Centre - FTG" indoor substation and removed the customers copper cables that goes through to the customers switch room. There was minor damage to the substation locking mechanism but a substantial amount of copper cables have been removed. | Equipment;Indoor;Connector/termination | 0 | 0 | 0 |  | MGE 23 | Theft of consumers copper cables from an indoor substation. | Significant disruption to the community;No Go Zone (contact) | 19/12/2016 20:00 |  |  | 4330 | Commercial |  | 20161222UTD_03 | Infrastructure (network-based) | -37.9062 | 145.1884 | 1 | United Energy Distribution | Report | 5449 | 0.038362 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Wheelers Hill | Other
On arrival crew commenced repairs. | 148 ARTHURTON ROAD, NORTHCOTE VIC 3070 | 30198893 | Working too close to overhead lines |  |  |  | Ineffective planning/procedures/processes |  | 2 | A customer reported that a scissor lift has contacted the overhead lines at the incident location. On arrival the fault crew found that a scissor lift was being used to install flood lights to the building at the incident location. The two installers failed to observe the low voltage overhead conductors and other assets in the vicinity. The lift was raised and eventually contacted the low voltage conductors causing shorting between the white and blue phases. There was no Permit to work on issue. There was no fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | NC005 | Scissor lift contacted Low voltage | No Go Zone (contact) | 22/12/2016 12:00 |  |  | 4335 | Roadway |  | 20161223PWA_03 | Infrastructure (network-based) | -37.7677 | 144.9868 | 1 | CitiPower | Report | 5456 | 0.04065 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
On arrival crew isolated supply | WESTERN HIGHWAY, LILLIMUR VIC 3420 | 32102468 |  |  |  | Fault on customer installation |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a VicRoads Traffic Counter unmetered supply installation located in the road reserve and connected to a high voltage/low voltage wooden pole had burnt through at a supply protection device located on the pole approximately 4m above ground. There was a ground fire in the road reserve and private property covering an area of approximately 80m x 10m. There were no reported injuries. | Customer installation | 2 | 2 | 2 |  | NHL031 | unknown fault in customers installation | Grassfire | 22/12/2016 16:22 | 0 | Small: 10 - 1000 sq.m | 4337 | Roadway |  | 20161223PWA_05 | Infrastructure (network-based) | -36.3618 | 141.1266 | 1 | Powercor | Report | 5458 | 0.0089745 | Low voltage AC (<1kV) | Horsham Aerodrome | 3420 | Lillimur | Pole
A faults truck attended the property but couldnâ€™t gain access due to the pad locked front gate and high fence. They proceeded to check connections at the pole end and found the three phase XLPE service had incorrect connections with two actives connected to the LV white phase conductor and the third phase was connected to the blue phase conductor. The three phase XLPE service and the termination clamps, including the new aluminium line taps, are a type commonly used by the Victorian Electricity Supply Industry. The crew measured current on the active conductors with greater than 60amps identified on each phase. The two man faults crew suspected possible drug related activities at the property and notified the Resource Coordinator of their findings. The Resource Coordinator contacted the Springvale Police Station and officers promptly attended and cut the pad lock to access the property and they commenced a drug bust investigation. The faults crew checked the three phase FOLCB at the POA that appeared to be a similar type used by the Victorian Electricity Supply Industry. The neutral terminal block was severely burnt out and the faults crew removed roof tiles and identified an illegal connection to the consumers mains behind the three phase FOLCB that bypassed the single phase meter. The three phase XLPE overhead service was abolished along with the single phase meter. | 25 ROYAL AVENUE, SPRINGVALE VIC 3171 |  | Unauthorised work;Unauthorised access |  |  | Electrical overload;Overheated connection |  |  | 2 | United Energy AMI technicians advised that meter number 0649984 has communicated extremely high voltages over 300v and they suspect there is a problem with the neutral. A single phase AMI meter at 25 Royal Avenue, Springvale was communicating high voltages and AMI technicians suspected there was a problem with a neutral conductor. A Downer faults crew was dispatched to investigate. Google Map images showed a single phase neutral screened service was connected to the property. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Unauthorised installation of a three phase XLPE overhead service by unknown persons and an illegal bypass of the single phase meter for drug related activities. | Singeing or local charring/blackening only | 18/12/2016 7:00 |  |  | 4341 | Residential |  | 20161228UTD_01 | Infrastructure (network-based) | -37.9507 | 145.1489 | 1 | United Energy Distribution | Report | 5462 | 0.0019792 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Other
On arrival crew carried out repairs | BOWLANDS ROAD, LEITCHVILLE VIC 3567 | 30028343 |  | Lightning |  |  |  |  | 1 | Powercor fault crew reported ground fire associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total. There were no reported injuries or 3rd party damage. Protection operated ( CHA3 & CHA6 feeder CBâ€™s reclosed ). | Conductor (bare);Pole (wood);Disconnector/isolator | 2 | 2 | 2 |  | CHA006 CHA003 | Lightning strike causing flashover | Grassfire | 24/12/2016 11:59 | 1 | Localised: less than 10 sq.m | 4346 | Roadway |  | 20161229PWA_01 | Infrastructure (network-based) | -35.8122 | 144.213 | 1 | Powercor | Report | 12095 | 0.013727 | 22kV AC | Swan Hill Aerodrome | 3567 | Leitchville | Lightning
On arrival crew commenced repairs | 9 LAMBHILL CRESCENT, HIGHTON VIC 3216 | 32083825 |  |  |  | Mechanical breakdown |  |  | 2 | Vicfire advised of a wire down with Arcing and sparking. Attending crew found service cable had parted in span and supply end had been brushing against cable guard on pole, and had ignited a small ground fire. There was no injuries or third property damage. | Service conductor | 2 | 2 | 2 |  | WPD013 | Service line parted mid span. | Grassfire | 25/12/2016 15:46 | 1 | Localised: less than 10 sq.m | 4354 | Roadway |  | 20161229PWA_08 | Infrastructure (network-based) | -38.1661 | 144.3135 | 1 | Powercor | Report | 5477 | 0.017241 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | OH Cable
The incident site was excavated and repairs were undertaken on a 4c x185mm LV mains cable. The stake had cut into two cores of the LV mains cable. | 7 PIRIE WAY, TAYLORS HILL VIC 3037 | 30302458 | Working too close to underground cables | [5 empty] | 1 | Suzanne Micallef of 7 Pirie Way Taylors Hill rang in to advise that her husband had struck an underground cable while staking a tree on the nature strip outside their residence. She reported that both her residence and her neighbourâ€™s were off supply. Powercor crews attended to this site in the afternoon and discovered blown R & W LV fuses on a short LV mains circuit ex â€œNorth-Pirieâ€ substation. Protection operated. There were no reported injuries or ground fire start. | Cable | 2 | 2 | 2 |  | SA011 | Vegetation: Trees Incident | Loss of supply | 42686.4743 |  |  | 4362 | Public space |  | 20161230PWA_01 | Infrastructure (network-based) | -37.7191 | 144.7434 | 1 | Powercor | Report | 5485 | 0.030545 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Taylors Hill | Trees
On arrival crew isolated supply to allow REC to carry out repairs. | 717 GRAHAM ROAD, KYABRAM VIC 3620 | 33088500 | Working too close to underground cables | [5 empty] | 2 | REC reported that Ranbuild excavator which was excavating for new footings for a new shed had hit underground cabling between pit and house exposing the cabling. REC needed PAL to disconnect in pit and attend to exposed cabling so that he can also do repair work. REC works for Ranbuild (Echuca) 03 5482-1100. There were no reported injuries or 3rd party damage Note: Ranbuild is contracted by Brian Savva (owner/witness) | Customer installation | 2 | 2 | 2 |  | KYM004 | contractor excavating | No Go Zone (no contact) | 42563.6771 |  |  | 4365 | Residential |  | 20161230PWA_03 | Infrastructure (network-based) | -36.2988 | 145.0522 | 1 | Powercor | Report | 12420 | 0.033988 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Kyabram | Dug up
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | MITCHELL ROAD, CAULFIELD NORTH VIC 3161 |  |  | Lightning |  | HV injection |  |  | 2 | Customers supplied from "Glen Eira - Hawthorn" substation are advising of a loss of their electricity supply after the storm passed. Following a storm that struck Melbourne at approximately 3.15PM on 29/12/2016, customers in Mitchell Road, Caulfield North lost their electricity supply after lightning struck at an unknown location. Several AMI meters were damaged and required replacement whilst others told the faults crew they had damaged appliances. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Glen Eira-Hawthorn" substation. The LEI confirmed a high voltage injection occurred (CLA 1607) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Smart meter | 0 | 0 | 0 |  | EL 12 | Lightning | HV injection;Loss of supply;Damage to network assets | 29/12/2016 15:30 |  |  | 4363 | Residential |  | 20161230UTD_01 | Infrastructure (network-based) | -37.878 | 145.0222 | 1 | United Energy Distribution | Report | 5486 | 0.00078704 | 11kV AC | Moorabbin Airport | 3161 | Caulfield North | Lightning
On arrival crews undertook repairs | 16-26 MANZEENE AVENUE, LARA VIC 3212 | 32067774 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | An employee reported damaged UG LV earth cable at incident location. On arrival the crews found the damaged earth cables near the base of the pole. No excavator was on site however it appeared the damage was done in the last few days while road civil work was being undertaken for an adjoining new subdivision. Supply was not interrupted. There was no shock, injuries, ground fire or other third party property damage reported. | Earth/earthing | 2 | 2 | 2 |  | FNS021 | Digging works near substation by unknown party. | No Go Zone (contact);Damage to network assets | 17/12/2016 12:07 |  |  | 4381 | Roadway |  | 20170103PWA_04 | Infrastructure (network-based) | -38.0193 | 144.3809 | 1 | Powercor | Report | 5516 | 0.015749 | Earthing cable | Avalon Airport | 3212 | Lara | Dug up
CEOT dispatched a fault crew isolate, make safe and investigate. The attending LEI inspected the customers' switchboards and associated wiring connected to the affected overhead reticulation and found visible damage to various properties. The LEI left the site after customers' assets were assessed and believed it was safe to energise when repairs were completed. | 1 CLIFFORD GROVE, TECOMA VIC 3160 | 1306847 |  | Fallen;MEC |  |  |  | Phase to phase | 1 | IMS 225928. A tree branch hit HV and LV line resulting in a HV injection. A tree branch fell across the HV & LV overhead reticulation next to house no. 1A CLIFFORD GROVE, TECOMA. The condition described above caused current to flow across the tree branch, causing a phase to phase high impedance fault (the tree fell across all overhead HV lines and bridged across to the LV). This condition was sufficient enough to blow the LV protection at the pole mounted substation. BGE23 feeder CB operated. Tree branches were outside the vegetation clearance space. The tree was not classed as a hazardous tree. LBRA location. | Conductor (bare) | 0 | 0 | 0 |  | bge23 | Vegetation: Trees Incident | HV injection | 26/12/2016 20:45 |  |  | 4376 | Residential |  | 20170103SPN_02 | Infrastructure (network-based) | -37.9081 | 145.3412 | 1 | AusNet Services Distribution | Report | 5502 | 0.040751 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 5 LEURA STREET, DONCASTER EAST VIC 3109 |  |  | Lightning |  |  |  |  | 1 | Customers supplied from the west circuit of "Leura-Blackburn" substation advised a loss of their electricity supply. Later this day, customers reported appliance damage following the fault with one caller advising there are burn marks around the smoke alarm following the storm. A thunderstorm struck Melbourne at approximately 3.15PM on 29/12/2016 and customers who reside in Leura Street, Doncaster East advised they lost their electricity supply after lightning struck a pole outside number 5. Supply was restored after the blue phase 200amp LV fuse was replaced on the west circuit of "Leura-Blackburn" substation. The faults crew also replaced the other two LV HRC fuses on the pole as they appeared to be deteriorated. Following the restoration of supply, customers reported they had damaged appliances. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the blue phase LV conductor at "Leura-Blackburn" substation. The LEI confirmed that a high voltage injection occurred (BWD 1609) affecting 5 customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | DC 10 | Lightning struck LV conductors in Leura Street, Doncaster East. | HV injection;Loss of supply | 29/12/2016 17:10 |  |  | 4373 | Residential |  | 20170103UTD_03 | Infrastructure (network-based) | -37.7864 | 145.1614 | 1 | United Energy Distribution | Report | 5496 | 0.029646 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Lightning
Site made safe and fault crew repaired and re-hung the conductor | 45 OGILVIE STREET, ESSENDON VIC 3040 |  | Unknown external/community factor |  |  | Unknown technical factor |  |  | 1 | White phase lv open wire conductor down o/s 45 Ogilvie Street Essendon. No apparent cause but excavator sighted near the vicinity | Conductor (bare) | 0 | 2 | 0 |  | ES-21 | No identified cause but an excavator was sighted in the vicinity | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42826.4194 |  |  | 4383 | Residential |  | 20170104JEM_01 | Infrastructure (network-based) | -37.7502 | 144.8923 | 1 | Jemena | Report | 6567 | 0.030509 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Vehicle
On arrival crew check conductor for damage (none detected) | HENTY HIGHWAY, KELLALAC VIC 3393 | 32106745 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customer reports of â€œno supplyâ€ were received beyond the incident location. On arrival the crew found that a farmer driving a tractor and towing a grain chaser bin with an auger which was not stowed had contacted an overhead high voltage line. There was a ground fire in private property covering an area of approximately 150 hectares. There is a burn mark on the auger and no other apparent damage to the grain chaser bin. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | HSM005 | Grain auger struck conductor | Grassfire | 42856.5549 | 1 | Large: more than 10 ha | 5385 | Agricultural |  | 20170106PWA_02 | Infrastructure (network-based) | -36.3917 | 142.3916 | 1 | Powercor | Report | 6535 | 0.036744 | 22kV AC | Horsham Aerodrome | 3393 | Kellalac | Vehicle
On arrival crew carried out repairs | 206 COBURNS ROAD, MELTON VIC 3337 | 30103772 |  |  |  | Overheated connection |  |  | 1 | Vicfire reported a fire at the incident location. On arrival the crew found that a LV bridge connection had overheated causing hot debris to fall to the ground resulting in a ground fire on the nature strip (1 sq mtr). The fire self extinguished. There were no reported injuries. | Dropper/bridge | 2 | 2 | 2 |  | MLN014 | Overheated connection | Grassfire | 42917.8104 | 1 | Localised: less than 10 sq.m | 5395 | Roadway |  | 20170109PWA_02 | Infrastructure (network-based) | -37.6747 | 144.5702 | 1 | Powercor | Report | 6547 | 0.023752 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
CEOT dispatched a fault crew to isolate, make safe, investigate and repair. CEOT also advised the local DAO to investigate and report. Repairs to the LV ABC connections were undertaken by lines personnel and supply was restored. The IPC connector caps appeared to have sheared correctly and a relatively high temperature day of approximately 35 degrees C with high load demand from the 300kVA transformer may have contributed to connector failure. Action raise to check transformer loading and circuit balance. | 3 OLIVER STREET, RINGWOOD VIC 3134 | 1212124 |  |  |  | Electrical overload |  |  | 1 | IMS 225987. Vic Fire report of a sparking pole outside 3 Oliver Street, Ringwood and customer at 1 Oliver St has no power. There was a small fire in the vicinity of the substation pole base. It is suspected a 4x150 sq.mm LV ABC IPC Connector on 4x150 sq.mm LV ABC mains conductor failed with hot molten plastic from the IPC connector igniting an approximately 1m x 1m small grass fire on the nature strip at the base of pole #1212124. Believe the failure may have been as a result of electrical load, not poor connections as there is a 300kVA transformer feeding 150 sq.mm LV ABC. | Connector/termination | 0 | 0 | 0 |  | rwt14 | LV ABC IPC connector on 4x150 sq.mm LV ABC mains conductor failed. | Grassfire | 42948.2882 | 1 | Localised: less than 10 sq.m | 5396 | Residential |  | 20170109SPN_03 | Infrastructure (network-based) | -37.8097 | 145.2385 | 1 | AusNet Services Distribution | Report | 6559 | 0.020718 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Ringwood | Conductor
A faults truck promptly attended and found the load side terminal burnt at the single phase 501 AMI meter. The cause was a probable loose connection. The wiring was re-terminated with the consumers load side cable re-made and the damaged meter replaced. Supply was restored with the customers meter board suffering small scorching marks but was safe. | 19 HOLDEN ROAD, RYE VIC 3941 | 8831884 |  |  |  | Overheated connection |  |  | 2 | Customer is reporting the meter is burning and has gone all black with a plastic smell now evident. The customer hasn't lost power but has now turned the main switch off. The occupier has contacted the United Energy faults and emergencies call centre advising that her smart meter is burning and is very warm to touch. | Connection to meter | 0 | 0 | 0 |  |  | A loose connection to the meter was the most probable cause. | Singeing or local charring/blackening only | 42856.5312 |  |  | 5402 | Residential |  | 20170109UTD_05 | Infrastructure (network-based) | -38.3765 | 144.7885 | 1 | United Energy Distribution | Report | 6562 | 0.021767 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | AF Other
On arrival crew investigated and repaired faulted cable. | 1 ELIZABETH STREET, MELBOURNE VIC 3000 | 30201223 | Working too close to underground cables | [5 empty] | 1 | A fault occurred on the LQ28 11kV feeder on the 9.12.2016 at 17:20 hours at the incident location. On arrival the fault crew found that a high voltage underground cable had faulted at the incident location. It was later determined by a CitiPower underground cable faults crew that the fault had been caused by a third party excavating in the vicinity of the cable. Marks on the cable determined that the fault was caused by a crow bar contacting and penetrating the steel wire armor on the cable, this eventually caused the cable to fault. Protection operated correctly to remove the faulted equipment form the Network. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | LQ028 | It appears terra cotta conduit was smashed (possibly mistaken for sewerage or other service) and possibly crow bar accidently damaged cable armor protection. | Loss of supply;No Go Zone (contact);Damage to network assets | 42625.7222 |  |  | 5408 | Public space |  | 20170110PWA_02 | Infrastructure (network-based) | -37.818 | 144.9646 | 1 | CitiPower | Report | 6571 | 0.037508 | 11kV AC | Essendon Airport | 3000 | Melbourne | Dug up
Service Crew discovered the loose split bolt connection of the ABC service neutral conductor to the reticulation neutral at the Powercor pole end. Crew remade the connection and performed NST at the house POA with a pass result recorded. | 31 ELIZABETH STREET, GEELONG WEST VIC 3218 | 32081808 |  |  |  | Unknown technical factor |  | Phase to earth | 2 | Lucy was standing bare foot on the polished concrete floor of the kitchen/dining room, when she received a minor shock through her right hand, when she touched the earthed metal of an electric kettle. | Conductor (ABC) | 2 | 2 | 2 |  | GLO22 | Loose split bolt connection of the ABC service neutral conductor | Minor shock | 42562.75 |  |  | 5410 | Residential |  | 20170110PWA_04 | Infrastructure (network-based) | -38.1396 | 144.3402 | 1 | Powercor | Report | 12423 | 0.026152 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Connection
On arrival crew isolated supply and carried out repairs. | 1 ANDERSON STREET, TORQUAY VIC 3228 | 30292613 |  |  |  | Overheated connection |  |  | 2 | A customer reported a meter board fire at the incident location. Upon arrival, the crew found that an overheated meter board fuse caught fire and melted. There were no injuries or ground fire. | Meter board (including fuses) | 2 | 2 | 2 |  | WPD024 | Overheated connection on meter board fuse | Meter board | 29/12/2016 13:57 | 1 | Negligible: no ground fire | 5415 | Residential |  | 20170111PWA_04 | Infrastructure (network-based) | -38.3341 | 144.3244 | 1 | Powercor | Report | 6580 | 0.034925 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Fuse
CEOT dispatched a fault crew to isolate, make safe, investigate and carry out necessary repairs. CEOT also advised the local DAO to investigate and report. Crew checked to ascertain if there was any damage to network assets and none was found. | 121 STEPHENSON STREET, SALE VIC 3850 | 2503205 |  | Bird |  |  |  | Phase to earth |  | IMS 226009. CEOT received an incident from the Fire Brigade stating that an eagle had hit overhead conductors and there was a grass fire in the vicinity. A fire had occurred in the vicinity of AusNet Services' pole #573 BIDPO: 2503205. The fire was extinguished by the CFA. The fire was approximately 4000 sq. metres in size. There was no apparent damage to any network assets and there was no damage to private property other than burnt grass. A burnt large eagle was found at the base of the 66kV/22kV concrete pole. Electrical protection operated: At 14:15:49 the MWTS-SLE Line Tripped. At MWTS the Y Prot operated for a zone 1 White Phase to Neutral fault. At SLE the X Prot operated for a three phase fault. In addition the SLE Line protection at MFA also detected the fault. The line reclosed at MWTS after 3 seconds and at SLE after 15 seconds (standard reclose times for subtransmission lines). | Conductor (bare) | 0 | 0 | 0 |  | MWTS-SLE 66kV line | Bird Incident | Grassfire | 43009.6389 | 1 | Medium: 1000 sq.m - 10 ha | 5413 | Agricultural |  | 20170111SPN_01 | Infrastructure (network-based) | -38.123 | 147.0796 | 1 | AusNet Services Distribution | Report | 7924 | 0.038948 | 66kV AC | Bairnsdale Airport | 3850 | Sale | Animal
On arrival crew isolated supply and carried out repairs | 26 PARWAN ROAD, MADDINGLEY VIC 3340 | 33075192 |  |  |  | Unknown technical factor |  |  | 2 | A passer-by named John Miller reported that a street light lantern (150W HPS on an outreach bracket) at pole LIS-105857 (12.5m conc pole) had caught fire resulting in the lantern cover melting. There was no ground fire, injuries or property damage. | Public lighting | 2 | 2 | 2 |  | BMH004 | Due to damage unable to determine cause | Pole-top fire | 42826.9069 | 1 | Negligible: no ground fire | 5423 | Roadway |  | 20170112PWA_06 | Infrastructure (network-based) | -37.6882 | 144.4362 | 1 | Powercor | Report | 6602 | 0.035098 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | AF Other
Site was made safe. Palm tree branches cut clear of HV overhead conductor. | 170 STEPHEN STREET, YARRAVILLE VIC 3013 | Pole no. A051445 |  | Within clearances |  |  |  | Three phase | 2 | Customer owned private palm tree was rubbing on the HV conductor, due to the constant friction it caused the palm tree branches to heat up and catch alight. | Conductor (bare) | 0 | 0 | 0 |  | YVE24 | Vegetation: Trees Incident | Other vegetation | 43009.5917 | 1 | Negligible: no ground fire | 5436 | Residential |  | 20170116JEM_03 | Infrastructure (network-based) | -37.8197 | 144.8937 | 1 | Jemena | Report | 12382 | 0.017626 | 22kV AC | Essendon Airport | 3013 | Yarraville | Trees
ON arrival crew checked structure for damage and repairs arranged. | 5 SUSAN STREET, IRONBARK VIC 3550 | 33021007 | Vandalism | [5 empty] | 1 | VICFIRE reported a grassfire at the incident location. Upon arrival the crew noted the CFA leaving the scene after extinguishing a small grass fire which burnt an area of approximately 150mÂ². The area was both private property and road reserve. Police were also in attendance. It is suspected object being thrown over 22kV overhead conductors at the incident location was the cause of the fire. There were no reported injuries or 3rd party damage. | Conductor (bare);Dropper/bridge | 2 | 2 | 2 |  | BET002 | Suspect vandalism | Grassfire | 43009.7812 | 1 | Small: 10 - 1000 sq.m | 5430 | Public space |  | 20170116PWA_01 | Infrastructure (network-based) | -36.7554 | 144.2608 | 1 | Powercor | Report | 6616 | 0.035021 | 22kV AC | Bendigo Airport | 3550 | Ironbark | Other
Site attended by Work Practises and ESV deemed safe. Incident reported by Operator at 12:45 hrs on 16/01/2017 â€¢ Incident site 316 Pascoe Vale Rd, corner of Cameron St Essendon, â€¢ Construction Company : V M Romano 03 9254 6600 â€¢ Construction Site Person-in-Charge, Mike McCrae mobile: 0404 065 712 â€¢ Site Project Manager, Rob Fontanini mobile: 0425 845 837 â€¢ Work Practices John Vasilopoulos arrived onsite at 14:30 hrs â€¢ John advised Mike McCrae that no persons are permitted to climb the structure or roof, under any circumstances. Meeting to be arranged asap to remove the structure â€¢ ESV notified at 19:45 hrs on 16/01/2017 ESV reference number: 6665708 â€¢ | 316 PASCOE VALE ROAD, ESSENDON VIC 3040 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Site sheds at a high rise development construction site have been attached to a single pole substation at Cameron-Little. | Pole (concrete) | 0 | 0 | 0 |  | NS08 | Site sheds at a high rise development construction site have been attached to a single pole substation at Cameron-Little. | No Go Zone (no contact) | 16/01/2017 11:42 |  |  | 5451 | Construction |  | 20170117JEM_04 | Infrastructure (network-based) | -37.7462 | 144.9261 | 1 | Jemena | Report | 12383 | 0.040144 | 11kV AC | Essendon Airport | 3040 | Essendon | Other
CEOT dispatched a fault crew to investigate. Crew arrived and isolated the streetlight, the neutral had burned off, checked all connections on the pole and investigated for further issues. Also checked for any possible high voltage injection into the low voltage - no issues were found. | 62 GAVAN STREET, KILMORE EAST VIC 3764 |  |  | Bird |  |  |  |  | 1 | IMS 217071. CEOT received a report for a pole fire and grass fire from Vic Fire Ballarat. The attending AusNet Services' fault crew found a spot mark on the overhead centre phase 66kV conductor. There was a fire at the base of the pole of approximate size 3m x 3m. The crew found bird feathers in the vicinity but could not find a burnt / dead bird. The pole is concrete. Feeder protection operated and reclosed. Appears to have been a flashover from the centre phase 66kV conductor to the bottom of the 66kV insulator to the concrete pole. There was evidence of feathers (possible a white cockatoo) around the base of the pole but nothing else found. The flashover caused a trip on the Kilmore to Seymour 66kV line. The flashover also tracked through the streetlight as the straps around the pole were holding the steel bracket and this was earthed inside the light fitting. The streetlight was damaged and needs to be replaced, no other damage sustained on the pole. A small fire at the base of the pole resulted approximately 3m x 3m in size. | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 17/01/2017 8:05 | 1 | Localised: less than 10 sq.m | 5448 | Residential |  | 20170117SPN_02 | Infrastructure (network-based) | -37.2956 | 144.9823 | 1 | AusNet Services Distribution | Report | 6641 | 0.0042488 | 66kV AC | Wallan (Kilmore Gap) | 3764 | Kilmore East | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure in Corr Street was repaired under Access Authority conditions. The HV bridge that failed, one pole north of the CHP to CH0044 "Kingway-ACI" substation was repaired using glove and barrier techniques. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers. | CORR STREET, MOORABBIN VIC 3189 | 1816503 |  |  |  | Electrical breakdown |  |  | 1 | At 0058hrs on 15/01/2017, 22kV feeder HT 09 circuit breaker reclosed to lockout affecting 219 customers. 22kV feeder HT 09 circuit breaker opened auto and failed. At the same time, the No. 2 and 3 22kV bus tie circuit breaker opened. The feeder was patrolled and the crew found a HV ampact and helical termination had burnt off in Corr Street at pole No. LIS 1816503, one pole west of Alex Avenue, Moorabbin. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Alex-Joel" substation. The LEI confirmed a high voltage injection occurred (CLA 1701) affecting light industrial customers that sustained minor damage to appliances and equipment. In addition, a HV bridge failed due to probable fault current at pole No. LIS 1816744, one pole north of the CHP to CH0044 "Kingway-ACI" substation that caused dim lights. | Conductor (bare);Aluminium;Dropper/bridge | 0 | 0 | 0 |  | HT 09 | Ampact connection failure | HV injection;Loss of supply | 15/01/2017 0:58 |  |  | 5441 | Industrial |  | 20170117UTD_01 | Infrastructure (network-based) | -37.941 | 145.0702 | 1 | United Energy Distribution | Report | 6631 | 0.024149 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Connection
On arrival crew carried out repairs | 12 CAWOOD STREET, APOLLO BAY VIC 3233 | 30054351 | Vehicle | [5 empty] | 2 | Vic Fire reported that a truck had contacted and bought down powerlines which were laying on the ground at the incident location. On arrival the crew found that a Low Voltage (LV) service had been hit by a truck, resulting in it breaking and coming to ground. There was no fire, reported injuries or other third party property damage. Police were on site when the crew attended but had no details of the truck. | Service conductor | 2 | 2 | 2 |  | CLC007 | Unknown vehicle struck service line | Loss of supply | 42948.7604 |  |  | 5464 | Roadway |  | 20170118PWA_02 | Infrastructure (network-based) | -38.7498 | 143.668 | 1 | Powercor | Report | 6663 | 0.020553 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Vehicle
On arrival crew carried out repairs | 1229 CALDER HIGHWAY, MARONG VIC 3515 | 32031800 | Working too close to underground cables | [5 empty] | 2 | A contractor rang to advise that they had dug up and broken an earth wire at a substation pole. A crew attended and found that the HV earth at sub pole Marong P109A had been dug up and broken. No shocks, injuries, third party damage or ground fire starts. | Earth/earthing | 2 | 2 | 2 |  | BET001 | Contractor excavating near earth system | Damage to network assets | 43040.4458 |  |  | 5468 | Public space |  | 20170119PWA_01 | Infrastructure (network-based) | -36.7381 | 144.1544 | 1 | Powercor | Report | 6668 | 0.0087523 | Earthing cable | Bendigo Airport | 3515 | Marong | Dug up
On arrival the fault crew found large tree branches resting across the power-lines at the incident location. A LEI was dispatched, high voltage injection to customers on the east circuit supplied from the Chatfield-Parkside substation has been confirmed. Forty seven customers supplied from this circuit | 13 CHATFIELD AVENUE, DEEPDENE VIC 3103 | 30172437 |  | Fallen |  |  |  |  | 1 | At the incident location two large tree branches have broken from an oak tree and fallen across power-lines causing damage to high voltage conductors. There was a high voltage injection to customers on the east circuit supplied from the Chatfield-Parkside substation. The L10 11kV feeder CB operated correctly to clear this fault. The broken White phase high voltage conductor was found to be resting on the Blue phase low voltage conductor and the neutral. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | L010 | Vegetation: Trees Incident | HV injection;Loss of supply | 20/01/2017 5:32 |  |  | 5478 | Public space |  | 20170123PWA_01 | Infrastructure (network-based) | -37.8142 | 145.0707 | 1 | CitiPower | Report | 6680 | 0.015274 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3103 | Deepdene | Trees
On arrival crew carried out repairs | 880 INGLISTON ROAD, INGLISTON VIC 3342 | 30116684 | Copper theft | [5 empty] | 2 | CFA reported a pole fire at the above location. A crew attended and found both the HV earths on the wooden SWER S/S pole had been removed. The resulting current leakage cause a pole fire. The embers from the pole fire started a grass fire at the base of the pole. There were no reported shocks, injuries or third party damage. | Pole (wood) | 2 | 2 | 2 |  | BMH003 | Theft of earthing | Pole-top fire;Grassfire | 23/01/2017 13:25 | 1 | Medium: 1000 sq.m - 10 ha | 5497 | Roadway |  | 20170125PWA_02 | Infrastructure (network-based) | -37.6514 | 144.3108 | 1 | Powercor | Report | 6706 | 0.025264 | 12.7kV AC (SWER) | Avalon Airport | 3342 | Ingliston | Other
On arrival crew carried out repairs | 989 SPRINGBANK ROAD, SPRINGBANK VIC 3352 | 33003276 | Copper theft | [5 empty] | 2 | An employee reported copper earth missing from Toohey Pole 12. The crew attended and found that the LV earth at the incident location has been stolen. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | cable theft | Damage to network assets | 22/01/2017 20:08 |  |  | 5499 | Roadway |  | 20170125PWA_04 | Infrastructure (network-based) | -37.5351 | 144.0823 | 1 | Powercor | Report | 6708 | 0.020264 | Earthing cable | Ballarat Aerodrome | 3352 | Springbank | Other
Crew attended, made safe and repaired steel conductor | 347 LOWER PLAINS ROAD, LETHBRIDGE VIC 3332 | 30249584 |  | Bird |  |  |  |  | 1 | Powercor received of a wire down and possible ground fire. On arrival the crew found both phases of the HV overhead line had broken and fallen to ground. A grass fire of some 150 x 300m occurred on roadside and private farm land. No fencing or other 3rd party property damage was reported damaged. | Conductor (bare) | 0 | 0 | 0 |  | GL015 | Bird Incident | Grassfire | 25/01/2017 18:44 | 1 | Medium: 1000 sq.m - 10 ha | 5508 | Agricultural |  | 20170127PWA_01 | Infrastructure (network-based) | -37.9409 | 144.0958 | 1 | Powercor | Report | 6719 | 0.036807 | 22kV AC | Avalon Airport | 3332 | Lethbridge | Animal
Site made safe. Sub transmission conductor and HV overhead conductor isolated. Pole replaced by Jemena work party under access permit. | 151-209 CAMP ROAD, BROADMEADOWS VIC 3047 | Pole no. A141577 | Vehicle | [5 empty] | 1 | Car hit a 66/22 KV pole, sub transmission conductor came off and contacted the pole and caused a pole top fire (due to tracking). There was no ground fire. No photo is available for this fire start incident. The delay in submitting this incident report is a result of recent work to populate the F-Factor Regulatory Information Notice (RIN) for the AER, during which we have identified several additional instances from our historical records which â€“ after further investigation â€“ now â€œmake the cutâ€ for fire start reporting. | Pole top | 0 | 0 | 0 |  | BMS23 | The pole top fire was as a result of vehicle hitting the pole and caused the high voltage conductor to contact the pole top asset. | Pole-top fire | 31/01/2016 15:39 | 1 | Negligible: no ground fire | 5518 | Roadway |  | 20170130JEM_02 | Infrastructure (network-based) | -37.6881 | 144.942 | 1 | Jemena | Report | 8422 | 0.024711 | 22kV AC;66kV AC | Essendon Airport | 3047 | Broadmeadows | Vehicle
On arrival crew carried out repairs | 104 FLAGSTAFF RIDGE ROAD, LINTON VIC 3360 | 33005605 |  |  |  | Fuse failed to eject |  |  | 0 | VicFire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve and private property. There was also minor damage caused to fencing and a private motor car parked on the property. There were no injuries. | EDO fuse | 2 | 2 | 2 |  | BAS021 | EDO hangup | Grassfire | 28/01/2017 14:35 | 1 | Small: 10 - 1000 sq.m | 5520 | Roadway |  | 20170130PWA_05 | Infrastructure (network-based) | -37.6746 | 143.5255 | 1 | Powercor | Report | 6735 | 0.025544 | 22kV AC | Ballarat Aerodrome | 3360 | Linton | Fuse
On arrival crew carried out repairs | 24 ANDERSON ROAD, HAWTHORN EAST VIC 3123 | 30199561 |  | Alive;Council |  |  |  |  | 1 | It is believed that the branch which came down outside 18 Anderson Street shorted across the 11kV high voltage conductors and the low voltage circuit below. However visual evidence of this could not found. Protection operated correctly to remove the fault from the distribution Network. Following customer calls an L.E.I was engaged and inspected a number of homes on the low voltage circuit. High voltage injection has been confirmed damage has been found at 6 premises with other premises still to be accessed. There are 31 customers on this low voltage circuit. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | K011 | Vegetation: Trees Incident | HV injection;Loss of supply | 30/01/2017 9:26 |  |  | 5521 | Roadway |  | 20170131PWA_01 | Infrastructure (network-based) | -37.8412 | 145.0488 | 1 | CitiPower | Report | 6736 | 0.013295 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3123 | Hawthorn East | Trees
On arrival crew carried out repairs | COBDEN STREET, QUAMBATOOK VIC 3540 | 30018118 | Vehicle | [5 empty] | 2 | Customer reported wire in ground at the incident location. On arrival the crew found a service cable had broken and with laying on ground. No protection operated. There were no reported shocks, injuries, fire start or third party damage. | Service conductor | 2 | 2 | 2 |  | CTN003 | Unknown truck struck service ( vehicle failed to stop) | Loss of supply;Damage to network assets | 23/01/2017 9:55 |  |  | 5524 | Roadway |  | 20170131PWA_02 | Infrastructure (network-based) | -35.8503 | 143.5195 | 1 | Powercor | Report | 6741 | 0.032799 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3540 | Quambatook | Vehicle
On arrival crew carried out repairs | 37 MALINGS ROAD, PORTLAND WEST VIC 3305 | 30240396 |  |  |  | Corrosion;Candled fuse |  |  | 0 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries. | EDO fuse | 2 | 2 | 2 |  | PLD006 | EDO Fuse unit did not drop out due to corrosion | Pole-top fire | 21/01/2017 2:35 | 1 | Negligible: no ground fire | 5527 | Agricultural |  | 20170131PWA_04 | Infrastructure (network-based) | -38.3724 | 141.5859 | 1 | Powercor | Report | 12432 | 0.037359 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland West | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 62 WARRIGAL ROAD, PARKDALE VIC 3195 | 1809060 | Recreation - Helium (party) balloons | [5 empty] | 1 | At 1329hrs on 18/12/2016, 11kV feeder M 35 circuit breaker reclosed to lockout affecting 1027 customers. A customer reported that helium balloons made contact with the 11kV overhead conductors outside 62 Warrigal Road, Mentone near pole No. LIS 1809060 that caused an explosion and a HV ampact connection to fail near the helical termination. This connection failure caused the conductor to fall to the ground and a small grass fire to start estimated to be approximately 10cm in length where the conductor contacted the ground. No HVI or major damaged was sustained. | Conductor (bare) | 0 | 0 | 0 |  | M 35 | Dur to probable fault current, a HV ampact connection failed near the helical termination. | Loss of supply;Grassfire | 18/12/2016 13:29 | 1 | Localised: less than 10 sq.m | 4328 | Roadway |  | 20161222UTD_02 | Infrastructure (network-based) | -37.9872 | 145.0706 | 1 | United Energy Distribution | Report | 6608 | 0.0084074 | 11kV AC | Moorabbin Airport | 3195 | Parkdale | Other
An investigation of the metering data confirmed that meter 00773383 was tampered with on 17/10/2016 with meter cover and ETBC alarm time stamps. | 81 MACKIE ROAD, BENTLEIGH EAST VIC 3165 |  | Theft;Unauthorised work;Unauthorised access | [5 empty] | 2 | The United Energy AMI Strategy Engineer requested the three phase meter at 81 Mackie Road be inspected as its suspected the occupier has been tampering with the meter and breaking meter terminal screws. A technician went to the site and discovered there was only 1 seal on the terminal cover that wasn't crimped with approved tamper tool. The seal on the config button was sealed with the Formway technicians seal ID. When the technician checked the meter potential screws, phase 1 was loose and when the technician tightened the screw, the screw head simply sheared and fell out suggesting it had been over tightened to the point of breaking the screw. The same applied for phase 3. The technician checked with the Formway technician who advised that he hadn't over tightened the screws and left the terminal cover with two seals crimped with an approved tool. The meter remains with two broken potential screws with phase 1 and 3 indicators flashing and needs to be replaced. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised meter damage and interference to the three phase AMI meter. | Damage to network assets | 16/12/2016 9:30 |  |  | 4332 | Commercial |  | 20161222UTD_04 | Infrastructure (network-based) | -37.9153 | 145.0745 | 2 | United Energy Distribution | Report | 5452 | 0.028954 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Other
On arrival crew commenced repairs. | 724 BLAKEVILLE ROAD, COLBROOK VIC 3342 | 32166522 |  |  |  | Overheated connection |  |  | 2 | CFA reported a pole fire at the incident location. On arrival the crew found that a pole fire had started near to the ground level and spread upwards on the pole. There was no ground fire, no injuries or third party property damage | Pole (wood);Earth/earthing | 2 | 2 | 2 |  | BMH003 | suspected damage to earthing at unknown time. | Pole-top fire | 18/12/2016 13:30 | 1 | Negligible: no ground fire | 4334 | Agricultural |  | 20161223PWA_02 | Infrastructure (network-based) | -37.5196 | 144.2185 | 1 | Powercor | Report | 5455 | 0.010374 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3342 | Colbrook | Pole
On arrival crew arranged for repairs | 20 MORTLAKE ROAD, WARRNAMBOOL VIC 3280 | 33099041 |  |  |  | Corrosion |  |  | 2 | Vicfire reported a streetlight pole on fire at the incident location. On arrival the crew found that a streetlight lantern mounted on a steel pole and bracket, had caught fire. There was no ground fire, no reported third party damage or any injuries. | Public lighting | 2 | 2 | 2 |  | WBL002 | due to damage unable to determine | Pole-top fire | 22/12/2016 9:33 | 1 | Negligible: no ground fire | 4336 | Roadway |  | 20161223PWA_04 | Infrastructure (network-based) | -38.3728 | 142.4931 | 1 | Powercor | Report | 5457 | 0.014649 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | AF Other
Emergency high voltage switching was requested by the crew due to close proximity of the HV conductor to the LV blue phase conductor with ACR CH7842 located in New Street opened affecting 960 customers. Further high voltage switching was completed to minimise the number of customers affected and the HV intermediate crossarm replaced under Access Authority conditions prior to the supply being restored. | 16 MANOR STREET, BRIGHTON VIC 3186 | 1805954 |  | Cold |  | Electrical breakdown;Leakage |  |  | 2 | MFB on site and advises of a pole fire. During cool morning conditions, a pole fire occurred at the HV/LV intermediate pole outside 16 Manor Street, Brighton. The 11kV brown fog type insulator had been tracking and burnt through the timber crossarm and caused the HV conductor with insulator still attached to fall and rest on the LV crossarm in close proximity to the LV blue phase conductor. No HVI occurred but the HV crossarm on pole No. LIS 1805954 required replacement. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MR 32 | The 11kV brown fog type insulator had been tracking and burnt through the intermediate timber crossarm. | Pole-top fire | 20/12/2016 8:42 | 1 | Negligible: no ground fire | 4342 | Residential |  | 20161228UTD_02 | Infrastructure (network-based) | -37.9167 | 144.9894 | 1 | United Energy Distribution | Report | 5463 | 0.0029387 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions prior to the supply being restored. | 40-44 BENNET STREET, DANDENONG VIC 3175 | 634920 |  | Lightning;Precipitation;Industrial or urban pollution |  | Electrical breakdown;Leakage |  |  | 1 | 22kV feeder KBH 31 circuit breaker successfully reclosed on two separate occasions. The United Energy Control Centre elected to suppress the reclose function to prevent any further operations. The 22kV feeder was patrolled and a pole fire at a ground type substation pole (LIS No. 0634920) named "Bennet N40 - Verey" substation was found to be the cause of the two previous successful recloses. The HV termination crossarm was burnt near the kingbolt and the centre phase termination severely enough to warrant the replacement of the substation pole. The faults crew suspected that a high voltage injection may have occurred and a LEI was called to investigate. The LEI tested electrical installations in the immediate area and confirmed that a high voltage injection did not occur. The suspected cause was a build up of industrial contaminants as the ground type substation pole is located in an industrial area. There was also light rain and lightning in the area at the time of the fault. | Conductor (bare);Pole (wood);Crossarm (wood);Outdoor | 0 | 0 | 0 |  | KBH 31 | The suspected cause was a build up of industrial contaminants as the ground type substation pole is located in an industrial area. There was also light rain and lightning in the area at the time of the fault. | Pole-top fire | 20/12/2016 9:38 | 1 | Negligible: no ground fire | 4343 | Industrial |  | 20161228UTD_03 | Infrastructure (network-based) | -37.9879 | 145.1991 | 1 | United Energy Distribution | Report | 5465 | 0.027833 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Crossarm
On arrival crew carried out repairs | 155 STRATHALLAN ROAD, STRATHALLAN VIC 3622 | 31026711 |  | Lightning |  |  |  |  | 1 | VicFire reported a pole fire at the incident location. On arrival the crew found that a transformer has failed rupturing the tank and the ejected oil had ignited, resulting in fire damage to the pole and commencing a ground fire. It is believed that the transformer had suffered damage due to lightning earlier that morning when the spur was affected by an lightning related outage that the crew attended and replaced a section fuse at P1 Quinn spur. A ground fire of approximately 50m x 60m resulted, some fencing was slightly burnt as the fire passed through it. There were no reported injuries. | Pole mounted;Transformer | 1 | 1 | 0 |  | ECA012 | Lightning strike | Grassfire | 24/12/2016 17:26 | 1 | Medium: 1000 sq.m - 10 ha | 4347 | Roadway |  | 20161229PWA_02 | Infrastructure (network-based) | -36.2564 | 144.7282 | 1 | Powercor | Report | 5470 | 0.02541 | 22kV AC | Bendigo Airport | 3622 | Strathallan | Lightning
On arrival crew carried out repairs | 671 NHILL-HARROW ROAD, NHILL VIC 3418 | 32122737 |  |  |  | Leakage |  |  | 2 | VicFire reported a pole fire at the incident location. On arrival the crew found that a three phase 22kV wooden cross arm had burnt through at the king bolt position. There was no ground fire or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | NHL015 | Excessive leakage current | Pole-top fire | 28/12/2016 6:42 | 1 | Negligible: no ground fire | 4353 | Agricultural |  | 20161229PWA_07 | Infrastructure (network-based) | -36.402 | 141.6429 | 1 | Powercor | Report | 5476 | 0.0043831 | 22kV AC | Horsham Aerodrome | 3418 | Nhill | Crossarm
On arrival crew removed branch and restored supply | 1117 EYRE STREET, NEWINGTON VIC 3350 | 30014532 |  | Blown branch/vegetation |  |  |  |  | 1 | VicFire reported a pole fire at the incident location. On arrival the crew found that a tree branch had broken in the windy weather conditions and had fallen across high voltage and low voltage conductors which resulted in the branch burning through. There was no ground fire. There were no injuries. | Conductor (bare) | 2 | 2 | 2 |  | BAS014 | Vegetation: Trees Incident | Loss of supply;Other vegetation | 28/12/2016 13:15 | 1 | Negligible: no ground fire | 4355 | Roadway |  | 20161229PWA_09 | Infrastructure (network-based) | -37.5639 | 143.8361 | 1 | Powercor | Report | 12419 | 0.037058 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Newington | Trees
On arrival crew commenced repairs | 125 GORDON STREET, BALWYN VIC 3103 | 30175325 |  |  |  | Overheated connection |  |  | 2 | A customer, Ms Anisca Vancea, reported that an explosion and a fire occurred outside 125 Gordon St Balwyn . On arrival the crew found the bimetal crimp on the blue phase of the LV conductor, overheated and as a result melted the aluminium connecting cable. This caused melted aluminium to drop down to the below grass creating a ground fire on the road reserve. There were no reported injuries or 3rd party damage.. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | L004 | failure of bi-metal crimp | Grassfire | 24/12/2016 16:37 | 1 | Localised: less than 10 sq.m | 4356 | Public space |  | 20161229PWA_10 | Infrastructure (network-based) | -37.8082 | 145.0761 | 1 | CitiPower | Report | 5479 | 0.00020833 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Connection
Isolated section for pole replacement. Supply was restored upon completion of rectification works. | 54 LARA WAY, CAMPBELLFIELD VIC 3061 |  | Vandalism |  |  |  |  | Phase to phase | 1 | Vandals threw jumper cables over high voltage overhead conductor. The jumper contacted between high voltage overhead conductor and high voltage cross arm and caused a fire which was confined to the pole top. | Pole (wood) | 0 | 0 | 0 |  |  | The pole top fire was as a result of Jumper leads contacting the high voltage overhead conductors and high voltage cross arm, the cause was due to vandalism. | Pole-top fire;Loss of supply | 30/12/2016 9:03 | 1 | Negligible: no ground fire | 4361 | Residential |  | 20161230JEM_02 | Infrastructure (network-based) | -37.6624 | 144.9682 | 1 | Jemena | Report | 5484 | 0.01976 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Other
On arrival crew carried out repairs | 4 SIGNATURE BOULEVARD, POINT COOK VIC 3030 | 34030635 | Working too close to underground cables | [5 empty] | 2 | A customer reported UG cable dug up while they are re-landscaping the roundabout at the incident location. Upon arrival, the Powercor crew noticed that the UG pit lifted and minor damage to the connections. There were no injuries or fire. | Services pit | 2 | 2 | 2 |  | LV006 | landscaping activities | Damage to network assets | 42563.4507 |  |  | 4364 | Roadway |  | 20161230PWA_02 | Infrastructure (network-based) | -37.8909 | 144.7736 | 1 | Powercor | Report | 5487 | 0.0088681 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
The length of timber was removed from the fence. Disconnection and dropping of the service line to # 32 ( with customers consent) was arranged so the construction work (piling) could be completed. | 30 AUBURN GROVE, HAWTHORN EAST VIC 3123 | 30202254 | Working too close to overhead lines | [5 empty] | 2 | During a site visit a realigned Service Line crossing building site to #32 auburn grove was discovered. The realignment was to allow operate mobile plant / piling rig to operate. The service was realigned by attaching length of timber to a fence. There was no injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | CL037 | service line interfered with | No Go Zone (contact) | 42625.4792 |  |  | 4367 | Construction |  | 20161230PWA_04 | Infrastructure (network-based) | -37.8258 | 145.0479 | 1 | CitiPower | Report | 5490 | 0.029354 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Other
A LEI and faults truck attended and tested the installation and measured 10v at the neutral bar. A NST was completed that passed. The LEI suspected a possible reticulation problem and the faults crew commenced to check all neutral connections with no defective connections identified. The fault was referred to the United Energy engineering team to investigate the transformer and attached wiring and to install a recorder to determine what rectification work is required. Supply was left on and the customer advised of findings. Downer have taken the following actions so far: â€¢ 8 Moon St was on the red phase and is now on the white phase. Straight joints in the pit changed to Ã—4 4ports, nst passed. â€¢ installed D3 at tx and installed D2 at pole in 8 Moon St. â€¢ found a defected FOLCB @ 2-4 Station St (attached) and â€¢ replaced service mid span @ 6 Bird St. | 8 MOON STREET, MOUNT ELIZA VIC 3930 |  |  | Heat |  | Neutral fault;Out of balance load |  |  | 2 | Customer advised that he experienced a shock when he touches the spa and the rear garden tap. The occupier was receiving slight electric shocks when he touches the spa and rear garden tap and contacted the United Energy faults and emergencies call centre for assistance. He was standing on the wet paving in bare feet when the shock was received. | Yet to be determined | 0 | 0 | 0 |  |  | Downer are waiting for the data from the power quality analysers (meters) to analyse if the issue still exists. | Minor shock | 29/12/2016 12:30 |  |  | 4366 | Residential |  | 20161230UTD_02 | Infrastructure (network-based) | -38.2096 | 145.0974 | 1 | United Energy Distribution | Report | 12322 | 0.036265 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Conductor
On arrival the customers cables were disconnected form the service pit and the damaged pit connectors where cut away and replaced with new pit connectors. | 840 OLD CALDER HIGHWAY, KEILOR VIC 3036 | 30291144 | Working too close to underground cables | [5 empty] | 2 | Mostatha from Unique All Steel 0433022866 advised that they have hit an underground cable while digging (fencing company) , no supply at site. Upon arrival the crew had discovered that the fencing contractor, had drilled/augured through the customers mains cable, adjacent to the LV Service Pit just north inside the customers property, running from the service pit on the boundary between No. 840/842 Old Calder Highway to Customers Main Switch Board. The sheer force of the drill/auger had ripped through and pulled out a substantial length (approx. 1m) of customerâ€™s mains cable. Due to this force, there was also some minor damage to the PCA pit connectors within the service pit. No protection operated, there were no reported injuries or ground fire start. | Connector/termination;Customer installation | 2 | 2 | 2 |  | SA006 | fencing contractor hit service cable | Loss of supply;No Go Zone (contact) | 17/12/2016 12:10 |  |  | 4382 | Residential |  | 20170103PWA_05 | Infrastructure (network-based) | -37.7044 | 144.8138 | 1 | Powercor | Report | 5522 | 0.021023 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Dug up
CEOT dispatched a fault crew and a LEI to isolate, make safe and investigate. Faults crew attended site and removed affected mains for the pit. LEI checked damaged consumer's mains in affected pit and issued a defect notice (NCID) to repair or replace consumer's mains to no. 28 and 30. LEI checked for damage to other customerâ€™s properties, and it was made safe. | 27 RIORDAN CRESCENT, MERNDA VIC 3754 | 5721772 |  | Lightning |  |  |  | Phase to earth | 2 | IMS 225920. Lightning is believed to have struck a public light pole connected to a URD area. The lightning is believed to have travelled through the earth, back through the MEN system at the pole, through the consumer's neutral supplying the pole, back through to the POS in the pit supplying no. 28 and 30, through the neutral consumer's main system supplying both houses and down to ground on the customers' earthing systems. It also travelled to 3 other service pits and dissipated through the customers' installations at noâ€™s 21, 23, 26 and 27 in the same manner. A high voltage injection was confirmed. | Customer installation | 0 | 0 | 0 |  | drn012 | Lightning caused HVI damage to customer's appliances. | HV injection | 24/12/2016 8:50 |  |  | 4375 | Residential |  | 20170103SPN_01 | Infrastructure (network-based) | -37.5987 | 145.0859 | 1 | AusNet Services Distribution | Report | 5499 | 0.034288 | Low voltage AC (<1kV) | Essendon Airport | 3754 | Mernda | Lightning
The substation was isolated HV and LV and the substation secured. Repairs were completed and supply restored to all customers supplied from the "Community Centre - FTG" indoor substation with the exception of the vacant premise that was previously Lifestyle. The United Energy duty manager was advised of the break-in and the stolen consumers copper cables. | 900 FERNTREE GULLY ROAD, WHEELERS HILL VIC 3150 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Customers supplied from "Community Centre - FTG" indoor substation advised they have lost their electricity supply. Refer also to incident report 20161222UTD_03 for a similar event that occurred on 19/12/2016 at the vacant building. For a second time, copper thieves have broken into "Community Centre - FTG" indoor substation and removed the remaining customers copper consumers cables up to the switchboard. In addition, the Distributors LV bus copper cables along with the street circuit conductors were also removed. There was minor damage to the substation locking mechanism and a substantial amount of copper cables have been stolen. It appears no shocks were received by the unknown persons. | Equipment;Indoor;Connector/termination | 0 | 0 | 0 |  | MGE 23 | Theft of Distributors and consumers copper cables from an indoor substation by unknown persons. | Significant disruption to the community;No Go Zone (contact) | 31/12/2016 10:20 |  |  | 4374 | Commercial |  | 20170103UTD_04 | Infrastructure (network-based) | -37.9063 | 145.1886 | 1 | United Energy Distribution | Report | 5497 | 0.022535 | 22kV AC | Moorabbin Airport | 3150 | Wheelers Hill | Other
On arrival crew replaced the Fuse box | 6276 BENALLA-TOCUMWAL ROAD, COBRAM VIC 3644 | 33085558 |  |  |  | Overheated connection |  |  | 2 | The CFA reported a pole had caused a grass fire at the incident location. On arrival the crew found that at the incident location a pole box had faulted resulting in approximately 4 acres ( 1.6 ha) of grassland being burnt. No injury and or other third party damage was reported. | Connection box | 2 | 2 | 2 |  | CME015 | Overheated connection | Grassfire | 42856.5014 | 1 | Medium: 1000 sq.m - 10 ha | 4385 | Agricultural |  | 20170106PWA_01 | Infrastructure (network-based) | -35.9738 | 145.6223 | 1 | Powercor | Report | 5535 | 0.021133 | Low voltage AC (<1kV) | Shepparton Airport | 3644 | Cobram | Connection
CEOT dispatched a fault crew to attend the site to isolate, make safe, investigate and repair. The fault crew confirmed that this was the case that a road works crew had damaged an underground LV cable. The fault crew could not get details of the offending company or the people involved in this incident. The underground crew repaired the LV mains cable by installing 2 x LV straight underground joints. | 26 PRESERVE CIRCUIT, DOREEN VIC 3754 | 917803 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 225689. Under INCD-124806-r, a customer reported that whilst carrying out road widening works, the road workers had dug up a LV underground mains cable. Electrical protection operated - LV fuses at the substation were blown. | Cable | 0 | 0 | 0 |  | drn012 | 3rd party civil road contractors dug up AusNet Services' LV mains cable. | Loss of supply;No Go Zone (contact) | 42563.3368 |  |  | 5386 | Residential |  | 20170106SPN_01 | Infrastructure (network-based) | -37.6039 | 145.1205 | 1 | AusNet Services Distribution | Report | 6536 | 0.0044525 | Low voltage AC (<1kV) | Essendon Airport | 3754 | Doreen | Dug up
On arrival crew carried out repairs | 95 SYCAMORE STREET, HOPPERS CROSSING VIC 3029 | 30113997 | Working too close to overhead lines | [5 empty] | 2 | A customer informed a tree branch contacted the service cable while house owner was trimming trees at the incident location. Upon arrival the crew found that the service wire (neutral wire) had been cut while the house owner was pruning trees. There were no reported injuries or fire. | Service conductor | 2 | 2 | 2 |  | LV009 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 19/12/2016 13:55 |  |  | 5391 | Residential |  | 20170109PWA_01 | Infrastructure (network-based) | -37.861 | 144.6971 | 1 | Powercor | Report | 6541 | 0.014109 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Trees
On arrival crew completed repairs | 3 WILLIAM STREET, NETHERBY VIC 3418 | 30142061 | Vehicle | [5 empty] | 2 | A customer reported that a truck had brought down a wire at the incident location. On arrival the crew found that an unknown high load vehicle had struck the LV neutral screen service at the incident location, causing it to break in the middle and fall to the ground. The driver or vehicle could not be identified, and there were no apparent witnesses. There was no ground fire, third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | NHL016 | Unidentified high load struck service cable. | Loss of supply | 19/12/2016 12:10 |  |  | 5398 | Roadway |  | 20170109PWA_03 | Infrastructure (network-based) | -36.1088 | 141.6523 | 1 | Powercor | Report | 6553 | 0.00095602 | Low voltage AC (<1kV) | Horsham Aerodrome | 3418 | Netherby | Vehicle
On arrival crew carried out repairs | 7 ROYALE DRIVE, PLUMPTON VIC 3335 | 30316289 | Working too close to underground cables | [5 empty] | 2 | A contractor reported damaging a cable while excavating at the incident location. Upon arrival the fault crew found that the service cable and its conduit had been damaged. No fire or injuries reported. | Services cable | 2 | 2 | 2 |  | SA009 | During excavation work contractor struck cable conduit | No Go Zone (contact) | 21/12/2016 9:51 |  |  | 5406 | Public space |  | 20170109PWA_08 | Infrastructure (network-based) | -37.7158 | 144.7255 | 1 | Powercor | Report | 6568 | 0.03633 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Dug up
On arrival crew isolated supply and commenced repairs | 651-669 LONSDALE STREET, MELBOURNE VIC 3000 | 30185011 | Working too close to underground cables | [5 empty] | 2 | A contractor was digging to install sewer lid (Test Holes) at the incident location. Damaged LV cable whilst using jackhammer function of excavator. MOCS onsite but depth of cable not identified correctly. There was no fire, injuries or third party property damage. | Cable | 2 | 2 | 2 |  | VM011 | Contractor misread depth of cable on DBYD information | No Go Zone (contact);Damage to network assets | 20/12/2016 0:30 |  |  | 5414 | Public space |  | 20170111PWA_03 | Infrastructure (network-based) | -37.8154 | 144.9527 | 1 | CitiPower | Report | 6579 | 0.013201 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew isolated supply and carried out repairs | 450 DIGGERS ROAD, WERRIBEE SOUTH VIC 3030 | 30149514 | Vehicle | [5 empty] | 2 | A number of members of the public reported wires down at the intersection of Whites Rd and Diggers Rd, Werribee South. On arrival the crew had found that an unknown vehicle had struck the LV OH Service Cable at the incident location, causing it to break mid-way and flick up into and wrap around the LV Bare Conductorâ€™s with the live end lying on the ground at the intersection. The driver or vehicle could not be identified, and there were no witnesses. There was no ground fire, third party damage, injuries, shocks or HVI as a result of the incident. | Service conductor | 2 | 2 | 2 |  | WBE034 | Unknown vehicle struck service line. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/12/2016 9:46 |  |  | 5416 | Roadway |  | 20170111PWA_05 | Infrastructure (network-based) | -37.9523 | 144.6882 | 1 | Powercor | Report | 6581 | 0.010473 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Vehicle
On arrival crew carried out repairs | 1092-1094 RAGLAN PARADE, WARRNAMBOOL VIC 3280 | 30136195 | Vehicle | [5 empty] | 2 | A representative from TNT reported that one of their drivers had brought down a service wire at the incident location. On arrival the crew found that a TNT truck making a delivery to the premises at the incident location had contacted the LV overhead service, causing it to break and fall to the ground. There was no ground fire, no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | KRT023 | Truck contacted service line | Loss of supply | 42826.3681 |  |  | 5418 | Roadway |  | 20170112PWA_01 | Infrastructure (network-based) | -38.3618 | 142.4556 | 1 | Powercor | Report | 12426 | 0.012524 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
On arrival crew carried out repairs | 6223 LODDON VALLEY HIGHWAY, BEARS LAGOON VIC 3517 | 33017867 |  |  |  | Overheated connection |  |  | 2 | Customer reported cables had started a small grass fire started at incident location. Crew attended and found small grass fire of approximately 10m X 5m was extinguished. Grey PVC Service cable leads insulation had shorted out causing grass fire. No injuries or property damage reported. | Service conductor | 2 | 2 | 2 |  | CHA006 | Overheated connection | Grassfire | 13/01/2017 14:57 | 1 | Small: 10 - 1000 sq.m | 5431 | Agricultural |  | 20170116PWA_02 | Infrastructure (network-based) | -36.3 | 143.9744 | 1 | Powercor | Report | 6618 | 0.038881 | Low voltage AC (<1kV) | Bendigo Airport | 3517 | Bears Lagoon | Connection
On arrival crew isolated supply for REC to carry out repairs | 14 MOKHTAR DRIVE, HOPPERS CROSSING VIC 3029 | 30106198 |  |  |  | Overheated connection |  |  | 2 | Customer (MRS BIANCA MANIC) reported that the bottom of the fuse box at her house had melted and was dripping onto the garden. She had turned the main switch off and contacted the property owner to arrange for an REC to replace the fuse box. On arrival the crew found that the connections in a 1 phase fused mains box (FOLCB) had overheated, resulting in the box melting at the bottom. There were no reported injuries. There was no ground fire. | Customer installation | 2 | 2 | 2 |  | LV009 | Overheated connection | Loss of supply;Melting or smoking only | 42887.8389 |  |  | 5434 | Residential |  | 20170116PWA_04 | Infrastructure (network-based) | -37.8735 | 144.7108 | 1 | Powercor | Report | 12427 | 0.040941 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | AF Other
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. A new overhead service cable was installed. There were no reports of a low service cable at this site. Linesmen installed a new 25sq.mm 3-Wire overhead service cable to replace the one found on the ground | 110 CREAMERY VALLEY ROAD, TOORA NORTH VIC 3962 | 2014374 | Vehicle | [5 empty] | 2 | IMS 226065. Grass fire near power lines per CFA. An AusNet Services' fault crew responded to a fault and a 3 Wire overhead service cable was found on the ground between pole 2014374 and customer's shed. Approximate fire area was 8m by 40m with most of the area being grass. 2 fence posts severely burnt and likely need replacing, 3 additional post burnt but not extensively. Also one fence post and gate burnt. No fire damage to our pole or the customer's shed. A tractor with a mowing unit attached contacted the overhead service cable which broke resulting in sparks. There was a resultant grass fire. No network caused asset failure. A 3rd party incident. New service installed at correct height. No reports of a low service. | Service conductor | 0 | 0 | 0 |  | ftr12 | Tractor with mowing unit contacted an overhead service cable. | Grassfire | 16/01/2017 16:10 | 1 | Small: 10 - 1000 sq.m | 5445 | Agricultural |  | 20170117SPN_01 | Infrastructure (network-based) | -38.6526 | 146.3256 | 1 | AusNet Services Distribution | Report | 6637 | 0.0038981 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3962 | Toora North | Vehicle
On arrival crew carried out repairs | 658 BUNGAREE-WALLACE ROAD, WALLACE VIC 3352 | 30001649 | Vehicle | [5 empty] | 2 | The Fire Brigade reported a wire down at the incident location. On arrival the crew found that an unknown truck had contacted the overhead service, causing it to break and fall to the ground. There was no ground fire, no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | BAN011 | Service contacted by unknown vehicle | Loss of supply | 42887.625 |  |  | 5466 | Roadway |  | 20170118PWA_03 | Infrastructure (network-based) | -37.5565 | 144.0421 | 1 | Powercor | Report | 6665 | 0.036705 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Wallace | Vehicle
CEOT dispatched a fault crew to isolate, make safe and investigate. The fault crew checked to make the area safe and proceeded to replace the neutral screen service cable to the house and the 2 Phase neutral screen service cable over the road was also replaced. The old service cable was unavailable to be examined but the fault location was at the termination clamp in discussions with the fault crew the rest of the service cable was in reasonable condition with no cracking. The other 2 services on the pole where newer twisted XLPE cable. All neutral screen services on this pole have now been replaced. | 90 POWERSCOURT STREET, MAFFRA VIC 3860 | 2514867 |  |  |  | Age;Electrical breakdown |  |  | 2 | IMS 226088. Reports of a wire fallen to the ground which started a small grass fire of 3 sq.m. Fire extinguished. The attending AusNet Services' fault crew found the fire was out when they arrived and a neutral screen service cable was on the ground from the service pole to the house. LIS number 2514867. The service cable to 90 Powerscourt St was on the ground and dead. | Service conductor | 0 | 0 | 0 |  | MFA31 | Fault location was at the neutral screen service cable termination clamp causing the cable to burn off resulting in sparks. | Grassfire | 17/01/2017 11:30 | 1 | Localised: less than 10 sq.m | 5461 | Residential |  | 20170118SPN_01 | Infrastructure (network-based) | -37.9631 | 146.9859 | 1 | AusNet Services Distribution | Report | 11245 | 0.028532 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3860 | Maffra | OH Cable
CEOT dispatched a fault crew to isolate, make safe and investigate. the crew isolated and checked for any damage. Customers supply restored. DAO & Claims Section advised. | 45 BRIDGE INN ROAD, WOLLERT VIC 3750 | 5803792 | Working too close to overhead lines |  |  | Fault on customer installation |  | Phase to earth | 1 | IMS 226107. EPG32 Trip. PH-PH Fault. Patrolled, crew were advised an Excavator at PIONEER QUARRY caused a line clash and was unaware of power outage. PIONEER's protection devices didn't operate causing FDr to trip. No call to AusNet Services' CEOT made. No Damage. No one hurt. Report from local attending DAO who visited the site: Excavator had misjudged and made contact with the privately owned 22kV O/H conductor on the 18th of Jan 2017. Their 22kV CB not operating. This has caused fault current to feed back and cause an outage on AusNet Services' feeder EPG32. Patrolled, crew were advised an Excavator at PIONEER QUARRY caused line clash and was unaware of power outage. The hit line occurred between Pole #5803794 and Pole #5803792. | Customer installation | 0 | 0 | 0 |  | epg32 | Excavator in quarry contacted private overhead HV conductors. | Loss of supply;No Go Zone (contact) | 18/01/2017 10:15 |  |  | 5471 | Industrial |  | 20170119SPN_01 | Infrastructure (network-based) | -37.5949 | 145.0425 | 1 | AusNet Services Distribution | Report | 12339 | 0.00050347 | 22kV AC | Essendon Airport | 3750 | Wollert | Vehicle
Site was made, conductor repaired and resagged and customer supply were restored | UNIT 1 287 BELL STREET, COBURG VIC 3058 | Pole no. A048916 | Vehicle | [5 empty] | 1 | Unknown third party truck made contact with HV/LV pole at the corner of Gordon St and Bell St Coburg, the impact from the truck in-turn brought down the LV open wire conductors. The incident resulted in the loss of supply to 19 customers supplied from substation Gordon-Bell. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CS02 | Truck hit pole A048916 Bell St cnr Gordon St Coburg | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/01/2017 16:16 |  |  | 5476 | Roadway |  | 20170120JEM_02 | Infrastructure (network-based) | -37.7398 | 144.9499 | 1 | Jemena | Report | 12385 | 0.0050394 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Vehicle
Site was inspected, repair undertaken and deemed safe. At the time of writing, the transformer has not been replaced yet. At this stage, we have not conducted other works to better secure this particular site because we are still working on how best to arrest or alleviate a recent trend of similar copper thefts. | 111 WHITEHALL STREET, FOOTSCRAY VIC 3011 |  | Vandalism;Copper theft | [5 empty] | 2 | Forced entry into fenced off outdoor substation resulting in copper and plant theft. Plant is a 750kVA ground-type transformer with wiring attached. The transformer was energised only (no customers were taking supply from the substation) and it appears that the vandals opened the HV fuses to de-energise the substation, then cut the transformer leads approx. 300mm below the fuse units. | Outdoor;Transformer | 0 | 1 | 0 |  | YVE21 | Copper theft and vandalism of the property | No Go Zone (contact) | 21/01/2017 14:00 |  |  | 5477 | Industrial |  | 20170121JEM_01 | Infrastructure (network-based) | -37.8107 | 144.9019 | 1 | Jemena | Report | 12386 | 0.0065347 | 22kV AC | Essendon Airport | 3011 | Footscray | Other
A faults crew attended and proceeded to replace the damaged krone switch and the 160amp DIN fuses. Supply was restored upon completion. | 5 PRESTIGE DRIVE, CLAYTON SOUTH VIC 3169 | 611069 |  | Heat |  | Electrical overload |  |  | 2 | Emergency services advise of a pole fire outside this premise. A pole fire was reported at the bus pole of "Prestige-Fairbank" pole type substation at pole No. LIS 0611069 outside 5 Prestige Drive where a LV krone switch was found to be burnt out and heat damaged and requires replacement. The suspected cause was overload. | Any other type | 0 | 0 | 0 |  |  | The suspected cause was overload. | Pole-top fire | 19/01/2017 13:00 | 1 | Negligible: no ground fire | 5487 | Industrial |  | 20170124UTD_01 | Infrastructure (network-based) | -37.9419 | 145.1218 | 1 | United Energy Distribution | Report | 6694 | 0.024446 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | NELSON STREET, MOORABBIN VIC 3189 | 1816429 |  | Precipitation |  | Leakage |  |  | 2 | Caller reports power lines sparking and a small fire on the crossarm has been extinguished. During early morning light rain, a pole fire occurred at a HV/LV strain pole No. LIS 1816429 located next to "Nelson 36-Roberna" pole type substation. The pole fire originated on the HV strain crossarm near the disc insulators that caused the blue phase HV conductor to fall in close proximity to the white and blue phase LV conductors below. Fortunately, a high voltage injection did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | HT 13 | Light rain after a dry hot day. | Pole-top fire | 24/01/2017 5:59 | 1 | Negligible: no ground fire | 5491 | Industrial |  | 20170124UTD_03 | Infrastructure (network-based) | -37.945 | 145.0716 | 1 | United Energy Distribution | Report | 11268 | 0.03974 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Crossarm
On arrival crew carried out repairs. | 4 TURNER STREET, ABBOTSFORD VIC 3067 | 30170685 |  |  |  | Leakage |  |  | 2 | Vic Fire informed that a pole on fire at the incident location. On arrival the crew found that HV cross arm had burnt but remained intact. There was no ground fire, third party damage or injury. | Crossarm (wood) | 2 | 2 | 2 |  | CW009 | excessive leakage current | Pole-top fire | 18/01/2017 7:47 | 1 | Negligible: no ground fire | 5496 | Public space |  | 20170125PWA_01 | Infrastructure (network-based) | -37.7984 | 144.9953 | 1 | CitiPower | Report | 6705 | 0.0024329 | 11kV AC | Essendon Airport | 3067 | Abbotsford | Crossarm
On arrival crew carried out repairs | 1 WINZE COURT, LONG GULLY VIC 3550 | 30019838 |  | Alive;Fallen;Property owner/customer |  |  |  |  | 2 | Customer reported a tree had brought down an LV service and had commenced a ground fire at the incident location. On arrival the crew found that a LV neutral screened service cable was brought down by a customer tree, resulting in the service breaking and igniting a small ground fire, 0.3m square in total burnt. The service remained alive on the ground until the Powercor fault crew arrived & isolated it. There were no reported injuries, no 3rd party damage. | Service conductor;Neutral screen | 2 | 2 | 2 |  | BET001 | Vegetation: Trees Incident | Grassfire | 23/01/2017 20:20 | 1 | Localised: less than 10 sq.m | 5498 | Residential |  | 20170125PWA_03 | Infrastructure (network-based) | -36.7477 | 144.256 | 1 | Powercor | Report | 6707 | 0.012056 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Long Gully | Trees
On arrival crew carried out repairs | 1065 SPRINGBANK ROAD, SPRINGBANK VIC 3352 | 32006084 | Copper theft | [5 empty] | 2 | An employee reported copper earths missing pole at Toohey Pole 15. The crew attended and found that the LV & HV earths on Toohey Pole 15 had been stolen. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | cable theft | Damage to network assets | 22/01/2017 20:28 |  |  | 5500 | Roadway |  | 20170125PWA_05 | Infrastructure (network-based) | -37.5359 | 144.0905 | 1 | Powercor | Report | 6709 | 0.022365 | Earthing cable | Ballarat Aerodrome | 3352 | Springbank | Other
On arrival crews commenced repairs. 70M of steel HV conductor replaced at pole 6. | 68 SNAPPER POINT ROAD, ALLESTREE VIC 3305 | 30148494 |  | Prone to salt deposition |  | Corrosion |  |  | 1 | Powercor received a call from Vic Fire advising of a fire at the base of a pole in Snapper Point Rd. When crew arrived they found a conductor on the ground at the incident location and CFA crews in attendance. No injuries were reported. | Conductor (bare) | 2 | 2 | 2 |  | PLD001 | Corrosion of steel conductor | Grassfire | 29/01/2017 11:57 | 1 | Small: 10 - 1000 sq.m | 5516 | Roadway |  | 20170130PWA_03 | Infrastructure (network-based) | -38.2691 | 141.6738 | 1 | Powercor | Report | 12431 | 0.024272 | 22kV AC | Portland (Cashmore Airport) | 3305 | Allestree | Conductor
The attending EIO conducted voltage tests and a voltage test of 85.0V AC was found to be present with the installation under load. An NST test was conducted at the switchboard which recorded a fail result. The existing neutral screen service was found to have weather damage about 1.0m from the pole. The service was disconnected and removed by the truck crew. A defect notice was written for an REC to relocate and replace the existing mains box to a riser bracket, mains to be tested and Prescribed Certificate of Electrical Safety to be issued. Until then, the property remains off supply. | 54 HILLSYDE PARADE, STRATHMORE VIC 3041 |  |  | Precipitation |  | Moisture ingress;Corrosion |  |  | 2 | A person was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | NS14 | A severely corroded neutral of a two-wire aluminium overhead neutral service cable was identified as the cause of the high impedance associated with the return path of the neutral current. The corrosion of the service cable was the result of water entering the insulation/sheath via a small perforation in the cable sheath. Cause of the damaged outer sheath is unknown. The existing neutral screen service was found to have weather damage about 1.0m from the pole. | Minor shock | 31/01/2017 9:25 |  |  | 5523 | Residential |  | 20170131JEM_02 | Infrastructure (network-based) | -37.7371 | 144.9252 | 1 | Jemena | Report | 12388 | 0.03824 | Low voltage AC (<1kV) | Essendon Airport | 3041 | Strathmore | OH Cable
On arrival crew carried out repairs. | 330 LONGS HILL ROAD, POOTILLA VIC 3352 | 30016329 |  |  |  | Overheated connection |  |  | 2 | A customer reported no supply at the incident location. On arrival the crew found that an LV FOLCB overheated and caught fire on the substation pole out front of this address. There was no ground fire, no reported third party damage or any injuries. | Connection box | 2 | 2 | 2 |  | BAN008 | Due to damage unable to determine direct cause | Pole-top fire | 19/01/2017 5:34 | 1 | Negligible: no ground fire | 5525 | Roadway |  | 20170131PWA_03 | Infrastructure (network-based) | -37.5117 | 143.9454 | 1 | Powercor | Report | 6744 | 0.040052 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Pootilla | Pole
The crew isolated the substation and replaced the missing HV earths. | 972 INGLISTON ROAD, INGLISTON VIC 3342 | 30116697 | Copper theft | [5 empty] | 2 | V-Line reported a supply issue at the signal box at this location. A crew attended and found the both HV earths on pole missing. There were no reported shocks, injuries, fire start or third party damage. | Earth/earthing | 2 | 2 | 2 |  | BMH003 | Cable theft | Damage to network assets | 22/01/2017 9:05 |  |  | 5536 | Roadway |  | 20170201PWA_06 | Infrastructure (network-based) | -37.657 | 144.3189 | 1 | Powercor | Report | 6758 | 0.019995 | 12.7kV AC (SWER) | Avalon Airport | 3342 | Ingliston | Other
On arrival crew carried out repairs | 4 WILLSMERE ROAD, KEW VIC 3101 | 30176785 | Vehicle | [5 empty] | 2 | A resident from the units at 4 Willsmere Road reported a truck has rolled over pillar, wires exposed outside his address. On arrival the crew found the pillar outside the property badly damaged. The truck working on gas assets approx.300m away rolled down the street, avoided making contact with pole and struck the electrical pillar and a water asset. The impact of the truck moved the pillar from its existing location and damaged the blue phase of the LV cable. | LV Pillar | 2 | 2 | 2 |  | Q09 | It was reported that the Tipper truckâ€™s hand brake failed which caused the incident. | Damage to network assets | 19/01/2017 3:14 |  |  | 5539 | Public space |  | 20170202PWA_01 | Infrastructure (network-based) | -37.799 | 145.031 | 1 | CitiPower | Report | 6761 | 0.0034618 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Vehicle
Requested TOC to offload Cap Bank and call MFB. Emergency isolation and earthing of Cap Bank completed under instruction from TOC. MFB attended and confirmed fire no longer active. Switching and new permit issued to assess damage and initiate repair. Regarding the fire on this reactor, there was no threat to other plant or vegetation areas within the switchyard or station, the fire was the fiberglass and reactor coil supports, it was extinguished with a fire extinguisher and most visible effects of the fire was smoke. Note to Greg Sieburn - the F-Factor scheme was established for fires related to the Distribution network only. No such scheme has been established for the Transmission network since Transmission related fires are very rare. | 917 PRINCES HIGHWAY, SPRINGVALE VIC 3171 |  |  |  |  | Incorrect design |  |  | 1 | IMS 226261. On Restoration of No. 4A Cap Bank after fault on 25/01/17 White Phase Reactor caught fire once it had been put on load. Energisation required to confirm rebalance of Red phase had been successful. CB tripped to Lockout. | Reactor;Other | 0 | 0 | 0 |  |  | Issue was the failure of a 66kV capacitor bank reactor, one phase failed when power restored to capacitor bank after routine switching. The failure of the reactor caused a small fire which was extinguished by the MFB. Reactor was located inside a secure Terminal Station, fenced in its own right on top of a concrete foundation. | Plant/equipment | 25/01/2017 0:00 | 2 | Negligible: no ground fire | 5540 | Other | Substation | 20170202SPN_01 | Infrastructure (network-based) | -37.9285 | 145.1427 | 1 | AusNet Services Transmission | Report | 12343 | 0.034389 | 66kV AC | Moorabbin Airport | 3171 | Springvale | AF Other
The 150mm LVABC over the road was replaced by a construction crew from pole No. LIS 1823700 to the factory. Supply was restored upon completion. | 10-12 INDEPENDENCE STREET, MOORABBIN VIC 3189 | 1823700 |  |  |  | Overheated connection |  |  | 2 | MFB state a service line is on fire. A 150mm LVABC connection failed and caused the service leads to briefly catch fire and melt. | Conductor (ABC) | 0 | 0 | 0 |  |  | Probable loose or overheated connection. | Plant/equipment | 31/01/2017 7:00 | 1 | Negligible: no ground fire | 5551 | Industrial |  | 20170203UTD_06 | Infrastructure (network-based) | -37.9444 | 145.0581 | 1 | United Energy Distribution | Report | 6775 | 0.033267 | Low voltage AC (<1kV) | Moorabbin Airport | 3189 | Moorabbin | Connection
On arrival crew isolated supply and carried out repairs. | 30 BROOKE STREET, MOYSTON VIC 3377 | 32090686 |  |  |  | Overheated connection |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that the HV dropper connected to the HV bushing had failed which caused arching at the joint resulting with sparks falling to the ground causing a small ground fire. There was a ground fire of approximately 15 mtrs x 5 mtrs in size. No protection operated. No reported shocks or injuries. | Dropper/bridge | 2 | 2 | 2 |  | ART033 | Connection failure on HV bushing | Grassfire | 42796.8389 | 1 | Small: 10 - 1000 sq.m | 5560 | Roadway |  | 20170206PWA_03 | Infrastructure (network-based) | -37.3039 | 142.7666 | 1 | Powercor | Report | 6788 | 0.041509 | 22kV AC | Hamilton Airport | 3377 | Moyston | Connection
On arrival crew isolated supply and carried out repairs. | 652 RUNNYMEDE SCHOOL ROAD W, RUNNYMEDE VIC 3558 | 33079146 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | VIC Fire reported pole down at incident location. Crew attended and speaking with attending Police were informed that a local farming contractor was shifting large hay bales . Contact was made with the HV conductor between pole # 1 Nhill Spur and pole # 2 Nhill Spur causing the cable to fail. As result of the shock load tee off pole # 14 Runnymede Spur failed at ground level (limited life pole]. A stubble fire started and burnt an estimated 10 acres . Ground fire attended by CFA. No property damage reported no shock or personal injury reported. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | KYM001 | Farmer shifting hay bales contacted overhead conductor | Grassfire | 42827.4674 | 1 | Medium: 1000 sq.m - 10 ha | 5564 | Agricultural |  | 20170206PWA_06 | Infrastructure (network-based) | -36.5394 | 144.6643 | 1 | Powercor | Report | 6796 | 0.040558 | 12.7kV AC (SWER) | Bendigo Airport | 3558 | Runnymede | Other
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. The fault crew found a dead bird at the base of the pole. A 15 acre grass fire was observes in the vicinity. CEOT advised the local DOA to investigate. CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. The fault crew found a dead bird at the base of the pole. A 15 acre grass fire was observes in the vicinity. CEOT advised the local DOA to investigate. The fire was extinguished by the fire brigade. No damage to network assets. | 705 HAZELWOOD ROAD, HAZELWOOD NORTH VIC 3840 | 2623408 |  | Bird |  |  |  | Phase to earth | 1 | IMS 226292. Grass fire in vicinity of Firmins Lane & Hazelwood Rd. Vic Fire want site checked to see if fittings on pole caused it. Report from local DAO: At 5:01pm on Saturday 6/2/17, I was called by the AusNet Services CEOT to go to 585 Hazelwood Rd, Hazelwood North to investigate a pole fire. I arrived at the site at approximately 5:15pm. The Maximum temperature of the day was 31.5 degrees and the maximum wind speed on the day was 56km/h at 10:53 in a NW direction (http://www.bom.gov.au). By the time I arrived, the fire had been extinguished and the linesmen were investigating. The Fire Brigade had left the site. The fire had burnt an area of approximately 600m x 100m. A dead bird was at the base of one of the poles. There were no obvious visible signs of damage to either pole #2607944 or #2623408. A large bird caused a flashover between a phase and steel crossarm / concrete pole and the bird and fell to the ground resulting in a grass fire. Electrical protection operated - a reclose occurred. | Conductor (bare);Crossarm (steel);Pole (concrete) | 0 | 0 | 0 |  | tgn23 | Bird Incident | Grassfire | 42857.6528 | 1 | Medium: 1000 sq.m - 10 ha | 5554 |  |  | 20170206SPN_01 | Infrastructure (network-based) | -38.2561 | 146.4895 | 1 | AusNet Services Distribution | Report | 6781 | 0.0066447 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | Animal
CEOT dispatched a fault crew to made safe, investigate and carry out necessary repairs. CEOT also informed the local DAO to investigate. Crew replaced the existing overhead neutral screen service cable with a new XLPE type service cable. | 44 STINTONS ROAD, PARK ORCHARDS VIC 3114 | 1205491 |  | Wind |  |  |  | Phase to earth | 2 | IMS 226293. Per Fire Brigade - Wire down and grass fire in the vicinity. A neutral screen service cable came away from the POA falling to the ground due to winds/weather causing sparks and a small grass fire approximately 1m x 1m in size. | Service conductor | 0 | 0 | 0 |  | rwn26 | Overhead service cable fell to ground due to strong winds. | Grassfire | 42857.7882 | 1 | Localised: less than 10 sq.m | 5555 | Residential |  | 20170206SPN_02 | Infrastructure (network-based) | -37.7701 | 145.204 | 1 | AusNet Services Distribution | Report | 6783 | 0.013493 | Low voltage AC (<1kV) | Moorabbin Airport | 3114 | Park Orchards | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the crew replaced the 22kV powder filled fuse units including the white and blue phase flex and insulators under Access Authority conditions prior to the supply being restored. As part of an internal investigation to the cause, there was a request for the Raychem cover to be quarantined. | ERAMOSA ROAD W, MOOROODUC VIC 3933 | 8831026 |  | Animal |  |  |  |  | 1 | At 0154hrs on 29/01/2017, 22kV feeder MTN 22 circuit breaker reclosed to lockout affecting 3188 customers. A large possum was found at the base of spur fuse pole MT 0102 near the corner of Eromosa and Derill Roads, Moorooduc. The possum appears to have been caught between the earthed HV steel crossarm to the bridging bar on the HV ABC interface pole. Initially there appeared no damage at pole No. LIS 8831026 but when the conductors were re-energised, the onsite operator observed arcing and fire from the top of the pole and supply was promptly isolated remotely at manual gas switch MT 7286. The Raychem covering the powder filled fuse unit caught fire and continued burning for approximately 20 minutes following the interruption of supply. The operator extinguished the fire with the use of a fire extinguisher from the EWP. | Conductor (ABC);Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | MTN 22 | Animal Incident | Pole-top fire | 29/01/2017 1:54 | 1 | Negligible: no ground fire | 5574 | Roadway |  | 20170208UTD_02 | Infrastructure (network-based) | -38.2147 | 145.1132 | 1 | United Energy Distribution | Report | 6813 | 0.038429 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Animal
Emergency high voltage switching was completed and the capacitor bank CB was racked out with the shutters locked until further notice. An investigation to the cause commenced. | CORRIGAN ROAD, NOBLE PARK VIC 3174 |  |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | Fire at NP (Noble Park) zone substation and the fire brigade are in attendance. A 22kV Capacitor Bank reactor failed and caught fire. The fire authority were promptly in attendance, cut the United Energy zone substation access lock and extinguished the fire. No customers were impacted. | Zone substation | 0 | 1 | 0 |  | NP Zone substation | The cause is under investigation. Due to the warm weather at the time of the fire, overheating was suspected. | Plant/equipment | 42949.7083 | 1 | Negligible: no ground fire | 5580 | Other | Substation | 20170209UTD_02 | Infrastructure (network-based) | -37.9787 | 145.166 | 1 | United Energy Distribution | Report | 12330 | 0.029824 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | AF Other
The initial action taken to address the low volts was to rebalance the customers by swapping from red phase to white phase. In an attempt to uncover a reason for the person receiving an electric shock, the attending had EIO conducted voltage tests; however there was no second point of contact. The customer reported having issues with fluctuating supply and during the investigation, the incoming supply voltage was recorded at 190V. An NST test was not able to be conducted due to the under-voltage. The adjacent property fed via an alternative phase recorded 245V between active/neutral and active/earth. The attending service crew re-fed 19A to an alternative phase and the control room was notified to organise further investigation in the daytime to investigate the transformer balancing issues. After the polly loggers were already installed on the circuit, the power quality team investigated the low volts at this premise and found there was no neutral connection between the ABC and open wire at the corner of David Avenue and Rachelle Road in Keilor East (Pole # A056971). The power quality team suspects that this would have been the cause for the minor shocks customer received. This has now been rectified as of 14/02/17. | 19A LINCOLN DRIVE, KEILOR EAST VIC 3033 |  |  |  |  | Neutral fault;Out of balance load |  |  | 2 | A person was using a hairdryer when she reported experiencing a tingling sensation in her hand. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, did not reveal any defective conditions or equipment. | Neutral screen | 0 | 0 | 0 |  | AW06 | No neutral connection between the ABC and open wire at the corner of David Avenue and Rachelle Road in Keilor East (Pole # A056971) | Minor shock | 42949.9021 |  |  | 5583 | Residential |  | 20170210JEM_02 | Infrastructure (network-based) | -37.7445 | 144.8746 | 1 | Jemena | Report | 12391 | 0.033456 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | Connection
On arrival crew carried out repairs. | 1321 TOOLAMBA ROAD, TOOLAMBA VIC 3614 | 33095056 |  | Bird |  | Overheated connection |  |  | 2 | CFA reported a pole fire at the above location. A crew attended and found a LV U/G pole box had overheated and melted. Crew advise they had found a birds nest in the box. There was no ground fire start. No shocks, injuries or third party damage. | Connection box | 2 | 2 | 2 |  | MNA034 | Bird Incident | Pole-top fire | 27/01/2017 6:27 | 1 | Negligible: no ground fire | 5585 | Agricultural |  | 20170210PWA_01 | Infrastructure (network-based) | -36.5073 | 145.3109 | 1 | Powercor | Report | 6825 | 0.040873 | Low voltage AC (<1kV) | Shepparton Airport | 3614 | Toolamba | Animal
The crew removed the underground cable from above the pit. | 3 LA ROSE STREET, BRUNSWICK VIC 3056 | 30157700 | Working too close to underground cables | [5 empty] | 2 | A plumber (Mr Ryan Flynn) reported that he had exposed an underground cable and wants CitiPower to attend to relocate the cable at the incident location. On arrival the fault crew found that the plumber had exposed the underground cable, excavated and installed an underground concrete pit at the incident location. The cable according to our records was Out Of Service, but not abandoned. The DBYD response indicated the cable was "live" There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | BK011 | plumber installing pit (refer notes) | No Go Zone (contact);Damage to network assets | 24/01/2017 0:00 |  |  | 5589 | Roadway |  | 20170213PWA_02 | Infrastructure (network-based) | -37.7599 | 144.9588 | 1 | CitiPower | Report | 6831 | 0.025688 | 11kV AC | Essendon Airport | 3056 | Brunswick | Dug up
On arrival crew carried out repairs | 951-971 MOUNT COTTRELL ROAD, ROCKBANK VIC 3335 | 30107450 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from ground level to two metres up the pole. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | cable theft | Damage to network assets | 30/01/2017 16:49 |  |  | 5603 | Roadway |  | 20170214PWA_03 | Infrastructure (network-based) | -37.7189 | 144.6184 | 1 | Powercor | Report | 6853 | 0.031802 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew carried out repairs | 367-397 PAYNES ROAD, ROCKBANK VIC 3335 | 30108407 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from a height of two metres up the pole to ground level. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | cable theft | Damage to network assets | 30/01/2017 16:49 |  |  | 5605 | Roadway |  | 20170214PWA_05 | Infrastructure (network-based) | -37.7339 | 144.6371 | 1 | Powercor | Report | 6855 | 0.016027 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
Emergency high voltage switching was completed and the HV tee-off crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 3309074 |  | Precipitation;Prone to salt deposition |  | Leakage |  |  | 1 | At 0909hrs on 13/02/2017, 22kV ACR FS8164 located in Merewether Avenue reclosed to lockout affecting 1012 customers. During drizzly rain, a pole fire occurred at a HV tee-off crossarm on pole No. LIS 3309074 located on the corner of Nepean Highway and Allawah Avenue, Frankston. The CFA were also in attendance. The faults crew suspected that a high voltage injection occurred to customers supplied from "Allawah-Gould" substation and a LEI attended and checked premises in the vicinity for damage with no damage identified. The cause of the crossarm fire was tracking on the insulators caused by salt borne contaminates due to the poles location in close proximity to Port Phillip Bay. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | FTN 14 | The cause of the crossarm fire was tracking on the insulators caused by salt borne contaminates due to the poles location in close proximity to Port Phillip Bay. | Pole-top fire | 13/02/2017 9:09 | 1 | Negligible: no ground fire | 5609 | Roadway |  | 20170214UTD_02 | Infrastructure (network-based) | -38.1323 | 145.1246 | 1 | United Energy Distribution | Report | 6859 | 0.027473 | 22kV AC | Moorabbin Airport | 3199 | Frankston | Pole
A Powercor linesman repaired the defective termination in fuse main box. Voltage and NST tests were performed following the repair and normal results were obtained. | 42 APPIAN DRIVE, ALBANVALE VIC 3021 | 31022776 |  |  |  | Mechanical breakdown |  | Phase to earth | 2 | Stan received an electric shock when he contacted a metallic garden water tap located in an earthed situation. A voltage test with reference to an independent earth confirmed an 8 volts rise at the metallic garden water tap. An 18 volt rise was also measured at various points associated with the neutral conductor forming the consumerâ€™s mains and the aerial service line with reference to an independent earth. This voltage rise resulted from a loose neutral service tap clamp termination to the reticulation neutral conductor. | Connector/termination | 2 | 2 | 2 |  | SA004 | loose neutral service tap clamp termination | Minor shock | 25/12/2016 9:00 |  |  | 5619 | Residential |  | 20170215PWA_02 | Infrastructure (network-based) | -37.7473 | 144.7731 | 1 | Powercor | Report | 6872 | 0.040852 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Albanvale | Connection
Crew attended, isolated supply and undertook repairs. defect notice issued. | 149 BRUCE STREET, TEESDALE VIC 3328 | 30142042 | Building too close or within the No Go Zone | [5 empty] | 2 | A customer informed a service cable accidently brought down by Bobcat at the incident location. Upon arrival the crew found the cable had been damaged. There were no reported injuries, third party damage or fire. | Service conductor | 0 | 0 | 0 |  | GL012 | Interference | Loss of supply;Damage to network assets | 42470.4313 |  |  | 3028 | Residential |  | 20161012PWA_01 | Infrastructure (network-based) | -38.0166 | 144.0491 | 1 | Powercor | Report | 3987 | 0.00061227 | Low voltage AC (<1kV) | Avalon Airport | 3328 | Teesdale | Vehicle
A crew attended and replaced missing earth cable, reported to police | 2 RAILWAY STREET, TALBOT VIC 3371 | 33015681 | Copper theft | [5 empty] | 2 | A pole inspector reported copper earth cable missing off a pole in Railway St, Talbot. A crew attended and replaced missing earth cable. There were no reported injuries, shocks or third party property damages. | Earth | 0 | 0 | 0 |  | MRO007 | interference | Damage to network assets | 42470.616 |  |  | 3029 | Public space |  | 20161012PWA_02 | Infrastructure (network-based) | -37.1734 | 143.7053 | 1 | Powercor | Report | 3988 | 0.015928 | Earthing cable | Ballarat Aerodrome | 3371 | Talbot | Other
The fault crew requested the SWER line be shutdown by the CEOT and the crew then subsequently repaired the SWER conductor. Actions have been raised to improve the processes. Actions required: Update Fault Scout info pack and Call taker info pack in IRT. For all fallen/low HV/LV Conductors: Fault Scout is to confirm all Isolation points and install warning tag if open including INCD # including fault details e.g. low conductor at x location. If there is not an open point, then one needs to be created via a request to CEOT or local IRT, once an open point is created the above process needs to be followed. The above information shall be reported through to CEOT or IRT resolutions once completed for DOMS update. If the above cannot be completed then the Scout is to remain on-site and request make safe to attend ASAP. A patrol of the switching zone shall be undertaken prior to energising after Fault repairs, this is to ensure that there is no other potential Electrical Hazards in the vicinity. | 46 JOHANSSEN ROAD, KINGLAKE VIC 3763 | 1400946 |  |  |  |  | Ineffective planning/procedures/processes |  | 2 | IMS 224698. A Downer fault crew arrived at a job site (to repair a SWER line on the ground downed by a fallen tree) issued by AusNet Services' Scout Crew in Kinglake after a storm. On arrival the Downer crew performed a patrol of the line and found a SWER line that had been damaged and further along the line the crew performed a Safe To Approach test and found the SWER conductors to be alive. From our understanding the Fault Scout Crew called the damaged SWER conductor into the CEOT, the CEOT were meant to isolate this line before the feeder was put back in, but they failed to do so. This may have been due to it being missed, and follow up action is required. | Conductor (bare) | 0 | 0 | 0 |  | klk1 | There were a couple of issues: 1. The fault address provided to the Fault Scout was wrong. It was for the south side and not the north side of the intersection. The Fault Scout rang in Resolutions for some more information and was told to ring the customer. So the fault location took a while to find after the Fault Scout rang the reporting customer. When the Fault Scout rang in with the report the Fault Scout informed Resolutions that the location was wrong and on the other side of the intersection but could not find a street number so provided a CAM asset number. 2. The KLK feeder was out at the time. The Fault Scout enquired if this line was out in conjunction with the feeder and was told yes and to move on. The Fault Scout issued a warning that when the line was livened up this faulted SWER conductor had the potential to be live. Not knowing which direction the SWER was going to be livened up from it was a real possibility. Given this information the Fault Scout did not test with the Modiewark. The Fault Scout could not see the other CAM asset numbers as the tree fell across the entire road and could not determine if further damage occurred passed this point and advised of this. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42684.5104 |  |  | 3025 | Roadway |  | 20161012SPN_03 | Infrastructure (network-based) | -37.5342 | 145.3774 | 1 | AusNet Services Distribution | Report | 3984 | 0.041101 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3763 | Kinglake | Other
On arrival crew carried out repairs | 5 MORAS COURT, GISBORNE VIC 3437 | 30034797 |  | Wind;Alive;Fallen |  |  |  |  | 1 | Customer reported a tree over HV conductors at the incident location. On arrival the crew found that a HV conductor had been brought down by a large tree, resulting in a several small ground fires, 4m square in total. The tree has been confirmed as falling from outside the clearance space. There was no injuries. | Conductor (bare) | 2 | 2 | 2 |  | GSB011 | Vegetation: Trees Incident | Loss of supply;Grassfire | 15/10/2016 14:29 | 1 | Localised: less than 10 sq.m | 4052 | Agricultural |  | 20161017PWA_01 | Infrastructure (network-based) | -37.4898 | 144.5686 | 1 | Powercor | Report | 5028 | 0.022297 | 22kV AC | Melbourne Airport | 3437 | Gisborne | Trees
On arrival crew carried out repairs | 39 COWANNA AVENUE S, MERBEIN SOUTH VIC 3505 | 33066831 |  | Bird |  |  |  |  | 2 | Customer reported a supply interruption and wires hanging low at the incident location. On arrival the crew found that a birds nest containing numerous pieces of wire had shorted out between the concrete pole and an LV isolator, resulting in the wooden LV crossarm burning through and failing. Falling combusting material also started a ground fire of approximately 10m square which self extinguished. There were no injuries. | Crossarm (wood);Disconnector/isolator | 2 | 2 | 2 |  | MBN014 | Bird Incident | Loss of supply;Grassfire | 15/10/2016 11:35 | 1 | Localised: less than 10 sq.m | 4055 | Agricultural |  | 20161017PWA_03 | Infrastructure (network-based) | -34.1963 | 142.032 | 1 | Powercor | Report | 5032 | 0.026218 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Merbein South | Animal
on arrival crew carried out repairs | 674-740 COBURNS ROAD, TOOLERN VALE VIC 3337 | 30114228 | Copper theft | [5 empty] | 2 | A Powercor employee noticed an earth at pole LIS-112485 (25kVA 1ph pole sub) swinging in the breeze, and upon further inspection he noticed that someone had cut away and stolen approximately a 1m length of both the HV & LV earth at the pole. There were no reported injuries or third party property damages. | Earth/earthing | 2 | 2 | 2 |  | MLN014 | cable theft | Damage to network assets | 42592.6285 |  |  | 4059 | Roadway |  | 20161018PWA_03 | Infrastructure (network-based) | -37.6433 | 144.5763 | 1 | Powercor | Report | 5037 | 0.021387 | Earthing cable | Melbourne Airport | 3337 | Toolern Vale | Other
Overhead conductors (section) were isolated via the fuses at location 58608 & and fault crews repaired and restrained high voltage overhead conductors. | 63 KERRIE ROAD, RIDDELLS CREEK VIC 3431 |  |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | Council tree fell due to high winds across high voltage overhead conductors resulting in high voltage conductor to fall to the ground. | Conductor (bare) | 0 | 0 | 0 |  | SBY11 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/10/2016 1:38 |  |  | 4067 | Residential |  | 20161021JEM_01 | Infrastructure (network-based) | -37.4951 | 144.6746 | 1 | Jemena | Report | 5325 | 0.010117 | 22kV AC | Melbourne Airport | 3431 | Riddells Creek | Trees
On arrival crew confirmed isolations and commenced repairs. A LEI carried out inspections and confirmed there was no HVI's | 33 SHAWS ROAD, WERRIBEE VIC 3030 | 30105209 | Vehicle | [5 empty] | 1 | Vicfire reported that a car had collided with a pole at the the incident location and that HV conductors and few services were down. On arrival the fault crew found that a vehicle had struck the ground stay on pole LIS- 201882 which resulted in the pole shaking and this caused 2 x bays of HV conductors (Feeders WB023 and WBE014) to break and fall to the ground. As well, the HV conductors fell on top of the 3 service conductors. Follow up from LEI confirmed there was no HVI. The driver of the car left the scene of the accident, leaving the vehicle in the middle of road. There was no ground fire and no reported injuries, the condition of the car driver was unknown. | Conductor (bare);Services cable | 2 | 2 | 2 |  | WBE014 WBE023 | Vehicle collision with stay wire | Loss of supply;Damage to network assets | 18/10/2016 6:30 |  |  | 4070 |  |  | 20161021PWA_01 | Infrastructure (network-based) | -37.8882 | 144.6466 | 1 | Powercor | Report | 5052 | 0.037019 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival crew carried out repairs | 35 BRIGGS DRIVE, DERRIMUT VIC 3030 | 30139331 | Copper theft | [5 empty] | 2 | Powercor contact centre received a report of stolen copper earths at the incident location. There was no ground fire and no injury as a result of this incident. | Pole mounted;Earth/earthing | 2 | 2 | 2 |  | SU013 | Theft | Damage to network assets | 19/10/2016 10:45 |  |  | 4073 | Roadway |  | 20161021PWA_02 | Infrastructure (network-based) | -37.8052 | 144.7811 | 1 | Powercor | Report | 5078 | 0.037584 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply and carried out replaced crossarm | 3 KENNINGTON RISE, GISBORNE VIC 3437 | 30034631 |  |  |  | Rot |  |  | 1 | Vicfire reported HV conductors in contact with vegetation at the incident location. On arrival the crew found that a HV t/off cross-arm on Bundaleer P2 broke causing conductor to hang low and make intermittent contact with vegetation beneath. The arcing intermittently caused the vegetation to ignite. There was no ground fire, injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | GSB011 | broken crossarm | Other vegetation;Damage to network assets | 15/10/2016 11:47 | 1 | Negligible: no ground fire | 4074 | Agricultural |  | 20161021PWA_03 | Infrastructure (network-based) | -37.5048 | 144.5814 | 1 | Powercor | Report | 5076 | 0.023946 | 22kV AC | Melbourne Airport | 3437 | Gisborne | Crossarm
On arrival crew carried out repairs | 29 BOWDEN STREET, BIRREGURRA VIC 3242 | 32062029 |  |  |  | Moisture ingress |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Section of Low Voltage underground cable attached to the pole had faulted and showed signs of burning. There was no ground fire. No third party damage or injury was reported. | Conductor (insulated);Services cable | 2 | 2 | 2 |  | CLC007 | Due to damage unable to accurately identify cause. | Pole-top fire;Loss of supply;Damage to network assets | 18/10/2016 19:22 | 1 | Negligible: no ground fire | 4075 | Roadway |  | 20161021PWA_04 | Infrastructure (network-based) | -38.3466 | 143.7836 | 1 | Powercor | Report | 5057 | 0.0086493 | Low voltage AC (<1kV) | Avalon Airport | 3242 | Birregurra | Pole
CEOT dispatched a fault crew to isolate, make safe, investigate and repair. The crew isolated supply and made safe. A construction crew was advised to make necessary repairs. | 51 CASTELLA ROAD, CASTELLA VIC 3777 | 1400818 |  | Fallen |  |  |  | Phase to earth | 1 | IMS 223793. HV .093 AAC conductor on ground due to a tree falling and taking out a 5m bay ex HED057. One 15E Boric Acid fuse was blown on single phase spur HV Switch @ HE057. The HV conductor was back fed through other the spur fuse. The HV conductor was back fed from LIS 400813 through the other downstream transformers on the line. | Conductor (bare) | 0 | 0 | 0 |  | klk1 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/08/2016 11:00 |  |  | 4084 | Agricultural |  | 20161025SPN_01 | Infrastructure (network-based) | -37.5254 | 145.4317 | 1 | AusNet Services Distribution | Report | 5080 | 0.013634 | 22kV AC | Wallan (Kilmore Gap) | 3777 | Castella | Trees
On arrival crew carried out repairs | 680 SHELFORD-MT MERCER ROAD, MOUNT MERCER VIC 3352 | 30317952 | Manned aircraft | [5 empty] | 1 | A customer reported that a crop duster plane had hit power lines at the above location, but did not provide any further details at that point in time. On arrival the crew found the SWER conductor between Pole 29 Shelford and Charlton Shed P1 had been hit and broken as a result of the contact with the plane. The plane returned to Ballarat Airport safely There was no other damage, no injury, no shock and no ground fire start | Conductor (bare) | 2 | 2 | 2 |  | BAS022 | Aircraft flew into line | Loss of supply | 24/10/2016 17:53 |  |  | 4088 | Agricultural |  | 20161026PWA_01 | Infrastructure (network-based) | -37.8676 | 143.8987 | 1 | Powercor | Report | 5077 | 0.0009838 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3352 | Mount Mercer | Other
On arrival crew carried out repairs | 79 PEARSONS ROAD, MOUNT DORAN VIC 3334 | 30010307 |  | Wind;Alive;Fallen |  |  |  |  | 1 | A customer reported a tree was on an overhead conductor and a small grass fire has started at the incident location. On arrival the crew found that a tree had fallen onto the 12.7 KV SWER conductor causing it to break and fall to the ground, resulting in a ground fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BAS022 | Vegetation: Trees Incident | Loss of supply;Grassfire | 30/10/2016 13:35 | 1 | Small: 10 - 1000 sq.m | 4113 | Roadway |  | 20161031PWA_02 | Infrastructure (network-based) | -37.7173 | 144.0329 | 1 | Powercor | Report | 5111 | 0.038291 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3334 | Mount Doran | Trees
On arrival crew isolated supply and carried out repairs | 36-44 WOODWARD ROAD, GOLDEN GULLY VIC 3255 | 32053336 |  | Alive;Fallen;MEC |  |  |  |  | 1 | VicFire reported conductors smoking at the incident location. On arrival the crew found that a HV conductors had been brought down by a large tree from across the road, resulting in a small ground fire, 3m square in total. Cross arm on P15 had broken due to the impact and required replacing. There were no reported injuries or 3rd party damage. Protection operated. | Conductor (bare) | 2 | 2 | 2 |  | BET007 | Vegetation: Trees Incident | Loss of supply;Grassfire | 30/10/2016 16:50 | 1 | Localised: less than 10 sq.m | 4117 | Roadway |  | 20161102PWA_01 | Infrastructure (network-based) | -36.7941 | 144.2654 | 1 | Powercor | Report | 8044 | 0.016764 | 22kV AC | Bendigo Airport | 3255 | Golden Gully | Trees
On arrival crew carried out repairs | 9 CLARKE STREET, MOUNT MACEDON VIC 3441 | 32043265 |  | Wind | [5 empty] | An alarm indicated supply had been lost beyond â€œMt Macedon P130 ACRâ€. On arrival and subsequent line patrol the crew found that a branch from a cypress tree had fallen over conductors outside #9 Clarke Street, Macedon caused the ACR to trip to L/O, There were no reported injuries, no ground fire & no 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | GSB014 | Vegetation: Trees Incident | Other vegetation | 15/10/2016 10:09 | 1 | Negligible: no ground fire | 4121 | Roadway |  | 20161102PWA_03 | Infrastructure (network-based) | -37.4161 | 144.5887 | 1 | Powercor | Report | 5121 | 0.001735 | 22kV AC | Melbourne Airport | 3441 | Mount Macedon | Trees
On arrival crew removed debris from line | 115 ZEERUST SCHOOL ROAD, ZEERUST VIC 3634 | 33095292 |  | Wind |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival the crew found that wind-blown grass had caused a flashover on a pole, then fell to the ground resulting in a ground fire (approx. 25m x 2m) on road reserve. There were no reported injuries, Shocks of third party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHTSNKA2 | Farmer in an adjacent paddock was raking hay | Grassfire | 42411.5958 | 0 | Small: 10 - 1000 sq.m | 4131 | Roadway |  | 20161104PWA_01 | Infrastructure (network-based) | -36.266 | 145.404 | 1 | Powercor | Report | 5141 | 0.0085162 | 66kV AC | Shepparton Airport | 3634 | Zeerust | Other
An electrical inspector inspected a number of premises at the incident location. Minor damage was found at a number of premises. The crew completed repairs and supply was restored. | 235 DUFFIELDS ROAD, JAN JUC VIC 3228 | 32085842 |  |  |  | Neutral fault |  |  | 2 | A customer reported irregularities with her power supply. Following testing it was confirmed that the Low Voltage neutral transformer connection was damaged. There was no fire or injuries | Pole mounted;Connector/termination | 2 | 2 | 2 |  | WPD032 | Damaged Neutral connection | Less than $50k damage | 20/10/2016 18:01 |  |  | 4135 | Roadway |  | 20161104PWA_03 | Infrastructure (network-based) | -38.3407 | 144.3045 | 1 | Powercor | Report | 5147 | 0.012362 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
Emergency switching was completed and new insulated leads were delivered to the site and the repairs completed on pole No. LIS 11007312 under Access Authority conditions prior to the supply being restored. The failed lead has been quarantined at the ZNX depot for United Energy engineers to commence an investigation. | MERRICKS ROAD, MERRICKS VIC 3916 | 1107313 |  |  |  | Electrical breakdown |  |  | 2 | A ZNX construction crew had the task of completing minor HV maintenance on HVABC on 22kV feeder MTN32 from the ACR MT7621 in Merricks Road to the HV cabinet "Tubbarubba -Bit Drom" including "Merricks -Bit Drom", "Kerr-Merricks", "Merricks-Kentucky", "Kentucky P3-Merricks" and "Merricks-Warneeke" substations. Tasks included: - Possum proofing - Restrain and alter HVABC terminations at "Kerr-Merricks" substation - Retire redundant HVABC and 6 poles from pole No. LIS 11007303 to pole 9738806, 1 pole north of "Merricks-Bit Drom" substation. Following the completion of the planned work, supply was restored along Merricks Road and a failure at "Merricks-Kentucky" substation on the existing insulated droppers to the transformer caused the HV bushing cover to briefly catch on fire. The substation was promptly isolated and the fire extinguished. The initial suspected cause, was a deteriorated connection that was made worse during the planned work. | Conductor (ABC);Aluminium;Connector/termination | 0 | 0 | 0 |  | MTN 32 | The initial suspected cause, was a deteriorated connection that was made worse during the planned work. | Pole-top fire;Loss of supply | 42440.625 | 1 | Negligible: no ground fire | 4133 | Residential |  | 20161104UTD_02 | Infrastructure (network-based) | -38.3633 | 145.0747 | 1 | United Energy Distribution | Report | 11264 | 0.030796 | 22kV AC | Moorabbin Airport | 3916 | Merricks | Connection
Emergency high voltage switching was completed and two HV strain crossarms (Pole No. LIS 7066298) and one HV intermediate crossarm (Pole No. LIS 7066510) was replaced under Access Authority conditions. In addition, the HV isolators were replaced and copper conductors were re-conducted as they sustained damage during the fault. Supply was restored upon completion. | TUNSTALL ROAD, DONVALE VIC 3111 | 7066298 |  | Wind |  | Conductor clashing |  |  | 0 | At 1637hrs on 04/11/2016, 22kV feeder NW 23 circuit breaker successfully reclosed and held. Emergency services advised of wires down in Tunstall Road near the corner of St Clems Road. During strong winds, slack HV copper conductor stringing may have contributed to the blue phase tee-off conductor contacting the red phase through line conductor near HV switch DT0045 at pole No. LIS 7066298 that caused the HV conductor to fall to the ground. The faults crew advised that a small grass fire started on the nature strip that measured approximately 5cm x 1.5m long. No HVI or major damage was sustained. | Conductor (bare);Crossarm (wood);Copper;Disconnector/isolator | 0 | 0 | 0 |  | NW 23 | Slack HV copper conductor stringing may have contributed to the cause of the incident. | Grassfire | 42471.6924 | 1 | Localised: less than 10 sq.m | 4147 | Roadway |  | 20161108UTD_02 | Infrastructure (network-based) | -37.7969 | 145.1698 | 1 | United Energy Distribution | Report | 5347 | 0.031683 | 22kV AC | Moorabbin Airport | 3111 | Donvale | Conductor
On arrival crew isolated supply and carried out repairs | 100A ST GEORGES ROAD, FITZROY NORTH VIC 3068 | CP0002866 |  |  |  | Overheated connection |  |  | 2 | MFB reported smokes coming from Northern end of Grandstand meter box at the above incident location. On arrival, the crew found that a low voltage fuse (red phase) had overheated and melted the meter cover above the fuse. There was no ground fire nor third party damaged. There were no reported injuries. | Meter board (including fuses) | 2 | 2 | 2 |  | F027 | Fuse too damaged to establish cause | Meter board | 31/10/2016 21:01 | 0 | Negligible: no ground fire | 4155 | Commercial |  | 20161110PWA_01 | Infrastructure (network-based) | -37.7886 | 144.9805 | 1 | CitiPower | Report | 5183 | 0.0087014 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 632 ESPLANADE, MORNINGTON VIC 3931 | 1102056 |  | Precipitation;Cold |  | HV injection;Leakage |  |  | 1 | At 0728hrs on 07/11/2016, 22kV ACR MT0321 located in Bentons Road reclosed to lockout affecting 1143 customers. During cool drizzly weather, a pole fire occurred at "Footway-Esplanade" pole type substation at pole No. LIS 1102056 located next to 632 Esplanade, Mount Martha. The pole fire originated at the crossarm brace bolt on the HV termination crossarm that caused the HV fuse unit and insulator to fall and make contact with the white and blue phase LV conductors below. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Footway-Esplanade" substation. The LEI confirmed a high voltage injection occurred (MOR 1609) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The cause was a build up of salt borne contaminants as the substation pole is located opposite Port Phillip Bay. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MTN 31 | The cause was a build up of salt borne contaminants as the substation pole is located opposite Port Phillip Bay. | Pole-top fire;HV injection;Loss of supply | 42562.3111 | 1 | Negligible: no ground fire | 4164 | Residential |  | 20161114UTD_02 | Infrastructure (network-based) | -38.241 | 145.03 | 1 | United Energy Distribution | Report | 5196 | 0.012763 | 22kV AC | Moorabbin Airport | 3931 | Mornington | Pole
Overhead conductors were isolated and made safe. | 1015 SOMERTON ROAD, GREENVALE VIC 3059 | A054676 | Vehicle |  |  |  |  | Phase to earth | 1 | Car crashed into pole on Somerton Road, Greenvale. This resulted in the pole breaking causing the high voltage conductors to fall to ground. | Pole (wood) | 0 | 0 | 0 |  | COO11 | Car crashed into pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/11/2016 20:25 |  |  | 4169 | Roadway |  | 20161115JEM_01 | Infrastructure (network-based) | -37.6318 | 144.8554 | 1 | Jemena | Report | 5205 | 0.022811 | 22kV AC | Melbourne Airport | 3059 | Greenvale | Vehicle
On arrival the faults crew conducted an NST test which failed registering 1.5 Ohms on the neutral, and 2.2 Volts to an independent earth. The fault was tracked down to a corrosive joint in a junction box on pole 2811749 and a faulty grey twisted overhead service cable. The faulty joint was repaired and the service cable was replaced with anew XLPE type service cable. Tests conducted at numbers 60/64/66/68 Daly St, Dalyston, showed 0.2 Ohms on the neutral and 0 Volts to an independent earth. | 60 DALY STREET, DALYSTON VIC 3992 | 2811749 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 223481. A water board employee received an electric shock whilst in the process of applying a bonder to a water meter he was in the process of changing, He stopped work immediately and informed his supervisor who called the fault in to AusNet Services. Note by Glenn Davidfson: please note the attending AusNet Services' LEI has not provided the personal details of the plumber involved in this incident. | Service conductor;Connection box | 0 | 0 | 0 |  | wgl23 | Corrosive joint in pole junction box and faulty grey twisted overhead service cable. | Minor shock | 42498.5417 |  |  | 4166 | Residential |  | 20161115SPN_01 | Infrastructure (network-based) | -38.5619 | 145.5458 | 1 | AusNet Services Distribution | Report | 5201 | 0.023097 | Low voltage AC (<1kV) | Moorabbin Airport | 3992 | Dalyston | Connection
Restored supply to Melbourne Airport. | 56-58 SOUTH CENTRE ROAD, MELBOURNE AIRPORT VIC 3045 |  |  |  | Likely |  | Ineffective planning/procedures/processes |  | 2 | On Wednesday 16th November 2016 at approximately 15:52:32 hours (3:52pm) the following occurred on the Jemena Electricity Network (JEN): a) Supply to the following customers from JEN was interrupted for approximately 17 seconds: * Loss of supply to approximately 9200 customers of the number 1 (#1) 22kv bus at Airport West (AW) Zone Substation via the attached 22kv distribution feeders (6 feeders in total) * Loss of supply to the number 1 (#1) and number 3 (#3) 22kv buses at Melbourne Airport Zone Substation (MAT). As the customer numbers and configuration exiting the MAT are unknown to the investigator at this time the impact to this installation is currently not determined b) Supply was restored from JEN at 15:52:49 by a Network Controller in the Jemena Network Control Room (567 Collins St). | No failed asset | 0 | 2 | 2 |  |  | EXECUTIVE SUMMARY On Wednesday 16th November 2016 at approximately 15:52:32 hours (3:52pm) the following occurred on the Jemena Electricity Network (JEN): a) Supply to the following customers from JEN was interrupted for approximately 17 seconds: ? Loss of supply to approximately 9200 customers of the number 1 (#1) 22kv bus at Airport West (AW) Zone Substation via the attached 22kv distribution feeders (6 feeders in total) ? Loss of supply to the number 1 (#1) and number 3 (#3) 22kv buses at Melbourne Airport Zone Substation (MAT). As the customer numbers and configuration exiting the MAT are unknown to the investigator at this time the impact to this installation is currently not determined b) Supply was restored from JEN at 15:52:49 by a Network Controller in the Jemena Network Control Room (567 Collins St). 2 WHAT HAPPENED AND WHEN Investigations to date have confirmed the following: a) Two planned 66kv Sub transmission interruptions involving associated apparatus were scheduled on the Keilor Terminal Station â€“ Tullamarine Z/S â€“ Melbourne Airport Z/S Airport West Z/S â€“ Pascoe Vale Z/S 66kv Loop (i.e. the KTS â€“ TMA â€“ MAT â€“ AW â€“ PV LOOP). b) The first interruption relates to work at AW. The work was planned to occur on Wednesday 16th Nov 16. c) The second interruption relates to work at MAT. The work was planned to occur between Monday 7th Nov 16 to Fri 11th Nov 16. The work actually occurred on Wednesday 16th November. d) At 15:52:24 hours as part of planned switching involving the restoration of the number 1 â€“ 66/22kv transformer at AW, a controller located at 567 Collins St, Melbourne performed the following steps associated with AW: 15:52:24 â€“ Opened the #1 -#2 66KV B/T CB 15:52:32 â€“ Opened the #4 -#1 66KV B/T CB e) The following supplies were interrupted for 17 seconds: ? Loss of supply to approximately 9200 customers of the number 1 (#1) 22kv bus at Airport West (AW)Zone Substation via the attached 22kv distribution feeders (6 feeders in total) ? Loss of supply to the number 1 (#1) and number 3 (#3) 22kv buses at MAT. As Melbourne Airport owns and controls the 22kv switch room at MAT and the associated 22kv Distribution Network (including its configuration, orientation and interface with generation capability), the full impact to Melbourne Airport cannot be determined. Further inquiries will be made with Melbourne Airportâ€™s network controllers. f) Upon detecting the interruption to supply the controller immediately closed the #4 - #1 66kv | Loss of supply | 16/11/2016 15:52 |  |  | 4182 | Industrial |  | 20161118JEM_01 | Infrastructure (network-based) | -37.693 | 144.8564 | 1 | Jemena | Report | 5369 | 0.010581 | 66kV AC | Melbourne Airport | 3045 | Melbourne Airport | AF Other
On arrival crew carried out repairs | 283 RYRIE STREET, GEELONG VIC 3220 | 32076201 |  | Blown branch/vegetation |  |  |  |  | 2 | Vicfire called to report sparking wires caused a Vegetation fire at the incident location. Powercor crew found a tree branch had fallen on a 2 wire lighting circuit causing it to spark which ignited a shrub near the line. | Service conductor | 2 | 2 | 2 |  | GCY012 | Vegetation: Trees Incident | Other vegetation | 21/11/2016 17:30 | 1 | Localised: less than 10 sq.m | 4196 | Residential |  | 20161122PWA_03 | Infrastructure (network-based) | -38.1508 | 144.3656 | 1 | Powercor | Report | 5526 | 0.023154 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Geelong | Trees
The crew isolated the Gerrard S/L at Tee pole 6 and repaired the 3/12 conductor. | 25 ONDIT-WARRION ROAD, ONDIT VIC 3249 | 30050973 |  | Blown branch/vegetation |  |  |  |  | 1 | The property owner reported a blown fuse and the line on the ground at the incident location. A crew attended and found 1 phase of a Single phase HV line on the ground and 1 HV fuse at the Tee Off blown. A tree branch had fallen into the conductor and broke the conductor approx. 10m from substation. The 10m length of conductor hanging from the substation pole remained alive thru back feed from the transformer. The end of the live conductor came into contact with a portion of old wire fencing causing arcing resulting in a grass fire of approx. 1m/sq. The fire had self-extinguished by the time the crew had arrived. No CFA attended. No shocks, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CLC003 | Vegetation: Trees Incident | Loss of supply;Grassfire | 25/11/2016 10:40 | 1 | Localised: less than 10 sq.m | 4221 | Agricultural |  | 20161128PWA_01 | Infrastructure (network-based) | -38.2517 | 143.6286 | 1 | Powercor | Report | 5275 | 0.0026169 | 22kV AC | Ballarat Aerodrome | 3249 | Ondit | Trees
On arrival crew isolated line for repairs | 16 KENNY ROAD, HORSHAM VIC 3400 | 33052548 | Working too close to overhead lines | [5 empty] | 1 | Operations received system advise of a lock out of a 22kV feeder CB at the Horsham ZSS. A customer rang to advise an excavator had struck the overhead line at the above incident location. The attending crew found an excavator had struck the footpath side HV conductor. There was a grass fire of approx. 1msq at the base of the excavator. No CFA attended. No shocks, injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | HSM002 | Excavator working too close to line | Loss of supply;Grassfire;No Go Zone (contact) | 28/11/2016 8:10 | 1 | Localised: less than 10 sq.m | 4223 | Roadway |  | 20161128PWA_03 | Infrastructure (network-based) | -36.7407 | 142.2024 | 1 | Powercor | Report | 5277 | 0.013036 | 22kV AC | Horsham Aerodrome | 3400 | Horsham | Vehicle
On arrival crew commenced repairs | 19 CEDMAR AVENUE, HIGHTON VIC 3216 | 30317819 | Working too close to overhead lines | [5 empty] | 2 | A gardener contacted a 2x25mm LVABC service with a hedge trimmer and cut through the LV neutral. The crew found that the neutral was cut but the service remained in the air. The gardener also mention he had seen the Telstra service but not the electrical service as it was obscured by the tree he was trimming. No injuries or ground fire. | Service conductor | 2 | 2 | 2 |  | WPD033 | vegetation trimming | No Go Zone (contact);Damage to network assets | 19/11/2016 11:53 |  |  | 4226 | Residential |  | 20161129PWA_01 | Infrastructure (network-based) | -38.1786 | 144.3126 | 1 | Powercor | Report | 5284 | 0.0049213 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Other
On arrival crew commenced repairs and issued a defect notice for repairs required to POA | 76 WILLIAM STREET, ST ALBANS VIC 3021 | 30231058 | Working too close to overhead lines | [5 empty] | 2 | A builder informed a service cable brought down by his excavator at the incident location. Upon arrival the crew found the cable pulled from the POA and it was lying on the ground. This is a residential construction site and the service wire runs over the boundary line. There were no reported injuries or fire | Service conductor | 2 | 2 | 2 |  | SA012 | Operation of excavator to close to service line | Loss of supply;No Go Zone (contact) | 21/11/2016 7:30 |  |  | 4228 | Residential |  | 20161129PWA_02 | Infrastructure (network-based) | -37.7373 | 144.8156 | 1 | Powercor | Report | 5286 | 0.030509 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
On arrival crew commenced repairs | 87 CLARENCE STREET, GEELONG WEST VIC 3218 | 32084244 |  | Lightning |  |  |  |  | 1 | Vicfire called to report wire down and across car at the incident location. Powercor crew found a HV conductor had snapped 1m from pole and fallen to ground. Scratch marks were found on 2 vehicles. There was no fire or injuries | Conductor (bare) | 2 | 2 | 2 |  | GL022 | Lightning strike | Loss of supply;Damage to network assets | 21/11/2016 17:47 |  |  | 4229 | Roadway |  | 20161129PWA_03 | Infrastructure (network-based) | -38.1392 | 144.3413 | 1 | Powercor | Report | 5287 | 0.0086308 | 22kV AC | Avalon Airport | 3218 | Geelong West | Lightning
Site secured | 242-254 ST ALBANS ROAD, BREAKWATER VIC 3219 |  | Copper theft | [5 empty] | 2 | Project manager Rohan Kent reported to the on call operator Andre Willis that there had been a break-in at GLE Zone Substation. A ductor along with the station earths (Flexible detachable earths) were removed from GLE ZSS. These were transported from GLE ZSS by a trolley and wheel barrow, the trolley and wheel barrow were recovered down the street. Rohan Burgess (Project Leader) informed Police of the break-in. The estimated the costs to replace the stolen equipment would be around $4,000. The site was made safe and repairs were made to secure the ZSS. There were no reported injuries or other third party damage. | Zone substation | 2 | 2 | 2 |  |  | Break in | Less than $50k damage | 13/11/2016 22:15 |  |  | 4239 | Commercial |  | 20161201PWA_02 | Infrastructure (network-based) | -38.1796 | 144.3817 | 1 | Powercor | Report | 5305 | 0.015788 | Earthing cable | Avalon Airport | 3219 | Breakwater | Other
on arrival crew carried out repairs | 48 HIGH STREET, EAGLEHAWK VIC 3556 | 30223654 |  |  |  | Overheated connection |  |  | 2 | CFA, reported street light lantern on fire Corner Victoria Street & High Street, Eaglehawk outside 48-48A High Street. When crew arrived onsite the fire had extinguished and CFA no longer present. The 150W HP Sodium lantern had burnt internally and required replacement. There was no ground fire, no reported property damage or reported injuries. | Public lighting | 2 | 2 | 2 |  | EHK031 | Burnt out lantern | Pole-top fire;Damage to network assets | 19/11/2016 20:43 | 1 | Negligible: no ground fire | 4240 | Roadway |  | 20161201PWA_03 | Infrastructure (network-based) | -36.7187 | 144.2533 | 1 | Powercor | Report | 5306 | 0.037463 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Eaglehawk | AF Other
On arrival crew isolated supply and commenced repairs | 326 PINKS ROAD, JEFFCOTT NORTH VIC 3480 | 32016398 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customer reported that he had made contact with SWER line with Tractor Forks with big bales on dropping cable off 2 poles in the paddock. SWER cable across paddock dislodged off pole # 5 and Pole # 6 of the Corack East SWER Spur. No ground fire, no reported property damage, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CTN006 | Farmer moving hay bales | Loss of supply;No Go Zone (contact) | 20/11/2016 11:49 |  |  | 4242 | Agricultural |  | 20161201PWA_04 | Infrastructure (network-based) | -36.2698 | 143.0978 | 1 | Powercor | Report | 5308 | 0.016907 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3480 | Jeffcott North | Other
CEOT dispatched a fault crew to isolate supply, make safe, investigate and repair. The cable was isolated at Switch BW3574. A Downer underground crew completed the necessary repairs by installing 2 x HV straight joints. The crew replaced 6 metres of 185 sq.mm HV XLPE underground cable. | 191 RIX ROAD, OFFICER VIC 3809 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 225583. IMS 225583. Steve from "streetworks" advised the CEOT that whilst they were excavating for road works they had dug up an underground cable in the street outside 191 Rix Rd, Officer. Steve's mobile number is 0419 872882. The excavator had hit an underground HV cable. Feeder protection tripped. | Cable | 0 | 0 | 0 |  | ofr21 | A roads contractor hit an underground HV cable. | Loss of supply;No Go Zone (contact) | 42412.5729 |  |  | 4252 | Roadway |  | 20161205SPN_03 | Infrastructure (network-based) | -38.0659 | 145.3866 | 1 | AusNet Services Distribution | Report | 5330 | 0.020736 | 22kV AC | Moorabbin Airport | 3809 | Officer | Dug up
On arrival crew commenced repairs | GELLIBRAND-CARLISLE ROAD, CARLISLE RIVER VIC 3239 | 32064661 |  |  |  | Leakage |  |  | 2 | An employee doing a line condition audit found a crossarm had caught fire and self-extinguished at the incident location some time previous to the audit. The crossarm was listed as a P1 item and changed later that evening. There was no ground fire. No third party damage or injury was reported. | Crossarm (wood) | 2 | 2 | 2 |  | CLC006 | Electrical leakage current | Pole-top fire | 24/11/2016 15:12 | 1 | Negligible: no ground fire | 4255 | Forest - native (not park) |  | 20161206PWA_01 | Infrastructure (network-based) | -38.5466 | 143.5057 | 1 | Powercor | Report | 5336 | 0.016794 | 22kV AC | Ballarat Aerodrome | 3239 | Carlisle River | Crossarm
On arrival crew commenced repairs. LEI engaged to check HVI. | 180 WILSONS ROAD, WHITTINGTON VIC 3219 | 30146519 | Vehicle | [5 empty] | 1 | Powercor began receiving calls from customers, and the fire authority, advising of a power outage and wires down due to a truck hitting overhead line. The field crew attending incident site, found that a truck had hit a cable TV line. The field crew advised that the cable TV catenary wire snapped and contacted HV and LV wires, resulting in a High Voltage Injection affecting approximately 15 installations. HV and LV Protection operated. Matt (Incident LEI) advised there was mostly appliance damage to all affected properties, all meters were replaced. Approximately 5 street lights required replacement the following day. There was no ground fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | GLE024 | Truck hit cable TV cable | HV injection;Loss of supply | 42441.6375 |  |  | 4256 | Roadway |  | 20161206PWA_02 | Infrastructure (network-based) | -38.1756 | 144.3903 | 1 | Powercor | Report | 5339 | 0.01799 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3219 | Whittington | Vehicle
The LV supply was isolated and bonded and the Geiger crew contacted their supervisor to report the incident. A new Electrical Access Permit was issued for access to the high and low voltage conductors and an investigation commenced. | 29 DALGETY STREET, OAKLEIGH VIC 3166 |  |  |  |  | Conductor clashing;Not built/maintained to design | Poor workmanship |  | 1 | Planned work for Geiger to convert an existing high voltage intermediate crossarm to a new high voltage strain crossarm for a new Manual Gas Switch. A Geiger construction crew were working for ZNX for planned work under Access Authority conditions on the 11kV overhead conductors in Dalgety Street east of Drummond Street, Oakleigh. At approximately 10.52AM, customers supplied from "Drummond-Dandenong", "Allan-Warrigal", "Warrigal 808-Dalgetty" and "Warrigal P2N-Camira" substations that were under LV parallel for the planned work. This has resulted in a loss of supply to customers for approximately three hours. The initial investigation found that while undertaking work to replace a HV intermediate cross arm to a strain cross arm under an Electrical Access Permit conditions, a Geiger work crew have installed the incorrect helical termination to secure the HV conductor to the new strain insulator. This has resulted in the HV conductor slipping through the helical termination when it was cut and made contact with the live LV blue phase conductor below. - LV 400amp HRC fuse operated causing a supply failure on the blue phase - HV conductor remained clear of the ground due to it having been attached to the on-site earth and short circuit - HV earth tail was connected to the neutral conductor of a CMEN system - No injuries or damage was sustained | Helical termination;Conductor (bare);Crossarm (steel);Aluminium;Other | 0 | 0 | 0 |  | OAK 25 | Geiger contract work crew have installed the incorrect helical termination to secure the HV conductor to the new strain insulator. | Loss of supply | 42412.4528 |  |  | 4278 | Roadway |  | 20161212UTD_01 | Infrastructure (network-based) | -37.8919 | 145.0922 | 1 | United Energy Distribution | Report | 5433 | 0.036934 | 11kV AC | Moorabbin Airport | 3166 | Oakleigh | Other
On arrival crew isolated supply and carried out repairs to HV bridge | 62 SEMPLES ROAD, MCMILLANS VIC 3568 | 32035769 |  |  |  | Overheated connection |  |  | 2 | Vic Fire reported a pole fire at the incident location. On arrival the crew found a HV bridge on centre phase had ruptured. There was a ground fire of some 30 by 200 metres. No injuries reported. There was some third party property damage to customer fence, hay bales and paddock stubble. | Dropper/bridge | 2 | 2 | 2 |  | CHA006 | Lead/Connection failure | Loss of supply;Less than $50k damage;Grassfire | 42716.7049 | 1 | Medium: 1000 sq.m - 10 ha | 4281 | Roadway |  | 20161213PWA_01 | Infrastructure (network-based) | -35.8538 | 144.1412 | 1 | Powercor | Report | 5378 | 0.0026806 | 22kV AC | Swan Hill Aerodrome | 3568 | Mcmillans | Connection
CFA were on-site and they extinguished the small ground fire. CEOT dispatched a fault crew to isolate supply, make safe and repair. The crew isolated supply, made the situation safe and fixed the stay wire. CEOT advised the DAO to attend and prepare a fire report. No one was injured. Stay wire helical termination was replaced and conductors re-sagged and supply restored. | 100 CHURCHILL ROAD, NEWHAVEN VIC 3925 | 2800945 |  |  |  | Corrosion |  | Phase to earth |  | IMS 225705. Corroded stay wire helical termination failed at ground level on HV anchor pole (with single phase transformer) and flicked into HV droppers of transformer becoming alive on ground where a small fire occurred. A thin strip of ground (grass fire) burnt approx. 2 metres long 300mm wide consistent with the tail of the stay wire. CFA attended and fire was extinguished | Guy wire | 0 | 0 | 0 |  | wgi31 | Corroded stay wire helical termination failed at ground level on HV anchor pole (with single phase transformer) and flicked into HV droppers of transformer, becoming alive on ground where small fire occurred. | Grassfire | 42625.3507 | 1 | Localised: less than 10 sq.m | 4291 |  |  | 20161216SPN_01 | Infrastructure (network-based) | -38.5105 | 145.3294 | 1 | AusNet Services Distribution | Report | 5400 | 0.031734 | 22kV AC | Moorabbin Airport | 3925 | Newhaven | AF Other
On arrival crew inspected conduit and made permanent repairs to conduit. No cable damage found. | 30 HOPETOUN ROAD, TOORAK VIC 3142 | 30218217 | Working too close to underground cables | [5 empty] | 2 | A contractor to the water utility reported UG cable dug up while excavating but no damage to the cable at the incident location. Upon arrival, the Powercor crew noticed that the UG conduit had been slightly damaged. There were no injuries or other damage. | Cable | 2 | 2 | 2 |  | AR003 | Digging to close to underground cable | No Go Zone (no contact);Damage to network assets | 42533.3271 |  |  | 4296 | Roadway |  | 20161219PWA_02 | Infrastructure (network-based) | -37.8481 | 145.0284 | 1 | CitiPower | Report | 7993 | 0.03789 | 11kV AC | Moorabbin Airport | 3142 | Toorak | Dug up
On arrival crew carried out repairs | 1-5 CANTERBURY STREET, DEER PARK VIC 3023 | 32163591 | Copper theft | [5 empty] | 2 | Powercor employee, Mick Muldoon, advised of copper theft on substation pole at corner of Canterbury St and Station Rd., Deer Park. No protection operated. There were no reported injuries or ground fire start. | Earth/earthing | 2 | 2 | 2 |  | SU021 | Theft of earthing | Damage to network assets | 42533.9424 |  |  | 4298 | Commercial |  | 20161219PWA_03 | Infrastructure (network-based) | -37.7713 | 144.7738 | 1 | Powercor | Report | 5409 | 0.020813 | Earthing cable | Laverton Raaf | 3023 | Deer Park | Other
Voltage tests between an independent earth and various points round the pole found voltage of 235volts. Service truck disconnected public lighting service in pit. The installation was tested by the CTA and zero volts were recorded | 49 STONY BROOK WAY, TRUGANINA VIC 3029 | 30257318 |  |  |  | Electrical breakdown |  | Phase to earth | 2 | Mr maccallun was learning again pole when he made simultaneous contact between his hand on the public lighting pole o/s 49 stony brook way and the wet ground when he received an electric shock. There was no fire or other third party property damage. | Services cable;Public lighting;Pole (steel) | 2 | 2 | 2 |  | LV003 | Damaged underground P/L cable in service cable pit. | Minor shock | 24/10/2016 8:55 |  |  | 4299 | Roadway |  | 20161219PWA_04 | Infrastructure (network-based) | -37.84 | 144.7152 | 1 | Powercor | Report | 12414 | 0.038978 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | UG Cable
CEOT dispatched a fault crew to isolate, make safe and repair. CEOT also dispatched the DAO. Made safe and carried out necessary repairs to the SWER line. | 285 SINCLAIRS ROAD, MUNRO VIC 3862 | 2512255 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | IMS 225833. A tree fell into a SWER conductor bringing the conductor to the ground and allegedly starting a grass fire. ACR reclosed a number of times then went to lockout. The following report is by the local DAO who attended the incident scene: At 4:01pm on Saturday 17/12/16, I was called by the AusNet Services' CEOT to go to 285 Sinclairs Rd, Munro, to investigate a pole fire. I was advised that a conductor was down between Pole #2512252 and Pole #2512255 on the SWER Sinclair Spur, and that linesmen had been called out to repair the line. I arrived at the site at approximately 6:00pm. Maximum wind speed on the day was 94km at 13:32 in a WSW direction. By the time I arrived the fire had been extinguished and the linesmen were preparing to rectify the line. The Fire Brigade had left the site. The fire had burnt an area of approximately 25m x 5m. A tree branch was on the ground underneath where the conductor had been dislodged. The base of the tree was approximately 9m from the conductor. | Conductor (bare) | 0 | 0 | 0 |  | mfa21 | Vegetation: Trees Incident | Grassfire | 16/12/2016 15:55 | 1 | Localised: less than 10 sq.m | 4294 | Agricultural |  | 20161219SPN_01 | Infrastructure (network-based) | -37.9052 | 147.216 | 1 | AusNet Services Distribution | Report | 5404 | 0.025109 | 12.7kV AC (SWER) | Bairnsdale Airport | 3862 | Munro | Trees
CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. The site was made safe, the loose LV connection was repaired and supply restored. The work crew re-connected the underground cable conductors to the Krone box (FSD). | 555 COSTER ROAD, RIPPLEBROOK VIC 3818 | 2702476 |  |  |  | Age |  | Phase to earth | 2 | IMS 225834. Hot metal from a loose LV connection on the pole supplying an underground cable appeared to have fallen to the ground. A 8m x 7m ground fire was observed in the vicinity. No other damage. | Connection box | 0 | 0 | 0 |  | wgl13 | Loose LV connection. | Grassfire | 17/12/2016 21:35 | 1 | Small: 10 - 1000 sq.m | 4295 | Agricultural |  | 20161219SPN_02 | Infrastructure (network-based) | -38.1826 | 145.7814 | 1 | AusNet Services Distribution | Report | 5407 | 0.031514 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3818 | Ripplebrook | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions prior to the supply being restored. | EMERALD DRIVE, SPRINGVALE VIC 3171 | 202366 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 1 | At 8.56AM on 09/12/2016, 22kV feeder SS 13 circuit breaker successfully reclosed and held. During cool morning conditions, a pole fire occurred at the HV/LV tee-off pole to "Olinda-Emerald" substation in Olinda Avenue on the corner of Emerald Drive, Springvale. There was small metal debris found on the HV crossarm, possibly attributed to a bird nesting. The HV tee-off crossarm was burnt off at the crossarm strap and burnt the pole near the LV crossarm kingbolt severely enough to warrant the replacement of pole No. LIS 0613176. | Pole (wood);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | SS 13 | Pole fire - 22kV grey insulators. | Pole-top fire | 42625.3722 | 1 | Negligible: no ground fire | 4310 | Residential |  | 20161220UTD_02 | Infrastructure (network-based) | -37.9582 | 145.1446 | 1 | United Energy Distribution | Report | 5425 | 0.032155 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Animal
Emergency high voltage switching was completed and a short interruption was required to allow the isolation of the sparking HV conductor on the ground in South Boundary Road east of FS0648 spur fuses. The RCGS was opened and closed by SCADA to allow isolation of the fault. A HV intermediate crossarm was replaced under Access Authority conditions and supply restored when the Electrical Access Permit was relinquished. | 1 SOUTH BOUNDARY ROAD E, SOMERVILLE VIC 3912 | 9866573 |  |  |  | Fatigue;Electrical breakdown |  |  | 2 | CFA advise of wires down and there is a grass fire. Business name: Hussey and Co P/L have lost their power and can see a powerline down in the front of the factory. Two HV conductors were down and still sparking when the fault crew arrived on site with burn marks on the ground (0.5sqm) but not enough to start a grass fire. - The centre phase HV conductor was on the ground in South Boundary Road east of FS0648 spur fuses. There was pitting evident on the ampact and the 3/12 steel conductor inside burnt away. - a second HV conductor was down in the bay west of FS7919 spur fusing in South Boundary Road that appeared to have burnt through a splice. No HVI or fire damage occurred at this location. | Conductor (bare) | 0 | 0 | 0 |  | HGS 33 | Ampact connection failure and conductor splice burnt through. | Grassfire | 42441.3778 | 1 | Negligible: no ground fire | 4314 | Roadway |  | 20161221UTD_01 | Infrastructure (network-based) | -38.2223 | 145.2445 | 1 | United Energy Distribution | Report | 5431 | 0.0070706 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the tree was cut clear of the HV conductors prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 9 HOWLEYS ROAD, NOTTING HILL VIC 3168 |  |  | Wind;Fallen |  | Conductor clashing;HV injection |  |  | 1 | At 1133hrs on 13/12/2016, 22kV feeder NO 06 circuit breaker reclosed to lockout affecting 724 customers. A tree located between 9-11 Howleys Road, Notting Hill has fallen and contacted the HV and LV conductors. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Howleys N21-FTG" substation. The LEI confirmed a high voltage injection occurred (BWD 1608) affecting 4 customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | NO 06 | Vegetation: Trees Incident | HV injection;Loss of supply | 13/12/2016 11:33 |  |  | 4317 | Roadway |  | 20161221UTD_03 | Infrastructure (network-based) | -37.9016 | 145.138 | 1 | United Energy Distribution | Report | 5435 | 0.039795 | 22kV AC | Moorabbin Airport | 3168 | Notting Hill | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the Reticulation Pole Top Connection Box and completed an NST test which confirmed a Pass result. | 47 HERTFORD STREET, SEBASTOPOL VIC 3356 | 32002719 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Glen Hope was in the Kitchen when he received an electric shock as he made simultaneous contact with one hand while operating the metal taps and his other hand in contact with the metallic sink. | Connection box | 2 | 2 | 2 |  | BAS034 | Corroded O/H Service Neutral Conductor termination | Minor shock | 29/10/2016 20:00 |  |  | 4329 | Roadway |  | 20161222PWA_04 | Infrastructure (network-based) | -37.5862 | 143.8352 | 1 | Powercor | Report | 5448 | 0.026721 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Sebastopol | Connection
On arrival crew commenced repairs LEI dispatched to check for HVI | 169 MCCALLUM STREET, SWAN HILL VIC 3585 | 32158617 | Vehicle | [5 empty] | 1 | Victorian Police reported a car has hit a pole and broken off at the ground, driver is still in the vehicle and wires are laying across the vehicle. Driver was not badly injured and transported to hospital. There was no fire. Brick rendered fence damaged by car and RFD stake around pole. There was potentially property damage due to HV injection. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SHL008 | Vehicle collision with pole. | HV injection;Loss of supply;Significant disruption to the community | 21/12/2016 22:54 |  |  | 4333 | Roadway |  | 20161223PWA_01 | Infrastructure (network-based) | -35.3409 | 143.545 | 1 | Powercor | Report | 5453 | 0.010631 | Low voltage AC (<1kV);22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Vehicle
The faults crew made the site safe and replaced the damaged IPC that supplied a three phase underground cable to the Sunny Ridge Strawberry Farm. Installation tests were completed and supply was left on. | 244 SHANDS ROAD, MAIN RIDGE VIC 3928 | 1313961 |  |  |  | Electrical breakdown;Overheated connection |  |  | 2 | Caller has lost their electricity supply and the Fire Brigade are at a pole outside the cafÃ© at Strawberry Farm. The local fire authority advised of a sparking fuse at a pole in Shands Road. A customer supplied from the blue phase conductor from "Mtn Flind P19 - Shand" substation advised of a power outage and the CFA are in attendance for a pole fire that caused a 1sqm grass fire at the base of pole number LIS 1313961. The cause was a low voltage IPC for an underground cable that failed causing molten metal and sparks to fall into the dry grass. | Connector/termination | 0 | 0 | 0 |  |  | The cause was a probable loose low voltage IPC for an LV underground cable. | Grassfire | 24/12/2016 12:10 | 1 | Localised: less than 10 sq.m | 4344 | Roadway |  | 20161228UTD_04 | Infrastructure (network-based) | -38.4012 | 144.9927 | 1 | United Energy Distribution | Report | 5533 | 0.018653 | Low voltage AC (<1kV) | Moorabbin Airport | 3928 | Main Ridge | Connection
Site was attended by MFB to extinguish the grass fire and a Jemena Network Operator made the site safe by isolating section of conductor. Additionally, a faults crew undertook repairs on the night of the incident to replace the faulted section of conductor. | 275 MAHONEYS ROAD, RESERVOIR VIC 3073 | Pole no. A035962 |  | Bird |  | Overheated connection |  |  | 1 | HV conductor down on ground opposite 275 Mahoneys Rd Reservoir, causing a grass fire approximately 600sqm which was attended by the MFB. JEN fault crew attended and made site safe. | Conductor (bare) | 0 | 0 | 0 |  | CN06 | Bird Incident | Grassfire | 28/12/2016 20:09 | 1 | Small: 10 - 1000 sq.m | 4358 | Industrial |  | 20161229JEM_02 | Infrastructure (network-based) | -37.691 | 144.9754 | 1 | Jemena | Report | 12381 | 0.0011713 | 22kV AC | Essendon Airport | 3073 | Reservoir | Animal
On arrival crew commenced repairs | 115 HENDRYS LANE, BRIDGEWATER VIC 3516 | 32039847 |  | Blown branch/vegetation |  |  |  |  | 1 | VicFire reported wire down and ground fire at the incident location. On arrival the crew found that large tree branch had come away from a tree outside the clearance space and fallen onto 1 phase of the 3 phase 22kV line, breaking the conductor and commencing a ground fire. A ground fire of approximately 120Ha resulted, an estimated 300>600M of fencing was burnt to varying degrees and 2 farm sheds also damaged by the fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BET001 | Vegetation: Trees Incident | Grassfire | 24/12/2016 15:11 | 1 | Large: more than 10 ha | 4348 | Agricultural |  | 20161229PWA_03 | Infrastructure (network-based) | -36.6664 | 143.9149 | 1 | Powercor | Report | 12416 | 0.0085961 | 22kV AC | Bendigo Airport | 3516 | Bridgewater | Trees
On arrival crew commenced repairs. | MALLEE HIGHWAY, LINGA Vic 3509 | 32139791 |  | Wind;Fallen |  |  |  |  | 1 | VicFire reported wire down and ground fire at the incident location (Mallee Highway, approximately 6km west of Underbool). On arrival the crew found that a tree had fallen over in high winds from outside the clearance space onto 1 phase of the 3 phase 22kV line, breaking the insulator, dislodging the conductor which fell to the ground and commenced a ground fire. There were no reported injuries or 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | OYN001 | Vegetation: Trees Incident | Loss of supply;Grassfire | 28/12/2016 8:35 | 1 | Medium: 1000 sq.m - 10 ha | 4349 | Roadway |  | 20161229PWA_04 | Infrastructure (network-based) | -35.1664 | 141.7415 | 1 | Powercor | Report | 12417 | 0.027731 | 22kV AC | Mildura Airport | 3509 |  | Trees
On arrival crew commenced repairs. LEI Despatched | 170 THIRTEENTH STREET, MILDURA VIC 3500 | 32140356 |  | Blown branch/vegetation |  |  |  |  | 1 | Customers reported damage at their installations at the incident location. On arrival the crew found that a council tree positioned in the road centre had lost a branch in high winds, the branch fell over 22kV conductors between P22 & P23 and caused HV conductor to make contact with the red phase LV conductor ex â€œ13th Poplar 35â€ 200kVA substation. Damage at 20 installations connected to the red phase of varying degrees resulted from this HV injection. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | MDA022 | Vegetation: Trees Incident | HV injection;Loss of supply | 28/12/2016 5:03 |  |  | 4350 | Roadway |  | 20161229PWA_05 | Infrastructure (network-based) | -34.1893 | 142.1499 | 1 | Powercor | Report | 12418 | 0.018385 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3500 | Mildura | Trees
On arrival crew commenced repairs. | 13 TINWORTH AVENUE, MOUNT CLEAR VIC 3350 | 32010016 |  |  |  | Leakage |  |  | 2 | A Powercor employee reported a pole fire at the incident location. On arrival the crew found that a three phase 22kV wooden cross arm had burnt through at a cross arm strap position. There was no ground fire or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | BAS013 | excessive leakage current | Pole-top fire | 25/12/2016 12:50 | 1 | Negligible: no ground fire | 4352 | Roadway |  | 20161229PWA_06 | Infrastructure (network-based) | -37.5921 | 143.8657 | 1 | Powercor | Report | 5475 | 0.031492 | 22kV AC | Ballarat Aerodrome | 3350 | Mount Clear | Crossarm
On arrival crew removed vegetation and carried out repairs | 945 KIOTA ROAD, DHURRINGILE VIC 3610 | 32191788 |  | Wind |  |  |  |  | 1 | The customer at the incident location reported that a tree had fallen over the overhead line. On arrival the crew found that at the incident location a tree branch had fallen across the conductors near P1 Dickenson Spur and bought them close to ground. Some soot ( arc proximity) was identified on the tree branch however no evidence of burning was found No injury and only minor third party damage was reported. | Conductor (bare) | 2 | 2 | 2 |  | MNA021 | During storm condition wind blew limb into line | Loss of supply;Grassfire | 29/12/2016 13:11 | 1 | Localised: less than 10 sq.m | 4368 | Agricultural |  | 20161230PWA_05 | Infrastructure (network-based) | -36.5139 | 145.2037 | 1 | Powercor | Report | 8383 | 0.03299 | 22kV AC | Shepparton Airport | 3610 | Dhurringile | Trees
On arrival crew carried out repairs to replace fuse box | 755 BLACKGATE ROAD, TORQUAY VIC 3228 | 33042148 |  |  |  | Overheated connection |  |  | 2 | Customer reported all supply fail at the incident location. On arrival the crew found an overheated fuse had melted through the box on the substation pole and fallen to the ground burning a small patch of grass. There was no injury or third party property damage. | Connection box | 0 | 0 | 2 |  | WPD022 | Unable to determine from remains of box due to extent of damage, overheated connection is probable | Loss of supply;Grassfire | 42736.7083 | 1 | Localised: less than 10 sq.m | 4377 | Agricultural |  | 20170103PWA_02 | Infrastructure (network-based) | -38.2903 | 144.3096 | 1 | Powercor | Report | 12421 | 0.038736 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Fuse
The crew isolated supply to the area and the pole and x-arm was replaced | 1253 HOWITT STREET, WENDOUREE VIC 3355 | 30014161 |  |  |  | Leakage |  |  | 2 | A call was received from the CFA that a pole was on fire at the incident location. On arrival the crew found that a Pole Fire had occurred on Lake Nth Howitt Pole 20. Leakage on the HV switch pole had caused damage to the pole where the LV X-arm attaches and burnt through the LV X-arm. The HV switch mounted on the pole was not earthed and it is assumed that leakage current from the HV tracked to the LV neutral conductor and then to earth. The was no ground fire, third party damage or injury. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BAN001 | excessive leakage current | Pole-top fire | 42767.3014 | 1 | Negligible: no ground fire | 4380 | Roadway |  | 20170103PWA_03 | Infrastructure (network-based) | -37.5399 | 143.8255 | 1 | Powercor | Report | 5509 | 0.032495 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3355 | Wendouree | Pole
On arrival crew isolated the damaged service wire , A REC undertook repairs repairs at the customers fascia. | 10 WILLIS STREET, WINCHELSEA VIC 3241 | 30054109 | Vehicle | [5 empty] | 2 | Fire authority report to PCA of a sparking wire on a car at the incident location. When crews arrived they confirmed that a broken service wire was on the road. The vehicle causing the damage was unable to be located, there was no other vehicle found in the area (CFA and Police were on site). No fire or injuries were reported. | Service conductor | 2 | 2 | 2 |  | WIN011 | Unknown vehicle struck service line | Loss of supply;Damage to network assets | 15/12/2016 20:10 |  |  | 5400 | Roadway |  | 20170109PWA_04 | Infrastructure (network-based) | -38.2398 | 143.9925 | 1 | Powercor | Report | 6558 | 0.017216 | Low voltage AC (<1kV) | Avalon Airport | 3241 | Winchelsea | Vehicle
AusNet Services' fault crew attended site and made safe. The fault crew assessed the condition of the HV conductors and nil damage was observed. The ANC crew was stood down. Supply restored exTN186F. An incident report was received from ANC Forestry. A new PTW was issued under NEMS 331224. AusNet Services' Customer & Community Managers met Michael Dent and Chris Barklay from HVP to discuss incident. Please refer to attached AusNet Services' HSE Incident Investigation Report for Remedial Actions recommendations. | 380 SNOWDENS ROAD, BOOLARRA SOUTH VIC 3870 | 2623127 |  | Within clearances |  |  | Not followed;Poor or no communication | Phase to earth | 1 | IMS 226242. ANC Forestry crew removing trees between poles 2623125 and 2623127 under Permit to Work 15398. Head of tree made contact with the 22kV overhead conductors as it was being machine felled. ACR TN186F Tripped to Lock out (A/R supressed under PTW). ANC crew was working under a PTW which was issued under NEMS app 329319 for the period 20/1/17 to 20/2/17. Crew made to apply for a new PTW which is due to be issued 17 Feb 2017 by Extec under NEMS app 331224. Contact with the powerline occurred as the head of the tree whipped around as it was cut and being slewed by the machine. Uncontrolled movement of the tree. Inability of spotter to clearly see the trees being handled and warn operator of impending contact with overhead line. Key Learning's and Root Causes: â€¢ Spotter task not performed adequately.â€¢ Communication of PTW conditions to new spotter who arrived on the day of the incident not completed. â€¢ PTW conditions lacking (conditions noted on NEMS adequate but should have been transposed onto PTW precautions. â€¢ Communication between spotter and operator insufficient in relation to risk assessment and positioning of harvester. â€¢ PTW not referenced in ANC incident investigation (may have been a contributing factor). â€¢ Actions associated with preventing a re-occurrence not detailed in incident investigation (provided later). | Conductor (bare) | 0 | 0 | 0 |  | mwts14 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 31/01/2017 11:25 |  |  | 5528 | Forest - plantation |  | 20170131SPN_01 | Infrastructure (network-based) | -38.4692 | 146.3058 | 1 | AusNet Services Distribution | Report | 12341 | 0.026479 | 22kV AC | Morwell (Latrobe Valley Airport) | 3870 | Boolarra South | Trees
Contractor reinstated pit and service cable. | 339 BOUNDARY ROAD, LANCEFIELD VIC 3435 | 33029473 | Copper theft | [5 empty] | 1 | Our contractor advised that a newly installed service pit had been stolen. Contractor also advised that the consumers underground cable had been stolen. Supply had not been connected. Customer had advised police , Ref # Police Incident number: 170030071. | Services cable;Services pit;Customer installation | 0 | 0 | 0 |  | WND013 | Interference - copper theft | Less than $50k damage;Damage to network assets | 30/01/2017 9:00 |  |  | 5531 | Agricultural |  | 20170201PWA_03 | Infrastructure (network-based) | -37.3142 | 144.7019 | 1 | Powercor | Report | 6753 | 0.036338 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3435 | Lancefield | Other
On arrival crew carried out repairs | 1105 BIRREGURRA-DEANS MARSH ROAD, WHOOREL VIC 3243 | 32065952 |  |  |  | Fuse failed to eject;Candled fuse |  |  | 0 | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries. | EDO fuse | 2 | 2 | 2 |  | WIN011 | EDO Fuse barrell did not drop out | Pole-top fire | 22/01/2017 1:41 | 1 | Negligible: no ground fire | 5533 | Roadway |  | 20170201PWA_05 | Infrastructure (network-based) | -38.3932 | 143.8481 | 1 | Powercor | Report | 6755 | 0.034215 | 22kV AC | Avalon Airport | 3243 | Whoorel | Fuse
MADE SAFE AND REPAIRS ARE BEING UNDERTAKEN. New transformer, LV isolation box and underground conductor required | 920 WILDWOOD ROAD, WILDWOOD VIC 3429 |  | Copper theft | [5 empty] | 2 | Underground conductor from LV bus fuse pit to LV pit was stolen Copper removed from pole without permission and damaged distribution substation Customer box damaged and customer mains stolen. Meter missing | Services cable;Pole mounted | 0 | 2 | 0 |  | SBY14 | Theft | Damage to network assets | 42768.4583 |  |  | 5545 | Roadway |  | 20170202JEM_01 | Infrastructure (network-based) | -37.5342 | 144.7989 | 1 | Jemena | Report | 12389 | 0.0088206 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Wildwood | Other
The faults crew installed a hopper over the connection to temporary restore supply to customers and returned later in the evening to complete the rectification work. | THIRD AVENUE, CHELSEA HEIGHTS VIC 3196 | 3306941 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | Customer advised that a pole caught on fire momentarily and caused a fire on the nature strip that was put out by blankets. The location is on the corner of Third and Ninth Avenue and the fire is now out. A LV ampact connection failed on the blue phase of west LV bus pole at "Ninth-Fourth" substation pole (LIS No. 3306941) that caused molten metal to fall onto the dry nature strip below and a small fire to start that was approximately 2sqm in size. Customers promptly extinguished the fire by the use of blankets and fire authorities were not required. The cause of the connection failure was unknown but was a probable loose overheated connection. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | CRM 35 | The cause of the connection failure was unknown but was a probable loose overheated connection. | Grassfire | 23/01/2017 19:00 | 1 | Localised: less than 10 sq.m | 5543 | Roadway |  | 20170202UTD_01 | Infrastructure (network-based) | -38.0439 | 145.1339 | 1 | United Energy Distribution | Report | 6767 | 0.011743 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea Heights | Connection
On arrival crew isolated supply and completed repairs. | 7 YARRA STREET, KEW VIC 3101 | 30165751 |  | Wind;Fallen;Property owner/customer |  |  |  |  | 2 | A customer reported that a large tree has fallen across power-lines. Wires are sparking on the ground at the incident location. On arrival the fault crew found that a large tree had broken low voltage conductors which were on the ground at the incident location. | Conductor (bare) | 2 | 2 | 2 |  | Q002 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42857.8153 |  |  | 5562 | Roadway |  | 20170206PWA_04 | Infrastructure (network-based) | -37.8038 | 145.022 | 1 | CitiPower | Report | 6792 | 0.0029572 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Trees
On arrival crew carried out repairs | 731 PARK STREET, BRUNSWICK VIC 3056 | 30182582 |  | Alive;MEC |  |  |  |  | 2 | A passer-by reported that a large tree branch broke off and has fallen across power-lines. Wires are sparking on the ground at the incident location. On arrival the fault crew found that a large tree branch had fallen onto the low voltage conductors and these had been damaged and were â€œALIVEâ€ on the ground at the incident location. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | VM004 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42857.8819 |  |  | 5563 | Public space |  | 20170206PWA_05 | Infrastructure (network-based) | -37.7776 | 144.958 | 1 | CitiPower | Report | 6793 | 0.016536 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and repairs were completed to the electrical infrastructure under electrical access permit conditions. Supply was restored upon completion. | 177 BRANDON PARK DRIVE, WHEELERS HILL VIC 3150 | 620680 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | A HV intermediate crossarm has snapped and fallen in close proximity to the LV conductors. During light drizzle, a pole fire occurred at the high voltage intermediate crossarm on pole No. LIS 0620680 located outside 177 Brandon Park Drive, Mulgrave. The crossarm fire occurred at the crossarm strap and the blue phase HV conductor fell in close proximity to the LV crossarm but a high voltage injection did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | MGE 22 | Probable tracking during light drizzle. | Pole-top fire | 42737.375 | 1 | Negligible: no ground fire | 5559 | Residential |  | 20170206UTD_03 | Infrastructure (network-based) | -37.917 | 145.1713 | 1 | United Energy Distribution | Report | 6787 | 0.033025 | 22kV AC | Moorabbin Airport | 3150 | Wheelers Hill | Crossarm
On arrival crew carried out repairs | 520 WERRIBEE VALE ROAD, MADDINGLEY VIC 3340 | 30102859 |  |  |  | Leakage |  |  | 1 | A field crew attending an outage found that a pole fire had occurred at the incident location. The pole fire resulted in the HV crossarm failing and debris set fire to grass at base of pole. | Crossarm (wood) | 2 | 2 | 2 |  | BMH003 | Excessive leakage current | Grassfire | 23/01/2017 14:55 | 1 | Localised: less than 10 sq.m | 5569 | Agricultural |  | 20170207PWA_01 | Infrastructure (network-based) | -37.6814 | 144.3792 | 1 | Powercor | Report | 6803 | 0.014384 | 22kV AC | Avalon Airport | 3340 | Maddingley | Crossarm
Optus contacted to attend site. Optus cable removed from red phase of LV conductor. Repairs made to LV conductor between poles A051060 and A051007. | 101 MICKLEHAM ROAD, TULLAMARINE VIC 3043 |  | Vehicle | [5 empty] | 2 | A truck hit has communications (Optus) cable, resulting in the Optus cable to wrap around red phase of LV conductor and causing a minor grass fire on median strip. No photo is available for this fire start incident. The delay in submitting this incident report is a result of recent work to populate the F-Factor Regulatory Information Notice (RIN) for the AER, during which we have identified several additional instances from our historical records which â€“ after further investigation â€“ now â€œmake the cutâ€ for fire start reporting. | Conductor (insulated);Communication cable/equipment | 0 | 0 | 0 |  | AW09 | Third party impact by truck on communications (Optus) cable resulted in the Optus cable to wrap around red phase of LV conductor | Grassfire;Other vegetation | 42617.5069 | 1 | Localised: less than 10 sq.m | 5586 | Residential |  | 20170210JEM_03 | Infrastructure (network-based) | -37.6961 | 144.8811 | 1 | Jemena | Report | 8423 | 0.023677 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Vehicle
A REC together with Powercor crews undertook the necessary repairs and cleaned the Meter Board and metering. Supply was restored to the customer. | 25 LORD STREET, PORT CAMPBELL VIC 3269 | 34031422 |  |  |  | Overheated connection |  |  | 2 | Powercor received a call from a take away food premises reporting â€œflames coming from main switch board at meter locationâ€. On arrival the crew found that a customer mains fuse holder (red phase) on the hinged composite meter board had overheated causing it to catch on fire. The CFA were in attendance and had discharged a fire extinguisher onto the meter board. There was no report of injuries, ground fire or other third party property damage . | Meter board (including fuses) | 2 | 2 | 2 |  | TRG003 | Overheated meter board fuse | Meter board | 28/01/2017 15:46 | 0 | Negligible: no ground fire | 5593 | Commercial |  | 20170213PWA_03 | Infrastructure (network-based) | -38.6198 | 142.9947 | 1 | Powercor | Report | 8430 | 0.021983 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Port Campbell | AF Other
On arrival crew carried out repairs | 3 CEDAR AVENUE, MILDURA VIC 3500 | 34004640 | Vehicle | [5 empty] | 2 | A passer-by informed a truck has pulled down a cable at the incident location. Upon arrival the crew found that the service cable lying on the ground. The truck was parked in the vicinity but no driver located. There were no injuries or fire. | Service conductor | 2 | 2 | 2 |  | MDA022 | Garbage truck struck service | Loss of supply | 30/01/2017 10:01 |  |  | 5596 | Roadway |  | 20170213PWA_05 | Infrastructure (network-based) | -34.1919 | 142.1586 | 1 | Powercor | Report | 6846 | 0.0087083 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Vehicle
on arrival crew carried out repairs | 1 IRAMOO CIRCUIT, ROCKBANK VIC 3335 | 30107842 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from a height of two metres up the pole to ground level. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Cable theft | Damage to network assets | 30/01/2017 16:49 |  |  | 5604 | Roadway |  | 20170214PWA_04 | Infrastructure (network-based) | -37.7298 | 144.6227 | 2 | Powercor | Report | 6854 | 0.0090463 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. AusNet Service's fault crew attended and removed the tree from the line. | THE PELICAN, 606 OXLEY FLATS ROAD, OXLEY FLATS VIC 3678 | 5110868 |  | Wind;Fallen |  |  |  |  | 1 | IMS 226337. Tree down over 22kV line near Oxley Flats Rd. Vic Roads 34 G8. AusNet Service's fault crew attended and removed the tree from the line. CFA extinguished a 100m X 30m fire on the ground in the vicinity. Two HV fuses operated. Negligible damage to network assets. | Conductor (bare) | 0 | 0 | 0 |  | wn5 | Vegetation: Trees Incident | Grassfire | 42949.6875 | 1 | Medium: 1000 sq.m - 10 ha | 5621 | Roadway |  | 20170215SPN_02 | Infrastructure (network-based) | -36.3901 | 146.3724 | 1 | AusNet Services Distribution | Report | 6877 | 0.012307 | 22kV AC | Wangaratta Aero | 3678 | Oxley Flats | Trees
Jemena crew was dispatched to the site immediately and the crew attended 23 Pascoe St, Pascoe Vale at 12.00pm, and found a real estate (Barry Plant) "for sale" sign on the top of a building at 23 Pascoe St. The sign had been put up within 50mm of overhead power lines. Jemena crew made the site safe by applying mechanical protection over the bare conductor which made contact with the real estate board and restored customer supply by replacing the fuse at the end of the mains circuit (315A blue phase fuse on west circuit out of PASCOE-WEST sub). Power was restored to shops which were off-supply by 12.30pm. Once customer supply was restored and site was made safe (including the putting up of spreaders and tigermats around the sign), Jemena crew contacted Barry Plant and notified them for the board to be removed immediately. The Jemena crew waited on site for Barry Plant service provider ABC Photosigns to attend and remove the sign with Jemena crew assistance (due to live conductors). | 23 PASCOE STREET, PASCOE VALE VIC 3044 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Thursday 16th of February 2017 at 11.12am, Jemena dispatch received a call from MFB reporting of an overhead bare conductor clashing with a real estate board that was mounted on a shop front (top of their veranda) and created an explosion sound from arcing against the metal board. | Conductor (bare) | 0 | 0 | 0 |  |  | Real estate agent 'for sale' board had been put up within 50mm of overhead power lines. | No Go Zone (no contact) | 16/02/2017 11:12 |  |  | 5630 | Commercial |  | 20170216JEM_01 | Infrastructure (network-based) | -37.7165 | 144.9344 | 1 | Jemena | Report | 6891 | 0.0018391 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
CEOT dispatched a fault crew to make safe, investigate and carry our necessary repairs. Crew isolated supply, made safe and replaced LV isolators. Supply restored. | 7-9 CADEL TERRACE, WAHGUNYAH VIC 3687 | 5207130 |  |  |  | Overheated connection |  |  | 2 | IMS 226441. Peter (tel 0417 442645) from North East Water advised AusNet Services of fire on a pole. It appears that a LV fused isolator on a substation pole overheated where the copper lead is attached to the isolator. Any hot material falling from the isolator may have still been alight when it hit the ground. The size of the grass fire (in green grass) was approximately 40 sq.m and it was extinguished by Peter. | Disconnector/isolator;Pole mounted | 0 | 0 | 0 |  | wn3 | LV isolator connection overheated. | Grassfire | 14/02/2017 15:15 | 1 | Small: 10 - 1000 sq.m | 5631 | Roadway |  | 20170216SPN_02 | Infrastructure (network-based) | -36.0075 | 146.3937 | 1 | AusNet Services Distribution | Report | 6893 | 0.0072199 | Low voltage AC (<1kV) | Wangaratta Aero | 3687 | Wahgunyah | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The crew attended and advised there was a grass fire in the vicinity of the pole. The remaining silage wrapping was removed from the from the HV conductors. The HV conductors were pulled up to correct sag. The fire was extinguished by the fire brigade. | 427 BACK BEACH ROAD, VENTNOR VIC 3922 | 2806401 | Blown detritus | Wind |  |  |  | Phase to phase | 1 | IMS 226461. Call received from Fire Brigade for sparking conductors. The local DAO attended & observed burnt grass in paddock in 2 areas of 20x60m & 20x10m. The burnt grass began under our HV OH conductors a third of span length from pole 2806401 towards 2806402. No dead animals or birds & no sign of any conductor clash marks. Conductors were out of sag on road side & were pulled up by faults crew. Spur fuse did not blow, Ventnor ACR reclosed. Observed a heap of silage hay wrap blown up against fence & crew found some on conductors in an adjacent span. Although one conductor was out of sag there were no signs of conductors clashing - there are large crossarms and there is adequate clearances between the conductors. | Conductor (bare) | 0 | 0 | 0 |  | phi12 | Suspected the fire was caused by silage hay wrapping blowing onto overhead HV conductors by strong winds which caught fire with hot plastic falling to the ground. | Grassfire | 15/02/2017 16:50 | 1 | Medium: 1000 sq.m - 10 ha | 5633 | Agricultural |  | 20170216SPN_04 | Infrastructure (network-based) | -38.4969 | 145.2277 | 1 | AusNet Services Distribution | Report | 7241 | 0.010566 | 22kV AC | Moorabbin Airport | 3922 | Ventnor | Other
The faults crew removed the overhead service and meter, took photos and advised their supervisor. | 18 AUSTIN AVENUE, MCCRAE VIC 3938 | 1310618 | Vandalism;Caused by REC/contractor | [5 empty] | 2 | REC called to advise the wires are exposed at the fused mains box and the consumers mains have been damaged by the builder and there is no power. The cover of the POA has also been smashed by the builder and the REC doesn't know his name. 5.41PM - smart meter gave a last gasp as the power went off. 5.49 PM - REC called to suggest the unknown owner / builder has cut the single phase consumers mains and removed the service fuse. The REC didn't leave his contact details when he rang the United Energy faults and emergencies call centre. 8.15 PM - The Downer faults crew attended and believed the REC had completed the above activities to save the costs associated with an abolishment. Apparently, the owner / builder lives next door. Contact details of the occupier in United Energy systems shows a Mrs Liz Ruth - 0411 433 572. Signage on the front fence indicates that Nepean Building Permits are involved. | Customer installation | 0 | 0 | 0 |  |  | It's believed the work was initiated to save the costs associated with an abolishment. | No Go Zone (contact) | 14/02/2017 17:41 |  |  | 5625 | Residential |  | 20170216UTD_01 | Infrastructure (network-based) | -38.3647 | 144.9275 | 1 | United Energy Distribution | Report | 6882 | 0.018338 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | Other
On arrival crew carried out repairs | 455 HAMILTON-PORT FAIRY ROAD, PORT FAIRY VIC 3284 | 31029615 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A call was made to Powercor from a customer advising of how the High Voltage overhead wires were struck with an excavator at the incident location. When crews arrived on site they found an excavator had been unearthing rocks on a Dairy Farm property beneath the HV overhead conductors. Excavator contact was made with one phase, damaging two strands of the 3/12 steel conductor. No conductors fell to ground. The excavator operator had moved the vehicle away from the line and briefly spoke to the crews. He advised that he had not seen the conductors while he was working, suddenly saw the sparks and heard an explosion. The crews reported that the excavator operator did not appear to be injured or receive any shock, however he appeared to be a bit shaken by the ordeal. He then left the incident site without leaving any contact details. No injuries have been reported. No ground fire starts occurred | Conductor (bare) | 2 | 2 | 2 |  | KRT013 | Excavator working beneath line | Loss of supply;No Go Zone (contact) | 19/02/2017 13:57 |  |  | 5640 | Agricultural |  | 20170220PWA_01 | Infrastructure (network-based) | -38.3572 | 142.1892 | 1 | Powercor | Report | 12436 | 0.03403 | 22kV AC | Warrnambool Airport Ndb | 3284 | Port Fairy | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew attended and found a hung-up EDO fuse. The fuse was not broken or on fire when the crew arrived. The crew replaced the EDO tube and restored supply. NOTI number 102207826 raised to replace EDO fuse units with BA fuse units. | 12 LANG PLACE, TOONGABBIE VIC 3856 | 2602874 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 226033. CEROT received a call that a customer heard a loud bang on pole outside, advised the pole was catching fire. The customer was calling the fire brigade. The attending AusNet Services' fault crew sent to investigate found a 6 Amp EDO fuse candling. | EDO fuse | 0 | 0 | 0 |  | tgn31 | EDO fuse tube candled. | Other electricity related | 43009.4062 | 1 | Localised: less than 10 sq.m | 5643 | Agricultural |  | 20170220SPN_03 | Infrastructure (network-based) | -38.0212 | 146.6347 | 1 | AusNet Services Distribution | Report | 6911 | 0.011957 | 22kV AC | Morwell (Latrobe Valley Airport) | 3856 | Toongabbie | Fuse
On arrival crew arranged for repairs to be undertaken. | 166-180 DOHERTYS ROAD, LAVERTON NORTH VIC 3026 | 33074084 | Vehicle |  |  | Overheated connection |  |  | 1 | During feeder patrol following a truck collision reported in incident 20170221PWA_01 a grass fire occurred at the base of a hv switch at the incident location. The contacts of the switch appear to be welded shut. There were no injuries reported | Disconnector/isolator | 2 | 2 | 2 |  | LVN024 | Flash-over on switch following vehicle collision | Grassfire;Damage to network assets | 17/02/2017 15:24 | 1 | Small: 10 - 1000 sq.m | 5645 | Roadway |  | 20170221PWA_02 | Infrastructure (network-based) | -37.827 | 144.7767 | 1 | Powercor | Report | 6913 | 0.038976 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
Crew made site safe and isolated kiosk for repairs | 29 LONG ISLAND CIRCUIT, CRAIGIEBURN VIC 3064 |  | Vehicle | [6 empty] | LV pillar at 50 Mission Hills Way was struck by vehicle. As the blue phase cable of pillar was in contact with the pillar frame and the LV fuse at Royal-Troon substation did not operate due to insufficient current, this caused the blue phase cable to short circuit to earth. Consequently, the blue phase cable heated up and molten metal fell on the leaves and bark below, resulting in a fire at the LV board at the kiosk. The fire was contained to the LV end of the kiosk. | Cable;Pad mounted equipment/kiosk;LV Pillar | 0 | 1 | 0 |  |  | Vehicle impact on a LV pillar | Plant/equipment | 22/02/2017 14:12 | 1 | Localised: less than 10 sq.m | 5661 | Residential |  | 20170223JEM_01 | Infrastructure (network-based) | -37.6027 | 144.9153 | 1 | Jemena | Report | 7724 | 0.034126 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. Supply isolated and issued a permit for the faulted section of the network to be repaired. Downer crews made safe and repaired conductors. | UNIT 6 7 DUNSTANS COURT, THOMASTOWN VIC 3074 | 910939 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 226578. Truck contacted guy wire on LIS 910939 causing feeder TT12 to trip and reclose. HV conductor damaged in four spots. Wire was hanging down and detached from pole. The truck driver was Darren Cumming, telephone 0414 399 480 of Rodney's Transport, telephone 0455 550 832. TT12 Feeder CB tripped and reclosed. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | tt12 | A truck contacted a guy wire resulting in damage to HV conductor. | No Go Zone (contact) | 22/02/2017 11:05 |  |  | 5660 | Industrial |  | 20170223SPN_02 | Infrastructure (network-based) | -37.6932 | 145.0187 | 1 | AusNet Services Distribution | Report | 6934 | 0.032321 | 22kV AC | Essendon Airport | 3074 | Thomastown | Vehicle
The low voltage pit has been made safe and has now been replaced, by CitiPower underground cables group. | 2-42 AURORA LANE, DOCKLANDS VIC 3008 | 30198692 | Working too close to underground cables | [5 empty] | 2 | Lead lease advise that they have damaged a low voltage pit at the incident location. On arrival the fault crew found that an excavator being used to install piles had caused significant damage to the low voltage pit and â€œLIVEâ€ low voltage wires inside were exposed, A wooden cover had been placed over the pit this appears to have been in place for a period of time. Area has been made safe by the CitiPower work crew. The low voltage pit has been made safe and has now been replaced, by CitiPower underground cables group. There was no ground fire and no injury as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | JA041 | Construction works | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/02/2017 13:16 |  |  | 5681 | Commercial |  | 20170227PWA_05 | Infrastructure (network-based) | -37.8201 | 144.9513 | 1 | CitiPower | Report | 6959 | 0.028407 | Low voltage AC (<1kV) | Essendon Airport | 3008 | Docklands | Dug up
CEOT sent a fault crew to investigate and found a pole junction box for an UG cable had failed and caused a fire at pole LIS 3900143. Supply isolations were made. An AusNet Services' LEI advised to attend. Owners engaged an REC (Luke Johnson, 11 Arundel St, Benalla, 0419 897 639) who completed temporary repairs to the switchboard. The fire at the top of the shop was the wiring between the internal and external sections of the split system air conditioner, and this was replaced by about 7pm. The owner Neil obtained suitable long replacement flexible hoses for the coffee machine and fitted these himself, with considerable savings. AusNet Services carried out substantial work to replace fire damaged assets on pole 3900143, including replacing the junction box with a Krone type box (FSD), and replacing all four three phase overhead services radiating from this pole, which were all fire damaged at the pole end. An AusNet Services' crew returned to the premises, and after testing, supply was restored at approximately 10pm. | 70-80 NUNN STREET, BENALLA VIC 3672 | 3900143 |  |  |  | Overheated connection |  | Phase to neutral | 2 | IMS 226246. On 31 Jan 2017 partners and proprietors of Benalta CafÃ© & Health Foods, Neil Mathews and Marlene McCready, thought they heard some bangs. They observed the switchboard was sparking and that the shop was filling with smoke. Employee, Mandy, removed customers from the proximity of the switchboard, including one with an oxygen bottle, outside. Neil observed a puff of smoke under the coffee machine, and looked under and saw water was leaking and sparks were coming from where the stainless braided rubber hoses went through the stainless bench. It was some time later that Marlene told Neil that she had received an electric shock up her right arm from the expresso machine, when she had reached around to attempt to turn off the tap, after she had observed water on the floor. Customers came in to the shop to say there was a fire up the top of the premises. Soon after an AusNet Services' employee removed the under-verandah fuses at the front of their premises, and things started to settle down. An AusNet Services' employee recommended to Marlene to attend a doctor for a check-up, as did the Police who attended, but she has not done so, to date. A junction box on pole 3900143 on the boundary of number 73 and 75 Nunn St continued to intermittently short and flames were observed. It took some time to establish where the underground service cable was supplied from, and supply was isolated from Church-Walker substation. The pole junction box that failed, was a junction point for the 50 sq.mm service cable which Tee'd off the mains cable at the foot of the pole, to four overhead services. The road crossing service supplied a streetlight. The service to 75 Nunn St supplied the National Bank and a residence upstairs. A service to 73 Nunn St supplied three installations, two for the Yooralla Op shop, and a third for a coffee shop known as 73C at the rear. A forth service supplied a block of shops from a point of attachment on the south end of No 71, the dry cleaners, which then supplied a further two installations including No 69 and Benalta CafÃ© & Health Foods at No 67. The low voltage pole had been replaced approximately 18 months earlier, and the servicing was put back in a similar fashion to what existed prior, (still vaguely visible on Google street view) with all the load for nine installations having to go through the one junction box, which was standard issue rated at 100 Amps per phase. The owners Neil & Marlene were very open with their discussion, and willingly showed me the damaged property. They intend to lodge a claim for reasonable costs. | Connection box | 0 | 0 | 0 |  | bn4 | Service cable junction box on pole failed. | Minor shock;Other electricity related | 31/01/2017 12:30 | 1 | Negligible: no ground fire | 5693 | Commercial |  | 20170301SPN_03 | Infrastructure (network-based) | -36.5508 | 145.9827 | 1 | AusNet Services Distribution | Report | 12352 | 0.035726 | Low voltage AC (<1kV) | Wangaratta Aero | 3672 | Benalla | Connection
The builder is unable to move or dismantle the gantry. The No Go Zone assessor has advised the builder that Jemena can put a new Krone box on the other side of the pole and transfer the LV/HV over. On Friday 24th March 2017, the krone box temp was relocated to other side of pole with the active leads. | 56 NICHOLSON STREET, FOOTSCRAY VIC 3011 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Jemena crew found scaffolding hard up against closed krone box. A member of Jemena's Works Practices attended site on 3 March 2017 and spoke to the acting construction supervisor (the original foreman / construction supervisor from the building site was on holidays), who produced some permits he had been given in the past, but the permits have expired at the end of 2016. It was found that there was no evidence of a No Go Zone permit for the installation of footpath containers and the scaffold on top of the footpath containers. The Krone box is obstructed by the containers and cannot be operated; the blue phase of the insulated conductor is rubbing against the board of the scaffolding. | Conductor (ABC);Connection box | 0 | 0 | 0 |  | FE8 | Builder built scaffold too close to Jemena assets | No Go Zone (contact) | 42738.6021 |  |  | 5704 | Residential |  | 20170302JEM_02 | Infrastructure (network-based) | -37.798 | 144.8997 | 1 | Jemena | Report | 6989 | 0.0068866 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Other
On arrival crew carried out repairs | 3 ELY COURT, CASTLEMAINE VIC 3450 | 60068588 | Vehicle | [5 empty] | 2 | There was a customer report that they had backed his trailer into a pillar and that the cover was off and wires exposed. Reported seeing smoking and sparking. Crew attended and found that the pillar had been damaged but didnâ€™t notice sparking or smoking at that time. There was no reported no shocks, injuries or fire. | LV Pillar | 2 | 2 | 2 |  | CMN005 | vehicle hit pit | Damage to network assets | 43071.4479 |  |  | 5701 | Roadway |  | 20170302PWA_03 | Infrastructure (network-based) | -37.0677 | 144.1954 | 1 | Powercor | Report | 6985 | 0.041307 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Vehicle
On arrival crew carried out repairs | 6 ST ANDREWS ROAD, SHEPPARTON VIC 3630 | 32191439 | Working too close to overhead lines | [5 empty] | 2 | A contractor reported an excavator had struck an overhead service cable at the above address. A crew attended and found that the active phase of the 2W service cable to 6 St Andrews Rd had been broken and the POA on the building was damaged. The crew isolated the service cable and the customer engaged an REC to repair the POA before a new service was installed and supply was restored. There were no shocks, injuries or ground fire start. | Service conductor | 2 | 2 | 2 |  | STN022 | Excavator operating near service line | Loss of supply;No Go Zone (contact) | 16/02/2017 14:49 |  |  | 5705 | Residential |  | 20170302PWA_05 | Infrastructure (network-based) | -36.3921 | 145.4067 | 1 | Powercor | Report | 6990 | 0.031703 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
On arrival crew carried out repairs | 304 LAL LAL STREET, CANADIAN VIC 3350 | 32009382 |  |  |  | Mechanical breakdown |  |  | 2 | A customer reported a wire down at the incident location. On arrival the crew found that a service cable had ruptured at house end roller clamp and fallen to the ground, resulting in a ground fire of approx. 1m/sq. No protection operated. There were no reported injuries. | Service conductor;Neutral screen | 2 | 2 | 2 |  | BAS013 | Service ruptured at house end roller clamp | Loss of supply;Grassfire | 42797.5368 | 1 | Localised: less than 10 sq.m | 5716 | Residential |  | 20170306PWA_04 | Infrastructure (network-based) | -37.5803 | 143.8771 | 1 | Powercor | Report | 7008 | 0.028429 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Canadian | Conductor
The damaged single phase service was replaced by the faults crew after the council tree branch had been removed. | 2 HEADINGLEY ROAD, MOUNT WAVERLEY VIC 3149 | 600806 |  | Alive;Council |  |  |  |  | 2 | The MFB advised there is a wire down outside the premise. A single phase service supplying 2 Headingly Road, Mount Waverley from pole number LIS 0600806 was damaged by a council tree and ignited a tree branch and the service. The MFB were in attendance and had extinguished the fire prior to the crew arriving onsite. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | EB 22 | Vegetation: Trees Incident | Other vegetation | 42828.625 | 1 | Negligible: no ground fire | 5713 | Roadway |  | 20170306UTD_01 | Infrastructure (network-based) | -37.862 | 145.1371 | 1 | United Energy Distribution | Report | 7002 | 0.031075 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Conductor
Once scene cleared by authorities work party commenced repairs | SHELFORD-MT MERCER ROAD, MOUNT MERCER VIC 3352 | 32003576 | Vehicle | [5 empty] | 1 | At approx. 01:02 am on 7/3/17, multiple AMI meter Power-downs were received by our control centre for an outage in the Mt Mercer area. An availability crew was dispatched from Ballarat to investigate. Upon arrival at the area the crew commenced a patrol of the line. Shortly after beginning the patrol the crew came upon a single vehicle accident. A Toyota Corolla had collided with Shelford Pole 15 snapping the pole at the base. The crew also found a badly injured person who they believed to have been the driver lying on the ground in the vicinity of the pole. The crew called emergency services and commenced CPR, but the person died at the scene. Emergency Service crews (Police/Ambulance/CFA) attended and completed their work. Police are still investigating the exact cause of the incident. Access the site has been since been given to Powercor and work has commenced to replace the damaged pole. The protection controlling this line operated as expected. There was no ground fire start. | Pole (wood) | 2 | 2 | 2 |  | BAS022 | Vehicle collided with pole | Loss of supply;Damage to network assets | 42919.0431 |  |  | 5724 | Roadway |  | 20170307PWA_04 | Infrastructure (network-based) | -37.8424 | 143.8922 | 1 | Powercor | Report | 7020 | 0.014641 | 22kV AC | Ballarat Aerodrome | 3352 | Mount Mercer | Vehicle
On arrival crew carried out repairs | 64-68 AITKEN AVENUE, DONALD VIC 3480 | 30326646 | Vehicle | [5 empty] | 2 | Customer reported that truck has hit wires crossing road. On arrival crew found a service line crossing the road had been hit and the neutral had broken. Crew were unable to obtain details of the offending vehicle as it had not stopped. No injuries, no ground fire, no third party damage. | Service conductor | 2 | 2 | 2 |  | CTN006 | Unknown vehicle struck service line | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 19/02/2017 13:42 |  |  | 5733 | Roadway |  | 20170308PWA_05 | Infrastructure (network-based) | -36.3607 | 142.972 | 1 | Powercor | Report | 7029 | 0.036745 | Low voltage AC (<1kV) | Horsham Aerodrome | 3480 | Donald | Vehicle
On arrival crew confirmed line isolation. Repairs commence following CFA clearance. | 300 MALIM ROAD, WILLAURA VIC 3379 | 30151626 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | CFA called to advise of a wire down and a fire start at the above location. On arrival the crew found a farmer had been building a large hay stack under a SWER O/H line. During construction of the stack, the loader contacted the SWER line resulting in the line breaking and falling onto the stack, starting a fire. Protection operated at P1 Gleeson S/L when a fuse blew. The CFA attended and extinguished the surrounding ground fire. There were no shocks, injuries, there was damage to tractor/loader. | Conductor (bare) | 2 | 2 | 2 |  | ART033 | Haystack operations under line | Grassfire | 42919.5333 | 1 | Small: 10 - 1000 sq.m | 5735 | Agricultural |  | 20170308PWA_07 | Infrastructure (network-based) | -37.5044 | 142.8177 | 1 | Powercor | Report | 7098 | 0.02152 | 12.7kV AC (SWER) | Hamilton Airport | 3379 | Willaura | Vehicle
Jemena Emergency crew attended and isolated circuit. Jemena emergency crew excavated the low voltage underground cable back approximately 3 metres from incident position, cut the cable, end cap seal and restored supply. | 20 WIRRAWAY AVENUE, BRAYBROOK VIC 3019 |  | Building too close or within the No Go Zone | [5 empty] | 2 | A civil contractor was installing a new cable in a conduit when it jammed and he decided to cut the conduit to investigate. On cutting the conduit with a battery operated Sabre saw, the blade made contact with a 'live' low voltage mains cable buried under the conduit. The worker received flash injury to his face and was transported to seek medical treatment. Live high voltage and low voltage cables are located within the development property for future connection. 15 customers affected. 1 person attended hospital and has been released. | Cable | 0 | 0 | 2 |  | TH22 | Battery operated sabre saw blade made contact with 'live' low voltage XLPE 185mm mains cable | Medical attention (first aid/doctor/hospital) | 42981.6181 |  |  | 5750 | Construction |  | 20170309JEM_01 | Infrastructure (network-based) | -37.7941 | 144.8561 | 1 | Jemena | Report | 12394 | 0.0039792 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
On arrival work crew carried out repairs. A defect notice was issued to the customer to repair POA. | 28 NEWRY STREET, RICHMOND VIC 3121 | 30189293 | Vehicle | [5 empty] | 2 | A Builder contacted CitiPower advising that a truck had bought down a service wire. The pole end attachment had come down on the road and the service was still connected to the house at 28 Newry St, Richmond. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | NR003 | Truck struck service | Loss of supply;Damage to network assets | 25/02/2017 13:17 |  |  | 5745 | Residential |  | 20170309PWA_05 | Infrastructure (network-based) | -37.8249 | 145.0064 | 1 | CitiPower | Report | 7046 | 0.012892 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Vehicle
Emergency low voltage switching was completed and the LV connection was repaired under Access Authority conditions. Supply was restored upon completion. | 38 GLENBURNIE ROAD, MITCHAM VIC 3132 | 7031323 |  |  |  | Overheated connection |  |  | 2 | Customer has advised there is sparks and flames coming from the crossarm at the top of the pole. The crossarm is glowing red and a flame is visible on the pole outside 38 Glenburnie Road. The MFB are in attendance. A aluminium to copper IPC failed on the LV white phase conductor at "Glenburnie-Langford" pole type substation that caused flames to be witnessed and the MFB called to attend at pole No. LIS 7031323. | Pole mounted;Dropper/bridge | 0 | 0 | 0 |  | RWT 24 | The probable cause was a loose connection that overheated as a result. | Pole-top fire | 42889.8194 | 1 | Negligible: no ground fire | 5739 | Roadway |  | 20170309UTD_02 | Infrastructure (network-based) | -37.8293 | 145.2004 | 1 | United Energy Distribution | Report | 7036 | 0.0089861 | Low voltage AC (<1kV) | Moorabbin Airport | 3132 | Mitcham | Crossarm
on arrival crew carried our repairs | 6 SHEAHAN CRESCENT, HOPPERS CROSSING VIC 3029 | 30111186 |  |  |  | Unknown technical factor |  |  | 2 | VicFire phoned in to advise of a wire down at the premises, pole to house and a small grass fire at the incident location. Upon arrival the crew had found that the 2/C Twisted Grey PVC service cable from at the incident location had ruptured at the house end which caused the Live LV Service Cable to come to ground in the front yard. The resultant sparks from this caused a minor grass fire in the front yard. There was no reported injury or shocks as a result of this incident. | Service conductor | 2 | 2 | 2 |  | LV004 | Ruptured service | Loss of supply;Grassfire | 42981.9486 | 1 | Small: 10 - 1000 sq.m | 5754 | Residential |  | 20170314PWA_02 | Infrastructure (network-based) | -37.8706 | 144.7008 | 1 | Powercor | Report | 7059 | 0.018516 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | OH Cable
On Arrival crew carried out repairs. LEI inspected for HVI | 295-317 ST ALBANS ROAD, SUNSHINE NORTH VIC 3020 | 30113183 |  |  |  | Leakage |  |  | 0 | A number of residents/customers in the Sunshine & St Albans Area phoned in to advise that they had no power. Upon arrival the PCA HV Operator, discovered that a HV X-arm Fire had occurred at the incident location The resultant HV X-arm fire had caused the outer side phase conductor and strain/bridging insulatorâ€™s to come away from the HV X-arm and fall onto the LV conductorâ€™s below. Initial reports from the field crew suggested possible HVI, this was later confirmed by the LEI who attended. There was no reported ground fire, injury or shocks as a result of this incident. | Crossarm (wood) | 2 | 2 | 2 |  | SSE011 | Excessive leakage current | Pole-top fire;HV injection;Loss of supply;Significant disruption to the community;Damage to network assets | 43072.3403 | 1 | Negligible: no ground fire | 5756 | Public space |  | 20170314PWA_04 | Infrastructure (network-based) | -37.7717 | 144.8209 | 1 | Powercor | Report | 7062 | 0.003 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Pole
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 34 BURSARIA CRESCENT, FRANKSTON NORTH VIC 3200 |  |  | Lightning |  | HV injection |  |  | 2 | Caller advised that lightning has struck their house and they have lost a phase. During a thunderstorm, it appears that lightning has struck unknown assets and caused damage to customers appliances and electrical equipment. Affected customers were supplied from the south circuit of "Mitre-Fton Dnong" substation where no protection equipment had operated. A LEI was called to inspect properties supplied from the circuit and damage was found at 7,9,22,24,15,19,21,30,23 Bursaria Crescent, Frankston North. In addition, 34 Bursaria Crescent also had no access and was issued with a defect notice as there was damage evident at the switchboard along with the AMI meter that required replacement. | Smart meter;Customer installation | 0 | 0 | 0 |  | FTN 25 | Lightning struck an unknown customer or United Energy asset? | HV injection | 43072.375 |  |  | 5757 | Residential |  | 20170314UTD_01 | Infrastructure (network-based) | -38.1138 | 145.157 | 1 | United Energy Distribution | Report | 7063 | 0.020745 | Low voltage AC (<1kV) | Moorabbin Airport | 3200 | Frankston North | Lightning
Crew attended but were unable to identify cause of fire | 2720 CAMPERDOWN-LISMORE ROAD, LARRALEA VIC 3325 | 32055045 |  |  |  | Unknown technical factor |  |  | 1 | Vic Fire reported a ground fire at the incident location. On arrival the crew found that a grassfire of approx. 8ha in size had ignited near Cable Head Pole 210 of the Lismore Line. Inspections of the pole by the attending crew did not identify any cause for the grassfire. The area burnt was a mixture of road reserve and private land, with damage caused to fences and approx. 15 hay bales. There was no other reported third party damage or any injuries. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CDN004 | Not found, | Less than $50k damage;Grassfire | 15/03/2017 14:08 | 1 | Medium: 1000 sq.m - 10 ha | 5767 | Agricultural |  | 20170316PWA_02 | Infrastructure (network-based) | -38.0249 | 143.2512 | 1 | Powercor | Report | 7082 | 0.0091458 | 22kV AC | Ballarat Aerodrome | 3325 | Larralea | AF Other
Fault crew removed damaged street light. Notification has been raised to Jemena's public lighting contractor to replace street light. | 46 HOTHAM ROAD, NIDDRIE VIC 3042 |  |  |  |  | Defective component |  |  |  | Street light on pole on fire. | Public lighting | 0 | 0 | 0 |  |  | Failure of street light. | Pole-top fire | 16/03/2017 15:16 | 1 | Localised: less than 10 sq.m | 5774 | Residential |  | 20170317JEM_01 | Infrastructure (network-based) | -37.7361 | 144.8842 | 1 | Jemena | Report | 7094 | 0.021815 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | AF Other
The tree branch was that touching the SS23 overhead conductors was cut clear using live line techniques. | 47 VILLAGE DRIVE, DINGLEY VILLAGE VIC 3172 | 608434 |  | Alive;MEC |  |  |  |  | 2 | Caller advised that a tree within the property is touching the power lines and causing smoking, sparking and making crackling noises. Fire is evident but goes out and comes back randomly. A private tree located in the front yard of 47 Village Drive, Dingley Village was in contact with the 22kV overhead conductors near pole number LIS 0608434 that caused the tree branch to catch fire. | Conductor (bare) | 0 | 0 | 0 |  | SS 23 | Vegetation: Trees Incident | Other vegetation | 43072.4965 | 1 | Negligible: no ground fire | 5771 | Roadway |  | 20170317UTD_01 | Infrastructure (network-based) | -37.9801 | 145.1202 | 1 | United Energy Distribution | Report | 7091 | 0.026041 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Trees
On arrival crew isolated supply and completed repairs. | 68 BARKLY STREET, PORTLAND VIC 3305 | 32139117 |  |  |  | Leakage |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that the crossarm had caught fire at one of the outside HV insulators. No conductors came to ground hence, no protection activated for this incident. There was no ground fire. No third party damage or injury was reported. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | PLD006 | Excessive leakage current | Pole-top fire | 42950.0083 | 1 | Negligible: no ground fire | 5786 | Roadway |  | 20170321PWA_02 | Infrastructure (network-based) | -38.3627 | 141.618 | 1 | Powercor | Report | 7109 | 0.025149 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Crossarm
On arrival crew isolated supply and carried our repairs | 3 MCLEOD STREET, YARRAWONGA VIC 3730 | 30239162 |  | Fallen |  |  |  |  | 1 | The Police reported a pole fire at the incident location. On arrival the crew found that a tree had fallen across the line and the blue and white phase conductors had clashed. The clashing caused a flashover at the FSD, this in turn caused a small fire in the area of the FSD. The crew said there was no ground fire. No third party damage or injury was reported. | Conductor (bare);Disconnector/isolator | 2 | 2 | 2 |  | CME014 | Vegetation: Trees Incident | Pole-top fire | 14/03/2017 10:23 | 1 | Negligible: no ground fire | 5789 | Roadway |  | 20170321PWA_05 | Infrastructure (network-based) | -36.0242 | 146.0006 | 1 | Powercor | Report | 7112 | 0.00022917 | Low voltage AC (<1kV) | Wangaratta Aero | 3730 | Yarrawonga | Trees
Fault crew attended and hole has been partially back-filled to make safe. Jemena's NGZ assessor attended the site to issue a NGZ Report to third-party working at the site | 1485 MICKLEHAM ROAD, YUROKE VIC 3063 |  | Building too close or within the No Go Zone |  | Likely |  |  |  | 0 | A Vic Roads contractor were carrying out maintenance on spoon drain on the side of the road. While the contractor was carrying out the works, HV cable was located through non-destructive digging on guidance of DBYD maps and it was found that the DBYD maps do not reflect the HV underground cable to the location and depth on site. | Cable | 2 | 2 | 2 |  |  | Non-destructive works by third party uncovered HV underground cable. Contracting crew For VicRoads were digging a new spoon drain and believe they within dial before DBYD maps near our electrical asset. Contracting crew did not have NGZ report or permit at the time of the Incident. | No Go Zone (no contact) | 22/03/2017 9:59 |  |  | 5803 | Construction |  | 20170322JEM_02 | Infrastructure (network-based) | -37.5919 | 144.8796 | 1 | Jemena | Report | 7130 | 0.00058565 | 22kV AC | Melbourne Airport | 3063 | Yuroke | Other
Crew attended and replaced pole | 1008 DANYO NORTH ROAD, COWANGIE VIC 3506 | 32152227 |  | Lightning |  |  |  |  | 2 | CFA reported a pole fire at the incident location. Upon arrival, the fault crew found that a HV SWER pole was struck by lightning. This resulted in a ground fire of some 35 acres in salt bush. No injuries were reported There were no reported injuries. | Pole (wood) | 0 | 0 | 0 |  | OYN001 | Crew attributes cause as lightning | Grassfire | 21/03/2017 15:34 | 1 | Large: more than 10 ha | 5810 | Agricultural |  | 20170322PWA_13 | Infrastructure (network-based) | -35.2004 | 141.2853 | 1 | Powercor | Report | 8397 | 0.0072847 | 12.7kV AC (SWER) | Mildura Airport | 3506 | Cowangie | Lightning
On arrival crew carrie dout repairs | 116 BURKE ROAD, ARARAT VIC 3377 | 30079009 | Vehicle | [5 empty] | 2 | Service wire down reported at the incident location. On arrival the crew found that a truck with an excavator on board had been driven along the driveway in private property and under the overhead service line which was not observed in the dark and possibly foggy conditions. The overhead service line to a house was pulled down from the pole end. There was no ground fire. There were no injuries. | Service conductor | 2 | 2 | 2 |  | ART034 | Vehicle struck service line | Loss of supply;Damage to network assets | 14/03/2017 7:07 |  |  | 5819 | Roadway |  | 20170327PWA_01 | Infrastructure (network-based) | -37.3035 | 142.9324 | 1 | Powercor | Report | 7150 | 0.02964 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Vehicle
Upon arrival the crew isolated the line and removed the section of red gum limb, correct line height restored | 361 OLD EDDINGTON ROAD, BETLEY VIC 3472 | 31003500 | Working too close to overhead lines | [5 empty] | 2 | Customer advised that during performing the lopping of a red gum that upon falling the top end had caught the adjacent SWER line and had pulled it down to a height of 4m. Customer was concerned regarding the fact that the line was sparking and smoking and called Powercor. There was no fire , no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO005 | Vegetation: Trees Incident | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/03/2017 16:00 |  |  | 5823 | Agricultural |  | 20170328PWA_01 | Infrastructure (network-based) | -36.9176 | 143.7983 | 1 | Powercor | Report | 7155 | 0.010037 | 12.7kV AC (SWER) | Bendigo Airport | 3472 | Betley | Trees
On arrival crew carried out repairs | 64 TOWER ROAD, WERRIBEE VIC 3030 | 32174835 | Vehicle | [5 empty] | 2 | A customer informed a truck has pulled down a cable at the incident location. Upon arrival the crew found that the service cable had been damaged, Some damage has also been done to the LV termination/fuse box. There was no fire, no reported injuries or third party property damage. | Service conductor;Connection box | 2 | 2 | 2 |  | WBE034 | Vehicle struck service line | Loss of supply;Damage to network assets | 15/03/2017 13:50 |  |  | 5834 | Roadway |  | 20170328PWA_12 | Infrastructure (network-based) | -37.9046 | 144.6712 | 1 | Powercor | Report | 7167 | 0.039249 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
Supply was disconnected by the crew. | 54 FITZROY AVENUE, RED CLIFFS VIC 3496 | 30096021 | Unauthorised work | [5 empty] | 2 | A Registered Electrical Contractor (Tanner 0404 521 638) called to say he had attended the incident location and found live cables on the ground. On arrival the crew found that the service wire attached to the customers POEL had be cut and was still alive. The dwelling that was connected to supply was in the process of being demolished. It is assumed, but not confirmed that the demolishing crew cut the live cables while demolishing the building. Supply was disconnected by the crew. | Private overhead electric line (POEL) | 2 | 2 | 2 |  | RCT023 | Interference by unknown person/s | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/03/2017 15:34 |  |  | 5843 | Agricultural |  | 20170329PWA_08 | Infrastructure (network-based) | -34.3012 | 142.195 | 1 | Powercor | Report | 7179 | 0.030894 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | Other
CEOT dispatched a fault crew to isolate, make safe, investigate and repair. CEOT also dispatched an AusNet Services' LEI to attend. The attending service crew isolated supply to the Pole to Pit supply at the FOLCB (at the pole) due to a suspected possum causing the FOLCB fuses to blow and suspected a HVI, awaited support from LEI to assess damage. The attending LEI inspected affected properties at 33 Bungalook Rd East, Bayswater Nth, and found HVI damage. Report of damage sheets (customer claims forms) left with the re-connected owners. The fault crew made necessary network repairs and restored supply to the affected houses. No other customers' installations were deemed to be affected on LV cct. | 33 BUNGALOOK ROAD E, BAYSWATER NORTH VIC 3153 | 1220572 |  | Animal |  |  |  | Phase to phase | 2 | IMS 227113. Suspected HVI on pole 1220572, Bangalook Rd E. Possum found at site. No HV or LV fuses blown. Customer's FMB fuses were blown affecting two houses. Fed from Bangalook Elmhurst substation. | Conductor (bare) | 0 | 0 | 0 |  | bwr23 | Animal Incident | HV injection;Loss of supply | 25/03/2017 0:20 |  |  | 5850 | Residential |  | 20170329SPN_01 | Infrastructure (network-based) | -37.836 | 145.2645 | 1 | AusNet Services Distribution | Report | 7187 | 0.036128 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3153 | Bayswater North | Animal
There was no fire visible when the crew attended but the pole top was burnt and the strain eye bolt for the centre phase conductor had pulled through the pole. Emergency high voltage switching took place to minimise the number of customers affected and the top of the pole was cut off and the assets lowered. Supply was restored upon completion. | 2 BASS STREET, FLINDERS VIC 3929 | 1313402 |  | Precipitation;Prone to salt deposition |  | Electrical breakdown;Leakage |  |  | 2 | CFA report that a power pole is on fire and looks like the lines may drop. During light drizzly rain, a pole fire occurred at pole No. LIS 1313402 located on the corner of Bass Street and Golf Links Road next to the ocean. It was suspected that tracking on the pole top assembly was the cause that contributed to the pole to burn at the eye bolts. | Conductor (bare);Pole (wood);Pole top | 0 | 0 | 0 |  | DMA 23 | Pole No. LIS 1313402 is located on the corner of Bass Street and Golf Links Road next to the ocean. | Pole-top fire | 27/03/2017 19:10 | 1 | Negligible: no ground fire | 5858 | Roadway |  | 20170330UTD_03 | Infrastructure (network-based) | -38.4777 | 145.0237 | 1 | United Energy Distribution | Report | 7200 | 0.02431 | 22kV AC | Moorabbin Airport | 3929 | Flinders | Pole
On arrival crew carried out repairs pole recovered for investigation | 2547 QUAMBATOOK-SWAN HILL ROAD, LALBERT VIC 3542 | 32155539 |  | Wind |  | Rot |  |  | 1 | Customer reported a grass fire caused by Powercor assets ( pole fallen over ) at the incident location. On arrival the crew found that a pole had fallen and the SWER conductor made contact with the ground in an adjacent span, a ground fire ignited resulting in stubble paddock being burnt. CFA attended & extinguished the fire. There were no reported injuries | Pole (wood) | 2 | 2 | 2 |  | SHL005 | Degradation of timber | Grassfire | 30/03/2017 18:38 | 1 | Medium: 1000 sq.m - 10 ha | 5861 |  |  | 20170331PWA_01 | Infrastructure (network-based) | -35.5975 | 143.5422 | 1 | Powercor | Report | 12452 | 0.017766 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3542 | Lalbert | Pole
On arrival crew isolated supply and arranged repairs | PRINCES PARK, 200-590 ROYAL PARADE, CARLTON NORTH VIC 3054 | 30192194 | Working too close to underground cables | [5 empty] | 2 | The City of Melbourne reported that their plumber has dug up a low voltage underground cable at the incident location. On arrival the fault crew found that a plumber had hit the low voltage underground cable with his excavator one phase has been damaged and is open circuit. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | VM030 | Underground excavation | No Go Zone (contact) | 20/03/2017 13:05 |  |  | 5865 | Public space |  | 20170331PWA_03 | Infrastructure (network-based) | -37.7789 | 144.962 | 1 | CitiPower | Report | 7209 | 0.018845 | Low voltage AC (<1kV) | Essendon Airport | 3054 | Carlton North | Dug up
CEOT dispatched a fault crew to make safe, investigate and repair. Isolated and made safe. The crew isolated supply, made safe and replaced the fuse and fuse tube. | 6 BALDING STREET, MIRBOO NORTH VIC 3871 | 2021888 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 227320. Under INCD-28651-s, a fault crew reported a burnt out 6A EDO fuse tube @ LIS #2021888. No ground fire. | EDO fuse | 0 | 0 | 0 |  | lga11 | Burnt EDO fuse tube. | Other electricity related | 42770.3368 | 1 | Negligible: no ground fire | 5869 | Residential |  | 20170403SPN_01 | Infrastructure (network-based) | -38.3985 | 146.1588 | 1 | AusNet Services Distribution | Report | 7214 | 0.022159 | 22kV AC | Morwell (Latrobe Valley Airport) | 3871 | Mirboo North | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 411 BALCOMBE ROAD, BEAUMARIS VIC 3193 | 1811906 |  | Blown branch/vegetation |  |  |  |  | 1 | At 1540hrs on 29/03/2017, 11kV feeder BR 15 circuit breaker successfully reclosed and held but customers beyond HV isolators CH2924 advised of dim lights. During strong winds and rain, private tree branches contacted the HV conductors outside 141 Pellatt Street near pole No. LIS 1810758. The branches fell to the ground clear of the HV overhead conductors but fault current caused the centre phase HV bridge to fail and a glass disc to break at HV isolators CH2924 located in Balcombe Road at pole No. LIS 1811906. Hot molten metal fell to the ground and a small grass fire started that was estimated to be less than 1sqm and the MFB were in attendance. | Conductor (bare);Disconnector/isolator | 0 | 0 | 0 |  | BR 15 | Vegetation: Trees Incident | Grassfire | 29/03/2017 15:40 | 1 | Localised: less than 10 sq.m | 5873 | Roadway |  | 20170403UTD_01 | Infrastructure (network-based) | -37.9783 | 145.0394 | 1 | United Energy Distribution | Report | 7220 | 0.034127 | 11kV AC | Moorabbin Airport | 3193 | Beaumaris | Trees
On arrival crew isolated supply and arranged repairs | 37 RIPPLESIDE TERRACE, TARNEIT VIC 3029 | PA0129419 |  |  |  | Not built/maintained to design |  |  | 1 | A 315kVA, Etel kiosk in a residential subdivision appears to have sustained a major fault, this has resulted in the tank rupturing. A grass fire was initiated in reserve landscaping surrounding the Kiosk location. There were no reports of injuries or third party property damage. | Pad mounted equipment/kiosk | 1 | 1 | 2 |  | LV001 | Low oil | Loss of supply;Grassfire;Damage to network assets | 42770.9632 | 1 | Localised: less than 10 sq.m | 5876 | Public space |  | 20170404PWA_01 | Infrastructure (network-based) | -37.8462 | 144.6852 | 1 | Powercor | Report | 12083 | 0.021966 | 22kV AC | Laverton Raaf | 3029 | Tarneit | OH Cable
On arrival crew carried out repairs. | 343 BARNARD STREET, BENDIGO VIC 3550 | 32034497 |  |  |  | Leakage |  |  | 1 | An Employee reported a pole fire at the incident location. It was reported that the HV crossarm had burnt through and the HV insulator was sitting on the LV crossarm. There was no report of ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | BET02 | excessive leakage current | Pole-top fire;Loss of supply | 27/03/2017 10:43 | 1 | Negligible: no ground fire | 5880 | Roadway |  | 20170404PWA_03 | Infrastructure (network-based) | -36.7595 | 144.2665 | 1 | Powercor | Report | 7229 | 0.011219 | 22kV AC | Bendigo Airport | 3550 | Bendigo | Crossarm
CEOT dispatched a fault crew to make safe, investigate and repair. The SWER ISO was isolated and repairs made to the HV & LV earthing system. The HV earth was tested at 14 Ohms and a 30 day follow up Notification was raised to have the HV & LV earthing systems repaired. | 180 MT STANLEY ROAD, STANLEY VIC 3747 | 4506354 | Working too close to underground cables | [5 empty] | 2 | IMS 226539. Customer had trenching done around the Stanley SWER ISO for installing water pipes. The ISO HV and LV Earths were damaged (cut off). The trenching had been done 4 or 5 days prior to AusNet Services being notified. It appears that it had been done using a chain type trencher and the HV & LV earthing system were both cut in 3 different locations. The earthing system passed a Safe to Approach test when the AusNet Services' crew arrived on site. There were no warning signs (no excavation) attached to the SWER ISO pole. The crew on site could not ascertain who did the digging or installed the water pipes. | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | myt7 | Customer's contractors dug up SWER ISO substation earths. | No Go Zone (contact) | 20/02/2017 12:30 |  |  | 5878 | Agricultural |  | 20170404SPN_01 | Infrastructure (network-based) | -36.415 | 146.7682 | 1 | AusNet Services Distribution | Report | 7227 | 0.027365 | Earthing cable | Wangaratta Aero | 3747 | Stanley | Dug up
CEOT dispatched a fault crew to make safe, investigate and repair. The FOLCB box was replaced and the underground service cable and transformer leads were reconnected / replaced. | 200 BIRDS ROAD, HEDLEY VIC 3967 | 2609024 |  |  |  | Overheated connection |  |  | 2 | IMS 2262015. CEOT received a report of a pole on fire. A faulty pole mounted FOLCB protecting an underground service cable was burnt / melted causing molten plastic to fall to the ground which caused a small fire on the ground. The CFA attended and extinguished the fire. A loose connection coupled with salt air in the FOLCB caused arcing and the FOLCB box eventually caught on fire and burnt to the ground. PLEASE NOTE - this incident was initially reported as a melted FOLCB on pole and not as a ground fire. Therefore in accordance with ESV reporting guide a Schedule 1 report was not initially entered into OSIRIS. It wasn't until the IMS was work flowed that it was realised a very small ground fire did occur - actual size is only approximately 75 sq.mm (very tiny but the CFA did attend and extinguished the molten plastic on the ground. | Connector/termination;Connection box | 0 | 0 | 0 |  | FTR12 | A loose connection coupled with salt air in the FOLCB caused arcing and the FOLCB box eventually caught on fire and burnt to the ground. | Grassfire | 26/01/2017 7:45 | 1 | Localised: less than 10 sq.m | 5618 | Agricultural |  | 20170215SPN_01 | Infrastructure (network-based) | -38.6311 | 146.5053 | 1 | AusNet Services Distribution | Report | 11249 | 0.0032674 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3967 | Hedley | Connection
CEOT dispatched a fault crew make safe to isolate, make and investigate. The crew attended and isolated supply to make safe. The local DAO was notified. Construction crew attended to make repairs. | 26 BAMFIELD ROAD, MOUNT EVELYN VIC 3796 | 1010839 |  |  |  | Overheated connection |  |  | 2 | IMS 226450. CFA reported a grass fire and sparks at a pole. Burnt out active conductors at LV ABC IPC connections at pole top caused sparks and molten plastic to fall to the ground resulting in a very small grass fire. The IPC connections from a three phase fused mains box to the 95mm LV ABC had shorted and bits fell to the ground. This caused smouldering on the ground under the fence. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  | ldl13 | Burnt out active conductors at LV ABC IPC connections. | Grassfire | 15/02/2017 12:05 | 1 | Localised: less than 10 sq.m | 5632 | Agricultural |  | 20170216SPN_03 | Infrastructure (network-based) | -37.7989 | 145.4076 | 1 | AusNet Services Distribution | Report | 7927 | 0.028566 | Low voltage AC (<1kV) | Moorabbin Airport | 3796 | Mount Evelyn | Conductor
Lineworker contacted his supervisor and then isolated the supply in the service pit. Submission to have the installation abolished has only just been lodged with the Retailer. Owner of property is: Ramsey Croft, ph 0439992249. REC who lodged the request for abolishment is: Justin Randell from ARB Electrical, ph 0418325755. Developer is: Craig Rice, ph 95810100. | 18 ALBERT STREET, MOE VIC 3825 | 2721247 | Unauthorised work |  |  |  |  | Phase to earth | 2 | IMS 226479. Lineworker was attending abolishment at 1C Haigh St, Moe, (Service Order 41749203) when a person from an adjacent sight approached him with a query at address 18 Albert St, Moe. Lineworker attended 18 Albert St to find a meter (number 4495177) on the ground and noticed an upside down bin which was covering a 3 phase supply cable which had been cut off and when tested was still alive to 415 Volts. This cable was the underground consumer's mains to a building which has just been abolished. ESV and AusNet Services have been in contact regarding this incident and ESV is conducting an investigation. | Customer installation | 0 | 0 | 0 |  | moe31 | Demolished building prior to Abolishment service order being able to be exercised. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/02/2017 10:00 |  |  | 5634 | Construction |  | 20170216SPN_05 | Infrastructure (network-based) | -38.1759 | 146.2697 | 1 | AusNet Services Distribution | Report | 6899 | 0.022274 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Moe | Other
CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew found a EDO fuse tube broken in half. No fire was present. The crew replaced the EDO fuse tube and restored supply. NOTI number 102207890 raised to replace the faulty EDO fuse units with BA fuse units. | 455 CLEAR CREEK VALLEY ROAD, MIRBOO VIC 3871 | 2721123 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 226011. Customer call with no power. The attending AusNet Services' fault crew found a 5 Amp EDO fuse tube burnt off at Swain Pole 4 Substation. No fire on the ground or on the pole. | EDO fuse | 0 | 0 | 0 |  | mwts14 | EDO fuse tube burnt / candled. | Other electricity related | 43009.7535 | 1 | Negligible: no ground fire | 5642 | Agricultural |  | 20170220SPN_02 | Infrastructure (network-based) | -38.4601 | 146.2466 | 1 | AusNet Services Distribution | Report | 6910 | 0.0405 | 22kV AC | Morwell (Latrobe Valley Airport) | 3871 | Mirboo | Fuse
Crew attended, isolated supply and repaired conductor | 85 HEALES ROAD, CORIO VIC 3214 | 33043567 | Working too close to overhead lines | [5 empty] | 1 | customer advised a crane brought down a cable at the incident location. Upon arrival the crew found that the low voltage conductors had been struck by a mobile crane. There were no injuries or fire. | Conductor (bare) | 0 | 0 | 0 |  | FNS012 | Interference | Loss of supply;Damage to network assets | 16/02/2017 9:24 |  |  | 5659 | Industrial |  | 20170223PWA_02 | Infrastructure (network-based) | -38.0508 | 144.3806 | 1 | Powercor | Report | 6932 | 0.029934 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Vehicle
CEOT dispatched a fault crew to isolate, make safe, investigate and carry out necessary repairs. CEOT Dispatcher notified the local DAO & TOC. Fault crew attended initially, followed by DAO. Obtained details from property owner who requested claim form for lost pasture. Broken crossarm on ground at pole had active termites. Took photos and checked fence line. Singed posts and bottom wire blackened but not damaged. Only damage was an area of pasture approximately 300 metres x 150 metres. Crew extinguished burning branch that had re-ignited after CFA departed (Used knapsack and shovel to completely extinguish). The HPS-WOTS 66kV line was constructed as two parallel vertical circuits on pole 21. The top and bottom x-arms had been changed previously to steel x-arms. The X-arm was replaced on the following day and the line restored to service. The pole was last ground inspected on 3/7/2012. Active Termites were noted in the pole on replacement of the x-arm and a Notification #102354048 has been raised for an inspection and treatment if found OK or replacement if not OK. | 38 CAMP ROAD, BONEGILLA VIC 3691 |  |  | Animal |  | Conductor clashing |  | Phase to phase | 1 | IMS 226579. The WOTS-HPS 66kV line locked out. Reports of fire around Lis #5235747. On arrival fault crew found broken x-arm. Found fire around our assets. CFA were in attendance. CFA allocated 4 water bombing aircraft and 9 fire trucks to control the fire. Centre position crossarm failed due to white ants. | Crossarm (wood) | 0 | 0 | 0 |  | WOTS-HPS 66kV line | Animal Incident | Grassfire | 22/02/2017 14:50 | 1 | Medium: 1000 sq.m - 10 ha | 5658 | Agricultural |  | 20170223SPN_01 | Infrastructure (network-based) | -36.1256 | 147.0058 | 1 | AusNet Services Distribution | Report | 6931 | 0.019348 | 66kV AC | Wangaratta Aero | 3691 | Bonegilla | Animal
On arrival crew carried out repairs | 5 RACECOURSE ROAD, RIDDELLS CREEK VIC 3431 | 30034981 | Working too close to overhead lines | [5 empty] | 2 | A customer reported a excavator had struck and pulled down service cable to premises at this location. A crew attended and found service cable had been struck and broken, resulting I the live end of the cable laying on the ground. . The crew isolated the cable and replaced it. There were no reported shocks, injuries, ground fire start or third party damage. | Service conductor | 2 | 2 | 2 |  | GSB012 | excavator struck service | Loss of supply;No Go Zone (contact) | 16/02/2017 8:44 |  |  | 5683 | Roadway |  | 20170227PWA_07 | Infrastructure (network-based) | -37.4633 | 144.6864 | 1 | Powercor | Report | 6961 | 0.032575 | Low voltage AC (<1kV) | Melbourne Airport | 3431 | Riddells Creek | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. CEOT notified the local DAO to investigate. A Downer crew were on-site waiting for a shutdown to changeover the existing Gas Switch with a new Gas Switch. The Gas Switch was replaced by the crew. | 200 EASTFIELD ROAD, CROYDON SOUTH VIC 3136 | 1206763 |  | Bird |  |  |  | Phase to earth | 2 | IMS 226658. The local AusNet Services' DAO attended the site and found a burnt grassed area of 8m x 0.8m. It is apparent that a bird shorted out between the live leads and the lever of a Gas Switch RW151, LIS 1206763, despite animal proofing. No property damage and only scorching of grass against customer fence at 200 Eastfield Rd, Croydon South. The Gas Switch was still operational despite scorching to one side. the dead burnt bird was still attached when on-site. | Disconnector/isolator | 0 | 0 | 0 |  | CYN11 | Bird Incident | Grassfire | 28/02/2017 14:45 | 1 | Localised: less than 10 sq.m | 5688 |  |  | 20170228SPN_01 | Infrastructure (network-based) | -37.8134 | 145.2869 | 1 | AusNet Services Distribution | Report | 11251 | 0.027726 | 22kV AC | Moorabbin Airport | 3136 | Croydon South | Animal
CEOT dispatched a fault crew to make safe, investigate and repair. The Boric Acid fuse opened and removed and was replaced by the fault crew. CEOT notified the local DAO. | 332 LONGWOOD-RUFFY ROAD, LONGWOOD EAST VIC 3666 | 3901723 |  |  |  | Electrical breakdown |  |  | 2 | IMS 226667. An AusNet Services' HV Operator was out on a fault call and found a 6K Boric Acid fuse candling. Also found 10,000 square metres of grass fire which was under control by the CFA. No damage besides BA fuse tube. | Boric acid | 0 | 0 | 0 |  | bn1 | Candled Boric Acid fuse tube. | Grassfire | 42738.2708 | 1 | Medium: 1000 sq.m - 10 ha | 5690 | Agricultural |  | 20170301SPN_01 | Infrastructure (network-based) | -36.8436 | 145.464 | 1 | AusNet Services Distribution | Report | 6971 | 0.011087 | 22kV AC | Mangalore Airport | 3666 | Longwood East | Fuse
CEOT dispatched a fault crew to make safe, investigate and repair. Isolated, made safe and replaced fuse tube. | 269 SHEFFIELD ROAD, MONTROSE VIC 3765 | 1208865 |  | Animal |  | Electrical breakdown |  |  | 2 | IMS 226200. 6A Boric Acid fuse candling @ LIS1208865. Fuse tube burnt out possibly due to animal. No pole or ground fire occurred. | Boric acid | 0 | 0 | 0 |  | BWR13 | Animal Incident | Other electricity related | 25/01/2017 17:20 | 1 | Negligible: no ground fire | 5691 | Residential |  | 20170301SPN_02 | Infrastructure (network-based) | -37.8245 | 145.3375 | 1 | AusNet Services Distribution | Report | 11252 | 0.0020451 | 22kV AC | Moorabbin Airport | 3765 | Montrose | Animal
On arrival crew carried out repairs | LEE BREAKWATER ROAD, PORTLAND VIC 3305 | 32135103 | Working too close to overhead lines | [5 empty] | 1 | A call was made to Powercor advising of a crane making contact with overhead High Voltage wires at the incident location. When crews arrived on site they found that an ISO Marshalling timber transporting crane had hit the 3 phase 22kV line. It appeared that the crane operator may have driven underneath the line with the boom still in the air. The crew reported that the excavator operator did not appear to be injured or receive any shock. No injuries have been reported. Protection systems operated as expected. | Conductor (bare) | 2 | 2 | 2 |  | PLD005 | Crane contacted conductor | Loss of supply;Grassfire;No Go Zone (contact) | 28/02/2017 20:34 | 1 | Localised: less than 10 sq.m | 5700 |  |  | 20170302PWA_02 | Infrastructure (network-based) | -38.3549 | 141.6141 | 1 | Powercor | Report | 6984 | 0.040781 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
On arrival crew arranged for pole replacement | 34 BEAVIS ROAD, NARRAWONG VIC 3285 | 32135590 |  |  |  | Leakage |  |  | 1 | Vicfire reported a fire start at the incident location. A crew attended and found a pole fire had occurred at the incident location. A fire had started at the head of the pole, burning thru the pole at the king bolt. The cross arm released from the pole and the conductor came to ground. The conductor did not break. Protection operated. This resulted in a ground fire start of approx. 5m x 5m on private property. There were no injuries or third party damage. The CFA attended and extinguished the fire. | Pole (wood) | 2 | 2 | 2 |  | PLD001 | excessive Leakage current | Grassfire | 42797.3639 | 1 | Small: 10 - 1000 sq.m | 5708 | Agricultural |  | 20170303PWA_01 | Infrastructure (network-based) | -38.2179 | 141.7118 | 1 | Powercor | Report | 6997 | 0.0042998 | 22kV AC | Portland (Cashmore Airport) | 3285 | Narrawong | Crossarm
CEOT dispatched a fault crew to make safe, isolate, investigate and repair. The SWER line was isolated and earthed and prepared for an Access Permit. CFA got the fire under control. Estimated fire size: 40m x 120m. The HV line was repaired the next day when additional resources were available. Local DAO attended site on the 4th March 7am to gather information. | 260 CRYSTAL CREEK ROAD, WHANREGARWEN VIC 3714 | 4712442 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | IMS 226756. AL059 ACR tripped & locked out. Customer called in conductor on the ground. AusNet Services' crew found a SWER conductor on the ground # LIS: 4712442 and LIS 4712443 due to a tree branch that fell on the line during strong wind conditions. CFA on site busy extinguishing the grass fire in the vicinity. There were signs of rot in the tree branch. | Conductor (bare) | 0 | 0 | 0 |  | RubA12 | Vegetation: Trees Incident | Grassfire | 42828.0278 | 1 | Medium: 1000 sq.m - 10 ha | 5715 | Agricultural |  | 20170306SPN_02 | Infrastructure (network-based) | -37.2272 | 145.6492 | 1 | AusNet Services Distribution | Report | 12354 | 0.00018287 | 12.7kV AC (SWER) | Mangalore Airport | 3714 | Whanregarwen | Trees
A faults truck attended and isolated supply to make the site safe. Referred to the depot to arrange for a public lighting crew to attend and replace the damaged watchman light, PE cell and associated wiring. | HARTNETT DRIVE, SEAFORD VIC 3198 | 3304726 |  |  |  | Fatigue;Overheated connection |  |  | 2 | The CFA report there is a fire on the pole on the corner and they might not be there when the truck arrives. Wiring from a PE cell supplying a watchman light installed on pole number LIS 3304726 located on the corner of Harnett Drive and Klauer Street, Seaford caught fire and the CFA were called to investigate. The active and neutral tails supplying the watchman light were found to be burnt out and the cause was unknown. | Public lighting | 0 | 0 | 0 |  |  | The cause of the wiring failure was unknown on the concrete pole. | Pole-top fire | 42797.7083 | 1 | Negligible: no ground fire | 5719 | Roadway |  | 20170306UTD_02 | Infrastructure (network-based) | -38.1189 | 145.1404 | 1 | United Energy Distribution | Report | 7013 | 0.019841 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | AF Other
On arrival crew carried out repairs, customers engaged a REC to carry out fascia repairs. | 18 CLEVELAND STREET, ST ALBANS VIC 3021 | 31023114 | Vehicle | [5 empty] | 2 | Samuel Smits reported that a truck had hit and cut the service cable to #18 Cleveland street, ST Albans. He advised that 3 houses were affected. There was no supply and probably some damage to the fascia of the house. On arrival the Powercor crew found the LV service wire on the ground on the side of the road. . No Protection operated. There were no reported injuries or Fire. | Service conductor | 2 | 2 | 2 |  | SA004 | Truck struck service cable | Loss of supply;Damage to network assets | 21/02/2017 20:52 |  |  | 5734 | Roadway |  | 20170308PWA_06 | Infrastructure (network-based) | -37.7455 | 144.7872 | 1 | Powercor | Report | 7030 | 0.0098669 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
on arrival crew isolated line and carried out repairs | 900 HELENDOITE ROAD, TATYOON VIC 3378 | 33048290 | Working too close to overhead lines | [5 empty] | 1 | A farmer reported that a B-Double tip truck working on his property had hit the overhead power lines and bought them down. On arrival the crew found that a B-Double tip truck had contacted the SWER conductor between king Pole 35 and King Pole 36 and pulled the SWER conductor low. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. There was no other damage, no injury and no shock. | Conductor (bare) | 2 | 2 | 2 |  | ART033 | Tipper contacted conductor | Grassfire | 42919.8792 | 1 | Small: 10 - 1000 sq.m | 5737 | Agricultural |  | 20170308PWA_08 | Infrastructure (network-based) | -37.449 | 142.9547 | 1 | Powercor | Report | 7034 | 0.039056 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3378 | Tatyoon | Vehicle
Crew arrived and found HV on deck and apparently LIS 523017 has been chain sawed at base of pole. DAO Ben Sharrock to investigate. The following information was written by Ben Sharrock (DAO): "I advised Downer to Remove the 2x bays of HV from pole 523016 to 523824 and also remove the Felled Pole. Downer will leave the stump in the ground as a mark should this require re-instatement at a later date. The Centre Towerline Tx and pole will remain onsite should the customer wish for this to be re-instated. I noticed that the Security Systems business across the road had cameras out front angles towards the Melb Water Gate. â€“ Eclipse Security Systems 1300 66 11 99. I spoke with a consultant (Greg) and he advised that he felt the wires had been down for 2 days. He also advised they have a camera pointed on the gate and was confident he would have something on camera if anyone was in the area. I spoke to the CEOT and requested they look over their systems for any blips or indication of a fault occurring on this part of the network and advise. CEOT advised that there was an indication of something at approx 04:16hrs on 1/2/17. I looked through the camera footage from Eclipse Security for the 1/2/17 â€“ 3/2/17 from 00:00hrs to 0700hrs for each Day. There is no footage of any persons walking by the area at the time of the blip as advised from CEOT (04:16hrs). At 00:57hrs (12:57am) on 1/2/17 there is approx 10 seconds of footage showing 2 Males walking past Eclipse Security, towards the Melbourne Water Gate, in the direction of the Felled Pole. In the footage, 1 male is wearing a Bandana over the lower portion of his face (Nose/Mouth/Chin) and the other is visible for 2 seconds and is wearing a Hooded Jumper. There is no indication of them carrying anything, and there is no footage of them leaving the site. I advised Greg that I would like to get a copy of this footage which he was happy to provide, I will need to provide Greg with a USB Stick so that he can copy this for me. I will provide a copy of this in the future. I spoke to Chris from Narre Warren Police regarding this and he said that, should AusNet wish to have the police investigate this for criminal damages, we would need to make a report at the Station. Chris was also very interested to hear about the Security Business and said the police would like a copy of this, if we are to proceed with the criminal damages investigation. Traffic Control was organised by GHocking, to babysit the down line, until Downer arrive this afternoon (approx 5pm) to temporarily de-commission. Downer to attend later that day (5pm) and make safe via temporarily de-commissioning of the line, so that the impact of the loss of supply to industrial business is reduced." | 41-59 CENTRE ROAD, HAMPTON PARK VIC 3976 | 523017 | Vandalism | [5 empty] | 1 | IMS 226287. Passer-by (linesman) reports HV down from LIS 523016, not live as fuse blown. Ben Sharrock (DAO) attended site. Pole cut down intentionally via chainsaw. No Fire. Photos taken. See Investigations Tab for more information. There were no people onsite at the time of attendance (other than Downer) and no police were required. The following information was written by Ben Sharrock: "Downer Advised of felled line approx 10am 3/2/17. I was notified at approx. 1030 and received information via email from JDrapos at 1130am. I arrived on site at 1150am. After attending site it was noted that there are 2 poles on this property, these seem to be on Road Reserve. The pole cut down was a HV Intermediate Pole â€“ LIS: 523017. The next pole along is a HV Term pole with a Supply Transformer on it. (1Ph 10kVA â€“ Centre Towerline). There is a Builders Temp pole and Meter Box with a meter inside it (Meter Number - 4256814), near the Substation Pole. This Builders Temp is not connected and there are no supply wires from this Substation pole. I checked the meter number in Calltaker and the details say Site Vacant. There are no other contact details â€“ This will be followed up from Council." | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | hpk12 | HV pole cut down by unknown person/s. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42796.3924 |  |  | 5732 | Industrial |  | 20170308SPN_03 | Infrastructure (network-based) | -38.0213 | 145.2783 | 1 | AusNet Services Distribution | Report | 7028 | 0.012529 | 22kV AC | Moorabbin Airport | 3976 | Hampton Park | Other
A crew attended and isolated the Stawell gold mine HV supply at the HV SW Pole before restoring HV supply to the feeder and township. | 11 LITTLE RICKARD STREET, STAWELL VIC 3380 | 33052426 | Unauthorised work;Caused by REC/contractor | [5 empty] | 1 | At approx. 09:06hrs on Wed 8th March, the Stawell Gold Mine experienced a failure of one of their HV switching cabinets that resulted in a loss of the STL004 feeder at the CB. A crew attended and isolated the Stawell gold mine HV supply at the HV SW Pole before restoring HV supply to the STL004 feeder. | Cable;Customer installation | 0 | 0 | 0 |  | STL004 | Interference - Powercor assets severed and HV metering removed | Loss of supply;More than $50k damage;Damage to network assets | 42950.3792 |  |  | 5747 | Industrial |  | 20170309PWA_06 | Infrastructure (network-based) | -37.0481 | 142.7833 | 1 | Powercor | Report | 7049 | 0.026021 | 22kV AC | Horsham Aerodrome | 3380 | Stawell | AF Other
A faults truck attended and isolated supply to enable the repairs to be completed safely. The burn mark on the red phase conductor was repaired and the neutral conductor sleeved prior to the supply being restored. | 4 HASTINGS ROAD, FRANKSTON VIC 3199 | 3318715 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  | Conductor clashing |  |  | 2 | Caller reports wire has come down and fallen inside the construction site (Kane Constructions) going from pole to pole. An excavator has contacted the LV red phase and neutral conductors that caused them to clash and the neutral conductor to fall to the ground near pole number LIS 3318715. No shocks or injuries were received and there was no damage to plant. The crew completed a damage to UE asset form that captured the site managers contact details. | Conductor (bare);Aluminium | 0 | 0 | 0 |  |  | No Go Zone breach with contact made to the LV overhead conductors. | No Go Zone (contact) | 42981.4271 |  |  | 5746 | Roadway |  | 20170309UTD_04 | Infrastructure (network-based) | -38.1518 | 145.1309 | 1 | United Energy Distribution | Report | 7047 | 0.035036 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Other
Area made safe and repairs made. All properties and AMI meters on the affected side of the substation were inspected and no visible HVI damage was noted. | 114 HYDE STREET, YARRAVILLE VIC 3013 | Pole no. A002453 |  | Animal |  |  |  |  | 2 | Possum shorted HV conductor to steel cross-arm on pole A002453 which in turn tracked down the pole and shorted into the LV pole mounted FOLCB supplying a park pillar MSB. TechSafe report attached in "Notes & Findings" section. As a result of the short, the FOLCB burnt and melted to the ground and the blue phase LV bus fuse within the kiosk ground type substation blew. Evidence of melting is not considered an F-factor reportable fire start. There were no firm indications of fire in the surrounding vegetation or infrastructure, and the causes of fire could not be directly attributed to the melted material. | Conductor (bare);Service conductor;Pole (wood);Crossarm (steel);Neutral screen;Connection box;Insulators | 0 | 0 | 0 |  | FE05 | Animal Incident | Loss of supply;Melting or smoking only | 43072.2486 |  |  | 5752 | Residential |  | 20170312JEM_01 | Infrastructure (network-based) | -37.813 | 144.8972 | 1 | Jemena | Report | 8421 | 0.0033021 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3013 | Yarraville | Animal
On arrival crew carried out repairs | OZENKADNOOK-MORTAT ROAD, PERONNE VIC 3413 | 32121997 | Working too close to overhead lines | [5 empty] | 1 | A customer called to advise a tip truck had contacted a power line at the incident location. On arrival the crew found that a tip truck had contacted the SWER overhead conductor causing the ties on adjacent poles to break resulting in the conductor to fall onto the truck. Protection operated. There was no fire,r eported injuries or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | HSM004 | Tipper dumping gravel | Loss of supply;No Go Zone (contact);Damage to network assets | 42950.4403 |  |  | 5753 | Agricultural |  | 20170314PWA_01 | Infrastructure (network-based) | -36.7888 | 141.3517 | 1 | Powercor | Report | 12440 | 0.0031551 | 12.7kV AC (SWER) | Horsham Aerodrome | 3413 | Peronne | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. The local DAO went on-site to take photos and make observations. Grass burnt was covered up by EPV in the process of replacing the gas switch. 16/3/2016 - DAO revisited the site, took photos and observed burnt grass area of 0.5m x 0.5 m. The DAO also took photos of the gas switch in quarantine at Thomastown Downer Depot - indicator still showed switch still had gas. | UNIT 1 2 FRANK STREET, ELTHAM VIC 3095 | 918947 |  | Animal |  |  |  | Phase to phase | 1 | IMS 226903. 2:56 am ELM13 Circuit Breaker at Zone substation went to lock out. AusNet Services' fault crew performed a patrol and found a damaged gas switch GB1054 and a very small ground fire at the base of pole LIS 918947. Alleged cause of damage to be due to a possum. | Disconnector/isolator | 0 | 0 | 0 |  | elm13 | Animal Incident | Grassfire | 15/03/2017 2:55 | 1 | Localised: less than 10 sq.m | 5765 | Residential |  | 20170316SPN_02 | Infrastructure (network-based) | -37.7075 | 145.1616 | 1 | AusNet Services Distribution | Report | 7077 | 0.040083 | 22kV AC | Essendon Airport | 3095 | Eltham | Animal
Crew attended and replaced 2 poles before restoring supply | 597 KARAWINNA NORTH ROAD, MERRINEE VIC 3496 | 32144890 | Vehicle | [5 empty] | 1 | Vic Fire reported a tractor hit a pole and caused a ground fire. The crew attended and confirmed that a tractor had hit a pole and bought it and the conductors to ground. This caused a ground fire of approximately 5 meters X 40 meters. The site the was made safe | Pole (wood) | 0 | 0 | 0 |  | RCT023 | Interference - farm vehicle impact | Loss of supply;Grassfire;Damage to network assets | 16/03/2017 11:01 | 1 | Small: 10 - 1000 sq.m | 5770 | Agricultural |  | 20170317PWA_01 | Infrastructure (network-based) | -34.3302 | 141.735 | 1 | Powercor | Report | 8075 | 0.012135 | 12.7kV AC (SWER) | Mildura Airport | 3496 | Merrinee | Vehicle
The fire was out when the faults crew attended the site and they proceeded to replace the red phase copper to aluminium 'D' transformer lead, sleeved the aluminium and ampacted the lead to the overhead conductors. | 5 GOOLGOWIE STREET, ROSEBUD VIC 3939 | 1311305 |  | Heat |  | Mechanical overload;Overheated connection |  |  | 2 | Per CFA - pole is sparking and possibly caused a hedge fire. At pole number LIS 1311305 located on the corner of Murawa Drive and Goolgowie Street, the red phase copper to aluminium lead between the transformer and the overhead conductors failed at "Murawa-Goolgowie" substation. The connection failure caused molten metal to fall to the ground and a small grass and hedge fire started that was extinguished by the CFA. | Dropper/bridge | 0 | 0 | 0 |  | RBD12 | A probable loose connection may have attributed to the cause. | Grassfire | 15/03/2017 18:00 | 1 | Localised: less than 10 sq.m | 5772 | Roadway |  | 20170317UTD_02 | Infrastructure (network-based) | -38.3782 | 144.9252 | 1 | United Energy Distribution | Report | 7092 | 0.0045405 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Connection
On arrival crew inspected site. There was no asset damage or cause for fire located. | 228 COBRAM SOUTH ROAD, COBRAM VIC 3644 | 33087486 | Unknown external/community factor | [5 empty] | 2 | During a patrol of CME15 Feeder, a crew reported evidence of grass fire at base of Pole 83 Cobram West fdr. The burnt area was approximately 4m x 40m in road reserve. On investigation there was no evidence found to indicate an electrical cause for the fire There were no injuries or property damage. | No failed asset | 2 | 2 | 2 |  | CME015 | Following a thorough site inspection, no cause was found. | Grassfire | 18/03/2017 22:01 | 0 | Small: 10 - 1000 sq.m | 5778 | Roadway |  | 20170320PWA_01 | Infrastructure (network-based) | -35.9459 | 145.6315 | 1 | Powercor | Report | 7099 | 0.0076053 | 22kV AC | Shepparton Airport | 3644 | Cobram | AF Other
On arrival crew isolated supply and carried out repairs | 25 CLARINDA STREET, BACCHUS MARSH VIC 3340 | 31033069 |  |  |  | Leakage |  |  | 2 | CFA called in to advise of a pole on fire cnr Clarinda St & Turner St, Bacchus Marsh. Upon arrival the crew, had discovered that a HV X-arm had caught fire and burnt through at the HV X-arm Strap. Please Note:- The HV Conductors remained in place and connected to the HV Wood Strain X-arm/HV Insulators. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | BMH004 | Excessive leakage current | Pole-top fire | 43072.1924 | 1 | Negligible: no ground fire | 5787 | Roadway |  | 20170321PWA_03 | Infrastructure (network-based) | -37.677 | 144.4322 | 1 | Powercor | Report | 7110 | 0.028856 | 22kV AC | Avalon Airport | 3340 | Bacchus Marsh | Crossarm
On arrival crew isolated supply and carried out repairs | 360 SETTLEMENT ROAD, SWAN MARSH VIC 3249 | 32065090 |  |  |  | Overheated connection |  |  | 2 | A customer reported that the pole out front of their house was on fire at the incident location. On arrival the crew found that a fuse box on the substation pole had overheated, resulting in the box catching fire and dropping melted plastic and debris to the ground. The debris landed on short green grass and there was no ground fire, no reported third party damage or any injuries. | Connection box | 2 | 2 | 2 |  | CLC006 | box destroyed unable to determine direct cause | Pole-top fire | 14/03/2017 12:38 | 1 | Negligible: no ground fire | 5788 | Agricultural |  | 20170321PWA_04 | Infrastructure (network-based) | -38.3525 | 143.3519 | 1 | Powercor | Report | 7111 | 0.035878 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3249 | Swan Marsh | Crossarm
Area isolated and HV crossarm replaced | 8 HOLMWOOD ROAD, TOTTENHAM VIC 3012 | pole number A030074 |  | Humidity |  | Leakage |  |  | 2 | HV crossarm fire at pole number A030074 | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | FW5 | Light rainy condition conducive to tracking led to fire start | Pole-top fire | 22/03/2017 4:11 | 1 | Negligible: no ground fire | 5802 | Industrial |  | 20170322JEM_01 | Infrastructure (network-based) | -37.8115 | 144.8586 | 1 | Jemena | Report | 7129 | 0.019211 | 22kV AC | Essendon Airport | 3012 | Tottenham | Crossarm
The cable has been excavated and replaced. | 250 SPRING STREET, EAST MELBOURNE VIC 3002 | 30187345 | Working too close to underground cables | [5 empty] | 2 | A customer reported that public lighting is not working at the incident location. On arrival the fault crew found that the area where the public lighting cable had been laid had been dug up and a tree had been planted by the Melbourne City Council at the incident location. The underground cable was tested and found to be faulty. Later excavation confirmed the cable had been damaged by third party believed to be Citywide contracted by the Melbourne Council. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | MP058 | council contractor damaged cable | Loss of supply;No Go Zone (contact) | 22/12/2016 13:42 |  |  | 5798 | Public space |  | 20170322PWA_05 | Infrastructure (network-based) | -37.8085 | 144.9719 | 1 | CitiPower | Report | 12442 | 0.028314 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Other
Isolated supply and conductor repaired | 48 STATION STREET, MURCHISON VIC 3610 | 32192135 |  |  |  |  | Human error;Other | Phase to phase | 1 | Crew advised of a small fire resulting from clashing of Low voltage conductors during works. The white phase overhead conductor burnt through fell to the ground and a fire of less than 1 square metre was initiated. The crew extinguished the fire. Supply isolated for installation to complete repairs. There was no injuries | Conductor (bare) | 0 | 0 | 0 |  | MNA034 | LV overhead conductor clashed in span during work | Grassfire | 42889.4931 | 1 | Localised: less than 10 sq.m | 5812 | Roadway |  | 20170323PWA_01 | Infrastructure (network-based) | -36.6214 | 145.2194 | 1 | Powercor | Report | 12562 | 0.02094 | Low voltage AC (<1kV) | Shepparton Airport | 3610 | Murchison | Conductor
A faults crew attended and disconnected supply at the POA. A defect notice was issued on the consumers mains, FMJB, switchboard and meter panel and a truck appointment is required. A note was placed in United Energy systems advising the customer / REC had removed the meter. The site was left safe. | 281 JETTY ROAD, ROSEBUD VIC 3939 |  | Unauthorised work | [5 empty] | 2 | Caller reports that workers have cut a cable and have placed tape over the ends. The meter panel has fallen to the ground at the house that is under renovation. The home is either being renovated or abolished and the customer or REC has removed the meter and wanted the overhead service removed also. | Connection to meter | 0 | 0 | 0 |  |  | The home is either being renovated or abolished and the customer or REC has removed the meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/03/2017 16:00 |  |  | 5813 | Residential |  | 20170323UTD_01 | Infrastructure (network-based) | -38.3795 | 144.9123 | 1 | United Energy Distribution | Report | 7144 | 0.0045289 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Other
On arrival crew carried out repairs | 1 DAVIES AVENUE, SUNSHINE NORTH VIC 3020 | 30245825 | Vehicle | [5 empty] | 2 | A customer informed a truck has pulled down a cable at the incident location. Upon arrival the crew found that the service cable lying on the ground. The identity of the vehicle or driver was unknown. There was no fire, no injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | SSE012 | Unknown vehicle struck service line | Loss of supply;Damage to network assets | 43011.4451 |  |  | 5824 | Roadway |  | 20170328PWA_02 | Infrastructure (network-based) | -37.7573 | 144.8353 | 1 | Powercor | Report | 7156 | 0.018624 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
On arrival crew carried out repairs | 6 WANDIN COURT, WERRIBEE VIC 3030 | 34009005 | Vehicle | [5 empty] | 2 | Natalie reported that she has reversed over a low voltage pillar at the incident location. On arrival the fault crew found that the low voltage pillar had been pushed over and a connection had broken within the pillar. There was no fire, reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | WBE024 | Vehicle struck pillar | Loss of supply;Damage to network assets | 16/03/2017 12:23 |  |  | 5835 | Residential |  | 20170328PWA_13 | Infrastructure (network-based) | -37.9096 | 144.67 | 1 | Powercor | Report | 7168 | 0.0013252 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival crew carried out repairs | 125 REES ROAD, MELTON SOUTH VIC 3338 | 30306234 | Copper theft | [5 empty] | 2 | A Customer, advised that the HV & LV Earth leads are cut on a Pole at the incident location. The crew had found that a length of 3m HV Earth had been cut away and removed from a at HVCHP Pole . There was no fire, no reported injuries or third party property damage. | Earth | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 14/03/2017 15:41 |  |  | 5844 | Industrial |  | 20170329PWA_09 | Infrastructure (network-based) | -37.7187 | 144.5615 | 1 | Powercor | Report | 7180 | 0.0065694 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
On arrival crew carried out repairs | 48 EAST ESPLANADE, ST ALBANS VIC 3021 | 32177079 | Vehicle | [5 empty] | 2 | A customer phoned in to advise that a truck in neighbours property has reversed & clipped customer service cable â€“ wire has broken off at house end and is draped over customer car, wire still attached to pole, no supply. Upon arrival the crew found that the LVABC service cable running from LV Pole to POA House #48 East Esplanade, St Albans 3021, had been hit by an unknown truck about half way along with the live end lying in the front nature strip beside the LV Pole and the other end was lying in the customerâ€™s driveway at #48 on the ground and not draped over any vehicle/car as indicated by the customer. There were no reported shockâ€™s, injuries, fire or third party damage. | Service conductor | 2 | 2 | 2 |  | SA005 | Unknown vehicle struck service line | Loss of supply;Damage to network assets | 18/03/2017 6:25 |  |  | 5845 | Roadway |  | 20170329PWA_10 | Infrastructure (network-based) | -37.739 | 144.7974 | 1 | Powercor | Report | 7181 | 0.011481 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. CEOT informed the local DAO. Fault crew made the site safe and replaced the pole mounted FOLCB. | 16 HUNTS ROAD, LEONGATHA SOUTH VIC 3953 | 2010501 |  |  |  | Overheated connection |  |  | 2 | IMS 227122. A LV fuse carrier from a pole mounted FOLCB to fell to the ground. A fire occurred at the base of the pole and the fire was approximately 5mx5m in size. The fault crew advised the cause is unknown apart from the melted fuse carrier found on the ground. An overheated connection caused by a likely high impedance connection. | Connection box | 0 | 0 | 0 |  | lga23 | A molten LV fuse carrier from a pole mounted FOLCB fell to the ground starting a small grass fire. Cause unknown but likely high impedance connection of the inserted fuse carrier. | Grassfire | 27/03/2017 12:30 | 1 | Small: 10 - 1000 sq.m | 5851 | Agricultural |  | 20170329SPN_02 | Infrastructure (network-based) | -38.5583 | 145.881 | 1 | AusNet Services Distribution | Report | 7958 | 0.0050127 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha South | Fuse
The fire was out when the faults crew attended and its unclear of how long the termination clamp had been in place. There was no damage to the customers premise and the grey twisted service was replaced with a new XLPE type. To prevent incidences such as this from occurring, the United Energy Asset Inspection Manual has a maintenance Code of 51B to identify any Grey/Green Twisted services terminated with black XLPE strain clamps. This notification is in addition to any previously raised under code 51. | 12 GLENMORE CRESCENT, BLACK ROCK VIC 3193 | 1817406 |  |  |  |  | Not followed |  | 2 | Per MFB - House fire. A three phase grey overhead twisted service had a XLPE termination clamp installed that had worn through the cable causing it to flash over and a small fire at the clamp near the POA. XLPE overhead service cables are terminated using bolted clamp-type terminations. Note that these clamp-type terminations cannot be used with the superseded PVC overhead service cable due to the likelihood of damage to the softer PVC insulation | Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | A three phase grey overhead twisted service had a XLPE termination clamp installed. This is not | Plant/equipment | 22/03/2017 6:30 | 1 | Negligible: no ground fire | 5849 | Residential |  | 20170329UTD_03 | Infrastructure (network-based) | -37.9717 | 145.0152 | 1 | United Energy Distribution | Report | 7185 | 0.017118 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Black Rock | Conductor
On arrival crew carried out repairs | 160 PRENTICE ROAD, ORRVALE VIC 3631 | 32191270 | Working too close to underground cables | [5 empty] | 1 | REC advised excavator had dug up cables on nature strip and damaged and exposed cables. On arrival crew found that excavator had struck the top of a pit that was approx. 6m inside private property which had pulled the LV cable and damaged the consumer mains. Customer had cable identified and marked onsite although they were not aware of the pit. 1 of the phases was still live when the crew arrived. No information on the pit is visible in GIS. There was no fire or reported injuries | Services cable;Customer installation | 2 | 2 | 2 |  | STN011 | Underground struck during exavation | Loss of supply;Damage to network assets | 18/03/2017 15:28 |  |  | 5864 | Agricultural |  | 20170331PWA_02 | Infrastructure (network-based) | -36.4238 | 145.454 | 1 | Powercor | Report | 7208 | 0.024687 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Orrvale | Dug up
Pre-rectification test results Faults crew & LEI dispatched. Initial NST test performed which passed. Voltage from independent earth to exposed active conductor was measured at 250 volts. What was rectification? Disconnected unused metering conductors from meter panel links. 1 x 10 sq.mm (7/1.35) active conductor 250mm long 1 x 6 sq.mm (7/1.04) neutral conductor 350mm long, was tucked behind panel. After-rectification test results: Final NST test performed which passed. Z=0.14 Ohms. | 9 CHICKERELL STREET, MORWELL VIC 3840 | 2617987 |  |  |  |  | Not followed | Phase to earth | 2 | IMS 226453. Mr Young was replacing a RCD combo in the switchboard located beside the meter panel at L&H electrical wholesalers in Morwell when he received a shock on his elbow from timber meter panel. The installation was isolated at the main switch while Mr Young was working on the switchboard and at first thought his tester was faulty until he noticed 25mm of exposed conductor protruding through the timber panel where a time switch service fuse once belonged. He was even more shocked to find it alive with 250 Volts and his tester was working. The cause was found to be the meter installer who failed to make safe an active conductor when the time switch service fuse base was removed. The 10mm2 (7/1.35) copper building wire conductor was supplied via a 100A red phase active link on the meter panel and had 25mm of PVC insulation removed exposing the copper conductor through the hole where the time switch service fuse was once installed. | Meter board (including fuses) | 0 | 0 | 0 |  | mwts22 | A metering tail from the active link on the meter panel was not disconnected or made safe and was protruding through a hole in the meter panel where a time switch fuse base was removed exposing a live conductor. | Minor shock | 15/02/2017 13:30 |  |  | 5863 | Commercial |  | 20170331SPN_01 | Infrastructure (network-based) | -38.2325 | 146.4332 | 1 | AusNet Services Distribution | Report | 7207 | 0.024834 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Other
On arrival crew carried out repairs | 6111 DARTMOOR-HAMILTON ROAD, YULECART VIC 3301 | 30090621 |  | Fallen |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival, the crew found that a tree (from outside the clearance space) had fallen across an adjacent 22kV line causing the line to break and fall to the ground resulting in a ground fire (Approx. 300 sq/m) on the road reserve. Protection operated. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | HTN002 | Vegetation: Trees Incident | Loss of supply;Grassfire | 42798.5576 | 1 | Small: 10 - 1000 sq.m | 5877 | Public space |  | 20170404PWA_02 | Infrastructure (network-based) | -37.7719 | 141.8796 | 1 | Powercor | Report | 7226 | 0.037318 | 22kV AC | Hamilton Airport | 3301 | Yulecart | Trees
On arrival crew isolated supply. The crew has removed the substation and disconnected the supply from the CHP. | 188-198 BLACKSHAWS ROAD, ALTONA NORTH VIC 3025 | 30143694 | Unauthorised work;Copper theft | [5 empty] | 2 | Indent A Powercor employee reported unknown third party damaged substation at the incident location and cables were taken away. Upon arrival, the fault crew found that substation HV switch had been opened, the door lock had been damaged and LV bus section and associated cables had been stolen. This was an energised substation. There were no injuries or fire. | Pole mounted | 2 | 2 | 2 |  | BLT022 | Vandalism and copper theft | Loss of supply;Damage to network assets | 42829.6458 |  |  | 5886 | Industrial |  | 20170405PWA_03 | Infrastructure (network-based) | -37.8328 | 144.8644 | 1 | Powercor | Report | 7237 | 0.010576 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3025 | Altona North | Other
On arrival crew isolated supply for repairs to take place | 19 BALDWIN AVENUE, NORLANE VIC 3214 | 32068748 |  |  |  | Fault on customer installation |  |  | 2 | Vicfire advised of a fuse box on fire. Attending crew found customers FOLCB had overheated due to a combination of a birds nest and water ingress after very heavy rain. There was no injuries or ground fire. | Customer installation | 2 | 2 | 2 |  | CRO021 | Bird Incident | Melting or smoking only | 21/03/2017 18:18 |  |  | 5893 | Residential |  | 20170406PWA_02 | Infrastructure (network-based) | -38.1001 | 144.3537 | 1 | Powercor | Report | 7249 | 0.024727 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Animal
On arrival crew carried out repairs | 55 KENNING ROAD, TARNEIT VIC 3029 | 30286726 | Copper theft | [5 empty] | 2 | A Powercor Employee, reported stolen HV earth at incident location. On arrival the Faults crew had found that a length of 2m HV Earth had been cut away, removed and stolen. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LV002 | Theft | Damage to network assets | 22/03/2017 14:15 |  |  | 5900 | Roadway |  | 20170407PWA_02 | Infrastructure (network-based) | -37.8111 | 144.6762 | 1 | Powercor | Report | 7258 | 0.010763 | Earthing cable | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew carried out repairs | 3521 SUNRAYSIA HIGHWAY, LEXTON VIC 3352 | 31001449 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A customer called to advise a tractor had contacted a power line at the incident location. On arrival the crew found that a Header had contacted an LV overhead service cable causing the cable the detach from the premises point of attachment. No protection operated. There were no reported injuries or shocks. | Service conductor | 2 | 2 | 2 |  | BAN006 | Header struck service | Loss of supply;Damage to network assets | 23/03/2017 9:38 |  |  | 5902 | Roadway |  | 20170407PWA_04 | Infrastructure (network-based) | -37.2773 | 143.5158 | 1 | Powercor | Report | 7260 | 0.024632 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3521 | Lexton | Vehicle
On arrival crew carried out repairs | 219 BABBA MIA LANE, HARROW VIC 3317 | 32101722 |  |  |  | Overheated connection |  |  | 2 | A customer called to report arcing and fire from the top of the pole at the incident location. On arrival the crew found a HV flex disconnected and EDO bushing cover partially melted and burnt. There was no ground fire or reported injuries or shocks. | Dropper/bridge | 2 | 2 | 2 |  | CHM011 | connection failure | Pole-top fire | 42798.4931 | 1 | Negligible: no ground fire | 5907 | Agricultural |  | 20170411PWA_01 | Infrastructure (network-based) | -37.1765 | 141.5055 | 1 | Powercor | Report | 7266 | 0.009831 | 12.7kV AC (SWER) | Hamilton Airport | 3317 | Harrow | Fuse
On arrival crew carried out repairs | 6 RIVER RESERVE ROAD, ANGLESEA VIC 3230 | 30065718 |  |  |  | Corrosion |  |  | 1 | On Sunday evening, WPD014 tripped at the CB . The Powercor control room notified the A/H Operator to investigate the cause. The operator patrolled and conducted some switching to isolated the problem, but could not locate the exact location/cause. A crew was dispatched to investigate early the following morning, a customer reported a leaning pole near the Anglesea River which lead the crew to the incident location. Upon arrival, the crew identified a 21/12 wood pole leaning approx. 45Â°. This was causing a span of 22kV conductor to be sagging into the Anglesea River. A tree top was burnt where the conductor had made contact. There were no reported injuries or third party damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | WPD014 | It was identified that the stay rod had rusted through and gave way. | Other vegetation;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42982.9313 | 1 | Negligible: no ground fire | 5913 | Public space |  | 20170412PWA_05 | Infrastructure (network-based) | -38.4052 | 144.1853 | 1 | Powercor | Report | 7274 | 0.039508 | 22kV AC | Avalon Airport | 3230 | Anglesea | Pole
Area isolated and conductors were repaired. | 218 WHITEHALL STREET, YARRAVILLE VIC 3013 |  | Vehicle | [5 empty] | 2 | A car hit pole at location below causing LV conductors to come to ground. Pole required replacement. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | yve-14 | Vehicle hit pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/04/2017 11:42 |  |  | 5917 | Industrial |  | 20170413JEM_01 | Infrastructure (network-based) | -37.8157 | 144.8993 | 1 | Jemena | Report | 7278 | 0.031762 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Vehicle
On arrival crew carried out repairs | 209 CENTRE SPUR ROAD, COORIEMUNGLE VIC 3268 | 33035900 |  | Blown branch/vegetation |  |  |  |  | 2 | Powercor was contacted by a customer reporting no supply, sparking wires down on ground and over tractor. A crew was dispatched to investigate. On arrival, the crew found that a tree had fallen onto the line and caused 4 bays of 22kV single phase 3/12 steel to hit the ground. There were no reported injuries or third party damage that crew were aware of. There was no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | CDN001 | Vegetation: Trees Incident | Loss of supply | 42982.6347 |  |  | 5915 | Agricultural |  | 20170413PWA_02 | Infrastructure (network-based) | -38.5614 | 143.2366 | 1 | Powercor | Report | 7276 | 0.018648 | 22kV AC | Warrnambool Airport Ndb | 3268 | Cooriemungle | Trees
On arrival crew carried out repairs | 750 POORNEET ROAD, WEERING VIC 3251 | 32062880 |  | Lightning |  |  |  |  | 2 | A customer reported Transformer appears to have flames coming out of top of it On arrival crew crew found that HV fuse had candled. There was no evidence of ground fire, no reported injuries or third party property damage. | Pole mounted | 2 | 2 | 2 |  | CLC003 | Lightning storm | Pole-top fire;Loss of supply | 42951.5667 | 1 | Negligible: no ground fire | 5918 | Public space |  | 20170413PWA_04 | Infrastructure (network-based) | -38.0947 | 143.6893 | 1 | Powercor | Report | 7307 | 0.028337 | 22kV AC | Ballarat Aerodrome | 3251 | Weering | Pole
On arrival crew carried out repairs | 2836 MORRISON PLAIN ROAD, MURRAYVILLE VIC 3512 | 32149124 |  |  |  | Leakage |  |  |  | The crew found the customer outage was the result of a burnt HV strain arm at the incident location. There were no reported injuries, no 3rd party damage or grass fire for the incident. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 42982.3319 | 1 | Negligible: no ground fire | 5926 | Agricultural |  | 20170418PWA_03 | Infrastructure (network-based) | -35.1019 | 141.1983 | 1 | Powercor | Report | 8398 | 0.014179 | 22kV AC | Mildura Airport | 3512 | Murrayville | Crossarm
On arrival crew carried out repairs | 10A HUNT STREET, OUYEN VIC 3490 | 32148359 | Vehicle | [5 empty] | 2 | Emergency Services reported a car into a pole at the incident location. Upon arrival, the crew found that a car had collided with a pole breaking the pole off at ground level . The pole was supported by the Low voltage conductors. This is a Tee Off LV pole, the LV conductors hanging low and partially live. There was no ground fire. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | OYN007 | Vehicle collision | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43043.3153 |  |  | 5928 | Roadway |  | 20170418PWA_05 | Infrastructure (network-based) | -35.0664 | 142.3145 | 1 | Powercor | Report | 7289 | 0.0027269 | Low voltage AC (<1kV) | Mildura Airport | 3490 | Ouyen | Vehicle
On arrival crew carried our repairs | 4 MARARA COURT, MILDURA VIC 3500 | 33064708 | Working too close to underground cables | [5 empty] | 1 | On Thursday afternoon, civil contractor reported that they had contacted a service cable in road reserve when boring under a concrete driveway cross over whilst installing a pole to pit. The civil contractor advised that he believes calibration issues with the asset locator and incorrect MOCS were the main contributing factors in this incident. Upon arrival, the crew found that the fuse had blown up the pole at the 4m mark. There was no fire , no reported injuries or third party damage. | Services cable | 2 | 2 | 2 |  | MBN032 | Under road boring operations | Loss of supply;No Go Zone (contact) | 13/04/2017 13:01 |  |  | 5934 | Roadway |  | 20170419PWA_02 | Infrastructure (network-based) | -34.2111 | 142.1222 | 1 | Powercor | Report | 12561 | 0.025596 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Dug up
On arrival crew carried out repairs | 451 DOHERTYS ROAD, TRUGANINA VIC 3029 | 30309861 | Working too close to underground cables | [5 empty] | 2 | A contractor advised that an UG cable was dug up at the incident location. Upon arrival, the Powercor crew noticed that the cable had been dug up by the contractor. The LV conduit damaged but no damage done to the cable. There were no injuries or fire. | Services cable | 2 | 2 | 2 |  | LVN021 | excavating too close to cable | No Go Zone (contact);Damage to network assets | 43073.3167 |  |  | 5938 |  |  | 20170420PWA_02 | Infrastructure (network-based) | -37.8255 | 144.753 | 1 | Powercor | Report | 7300 | 0.0027361 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Dug up
On arrival crew carried out repairs | 73 FITZROY ROAD, WARRNAMBOOL VIC 3280 | 30137969 |  |  |  | Leakage |  |  | 2 | Vic fire reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | WBL006 | Excessive leakage current | Pole-top fire;Damage to network assets | 19/04/2017 7:19 | 1 | Negligible: no ground fire | 5942 | Roadway |  | 20170420PWA_04 | Infrastructure (network-based) | -38.3708 | 142.4633 | 1 | Powercor | Report | 7306 | 0.021604 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Crossarm
LEI and fault crew investigated and found private pole was energised. Supply was then disconnected and defect notices issued. | 1 GIPPS STREET, PORT FAIRY VIC 3284 | 30134581 |  |  |  | Defective component |  |  | 2 | An unknown member of the public reported receiving an electric shock from a steel pole located in Matins Point Reserve, Gipps St, Port Fairy. The unknown person initially reported the incident to the Moyne Shire Council who sent their Electrician to investigate the incident. The Electrician identified the steel pole was a navigation light pole (council or port authority owned) located near the entrance to the Moyne river. | Customer installation | 0 | 0 | 0 |  | KRT022 | fault within installation wiring | Minor shock | 21/04/2017 16:54 |  |  | 5952 | Public space |  | 20170426PWA_01 | Infrastructure (network-based) | -38.3903 | 142.2438 | 1 | Powercor | Report | 7319 | 0.032977 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Other
CEOT dispatched a fault crew who found a streetlight head fire. The fault crew isolated supply to the streetlight fitting, made safe and arranged for repair. | 33 SASSES AVENUE, BAYSWATER VIC 3153 | 1219519 |  |  |  | Electrical breakdown |  |  | 2 | IMS 227611. MFB reported a pole fire. An AusNet Services' fault crew found a 150 Watt HPS streetlight head was on fire. The fire was contained to the 150 Watt HPS street light head (lantern). | Public lighting | 0 | 0 | 0 |  | bwr34 | Street light head fire. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors. | Other electricity related | 24/04/2017 1:40 | 1 | Negligible: no ground fire | 5953 | Residential |  | 20170426SPN_01 | Infrastructure (network-based) | -37.8514 | 145.2602 | 1 | AusNet Services Distribution | Report | 7321 | 0.031926 | Low voltage AC (<1kV) | Moorabbin Airport | 3153 | Bayswater | AF Other
On arrival crew carried out repairs | 170 MASONS LANE, BACCHUS MARSH VIC 3340 | 30112526 |  |  |  | Overheated connection |  |  | 2 | Vic fire reported a pole fire at the incident location. On arrival the fault crew found that a junction box had overheated and caught fire at the incident location. There was no ground fire and no injury as a result of this incident. | Connection box | 2 | 2 | 2 |  | BMH005 | unable to determine due to damage | Pole-top fire | 21/04/2017 8:41 | 1 | Negligible: no ground fire | 5965 | Roadway |  | 20170427PWA_04 | Infrastructure (network-based) | -37.6686 | 144.4451 | 1 | Powercor | Report | 7336 | 0.014847 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Bacchus Marsh | Pole
On arrival crew carried out repairs | 18 BURKES ROAD, TERANG VIC 3264 | 30048066 | Vehicle | [5 empty] | 2 | Powercor received a call advising of a wire down at the incident location. On arrival the crew found that an unknown truck had contacted the neutral screen LV overhead service, causing it to break mid-span and fall to the ground. There was no ground fire, no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | TRG004 | unknown vehicle struck service line | Loss of supply;Damage to network assets | 23/04/2017 13:32 |  |  | 5968 | Roadway |  | 20170427PWA_07 | Infrastructure (network-based) | -38.2397 | 142.9216 | 1 | Powercor | Report | 7339 | 0.028682 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3264 | Terang | Vehicle
On arrival crew carried out repairs | 70 HARCOURT ROAD, ALTONA VIC 3018 | 30236685 | Copper theft | [5 empty] | 2 | A Powercor Employee, reported broken HV earth at incident location near 70 Harcourt Rd, Altona. On arrival the faults crew had found that a length of 2m HV Earth had been cut away, removed and stolen. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LVN022 | cable theft | Damage to network assets | 27/04/2017 17:02 |  |  | 5973 | Roadway |  | 20170428PWA_03 | Infrastructure (network-based) | -37.851 | 144.7815 | 1 | Powercor | Report | 7344 | 0.015311 | Earthing cable | Laverton Raaf | 3018 | Altona | Other
On arrival crew carried out repairs | 75 POTTERS ROAD, ONDIT VIC 3249 | 32061990 |  |  |  | Corrosion |  |  | 2 | REC reports a conductor down and fire start at the incident location. On arrival the crew found the HV conductor had broken and was laying on a tree below, resulting in the tree smouldering. CFA attended. There were no reported shocks, injuries or ground fire start. | Conductor (bare) | 2 | 2 | 2 |  | CLC003 | conductor broken | Other vegetation | 42799.2993 | 1 | Negligible: no ground fire | 5990 | Roadway |  | 20170504PWA_01 | Infrastructure (network-based) | -38.2533 | 143.6124 | 1 | Powercor | Report | 7368 | 0.039868 | 22kV AC | Ballarat Aerodrome | 3249 | Ondit | Conductor
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Consumers Mains Junction Box at the Customerâ€™s POA, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 18 PETTITT CRESCENT, NORLANE VIC 3214 | 30294629 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Braden McKay was in the Kitchen unpacking the dishwasher when he received an electric shock as he made simultaneous contact between his hand on the metallic parts of dishwasher and his arm on the metal sink. | Service conductor | 2 | 2 | 2 |  | CRO021 | Corroded O/H Service Neutral Conductor termination | Minor shock | 29/03/2017 14:30 |  |  | 6002 | Residential |  | 20170508PWA_04 | Infrastructure (customer connection) | -38.0977 | 144.3589 | 1 | Powercor | Report | 7381 | 0.001191 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Connection
On arrival crew inspected conductors | AIRPORT, 3 AIRPORT ROAD, MITCHELL PARK VIC 3355 | 30336567 | Working too close to overhead lines | [5 empty] | 1 | A nearby customer reported that a tipper truck had hit wires on the construction site opposite at the incident locations. On arrival the crew found that a large tipper truck had been dumping fill beneath a 22kV line in the fully raised position, when the top of the tipper contacted a 22kV HV conductor. The conductors remained aloft, with the truck resting against the conductor. There were visible scorch marks on the surface of the ground, however there was no fire. There were no injuries, and the protection operated. Barricades and signs warning of the overhead conductors had apparently been pushed over and partly buried by some type of machinery at an unknown time, prior to the truck depositing the fill at this location. | Conductor (bare) | 2 | 2 | 2 |  | BAN004 | Tipper contacted conductors | Loss of supply;No Go Zone (contact) | 42952.3514 |  |  | 6010 | Construction |  | 20170508PWA_09 | Infrastructure (network-based) | -37.5194 | 143.7919 | 1 | Powercor | Report | 7390 | 0.0312 | 22kV AC | Ballarat Aerodrome | 3355 | Mitchell Park | Vehicle
On arrival crew isolated supply and arrange for pole replacement. | GOYURA EAST SCHOOL BUS ROUTE ROAD, HOPETOUN VIC 3396 | 32156721 |  | Fire |  |  |  |  | 2 | CFA advised that there was a small grass fire at incident location. On arrival the crew found there had been a 700 square mtr grass fire and pole badly at Base. The CFA had extinguished the fire and left the scene. The fire was not caused by electricity assets. There was no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | OYN005 | Externally caused grass fire burnt pole. | Grassfire | 42856.8896 | 0 | Small: 10 - 1000 sq.m | 5403 | Agricultural |  | 20170109PWA_05 | Infrastructure (network-based) | -35.7611 | 142.5345 | 1 | Powercor | Report | 6587 | 0.034802 | 12.7kV AC (SWER) | Horsham Aerodrome | 3396 | Hopetoun | Other
Replacement of Insulator and bird covers programmed. | MCKENZIE ROAD, KYABRAM VIC 3620 | 33092311 |  | Bird |  |  |  |  | 1 | Control room noted a reclose on KYM-ECA No..1 66kV line. Control Room contacted on call ZSO to perform patrol of KYM-ECA 1 66kV line. The Zone substation operator advised that he has found a centre phase to earth flashover at pole 43 of the KYM-ECA 1 66kV line the cause of which seemed to be a bird (crow) as there were burnt feathers at the base of the pole. This has resulted in approximately 1100mÂ² of burnt grass reserve. CFA had attended. There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | KYM - ECA 1 | Bird Incident | Grassfire | 42917.5222 | 1 | Medium: 1000 sq.m - 10 ha | 5404 | Roadway |  | 20170109PWA_06 | Infrastructure (network-based) | -36.3245 | 144.9779 | 1 | Powercor | Report | 6564 | 0.036059 | 66kV AC | Shepparton Airport | 3620 | Kyabram | Animal
On arrival crew carried out repairs | 3 CURRUNGHI COURT, ST ALBANS VIC 3021 | 30337731 | Vehicle | [5 empty] | 2 | A Passer-by reported UG pillar has been damaged at the incident location. Upon arrival, the Powercor crew noticed that the UG pillar cover had been damaged. The crew believe this was a possible vehicle impact but no more details available how the incident was occurred. No power interruption reported, no cable termination damage found. There was no evidence of injuries or fire. | LV Pillar | 2 | 2 | 2 |  | SSE012 | Unknown vehicle struck LV pillar | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/12/2016 10:49 |  |  | 5405 | Public space |  | 20170109PWA_07 | Infrastructure (network-based) | -37.7516 | 144.8274 | 1 | Powercor | Report | 6565 | 0.0092778 | Low voltage AC (<1kV) | Essendon Airport | 3021 | St Albans | Vehicle
CEOT dispatched a fault crew to isolate, make safe and repair. De-energised to make safe and DAO notified of incident for investigation. De-energised to make safe and DAO notified of incident for investigation. Issued as maintenance through SAP, under Notifications 102187539 and 102187609 and Orders 110455425 and 110455434. Both Orders issued as 30 day items. One order to replace HV Fused strain arm, and the other to replace droppers to HV switch. | 1425 MERRIANG ROAD, BEVERIDGE VIC 3753 | 914158 |  |  |  | Overheated connection |  |  |  | IMS 225981. Fire in vicinity of pole @ GB786 with Nth Side HV Isolators glowing red. A suspected a loose connector for a HV Isolator on pole #914158 that was seen glowing red by attending fault lines personnel failed with fallen hot molten metal igniting a grass fire of approx. 200m x 20m around and north of the pole that was extinguished by MFB. The grass fire also damaged HV earthing cover pleats and transformer LV bushing covers on s/s pole #914163. There was burnt roadside, private property vegetation and fencing damage of no. 1425 Merriang Rd. | Disconnector/isolator | 0 | 0 | 0 |  | klo14 | A loose connector on the HV isolator. | Grassfire | 42887.7917 | 1 | Medium: 1000 sq.m - 10 ha | 5393 | Agricultural |  | 20170109SPN_01 | Infrastructure (network-based) | -37.5112 | 145.0254 | 1 | AusNet Services Distribution | Report | 6545 | 0.032466 | 22kV AC | Wallan (Kilmore Gap) | 3753 | Beveridge | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The fault crew attended and found that a HV ABC had failed and observed a ground fire in the vicinity of LIS 1409918. A 5m x 10m ground fire was put out by the CFA. CEOT notified the local DAO to investigate and report. The attending DAO could not see any private property damage resulting from the small fire except for some burnt roadside vegetation. Repairs were undertaken by lines personnel to HV ABC conductor and supply restored. 2 spans of HV ABC cable being considered for replacement to eliminate high number of joints and aging conductor. | 332 MYERS CREEK ROAD, HEALESVILLE VIC 3777 | 1409917 |  |  |  | Age;Electrical breakdown |  | Phase to earth | 1 | IMS 225984. HE005 feeder CB tripped and crew allocated to investigate at HE127. There was a report of a fire in this vicinity. It is suspected a part of 4x185 sq.mm HV ABC cable insulation adjacent pole #1409917 failed with fault current then traversing the HV ABC steel cable centenary and concrete pole earthing to reclose and operate Myers Creek RD ACR on Feeder WYK24 and fallen particles of holt molten metal and plastic possibly igniting a small grass fire of approx. 5m x 10m around and north of the pole that was extinguished by CFA. | Conductor (ABC) | 0 | 0 | 0 |  | wyk24 | Vegetation: Trees Incident | Grassfire | 42917.5312 | 1 | Small: 10 - 1000 sq.m | 5394 | Agricultural |  | 20170109SPN_02 | Infrastructure (network-based) | -37.616 | 145.522 | 1 | AusNet Services Distribution | Report | 6549 | 0.0019329 | 22kV AC | Moorabbin Airport | 3777 | Healesville | OH Cable
On arrival crew isolated supply and carried out repairs. | 41 SMEATON CLOSE, LARA VIC 3212 | 33040304 |  |  |  | Overheated connection |  |  | 1 | The customer at the incident location reported that a conductor had faulted and fallen to ground. On arrival the crew found at the incident location, an LV conductor had fallen, there were signs of burning in small patches on the ground. No injury and no third party damage was reported. | Conductor (bare) | 2 | 2 | 2 |  | FNS012 | Overheated IPC connector at tee off | Grassfire | 42917.5271 | 1 | Localised: less than 10 sq.m | 5407 | Public space |  | 20170110PWA_01 | Infrastructure (network-based) | -38.0272 | 144.4228 | 1 | Powercor | Report | 6570 | 0.018806 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Conductor
On arrival crew isolated supply and commenced repairs. | 335 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631 | 30126804 | Vehicle | [5 empty] | 1 | An employee reported a car has struck pole 55 Grahamvale line. Unfortunately the incident was a fatality - Non electrically related. The HV/LV pole has fractured, HV conductors still in the air but ties broken. The LV ABC has come away from the termination and was alive on the roadway. There were no live exposed conductors at ground level or on the vehicle. The Incident was reported to ESV because of the fatality and likely media interest. After initial report NAO called back by ESV for further details @ 18:24 6/01/2017 asking whether conductors were alive. NAO advised live HV well clear of vehicle and live LV ABC on road a covered conductor, which was promptly isolated. There was no fire. | Conductor (bare);Conductor (insulated);Insulator tie wires/connections | 2 | 2 | 2 |  | SHN024 | Vehicle struck pole | Loss of supply;Not involving electrocution;Damage to network assets | 42856.6972 |  |  | 5421 | Roadway |  | 20170112PWA_04 | Infrastructure (network-based) | -36.3336 | 145.4317 | 1 | Powercor | Report | 6599 | 0.015235 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3631 | Grahamvale | Vehicle
On arrival crew carried out repairs | 1050 MURRAY VALLEY HIGHWAY, WHARPARILLA VIC 3564 | 33104974 |  | Lightning |  | Candled fuse |  |  | 2 | Nearby resident reported that pole sparking and flaming. CFA was leaving as line crew arrived. Upon arrival crew found that an EDO fuse had candled on sub pole (LIS-924576) P1 DYBALL SPURLINE. There had been recent lightning activity in the area. There was no ground fire, injuries or third party property damage | EDO fuse | 2 | 2 | 2 |  | ECA010 | Attributed to recent lightning activity | Pole-top fire | 42856.7083 | 1 | Negligible: no ground fire | 5422 | Agricultural |  | 20170112PWA_05 | Infrastructure (network-based) | -36.0923 | 144.664 | 1 | Powercor | Report | 6601 | 0.0088611 | 22kV AC | Bendigo Airport | 3564 | Wharparilla | Lightning
On arrival crew checked structure for damage Follow up action initiated to replace bird covers on this pole | 1606 BARINGHUP-EDDINGTON ROAD, BARINGHUP VIC 3463 | 33014297 |  | Bird |  |  |  |  | 1 | CFA reported a pole fire at the incident location. Upon arrival the crew found that a bird flashover on 66kV line and fell on to the ground resulting approx. 500 Sqm ground fire. The protection operated (line auto reclosed). There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BETS MRO | Bird Incident | Grassfire | 16/01/2017 7:48 | 1 | Small: 10 - 1000 sq.m | 5439 | Public space |  | 20170116PWA_06 | Infrastructure (network-based) | -36.9747 | 143.9596 | 1 | Powercor | Report | 12428 | 0.015661 | 66kV AC | Bendigo Airport | 3463 | Baringhup | Animal
CEOT dispatched a fault crew to isolate supply, make safe and carry out repairs. Crews replaced the 300kVA kiosk substation and installed LV underground straight joints as well as the HV/LV earth. | 79 AMESBURY AVENUE, WANTIRNA VIC 3152 |  |  |  |  | Electrical breakdown |  |  | 2 | IMS 225845. Fault crew were called to replace a 300kVA kiosk substation as well as LV straight joints to a LV paralleling pillar which had failed due to the cabling being old lead sheath underground cable. The LV paralleling pillar was burnt out. The fire was contained within the pillar. There was no ground /grass fire. | Pad mounted equipment/kiosk;LV Pillar | 0 | 0 | 0 |  |  | LV paralleling pillar fault due to a substation fault. | Plant/equipment | 42716.0312 | 1 | Negligible: no ground fire | 5437 | Residential |  | 20170116SPN_02 | Infrastructure (network-based) | -37.8565 | 145.2335 | 1 | AusNet Services Distribution | Report | 6626 | 0.029328 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | AF Other
CEOT dispatched a fault crew to isolate, make safe and investigate. 6 amp HV EDO fuse hung and burnt in half. The fault crew replaced a single EDO fuse tube and the substation went back into service - OK. ZA 90 day Noti 102175960 raised in SAP to replace both hung-up EDO's with BA fuse units as per policy 64-2009. | LAURENVALE, 2 TANNERS ROAD, INDIGO VALLEY VIC 3688 | 597646 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 225722. A rural customer called up a fault at 4:40 am, and reported arcing on transformer pole with sparks and lights dimming. Customer is fed via MARTINDALE 16, single phase 10kVA Substation, wood pole. Fault crew attended 05:35 am and found one of the two EDO fuse tubes burnt in half. No evidence of a fire on the pole or on the ground. | EDO fuse | 0 | 0 | 0 |  | bwa22 | Burnt EDO fuse tube. | Other electricity related | 42716.1944 | 1 | Negligible: no ground fire | 5452 | Agricultural |  | 20170117SPN_04 | Infrastructure (network-based) | -36.1648 | 146.7652 | 1 | AusNet Services Distribution | Report | 6645 | 0.010575 | 22kV AC | Wangaratta Aero | 3688 | Indigo Valley | Fuse
CEOT dispatched a fault crew and DAO to isolate, make safe and investigate. HV conductor sleeved and repaired including bridging. | 59 TOORAK ROAD, INVERLOCH VIC 3996 | 2810182 |  | Wind;Prone to salt deposition |  | Corrosion |  | Phase to earth | 1 | IMS 225792. CFA report street wire down o/s 59 Toorak Road, Inverloch, and very small grass fire in vicinity. HV centre phase 7/2.5AAC conductor failed at bridge where it has signs of corrosion at pole 2810182 Toorak Rd Spur P8, conductor falling to the ground where a small fire was noticed. Fire attended by CFA and extinguished. Very small grass fire in vicinity. Fire size 1m x 200mm in LBRA location. Feeder CB tripped to lockout. | Conductor (bare) | 0 | 0 | 0 |  | wgi34 | HV bridging failed and HV conductor fell to ground. | Grassfire | 14/12/2016 12:00 | 1 | Localised: less than 10 sq.m | 5455 | Residential |  | 20170117SPN_06 | Infrastructure (network-based) | -38.6368 | 145.7107 | 1 | AusNet Services Distribution | Report | 6649 | 0.037147 | 22kV AC | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Conductor
Brennan Drewett (ZNX Project Planner) is working through solutions with the REC and Deakin University to ensure there is adequate cover over the HV underground cable. | BURWOOD STUDENT VILLAGE, 221 BURWOOD HIGHWAY, BURWOOD VIC 3125 |  | Working too close to underground cables | [5 empty] | 2 | A REC has reported that a recently installed HV underground cable at Deakin University (Burwood Campus) has less than 600mm cover. The cable is located within private property and the conduits were audited as per the standard process prior to energisation. The University has undertaken recent landscaping works for a roadway and removed the majority of the cover for the underground cable. Deakin University has breached Regulation 312 of the Electricity Safety (Installations) Regulations by altering the level of the ground for road works that has reduced the cover over the HV underground cable. REC Scott Raymond provided United Energy As Built Drawings, Landscape Drawing, Madigan Surveying As Built Drawing and on Site Photos. The REC pointed out the discrepancy between the Madigan Surveying As Built Drawing and the existing cover depth over the high voltage underground cable. There is an area of approximately 9m under the roadway base which is constructed of a 200mm concrete slab base, 25mm screen and 60mm paving finish where there isn't the required 600mm cover. In addition, there is also an area of approximately 12m under a garden bed where there isn't the required cover after soil has been removed. | Cable | 0 | 0 | 0 |  | BH 21 | Altering the ground level over a HV underground cable. | No Go Zone (no contact) | 13/01/2017 11:00 |  |  | 5442 | Public space |  | 20170117UTD_02 | Infrastructure (network-based) | -37.8497 | 145.1145 | 1 | United Energy Distribution | Report | 6632 | 0.021035 | 22kV AC | Moorabbin Airport | 3125 | Burwood | Other
The timber substation pole was checked for damage and no major damage was sustained. The faults crew removed the electrical leads from the site. | MOOROOKYLE AVENUE, HUGHESDALE VIC 3166 | 2314407 | Vandalism | [5 empty] | 1 | At 0135hrs on 17/01/2017, 11kV ACR OA7316 located in Barkly Road successfully reclosed and held. Per MFB - Pole has been set alight and wire has been wrapped around pole causing a short circuit. The police have taken away the person responsible for the arson attack. An unknown person has poured petrol at the base of "Moorookyle-Warrigal" pole type substation and set it alight. In addition, the unknown person has thrown electrical leads over the HV overhead conductors and equipment that caused a nearby ACR to successfully reclose and hold. Police were quickly in attendance at pole No. LIS 2314407 and arrested the unknown person for the irresponsible arson attack. | Pole (wood);Pole mounted | 0 | 0 | 0 |  | OR 35 | An unknown person has poured petrol at the base of "Moorookyle-Warrigal" pole type substation and set it alight. | Damage to network assets | 17/01/2017 1:35 |  |  | 5459 | Roadway |  | 20170117UTD_03 | Infrastructure (network-based) | -37.9075 | 145.0851 | 1 | United Energy Distribution | Report | 6653 | 0.015119 | 11kV AC | Moorabbin Airport | 3166 | Hughesdale | Other
The faults crew replaced the damaged three phase FMJB and re-terminated the overhead cables before supply was restored. | 283 HIGH STREET, ASHBURTON VIC 3147 | 2300413 |  |  |  | Electrical breakdown;Electrical overload |  |  | 2 | Per MFB - substation on fire outside this property called the Milk Cloud CafÃ©. A three phase FMJB at pole No. LIS 2300413 located outside 283 High Street, Ashburton caught on fire and was extinguished prior to the faults crew attending. The cause was a probable loose connection. | Connection box | 0 | 0 | 0 |  |  | The cause was a probable loose connection. | Pole-top fire | 42716.4688 | 1 | Negligible: no ground fire | 5460 | Roadway |  | 20170117UTD_04 | Infrastructure (network-based) | -37.8633 | 145.0803 | 1 | United Energy Distribution | Report | 6654 | 0.028354 | Low voltage AC (<1kV) | Moorabbin Airport | 3147 | Ashburton | Connection
Emergency high voltage switching was completed and the HV strain crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | BLACKBURN ROAD, DONCASTER EAST VIC 3109 | 7066961 |  | Precipitation |  | Electrical breakdown |  |  | 1 | At 0645hrs on 18/01/2017, 22kV feeder NW 23 circuit breaker reclosed to lockout affecting 1330 customers. During drizzly rain, a pole fire occurred at a HV strain crossarm on pole No. LIS 7066961 located on the corner of Blackburn Road and Glenview Road, Doncaster East. The footpath side HV conductor remained attached to a burnt section of the timber crossarm that failed at the crossarm brace causing it to fall onto the LV crossarm. The faults crew suspected that a high voltage injection occurred to customers supplied from "Maxia-Blackburn" substation and a LEI attended and checked premises in the vicinity for damage with no damage identified. The cause of the crossarm fire was tracking on the grey porcelain disc insulators and the brown fog type bridging insulators. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | NW 23 | The cause of the crossarm fire was tracking on the grey porcelain disc insulators and the brown fog type bridging insulators. | Pole-top fire | 18/01/2017 6:45 | 1 | Negligible: no ground fire | 5469 | Roadway |  | 20170119UTD_02 | Infrastructure (network-based) | -37.7979 | 145.1604 | 1 | United Energy Distribution | Report | 6669 | 0.032117 | 22kV AC | Moorabbin Airport | 3109 | Doncaster East | Crossarm
The line was isolated and the conductor was repaired. | BAINGARRA, 311 NULLAN ROAD, MINYIP VIC 3392 | 32109005 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A customer reported that a farm worker on his property had driven a tipper truck into overhead power lines and bought them down. On arrival the crew found that a tip truck had contacted the SWER conductor at the incident location, the SWER conductor between Pole 14 and Pole 20 Nullan-Owen Spur had been pulled down. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. Approx. 5-6 hectares of wheat stubble was burnt. There was no other damage, no injury and no shock. | Conductor (bare) | 2 | 2 | 2 |  | HSM005 | Tipper Truck contacted conductor. | Grassfire | 19/01/2017 17:34 | 1 | Medium: 1000 sq.m - 10 ha | 5473 | Agricultural |  | 20170120PWA_01 | Infrastructure (network-based) | -36.4035 | 142.557 | 1 | Powercor | Report | 12430 | 0.00061921 | 12.7kV AC (SWER) | Horsham Aerodrome | 3392 | Minyip | Vehicle
A live line crew broke bridges to isolate the transformer. | 72-80 BUCKLEY GROVE, MOOLAP VIC 3224 | 30065968 | Vandalism;Copper theft | [5 empty] | 2 | A member of the public reported vandals stripping power cables at the incident location. On arrival the crew found that vandals had stolen a large amount of copper caballing and bus work at the customerâ€™s premises. They had also damaged earth screens, earth bars, the neutral and the doors to the kiosk / cabinet on our side. 72 â€“ 80 Buckley Grove is a disused factory, It provided services for Alcoa and has probably been shut for approximately eighteen months. Tom Chapman (Operator) attended this site on the 12th October 2016, regarding vandalism of electrical asset. There was no fire or injuries. | Earth/earthing | 2 | 2 | 2 |  | GLE031 | copper theft | Damage to network assets | 42979.7014 |  |  | 5474 | Industrial |  | 20170120PWA_02 | Infrastructure (network-based) | -38.1641 | 144.4299 | 1 | Powercor | Report | 6675 | 0.0019757 | Earthing cable | Avalon Airport | 3224 | Moolap | Other
CEOT requested a fault crew to attend. The local DAO, ESV and AusNet Services' Claims section were notified of the incident. Crew isolated and earthed the line, issued EAP and removed the paraglider from the line. | DOGWOODS, 136 HUGHES LANE, EUROBIN VIC 3739 | 4505416 | Manned aircraft |  |  |  |  | Phase to phase |  | IMS 226133. Reported that paraglider had collided with power lines. No injuries reported. Paraglider contacted single phase 22kV between poles 4505416 and 4505417. Ground clearance at approximately 35 degrees C was 6300mm on one phase and 6100mm on the other phase. Contact caused phases to clash resulting in 40E BA fuses on SW 568082 at pole 4501370 to blow. Also melted fist sized area of fabric on paraglider. Pilot had not seen HV conductors and was approximately 1 metre off the ground when his canopy contacted the conductors, hence he was able to safely release himself from the harness. Paraglider's details: Hans Bausenwean, tel 0497 492236. | Conductor (bare) | 0 | 0 | 0 |  | brt22 | A paraglider made contact withy overhead HV line. | No Go Zone (contact) | 19/01/2017 15:35 |  |  | 5479 | Agricultural |  | 20170123SPN_01 | Infrastructure (network-based) | -36.6501 | 146.8546 | 1 | AusNet Services Distribution | Report | 12340 | 0.041115 | 22kV AC | Wangaratta Aero | 3739 | Eurobin | Other
CEOT dispatched a fault crew. The overhead line was made safe and the irrigator machine was removed. The crew restored supply by replacing HV fuses at TN095. HV conductors measured and were 6.9 metres above ground clearance which met ESMS regulation height. | 3779 TRARALGON-MAFFRA ROAD, HEYFIELD VIC 3858 | 2628085 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 226160. An irrigator machine made contact with overhead HV conductors. Electrical protection operated at TN095. | Conductor (bare) | 0 | 0 | 0 |  | tgn31 | An Irrigation machine made contact with an overhead HV line. | No Go Zone (contact) | 21/01/2017 9:55 |  |  | 5480 | Agricultural |  | 20170123SPN_02 | Infrastructure (network-based) | -37.9922 | 146.7756 | 2 | AusNet Services Distribution | Report | 6684 | 0.0044294 | 22kV AC | Morwell (Latrobe Valley Airport) | 3779 | Heyfield | Vehicle
Jemena crew attended site, replaced degraded service and LV mains circuit fuse. | 6 FERGUSON STREET, SPOTSWOOD VIC 3015 |  |  |  |  | Age |  |  | 1 | Degraded service insulation caused a service fire. No photo is available for this fire start incident. | Service conductor | 0 | 0 | 0 |  | FE05 | Degraded service insulation. | Loss of supply;Other electricity related | 42380.3375 | 1 | Negligible: no ground fire | 5485 | Residential |  | 20170124JEM_01 | Infrastructure (network-based) | -37.8251 | 144.8727 | 1 | Jemena | Report | 8387 | 0.0017581 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Spotswood | OH Cable
Supply was isolated to make safe and complete repairs. | 465 SOMERVILLE ROAD, BROOKLYN VIC 3012 |  |  |  |  | Electrical breakdown |  |  | 2 | Corssarm Fire. High voltage crossarm burnt through. | Crossarm (wood) | 0 | 0 | 0 |  |  | Crossarm fire caused High Voltage Crossarm to break. | Pole-top fire | 42594.5986 | 1 | Negligible: no ground fire | 5494 | Industrial |  | 20170124JEM_03 | Infrastructure (network-based) | -37.8082 | 144.84 | 1 | Jemena | Report | 6703 | 0.029207 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | Crossarm
On arrival crew carried out repairs. The Shepparton council have been made aware of this incident and they will be speaking to the contractor involved to gather further details of the incident. | 55 WANGANUI ROAD, SHEPPARTON VIC 3630 | 32192992 | Working too close to overhead lines;Vehicle | [5 empty] | 1 | A neighbouring customer reported dim lights at the incident location. Crew attended and found 1 O/H HV conductor at P2 Demase S/L broken and was on the ground. Protection operated. Crew observed contract tip trucks working for Shepparton Council on site tipping off soil near line and believe one of these truck had contactor O/H HV. No shocks, injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHN021 | Suspect tipping operations | Loss of supply;Damage to network assets | 23/01/2017 8:19 |  |  | 5490 | Construction |  | 20170124PWA_03 | Infrastructure (network-based) | -36.3477 | 145.3954 | 1 | Powercor | Report | 6698 | 0.0031169 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Vehicle
On arrival crew carried out repairs | 47 SILVEREYE CRESCENT, WERRIBEE VIC 3030 | 33071396 |  |  |  | Corrosion |  |  | 2 | The MFB rang and advised they had extinguished a ground fire under our assets at the incident location On arrival fault crews found a low voltage copper to aluminium dee on the white phase had failed resulting in the ground fire and third party damage to a small bush. There was no injury as a result of this incident. | Dropper/bridge | 2 | 2 | 2 |  | WBE021 | connection failure | Grassfire | 23/01/2017 17:50 | 1 | Localised: less than 10 sq.m | 5492 | Public space |  | 20170124PWA_04 | Infrastructure (network-based) | -37.8793 | 144.676 | 1 | Powercor | Report | 6700 | 0.041662 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
A faults crew attended and proceeded to replace the bridge and re-terminated the 95mm LVABC with a new IPC and supply was restored. | ASHLEIGH AVENUE, FRANKSTON VIC 3199 | 3319689 |  | Heat |  | Overheated connection |  |  | 2 | CFA report that a power pole is on fire. A pole fire was reported at "Ashleigh-Beach" pole type substation at pole No. LIS 3319689 outside the IGA store where it was found that a IPC burnt out on the 95mm LVABC service. The attributing cause appeared to be a loose connection on the blue phase was the probable cause. A REC is also in attendance. | Conductor (ABC);Equipment | 0 | 0 | 0 |  |  | The attributing cause appeared to be a loose connection on the blue phase was the probable cause | Pole-top fire | 23/01/2017 10:25 | 1 | Negligible: no ground fire | 5489 | Commercial |  | 20170124UTD_02 | Infrastructure (network-based) | -38.1457 | 145.1445 | 1 | United Energy Distribution | Report | 6697 | 0.00032639 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
The crews have been instructed make safe, return supply to any customerâ€™s affected and ensure security of the substation. This building and substation are earmarked for demolition in February 2017. | 83-113 BATMAN STREET, WEST MELBOURNE VIC 3003 | 30206760 | Copper theft | [5 empty] | 2 | A fault crew were instructed to check equipment at the incident location due to traffic lights not working. On arrival the fault crew found that thieves had gained access to the substation and removed a number of earths and a quantity of copper cables from the substation. The main substation earth was also damaged. Unsuccessful attempts were made to cut into a â€œLIVEâ€ high voltage underground cable. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | VM020 | cable theft | Loss of supply;Damage to network assets | 23/01/2017 1:00 |  |  | 5501 | Commercial |  | 20170125PWA_06 | Infrastructure (network-based) | -37.8114 | 144.9498 | 1 | CitiPower | Report | 6711 | 0.020031 | Earthing cable | Essendon Airport | 3003 | West Melbourne | Other
On arrival crew carried out repairs | 1203-1225 MIDDLE ROAD, MOUNT COTTRELL VIC 3024 | 30118691 | Copper theft | [5 empty] | 2 | A passer-by reported that wires have been broken at the incident location. On arrival the fault crew found that a possum guard had been ripped from the pole and 3 meters of high voltage earths had been stolen from the substation. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LV002 | Cable theft | Damage to network assets | 24/01/2017 10:12 |  |  | 5502 | Roadway |  | 20170125PWA_07 | Infrastructure (network-based) | -37.7853 | 144.6445 | 1 | Powercor | Report | 6712 | 0.027712 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival crew carried out repairs | 1025-1051 MOUNT COTTRELL ROAD, ROCKBANK VIC 3335 | 30116112 | Copper theft | [5 empty] | 2 | Melton Police advised a customer had reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that the earthing cable on the sub pole had been stolen. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Cable theft | Damage to network assets | 20/01/2017 15:48 |  |  | 5504 | Roadway |  | 20170125PWA_09 | Infrastructure (network-based) | -37.7236 | 144.622 | 1 | Powercor | Report | 6714 | 0.019008 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply to allow customer REC to complete repairs | 79 INJEMIRA ROAD, GRASSMERE VIC 3281 | 30264091 |  |  |  | Fault on customer installation |  |  | 1 | A customer from Numeralla Dairy Co, contacted Powercor to report a loss of supply. When crews arrived they determined that a customer Krone box, attached to the substation pole at the incident location, had failed and started a small grass fire at the base of the pole that had self-extinguished. A separate Powercor Krone box is also mounted on the same pole. There were no injuries. | Customer installation | 2 | 2 | 2 |  | KRT012 | fault in customers Krone box | Grassfire | 29/01/2017 7:01 | 0 | Localised: less than 10 sq.m | 5513 | Industrial |  | 20170130PWA_01 | Infrastructure (network-based) | -38.2503 | 142.5299 | 1 | Powercor | Report | 6726 | 0.024803 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3281 | Grassmere | AF Other
On arrival crew isolated supply and carried out repairs. | 29 BAEL BAEL ROAD, TRESCO VIC 3583 | 31021765 |  | Bird |  |  |  |  | 1 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a swan had struck HV 3 phase steel conductors between pole 21 & pole 22 of the Tresco spur line, the swan fell to the ground and ignited an area of grass, approximately 50M x 40M was burnt. There were no reported injuries, no 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHL005 | Bird Incident | Grassfire | 27/01/2017 22:39 | 1 | Medium: 1000 sq.m - 10 ha | 5514 | Roadway |  | 20170130PWA_02 | Infrastructure (network-based) | -35.4694 | 143.6558 | 1 | Powercor | Report | 6727 | 0.0002581 | 22kV AC | Swan Hill Aerodrome | 3583 | Tresco | Animal
On arrival crew carried out repairs. | 19 LEE STREET, KANGAROO FLAT VIC 3555 | 30235097 | Working too close to underground cables | [5 empty] | 1 | A Bobcat operator reported that while carrying out surface landscaping his machine has hit a pole and smoke was coming from the pole at the incident location. Upon arrival, the Powercor crew found that the Bobcat had made contact with cable head pole near ground level. The impact punctured the steel cover protection and pierced the underground 22kv cable. The resultant arcing caused the pole to ignite. The protection operated. There were no injuries or ground fire. | Pole (wood);Cable | 2 | 2 | 2 |  | BET004 | Bobcat contacted underground cable on cable head pole | Pole-top fire;Loss of supply;No Go Zone (contact) | 27/01/2017 14:02 | 1 | Negligible: no ground fire | 5519 | Public space |  | 20170130PWA_04 | Infrastructure (network-based) | -36.8203 | 144.244 | 1 | Powercor | Report | 6734 | 0.031057 | 22kV AC | Bendigo Airport | 3555 | Kangaroo Flat | Vehicle
On arrival crew completed repairs | 895 ARCHER ROAD, KIALLA VIC 3631 | 32191546 |  |  |  | Corrosion |  |  | 2 | Customer reported a fire on a pole at the incident location. On arrival the crew found that a LV FSD had failed due to suspected poor connection and caught on fire, molten plastic fell to the ground but no ground fire resulted. | Connection box | 2 | 2 | 2 |  | STN021 | Connection Failure | Pole-top fire | 22/01/2017 21:25 | 1 | Negligible: no ground fire | 5537 | Roadway |  | 20170201PWA_07 | Infrastructure (network-based) | -36.4603 | 145.4083 | 1 | Powercor | Report | 6759 | 0.0064456 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Kialla | Connection
CEOT dispatched a fault crew to isolate, make safe, investigate and carry out necessary repairs. The fault crew replaced the Krone box (FSD) and repaired burnt cables and restored supply. | 90 MCMILLAN STREET, LUCKNOW VIC 3875 | 1610888 |  |  |  | Unknown technical factor |  |  | 2 | IMS 225879. Received INCD for part supply failure at this address. Upon investigation found a melted Krone box (FSD). Two small grass fires were observed at the base of the pole. One fire was approximately 6m x 4m in size and the other was approximately 3m x1m in size. The Krone box was melted from heat/fire with no direct cause found for the damage. Grass fires in the vicinity of pole. | Connection box | 0 | 0 | 0 |  | BDL4 | Cause was not determined. | Grassfire | 21/12/2016 6:55 | 1 | Small: 10 - 1000 sq.m | 5534 |  |  | 20170201SPN_01 | Infrastructure (network-based) | -37.8234 | 147.6581 | 1 | AusNet Services Distribution | Report | 11246 | 0.0070845 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Lucknow | Connection
CEOT dispatched an AusNet Services' LEI and a fault crew to isolate, make safe and investigate. The LEI on arrival noticed that the neutral was not connected at the customerâ€™s FOLCB at the POA. An NST test was completed which failed. Neutral to earth measurement was found to be 42 Volts. The fault truck reconnected the neutral at the customerâ€™s FOLCB. After repairs were completed another NST test was conducted which passed, and the neutral to earth measurement was found to be 0 Volts. | 41 PERRINS CREEK ROAD, KALLISTA VIC 3791 | 1309237 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 225886. Customer reports shocks from bath and shower, customer OK. No other damage. Customer touched tap and received an electric shock. The cause of the incident was the service neutral conductor wasnâ€™t connected at the FOLCB at the POA - it appeared to have fallen out of its connection terminal. | Service conductor | 0 | 0 | 0 |  | bge11 | Service cable neutral conductor had fallen out of the customer's FOLCB at the POA. | Minor shock | 22/12/2016 8:35 |  |  | 5535 | Residential |  | 20170201SPN_02 | Infrastructure (network-based) | -37.8774 | 145.3728 | 1 | AusNet Services Distribution | Report | 6757 | 0.032787 | Low voltage AC (<1kV) | Moorabbin Airport | 3791 | Kallista | OH Cable
Faults crew attended site and unravelled the burnt wire from the HV overhead reticulation. LEI checked for damage to customer property, and it was made safe. All other properties unaffected . | 420 BELGRAVE-GEMBROOK ROAD, GEMBROOK VIC 3783 |  | Caused by REC/contractor;Blown detritus |  |  | HV injection |  |  | 0 | IMS 225917. A council tractor was cutting grass on the roadside when its blades came into contact with a Telstra phone line. It was thrown up into the air and wrapped itself around the 22KV O/H reticulation between poles 416674 abd 416675. This cause a HV injection into the Telstra phone system and burnt out various jboxes on pole no. 416673 and damaged the phone system at customer property 420 BELGRAVE GEMBROOK RD, GEMBROOK. A high voltage injection was confirmed. No AusNet Services' fuses were blown. | Conductor (bare) | 0 | 0 | 0 |  |  | It appears that the Telco cable had been disconnected and coiled up on the ground. Grass had grown over the cable which prevented the mowing contractor from seeing it when he mowed the grass. This incident was caused by Telco and mowing contractor, and as such not AusNet Services' responsibility. | HV injection | 23/12/2016 11:50 |  |  | 5538 | Residential |  | 20170201SPN_03 | Infrastructure (network-based) | -37.947 | 145.5346 | 1 | AusNet Services Distribution | Report | 12342 | 0.032622 | 22kV AC | Moorabbin Airport | 3783 | Gembrook | Other
On arrival crew carried out repairs | HATTAH-ROBINVALE ROAD, WEMEN VIC 3549 | 32141451 |  |  |  | Leakage |  |  | 2 | Customer reported a low wire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang approximately 4.0M above ground at the lowest point. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | WMN013 | Excessive leakage current | Pole-top fire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/01/2017 10:55 | 1 | Negligible: no ground fire | 5542 | Roadway |  | 20170202PWA_02 | Infrastructure (network-based) | -34.7807 | 142.6402 | 1 | Powercor | Report | 6765 | 0.027634 | 22kV AC | Mildura Airport | 3549 | Wemen | Crossarm
CEOT dispatch a fault crew to make safe, investigate and repair. The crew replaced the substation transformer, the Boric Acid fuse and the lightning arrestor. | 260 CLONBINANE ROAD, CLONBINANE VIC 3658 | 4701417 |  | Lightning |  |  |  |  | 2 | IMS 225923. A fault crew were sent to all an supply fault and found a 6K Boric Acid fuse had hung-up with minor candling/burning of the fuse tube. The crew also found a blown transformer and damage to a lightning arrestor. Lightning is suspected as the cause. | Boric acid;Surge diverter;Transformer | 0 | 0 | 0 |  | smr3 | Slightly burnt / candled Boric Acid fuse tube. | Other electricity related | 24/12/2016 17:30 | 1 | Negligible: no ground fire | 5541 | Agricultural |  | 20170202SPN_02 | Infrastructure (network-based) | -37.3184 | 145.0693 | 1 | AusNet Services Distribution | Report | 7923 | 0.039451 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3658 | Clonbinane | Fuse
A LEI and faults truck attended and commenced an investigation to the cause. Voltage tests between various points of the installation to an independent earth measured 30v. The faults crew checked the single phase overhead connections at the POA and pole ends and identified a loose neutral connection consumers FMJB at the POA. They proceeded to clean, grease and re-terminate the neutral connection. Installation tests at the completion confirmed the fault had been rectified. | 16 THE TROSSACHS, FRANKSTON VIC 3199 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Customer advised of dimming lights and received a tingle from the shower taps a few days ago. The occupier has noticed the recent dimming of lights and received a slight electric shock to her hand when showering and contacted the United Energy faults and emergencies call centre. | Connection box;Customer installation | 0 | 0 | 0 |  |  | A loose neutral connection at the POA was the cause. | Minor shock | 25/01/2017 10:00 |  |  | 5546 | Residential |  | 20170203UTD_01 | Infrastructure (customer connection) | -38.161 | 145.151 | 1 | United Energy Distribution | Report | 12327 | 0.014192 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
CEOT dispatched a fault crew to make safe investigate and repair. The fault crew ascertained that the terminals in a service cable junction had burnt out. The fault crew replaced the junction box. | 203 NEPEAN STREET, GREENSBOROUGH VIC 3088 | 901742 |  |  |  | Overheated connection |  | Phase to phase | 2 | IMS 225934. Report of a pole fire to CEOT. The fault crew attended and found that a service cable pole junction box allegedly caught fire above the LV crossarm on a concrete pole. LIS 901742. | Connection box | 0 | 0 | 0 |  | wt7 | Pole junction box fire. | Other electricity related | 29/12/2016 6:55 | 1 | Negligible: no ground fire | 5565 | Residential |  | 20170206SPN_04 | Infrastructure (network-based) | -37.7134 | 145.1054 | 1 | AusNet Services Distribution | Report | 6797 | 0.0047187 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | Connection
CEOT dispatched a Fault crew to isolate, make safe and investigate. The crew attended site and found that the earth for the SWER ISO transformer was dug up and needs to be re re-buried deeper. The earth wire had not been broken. | 150 ELTHAM-YARRA GLEN ROAD, KANGAROO GROUND VIC 3097 | 925623 | Working too close to underground cables | [5 empty] | 2 | IMS 225945. Customer reports he has dug up under ground cable at base of pole. Customer is OK. No other damage. Appears the SWER earth was dug up at Avalon ISO transformer. | Earth/earthing | 0 | 0 | 0 |  | elm33 | Customer dug up SWER earthing conductor. | No Go Zone (contact) | 30/12/2016 13:05 |  |  | 5566 | Agricultural |  | 20170206SPN_05 | Infrastructure (network-based) | -37.7018 | 145.2129 | 1 | AusNet Services Distribution | Report | 6798 | 0.019249 | 12.7kV AC (SWER) | Moorabbin Airport | 3097 | Kangaroo Ground | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions prior to the supply being restored. | NEPEAN HIGHWAY, ELSTERNWICK VIC 3185 | 2308669 |  | Animal |  | Electrical breakdown |  |  | 1 | At 2212hrs on 04/01/2017, 11kV feeder EW 03 circuit breaker reclosed to lockout affecting 675 customers. A possum was found at the base of the CHP to "Nepean-McMillan" indoor substation that also caused damage to the electrical infrastructure. The HV red phase bridge was blown at the tee-off in Nepean Highway on the corner of Glendora Avenue along with the red phase HV conductor on the ground at the two way tee-off to "New-Rusden" indoor substation - pole number LIS 2308212. A very small patch of grass estimated to be 3sq cm in size was found burnt outside 37 Nepean Highway that self extinguished. | Conductor (bare) | 0 | 0 | 0 |  | EW 03 | Bird Incident | Grassfire | 42826.8417 | 1 | Localised: less than 10 sq.m | 5556 | Residential |  | 20170206UTD_01 | Infrastructure (network-based) | -37.8872 | 145.0004 | 1 | United Energy Distribution | Report | 11266 | 0.030475 | 11kV AC | Moorabbin Airport | 3185 | Elsternwick | Animal
The faults crew isolated the capacitor bank and the capacitor bank lead was cut clear with rectification work to be programmed at the earliest opportunity. | SIMPSON STREET, MOORABBIN VIC 3189 |  |  |  |  | Electrical breakdown |  |  | 1 | Pole fire per MFB. The blue phase HV fuse operated at "Powlett-Simpson" capacitor bank after the lead of the capacitor bank blew off. The cause was unknown and no customers were affected with flames seen when the HV fuse operated. | Pole top;EDO fuse;Surge diverter | 0 | 0 | 0 |  | HT 13 | The cause of the event was unknowm. | Pole-top fire | 20/01/2017 7:25 | 1 | Negligible: no ground fire | 5558 | Industrial |  | 20170206UTD_02 | Infrastructure (network-based) | -37.9477 | 145.0746 | 1 | United Energy Distribution | Report | 6786 | 0.0068704 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | AF Other
On arrival crew commenced repairs | 247 ST ALBANS ROAD, SUNSHINE NORTH VIC 3020 | 30113060 | Working too close to underground cables | [5 empty] | 2 | Anthony Selvaggi 0499 800 222 from Express Demolition called to advice that they have dug up the HV cable during excavation of footings and live cable exposed at the incident location(former City West Water site). On arrival the crew found that an excavation had occurred. There were no reported injuries, no fire and no HV injection. | Cable | 2 | 2 | 2 |  | SSE014 | contractor carrying out excavations | No Go Zone (contact);Damage to network assets | 42918.6806 |  |  | 5570 | Industrial |  | 20170208PWA_01 | Infrastructure (network-based) | -37.767 | 144.8173 | 1 | Powercor | Report | 6808 | 0.0060347 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Dug up
White phase LV fuse at transformer (Gordon-Bell) supplying LV circuit operated. Section was isolated and connector and fuse replaced on the night of the incident. Conductors repaired. | 297 BELL STREET, COBURG VIC 3058 |  |  |  |  | Mechanical breakdown |  |  | 1 | Wires down corner of Bell St and Bruce St due to full tension sleeve failure. The conductor fell on the roadway below situated along Bell street (approximate address: 297 Bell St, Coburg VIC 3058) Jemena informed by the MFB at approximately 16:30 White phase conductor is just before an LV open point and failed on the supply end, so it was not live on ground. | Conductor (bare) | 0 | 0 | 0 |  | CS02 | Full tension sleeve failure Crew was not able to identify any cause of failure for the LV sleeve on the day of the incident. | Loss of supply | 17/12/2016 15:35 |  |  | 5581 | Residential |  | 20170209JEM_02 | Infrastructure (network-based) | -37.7395 | 144.9489 | 1 | Jemena | Report | 12390 | 0.04065 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | AF Other
The attending faults crew isolated and replaced the damaged FMJB and reconnected supply to the school that was now closed. | CENTRE ROAD, CLAYTON VIC 3168 | 8804574 |  | Heat |  | Overheated connection |  |  | 2 | Per MFB - Pole fire outside Clarinda Primary School in Centre Road on the corner of Crawford Road. During warm afternoon conditions, a three phase FMJB containing an underground cable supplying the Clarinda Primary School on pole No. LIS 8804574 was burnt out due to probable overload. | Services cable;Connection box | 0 | 0 | 0 |  |  | The cause was due to probable overload on the hot day. | Pole-top fire | 42949.625 | 1 | Negligible: no ground fire | 5577 | Roadway |  | 20170209UTD_01 | Infrastructure (network-based) | -37.9265 | 145.102 | 1 | United Energy Distribution | Report | 6816 | 0.0068171 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Pole
On arrival crew carried out repairs | 305-329 FERRIS ROAD, MELTON SOUTH VIC 3338 | 30107878 | Copper theft | [5 empty] | 2 | Mrs Maryrose Portelli phoned in to advise that she believes vandals have cut earth wire on transformer pole opp her driveway. She can see wire running down the pole & goes underground has large cut. No problems with supply to house. There was no fire, injuries or third party property damage | Earth/earthing | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 30/01/2017 16:52 |  |  | 5600 | Roadway |  | 20170213PWA_06 | Infrastructure (network-based) | -37.72 | 144.6027 | 1 | Powercor | Report | 6850 | 0.021633 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Initial report: CEOT dispatched a fault crew to make asset safe and isolate service to hay shed. Final report: Crew attended property to isolate supply as per request from AusNet Services' control room. Remedial works performed and fuse replaced. Several dead magpies were identified within a 5m radius of the substation pole, and pole showed significant signs of bird activity (droppings). EDO fuse replaced with Boric Acid fuse unit. | 172 BASIN ROAD, BENALLA VIC 3672 | 597128 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 226356. Initial report: Fire at Hayshed. Crew dispatched to make safe. The DAO reported the fire was under control and he would investigate futher in the morning. Pole inspector required. Claims notified. Still under investigation. Final report: Transformer pole adjacent to property fire in hay bales. It appears the fire may have started when an EDO fuse candled. | EDO fuse;Yet to be determined | 0 | 0 | 0 |  | BN3 | Candled EDO fuse tube. | Property;Other electricity related | 42980.7014 | 1 | Small: 10 - 1000 sq.m | 5590 | Agricultural |  | 20170213SPN_01 | Infrastructure (network-based) | -36.5372 | 145.9252 | 1 | AusNet Services Distribution | Report | 11248 | 0.0023252 | 22kV AC | Wangaratta Aero | 3672 | Benalla | Fuse
CEOT dispatched a fault crew. Operator sent out to isolate faulty cable and restored supply to rest of the customers. The local DAO was notified and an underground crew to investigate magnitude of damage. CEOT dispatched a fault crew. Operator sent out to isolate faulty cable and restored supply to rest of the customers. The local DAO was notified and an underground crew to investigate magnitude of damage. Underground crew attended site to find underground boring machine has damaged HV underground cable between Galloway-View Hill and Charolais-Jersey substations. Contractor did not have an auto reclose suppression or a Permit to Work to excavate around HV cable - (please note that this previous clause has been clarified as per Greg Sieburn's request). Underground crew removed damaged section of cable and did straight joint to join cable together. Supply restored. | 20 CHAROLAIS STREET, TRARALGON VIC 3844 | 5816227 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 226390. Tony Howden from CKE - 0428666507 was drilling an under road bore for the gas and drilled upon a HV Cable. No injuries occurred. Protection operated and de-energised faulted section. | Cable | 0 | 0 | 0 |  | tgn11 | A 3rd party contractor caused an underground boring machine to contact a live underground HV cable. | No Go Zone (contact) | 43010.6111 |  |  | 5591 | Residential |  | 20170213SPN_02 | Infrastructure (network-based) | -38.1793 | 146.5047 | 1 | AusNet Services Distribution | Report | 12347 | 0.0090313 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Dug up
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT advised the local DAO to investigate and complete fire report. Crew isolated line, removed tree branch and made safe. Construction crew made repairs to the overhead line, removed branch and put existing substations back into service after conducting appropriate tests. | 255 BEENAK ROAD, YELLINGBO VIC 3139 | 1316030 |  | Blown branch/vegetation |  |  |  | Phase to earth | 2 | IMS 226393. Attending DAO report: Call came through from the CEOT advising that there had been a fire cause by a branch down in Yellingbo. Fire had been put out, and the construction crew were already out on site. Attended site. Spoke to first response crew who had advised that the line was now isolated. Proceeded to take photos and notes of the site. Branch came down between Pole#1316030 and Pole#1316031. The contact with the line and the branch has caused a small fire to start. The fire did not spread from the immediate area. Construction to repair existing line, remove branch and put existing substations back in service after conducting appropriate tests. Overhead line to be repaired. Branch to be removed. Line to be placed back in service once line reconnected. | Conductor (bare) | 0 | 0 | 0 |  | ldl13 | Vegetation: Trees Incident | Grassfire | 43041.6667 | 1 | Localised: less than 10 sq.m | 5592 | Agricultural |  | 20170213SPN_03 | Infrastructure (network-based) | -37.8561 | 145.5438 | 1 | AusNet Services Distribution | Report | 7926 | 0.015444 | 12.7kV AC (SWER) | Moorabbin Airport | 3139 | Yellingbo | Trees
CEOT dispatched a fault crew to make safe, investigate and repair. Isolated and made safe. Replaced BA fuse tube and restored supply. | 1432 GEORGES CREEK ROAD, GEORGES CREEK VIC 3700 | 5212292 |  | Lightning |  |  |  |  | 2 | IMS 226394. Under INCD-129421-r @ LIS #5212292, a 6K BA fuse tube candled due to lightning in the vicinity. No fire occurred. | Boric acid | 0 | 0 | 0 |  | wots24 | Lightning in the vicinity. | Other electricity related | 43071.2396 | 1 | Negligible: no ground fire | 5594 | Agricultural |  | 20170213SPN_04 | Infrastructure (network-based) | -36.1559 | 147.2608 | 1 | AusNet Services Distribution | Report | 7960 | 0.028969 | 12.7kV AC (SWER) | Wangaratta Aero | 3700 | Georges Creek | Lightning
On arrival crew carried out repairs | 171-211 ALFRED ROAD, STRATHTULLOH VIC 3338 | 30104658 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a switch pole at the incident location. The earthing was removed from ground level to two metres up the pole. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Cable theft | Damage to network assets | 30/01/2017 16:49 |  |  | 5601 | Roadway |  | 20170214PWA_01 | Infrastructure (network-based) | -37.7211 | 144.5993 | 1 | Powercor | Report | 12433 | 0.024876 | Earthing cable | Laverton Raaf | 3338 | Strathtulloh | Other
On arrival crew carried out repairs | 115 ALFRED ROAD, MELTON SOUTH VIC 3338 | 30304622 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from ground level to two metres up the pole. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Cable theft | Damage to network assets | 30/01/2017 16:49 |  |  | 5602 | Roadway |  | 20170214PWA_02 | Infrastructure (network-based) | -37.7214 | 144.6066 | 1 | Powercor | Report | 12434 | 0.028737 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Emergency high voltage switching was completed with LV parallels installed to maintain supply to customers in the small street and the 22kV transformer was replaced under Access Authority conditions. Supply was restored upon completion. | MCGUIRE STREET, CHELTENHAM VIC 3192 | 1819881 |  | Precipitation |  | Electrical breakdown |  |  | 0 | At 1134hrs on 13/02/2017, 22kV feeder HT 11 circuit breaker reclosed to lockout affecting 33 customers. During light drizzly rain, the blue phase HV fuse assembly faulted with pieces of porcelain contacting a vehicle (no damage) and a small grass fire estimated to be 3 x 2m starting in the surrounds of "McGuire-Warrigal" ground type substation containing pole No. LIS 1819880. The 22kV transformer was found to have faulted and requires replacement. | Powder filled;Outdoor | 0 | 0 | 0 |  | HT 11 | The 22kV transformer failed in the ground type substation that caused the HV fuse unit to explode. | Grassfire | 13/02/2017 11:34 | 1 | Localised: less than 10 sq.m | 5613 | Industrial |  | 20170214UTD_03 | Infrastructure (network-based) | -37.9531 | 145.0759 | 1 | United Energy Distribution | Report | 11267 | 0.017767 | 22kV AC | Moorabbin Airport | 3192 | Cheltenham | Fuse
The attending Powercor Fault Crew reterminated the broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. | 302 THE ESPLANADE, INDENTED HEAD VIC 3223 | 33042745 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Lou Talevski was turning on the front garden tap when he received an electric shock as he made contact with his hand on the handle of the metal tap. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA, which was identified as the cause of the high impedance within the neutral conductor. | Connector/termination | 2 | 2 | 2 |  | DDL013 | Broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA. | Minor shock | 28/12/2016 9:00 |  |  | 5622 | Residential |  | 20170215PWA_04 | Infrastructure (network-based) | -38.1379 | 144.7105 | 1 | Powercor | Report | 6876 | 0.0089016 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Indented Head | OH Cable
CEOT dispatched a fault crew and a LEI to make safe, investigate and carry out any necessary repairs on network assets. As reported by the customer a loud bang was heard at the gas meter and a small fire was reported to the MFB. The fire brigade attended and extinguished the fire and turned off the gas supply. INCD-129788-r â€“ replaced faulty meter at 32 Washusen Rd â€“ Old 4313424, New 4152370. LEI attended site and completed an NST that passed at 36 Washuen Rd, Heathmont. Also checked for voltage on the house gas main and found no volts. For preventative measures against animal flashovers this pole structure and has stretched insulators and Raychem covers on HV bridges for 22kV. In general 66kV should have adequate clearance for bird/animal issues. There are no insulated covers for 66kV. Preventative measures in accordance with asset maintenance guidelines. On 3 March regarding an incident at 2 Karen Court, Heathmont, where the RWTS-BWR Line tripped and reclosed at 02:39 â€“ GCEOT canâ€™t be certain but believes / is possible that the line trip here may have been caused by a possum. RWT15 Earth Fault current pick up to 46.1A on 2/3/17 21:50:33 according to an instantaneous SCADA limit alarm. We agree that both incidents were at the same pole. The pole structure has our standard HV clearances. We think the neutral being against the stay may have enabled the flashover to earth via the stay, and into the gas network seeking the best path to earth, resulting in stray gas at the meter igniting. The flashover has welded the arm bracket to the pole reo, confirming that it probably went to earth via the stay). The only way a spark could be detected at the gas meter would be if the bonding lead was attached after the meter was removed. In this case the stay voltage in the earthing system is most likely a result of a defect on the customer side and not a result of the flashover, i.e a faulty appliance or power board. An action has been placed on the maintenance group to also provide greater separation between the neutral conductor and the pole guy as a subsequent incident. For 2 Karen Court we recently dispatched another fault crew to recheck that the electrical supply was safe - NST test completed and passed, 0 Volts on neutral bar and at gas meter, disconnected smart meter antenna due to previous gas meter fire and the meter is OK. It has been reported that the possums in this area are very large animals and are very prolific. | 30 WASHUSEN ROAD, HEATHMONT VIC 3135 | 1204917 |  | Animal | Highly unlikely |  |  | Phase to earth | 1 | IMS 226488. Pole Lis 1204917 (ILFORD SUNSET), 66kV injection into neutral via Optus earth by a possum on a concrete pole with steel crossarms. Incident caused a gas meter explosion at 36 Washusen Rd. An AusNet Services' LEI was dispatched to inspect customer's appliances for damage. The LEI attended and found: damaged to 3 properties 30, 31, and 32 Washusen Rd and a blown up gas meter at 36 Washusen Rd, Also no display on meter at 32 Washusen Rd. Substation fuse didn't blow. RWTS-BWR Line tripped and reclosed at 04:50. RWT15 White phase current pick up to 1037A on 15/2/17 01:33:28 according to a SCADA limit alarm. (note only white phase has an alarm set). | Conductor (bare);Guy wire;Crossarm (steel);Pole (concrete) | 0 | 0 | 0 |  | RWT15 | Bird Incident | HV injection;Property | 16/02/2017 5:00 | 1 | Negligible: no ground fire | 5637 | Residential |  | 20170217SPN_01 | Infrastructure (network-based) | -37.8372 | 145.2404 | 1 | AusNet Services Distribution | Report | 11250 | 0.032561 | 66kV AC | Moorabbin Airport | 3135 | Heathmont | Animal
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The crew found a blown fuse and a grass fire approximately 35m x 35 m in size at the base of the pole. Final report: CEOT turned off the power upstream at Switch WO029. The linesmen opened the gas switch 831890 at pole 1 Upper Sandy Creek spur(5217958). The top and bottom sections of damaged fuse tube were removed with a telescopic stick and supply was restored at the upstream switch WO029. The damaged sections of the fuse tube came out of the holder easily and the brass fittings showed evidence of any damage. The fuse holder was examined with binoculars and it also showed no signs of damage. The striker pin had pierced the end of the tube. The brass fittings were reattached to a new 12k BA fuse tube and installed in the fuse holder at pole 1 Upper Sandy Creek spur (5217958). The gas switch 831890 was closed and supply restored to the balance of customers downstream of the fused switch. The linesmen observed some molten plastic (red) and other items believed to be from the fuse tube on the ground under the damaged BA fuse tube approximately 1m east of the pole within the burnt area. A lightning storm had passed through the area earlier in the day with 2 fuses replaced at switch pole 602466 downstream of switch 831890 following a lightning strike at 1317. | 41 MILLER LANE, CHARLEROI VIC 3695 | 5217958 |  | Lightning |  | Electrical breakdown |  |  | 2 | IMS 226507. Initial report: CEOT received a report of a fire at the base of a pole. A Boric Acid fuse hung-up and the fuse tube was arcing /burnt in the middle with molten material falling to the ground. A medium size grass fire was observed at the base of the pole. Final report: Linesmen were dispatched to a report of a fire by CFA at pole 1 Upper Sandy Creek spur(5217958). On arrival they found the CFA on-site who had extinguished the fire. They also observed a BA Fuse hung-up in the fuse holder on the southern side of the pole, arcing between the top and bottom sections of the fuse tube. The fire size was approximately 800 sq. metres. The fire spread was limited due to some green grass within the burnt area, rain had fallen earlier in the day from storms and the wind was reported as light to none by the linesmen on sight. The area burnt appears to be all on road reserve, however part of the burnt area is fenced as part of the adjoining land holder's land. His fence runs through the burnt area. | Boric acid | 0 | 0 | 0 |  | wots13 | Candled/burnt Boric Acid fuse tube. | Grassfire | 17/02/2017 17:25 | 1 | Small: 10 - 1000 sq.m | 5639 | Agricultural |  | 20170220SPN_01 | Infrastructure (network-based) | -36.2891 | 147.1188 | 1 | AusNet Services Distribution | Report | 6906 | 0.030961 | 22kV AC | Wangaratta Aero | 3695 | Charleroi | Fuse
CEOT dispatched a fault crew to make safe, investigate and repair. The crew replaced the damaged 250 Amp FSD with a new 400 Amp FSD Krone box with 3 x 200 Amp LV fuses. | 1571 FERNTREE GULLY ROAD, KNOXFIELD VIC 3180 | 1311306 |  |  |  | Overheated connection |  |  | 2 | IMS 226090. Krone box (FSD) on pole caught fire. No fire on ground, contained to the Krone box. | Connection box | 0 | 0 | 0 |  | bra13 | Believe the cause was overheating. | Other electricity related | 17/01/2017 15:55 | 1 | Negligible: no ground fire | 5654 | Commercial |  | 20170222SPN_01 | Infrastructure (network-based) | -37.8944 | 145.2494 | 1 | AusNet Services Distribution | Report | 7955 | 0.0080856 | Low voltage AC (<1kV) | Moorabbin Airport | 3180 | Knoxfield | AF Other
Conductor was repaired and put back in service. Notification was raised to have seven spans in this section replaced with LV ABC in the next 6 months. | 50 TUPPEN STREET, YARRAVILLE VIC 3013 | Pole no. A044917 |  | Wind |  | Mechanical breakdown |  |  | 2 | LV conductor down in car park adjacent to 50 Tuppen St, Yarraville between poles A044917 and A044916. Possibly caused by high winds on the day. Closer inspection of the failed conductor following the incident found that the conductor had broken at a point mid-span where conductors had previously clashed. LV spreaders had been fitted prior to the conductor failing. | Conductor (bare) | 0 | 0 | 0 |  | FW08 | Mechanical failure caused by previous conductor clashing and triggered on the day by possible high wind gusts (75 km/h). | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/12/2016 16:32 |  |  | 4357 | Residential |  | 20161229JEM_01 | Infrastructure (network-based) | -37.8153 | 144.8774 | 1 | Jemena | Report | 12380 | 0.01495 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions prior to the supply being restored. | WAVERLEY ROAD, MOUNT WAVERLEY VIC 3149 | 602729 |  | Animal |  | Electrical breakdown |  |  | 1 | At 0318hrs on 24/12/2016, 22kV feeder GW 03 circuit breaker successfully reclosed and held. Emergency services were called to a pole fire in Waverley Road on the corner of Coolarn Street, Mount Waverley. A possum caused a large flashover on the HV/LV intermediate pole with a tee-off to "Coolarn-Waverley" substation. The MFB were in attendance as the timber pole was badly damaged and pole No. LIS 0602729 required replacement. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | GW 03 | Bird Incident | Pole-top fire | 24/12/2016 3:18 | 1 | Negligible: no ground fire | 4351 | Roadway |  | 20161229UTD_01 | Infrastructure (network-based) | -37.8863 | 145.1419 | 1 | United Energy Distribution | Report | 5474 | 0.028836 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Animal
On arrival crew carried out repairs | 70 OSWELLS ROAD, BOORCAN VIC 3265 | 30042574 |  |  |  | Electrical overload |  |  | 2 | Vicfire reported a 'J'box on building at dairy on fire at the incident location. On arrival the crew found a customer switchboard had caught fire above the meterboard. The fuse at the pole FOLCB servicing the property Overheated and fell to the ground. There was a ground fire, no injuries and there were scorch marks on the fence posts but no structural damage. | Connection box | 2 | 2 | 2 |  | CDN006 | Following fault on customers switchboard the fuse in FOLCB operated and fell to ground. | Loss of supply;Grassfire | 30/12/2016 17:43 | 1 | Small: 10 - 1000 sq.m | 4371 | Roadway |  | 20170103PWA_01 | Infrastructure (network-based) | -38.2127 | 143.0406 | 1 | Powercor | Report | 8386 | 0.040263 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Boorcan | Fuse
CEOT dispatched a fault truck to attend LIS#5201337. The fault crew attended and confirmed location and cause of incident. The crew found that a magpie damaged a 5-shed insulator. A grass fire of 250 sq. metres in size had been extinguished at the site. The local DAO was notified to attend. One outer 5-shed insulator had previously been replaced due to an incident at the pole. Remaining two 5-shed insulators replaced under EAP with 9-shed tie-top insulators this time. | 22 KIEWA VALLEY HIGHWAY, KIEWA VIC 3691 | 5201337 |  | Bird |  |  |  | Phase to earth | 1 | IMS 225927. Magpie across insulator @ LIS 5201337. A 5 Shed insulator was damaged. Grass fire reported by CFA. EAP required to change the Insulator'. Phone call from CFA was at 0744hrs. WOTS11 reclose was at 0701hrs. Magpie bridged from crossarm to top of 5-shed vertical insulator. Raychem cover and grey-back installed but no disc at base of insulator. Feeder CB tripped. | Insulators | 0 | 0 | 0 |  | wots11 | Bird Incident | Grassfire | 26/12/2016 7:00 | 1 | Small: 10 - 1000 sq.m | 4378 | Residential |  | 20170103SPN_03 | Infrastructure (network-based) | -36.2611 | 147.0091 | 1 | AusNet Services Distribution | Report | 5504 | 0.0084664 | 22kV AC | Wangaratta Aero | 3691 | Kiewa | Animal
CEOT dispatched a fault crew to isolate, make safe, investigate and repair. The fault crew attended and found a pine tree down over HV & LV conductors. A 15 sq. metre fire was on the ground in the vicinity. The local DAO attended. For further details please refer to the Select Solutions' Arborist's Assessment and Fault Report. The 15 sq. metre grass fire had been extinguished and the Downer construction crew were on-site when the local DAO arrived. The fault crew repaired four spans of HV/LV conductor which had came down. The local DAO advised that no HVI damage had occurred to properties. | 775 WHITTLESEA-KINGLAKE ROAD, PHEASANT CREEK VIC 3757 | 1401497 |  | Wind;Fallen;MEC |  |  |  | Phase to earth | 1 | IMS 225932. Feeder off on KLK1-2. Report of a wire down in a paddock. A large pine tree broke off near base and fell across HV/LV overhead line just south of pole 1400108. A small grass fire was started mid-span between poles 5765123 and 1401497. | Conductor (bare) | 0 | 0 | 0 |  | KLK1 | Vegetation: Trees Incident | Grassfire | 28/12/2016 12:35 | 1 | Small: 10 - 1000 sq.m | 4379 | Agricultural |  | 20170103SPN_04 | Infrastructure (network-based) | -37.4823 | 145.2909 | 1 | AusNet Services Distribution | Report | 11243 | 0.029134 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3757 | Pheasant Creek | Trees
On arrival crew isolated supply and carried out repairs | 77 PERTOBE ROAD, WARRNAMBOOL VIC 3280 | 31029748 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Powercor received a number of calls from the public and Vicfire reporting a â€œcraneâ€ had hit wires in Pertobe Rd and had brought them to ground, opposite the Carnival site. When crews arrived they found that up to 5 bays of LVABC were on the road and Public Lighting was damaged. Police and CFA were in attendance. There was no shock, injuries, ground fire or other third party property damage reported. | Conductor (insulated) | 2 | 2 | 2 |  | WBL008 | Crane in travelling mode contacted ABC cable | Damage to network assets | 19/12/2016 16:21 |  |  | 4384 | Roadway |  | 20170105PWA_01 | Infrastructure (network-based) | -38.3928 | 142.4804 | 1 | Powercor | Report | 5528 | 0.02585 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
crew isolated and assisted REC replace under verandah fused isolation point | UNIT 5 64 THE TERRACE, OCEAN GROVE VIC 3226 |  |  |  |  | Fault on customer installation |  |  | 2 | Vic fire reported property structure fire Attending crew found customers fuse mount had overheated. | Customer installation | 0 | 0 | 0 |  | DDL011 | Connection failure | Property | 31/12/2016 12:44 | 0 | Negligible: no ground fire | 5388 | Commercial |  | 20170106PWA_03 | Infrastructure (network-based) | -38.268 | 144.5225 | 1 | Powercor | Report | 6538 | 0.0082743 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Fuse
CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. CEOT also advised the local DAO to investigate and report. The fault crew carried out repairs to the LV cables and connections. | 271 BUSHY PARK-VALENCIA CREEK ROAD, BUSHY PARK VIC 3860 | 2513880 |  |  |  | Overheated connection |  |  | 2 | IMS 225988. Vic Fires advised AusNet Services' that substation pole LIS 2513880 Boisdale North 15 needs to be checked as a fire is in the vicinity of the pole base. The fire size was approximately 30 sq. metres on the road reserve and in a paddock. The fire was extinguished by the CFA before the arrival on site by the attending AusNet Services' DAO. There was no damage to private property other than burnt grass. The cover of the 2 LV cables joined onto the Blue phase of the under crossarm LV fuse isolator had visibly melted. The cause was determined to be a loose connection on the LV fuse isolators on load side at the substation. | Connector/termination | 0 | 0 | 0 |  | mfa21 | Loose LV connection at LV fuse at substation resulting in a high impedance and overheated connection. | Grassfire | 42948.5104 | 1 | Small: 10 - 1000 sq.m | 5397 | Agricultural |  | 20170109SPN_04 | Infrastructure (network-based) | -37.8477 | 147.0099 | 1 | AusNet Services Distribution | Report | 6560 | 0.02562 | Low voltage AC (<1kV) | Bairnsdale Airport | 3860 | Bushy Park | Connection
On arrival crew carried out repairs | 111 FYANS STREET, SOUTH GEELONG VIC 3220 | 30061878 | Vehicle | [5 empty] | 2 | A customer informed a truck has pulled down a cable at the incident location. Upon arrival the crew found that the insulated three phase live service had been lying on the ground. There were no reported injuries or fire. | Service conductor | 2 | 2 | 2 |  | GL033 | vehicle struck service line | Loss of supply | 42826.4375 |  |  | 5417 | Roadway |  | 20170111PWA_06 | Infrastructure (network-based) | -38.1633 | 144.3604 | 1 | Powercor | Report | 6582 | 0.00056944 | Low voltage AC (<1kV) | Avalon Airport | 3220 | South Geelong | Vehicle
LEI tested and confirmed supply was connected. Fault crew attended and abolished supply | 160 BATTEN ROAD, ARMSTRONG CREEK VIC 3217 | 30067527 | Unauthorised work | [5 empty] | 2 | Powercor LEI attended premises to review supply arrangements. On arrival it was observed that the house had been removed and the meter panel was lying on the ground. The supply remained connected through the energized underground consumers mains and live terminals were exposed. There was no fire or injuries reported. | Meter board (including fuses);Customer installation | 0 | 0 | 0 |  | WPD024 | Interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42979.5444 |  |  | 5419 | Agricultural |  | 20170112PWA_02 | Infrastructure (network-based) | -38.2316 | 144.3638 | 1 | Powercor | Report | 6597 | 0.026895 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Armstrong Creek | Other
Fault crew attended, isolated supply and issued defect notice. | 24 FAIRWATER DRIVE, POINT COOK VIC 3030 | 30264804 | Unauthorised work | [5 empty] | 2 | Powercor meter technician working in area observed metal meter enclosure had been dislodged and was hanging upside down by underground cables. The meter enclosure was tested and not found not energized however there was damage to the insulation of the underground cables. Supply arrangement was temporary supply in permanent position No injuries or other damage identified | Meter board (including fuses);Customer installation | 0 | 0 | 0 |  | LV004 | Interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42795.5708 |  |  | 5420 | Construction |  | 20170112PWA_03 | Infrastructure (network-based) | -37.906 | 144.7175 | 1 | Powercor | Report | 6598 | 0.0016678 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Crew attended and checked conductor prior to restoring supply | 26 LERDERDERG PARK ROAD, MERRIMU VIC 3340 | 33072468 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A customer reported that his light truck has contacted HV line at the incident location. Upon arrival, the Powercor crew found that the HV conductors over the agricultural farm had been contacted by a hydraulic lighting tower towed by a tractor. No damage to the conductor or visible damage to the tower. The protection operated. There were no injuries or fire. | Conductor (bare) | 0 | 0 | 0 |  | BMH006 | Interference | Loss of supply | 43070.3056 |  |  | 5425 | Agricultural |  | 20170113PWA_01 | Infrastructure (network-based) | -37.6564 | 144.4518 | 1 | Powercor | Report | 6609 | 0.0022037 | 22kV AC | Laverton Raaf | 3340 | Merrimu | Vehicle
Emergency high voltage switching was completed and the HV termination crossarm was replaced under Access Authority conditions. Supply was restored upon completion. | 21 KARDINIAN AVENUE, CHELTENHAM VIC 3192 | 1813390 |  | Precipitation |  | Insulator;Leakage |  |  | 1 | At 1259hrs on 28/12/2016, 22kV feeder HT 01 circuit breaker reclosed to lockout affecting 556 customers. Following light drizzly rain, a pole fire occurred at a HV termination crossarm on pole No. LIS 1813390 located in Joyce Street, Cheltenham. The cause was suspected to be tracking on the HV disc insulator causing the termination crossarm to burn and fail. The conductor fell to the ground but no high voltage injection occurred. Note: The address has been created on the corner of Kardinian Avenue as there are no homes fronting Joyce Street. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | HT 01 | The cause was suspected to be tracking on the HV disc insulator causing the termination crossarm to burn and fail. | Pole-top fire | 28/12/2016 12:59 | 1 | Negligible: no ground fire | 5424 | Residential |  | 20170113UTD_01 | Infrastructure (network-based) | -37.9666 | 145.081 | 1 | United Energy Distribution | Report | 6606 | 0.010109 | 22kV AC | Moorabbin Airport | 3192 | Cheltenham | Crossarm
CEOT dispatched a fault crew to make safe and carry out necessary repairs. The crew found and replaced blown EDO HV fuse and damaged candling fuse holder. Located 2m x 4m grass fire in the vicinity which was extinguished by customer. CEOT notified the local DAO to investigate. Candling fuse found no apparent reason found, evidence of grass fire at the base of pole. The fire was out when the crew arrived. | 301 TAMBO UPPER ROAD, SWAN REACH VIC 3903 | 1900002 |  |  | Highly unlikely | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 225985. Customer reported line down and something melting opposite 301 Tambo Upper Rd. EDO fuse blown and candling fuse tube. A grass fire at the base of the pole was extinguished by the customer. NOTE - this IMS was not work flowed by CEOT until 12 January thus the late reporting in OSIRIS. | EDO fuse | 0 | 0 | 0 |  | BDL41 | EDO fuse hang-up and candled fuse tube. | Grassfire | 42917.6319 | 1 | Localised: less than 10 sq.m | 5429 | Agricultural |  | 20170116SPN_01 | Infrastructure (network-based) | -37.797 | 147.8575 | 1 | AusNet Services Distribution | Report | 11244 | 0.01438 | 22kV AC | Bairnsdale Airport | 3903 | Swan Reach | Fuse
On arrival crew carried out repairs | 110 CLARKES ROAD, LETHBRIDGE VIC 3332 | 31012957 |  | Bird |  |  |  |  | 1 | System Controller reported that Lethbridge P179 ACR had operated with a nearby grassfire being attended to by CFA . Attending crew found steel conductor had broken between P7 and P8 Burr spur line resulting in a small ground fire. There was no third party damage or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | GL015 | Bird Incident | Grassfire | 15/01/2017 7:29 | 1 | Localised: less than 10 sq.m | 5443 | Roadway |  | 20170117PWA_01 | Infrastructure (network-based) | -37.9535 | 144.0935 | 1 | Powercor | Report | 12429 | 0.020627 | 22kV AC | Avalon Airport | 3332 | Lethbridge | Conductor
On arrival crew identified fault and completed repairs | 160 BULLOCK SWAMP ROAD, CORAGULAC VIC 3249 | 30054319 |  |  |  | Corrosion;Overheated connection |  |  | 2 | A farmer reported that a small grassfire had started on his property. He stated that a nearby pole had been sparking, smoking and glowing orange. The attending crew found evidence of a small grass fire which had been extinguished by the farmer. Inspection of pole identified a corroded and overheated LV isolator connection. There was no third party damage or injuries reported. | Disconnector/isolator | 2 | 2 | 2 |  | CLC003 | corrosion of joint | Grassfire | 15/01/2017 10:56 | 1 | Localised: less than 10 sq.m | 5444 | Agricultural |  | 20170117PWA_02 | Infrastructure (network-based) | -38.2629 | 143.5535 | 1 | Powercor | Report | 6635 | 0.0042789 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3249 | Coragulac | Connection
On arrival crew carried out repairs | 362 ALBERT STREET, SEBASTOPOL VIC 3356 | 30001216 | Vehicle | [5 empty] | 2 | Vic fire reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an unknown vehicle had contacted the LV overhead service, causing it to scrape on a metal saddle and drop debris to the ground, resulting in a small grassfire of approx. 10m x 20m = 200m2 on the road reserve. There was no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | BAS022 | Unknown vehicle brushed service line | Grassfire | 16/01/2017 13:22 | 1 | Small: 10 - 1000 sq.m | 5453 | Public space |  | 20170117PWA_03 | Infrastructure (network-based) | -37.6182 | 143.8339 | 1 | Powercor | Report | 6647 | 0.023243 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Sebastopol | Vehicle
On arrival crew carried out repairs | 316 ST GEORGES ROAD, THORNBURY VIC 3071 | 30197792 |  |  |  | Overheated connection |  |  | 2 | MFB reported a fire at the pole outside 316 St Georges Rd. On arrival the crew found that a krone box had burnt and required replacement. The krone box was open at the time of the fault & the cause of the fire was attributed to a loose connection. There were no reported injuries, ground fire or property damage. | Connection box | 2 | 2 | 2 |  | NC013 | connection failure | Pole-top fire | 29/12/2016 19:05 | 1 | Negligible: no ground fire | 5456 | Roadway |  | 20170117PWA_04 | Infrastructure (network-based) | -37.76 | 144.9935 | 1 | CitiPower | Report | 6650 | 0.018072 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Connection
Made site safe, replaced HV Crossarm | 22 BROADMEADOWS ROAD, TULLAMARINE VIC 3043 |  |  | Precipitation |  | Leakage |  |  | 2 | A small high voltage crossarm fire started on footpath phase of the pole. The high volatge crossarm was replaced. | Crossarm (wood) | 0 | 0 | 0 |  |  | The high voltage crossarm fire was as a result of electricity leakage during periods of light rain/drizzle following a dry period. | Pole-top fire | 18/01/2017 7:00 | 1 | Negligible: no ground fire | 5463 | Roadway |  | 20170118JEM_01 | Infrastructure (network-based) | -37.7064 | 144.8792 | 1 | Jemena | Report | 6743 | 0.0024514 | 22kV AC | Essendon Airport | 3043 | Tullamarine | Pole
Crew assessed site, made safe and undertook repairs. Copper theft was reported to Sunbury police station. Police officer took down details and advised that police report will be sent to Jemena Broadmeadows depot. | 60 BUCKLAND WAY, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Approximately 100 meters of 16ml covered 4 core low voltage underground cable was stolen. Cable was located in the nature strip outside the property of 60 Buckland Way from Pole A004056 (Buckland Way-p8 Substation to customers services pit). Last time seen intact was on the 30/11/2016 when the same section of cable was stolen. | Cable | 2 | 2 | 2 |  |  | Unknown person stole the underground mains from the pole to pit. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/01/2017 10:01 |  |  | 5465 | Public space |  | 20170118JEM_02 | Infrastructure (network-based) | -37.6063 | 144.7239 | 1 | Jemena | Report | 12384 | 0.036282 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew completed repairs | ST GEORGES ROAD, CORIO VIC 3214 | 30073835 |  |  |  | Corrosion |  |  | 1 | The CFA reported to Powercor wires down in Foreshore Rd, Corio. A reclose was recorded on FNS032 feeder. Attending crew found centre phase HV conductor had fallen to the ground at incident location. The conductor had failed at strain termination fitting. The conductor on the ground was fed through the windings of the down-stream transformer/s, causing small spot fires/burns to the grass. There was no third party damage or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | FNS032 | Overheated connection | Grassfire | 16/01/2017 21:14 | 1 | Medium: 1000 sq.m - 10 ha | 5462 | Public space |  | 20170118PWA_01 | Infrastructure (network-based) | -38.0742 | 144.3952 | 1 | Powercor | Report | 6659 | 0.004912 | 22kV AC | Avalon Airport | 3214 | Corio | Connection
On arrival crew carried out repairs. The contractor involved with the road installation is to be contacted and discussion held about the issues found. | 203 SMYTHES ROAD, DELACOMBE VIC 3356 | 30004548 | Working too close to underground cables;Unauthorised work | [5 empty] | 1 | A REC rang to advise a customer had no supply on the red and blue phases at their premises . A crew attended and found that the main LV U/G cable feeding the street had blown red and blue LV fuses on the cable head at P37. it was discovered the location of the fault btn the red and blue phases had been previously repaired by an unknown third party and subsequently failed. The site of the failure corresponded to where a service road had been installed last year for a new subdivision. No shocks, injuries, third party damage or ground fire starts. | Cable | 2 | 2 | 2 |  | BAS021 | Attributed to road construction at previous time | Loss of supply;No Go Zone (contact) | 43040.3451 |  |  | 5481 | Roadway |  | 20170123PWA_02 | Infrastructure (network-based) | -37.5899 | 143.8122 | 1 | Powercor | Report | 6685 | 0.034627 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Delacombe | Fuse
On arrival crew commenced repairs. Environmental cleanup initiated at pole 10 | 15 DAVIES LANE, PORTLAND WEST VIC 3305 | 32134228 |  | Lightning |  |  |  |  | 1 | Customers reported a loss of supply and a wire down following a lightning strike at the incident location. The SWER conductor had broken and was on the ground between P8 and P10 Logan S/L. P9 had been struck by lightning. There was also a 2m/sq patch of grass burnt at the base of P9. A burnt area of approx. 30m in length occurred btn P8A and P9. At P10, the pole mounted TX had failed, dropping oil at the base of the pole. There was no run off of oil from site. CFA attended and extinguished the fire. No shocks, injuries or third party damage. | Conductor (bare);Pole mounted | 2 | 1 | 2 |  | PLD006 | Lightning strike | Loss of supply;Grassfire;Damage to network assets | 19/01/2017 23:07 | 1 | Small: 10 - 1000 sq.m | 5482 | Agricultural |  | 20170123PWA_03 | Infrastructure (network-based) | -38.3372 | 141.518 | 1 | Powercor | Report | 6686 | 6.1343e-05 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3305 | Portland West | Lightning
On arrival crew carried out repairs | 740 DICKINS ROAD, FRESHWATER CREEK VIC 3217 | 32079759 |  |  |  | Overheated connection |  |  | 2 | A customer reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an LV fuse box overheated, causing it to drop debris to the ground, resulting in a small grassfire on the road reserve and part private property. There was no reported third party damage or any injuries. | Connection box | 2 | 2 | 2 |  | WPD014 | unable to determine due to damage sustained | Loss of supply;Grassfire | 19/01/2017 22:21 | 1 | Small: 10 - 1000 sq.m | 5483 | Roadway |  | 20170123PWA_04 | Infrastructure (network-based) | -38.253 | 144.2476 | 1 | Powercor | Report | 6687 | 0.037903 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Freshwater Creek | Fuse
On arrival crew organised cable replacement. | 76 CYCLAMEN AVENUE, ALTONA NORTH VIC 3025 | 30105080 | Copper theft | [5 empty] | 2 | A crew attending to provide a customer connection found that the UG service cable had been stolen at the incident location. This was a 26m long 16mm service cable. Note: the supply was disconnected at the time of theft. There were no reported injuries or other damage. | Services cable | 2 | 2 | 2 |  | BLT031 | Theft of service cable | Damage to network assets | 17/01/2017 14:47 |  |  | 5484 | Roadway |  | 20170123PWA_05 | Infrastructure (network-based) | -37.828 | 144.8497 | 1 | Powercor | Report | 6688 | 0.035779 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
On arrival crew isolated fault and arranged repairs | 74 MONTGOMERYS LANE, WOODEND VIC 3442 | 41110718 |  | Bird |  |  |  |  | 1 | WND Z/S/S was station black. Upon attending the crew found that a crow had shorted out the cap bank and had blown up the lower insulator on one of the reactors within the cap bank. Some flash marks were evident on the capacitor bank itself. There were no third party damage or injuries reported. | Zone substation | 2 | 2 | 2 |  | WND011 | Bird Incident | Loss of supply | 43040.7312 |  |  | 5486 | Other | Substation | 20170124PWA_01 | Infrastructure (network-based) | -37.3348 | 144.5167 | 1 | Powercor | Report | 12086 | 0.019403 | 22kV AC | Wallan (Kilmore Gap) | 3442 | Woodend | Animal
On arrival crew carried out repairs. | 2 WARNE STREET, BRUNSWICK VIC 3056 | 30157700 | Copper theft | [5 empty] | 2 | A crew attending to provide a customer connection found that the UG service cable had been stolen at the incident location. This was a 10m long 16mm service cable. There were no reported injuries or other damage. | Services cable | 2 | 2 | 2 |  | BK011 | Cable Theft | Damage to network assets | 17/01/2017 17:01 |  |  | 5488 | Roadway |  | 20170124PWA_02 | Infrastructure (network-based) | -37.7598 | 144.9585 | 1 | CitiPower | Report | 6695 | 0.0098438 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Other
Crew isolated supply and made repairs, at both sites | 6 WOOD STREET, LONG GULLY VIC 3550 | 30031270 |  | Bird |  | Electrical breakdown |  | Phase to earth | 1 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a bird had made contact with the surge divertor on HV cable head structure. The bird apparently fell to the ground and ignited a small area of grass at the base of the pole, approximately 1M square was burnt. The resulting fault current appears to have ruptured a connection in Susan street Ironbark leading to a second fire of some 50 sq metres There were no reported injuries or 3rd party damage. | Conductor (covered uninsulated);Conductor (bare) | 0 | 0 | 0 |  | BET002 | Bird Incident | Grassfire | 26/01/2017 17:16 | 1 | Small: 10 - 1000 sq.m | 5509 | Residential |  | 20170127PWA_02 | Infrastructure (network-based) | -36.7398 | 144.2665 | 1 | Powercor | Report | 12096 | 0.0056516 | 22kV AC | Bendigo Airport | 3550 | Long Gully | Animal
Replaced service line and connections into customers connection enclosure | 65 SCOTCHMANS ROAD, BELLARINE VIC 3223 | 30065422 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | CFA fire investigator requested assistance to determine cause of grass fire. No fault / outage reports had been received for a small grass fire that had occurred several days previously. Attending crew lowered service cable to private pole to assist fire investigation. Crew identified overheated connection in customers API box on private pole and remnants of cable tie where CFA had identified the location of grass fire ignition. Crew replaced service, reconnected and restored supply. There was no injuries or third property damage. | Service conductor;Connector/termination | 0 | 0 | 0 |  | DDL021 | Overheated connection at POA | Grassfire | 23/01/2017 15:22 | 1 | Small: 10 - 1000 sq.m | 5511 | Agricultural |  | 20170127PWA_03 | Infrastructure (customer connection) | -38.1473 | 144.6047 | 1 | Powercor | Report | 6724 | 0.021634 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Bellarine | Connection
A faults crew attended and removed the single phase overhead service to 39 Andrew Street that was alive with bare terminations. The meter from the property had also been abolished and couldn't be located on site. | 39 ANDREW STREET, OAKLEIGH VIC 3166 |  | Unauthorised work | [5 empty] | 2 | House on the property has been demolished and the overhead service has been left wrapped around the pole. Unknown persons have removed the single phase ZLPE overhead service at a demolished property and wrapped the live service around the pole across the road. Signage at the demolished property indicates that SBM Demolishers proudly demolished the home. | Aluminium twisted (XLPE);Smart meter | 0 | 0 | 0 |  |  | Unsafe removal of an overhead service as a home was being abolished. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/01/2017 14:00 |  |  | 5512 | Residential |  | 20170127UTD_05 | Infrastructure (network-based) | -37.9093 | 145.0937 | 1 | United Energy Distribution | Report | 6725 | 0.031985 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh | Other
Techsafe Electrical Inspector, Faults Crew and Jemena Works Practices responded and attended onsite as soon as possible and checked for damage. No notifications or work orders have been raised to repair any Jemena assets. Jemena also provided HB15 feeder protection relay event sequence to ESV. | 1 MENZIE GROVE, EAGLEMONT VIC 3084 | Pole no. A016848 | Working too close to overhead lines |  | Highly unlikely |  |  | Phase to earth | 2 | Tradesman working on Scaffolding received electric shock while using extendable metal tape measure | Conductor (bare) | 0 | 0 | 0 |  | HB15 | Tradesmans using extendable metal tape measure made contact with High voltage bare overhead conductor | Medical attention (first aid/doctor/hospital) | 30/01/2017 9:34 |  |  | 5515 | Residential |  | 20170130JEM_01 | Infrastructure (network-based) | -37.7684 | 145.0577 | 1 | Jemena | Report | 12470 | 0.035845 | 11kV AC | Essendon Airport | 3084 | Eaglemont | Other
CEOT dispatched a fault crew to attend the site to make safe, investigate and check for any damage to network assets. CEOT notified the local DAO, entered the incident in IMS and advised ESV. When the fault truck arrived, AusNet Services' technical representatives said the tip truck and CFA were gone from the site, and they spoke with the owner Russell Whinray, aged 52, and explained they needed to check the condition of the powerline, and he said ok. After the technical representatives had observed minor burn marks on the conductor, and stepped out the burnt area, he advised the CEOT, who restored power remotely at SWER ACR WN216 at 19.58. A pile of mulch was observed to the east of the SWER line, and a burnt area approximately 10 square metres was observed to the west of the line, where it is likely that the tipping truck was set up. A technical representative asked if everybody was ok and particularly if the driver of the truck was ok. Russell responded that it had arced 3 times and the driver had then got out of the truck, after it stopped. Russell admitted it was the third or fourth time he had contacted power lines. A technical representative pulled out a camera and was standing past the contact area, and was about to commence taking photos, starting with towards pole 21, when the owner came out quite upset and told him not to take photos of his private property. The technical representative said he was only doing his job, but the owner became upset, and admitted it was the 3rd time he had contacted power lines, and he was angry that he had been made to pay for replacement of a pole that he knocked over previously, when in his opinion it was already rotten, and it had cost him $4,000. The technical representatives decided discretion was the best course of action and left the property. CEOT Dispatch advised the local DAO at 20.30. With the extreme heat recently, The DOA decided to leave it a while, for the owner to perhaps get over his initial shock, and that I should then be able to talk to him. With IMS reminders, the DAO decided to visit on Monday 13 Feb. The DAO realised he had left my phone at home, but decided to continue the journey of approximately 40-50 minutes. The DAO arrived some time after 14.30, parked near the substation, near the house, and knocked at the door of the house. A lady in perhaps her young twenties answered, and she is the daughter Morgan. The DAO said he was there to have a look at where the truck had contacted the powerlines. Her father had just left to go into town. In general conversation she said she had not been present when the incident occurred, and that her father he was upset that it had happened, and that the truck was associated with Chapman Grains, Mark and Claire Chapman, who have the hot bread bakery in Woolworths in Yarrawonga. She said Chapmans had offered the mulch for nothing, as they needed to get rid of it. She had once worked at the bakery in secondary school years. She later rescinded this information, stating that she must have been confused. She tried to call Russell, and then called her mother. Her mother said it was ok to have a look, but no photos, until Russell had been spoken to. The DAO stepped out from substation pole 20, a 12.5-12 concrete pole with stretched post insulator, some 60 metres to the alleged site. I estimated the height of the conductor to be approximately 9 metres. The DAO drew a sketch, and Morgan approached me with her phone. Her father had called her back and wanted to talk to me. Morgan had already conveyed my earlier statement to her that it was unlikely that Ausnet Services would be billing for this incident. The DAO told him his name and that he was from Ausnet Services, the power company, and was having a look at the site. He said I had upset his daughter, which I denied, as we had got on fine I later asked her if she was upset, and she stated she was not. I was told to leave the property, no buts, and he was turning around and returning to the property, and if I was there when he arrived there would be hell to play. He was also going to report me to AusNet Services. The DAO said that he respected his wish not to take photos, and he again repeated his earlier demand for me to leave, and his threat. The DAO asked him to listen, that he wanted to convey the safety aspects of having wheel bearings and tyres on the tip truck checked, but he hung up on the DAO. | 114 WHINRAYS ROAD, WILBY VIC 3728 | 5131906 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 226201. A tip truck (owner and registration unknown), delivered a load of dark material described as mulch, to a property 114 Whinray Rd, Wilby, to a property owned by Russell Whinray, and at 18.18 contacted the 12.7kV SWER line, approximately 60 metres from pole 20 Hargreaves spur (5131906) towards pole 21 (5131907). A small grass fire started - approximately 10 sq. metres in size. CFA put fire out, ACR tripped to lockout. | Conductor (bare) | 0 | 0 | 0 |  | wn2 | Tip truck made contact with overhead SWER ine. | Grassfire;No Go Zone (contact) | 25/01/2017 18:20 | 1 | Small: 10 - 1000 sq.m | 5517 | Agricultural |  | 20170130SPN_01 | Infrastructure (network-based) | -36.1552 | 146.0497 | 1 | AusNet Services Distribution | Report | 8380 | 0.0012083 | 12.7kV AC (SWER) | Wangaratta Aero | 3728 | Wilby | Vehicle
On arrival crew carried out repairs | 1 CHURCH STREET, NHILL VIC 3418 | 30077836 |  |  |  | Corrosion |  |  | 2 | Vic Fire reported a service down and a ground fire at the incident location. On arrival the crew found that an LV neutral screen service had broken away from the roller at the POA, falling to the ground alive. The sparking service ignited some straw mulch in a garden bed resulting in a ground fire of approx. 10m x 2m = 20m2 on private property. There was no other reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | NHL016 | Service Failure | Grassfire | 31/01/2017 13:48 | 1 | Small: 10 - 1000 sq.m | 5530 | Residential |  | 20170201PWA_02 | Infrastructure (network-based) | -36.3331 | 141.6441 | 1 | Powercor | Report | 6752 | 0.0028484 | Low voltage AC (<1kV) | Horsham Aerodrome | 3418 | Nhill | OH Cable
On arrival crew carried out repairs | 32 PORTER STREET, WOOLSTHORPE VIC 3276 | 32196229 | Working too close to overhead lines | Within clearances |  |  |  |  | 2 | A customer reported that he was chopping the limb of a tree, and the limb had fallen on the service at the incident location. On arrival the crew found that the customer had fallen a limb onto his service cable, resulting in the service cable breaking at the house end, and falling to the ground alive. There was no ground fire, no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | KRT012 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact);Damage to network assets | 21/01/2017 13:57 |  |  | 5532 | Residential |  | 20170201PWA_04 | Infrastructure (network-based) | -38.1862 | 142.4373 | 1 | Powercor | Report | 6754 | 0.01534 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3276 | Woolsthorpe | Trees
Fire was extinguished by MFB. Plant was inspected and deemed fit to switch through. Section was isolated and repairs initiated under Access Permit. | 23 STIRLING STREET, FOOTSCRAY VIC 3011 | 10245052 |  | Precipitation;Industrial or urban pollution |  | Insulator;Leakage |  |  | 2 | MFB attended and extinguished pole fire. Section isolated and HV X-Arm to be replaced under Access Permit. The cause of the fire was tracking on the road phase brown fog type 22KV high voltage insulator. | Pole (wood);Crossarm (wood);Insulators | 0 | 0 | 0 |  | Fdr FE6 | Airborne pollution or dust built up on the insulators and crosssarms, which caused the leakage current to track. When insulation levels are compromised because of contamination or moisture consumption, leakage current flow, or tracking, can increase and, under certain conditions, can create enough heat to result in a pole top fire. In this case, the pole top fire was due to tracking on the road phase brown fog type 22KV high voltage insulator to the high voltage wooden crossarm. | Pole-top fire | 42857.9979 | 1 | Negligible: no ground fire | 5552 | Residential |  | 20170205JEM_01 | Infrastructure (network-based) | -37.7959 | 144.9034 | 1 | Jemena | Report | 6778 | 0.026987 | 22kV AC | Essendon Airport | 3011 | Footscray | Pole
On arrival crew carried out repairs | 9 THYRA STREET, SUNSHINE VIC 3020 | 32178417 |  |  |  | Corrosion |  |  | 2 | Ms Jillian Powell reported a service down and a ground fire at the incident location. On arrival the crew found the service cable had ruptured at the house end termination, falling to the ground. The sparking service ignited some grass area in the garden resulting in a ground fire of approx. 1m x 1m on private property. There was no other reported third party damage or any injuries. | Service conductor;Neutral screen | 2 | 2 | 2 |  | SSE014 | Service cable ruptured at house end termination. | Loss of supply;Grassfire | 42857.4861 | 1 | Localised: less than 10 sq.m | 5553 | Residential |  | 20170206PWA_01 | Infrastructure (network-based) | -37.7946 | 144.8249 | 1 | Powercor | Report | 6779 | 0.020103 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine | OH Cable
The fault crew isolated supply, removed the damaged meter. The meter was replaced and restored supply. | FCTY 7 146-148 HIGH STREET, MELTON VIC 3337 | 30112225 |  |  |  | Defective component |  |  | 2 | Mr. John Tieppo reported meter is all black and burning smell coming from it at the incident location. On arrival the Powercor crew found meter had burnt internally. No external damage to cables or switch board. There was no ground fire. There were no reported injuries or third party property damages. | Smart meter | 2 | 2 | 2 |  | MLN021 | Internal fault, no further detail available | Loss of supply;Melting or smoking only | 42830.7236 |  |  | 5557 | Industrial |  | 20170206PWA_02 | Infrastructure (network-based) | -37.6843 | 144.598 | 1 | Powercor | Report | 7484 | 0.038237 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | AF Other
CEOT dispatched an AusNet Services' LEI to make safe and investigate. All tests and checks performed by the LEI revealed voltage of 242 Volts, which was made safe after the LV overhead conductor was removed from the phone line. Voltage tests between an independent earth and various points of the electrical installation, including the M.E.N. and metallic water pipe system, the distribution assets revealed a constant voltage of 0 Volts. An NST test carried at the MSB - pass result. Installation was safe and left on supply. | 390 ST HELENA ROAD, ELTHAM NORTH VIC 3095 | 926486 |  | Wind |  | Mechanical breakdown |  | Phase to earth | 2 | IMS 225941. Electric shock on downpipe. Everyone OK. REC turned off main switch but still getting 240V on roof & downpipe. Customeris Fred Hunt, 0455208999. REC is Robin 0418109148. Fred was removing leaves from his drain during a storm when he received an electric shock to his right hand after touching the down pipe. It was found that the insulator that supported the Blue phase LV overhead reticulation broke loose after a storm and lay across an overhead phone line. It is believed that the live LV conductor had worn back some insulation on the phone line catenary which in turn energised the phone line raiser bracket on the house which it was attached. The raiser bracket had a strainer that was attached to the metal roof, which energised the roof and associated parts. The attending AusNet Services' LEI believes that the current flow travelled through the phone line catenary, through the phone line raiser bracket, through the strainer, through the roof, down the downpipe, through the victim to earth and back to the substation. The Linesman removed the O/H LV conductor and made it safe. | Conductor (bare) | 0 | 0 | 0 |  | elm12 | It was found that the insulator that supported the Blue phase LV overhead conductor broke loose after a storm and the insulator and LV conductor laid across the overhead telephone line wearing the telephone line cable to its catenary wire. This in turn impressed 240 V onto the telephone catenary which livened up the telephone cable's termination raiser bracket and strain fitting at the house end and thus livened up the metal roof and down pipe. It is a possibility that during this storm event vegetation may have contacted the LV insulator and caused it to break, but there is no evidence of this. There was no damage to the electricity service cable or the POA. | Minor shock | 30/12/2016 13:50 |  |  | 5567 | Residential |  | 20170206SPN_06 | Infrastructure (network-based) | -37.687 | 145.1358 | 1 | AusNet Services Distribution | Report | 12344 | 0.033919 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham North | AF Other
Fault crew repaired damage LV isolator. Fire was extinguished by the fire department. | 48 LYNNES ROAD, ST CLAIR VIC 3995 | 2804984 |  |  |  | Overheated connection |  |  | 2 | IMS 225901. Small fire in waist high dry grass 4x6m size. Weather as per below, fault called in about 7pm, the local DAO was called at 8:30pm 22/12/16. Wood pole, wood LV xarm. Fire in road reserve just outside South Gippsland Water pump station (LBRA location). Fire size was 24 sq. metres. No damage to any property, just the grass. Blue phase fence side LV isolator replaced. Description in INCD - 22835 says Upon further investigation when putting sub on load crew realised loose connection on LV isolator was the cause of the fault. Crew repaired damaged LV isolator. PLEASE NOTE - the IMS did not have an Electrical tab by CEOT so this incident was not identified by Network Safety until we worked on the Quarterly Report for 2016, thus the reason for the late reporting. | Disconnector/isolator | 0 | 0 | 0 |  |  | Loose connection on LV isolator at substation pole. | Grassfire | 22/12/2016 14:55 | 1 | Small: 10 - 1000 sq.m | 5568 |  |  | 20170206SPN_07 | Infrastructure (network-based) | -38.5807 | 145.6369 | 1 | AusNet Services Distribution | Report | 12345 | 0.0048032 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | St Clair | Connection
Crew isolated transformer HV & LV. Transformer not supplying anything. | 206 BEATTYS ROAD, PLUMPTON VIC 3335 | A002315 | Copper theft | [5 empty] | 2 | Copper theft at Beattys Rd-P11 substation. Bolt heads were cut and removed with vehicle. Police has been notified. Service to private pole and underground mains stolen, resulting in damage to transformer bushings and damage to pole cabling. | Service conductor;Cable;Pole mounted | 2 | 2 | 0 |  | SHM14 | Unauthorised removal and theft of copper from Jemena asset. | Damage to network assets | 42949.3528 |  |  | 5571 | Roadway |  | 20170208JEM_01 | Infrastructure (network-based) | -37.701 | 144.7051 | 1 | Jemena | Report | 6809 | 0.033567 | 22kV AC | Melbourne Airport | 3335 | Plumpton | Other
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT advised the local DAO. The crew remade the White phase connection at the LV ABC interface connection on Pole#1216447. There was no other damage done to assets. Fault crew left site at 23.00. | 34 MYRTLE AVENUE, HEATHMONT VIC 3135 | 1216447 |  |  |  | Overheated connection |  |  | 2 | IMS 226336. Received INCD for fire at pole from Fire Brigade. Fire out by time the fault crew arrived. Reported that an LV IPC connector had caught fire. IPC melted causing slight burning. Burn marks on the ground were no greater than 10cm in diameter. | Services pit | 0 | 0 | 0 |  | rwt32 | Conductor joint failure - LV ABC cable IPC connector. | Grassfire | 42949.8889 | 1 | Localised: less than 10 sq.m | 5578 | Residential |  | 20170209SPN_01 | Infrastructure (network-based) | -37.8217 | 145.2426 | 1 | AusNet Services Distribution | Report | 6818 | 0.017201 | Low voltage AC (<1kV) | Moorabbin Airport | 3135 | Heathmont | Conductor
On arrival crew carried out repairs | 1580 BAILEYS ROAD, NIRRANDA SOUTH VIC 3268 | 30136052 |  |  |  | Overheated connection |  |  | 2 | Customer reported small ground fire at the incident location. On arrival the crew found a fuse box had caught fire and melted which started a ground fire burning a small patch of grass in road reserve. There were no injuries. | Connection box | 2 | 2 | 2 |  | WBL012 | Due to damage to FOLCB unable to determine cause. | Grassfire | 43041.4181 | 1 | Localised: less than 10 sq.m | 5588 | Roadway |  | 20170213PWA_01 | Infrastructure (network-based) | -38.5323 | 142.774 | 1 | Powercor | Report | 6830 | 0.016691 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Nirranda South | Fuse
On arrival crew carried out repairs | 22 KASEM DRIVE, WERRIBEE VIC 3030 | 34011835 | Vehicle | [5 empty] | 2 | Mr Christopher Plummer phoned in to advise that an unknown vehicle has hit pillar in front of house, billowing smoke, supply ok, at the incident location. Upon arrival the crew found that an unknown vehicle had come into contact with an old brown style LV P/P (possibly backed into pillar) on the nature strip at the incident location. The resultant impact caused a flash over between the red-phase and the metal pillar frame which was evident by the flash marks present. There was no fire, injury or shocks as a result of this incident. | LV Pillar | 2 | 2 | 2 |  | WBE012 | Unknown vehicle contacted pillar | Loss of supply | 28/01/2017 19:26 |  |  | 5595 | Public space |  | 20170213PWA_04 | Infrastructure (network-based) | -37.8796 | 144.6543 | 1 | Powercor | Report | 6845 | 0.00091898 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival crew carried out repairs | 1338-1362 MOUNT COTTRELL ROAD, MELTON SOUTH VIC 3338 | 33071989 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from a height of two metres up the pole to ground level. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | cable theft | Damage to network assets | 30/01/2017 16:48 |  |  | 5607 | Roadway |  | 20170214PWA_06 | Infrastructure (network-based) | -37.7452 | 144.6132 | 1 | Powercor | Report | 6857 | 0.001919 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
On arrival crew carried out repairs | 95-97 STRATHTULLOH CIRCUIT, MELTON SOUTH VIC 3338 | 33103085 | Copper theft | [5 empty] | 2 | Following a customer report, earthing cables were found stolen from a substation pole at the incident location. The earthing was removed from a height of two metres up the pole to ground level. There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | cable theft | Damage to network assets | 30/01/2017 16:48 |  |  | 5608 | Roadway |  | 20170214PWA_07 | Infrastructure (network-based) | -37.7413 | 144.6132 | 1 | Powercor | Report | 6858 | 0.0047801 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
On arrival crew carried out repairs | 6 BRUNSWICK ROAD, BRUNSWICK EAST VIC 3057 | 30159621 | Working too close to overhead lines | [5 empty] | 2 | A person trimming trees informed that during pruning activities he has severed a service cable at the incident location. Upon arrival the crew found that the service had been damaged causing it to fall to the ground. There was no no injuries, fire or third party property damage. | Service conductor | 2 | 2 | 2 |  | C029 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 31/01/2017 11:58 |  |  | 5614 | Residential |  | 20170214PWA_08 | Infrastructure (network-based) | -37.7792 | 144.9776 | 1 | CitiPower | Report | 6867 | 0.03981 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Trees
Service Crew discovered the loose split bolt connection of the ABC service neutral conductor to the reticulation neutral at the Powercor pole end. Crew remade the connection and performed NST at the house POA with a pass result recorded. | 42 BLANCHE STREET, ST LEONARDS VIC 3223 | 30242243 |  |  |  | Corrosion |  | Phase to earth | 2 | Ron was having a shower, when he received a minor shock to his right hand when adjusting the shower head. The incident was caused by a loose and corroded split bolt connection of the ABC service neutral conductor, to the neutral reticulation conductor at the Powercor pole end. | Service conductor | 2 | 2 | 2 |  | DDL013 | Loose and corroded split bolt connection of the ABC service. | Minor shock | 28/12/2016 12:00 |  |  | 5615 | Residential |  | 20170214PWA_09 | Infrastructure (network-based) | -38.1689 | 144.7148 | 1 | Powercor | Report | 6868 | 0.031216 | Low voltage AC (<1kV) | Avalon Airport | 3223 | St Leonards | Connection
WorkSafe notified. Site quarantine and management notified. No injuries were sustained as the operator of the crane was doing so via remote control pendant. Refer to Notes and Findings tab for actions required. | 5 MT RIDDELL ROAD, HEALESVILLE VIC 3777 |  |  |  | Likely |  | Ineffective planning/procedures/processes | Phase to earth | 1 | IMS 226389. A Downer truck mounted crane was lifting a transformer off a pole below live 22kV conductors, when the operator inadvertently contacted the road side phase when the boom of the crane struck the conductor. 40 Amp Boric Acid spur fuse operated. â€¢ On Friday 10th February a Downer crew was removing a transformer from a pole beneath live 22kV conductors. â€¢ In the process of removing the transformer from the pole, it has fouled on the bolts holding it to the pole. â€¢ As a result the operator of the crane has applied upwards pressure on the boom via the controls which has caused the transformer to free from the pole. However, the upwards pressure to free the transformer has caused the boom to make contact with the live 22kV conductors. There was damage to the truck crane boom and the vehicles tyres. Downer and Ausnet Services'representatives on site.Worksafe notified. Minor outage on the spur line. | Conductor (bare) | 0 | 0 | 0 |  |  | During authorised works an AusNet Services' contractor caused the crane boom to contact the overhead HV conductor. The upwards pressure on the boom has caused the crane to breach its safe approach limits of 1200mm for a non-insulated mobile plant and make contact with the live 22kV conductors.  The crew deemed it not necessary to cover (insulate) the overhead conductors.  The operator applied excessive force on the controls to free the transformer from the mounting bolts on the pole. | No Go Zone (contact) | 43010.4896 |  |  | 5610 | Roadway |  | 20170214SPN_01 | Infrastructure (network-based) | -37.6691 | 145.5127 | 1 | AusNet Services Distribution | Report | 7589 | 0.037615 | 22kV AC | Moorabbin Airport | 3777 | Healesville | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT also dispatched a LEI, the local DAO and advised Claims section. Everything replaced except for the transformer which was reused. | 14 TUNBRIDGE STREET, RHYLL VIC 3923 | 2805593 |  | Animal |  |  |  | Phase to phase | 1 | IMS 226406. Fire brigade reported a pole fire. Pole burnt at kingbolt at HV crossarm causing the HV conductors to fall into the LV conductors below resulting in a HVI. A dead possum was found at the base of the pole. Wood pole & x-arm, salt area, drizzle conditions. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | phi11 | Animal Incident | Pole-top fire;HV injection | 13/02/2017 10:15 | 1 | Negligible: no ground fire | 5611 |  |  | 20170214SPN_02 | Infrastructure (network-based) | -38.4699 | 145.2974 | 1 | AusNet Services Distribution | Report | 12348 | 0.0035868 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3923 | Rhyll | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT also advised the local DAO. Repairs carried out. | 26 HARDY AVENUE, CANNONS CREEK VIC 3977 | 517359 |  | Animal |  |  |  |  | 2 | IMS 226409. Report of a pole smouldering caused by a possum. CFA put out pole fire caused by possum shorted out between HV phases. The pole was charred but is OK. No other damage. On 3 phase HV anchor pole LIS 517359. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | cre33 | Animal Incident | Pole-top fire | 13/02/2017 13:05 | 1 | Negligible: no ground fire | 5612 | Residential |  | 20170214SPN_03 | Infrastructure (network-based) | -38.2146 | 145.3189 | 1 | AusNet Services Distribution | Report | 6866 | 0.014003 | 22kV AC | Moorabbin Airport | 3977 | Cannons Creek | Animal
On arrival crew carried out repairs to cable | 198 COTHAM ROAD, KEW VIC 3101 | 30180112 | Working too close to underground cables | [5 empty] | 1 | A contractor reported that they have struck an underground cable with a crow bar and smoke is coming out of the ground at the incident location. On arrival the fault crew found that contractors were installing gas services. They were using a crow bar to make a hole underneath a driveway. The crow bar has been driven into and caused the high voltage underground cable of the Q13 11kV feeder to fault. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | Q013 | Contractor installing gas main | Loss of supply;No Go Zone (contact) | 15/02/2017 14:12 |  |  | 5626 | Roadway |  | 20170216PWA_01 | Infrastructure (network-based) | -37.8087 | 145.0441 | 1 | CitiPower | Report | 6883 | 0.015966 | 11kV AC | Essendon Airport | 3101 | Kew | Dug up
On arrival crew carried out repairs | MANNINGA, 190 NOLANS ROAD, SCOTCHMANS LEAD VIC 3352 | 30247189 | Copper theft | [5 empty] | 2 | A Field inspection revealed HV & LV earths had been stolen from substation at the incident location There were no injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAS022 | Cable theft | Damage to network assets | 42737.3368 |  |  | 5627 | Roadway |  | 20170216PWA_02 | Infrastructure (network-based) | -37.6591 | 143.8504 | 1 | Powercor | Report | 6884 | 0.031465 | Earthing cable | Ballarat Aerodrome | 3352 | Scotchmans Lead | Other
On arrival crew commenced repairs | 354A ROBINSONS ROAD, DERRIMUT VIC 3030 | 33074084 | Vehicle | [5 empty] | 1 | The MFB reported that a truck had hit wires at corner of Australis drive and Robinsons road and started a fire at the incident location. The wood pole broke above ground level and fell to the ground causing a grass fire. There were no reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | LVN024 | Truck struck pole | Loss of supply;Grassfire;Damage to network assets | 17/02/2017 15:24 | 1 | Medium: 1000 sq.m - 10 ha | 5644 | Roadway |  | 20170221PWA_01 | Infrastructure (network-based) | -37.8044 | 144.752 | 1 | Powercor | Report | 6912 | 0.039225 | 22kV AC | Laverton Raaf | 3030 | Derrimut | Vehicle
On arrival crew commenced repairs | 21 GRAHAM STREET, ALBERT PARK VIC 3206 | 30172745 | Working too close to underground cables | [5 empty] | 1 | At approximately 09:39 hours on the 20.2.2017 the Albert Park #3 circuit breaker tripped to lockout. The control room dispatched operators to patrol the feeder. During the patrol the operators have located the fault cause at the incident location. The operators found an augur being used to install screw pylons had struck the underground cable of the AP3 feeder. The contractor had plans (MOCâ€™s onsite) of the area where work was being done There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | AP003 | Pile driver struck cable | Loss of supply;No Go Zone (contact) | 20/02/2017 9:39 |  |  | 5646 | Public space |  | 20170221PWA_03 | Infrastructure (network-based) | -37.8432 | 144.9462 | 1 | CitiPower | Report | 6916 | 0.032519 | 11kV AC | Essendon Airport | 3206 | Albert Park | Dug up
On arrival crew carried out repairs | 30 HYDEFIELD DRIVE, WYNDHAM VALE VIC 3024 | 33077905 |  |  |  | Corrosion |  |  | 2 | MFB reported sparks from pole Ballan Rd between Maquarrie Dr and Bolton Rd. On arrival, the crew found that the Low Voltage red phase Dee to the isolator had melted on sub pole. There were no reported ground fire,injuries or third party property damage. | Conductor (bare);Disconnector/isolator | 2 | 2 | 2 |  | WBE014 | overheated connection | Loss of supply;Damage to network assets | 42827.6951 |  |  | 5649 | Public space |  | 20170221PWA_04 | Infrastructure (network-based) | -37.8864 | 144.6253 | 1 | Powercor | Report | 6918 | 0.030069 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Connection
Visual inspection of the fuse holder couldnâ€™t detect any damage or deterioration. Tests were carried out using an independent earth and the customers earthing system and no voltage could be detected on or around the fuse holder. | 14 GEORGE STREET, NORTHCOTE VIC 3070 | 30187094 |  |  |  | Moisture ingress;Fault on customer installation |  | Phase to earth | 2 | Kane reports receiving a tingle from the fuse holder on the meter panel whilst painting. Kane was painting around the timber meter panel whilst standing on the ladder with both feet. He was painting with his right hand whist steadying himself with his left hand (on the meter panel/fuse holder). | Customer installation | 2 | 2 | 2 |  | NC001 | After further questioning it was revealed that the home owners had used a hose to wash down the front wall of the house and at the time of painting and receiving the electric shock the meter panel and fuse holder was damp. It is assumed that this was the cause for the customer receiving the shock. | Minor shock | 27/12/2016 0:00 |  |  | 5652 | Residential |  | 20170222PWA_01 | Infrastructure (network-based) | -37.778 | 144.9951 | 2 | CitiPower | Report | 12437 | 0.040086 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Other
The fault crew then isolated supply and issued a defect notice for the customers REC to replace the damaged conduit and cable (to be done at a later time). | 6 RADDLE ROAD, ROCKBANK VIC 3335 | 30334943 | Working too close to underground cables | [5 empty] | 2 | Call received from Dispatch at 4.04pm advising of a cable which had been dug up at this property. Upon arrival the fault crew determined that the customer LV mains cable within the property had been dug up by a contractor using a backhoe on site. The contractor stuck the conduit housing the cable, cracking the conduit and leaving the LV consumer mains exposed. There was no real damage to the cable itself. There were no reported shocks, injuries or third party property damages. | Services cable | 2 | 2 | 2 |  | MLN021 | Excavation on private property | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2017 16:04 |  |  | 5679 | Residential |  | 20170227PWA_04 | Infrastructure (network-based) | -37.7197 | 144.6616 | 1 | Powercor | Report | 8074 | 0.002316 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
On arrival crew commenced repairs | 1-39 CURLEWIS ROAD, CURLEWIS VIC 3222 | 32076029 | Vehicle | [6 empty] | Customers reported an outage and also a car impacting into a pole at corner of Portarlington and Curlewis Roads, Curlewis (originally reported as Coriyule Rd). Upon arrival the crew found that the car hit the 22/66kV intermediate pole. The driver was taken to hospital with non-life threatening injuries. The broken pole was on the ground and also one end on the roof of car. High voltage injection occurred involving 66Kv, 22kV an aerial earth (connected to LV neutrals remote from site) A number of surge diverters, 22Kv fuses and transformers were damaged in other parts of the 22kV feeders and a small ground fire of some 10M square occurred during restoration. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | DDL014 | Vehicle collided with pole | HV injection;Loss of supply;Grassfire;Damage to network assets | 42859.0681 | 1 | Small: 10 - 1000 sq.m | 5897 | Roadway |  | 20170406PWA_03 | Infrastructure (network-based) | -38.1811 | 144.5135 | 1 | Powercor | Report | 8050 | 0.0088113 | Low voltage AC (<1kV);22kV AC;66kV AC | Avalon Airport | 3222 | Curlewis | Vehicle
On arrival crew carried out repairs | 820-846 GREIGS ROAD, ROCKBANK VIC 3335 | 31023696 | Working too close to overhead lines | [5 empty] | 2 | A contractor reported that they have struck wires and they are on the ground at the incident location. On arrival the fault crew found that an excavator moving pipes had snagged the service causing damage to the insulated 4 core service cable which was on the the ground. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | MLN011 | Excavator struck service | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/03/2017 12:49 |  |  | 5901 | Roadway |  | 20170407PWA_03 | Infrastructure (network-based) | -37.7416 | 144.6199 | 1 | Powercor | Report | 7259 | 0.0062199 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
On arrival crew confirmed conductor not damaged. | 304 ANNYA ROAD, MILLTOWN VIC 3304 | 33055450 |  | Within clearances |  |  | Unknown work practice factor |  | 1 | A customer reported a power outage in the vicinity of the incident location. Upon arrival, the crew found that a tree branch had contacted the HV line during tree clearance work. The protection operated. No damage, injuries or fire was reported. | Conductor (bare) | 2 | 2 | 2 |  | HYT011 | Vegetation: Trees Incident | Loss of supply | 43073.4007 |  |  | 5911 | Forest - native (not park) |  | 20170412PWA_03 | Infrastructure (network-based) | -38.0335 | 141.6656 | 1 | Powercor | Report | 8051 | 0.012087 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3304 | Milltown | Trees
On arrival crew confirmed fire out no asset damage | 1384 PYRENEES HIGHWAY, AMPHITHEATRE VIC 3468 | 33013577 |  | Lightning |  |  |  |  | 2 | Customer reported a lightning strike and small grass fire around stay which was extinguished by heavy rain at the incident location. On arrival the crew found no asset or property damage, a ground fire had ignited resulting in approximately 1m x 1m of grass being burnt. There were no reported injuries, no 3rd party damage, no protection operated for the incident. | Guy wire | 2 | 2 | 2 |  | MRO008 | Lightning strike | Grassfire | 42951.6069 | 1 | Localised: less than 10 sq.m | 5916 | Public space |  | 20170413PWA_03 | Infrastructure (network-based) | -37.1844 | 143.3937 | 1 | Powercor | Report | 7277 | 0.032606 | 22kV AC | Ballarat Aerodrome | 3468 | Amphitheatre | Lightning
On arrivale crew isolated supply and issued a defect notice | 361 WERRIBEE VALE ROAD, MADDINGLEY VIC 3340 | 30102785 |  |  |  | Fault on customer installation |  |  | 2 | A customer reported a fuse board on fire at the incident location. On arrival, the Powercor crew found that the customerâ€™s fuse board caught fire and some damage done to the two meters. There was no ground fire or reported injuries | Customer installation | 2 | 2 | 2 |  | BMH003 | overheated customer fuses | Loss of supply | 43012.3729 |  |  | 5919 | Residential |  | 20170413PWA_05 | Infrastructure (network-based) | -37.6888 | 144.3942 | 1 | Powercor | Report | 7280 | 0.037253 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Fuse
On arrival crew carried out repairs | 335 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631 | 30305074 |  |  |  | Corrosion |  |  | 2 | CFA reported a grass fire at the incident location. The crew found a failed HV bridge caused a small fire 10m x 1m along the drain at the incident location. There were no reported injuries, no 3rd party damage for the incident. | Dropper/bridge | 2 | 2 | 2 |  | STN024 | connection failure | Grassfire | 43073.9299 | 1 | Localised: less than 10 sq.m | 5927 | Public space |  | 20170418PWA_04 | Infrastructure (network-based) | -36.3336 | 145.4317 | 1 | Powercor | Report | 7288 | 0.024663 | 22kV AC | Shepparton Airport | 3631 | Grahamvale | AF Other
On arrival crew carried out repairs | 9 VELLA DRIVE, SUNSHINE WEST VIC 3020 | 33105773 |  |  |  | Overheated connection |  |  | 2 | A customer reported a pole fire at the incident location. Upon arrival, the Powercor crew found that an overheated termination ignited the Krone box on concrete pole. There were no injuries, third party damages or ground fire. | Connection box | 2 | 2 | 2 |  | SSE033 | box destroyed cause difficult to establish | Pole-top fire | 43073.2924 | 1 | Negligible: no ground fire | 5929 | Roadway |  | 20170418PWA_06 | Infrastructure (network-based) | -37.8059 | 144.8316 | 1 | Powercor | Report | 8384 | 0.010076 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | AF Other
On arrival crew carried out repairs | 38 BRISTOL ROAD, TORQUAY VIC 3228 | 30319569 |  |  |  | Overheated connection |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. There was no ground fire, no third party damage or injury was reported. | Connection box | 2 | 2 | 2 |  | WPD032 | unable to determine due to damage | Pole-top fire | 15/04/2017 22:40 | 1 | Negligible: no ground fire | 5933 | Roadway |  | 20170419PWA_01 | Infrastructure (network-based) | -38.3311 | 144.3204 | 1 | Powercor | Report | 7294 | 0.0084236 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Pole
On arrival crew carried out repairs LEI attended site | 25-33 CYANAMID STREET, LAVERTON NORTH VIC 3026 | 31038884 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | During Transport an excavator has contacted the HV conductors at 25 Cyanamid st Laverton North. The conductors were slightly damaged and there were flashover marks on the boom of the excavator There were burnt HV connections and HV conductors on the ground outside 85 Cherry Lane. At 73 Cherry lane there was evidence of HVI and a ground fire of 3.5 square metres (attributed to HVI) There were a number of street lights damaged along Cherry Lane. The Protection operated as expected. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | LVN022 | Excavator (in transport mode) contacted HV conductor | HV injection;Loss of supply;Grassfire | 18/04/2017 16:12 | 1 | Localised: less than 10 sq.m | 5935 |  |  | 20170419PWA_03 | Infrastructure (network-based) | -37.8323 | 144.7992 | 1 | Powercor | Report | 7296 | 0.03666 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
On arrival crew carried out repairs | 6260 SUNRAYSIA HIGHWAY, MASSEY VIC 3482 | 32026679 |  |  |  | Insulator |  |  | 2 | Customer reported insulator had broken off the top of a SWER INT pole and the wire was hanging low. Upon arrival crew found that the pin insulator had broken and the live conductor had fallen. The conductor had brushed the side of the wood pole but no evidence of fire was found. There were no reported injuries or third party damage. | Conductor (bare);Insulators | 2 | 2 | 2 |  | CTN006 | Fractured pin insulator | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/04/2017 17:21 |  |  | 5937 | Agricultural |  | 20170420PWA_01 | Infrastructure (network-based) | -36.2218 | 142.8546 | 1 | Powercor | Report | 7299 | 0.0092049 | 12.7kV AC (SWER) | Horsham Aerodrome | 3482 | Massey | AF Other
On arrival crew carried out repairs | 1626 MURRAY VALLEY HIGHWAY, BEVERFORD VIC 3590 | 30276890 |  |  |  | Overheated connection |  |  | 2 | CFA reported that there had been a pole fire at the above-mentioned location. Upon arrival, the crew found that the fuse box had burnt at the 4m mark on the pole. There was no ground fire , no reported injuries or third party damage. | Connection box | 2 | 2 | 2 |  | SHL004 | due to damage to connection box cause not determined | Pole-top fire;Loss of supply | 14/04/2017 12:42 | 1 | Negligible: no ground fire | 5939 | Roadway |  | 20170420PWA_03 | Infrastructure (network-based) | -35.2211 | 143.4668 | 1 | Powercor | Report | 7301 | 0.038116 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3590 | Beverford | Fuse
The crew replaced the earths and the substation was returned to service. | 92 DOHERTYS ROAD, LAVERTON NORTH VIC 3026 | 30116421 | Copper theft | [5 empty] | 2 | A HV operator reported that copper earths have been stolen from the substation the incident location. On arrival the fault crew found that the high and low voltage earths had been cut away and removed from the substation. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LVN032 | Copper theft | Damage to network assets | 19/04/2017 10:43 |  |  | 5943 | Roadway |  | 20170421PWA_01 | Infrastructure (network-based) | -37.8287 | 144.7921 | 1 | Powercor | Report | 7309 | 0.0172 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
Additional emergency high voltage switching was completed as the 66kV sub-transmission, 11kV termination pole (LIS No. 1824943) with the SR24 underground cable exit cable attached required replacement. The pole was replaced and supply restored upon completion. | 426 BLUFF ROAD, HAMPTON VIC 3188 | 1824943 |  |  |  | Electrical breakdown |  |  | 2 | Per MFB who are onsite - fire in the inside of the pole. 11kV feeder SR24 exit switch (CH1751) failed that caused the blue phase to dim light the feeder. Emergency high voltage switching took place and supply to the feeder was restored by switching at the open point of SR15 and SR24 at CH6532. The HV isolator failed on the blue phase and broke apart that caused the 11kV to track onto the HV crossarm and create a hotspot within the pole that caused the pole to burn internally from the 11KV crossarm kingbolt to the top of the pole. | Pole (wood);Pole top;Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | SR24 | The 11kV isolator failed and broke apart that caused tracking to the HV crossarm and create a hotspot within the pole that caused the pole to burn internally from the 11KV crossarm kingbolt to the top of the pole. | Pole-top fire | 43043.5208 | 1 | Negligible: no ground fire | 5950 | Roadway |  | 20170425UTD_04 | Infrastructure (network-based) | -37.9455 | 145.0226 | 1 | United Energy Distribution | Report | 7317 | 0.032094 | 11kV AC;66kV AC | Moorabbin Airport | 3188 | Hampton | Pole
Initial report: CEOT dispatched a fault crew to make safe, investigate and repair. An AusNet Services' LEI attended and confirmed a HVI had occurred at the Mitre 10 store. Final report: Faults crew attended site, isolated HV and LV supply and repaired damaged surge diverter and LV earthing. AusNet Services' attending LEI inspected affected properties on Mountain Hwy (open point LS1222734 to LS1223206 ) and found evidence of HV injection. Control Room (CEOT) notified, customers OK, supply restored. | 862 MOUNTAIN HIGHWAY, BAYSWATER VIC 3153 | 1222734 |  | Industrial or urban pollution |  |  |  | Phase to earth | 1 | IMS 227625. Initial report: Two blown 40e fuses at transformer. Flash marks around the centre phase. LAs have tracking marks on them, possible cause. HVI occurred. Final report: A defective surge diverter (at Mountain Dunlop Sub) was the cause of a damage LV earthing cable, 22kV made contact with LV earthing conductor by means of arcing. Environmental factors and inclement weather causing the lighting arrestor to malfunction. | Pole mounted;Surge diverter | 0 | 0 | 0 |  | bwr33 | A defective lighting arrestor on substation pole resulted in 22kV cable making contact with an LV earthing cable by means of arcing. Environmental factors and inclement weather causing the lighting arrestor to malfunction. Please refer to attached photo of LA and damaged LV earth cable. | HV injection | 24/04/2017 6:45 |  |  | 5954 | Commercial |  | 20170426SPN_02 | Infrastructure (network-based) | -37.8414 | 145.2638 | 1 | AusNet Services Distribution | Report | 7323 | 0.038336 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3153 | Bayswater | AF Other
On arrival crew carried out repairs | 49 FISKEN STREET, MADDINGLEY VIC 3340 | 30115961 |  |  |  | Overheated connection |  |  | 1 | Vic Fire called in to advise of a wire on fire & brigade en-route. A resident Mrs Kerry Fay also called in to advise of a small box on pole outside property has caught fire, CFA have attended and fire now out, customer has no supply. On arrival the crew had discovered that a Single-Phase FOLCB and approximately 1m of 16mm LV UG Service Cable running down the pole had overheated and burnt out at incident location. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. The crew made the site safe and replaced the FOLCB and the affected 16mm LV UG Service Cable. | Connection box | 2 | 2 | 2 |  | BMH006 | connection failure | Pole-top fire;Loss of supply | 20/04/2017 18:31 | 1 | Negligible: no ground fire | 5966 | Roadway |  | 20170427PWA_05 | Infrastructure (network-based) | -37.6898 | 144.442 | 1 | Powercor | Report | 7337 | 0.02633 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Pole
On arrival crew carried out repairs | 500 AMIETS ROAD, WYELANGTA VIC 3237 | 33039339 |  | Lightning |  | Fuse failed to eject |  |  | 2 | Customer reported a transformer on fire at the incident location. On arrival the crew found that a HV EDO fuse had operated on a transformer pole, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. The previous day there had been a lightning strike at the incident location. There was no injuries, ground fire or third party property damage reported. | EDO fuse;Transformer | 2 | 2 | 2 |  | CLC006 | Lightning strike | Plant/equipment | 21/04/2017 10:16 | 1 | Negligible: no ground fire | 5967 | Agricultural |  | 20170427PWA_06 | Infrastructure (network-based) | -38.699 | 143.4267 | 1 | Powercor | Report | 7338 | 0.019012 | 22kV AC | Warrnambool Airport Ndb | 3237 | Wyelangta | Fuse
On arrival crew isolated supply and carried out repairs | 16 HAVERING LANE, STRATHFIELDSAYE VIC 3551 | 30039584 |  |  |  | Rot |  |  | 2 | A Customer reported broken crossarm and cables very low can be reached from footpath. Crew attended and found LV Termination Crossarm broken with one cable of the three wires hanging low. No ground fire, no property damage, no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | BGO013 | LV crossarm failure | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/04/2017 7:38 |  |  | 5970 | Roadway |  | 20170428PWA_01 | Infrastructure (network-based) | -36.798 | 144.3621 | 1 | Powercor | Report | 7341 | 0.035275 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Strathfieldsaye | Crossarm
On arrival crew carried out repairs | 2332 CASTLES ROAD, KANYAPELLA VIC 3564 | 32180040 | Working too close to overhead lines | [5 empty] | 1 | Customer reported that he had heard a loud bang and that wires are lying in paddock at incident location. On arrival the crew noted they could see an excavator in the paddock and excavator marks leading to and from where the HV wires had come down. Crew spoke with Leon Ash who said he had contacted HV conductor with excavator. There was no fire, No injuries, No third party damage. | Conductor (bare) | 2 | 2 | 2 |  | ECA003 | Excavator struck line | Loss of supply;Damage to network assets | 27/04/2017 17:27 |  |  | 5974 | Agricultural |  | 20170428PWA_04 | Infrastructure (network-based) | -36.0914 | 144.9048 | 1 | Powercor | Report | 7345 | 0.032007 | 22kV AC | Shepparton Airport | 3564 | Kanyapella | Vehicle
On arrival supply isolated for REC to carry out repairs | 20 SINCLAIR ROAD, DRUMBORG VIC 3304 | 30089430 |  |  |  | Fault on customer installation |  |  | 2 | customer advised of a fuse box on fire. Attending crew found customers FOLCB on substation pole had overheated and melted possibly due to overload. Supply isolated for REC to complete repairs. There was no injuries or ground fire. | Customer installation | 2 | 2 | 2 |  | PLD003 | melted Customer FOLCB | Loss of supply | 28/04/2017 18:35 |  |  | 5984 | Agricultural |  | 20170501PWA_03 | Infrastructure (network-based) | -38.0766 | 141.5006 | 1 | Powercor | Report | 7355 | 0.02266 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3304 | Drumborg | Fuse
On arrival crew carried out repairs | 79-81 MIDLAND HIGHWAY, EPSOM VIC 3551 | 30026302 |  |  |  | Overheated connection |  |  | 2 | Vic fire reports a pole fire at the incident location. On arrival the crew found a pole box had overheated and melted. CFA attended. The box was replaced. There were no reported shocks, injuries or ground fire start. | Connector/termination | 2 | 2 | 2 |  | EHK022 | connection failure | Loss of supply;Damage to network assets | 42799.4187 |  |  | 5991 | Roadway |  | 20170504PWA_02 | Infrastructure (network-based) | -36.7132 | 144.3141 | 1 | Powercor | Report | 7369 | 0.0070255 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Epsom | Pole
Fault crew attended and isolated the overhead service at the pole end and made safe with the service and meter left in place for further investigation. Defect notice was raised. | 33 PARK STREET, PASCOE VALE VIC 3044 |  | Unauthorised access | [5 empty] | 2 | Zinfra Compliance Officer identified abnormality of an abolishment, when requested to a new installation of three units at the below address. i.e. an existing installation requiring disconnection to enable demolishment of the premise which then allows new building works to occur. The site had been connected to a non-compliant Builder Supply Pole (BSP) whilst using the existing installation overhead service and meter. | Aluminium twisted (XLPE);Smart meter | 0 | 0 | 0 |  |  | Unauthorised access to the network by unknown person(s) | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42829.5 |  |  | 6003 | Residential |  | 20170508JEM_01 | Infrastructure (network-based) | -37.7265 | 144.9242 | 1 | Jemena | Report | 12397 | 0.039506 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
On arrival crew carried out repairs. | 9 WHITES ROAD, CARDIGAN VIC 3352 | 30004238 |  |  |  | Candled fuse |  |  | 2 | VicFire reported a sparking pole top at the incident location. On arrival the crew found a 22kV candled EDO fuse on the footpath side of the substation at the incident location. There was no ground fire, no injuries or third party property damage.. | EDO fuse | 2 | 2 | 2 |  | BAS011 | Leakage current | Pole-top fire | 42921.7993 | 1 | Negligible: no ground fire | 6012 | Roadway |  | 20170509PWA_01 | Infrastructure (network-based) | -37.5246 | 143.7416 | 1 | Powercor | Report | 7392 | 0.010466 | 22kV AC | Ballarat Aerodrome | 3352 | Cardigan | Fuse
CEOT dispatched a fault crew and an AusNet Services' LEI to site to isolate supply, make safe and investigate. The attending fault crew isolated supply due to the unsafe condition of line side cables entangled with the barb wire fence. The LEI conducted voltage tests between an independent earth and various parts of the installation, including the metallic parts of the fence, identified zero volts at site visit after supply isolation, but it was apparent that full line voltage would have been detected at the time of the incident. | 1645 WESTERNPORT ROAD, HEATH HILL VIC 3981 | 515213 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 227141. A customer received an electric shock from a fence that was tangled in a tree after the tree fell down onto the another customer's meter box and uprooted the meter box. The customer who received the shock is a farmer from an adjacent property (1645 Western Port Rd, Heath Hill), in the course of work repairing the property's barb wire fencing when he experienced a sensation that he at the time believed may have been a slight electric shock when he simultaneously contacted the metallic barb wire fence and the wet ground. The attending AusNet Services' voltage tests between an independent earth and various points of the installation could not detect any voltage due to the fact the fault crew had already isolated supply. At the time of the investigation it was apparent that full line voltage would have been running through the wire fencing as the line side cabling was in direct contact with the wire fence due to the upturned remote meter panel/switchboard at Lot 1 Phillips Rd, Heath Hill, due to a falling tree on the road reserve ripping up the meter panel and associated cables. | Customer installation | 0 | 0 | 0 |  | llg11 | Farmer from adjacent property (1645 Western Port Rd) received a slight electric shock while working on a barbed wire fence that had been energised by the upturned remote meter box causing the line side cable to be entangled and livened up the wire fencing. | Minor shock | 27/03/2017 18:25 |  |  | 6018 | Agricultural |  | 20170509SPN_04 | Infrastructure (network-based) | -38.2358 | 145.7195 | 1 | AusNet Services Distribution | Report | 7398 | 0.025471 | Low voltage AC (<1kV) | Moorabbin Airport | 3981 | Heath Hill | Trees
Two defect notices issued. Crew replaced service wire | 116 SCOTCHMER STREET, FITZROY NORTH VIC 3068 | 30164727 | Vehicle | [5 empty] | 2 | A passer-by (Matthew) reported that a truck has contacted an overhead wire and it is now on the ground at the incident location. On arrival the fault crew found that a garbage truck had contacted a four core service and it was torn of the fasciaâ€™s of the adjacent dwellings. The fasciaâ€™s will need to be repaired and a is REC required to inspect wiring for damage and issue certificate of electrical safety. There was no ground fire and no injury as a result of this incident. | Service conductor;Customer installation | 2 | 2 | 2 |  | F037 | Garbage truck struck service | Loss of supply;Damage to network assets | 42860.2507 |  |  | 6023 | Roadway |  | 20170510PWA_03 | Infrastructure (network-based) | -37.7829 | 144.9819 | 1 | CitiPower | Report | 7403 | 0.021069 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Vehicle
On arrival crew carried out repairs | 35-37 WHITEHILL AVENUE, SUNSHINE NORTH VIC 3020 | 33071369 | Working too close to underground cables | [5 empty] | 2 | Report received that an excavator working in the road had dug up an LV mains cable and conduit belonging to Powercor at the incident location. The excavator operator did have MOCs and was also working off their own road and drainage plans which also included information as to the location of the underground utilities in the area. The mains cable under the roadway from the pole to the property was identified and sprayed in blue on the nature strip, however the location indicated, for whatever reason, was incorrect, and out by approximately 1m, which ultimately contributed to this incident occurring. No shock, injuries, or third party damage reported. | Cable | 2 | 2 | 2 |  | SSE012 | excavator struck cable | No Go Zone (contact) | 43013.6375 |  |  | 6031 | Roadway |  | 20170511PWA_01 | Infrastructure (network-based) | -37.7549 | 144.8372 | 1 | Powercor | Report | 7500 | 0.025218 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Dug up
Initial report: CEOT dispatched a fault crew to make safe. CEOT advised the local DAO. Claims notified. Final report: Photos taken by the DAO. A Downer crew arrived and advised the works would be completed in daylight. Repairs subsequently carried out. | 2248 MELBA HIGHWAY, DIXONS CREEK VIC 3775 | 1007235 | Manned aircraft | [5 empty] | 1 | IMS 227919. Initial report: Plane into a single phase HV line causing one conductor to break and fall to the ground. HV fuse operated. Aircraft debris was found at the site but there was no sign of an aircraft at the scene. Final report: The local AusNet Services' DAO attended site. Police on site. Alleged someone stole a plane from a neighbouring property and hit 1 Phase HV conductor whilst taking off. Upon inspection, 1 bay of 1 Phase HV conductor has been snapped and segments of fiberglass and plastic believed to be from the aircraft were found on-site. No damage to property or livestock. | Conductor (bare) | 0 | 0 | 0 |  | ldl14 | An unknown person flying a plane caused the plane to make contact with a HV line. | No Go Zone (contact);Damage to network assets | 16/05/2017 15:30 |  |  | 6051 | Agricultural |  | 20170517SPN_01 | Infrastructure (network-based) | -37.5569 | 145.4173 | 1 | AusNet Services Distribution | Report | 7437 | 0.029421 | 22kV AC | Wallan (Kilmore Gap) | 3775 | Dixons Creek | Other
Supplies isolated Several zone substations remaining on single contingency | 132-140 TURNER STREET, PORT MELBOURNE VIC 3207 | 30160531 | Working too close to underground cables | [5 empty] | 1 | Operators responding to protection alarms found that 2 separate 66kV underground cables have been damaged at the incident location. Contractors working on the Tullamarine / Bolte Bridge widening project had damaged cables of two 66kV underground circuits. A Horizontal bore was being used to drill the holes under the Princes freeway. One of the cables is oil filled and as a result of damage sustained about two hundred litres of oil was released. There was no ground fire and no injury as a result of this incident. | Cable | 0 | 1 | 0 |  | FBTS-PM | Interference | No Go Zone (contact);Damage to network assets | 23/05/2017 12:25 |  |  | 6068 | Construction |  | 20170525PWA_01 | Infrastructure (network-based) | -37.8261 | 144.9296 | 1 | CitiPower | Report | 7460 | 0.028073 | 66kV AC | Essendon Airport | 3207 | Port Melbourne | Dug up
The site inspection identified clear evidence of a well orchestrated break-in with considerable damage to materials and theft of property. During the break-in, the unknown persons had accessed the zone substation switch room, switchyard and onsite construction containers. A full clean-up of the construction site facilities is required with a stock take required to asses the value of the damage and theft of materials estimated to be greater than $10,000. | MILROY STREET, BRIGHTON EAST VIC 3187 |  | Theft;Unauthorised access;Copper theft | [5 empty] | 2 | UGL were in attendance at NB zone substation in Milroy Street, Brighton East in preparation for electrical construction activities. Following the completion of the site risk assessment (SRA), the construction team accessed the site and observed that a rope had been attached to the main pedestrian gate and identified that a break-in had occurred. The UGL employees and subcontractors commenced initial inspections of the in-service plant to ensure there was no damage or unsafe situations created following the unauthorised entry. The Victorian Police and the United Energy Network Operations Centre were notified and the Police attended the site promptly and commenced a forensic examination. The zone substation was re-secured and some basic house keeping duties completed. | Equipment;Switchyard;Zone substation | 0 | 0 | 0 |  |  | The construction team accessed the zone substation and observed that a rope had been attached to the main pedestrian gate and identified that a break-in had occurred. | Damage to network assets | 43012.0417 |  |  | 6072 | Construction |  | 20170525UTD_02 | Infrastructure (network-based) | -37.9065 | 145.0091 | 1 | United Energy Distribution | Report | 7465 | 0.031062 | 66kV AC | Moorabbin Airport | 3187 | Brighton East | Other
CEOT dispatched a fault crew to attend the site to isolate, make safe, investigate and repair. The crew attended and made isolations to make safe. The fault crew isolated the line from switch BW1032. A construction crew attended to make the necessary repairs to the HV conductor. | 50 GRANT STREET, CRANBOURNE VIC 3977 | 510048 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 226053. CEOT received a report from emergency services of a live conductor on the ground which was sparking. The centre phase 3/12 steel HV conductor broke mid-span at the conductor joint. The HV conductor was alive on the ground. It is considered the conductor on the ground was possibly alive due to back feed from the downstream transformer windings creating a high impedance fault. The ground was burnt 5cm each side of the conductor. The incident occurred in a LBRA location. Please accept our apology that this incident was not identified by Network Safety until we did the Q1-2017 MEC quarterly report. The IMS record had a Fire tab only and did not have the Electrical tab as required so it was initially missed. I have consulted with a Controller in the CEOT concerning electrical protection operation and there is no record of any HV protection operating in relation to this incident. Please note a Schedule 1 report (notification) was sent to ESV by our CEOT (Control Room). This incident was included as a statistic in the Q1-2017 MEC Quarterly Report sent to ESV. | Conductor (bare) | 0 | 0 | 0 |  | cre32 | HV conductor joint failed. | Grassfire | 14/01/2017 0:10 | 1 | Localised: less than 10 sq.m | 6074 | Roadway |  | 20170526SPN_01 | Infrastructure (network-based) | -38.1176 | 145.2792 | 1 | AusNet Services Distribution | Report | 12360 | 0.039101 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne | Conductor
Fault crew isolated low voltage circuit to make safe. Fault crew repaired and replaced insulated piercing connector (IPC) connection in pit and restored supply. | 24 WATERFORD AVENUE, CRAIGIEBURN VIC 3064 |  |  |  | Highly unlikely | Overheated connection |  |  | 2 | Customer reported all supply failure, and later called to advise smoke coming from pit in nature strip | Connector/termination | 0 | 0 | 0 |  | ST32 | Insulation piercing connector (IPC) connection in pit failed and required replacement | Loss of supply | 28/05/2017 9:08 |  |  | 6077 | Residential |  | 20170528JEM_01 | Infrastructure (network-based) | -37.6092 | 144.9223 | 1 | Jemena | Report | 12399 | 0.018728 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Connection
On arrival crew carried out repairs | 14 HERRIOT STREET, HEATHCOTE VIC 3523 | 31008459 | Vehicle | [5 empty] | 2 | A customer (Tarina McLean) reported a truck had hit and bought down power lines at the incident location. On arrival the crew found that a Low Voltage (LV) service had been hit by a truck, resulting in it coming to ground across the road. There were no reported injuries or other third part damage. | Service conductor | 2 | 2 | 2 |  | BGO023 | Unknown vehicle struck service | Loss of supply | 18/05/2017 7:11 |  |  | 6079 | Roadway |  | 20170529PWA_02 | Infrastructure (network-based) | -36.9225 | 144.707 | 1 | Powercor | Report | 7472 | 0.023913 | Low voltage AC (<1kV) | Bendigo Airport | 3523 | Heathcote | Vehicle
On arrival crew carried out repairs | 849 WILLIAMS ROAD, SCOTTS CREEK VIC 3267 | 31008903 | Working too close to underground cables;Unauthorised work | [5 empty] | 2 | Powercor received a call from an REC Noel Newcombe reporting that an unknown Contractor had damaged an underground service pit and cables at the incident location. When crews arrived they found the damaged pit and severed cables at the property boundary. It appeared that an excavator or some other earthmoving machinery had been clearing a track to the property buildings and in the process had damaged the pit. The property is an unoccupied dairy farm shed and residence with a sign on the shed â€œA&P Symonds Farm No 2â€. No property owners or representatives were on site. It is unclear who contacted the REC to report the damage. There was no ground fire, no reported third party damage or any shock or injuries. | Services cable;Services pit | 2 | 2 | 2 |  | COB011 | earthworks by unknown person | No Go Zone (contact) | 18/05/2017 16:54 |  |  | 6080 | Public space |  | 20170529PWA_03 | Infrastructure (network-based) | -38.4984 | 143.1181 | 1 | Powercor | Report | 7473 | 0.02637 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3267 | Scotts Creek | Other
The civil contractor ceased work & sought the assistance of the incident reporting REC whose business premise was in the vicinity of the incident location, the REC confirmed the damaged LV U/G was alive and reported the incident via the Powercor faults number. On arrival crew commenced repairs | 95 OLD DOOKIE ROAD, SHEPPARTON VIC 3630 | 32187991 | Working too close to underground cables | [6 empty] | An REC reported that a LV U/G cable had been dug up at the incident location. Upon arrival the fault crew found civil contractor was excavating the road in preparation for road alteration works. The civil contractor had dial before you dig and MOCS plans, the U/G was not shown on the plans. There was no load connection within the service pit. There were no reported shocks, injuries, third party damage or ground fire start. | Services cable | 2 | 2 | 2 |  | STN024 | Excavation works | No Go Zone (contact) | 16/05/2017 12:40 |  |  | 6085 | Roadway |  | 20170529PWA_05 | Infrastructure (network-based) | -36.3773 | 145.4271 | 1 | Powercor | Report | 7478 | 0.00084259 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Dug up
All distribution metering equipment and customer switchboards at properties on both sides of the LV transformer were inspected and assessed for damage. Widespread damage was observed to ducted heaters, TVs and other electronic equipment and white goods at various properties. Faulted section was isolated and faults crew carried out required repairs to conductor. All accessible properties were made safe and re-energised. Emergency services did not attend this incident. An investigation report was not required for this incident because the HV conductor failure was a consequence of airborne debris (most likely a metallic balloon) coming into contact with the HV conductors. | 19 MAJOR ROAD, FAWKNER VIC 3060 | Pole numbers A122629 and A022554 | Recreation - Helium (party) balloons |  |  | HV injection |  |  | 1 | Red and white HV phases at tee off pole numbers A122629 and A022554 broke free from their respective insulators and fell down onto the LV neutral, resulting in a HV injection into the LV neutral. The HV and LV conductors fell on the ground. | Conductor (bare) | 0 | 0 | 0 |  | CN06 | After reviewing the load on the line for the incident date and time, it was concluded that the load was not excessive and could not have contributed to the conductor failure. Verbal evidence from a customer is that airborne debris (most likely a metallic balloon) was caught in the HV conductors, resulting in two phases to break free from their respective insulators. There were no known pre-existing conditions on the HV conductor which contributed to the incident. | HV injection;Less than $50k damage;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/05/2017 7:34 |  |  | 6103 | Residential |  | 20170531JEM_02 | Infrastructure (network-based) | -37.7082 | 144.974 | 1 | Jemena | Report | 12400 | 0.031289 | 22kV AC | Essendon Airport | 3060 | Fawkner | AF Other
Fault crew attended and identified underground cable fault between pole #A033157 and the park where it feeds public lighting. Fault crew isolated WILLIAM ST circuit out of PILGRIM-JOHN pole substation and tested earth to be live with 240v. Lighting cable has been disconnected via fuse removal and dummy inserted. A maintenance notification has been raised for the underground crew to follow up by 24 August 2017. | 130 PILGRIM STREET, SEDDON VIC 3011 | Pole no. A033157 |  |  |  | Earth fault |  |  | 2 | Report of pole smouldering at corner of James and Pilgrim St., Seddon VIC 3011 A visit by the asset performance team found no burn or charring marks were on the pole. | Pole (wood);Cable;Pole mounted | 2 | 2 | 2 |  | FE09 | Underground cable fault in cable that feeds lighting in park from pole #A033157, caused cover guard on pole to be live at 240v. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Melting or smoking only | 42741.2653 |  |  | 6107 | Residential |  | 20170601JEM_01 | Infrastructure (network-based) | -37.8049 | 144.8893 | 1 | Jemena | Report | 12401 | 0.035418 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Seddon | Pole
On arrival crew carried out repairs | 416A CHURCH STREET, RICHMOND VIC 3121 | 30221370 |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire at the above incident location. On arrival, the crew found that a Public Lighting Photo Electric Cell had faulted and caught on fire. There was no ground fire nor third party damaged. There were no reported injuries. | Public lighting | 2 | 2 | 2 |  | NR006 | Overheated connection | Pole-top fire | 28/05/2017 22:46 | 1 | Negligible: no ground fire | 6108 | Roadway |  | 20170601PWA_02 | Infrastructure (network-based) | -37.8248 | 144.9979 | 1 | CitiPower | Report | 7877 | 0.025669 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Pole
On arrival crew carried out repairs. | 409 TURRONG ROAD, COORIEMUNGLE VIC 3268 | 33035862 |  |  |  | Overheated connection |  |  | 2 | Customer reports a fire on a pole at the above location. A crew attended and found a fuse box had burnt and melted. The resulting falling debris started a grass fire at the base of the pole. There were no reported shocks, injuries or third party damage. | Connection box | 2 | 2 | 2 |  | COB011 | Unable to determine due to damage | Grassfire | 42772.3569 | 1 | Localised: less than 10 sq.m | 6115 | Roadway |  | 20170602PWA_01 | Infrastructure (network-based) | -38.5803 | 143.1607 | 1 | Powercor | Report | 7634 | 0.010521 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Cooriemungle | Fuse
1 June 2017 - There is a planned outage arranged to remove the scaffold and to repair the damaged conductor. The Zinfra No Go Zone Supervisor requested the section of damaged conductor is returned to him. | 261 CENTRE ROAD, BENTLEIGH VIC 3204 |  | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | At 1155hrs on 29/05/2017, 11kV feeder BT14 circuit breaker successfully reclosed and held. The feeder was patrolled and no cause was identified. The feeder patrol was completed and closed at 1259hrs. A Permit to Work (PTW) was on issue to Trio Construct at a construction site at 261 Centre Road, Bentleigh - Rose Street corner of Centre Road 1 pole south of "Rose-Centre" substation. At approximately 3.00PM on 29/05/2017, Ian Lark who is a No Go Zone (NGZ) Officer for Zinfra and issued the PTW, was notified by Bill Belvedere (Site Supervisor) from Trio Construct and informed that a breach of the NGZ clearances had occurred and Worksafe and ESV were in attendance after a site worker had made inadvertent contact with the blue phase 11kV HV conductor with a length of copper pipe. No injuries occurred but the copper pipe was damaged at both ends along with the scaffolding hand rail. The following day, a site meeting was held at 8.00AM with Work Safe inspector Allan McGuinness and the Zinfra No Go Zone Supervisor to discuss the incident. It was determined that a 75mm x 6.4m length of fire sprinkler copper pipe had been lifted by a plumber within the NGZ area without a spotter and made contact between the fall arrest hand rail and the 11KV overhead conductor. There was a PTW on issue (U22784) with preventative instructions regarding any work being done outside of the protective hoarding. The HV feeder patrol would not have identified any conductor damage at the construction site. The damage to the HV blue phase conductor near the helical termination could be observed from the third floor of the construction site as only the upper part of the HV conductor sustained damage and wasn't visible from the ground. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | BT 14 | Breach of No Go Zone clearances between 11,000v conductors whilst working from scaffolding. | Minor shock;No Go Zone (contact) | 29/05/2017 11:55 |  |  | 6113 | Construction |  | 20170602UTD_01 | Infrastructure (network-based) | -37.9174 | 145.0312 | 1 | United Energy Distribution | Report | 7513 | 0.00064815 | 11kV AC | Moorabbin Airport | 3204 | Bentleigh | Other
The customer was advised to engage an REC to carry out the necessary repairs. | 116 BURKE ROAD, ARARAT VIC 3377 | 30079009 | Working too close to overhead lines | [5 empty] | 2 | A report was received that an excavator had hit the service cable supplying the above address and was lying across the excavator. On arrival the crew found that an excavator that had been digging out dirt for a new driveway at the above location had hit a service cable and damaged the point of attachment at the incident location. Damage was sustained to the raiser bracket and point of attachment. There was no shock, injury or fire start. | Service conductor | 2 | 2 | 2 |  | ART034 | Excavation works | Loss of supply;No Go Zone (contact) | 23/05/2017 15:58 |  |  | 6118 | Agricultural |  | 20170605PWA_02 | Infrastructure (network-based) | -37.3035 | 142.9324 | 1 | Powercor | Report | 7518 | 0.020681 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Dug up
On arrival crew carried repairs | 7 DENBIGH COURT, KEILOR VIC 3036 | 34006900 | Working too close to underground cables | [5 empty] | 2 | A contractor advised they have dug up an UG cable at the incident location. Upon arrival, the Powercor crew noticed that cable had been damaged. There were no injuries or fire | Services cable | 2 | 2 | 2 |  | SA006 | Excavator struck cable | Damage to network assets | 24/05/2017 11:05 |  |  | 6120 | Public space |  | 20170605PWA_04 | Infrastructure (network-based) | -37.7137 | 144.8116 | 1 | Powercor | Report | 7521 | 0.019963 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Dug up
On arrival crew carried out repairs | 334 ABERDEEN STREET, MANIFOLD HEIGHTS VIC 3218 | 32087227 | Vehicle | [5 empty] | 2 | A customer called Powercor and advised of a broken wire lying on road, nature strip and through tree in front of property. When crews arrived on site they found that a neutral wire from a single phase open wire service to a residence at 334 Aberdeen St, Geelong West had broken mid span. It is suspected by the crews that a high vehicle had contributed to the wire damage. There was no ground fire, no reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | GL012 | Unknown vehicle struck service | Loss of supply;Damage to network assets | 24/05/2017 14:53 |  |  | 6122 |  |  | 20170605PWA_06 | Infrastructure (network-based) | -38.1449 | 144.3325 | 1 | Powercor | Report | 7523 | 0.011597 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Manifold Heights | Vehicle
On arrival crew carried out repairs | 1342 GRAHAM ROAD, KYVALLEY VIC 3621 | 33090786 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Customer advised a truck & Farm Machinery (no details) damaged overhead service cable, at the incident location. On arrival the crew found the 3 wire overhead service had been damaged, and was on the ground. There were no reported injuries, no fire, no property damage. | Service conductor | 2 | 2 | 2 |  | KYM006 | unknown farm machinery struck service | Loss of supply;Damage to network assets | 42921.5542 |  |  | 6154 | Roadway |  | 20170613PWA_08 | Infrastructure (network-based) | -36.2991 | 144.9859 | 1 | Powercor | Report | 7562 | 0.029086 | Low voltage AC (<1kV) | Shepparton Airport | 3621 | Kyvalley | Vehicle
On arrival crew carried out repairs | THE POPLAR, 87 HOCKINGS LANE, GOLDIE VIC 3435 | 31006369 |  | Lightning |  |  |  |  | 1 | Report of conductors on ground at the incident location. Weather conditions at time heavy rain and lightning in the area. The ACR controlling the spur line operated as expected. There was no ground fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WND013 | Lightning strike | Damage to network assets | 27/05/2017 3:30 |  |  | 6159 | Agricultural |  | 20170614PWA_04 | Infrastructure (network-based) | -37.2289 | 144.8071 | 1 | Powercor | Report | 7569 | 0.022154 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3435 | Goldie | Lightning
15/06/2017 - A faults truck was sent to the site to check for safety and removed the fuses at the POA. The REC is going to arrange a truck appointment to replace the damaged consumers mains at a later date when the replacement work has been completed. | 416 CENTRE ROAD, BENTLEIGH VIC 3204 |  |  |  |  | Fault on customer installation |  | Phase to neutral | 1 | 15/06/2017 - Caller advised that he cut through the consumers mains on 09/06/2017 and contacted ESV on this day but failed to notify United Energy. At 12.05PM on 09/06/2017, the meter at 416 Centre Road, Bentleigh communicated a last gasp and failed to power up. On 15/06/2017, Mr Vlad Schwab contacted the United Energy faults and emergencies call centre to advise that he cut through the consumers mains cable between the meter and switchboard with a demolition saw on 09/06/2017. No electric shocks or injuries were sustained but apparently he proceeded to contact ESV and his inspector but failed to notify United Energy. | Customer installation | 0 | 0 | 0 |  |  | The worker cut through the consumers mains cable between the meter and switchboard with a demolition saw | Loss of supply | 42984.5035 |  |  | 6163 | Residential |  | 20170615UTD_01 | Infrastructure (network-based) | -37.9185 | 145.0375 | 1 | United Energy Distribution | Report | 7574 | 0.03891 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Bentleigh | Other
On arrival crew carried out repairs | 2281-2303 BELLARINE HIGHWAY, POINT LONSDALE VIC 3225 | 30341136 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A passer-by reported that a truck has contacted overhead wires and they are on the ground at the incident location. On arrival the fault crew found that an excavator with boom & bucket raised had contacted and bought down a high voltage conductor at the incident location. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | DDL024 | Excavator struck line | Loss of supply;No Go Zone (contact);Damage to network assets | 16/06/2017 13:33 |  |  | 6167 | Industrial |  | 20170619PWA_01 | Infrastructure (network-based) | -38.2622 | 144.612 | 1 | Powercor | Report | 7579 | 0.015103 | 22kV AC | Avalon Airport | 3225 | Point Lonsdale | Vehicle
the fire brigade was called and responded, the fire self-extinguished. The CB was isolated and the bus was restored at 07:13hrs. There was no customer supply interruption as a result of this incident. A replacement unit has been identified and is undergoing suitability assessment at the time of this report. following the investigation and based on the preliminary findings, further actions are being implemented: (1) Set up Service Ops measuring point within SAP for all Cap Bank CBâ€™s, including triggering capability or report monitoring for Notification creation. (2) Develop process whereby cyclometer readings that are captured as part of Station Inspections is entered into SAP against the Service Ops measuring point (3) Develop process that ensure Service Ops are monitored and Notifications created when service ops reached | 917 PRINCES HIGHWAY, SPRINGVALE VIC 3171 |  |  |  |  | Mechanical breakdown;Not built/maintained to design |  |  | 0 | IMS 228585. At 06:36hrs on the 17/6/2017, the SVTS No1 66kV Bus tripped from protection due to a fault on the No1 Cap Bank 66kV CB. The CB was closed remotely by TOC at 06:32hrs as requested by AEMO. Approximately 4 minutes later, the No1 66kV Bus tripped. There was an operator at SVTS at the time that heard a loud bang when the bus tripped. The operator reported a fire coming from the 66kV switchyard that later was determined to be from the Red phase of the No1 Cap Bank 66kV CB which was on fire. | Circuit breaker | 0 | 1 | 0 |  |  | Preliminary finding: (1) excessive wear/damage of the main contacts on Red phase resulting in the contacts not closing correctly and failing on the 17/06/2017. (2) Pre-existing faults associated with the closing dashpot and the broken closing latch casting were indicators of the underlying problem with the Red phase contact wear/damage ultimately resulting in the contacts not closing correctly. (3) Since the changeover from the legacy system to SAP, the counter-based maintenance triggers were not transferred to the new system. There were no measures taken to address this deficiency either by managing counter-based maintenance outside of SAP or by the management via change request to implement the function via SAP. The system failure to trigger required maintenance following 300 open operations contributed to the contact wear/damage going undetected for a further 1,368 operations Details and photos see "Notes & Findings" | Plant/equipment | 17/06/2017 6:36 | 2 | Negligible: no ground fire | 6173 | Other | Substation | 20170619SPN_02 | Infrastructure (network-based) | -37.9285 | 145.1427 | 1 | AusNet Services Transmission | Report | 7944 | 0.023818 | 66kV AC | Moorabbin Airport | 3171 | Springvale | AF Other
Once field operator was on site the area was de-energised and made safe and repairs carried out. | 49 FOREST ROAD, FERNTREE GULLY VIC 3156 | 1313571 |  | Animal |  |  |  | Phase to earth | 1 | IMS 228163. At 06:26hrs FGY34 Feeder CB tripped and auto-reclosed - Inv Time O/C R, W & B. Live 22kV conductors were on the ground sparking. Live wire was on ground and being back fed via downstream distribution transformer windings with ~4 amps flowing - hence not enough fault current to trigger MEF (Master Earth Fault). The site was safe as CFA were on site. | Conductor (bare) | 0 | 0 | 0 |  | fgy34 | Animal Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/05/2017 6:25 |  |  | 6185 | Residential |  | 20170621SPN_01 | Infrastructure (network-based) | -37.8816 | 145.2973 | 1 | AusNet Services Distribution | Report | 7603 | 0.037681 | 22kV AC | Moorabbin Airport | 3156 | Ferntree Gully | Animal
Oil spill contained on site - no immediate risk to the environment - and clean up of oil spill organised. Vandalised transformer body and two header tanks removed from site and stored at Jemena Depot. | 260-262 GEELONG ROAD, WEST FOOTSCRAY VIC 3012 |  | Theft;Unauthorised access;Copper theft | [5 empty] | 2 | Unauthourised access and copper theft of two redundant transformers. One transformer was found tipped over (including oil spill) with windings removed, and the other transformer was stolen with header tank left behind. | Transformer | 2 | 1 | 2 |  |  | Unauthorised access and copper theft of redundant assets. | Damage to network assets | 42860.6354 |  |  | 6191 | Industrial |  | 20170623JEM_01 | Infrastructure (network-based) | -37.804 | 144.8819 | 1 | Jemena | Report | 7609 | 0.032197 | Not applicable | Essendon Airport | 3012 | West Footscray | Other
Fault truck arrived before CTA to isolate supply and were able to see neutral hanging out of pole box at pole end. Faults truck re-serviced property, NST testing passed, voltage at point of contact less than 0.5V | 31 POWELL DRIVE, HOPPERS CROSSING VIC 3029 | 33076380 |  |  |  | Corrosion |  | Phase to earth | 2 | Craig reports receiving an electric shock from the handle of his verandah security door. | Connection box | 2 | 2 | 2 |  | WBE013 | Corroded neutral | Minor shock | 28/05/2017 0:00 |  |  | 6204 | Residential |  | 20170628PWA_02 | Infrastructure (network-based) | -37.8825 | 144.6992 | 1 | Powercor | Report | 7636 | 0.010326 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
On arrival crew carried out repairs An LEI attended the site and did not find any evidence of high voltage injection damage. | 5 CAMP ROAD, ANGLESEA VIC 3230 | 32072937 |  |  |  | Corrosion |  |  | 2 | Resident reported a conductor that was hanging low. On arrival the crew discovered that a HV conductor had parted near a connection on a pole and the load side was hanging on a low voltage spreader. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | WPD021 | Connection parted near pole | Loss of supply;Damage to network assets | 42953.6972 |  |  | 6210 | Roadway |  | 20170629PWA_05 | Infrastructure (network-based) | -38.4038 | 144.1879 | 1 | Powercor | Report | 12463 | 0.0039363 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3230 | Anglesea | Connection
The crew made the site safe and left customer off supply for REC to make repairs. | C OF M - DNRE, 1399 BALLAN-DAYLESFORD ROAD, SPARGO CREEK VIC 3461 | 32012222 | Vandalism;Copper theft | [5 empty] | 2 | A customer reported an unknown person or persons have attempted to steal the underground consumer mains at the incident location. Upon arrival the Powercor crew found that the customers FOLCB service had been ripped from its mounting on the pole as they have attempted to pull out the consumer mains out of the underground conduits. Minor damage was caused to the cover strip on the substations earth cable. There was no ground fire and no injuries | Earth/earthing;Customer installation | 2 | 2 | 2 |  | BAN011 | copper theft | Loss of supply;Damage to network assets | 42800.4639 |  |  | 6212 | Public space |  | 20170629PWA_07 | Infrastructure (network-based) | -37.4738 | 144.1472 | 1 | Powercor | Report | 7646 | 0.012757 | Low voltage AC (<1kV);Earthing cable | Ballarat Aerodrome | 3461 | Spargo Creek | Other
CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew attended, isolated supply and made the site safe. The burnt out LV fuse box was replaced with a new fuse box. No apparent reason for the fire could be found. The fuse box was extensively damaged and the connections could not be checked. | 16 METUNG ROAD, METUNG VIC 3904 | 1911158 |  |  |  | Overheated connection |  |  | 2 | IMS228484. Reported that a fuse box on a pole was on fire. the LV fuse box was alight when the AusNet Services' fault crew arrived on site. no photo is available. | Connection box | 0 | 0 | 0 |  | BDL6 | No apparent reason for the fire could be found. | Other electricity related | 43014.8403 | 1 | Negligible: no ground fire | 6224 | Residential |  | 20170704SPN_01 | Infrastructure (network-based) | -37.8961 | 147.8556 | 2 | AusNet Services Distribution | Report | 11261 | 0.041433 | Low voltage AC (<1kV) | Bairnsdale Airport | 3904 | Metung | Fuse
Isolated spur, restored supply to main line. Patrolled suspected faulty line, NCF. Reloaded fuses and restored supply. On removal of hinged lower section of centre phase fuse tube it was found to be melted. There appeared to be no damage to BA fuse unit and a replacement fuse tube and mounts were installed The right side phase BA fuse tube was also replaced and installed. A patrol of the spur was conducted and no cause for the fuse operation was found, after consultation with CEOT the fuses were closed and the switch 833644 closed. | 119 MT PLEASANT ROAD, ALEXANDRA VIC 3714 | 4711213 |  |  |  | Electrical breakdown |  |  | 2 | IMS 228617. Feeder CB tripped off and L/Out. Sent out operator to investigate a loud bang which was reported by customer. Found 2 blown 15E BA fuses @ sw:833644. One of the fuses were candled. No bush or ground fires occurred. On arrival centre phase 15k BA fuse on fused switch pole 833644 had burnt through and fallen to ground. Landing on short wet grass on road reserve, with no sign of fire happening. Also the right side 15k BA fuse had operated and opened as per expectation. | Boric acid | 0 | 0 | 0 |  | RUBA12 | Burnt BA fuse tube. | Other electricity related | 20/06/2017 8:00 | 1 | Negligible: no ground fire | 6232 | Agricultural |  | 20170707SPN_01 | Infrastructure (network-based) | -37.2093 | 145.722 | 1 | AusNet Services Distribution | Report | 11262 | 0.037664 | 22kV AC | Mangalore Airport | 3714 | Alexandra | Fuse
Fault crew isolated and repaired blue and white phase low voltage conductors , replaced ruptured white phase low voltage fuse | 3 BOSTON STREET, FAWKNER VIC 3060 |  | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | Police reported conductors on the ground in Boston Street, Fawkner. Fault crews arrived to discover third party excavator had contacted the low voltage conductors. | Conductor (bare) | 2 | 2 | 2 |  |  | Catapillar driver raised excavating arm to drive machine onto demolition site and made contact with overhead communications cable causing low voltage conductors to clash and fall to ground level. | No Go Zone (contact) | 43015.3674 |  |  | 6233 | Residential |  | 20170710JEM_01 | Infrastructure (network-based) | -37.7008 | 144.9637 | 1 | Jemena | Report | 7673 | 0.027753 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | Vehicle
On arrival carried out repairs | 2 BLACK FOREST ROAD, LITTLE RIVER VIC 3211 | 31034384 | Copper theft | [5 empty] | 2 | Whilst undertaking routine maintenance inspection, it was identified and reported an HV earth had been stolen from substation pole 2 The attending crew confirmed the earth had been stolen. It appeared to have been stolen quite a while ago (>12 months). There were no reported injuries, ground fires or third party damage. | Earth/earthing | 2 | 2 | 2 |  | FNS022 | Theft | Damage to network assets | 42741.6208 |  |  | 6238 | Roadway |  | 20170712PWA_03 | Infrastructure (network-based) | -37.8845 | 144.4804 | 1 | Powercor | Report | 7685 | 0.037325 | Earthing cable | Avalon Airport | 3211 | Little River | Other
On arrival crew carried out repairs | 487 ORMOND ROAD, SPRINGBANK VIC 3352 | 30145804 | Copper theft | [5 empty] | 2 | A Powercor contractor, Rod from Electrix, reported a copper theft at the incident location. Upon arrival, the Powercor crew found that the 3m of earthing cables on the sub pole had been stolen. No more damage identified. THere was no fir, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | copper theft | Damage to network assets | 19/06/2017 14:38 |  |  | 6245 | Roadway |  | 20170713PWA_04 | Infrastructure (network-based) | -37.4975 | 144.0614 | 1 | Powercor | Report | 7697 | 0.0091944 | Earthing cable | Ballarat Aerodrome | 3352 | Springbank | Other
On arrival crew carried out repairs | 8 SYMONDS STREET, GOLDEN SQUARE VIC 3555 | 31004007 |  |  |  | Unknown technical factor |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. There was no ground fire, injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BET002 | Insufficient remains to accurately determine cause | Pole-top fire;Loss of supply | 20/06/2017 9:02 | 1 | Negligible: no ground fire | 6248 | Roadway |  | 20170713PWA_06 | Infrastructure (network-based) | -36.7731 | 144.2485 | 1 | Powercor | Report | 7715 | 0.0071852 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Golden Square | Pole
On arrival crew carried out repairs | 490 HIGH STREET, KEW VIC 3101 | 30177697 | Working too close to overhead lines | Within clearances |  |  |  |  | 2 | Mark (gardener / tree trimmer) reported that he has cut a large branch which has fallen onto a wire and caused it to break at the incident location. On arrival the fault crew found that a large branch had been cut and had fallen across insulated wires between two public light poles at the incident location (near corner of Parkhill Road and Adeney Avenue). There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | Q006 | Vegetation: Trees Incident | Damage to network assets | 19/06/2017 12:55 |  |  | 6251 | Public space |  | 20170714PWA_02 | Infrastructure (network-based) | -37.8045 | 145.048 | 1 | CitiPower | Report | 12464 | 0.024799 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Trees
On arrival crew carried out repairs | 2088 FIFTEENTH STREET, IRYMPLE VIC 3498 | 30099554 | Working too close to underground cables | [5 empty] | 2 | A customer (Lee Daniel) called to say he had hit an underground LV cable with a crow bar, while digging on the nature strip at the incident address on the Robyn Court boundary. On arrival the crew found that a Low Voltage (LV) UG 16mm service had been damaged by the customer. There were no reported injuries or other third part damage. | Services cable | 2 | 2 | 2 |  | MDA023 | Customer using crow bar | Loss of supply;No Go Zone (contact) | 16/06/2017 9:54 |  |  | 6253 | Residential |  | 20170714PWA_04 | Infrastructure (network-based) | -34.2311 | 142.165 | 1 | Powercor | Report | 7705 | 0.0033356 | Low voltage AC (<1kV) | Mildura Airport | 3498 | Irymple | Dug up
On arrival crew carried out repairs | 2 MARTIN STREET, EAST GEELONG VIC 3219 | 30060524 | Working too close to overhead lines | [5 empty] | 2 | A tree trimmer reported that he has cut an overhead service wire at the incident location. Upon arrival the crew found that the service had been cut. There were no injuries, fire or third party property damage. | Service conductor | 2 | 2 | 2 |  | GLE033 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 26/06/2017 9:44 |  |  | 6263 |  |  | 20170717PWA_05 | Infrastructure (network-based) | -38.1645 | 144.3726 | 1 | Powercor | Report | 7718 | 0.026519 | Low voltage AC (<1kV) | Avalon Airport | 3219 | East Geelong | Other
On arrival crew commenced repairs. REV completed repairs to customers POA | 65 DOURO STREET, NORTH GEELONG VIC 3215 | 30276505 | Vehicle | [5 empty] | 2 | A customer reported that a waste removal truck has ripped services off the fasciaâ€™s at the incident location. On arrival the fault crew found that a waste truck had torn the services of the fasciaâ€™s to Units 1&2 65 Douro and to 67 Douro Street, services lying on the road. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | GB031 | Vehicle struck services | Loss of supply;Damage to network assets | 29/06/2017 11:41 |  |  | 6288 | Roadway |  | 20170724PWA_04 | Infrastructure (network-based) | -38.118 | 144.3483 | 1 | Powercor | Report | 7746 | 0.016828 | Low voltage AC (<1kV) | Avalon Airport | 3215 | North Geelong | Vehicle
CEOT dispatched a faults crew and an AusNet Services' LEI to investigate and make safe. Conducted an initial NST test which failed. Voltage measured from an independent earth to meter box and neutral conductors was 5 Volts. Neutral service connection in customer's POA was found to be burning out. The fault crew isolated the installation and re-terminated the neutral conductor. The installation passed a final NST and the 5 Volts was no longer present on meter box or neutral conductors. Customer left on supply. | 8 SEAVIEW ROAD, COCKATOO VIC 3781 | 417506 |  |  |  | Overheated connection |  | Phase to earth | 2 | IMS 227025. Justin noticed the lights were dimming and kettle struggling to boil. He went to meter box to check the switchboard and as he made contact with the metallic meter box he received a tingle. Justin then called the electricity distributor AusNet Services. | Service conductor | 0 | 0 | 0 |  | bge22 | Neutral service termination at POA FOLCB failed/burnt out. | Minor shock | 22/03/2017 11:45 |  |  | 6017 | Residential |  | 20170509SPN_03 | Infrastructure (customer connection) | -37.9451 | 145.4883 | 1 | AusNet Services Distribution | Report | 7397 | 0.017103 | Low voltage AC (<1kV) | Moorabbin Airport | 3781 | Cockatoo | Connection
On arrival crew carried out repairs | 60-64 HIGH STREET, MARYBOROUGH VIC 3465 | 30017731 |  |  |  | Overheated connection |  |  | 1 | Vic Fire reported a pole fire at the above location. A crew attended and found a low voltage box had over heated and melted. There were no reported shocks, injuries or ground fire start. | Connection box | 2 | 2 | 2 |  | MRO006 | due to damage could not determine cause | Melting or smoking only | 42830.4194 |  |  | 6020 | Roadway |  | 20170510PWA_01 | Infrastructure (network-based) | -37.0487 | 143.7352 | 1 | Powercor | Report | 7400 | 0.015194 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | Pole
On arrival crew isolated supply and commenced repairs | 21 JEWELL CRESCENT, BRUNSWICK WEST VIC 3055 | 30157785 | Working too close to underground cables;Unauthorised work | [5 empty] | 2 | A contractor reported that they have damaged an underground cable at the incident location. On arrival the fault crew found that contractors had severed a low voltage underground cable while trenching to install drainage pipes. The damage to the cable is consistent with damage caused by mechanical plant. The live cable end was capped by the R.E.C using heat shrink tubing over the â€œLIVEâ€ end presumably to allow work to continue in the trench. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | WB013 | Service cable severed by excavator and un-authorised repairs | Loss of supply;No Go Zone (contact) | 43044.6771 |  |  | 6059 | Roadway |  | 20170523PWA_01 | Infrastructure (network-based) | -37.7705 | 144.9375 | 1 | CitiPower | Report | 7447 | 0.0027338 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Dug up
CEOT dispatched a fault crew to isolate, make safe and investigate. CEOT also requested the local DAO to investigate and report. The crew re-sleeved and strung one phase of the 3 Wire LV line. The crew re-sag 080 LV conductors measuring a height 5 metres in middle of the bay - should be 5.5 metres height. Unable to achieve 5.5 metres ground clearance due to the bay length. A Notification to be created in SAP to reassess to achieve 5.5 metres, bay lengths (110M) under Work Order 110526527. Note: No excavator or the excavator operator was at the site where the incident occurred - although there were excavator track marks under the overhead line where the line was struck. Excavator was parked in the paddock. Customer details are: Samantha Robinson, tel 0400 822 596 or 0408 422 204. The crew also replaced the 100 Amp fuse on the phase that was down. Corrective action 422324 - NOTI created in SAP. | 627 MEWBURN PARK ROAD, MAFFRA VIC 3860 | 2515162 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 227741. CEOT received a report from a customer line down in a paddock at Lis pole 2515162, that it appears LV mains across a gateway to the paddock were hit by an excavator. The road side phase was down on the ground. The excavator was still at the site but no operator was there. No one injured. Electrical protection operated - LV fuse on affected phase operated. | Conductor (bare) | 0 | 0 | 0 |  | mfa22 | 1 phase of 3-Wire open wire 080 copper LV conductor down, struck by excavator. | No Go Zone (contact) | 42830.5382 |  |  | 6073 | Agricultural |  | 20170525SPN_02 | Infrastructure (network-based) | -37.9627 | 146.9563 | 1 | AusNet Services Distribution | Report | 7466 | 0.031392 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3860 | Maffra | Vehicle
On arrival crew carried out repairs | 51 MAILEY STREET, SUNSHINE WEST VIC 3020 | 30107477 | Vehicle | [6 empty] | Vic fire and Police reported a car hit a power pole at incident location, and snapped pole, pole on ground. On arrival the crew found that a car had collided with a wood pole. The pole split vertically, but still holding the LV conductors aloft and power still on. No shock or fire reported. | Conductor (bare);Service conductor;Pole (wood) | 2 | 2 | 2 |  | SSE014 | Vehicle collided with pole | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/05/2017 1:25 |  |  | 6083 | Roadway |  | 20170529PWA_04 | Infrastructure (network-based) | -37.7916 | 144.8122 | 1 | Powercor | Report | 7476 | 0.020464 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
On arrival crew carried out repairs | 18 ANTHONY STREET, NEWCOMB VIC 3219 | 32073738 | Working too close to overhead lines | [5 empty] | 2 | Passer-by Daniel, mobile 0413 980 245 reported wire down at the incident location. On arrival the fault crew found that a tip truck delivering crushed rock to a building site at the incident location, had backed up with the tipper still in the air. The tipper snagged the service to 20 Anthony Street and severed it, one end â€œALIVEâ€ was lying across the temporary fencing to the construction site the other end was down in front of 20 Anthony Street. No damage to customers installation. Driver of truck decamped site: no details obtained. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | GLE024 | Tip Truck struck service | Loss of supply;No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/05/2017 9:25 |  |  | 6087 | Roadway |  | 20170529PWA_06 | Infrastructure (network-based) | -38.1674 | 144.3983 | 1 | Powercor | Report | 7480 | 0.016948 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Newcomb | Vehicle
crew abolished service | 50 WESTBROOK STREET, KEW EAST VIC 3102 | 30178559 | Working too close to overhead lines | [5 empty] | 2 | Meter and servicing crew were sent to erect a builders temporary supply. On arrival the crew had discovered that a service line to a partially demolished house had been damaged and a live conductor was hanging at approximately head height. The area below this hanging cable was a freshly cast concrete slab and it appears that the service cable was damaged by machinery when excavating for this slab. The crew removed the service to make the site safe. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Service conductor | 0 | 0 | 0 |  | Q014 | Interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/05/2017 9:30 |  |  | 6099 | Residential |  | 20170531PWA_01 | Infrastructure (network-based) | -37.7947 | 145.0531 | 1 | CitiPower | Report | 7495 | 0.036519 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | Dug up
CEOT dispatched a fault crew to make safe, investigate and repair. Crew made safe then restored supply. Crew advised the head of the fuse dropped to the ground however no fire was present nor any scorch marks, Crew replaced the fuse holder without any concerns. | 210 KOO WEE RUP-LONGWARRY ROAD, LONGWARRY VIC 3816 | 2716082 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS228037. Attending Incd-137597-r fault crew reported a candled EDO fuse tube. | EDO fuse | 0 | 0 | 0 |  | WGL12 | EDO fuse tube burnt. | Other electricity related | 24/05/2017 8:00 | 1 | Negligible: no ground fire | 6101 | Agricultural |  | 20170531SPN_02 | Infrastructure (network-based) | -38.1281 | 145.7544 | 1 | AusNet Services Distribution | Report | 11258 | 0.039219 | 22kV AC | Moorabbin Airport | 3816 | Longwarry | Fuse
On arrival crew carried out repairs | 8 CULLITON ROAD, CAMBERWELL VIC 3124 | 30177504 |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire opposite Wilson Park at the incident location. On arrival the Linesmen determined that an FOLCB on Pole LIS 10497 overheated causing it to be damaged. The Linesmen on further investigation found burn marks on the pole and concluded that there was a small fire on the pole. There were no reported injuries or third party damages. | Connection box | 2 | 2 | 2 |  | RD009 | Cause could not be confidently determined | Pole-top fire | 19/05/2017 17:09 | 1 | Negligible: no ground fire | 6109 | Roadway |  | 20170601PWA_03 | Infrastructure (network-based) | -37.8402 | 145.0724 | 1 | CitiPower | Report | 12456 | 0.035271 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Connection
A faults crew attended and found the 22kV red phase 31.5amp powder filled fuse at "Roberna-Levanswell2" ground type substation at pole No. LIS 1816401 had candled and exploded spraying porcelain fragments over the ground. No damage or injuries were sustained. The fuse was replaced restoring supply and the crew suspected the fuse was already cracked that caused it to fail. | 29 ROBERNA STREET, MOORABBIN VIC 3189 | 1816401 |  |  |  | Candled fuse |  |  | 1 | The factory owner advised of a part supply failure. Factories in Roberna Street, Moorabbin advised of a part supply failure and a faults crew was dispatched to investigate. | Powder filled;Outdoor | 0 | 0 | 0 |  | HT 06 | A HV fuse candled and operated. | Pole-top fire | 28/05/2017 13:35 | 1 | Negligible: no ground fire | 6104 | Industrial |  | 20170601UTD_01 | Infrastructure (network-based) | -37.9459 | 145.0675 | 1 | United Energy Distribution | Report | 7502 | 0.040043 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Fuse
On arrival crew commenced repairs | 308 YANDO SWAMP ROAD, YANDO VIC 3537 | 32027606 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customer reported that combine harvester had knocked over a pole in a paddock and wires on the ground. On arrival the crew found pole had been knocked over by a harvester. The harvester had approached from the North and hit the stay wire before the pole and knocked the pole. No wires had contacted the harvester and they were able to safely remove their staff once they had identified where the wires were. No fire, No injuries, No third party damage. | SWER conductor;Pole (wood) | 2 | 2 | 2 |  | CTN002 | Header struck stay and pole | Loss of supply;Damage to network assets | 42772.7674 |  |  | 6119 | Agricultural |  | 20170605PWA_03 | Infrastructure (network-based) | -36.0287 | 143.7814 | 1 | Powercor | Report | 7520 | 0.03069 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3537 | Yando | Vehicle
Crew attended and LV leads replaced. | 148-150 PINE AVENUE, MILDURA VIC 3500 | 33105997 |  |  |  | Age |  |  | 2 | A worker received an minor electric shock when his elbow accidentally touched the existing lead between a fuse switch disconnector and LV cable attached to a pole. He was securing a fuse box on the concrete pole pole with a band it strap at at the time. | Conductor (insulated) | 0 | 0 | 0 |  | MDA032 | Deteriorated electrical insulation | Minor shock | 17/01/2017 12:30 |  |  | 6121 | Roadway |  | 20170605PWA_05 | Infrastructure (network-based) | -34.1864 | 142.1551 | 1 | Powercor | Report | 12458 | 0.0077755 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | OH Cable
Site made safe and transformer oil spill contained. | 217 SUNSHINE ROAD, TOTTENHAM VIC 3012 |  | Copper theft | [5 empty] | 2 | Copper theft of (ground type) transformer windings. | Outdoor | 0 | 1 | 0 |  |  | Vandals cut fence to gain access to outdoor transformer. Transformer was pushed to the ground and transformer copper windings were stolen. | Damage to network assets | 43014.4583 |  |  | 6135 | Industrial |  | 20170610JEM_01 | Infrastructure (network-based) | -37.8004 | 144.8514 | 1 | Jemena | Report | 7541 | 0.030024 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3012 | Tottenham | Other
Fault crew attended & confirmed tails had been cut at his service pole in this property and going to meter as well. Crew removed fuses at pole end removed 4 core service to property & meters 0375804 & 0348204. | 390 PLENTY ROAD, PRESTON VIC 3072 | Pole No. A077673 | Unauthorised access | [5 empty] | 2 | Frank called the Zinfra complaints phone line stating that he climbed his service pole on his property and cut lived service cable due to being unable to gain an abolishment of the overhead service due to issues with paperwork and the retailer. Frank did not supply any further details as to who he was. | Neutral screen | 0 | 0 | 0 |  | EPN35 | Frank stated he climbed his service pole and cut overhead service. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/06/2017 9:45 |  |  | 6143 | Residential |  | 20170613JEM_01 | Infrastructure (network-based) | -37.7415 | 145.0097 | 1 | Jemena | Report | 12403 | 0.017698 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
On Arrival crew carried out repairs | 19 WONNON COURT, SWAN HILL VIC 3585 | 34005463 | Working too close to underground cables | [5 empty] | 2 | Customer advised a civil contractor had damaged an underground service cable, at the incident location. On arrival the crew found the underground service cable had been pierced by directional borer, supply unaffected, insulation damaged on 1 phase, made safe. There were no reported injuries, no fire, no property damage. | Services cable | 2 | 2 | 2 |  | SHL008 | Directional boring | Damage to network assets | 42860.7618 |  |  | 6144 | Roadway |  | 20170613PWA_03 | Infrastructure (network-based) | -35.3389 | 143.5486 | 1 | Powercor | Report | 7551 | 0.014042 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Dug up
CEOT dispatched a fault crew to investigate, make safe and carry out or arrange for any necessary repairs. The cut HV conductors were repaired. | 30 GALE STREET, WARATAH BAY VIC 3959 | 2021289 | Manned aircraft |  |  |  |  | Phase to phase | 1 | IMS 228477. Report of a crop duster aeroplane hitting HV conductors. The property owner advised it was the 3rd pass when the crop duster hit the conductors, the plane was able to keep flying even after the conductors were cut. All 3 conductors were cut and the conductors were reasonably new aluminium clad conductors. The span is approximately 600m in length and after rectifying the cut conductors the height was 7.1m high. HV fuses operated. No report of any injuries. | Conductor (bare) | 0 | 0 | 0 |  | ftr21 | Crop duster plane made contact with overhead HV/LV line. | No Go Zone (contact) | 42984.6215 |  |  | 6138 | Agricultural |  | 20170613SPN_01 | Infrastructure (network-based) | -38.8106 | 146.0634 | 1 | AusNet Services Distribution | Report | 12363 | 0.005853 | 22kV AC | Morwell (Latrobe Valley Airport) | 3959 | Waratah Bay | Other
Underground crew confirmed copper theft from pole to pit. However, there was no live feed to the box on this pole and it is all old material. Underground crew left cable capped at base of pole and made safe. | 650 KONAGADERRA ROAD, CLARKEFIELD VIC 3430 | A018290 | Theft | [5 empty] | 2 | Box on pole #A018290 smashed and cover guards ripped off. Standby fault crew attended and found underground 16mm 4core cable sticking out at base of pole and cables exposed. Dress down is ripped off pole. underground 4core cable ripped out and sticking up from ground. | Cable;Pole (concrete) | 2 | 2 | 2 |  | SBY14 | Copper theft. | Damage to network assets | 14/06/2017 15:48 |  |  | 6160 | Public space |  | 20170614JEM_01 | Infrastructure (network-based) | -37.5121 | 144.7841 | 1 | Jemena | Report | 7570 | 0.017058 | Low voltage AC (<1kV) | Melbourne Airport | 3430 | Clarkefield | Other
On arrival crew carried out repairs | 26-42 OLD AERODROME ROAD, ECHUCA VIC 3564 | 30140702 | Vehicle | [5 empty] | 2 | Customer advised a delivery truck had hit overhead lines, at the incident location. On arrival the crew found a damaged service cable, damaged 3 phase fuse box and LV leads were broken off the transformer bushings. A small tip truck struck service line while driving with tipper elevated. There was no ground fire , no reported injuries or third party property damage. | Service conductor;Pole mounted | 2 | 2 | 2 |  | ECA012 | Truck struck service line | Loss of supply;Damage to network assets | 42983.6062 |  |  | 6155 | Roadway |  | 20170614PWA_01 | Infrastructure (network-based) | -36.1438 | 144.7557 | 1 | Powercor | Report | 7563 | 0.037464 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | Vehicle
On arrival crew carried out repairs | 625 MIDLAND HIGHWAY, HUNTLY VIC 3551 | 30030127 | Vehicle | [5 empty] | 2 | CFA reported sparking from road crossing service cable and Brigade enroute to incident location. On arrival the crew found the overhead service had been pulled down by an unknown vehicle. Service wire down from pole to house laying in water channel and road, broken from pole end customer has no power There were no reported injuries, no fire, no property damage. | Service conductor | 2 | 2 | 2 |  | EHK023 | Unknown vehicle struck service line | Loss of supply;Damage to network assets | 43013.1854 |  |  | 6158 | Roadway |  | 20170614PWA_03 | Infrastructure (network-based) | -36.6654 | 144.3323 | 1 | Powercor | Report | 7568 | 0.0066898 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Huntly | Vehicle
The pole type substation was isolated and a construction crew attended and replaced the LV transformer leads, krone box and the 5amp HV fuse at pole number 34631 before supply was restored to normal. | 151 HUTTON ROAD, KEYSBOROUGH VIC 3173 | 211353 |  |  |  | Defective component;Overheated connection |  |  | 1 | At 5.38PM on 13/06/2017, 22kV ACR DN9850 located in Chapel Road successfully reclosed and held. The United Energy Faults and emergencies call centre received a call reporting that a transformer is on fire. Either the LV krone box or the low voltage transformer leads short circuited at "Hutton P13-Chapel" pole type substation that caused a 100amp LV fuse and the HV white phase 5amp powder filled fuse to operate. A pole fire was reported as the LV transformer leads melted. | Equipment;Connection box | 0 | 0 | 0 |  | KBH34 | Either the LV krone box or the low voltage transformer leads short circuited at "Hutton P13-Chapel" pole type substation. | Pole-top fire | 13/06/2017 17:30 | 1 | Negligible: no ground fire | 6164 | Roadway |  | 20170615UTD_02 | Infrastructure (network-based) | -38.0124 | 145.1572 | 1 | United Energy Distribution | Report | 11273 | 0.011834 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Pole
On arrival crew carried out repairs | 944 GLENELG HIGHWAY, WESTMERE VIC 3351 | 32097078 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Customer advised a Tractor with an air seeder behind it has made contact with an overhead service line and pulled it down at the incident location. On arrival the crew found a damaged service cable. There was no fire, injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | ART033 | Farm equipment being transported struck service | Damage to network assets | 31/05/2017 17:00 |  |  | 6175 |  |  | 20170619PWA_04 | Infrastructure (network-based) | -37.6894 | 142.9645 | 1 | Powercor | Report | 7588 | 0.027791 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3351 | Westmere | Vehicle
CEOT dispatched a fault crew to make safe, isolate and carry out or arrange for necessary repairs. SWER pole stay and conductor repaired. | 200 CAPE LIPTRAP ROAD, TARWIN LOWER VIC 3956 | 2013877 |  | Animal |  | Mechanical breakdown |  | Phase to earth | 1 | IMS 228540. After 5 Reclose Trips an AusNet Services' fault crew sent to patrol FTR21 Switch FT093. Upon arrival the crew found a broken stay at pole 2013877, AT3 in a paddock. The crew found 7 dead cows at the base of LIS 2013877. The make-off had broken at the end of the stay rod causing the pole to lean forward leaving the SWER conductor approximately 1.5m off the ground in the middle of the span. There is a large mud area around the pole and stay where animals have been standing and commonly rub against. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | ftr21 | Animal Incident | Less than $50k damage;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Fatality of livestock, pet or companion animal | 15/06/2017 13:55 |  |  | 6172 | Agricultural |  | 20170619SPN_01 | Infrastructure (network-based) | -38.8637 | 145.9554 | 1 | AusNet Services Distribution | Report | 12364 | 0.027118 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3956 | Tarwin Lower | AF Other
On arrival crew carried out repairs. | 28 OLD CHAPEL LANE, ELPHINSTONE VIC 3448 | 33026659 |  |  |  | Fuse failed to eject |  |  | 2 | Customer reported all supply fail. On arrival crew found that EDO fuse had failed to operate correctly and appears to burnt in half. They was no fire, injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | CMN001 | Ruptured fuse barrel | Pole-top fire | 42831.3472 | 1 | Negligible: no ground fire | 6184 | Agricultural |  | 20170621PWA_01 | Infrastructure (network-based) | -37.0843 | 144.315 | 1 | Powercor | Report | 7601 | 0.00076042 | 22kV AC | Bendigo Airport | 3448 | Elphinstone | Fuse
CEOT dispatched an AusNet Services' fault crew to isolate and make safe. An AusNet Services' electrical underground contractor was sent to repair the damaged underground service cable and was advised it was an AusNet Services' cable due to having a service pit installed further along the fence. The Tara Electrics; Electrician was reminded to physically identify any underground asset prior to excavating to ensure they know their exact locations. | 537 CALROSSIE-WON WRON ROAD, WON WRON VIC 3971 |  | Working too close to underground cables |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 228142. Contractor Tara Electrics, (contact person is Gary Phone 51826377), reported an AusNet Services' pole to pit underground LV service cable was dug up by a trencher machine. Tara Electrics were carrying out private underground works at the time of the incident. The Tara Electrics' contractor had MOCCs (Dial Before You Dig) plans on site and it identified the underground service cable,however the Tara Electrics' Electrician mistook it for the other underground service cable running parallel to the service pit on the closest boundary. It was an honest mistake. No one on site were hurt or injured and no electric shock was received by anyone. | Services cable | 0 | 0 | 0 |  | ftr21 | Private electrical contractor undertaking trenching work contacted an AusNet Service' underground service cable. | No Go Zone (contact) | 42830.5139 |  |  | 6186 |  |  | 20170621SPN_02 | Infrastructure (network-based) | -38.4653 | 146.7155 | 1 | AusNet Services Distribution | Report | 7604 | 0.014515 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3971 | Won Wron | Dug up
The investigating asset performance engineer paid a visit to the incident site and confirmed that the bare conductor has been replaced with LV ABC by Jemena crew. The incident was ruled out as a fire start as there was no evidence of an asset fire or vegetation fire during restoration works. | 6 GALLANT STREET, FOOTSCRAY VIC 3011 | Pole no. A036597 |  |  |  | Age;Fatigue |  |  | 2 | Bare conductor in a laneway at the rear of 6 Gallant Street, Footscray was reported by a resident to have burnt out mid-span (singeing) and fallen to ground. | Conductor (bare) | 0 | 0 | 0 |  | FE06 | The exact cause could not be determined by the investigating asset performance engineer because the bare conductor had already been replaced by LV ABC by the time he visited the incident site. The mostly likely cause of the bare conductor failure is age- and/or fatigue-related deterioration. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Singeing or local charring/blackening only | 29/05/2017 15:16 |  |  | 6188 | Residential |  | 20170622JEM_01 | Infrastructure (network-based) | -37.7971 | 144.8983 | 1 | Jemena | Report | 12404 | 0.017691 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Conductor
Area made electrically safe, oil spillage contained and samples sent for analysis. No oil contamination in waterways, creeks or storm water was identified. The transformer has been removed and site was made safe. | 217 SUNSHINE ROAD, TOTTENHAM VIC 3012 |  | Copper theft | [5 empty] | 2 | A live distribution ground-type transformer at a uninhabited business customer premises has been vandalised and its internals stolen. The vandals stole the LV bus, cut HV dropper leads, and pushed transformer over on its side. The transformer top was removed and copper windings were stolen. As a result of the transformer being tipped over during the criminal act, oil was spilled. | Outdoor;Transformer | 0 | 1 | 0 |  | TH22 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43014.6396 |  |  | 6192 | Industrial |  | 20170623JEM_02 | Infrastructure (network-based) | -37.8004 | 144.8514 | 1 | Jemena | Report | 12405 | 0.02526 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3012 | Tottenham | Other
On arrival crew carried out repaqirs. Defect notice issue for POA | 13 DRAKE STREET, SUNSHINE NORTH VIC 3020 | 32175993 | Vehicle | [5 empty] | 2 | A driver informed his truck has pulled down a wire at the incident location. Upon arrival the Powercor crew found that the service and the POA had been damaged, the service line was tangled on the vehicle in customers drivway. There was no fire or injuries reported. There was no fire or injuries. | Service conductor | 2 | 2 | 2 |  | SSE011 | Prime mover entangled with service | Loss of supply;Damage to network assets | 42892.5424 |  |  | 6193 | Residential |  | 20170626PWA_01 | Infrastructure (network-based) | -37.7667 | 144.829 | 1 | Powercor | Report | 7613 | 0.038848 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
On arrival crew carried out repairs | 134 MELBA PARADE, ANGLESEA VIC 3230 | 32079086 |  |  |  | Overheated connection |  |  | 2 | CFA reported that a pole mounted fuse box was on fire at the incident location. On arrival the crew found that the fuse box had been on fire and insulation melted away. Melted plastic and debris fell to the ground but did not start a fire due to moisture, no reported third party damage or any injuries. | Connection box | 2 | 2 | 2 |  | WP021 | Unable to determine due to damage | Pole-top fire;Loss of supply | 17/06/2017 17:27 | 1 | Negligible: no ground fire | 6202 | Roadway |  | 20170627PWA_04 | Infrastructure (network-based) | -38.428 | 144.1734 | 1 | Powercor | Report | 7693 | 0.03878 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Fuse
Site made safe by Jemena. Pole no. A028797 and a steel HV crossarm on pole no. A028798 were replaced. | 2 TOTTENHAM PARADE, WEST FOOTSCRAY VIC 3012 | Pole no. A147296 | Vehicle |  | Highly unlikely |  |  |  | 1 | Truck hit pole opposite 2 Tottenham Pde, West Footscray (pole no. A147296) resulting in HV and LV conductors falling to ground. Pole no. A147296 and a steel HV crossarm on pole no. A028798 had to be replaced. There was no HV injection and nobody was injured as a result of conductors on ground. Details of driver and company can be found in photos attached in Section 7. Notes & Findings | Conductor (ABC);Conductor (bare);Crossarm (steel) | 0 | 0 | 0 |  | FW05 | Vehicle impact on pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42984.6354 |  |  | 6222 | Industrial |  | 20170703JEM_01 | Infrastructure (network-based) | -37.8128 | 144.8601 | 1 | Jemena | Report | 12471 | 0.024568 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3012 | West Footscray | Vehicle
On arrival crew carried out repairs. | 431 ANDERSONS WOOLSHED ROAD, GOBARUP VIC 3559 | 33102775 | Working too close to overhead lines | [5 empty] | 1 | A customer ( Terry ) reports a tree had been cut and it had fallen onto the power lines and started a fire at the incident location. A crew attended and found the land owner had been pushing trees over with a bull dozer when one of the trees had contacted the overhead conductor, breaking the conductor, causing it to fall to the ground. The contacting tree branch started to burn. The customer extinguished the fire. There were no reported shocks, injuries or 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHP021 | Vegetation: Trees Incident | Other vegetation | 42862.5028 | 1 | Negligible: no ground fire | 6229 | Agricultural |  | 20170706PWA_02 | Infrastructure (network-based) | -36.6867 | 144.9183 | 1 | Powercor | Report | 7668 | 0.040439 | 12.7kV AC (SWER) | Mangalore Airport | 3559 | Gobarup | Vehicle
On arrival crew commenced repairs | 3842 BENDIGO-MARYBOROUGH ROAD, EDDINGTON VIC 3472 | 32029298 |  |  |  | Corrosion |  |  |  | VicFire reported that a conductor was down at the incident location. On arrival the crew found that a conductor of a single phase spur line had failed approximately 10Metres from T/off pole 213 Tarnagulla, the conductor remained back-fed via the HV winding of the load side transformer for a period prior to Tarnagulla ACR tripping to lockout on SEF. A section fuse on Tarnagulla P211 operated but hung up. Approximately 12 small patches of burnt crop were observed by the crew, caused by the downed HV conductor. There were no reported injuries or 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO007 | Previously undetected mid-span conductor damage | Grassfire | 42985.7778 | 1 | Localised: less than 10 sq.m | 6235 | Agricultural |  | 20170711PWA_01 | Infrastructure (network-based) | -36.8733 | 143.874 | 1 | Powercor | Report | 12580 | 0.029929 | 22kV AC | Bendigo Airport | 3842 | Eddington | Conductor
On arrival crew carried out repairs | 369 ORMOND ROAD, SPRINGBANK VIC 3352 | 30007479 | Copper theft | [5 empty] | 2 | A pole inspector reported an missing earth cable at the above location. A crew attended and found the high voltage earth cable missing from the pole. The crew replaced the earth cable. No protection operated. There were no reported shocks, injuries or fire start. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | Theft | Damage to network assets | 16/06/2017 8:17 |  |  | 6237 | Roadway |  | 20170712PWA_02 | Infrastructure (network-based) | -37.5222 | 144.0568 | 1 | Powercor | Report | 7684 | 0.027998 | Earthing cable | Ballarat Aerodrome | 3352 | Springbank | Other
On arrival crew commenced repairs | 58 NIMMO STREET, MIDDLE PARK VIC 3206 | 30213986 |  |  |  | Fault on customer installation |  |  | 2 | The MFB call the CitiPower report room to advise of a wire down and fire on service wire at 58 Nimmo Street, Middle Park. Upon attendance the CitiPower faults crew found the LV overhead neutral screen service had come away from the fascia and was resting on the ground at incident location. The crew found the LV fuse box and customer LV mains beyond the fuse box burnt out. There was no ground fire or injuries | Service conductor;Customer installation | 2 | 2 | 2 |  | AP008 | suspected customer side fault | Damage to network assets | 16/06/2017 3:03 |  |  | 6241 | Residential |  | 20170713PWA_01 | Infrastructure (network-based) | -37.8504 | 144.9617 | 1 | CitiPower | Report | 17437 | 0.020647 | Low voltage AC (<1kV) | Essendon Airport | 3206 | Middle Park | OH Cable
on arrival crew carried out repairs | 130 POUSTIES ROAD, AVALON VIC 3212 | 30250434 |  |  |  | Leakage |  |  | 2 | A Powercor inspector has reported a missing HV fuse at the incident location. On arrival, crew found that a fuse had hung up. This was not reported at the time of the fault as the connection is given to a pump station that has not been in service for some time. There were no injuries, no evidence of fire or ground fire. | EDO fuse | 2 | 2 | 2 |  | FNS022 | electrical leakage | Hung-up fuse only | 20/06/2017 9:08 |  |  | 6250 | Agricultural |  | 20170714PWA_01 | Infrastructure (network-based) | -38.0157 | 144.4905 | 1 | Powercor | Report | 7702 | 0.0032836 | 22kV AC | Avalon Airport | 3212 | Avalon | Fuse
Crew repaired pole. New 'P' bracket installed. | 9 OBRIENS LANE, LONGLEA VIC 3551 | 33031488 |  |  |  | Leakage |  |  | 1 | Crew attending outage found damaged and burnt SWER pole-top. Centre phase burnt off pole-top. Crew repaired and replaced with new 'P' bracket. (There is no photographic evidence of this event) | Pole top | 0 | 0 | 0 |  | BET005 | Leakage current causing pole fire. | Pole-top fire | 14/09/2016 9:37 | 1 | Negligible: no ground fire | 6252 | Agricultural |  | 20170714PWA_03 | Infrastructure (network-based) | -36.774 | 144.4392 | 1 | Powercor | Report | 7760 | 0.041304 | 12.7kV AC (SWER) | Bendigo Airport | 3551 | Longlea | Pole
On arrival crew carried out repairs | 2 NEILL STREET, BEAUFORT VIC 3373 | 33106523 | Vehicle | [5 empty] | 1 | A report was received from Vic Fire that a car had hit a pole in High Street Beaufort and conductor where on the ground and laying across the Western Hwy (High Street) Beaufort. On arrival the crew found that a car had hit a public lighting pole and broken the pole off at ground level. The pole has then fallen across the HV & LV conductors at the incident location. One HV conductor was broken and lying on the ground and all of the LV conductors had been broken and were lying on the ground. Protection operated as expected. The conductors were repaired and supply was restored. There was no shock, injury or fire start. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | BAS011 | Car struck pole | Loss of supply;Damage to network assets | 26/06/2017 17:10 |  |  | 6264 | Roadway |  | 20170717PWA_06 | Infrastructure (network-based) | -37.4293 | 143.3893 | 1 | Powercor | Report | 7719 | 0.041618 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3373 | Beaufort | Vehicle
A faults crew attended and placed the substation circuits to LV parallel and isolated the transformer HV and LV. The deteriorated krone box was replaced with new 315amp DIN type fuses installed and supply was restored to normal upon completion. | 27 WOODVALE DRIVE, CARRUM DOWNS VIC 3201 | 8814301 |  |  |  | Electrical breakdown;Overheated connection |  |  | 2 | Per fire authority - Transformer is on fire and a truck is on its way. A LV krone box attached to pole No. LIS 8814301 at "Woodvale-Strathearn" pole type substation caught fire and the cause was attributed to a probable loose connection that possibly overheated. No photos were taken at the time of the event. | Disconnector/isolator | 0 | 0 | 0 |  | FTN 23 | The cause was attributed to a probable loose connection that possibly overheated. | Pole-top fire | 30/06/2017 9:00 | 1 | Negligible: no ground fire | 6276 | Roadway |  | 20170721UTD_08 | Infrastructure (network-based) | -38.1055 | 145.1873 | 1 | United Energy Distribution | Report | 7733 | 0.031103 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Connection
On arrival crew isolated supply and carried out repairs | 366 ALBERT ROAD, SOUTH MELBOURNE VIC 3205 | 30214847 | Working too close to overhead lines | [6 empty] | A customer reported that her husband has contacted wires outside their property with a scissor lift at the incident location. On arrival the fault crew found that the customer had been cleaning the guttering to his home when he has inadvertently contacted live overhead low voltage mains conductors with the scissor lift. The Blue phase conductor burnt through and fell to the ground, white phase was burnt (50% through) but remained in situ. A spotter was being used at the time but this has failed to prevent the incident. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | AP017 | accidental contact with LV by Scissor lift | Loss of supply;No Go Zone (contact) | 21/07/2017 8:46 |  |  | 6279 | Residential |  | 20170724PWA_01 | Infrastructure (network-based) | -37.8409 | 144.9601 | 1 | CitiPower | Report | 7738 | 0.018063 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Vehicle
Made safe. Isolated faulted section and carried out repairs | 250 VENTNOR BEACH ROAD, VENTNOR VIC 3922 | 2807006 |  | Wind |  | Mechanical breakdown |  | Phase to earth | 2 | IMS 229329 - Operator sent out on call for dim lights. Found conductor broken and on ground ( Load Side ) LIS : 2807006. No damage was caused. | Conductor (bare) | 0 | 0 | 0 |  | PHI12 | 1ph 0.064Cu conductor believed to have failed during high winds | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/07/2017 19:25 |  |  | 6291 | Residential |  | 20170725SPN_01 | Infrastructure (network-based) | -38.4819 | 145.2103 | 1 | AusNet Services Distribution | Report | 13619 | 0.033594 | 22kV AC | Moorabbin Airport | 3922 | Ventnor | Conductor
A faults truck attended and removed the overhead service as the front of the property had been demolished. The neutral screen service was disconnected from pole No. LIS 2327405 and the smashed meter retrieved from the rubbish near the side gate. The attending faults crew took photos and advised their supervisor of their findings. | 201 GRANGE ROAD, GLEN HUNTLY VIC 3163 | 2327405 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Caller advised the overhead service has become detached from the pole and is laying in the front yard still attached to the house end. Demolition company workers dropped the overhead neutral screen from the house after they removed the front portion of the old timber home. The single phase meter had also been smashed and was laying in rubble at the front of the property. A review of United Energy records indicated that no effort had been made to correctly have the electricity supply abolished that created a serious risk to public safety. It appears that no electric shocks were received. | Service conductor;Neutral screen | 0 | 0 | 0 |  | CFD 15 | Demolition company workers dropped the live overhead neutral screen from the house. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/07/2017 10:40 |  |  | 6294 | Residential |  | 20170726UTD_02 | Infrastructure (network-based) | -37.8961 | 145.0454 | 1 | United Energy Distribution | Report | 7842 | 0.0020069 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Glen Huntly | Other
A faults crew attended and made the site safe and obtained details of the excavator driver and the company involved. The faults crew arranged for the replacement of the LV strain pole, crossarms and services that was completed under access authority conditions. Supply was restored upon completion following installation tests. | 2 MONACO STREET, DONCASTER VIC 3108 | 7069728 | Working too close to overhead lines | Fallen |  |  |  |  | 1 | Customers supplied from "Monaco-Buckingham" substation advised of an all supply failure and there are reports of wires down in Monaco Street, Doncaster. An excavator has brought down a large gum tree which has inadvertently fallen on LV overhead conductors in Monaco Street, Doncaster. This caused a LV strain pole LIS No. 7069728 to break that requires replacement along with an adjacent LV intermediate crossarm and four overhead services. No shocks or damage to the excavator occurred. | Conductor (bare);Service conductor;Crossarm (wood);Pole (concrete) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact) | 29/06/2017 13:15 |  |  | 6306 | Residential |  | 20170727UTD_01 | Infrastructure (network-based) | -37.7808 | 145.1108 | 1 | United Energy Distribution | Report | 7772 | 0.0033345 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | Trees
Transformer was isolated, then the fire was extinguished by MFB. Transformer was replaced and supply was restored via LV. | UNIT 7 177-181 NORTHBOURNE ROAD, CAMPBELLFIELD VIC 3061 | NORTHBOURNE-REX substation (pole no. A132829) |  |  |  | Age |  |  | 2 | MFB reported a fire on cable to 300kVA ground-type distribution transformer (next to pole no. A132829) Jemena operator arrived to find ground substation on fire. Jemena operator isolated the transformer, then MFB put out the fire. Photo is attached in the "Notes & Findings" section of this report. | Conductor (bare);Transformer | 0 | 1 | 0 |  | ST34 | Jemena operator arrived on site and confirmed that it was a bad connection that caused the overheating and eventually started a fire on the LV red phase bushing of the ground substation. | Plant/equipment | 27/07/2017 18:30 | 1 | Negligible: no ground fire | 6314 | Industrial |  | 20170728JEM_01 | Infrastructure (network-based) | -37.65 | 144.9616 | 1 | Jemena | Report | 12946 | 0.028591 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Connection
On arrival crew carried out repairs | 18 KIEWA STREET, CLIFTON HILL VIC 3068 | 30169158 |  |  |  | Overheated connection |  |  |  | A passer-by reported that the pole is on fire at the incident location. On arrival the fault crew found that a krone box had overheated caught fire and debris had fallen onto the footpath at the incident location. The krone box fire self-extinguished. There was no injury as a result of this incident. | Connection box | 2 | 2 | 2 |  | F029 | Overheated connection | Pole-top fire | 27/07/2017 7:10 | 1 | Negligible: no ground fire | 6313 | Public space |  | 20170728PWA_01 | Infrastructure (network-based) | -37.7922 | 145.0002 | 1 | CitiPower | Report | 7780 | 0.040016 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Clifton Hill | AF Other
Area isolated and made safe. Repairs made to HV conductors. Pole no. A025636 and pole-mounted substation were replaced. Police were in attendance, however no driver or vehicle details were obtained as the car was removed while switching was being performed. | 560 MT RIDLEY ROAD, MICKLEHAM VIC 3064 | Pole no. A025636 | Vehicle | [5 empty] | 1 | HV conductors on the ground due to vehicle impact on pole. Jemena electrical network operator found footpath and centre phase fuse blown, Mt Ridley Road east of Mickleham Road | Conductor (bare);Pole mounted;Pole (concrete) | 0 | 0 | 0 |  | C0011 - ACR10002 Mickleham Rd P085 | Car hit pole no. A025636 | Damage to network assets | 28/07/2017 21:48 |  |  | 6321 | Peri-urban |  | 20170729JEM_01 | Infrastructure (network-based) | -37.563 | 144.8876 | 1 | Jemena | Report | 7788 | 0.030314 | 22kV AC | Melbourne Airport | 3064 | Mickleham | Vehicle
Site made safe. Jemena crew Isolated affected area, made repairs to LV conductor and replaced LV bridge. | 78 KERFERD STREET, ESSENDON NORTH VIC 3041 |  |  | Wind | Neutral | Conductor clashing |  |  | 1 | Strong winds caused LV conductors to clash resulting in bare LV conductor (Aluminium Conductor Galvanised Steel Reinforced) on ground between pole no. A064659 and pole no. A042768. | Conductor (bare) | 2 | 2 | 2 |  | ES25 | Strong winds caused bare LV conductors to clash. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/07/2017 11:25 |  |  | 6323 | Residential |  | 20170729JEM_03 | Infrastructure (network-based) | -37.7367 | 144.9006 | 1 | Jemena | Report | 7975 | 0.015941 | Low voltage AC (<1kV) | Essendon Airport | 3041 | Essendon North | Other
Attending LEI conducted damage assessment of all properties on the circuit and confirmed that only the blue phase had been affected. Jemena faults crew isolated HV and LV section, then replaced pole and crossarms under Access Permit. Jemena faults crew tested HV and LV lines and found blown fuses in substation. The fuses were replaced and the circuit was re-energised. The attending LEIs inspected all distribution metering equipment and customer switchboards and installations and issued damage reports damage reports to affected properties. All distribution metering equipment and customer switchboards and installations were inspected for damage before being reconnected to supply. | 651 PASCOE VALE ROAD, OAK PARK VIC 3046 | A093270 | Vehicle |  |  | HV injection |  |  | 1 | Car hit HV/LV wooden pole in front of 649 Pascoe Vale Road, Oak Park, causing HV lines to make contact with LV lines resulting in a HV injection. HV and LV conductors fell down to the ground. | Pole (wood) | 0 | 0 | 0 |  | PV14 | Vehicle impact on pole | HV injection;Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/07/2017 2:26 |  |  | 6331 | Roadway |  | 20170731JEM_01 | Infrastructure (network-based) | -37.715 | 144.9176 | 1 | Jemena | Report | 7810 | 0.038266 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3046 | Oak Park | Vehicle
The crew isolated supply to the pole and the light will be replaced at a later date. | 235 ALBERT STREET, SEBASTOPOL VIC 3356 | 34000831 |  |  |  | Overheated connection |  |  |  | A report was received from Vic Fire that a street light was on fire at the incident location. On arrival the crew found that one of the light heads on the pole in the median strip at the above location had caught fire and self-extinguished. There was no injury, shock, ground fire or third party damage. | Public lighting | 2 | 2 | 2 |  | BAS034 | Overheated light fitting | Pole-top fire | 30/07/2017 21:56 | 1 | Negligible: no ground fire | 6326 | Roadway |  | 20170731PWA_01 | Infrastructure (network-based) | -37.6017 | 143.8412 | 1 | Powercor | Report | 7793 | 0.014214 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Sebastopol | AF Other
On arrival crew isolated supply and carried out repairs | 720 OLD MELBOURNE ROAD, LITTLE RIVER VIC 3211 | 30059970 |  |  |  | Unknown technical factor |  |  |  | A fault was reported as All Supply Fail at the incident location. The crew attended and found that a LV Crossarm and fuse box had caught fire overnight. Debris fell to the ground but did not start a fire. There were no reported shocks, injuries or ground fire. | Crossarm (wood);Connection box | 2 | 2 | 2 |  | FNS022 | Unable to determine due to damage | Pole-top fire;Loss of supply | 42742.2618 | 1 | Negligible: no ground fire | 6336 | Public space |  | 20170731PWA_05 | Infrastructure (network-based) | -37.9826 | 144.5011 | 1 | Powercor | Report | 7809 | 0.010803 | Low voltage AC (<1kV) | Avalon Airport | 3211 | Little River | Pole
Emergency services responded to report of smoke near Oakpark Road and Malings Road West Portland. Conductor reported on the ground and across Oakpark Road and report of small dry shrub smouldering. The road was closed and site secured by emergency services. Traffic management in place initially by shire and then by local contractor until repair works were completed the following day. AS A TRANSMISSION EVENT THIS IS NOT F FACTOR REPORTABLE ( F factor Scheme governs Distribution only) | 9 OAKPARK ROAD, PORTLAND WEST VIC 3305 |  |  |  |  | Insulator;Unknown technical factor |  |  | 1 | IMS 229499 - HYTS-APD No 2 500kV Line conductor down. Grass fire. | Conductor (bare) | 0 | 0 | 0 |  | HYTS-APD No 2 Lines | Polymeric suspension Insulator failed at tower (blue phase/bottom) on HYTS-APD No2 500kV Line. On going work with the insulator manufacturer to determine the root cause of insulator failure | Grassfire | 31/07/2017 13:15 | 0 | Localised: less than 10 sq.m | 6337 | Agricultural |  | 20170801SPN_01 | Infrastructure (network-based) | -38.3493 | 141.5732 | 1 | AusNet Services Transmission | Report | 13624 | 0.034697 | 500kV AC | Portland (Cashmore Airport) | 3305 | Portland West | Conductor
On arrival crew isolated supply and replaced service | 1 WHITFIELD COURT, SHEPPARTON VIC 3630 | 31027416 |  | Precipitation |  | Electrical breakdown |  |  |  | Customer called reporting service running across the road was sparking and banging and that sparks were landing on the road. The customers car was parked under the service line Upon arrival the attending linesman found that the rainy weather had caused the service to spark. There was no fire, injuries or third party property damage | Service conductor | 2 | 2 | 2 |  | STN022 | insulation failure | Singeing or local charring/blackening only | 42832.6965 |  |  | 6341 | Residential |  | 20170802PWA_02 | Infrastructure (network-based) | -36.3968 | 145.4022 | 1 | Powercor | Report | 7915 | 0.041243 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | OH Cable
On arrival crew isolated supply and carried our repairs. | 14 COLLINS STREET, MELBOURNE VIC 3000 | 30278957 | Working too close to underground cables | [6 empty] | A contractor reported that they have contacted a cable at the incident location. On arrival the fault crew found that a low voltage service cable (49mm double taped steel wire armour) located under the concrete pavement of the building was damaged by the contractor during building renovation works at the incident location. No MOCS details on site. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | MP051 | excavation work | No Go Zone (contact);Damage to network assets | 43015.3486 |  |  | 6350 | Commercial |  | 20170803PWA_03 | Infrastructure (network-based) | -37.8133 | 144.9731 | 1 | CitiPower | Report | 7828 | 0.037264 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew carried out repairs | 1 BARKLY STREET, CARLTON VIC 3053 | 30180584 |  |  |  | Leakage |  |  |  | MFB reported a street light pole on fire at the above incident location. On arrival, the crew found that MFB had extinguish the fire out of a Public Lighting head unit as it had faulted and caught on fire. There was no ground fire nor third party damaged. There were no reported injuries. Photo taken of poor quality due to dark environment. | Public lighting | 2 | 2 | 2 |  | BQ041 | not established | Pole-top fire | 42894.9889 | 1 | Negligible: no ground fire | 6369 |  |  | 20170807PWA_01 | Infrastructure (network-based) | -37.7983 | 144.9747 | 1 | CitiPower | Report | 7853 | 0.0074398 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | AF Other
Fault truck dispatched and replaced candling fuse. | 10 ANDREWS ROAD, LONGFORD VIC 3851 | 2505283 |  |  |  | Defective component;Candled fuse |  |  | 0 | IMS 229580 - Field crew advised of candling BA fuse. | Boric acid;EDO fuse | 0 | 0 | 0 |  | SLE31 | On arrival - fault crew observed candling BA on SL245 LIs No 2505283, Nil fire damage to ground. Note blown EDO fuse also at Sub pole LIS 1614360 WELLINGTON COBB SUB. Cause of Fault determined to be defective Surge Divertor on Wellington Cobb Substation. | Pole-top fire | 42802.8264 | 1 | Negligible: no ground fire | 6368 | Residential |  | 20170807SPN_01 | Infrastructure (network-based) | -38.1811 | 147.0908 | 1 | AusNet Services Distribution | Report | 7852 | 0.03847 | 22kV AC | Bairnsdale Airport | 3851 | Longford | Fuse
The crew isolated supply and carried out repairs. | 365 BUCHHOLZ ROAD, LISMORE VIC 3324 | 32054487 |  |  |  | Corrosion |  |  | 1 | Farmer reported a conductor that was hanging low in paddock. On arrival the crew discovered that a SWER conductor had dislodged from pole 6 and was hanging energised at approximately 1 metre above the ground. It appears that protection had not been called upon to operate. Armour rods and vibration dampers were present. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Conductor (bare);Insulator tie wires/connections | 2 | 2 | 2 |  | CDN004 | Conductor Tie damaged | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/07/2017 9:21 |  |  | 6375 | Agricultural |  | 20170808PWA_02 | Infrastructure (network-based) | -37.8898 | 143.2796 | 1 | Powercor | Report | 7859 | 0.026122 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3324 | Lismore | Connection
On arrival crew carried out repairs and issued a defect notice for POA repair. | 41 WHITES ROAD, WERRIBEE SOUTH VIC 3030 | 32171963 | Vehicle | [6 empty] | A passer-by advised a truck has pulled down a wire at the incident location. Upon arrival the Powercor crew found that the service and POA had been damaged. No other damage reported. | Service conductor | 2 | 2 | 2 |  | WBE034 | Truck contacted service line | Damage to network assets | 25/07/2017 11:35 |  |  | 6388 | Roadway |  | 20170809PWA_03 | Infrastructure (network-based) | -37.953 | 144.6953 | 1 | Powercor | Report | 7872 | 0.025676 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Vehicle
Attending Jemena operator isolated supply, contacted Jemena Network Control to arrange repairs and inform Jemena Works Practices for further investigation. | 77-81 GOWER STREET, PRESTON VIC 3072 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | Construction business undertaking excavation works on customer's property damaged HV underground cable supplying kiosk substation. | Cable | 0 | 0 | 0 |  | EP03 | Work Practices was advised by the Construction Supervisor as follows. The excavator operator was cleaning out the building foundation hole in preparation to pour the concrete, when the excavator bucket grabbed the concrete protective slab and the HV underground cable laying beneath. | Loss of supply;No Go Zone (contact) | 43047.35 |  |  | 6398 | Commercial |  | 20170811JEM_03 | Infrastructure (network-based) | -37.7428 | 145.0236 | 1 | Jemena | Report | 7898 | 0.029009 | 6.6kV AC | Essendon Airport | 3072 | Preston | Dug up
CitiPower faults crew attended to provide supervision for council workers removing the peoples bellowing from the substation. Victoria Police were also in attendance to ensure the safety of our crews. CitiPower faults crew replaced the Blue Phase conductor and re-instated the supply. The faults crew also repaired and fixed the door to allow the only access via an alternative pedestrian door. | 124-126 EXHIBITION STREET, MELBOURNE VIC 3000 | CP0006404 | Vandalism;Copper theft | [6 empty] | On Saturday July 29th CitiPower report room was notified by the by a passer-by that homeless people had broken into WESTWOOD PL â€˜Bâ€™ indoor substation and were using the substation for shelter. Upon further inspection the CitiPower crew had found the door damaged with asbestos particles on the floor, also the LV copper bus conductors on the Blue phase had been stolen affecting the building supply at 124-126 Exhibition St. On Sunday July 30th CitiPower report room had been advised by Victoria Police that the door had further been tampered with and the homeless people had re-entered the substation. No damage to the substation was evident and the CitiPower building contractor was contacted to secure the door with hoarding. | Indoor | 2 | 2 | 2 |  | MP020 | Vandalism & theft | Loss of supply;Damage to network assets | 29/07/2017 14:11 |  |  | 6397 | Commercial |  | 20170811PWA_02 | Infrastructure (network-based) | -37.8128 | 144.9711 | 1 | CitiPower | Report | 12079 | 0.018264 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
Crew attended and refitted conductor to pole and replaced the broken line tie. | 134 POPES ROAD, JUNORTOUN VIC 3551 | 30315272 |  | Within clearances |  |  |  |  | 2 | Tree clearing contractor were performing clearing for a transmission line running parallel to a Powercor 22kV line when a branch they were trimming came down across the Powercor distribution line crossing underneath. The lowered conductor impeded traffic flow on Popes road. The crew replaced the broken line tie and the conductorâ€™s original height was restored at 17:00 and There was no other damage to assets or private property. | Conductor (bare) | 0 | 0 | 0 |  | BET005 | Interference - vegetation being pruned from transmission line contacted distribution line. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42924.6458 |  |  | 6416 | Other | transmission easement | 20170816PWA_01 | Infrastructure (network-based) | -36.7629 | 144.3799 | 1 | Powercor | Report | 8122 | 0.0077141 | 22kV AC | Bendigo Airport | 3551 | Junortoun | Trees
The No4A 66kV Cap Bank CB was isolated pending investigation and repairs. | 917 PRINCES HIGHWAY, SPRINGVALE VIC 3171 |  |  |  |  | Earth fault;Out of balance load;Mechanical breakdown |  |  | 1 | IMS229106 - Co-incident with the opening of the No4A 66kV Cap Bank CB at SVTS, testers on site heard an explosion. The first responder was requested to attend. 13 capacitor cans failed internally, 3 of which ruptured, and the current balance CT cast epoxy housing on the Blue phase exploded. The explosion was contained within the CB enclosure, posed no threat to the safety of public and AusNet personnel. No customer outages. | Circuit breaker;Transformer | 1 | 1 | 0 |  |  | preliminary investigation findings indicated potential causes to be: - over-voltage from CB restrike, -cascade failure of cap cans from pre-stressed condition (earlier failure on 25/01/2017 - mechanical failure of the balance CT and the subsequent earth fault on the CT primary winding. Details attached in notes and findings. | Damage to network assets | 42985.6771 |  |  | 6422 |  |  | 20170817SPN_03 | Infrastructure (network-based) | -37.9285 | 145.1427 | 1 | AusNet Services Transmission | Report | 7918 | 0.028365 | 66kV AC | Moorabbin Airport | 3171 | Springvale | Other
On arrival crew isolated supply and carried out repairs. | 79 LUCAN STREET, BENDIGO VIC 3550 | 30027839 |  |  |  | Moisture ingress |  |  | 1 | Vicfire called reporting pole fireat the incident location. On arrival crew observed that FSD had partially melted, there was slight burning, (hardly visible) of the cross-arm under which sat the fuse box. There were no reported injuries or third party damage. There were no photos taken of the incident. | Connection box | 2 | 2 | 2 |  | EHK033 | attributed to Moisture ingress | Pole-top fire;Loss of supply | 42802.7431 | 1 | Negligible: no ground fire | 6425 | Public space |  | 20170818PWA_01 | Infrastructure (network-based) | -36.749 | 144.2851 | 1 | Powercor | Report | 7934 | 0.025914 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | Crossarm
Site made safe temporary fence is to be built. | 63-69 PIPE ROAD, LAVERTON NORTH VIC 3026 | 32174796 | Unauthorised work | [6 empty] | A customer informed a sparking transformer at the incident location. Upon arrival, The Powercor fault crew found that the ground type substation fence/wall and the live LV structure had been damaged. The building adjacent to the substation was being demolished by an excavator. At the time there were heavy winds and the excavator operator said the wall was collapsed by the wind while he was operating the machine nearby. The ESV informed and Work Safe attended. There were no injuries or fire. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | LVN032 | Demolition works in proximity to substation | No Go Zone (no contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43016.4403 |  |  | 6430 | Commercial |  | 20170821PWA_01 | Infrastructure (network-based) | -37.8245 | 144.8067 | 1 | Powercor | Report | 7940 | 0.010069 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3026 | Laverton North | Other
On arrival crew isolated supplies | DYNON PORT RAIL LINK, 470-474 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | Cp0002700 | Copper theft | [6 empty] | A Powercor employee, Peter Wright, reported a copper theft at the incident location. The crew found that the fruit market â€œJâ€ substation had been vandalised and live LV cables cut and taken away. A CB connected to LV circuits had also been stolen. There were no injuries or fire reported. | Indoor | 2 | 2 | 2 |  | DA020 | Copper theft | Damage to network assets | 43047.4618 |  |  | 6431 | Commercial |  | 20170821PWA_02 | Infrastructure (network-based) | -37.8085 | 144.9291 | 1 | CitiPower | Report | 7941 | 0.021211 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
Site made safe. Fault crew attended and confirmed, copper theft of HV and LV copper earth cable from underground pit to substation pole BIZANA-FONTEIN. Earth cable replaced. | 21 FONTEIN STREET, WEST FOOTSCRAY VIC 3012 | Pole no. A052733 | Copper theft | [5 empty] | 2 | Copper theft from substation pole BIZANA-FONTEIN to underground pit. | Copper;Pole mounted;Earth/earthing | 0 | 0 | 0 |  | FW09 | Theft of HV and LV copper earth cable. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/08/2017 13:51 |  |  | 6437 | Residential |  | 20170824JEM_01 | Infrastructure (network-based) | -37.801 | 144.8652 | 1 | Jemena | Report | 8168 | 0.025475 | 22kV AC | Essendon Airport | 3012 | West Footscray | Other
On arrival crew isolated supply and replaced EDO unit | 30 SHARP STREET, YARRAWONGA VIC 3730 | 30121235 |  |  |  | Fuse failed to eject |  |  |  | Customer reported pole on vacant block next door on fire. Upon arrival crew found that there was no evidence of fire and CFA had not attended. The EDO was still in service but had failed to drop out. There was slight damage to the fuse holder. There were no reported injuries or third party damage. | EDO fuse | 2 | 2 | 2 |  | CME014 | EDO hang up | Hung-up fuse only;Singeing or local charring/blackening only | 42863.5917 |  |  | 6444 | Public space |  | 20170825PWA_03 | Infrastructure (network-based) | -36.0143 | 146.0005 | 1 | Powercor | Report | 7972 | 0.02233 | 22kV AC | Wangaratta Aero | 3730 | Yarrawonga | Fuse
Crew isolated supply and removed the service for the adjoining property, the service hook and mains box was mounted on the shared facade with building being demolished. | 98 BELL STREET, HEIDELBERG HEIGHTS VIC 3081 |  | Unauthorised work | [5 empty] | 2 | Builder Arthur Lazaris demolishing premise at # 98 Bell St has removed a mains box & hook supplying 100 Bell St. and dropped the service onto a steel roof belonging to the premise next door, 100 Bell St. | Service conductor | 2 | 2 | 2 |  |  | Builder engaged to demolish the building engaged in conversation with the neighbouring property 100 Bell St, to move his POA off the facade of 98 Bell st which was to be demolished. The neighbour refused to pay for the works as he believed the builder should be responsible for the costs. the builder then removed the 'live' service and dropped it on the steel verandah. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 28/08/2017 11:10 |  |  | 6446 |  |  | 20170828JEM_02 | Infrastructure (network-based) | -37.7535 | 145.0528 | 1 | Jemena | Report | 8286 | 0.019293 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg Heights | Other
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. The crew confirmed that a tree had fallen onto a conductor and an approximately1/2 an acre grass fire in the vicinity which CFA had extinguished. The local DAO was informed and an AusNet Services LEI was called for a possible HVI. LIS 912282. There appeared no conductor or network damage apart from replacing HV, Boric Acid spur fuse on GB881097 and a successful reclose on GB1290 ACR with supply being restored. | 2 JUNCTION ROAD, HEATHCOTE JUNCTION VIC 3758 | 912281 |  | Fallen |  |  |  | Phase to earth | 1 | IMS 226575. An approximately 14 metre tall gum tree that appeared partly rotted located on private property of no. 37 Glenburnie Avenue and approximately 7.5 metres away from the nearest HV outer phase conductor is suspected to have broken in windy conditions at approximately 2.5 metres above ground level and while falling the tree contacted a 22 kV conductor. This caused the 22kV conductor to contact and clash with an open wire 230 Volt LV conductor with fault current from the tree and 22kV/LV conductor clashing causing sparks and small particles of hot molten metal to ignite and causing an approximately 2,000 sq. metre grass fire. The fire was extinguished by the attending CFA. There was some visual private property vegetation and minor paddock fencing damage to property no. 37 Glenburnie Avenue and possible premise HV into LV injection damage. No injection damage occurred. | Conductor (bare) | 0 | 0 | 0 |  | klo14 | Vegetation: Trees Incident | Grassfire | 22/02/2017 14:15 | 1 | Medium: 1000 sq.m - 10 ha | 5655 | Agricultural |  | 20170222SPN_02 | Infrastructure (network-based) | -37.3772 | 145.0349 | 1 | AusNet Services Distribution | Report | 6927 | 0.036627 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3758 | Heathcote Junction | Trees
On arrival crew carried out repairs | WALLACEDALE NORTH-HAMILTON ROAD, BRANXHOLME VIC 3302 | 32127314 |  | Alive;Fallen |  |  |  |  | 1 | CFA reported wire down and a fire at the incident location. On arrival the crew found that a tree (from outside the clearance space) had fallen across an adjacent SWER conductor, causing the conductor fall to the ground resulting in a ground fire on private property. Protection operated. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | HTN002 | Vegetation: Trees Incident | Grassfire | 22/02/2017 13:04 | 1 | Medium: 1000 sq.m - 10 ha | 5662 |  |  | 20170223PWA_03 | Infrastructure (network-based) | -37.8487 | 141.8367 | 1 | Powercor | Report | 6937 | 0.015169 | 12.7kV AC (SWER) | Hamilton Airport | 3302 | Branxholme | Trees
crew attended and removed POEL cable from substation pole on property | 34 GLENMORE ROAD, PARWAN VIC 3340 | 32163898 |  | Fallen;Property owner/customer |  |  |  |  | 2 | CFA rang to request Powercor assistance with attending to a grass fire. On arrival the crew observed a broken neutral screened cable in the vicinity of a cut tree at a derelict premise. There was evidence of a grass fire of 30 by 20 metres. | Private overhead electric line (POEL) | 0 | 0 | 0 |  | BMH006 | Vegetation: Trees Incident | Grassfire | 24/02/2017 16:53 | 0 | Small: 10 - 1000 sq.m | 5664 | Agricultural |  | 20170223PWA_04 | Infrastructure (network-based) | -37.7507 | 144.4405 | 1 | Powercor | Report | 12438 | 0.023278 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Parwan | Trees
CEOT dispatched a fault crew. Opened HV Switch BW16586 to make safe. Construction crew dispatched to carry out repairs. When the local DAO was on site, the Downer construction was in process of making repairs for supply restoration. | 1275 POUND ROAD, CLYDE NORTH VIC 3978 | 507786 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 2 | IMS 226595. An excavator while working for new estate works at approximately 12:25pm on 23/02/2017 made contact with live 22kV open wire three phase 3/12 steel conductors between poles #507786 and 507786 resulting in one of the conductors breaking and falling to the ground. The fault current from the 22kV contact causing some flashover burn marks on the excavator boom and scorching some ground vegetation around .3 sq. metre in area and causing out of balance sag for the other two overhead conductors. There were no reported injuries and Sr. Constable Simpson & Owen Holland from the Operation Response Unit (CBD) & Cranbourne CFA were at in attendance at the site. The excavator site officer / owner contact is Marian Pasoski, mobile 0411 412 144, from ZP Services. | Conductor (bare) | 0 | 0 | 0 |  | cln23 | Excavator contacted overhead HV conductor when leaving a work site. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/02/2017 11:20 |  |  | 5665 |  |  | 20170223SPN_04 | Infrastructure (network-based) | -38.0896 | 145.3498 | 1 | AusNet Services Distribution | Report | 12350 | 0.020446 | 22kV AC | Moorabbin Airport | 3978 | Clyde North | Vehicle
The ground type substation perimeter fence was temporary repaired and repairs to the damaged infrastructure will be completed on 24/02/2017. A substation crew attended and completed the following repairs: - repaired two hinges on the HV switch cabinet - reinstated hanging customer cables onto the cable tray - repaired substation fence following temporary repair yesterday - advised the occupier their pillar outside the substation had a damaged lid and the hasp and staple are broken away and require repairs or replacement. | 9-11 KEVLAR CLOSE, BRAESIDE VIC 3195 |  | Unauthorised access;Copper theft | [5 empty] | 2 | An ex United Energy employee contacted Wayne Kelly and advised that a ground type substation had been broken into in an attempted copper theft. Unknown persons broke into "Mills N47-Woodland" ground type substation after cutting the fence in an attempted copper theft. No copper was stolen but it appeared they may have tried to remove the HV elbows from the live 22kV transformer. No customers were off supply and there was no evidence that electric shocks were received. | Outdoor;No failed asset | 0 | 0 | 0 |  | MC 05 | Attempted copper theft by unknown persons. | Damage to network assets | 23/02/2017 14:00 |  |  | 5672 | Industrial |  | 20170224UTD_06 | Infrastructure (network-based) | -37.9937 | 145.1169 | 1 | United Energy Distribution | Report | 12534 | 0.0098067 | 22kV AC | Moorabbin Airport | 3195 | Braeside | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. Supply was restored to approximately 10 customers upon completion. | 14 PROSSORS LANE, RED HILL VIC 3937 | 1308108 |  |  |  | Fatigue;Electrical breakdown |  |  | 1 | Customers in Prossors Lane, Red Hill advised of a loss of supply. A HV fuse operated at RB7556 located in Prossors Lane after HVABC was reported to be on fire at pole number LIS 1308108 located outside 14 Prossors Lane. The HVABC at this location is old NMS HVABC and is scheduled to be replaced by Downer next month. It was later confirmed there was no fire start in this instance. | Conductor (ABC);Aluminium | 0 | 0 | 0 |  | DMA 15 | HVABC faulted. | Loss of supply | 23/02/2017 17:36 |  |  | 5673 | Agricultural |  | 20170224UTD_07 | Infrastructure (network-based) | -38.3735 | 145.0178 | 1 | United Energy Distribution | Report | 8595 | 0.032523 | 22kV AC | Moorabbin Airport | 3937 | Red Hill | OH Cable
On arrival crew carried out repairs | 293 KOOLOMURT ROAD, TARRAYOUKYAN VIC 3315 | 32100172 | Working too close to overhead lines | [5 empty] | 1 | An excavator contacted and broke a high voltage overhead conductor at the incident location. On arrival the crew found that an excavator being loaded after being used to remove a tree stump had hit a conductor on a 22kV single phase line. The damage caused to the steel conductor required approximately 3m of new conductor to be sleeved in to complete repairs. Protection operated. There was no fire, reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CHM011 | Excavator being loaded beneath overhead conductors | Loss of supply;No Go Zone (contact) | 25/02/2017 9:47 |  |  | 5675 | Agricultural |  | 20170227PWA_01 | Infrastructure (network-based) | -37.2794 | 141.5086 | 1 | Powercor | Report | 6953 | 0.02775 | 22kV AC | Hamilton Airport | 3315 | Tarrayoukyan | Vehicle
A faults crew attended and found the krone box supplying the west circuit of "Wellington P42 - Stud" substation pole (LIS No. 0618004) is burnt out (caught fire) that has affected the Eastlink supply. The faults crew replaced a metre of 95mm XLPE cable and installed 3 x 125amp DIN fuses and restored supply at completion. | WELLINGTON ROAD, ROWVILLE VIC 3178 | 618004 |  |  |  | Overheated connection |  |  | 2 | Eastlink REC advised of a part supply failure as the white phase is missing - CT metering. A REC advised that Eastlink have a part supply failure on their equipment at the Wellington Road entrance to Eastlink outbound. | Conductor (ABC);Connection box | 0 | 0 | 0 |  |  | The cause was a probable loose connection. | Pole-top fire;Loss of supply | 25/02/2017 9:30 | 1 | Negligible: no ground fire | 5678 | Roadway |  | 20170227UTD_01 | Infrastructure (network-based) | -37.9259 | 145.2148 | 1 | United Energy Distribution | Report | 7078 | 0.033317 | Low voltage AC (<1kV) | Moorabbin Airport | 3178 | Rowville | Connection
The faults crew extinguished the fire at the base of the pole that wasn't caused by United Energy assets. The crew spoke to the customer who notified United Energy of the fault and she didn't see anyone in the area at the time. | 25 HYGEIA STREET, RYE VIC 3941 | 1300972 | Vandalism | [5 empty] | 2 | Caller reports fire at the base of the pole located on the corner of Hygeia and Bimble Streets, Rye. Emergency services are not on site and the fire appears to have been deliberately lit. REFER ALSO TO 20160523UTD_02 An arson attempt was made at pole No. LIS 1300972 located outside 25 Hygeia Street, Rye after unknown persons attempted to light a fire at the base of the HV/LV intermediate pole that resulted in superficial damage to the timber pole. | Pole (wood) | 0 | 0 | 0 |  | STO 23 | Unknown persons attempted to light a fire at the base of the HV/LV intermediate pole. | Singeing or local charring/blackening only | 26/02/2017 11:30 |  |  | 5680 | Roadway |  | 20170227UTD_02 | Infrastructure (network-based) | -38.3738 | 144.8305 | 1 | United Energy Distribution | Report | 6958 | 0.0091343 | 22kV AC | Moorabbin Airport | 3941 | Rye | Other
On arrival crew isolated supply and commenced repairs. | 110 FLACKS LANE, BALLAN VIC 3342 | 30104525 |  | Animal |  |  |  |  | 2 | CFA reported a pole fire at the above address. A crew attended and found that a possum had bridged out btn the top of an EDO fuse unit and the steel Xarm on the pole. The resulting current flow caused the pole to burn at the Xarm king bolt. The crew removed the possum and isolated the EDO fuses. The CFA were in attendance and extinguished the pole fire. There were no shocks, injuries, ground fire start or third party damage. | Pole (wood);EDO fuse | 2 | 2 | 2 |  | BAN011 | Animal Incident | Pole-top fire | 16/02/2017 19:59 | 1 | Negligible: no ground fire | 5684 | Roadway |  | 20170228PWA_01 | Infrastructure (network-based) | -37.5757 | 144.1848 | 1 | Powercor | Report | 6962 | 0.029766 | 22kV AC | Ballarat Aerodrome | 3342 | Ballan | Trees
On arrival crew replaced fuses | 420 COOMBES ROAD, FRESHWATER CREEK VIC 3217 | 32084185 |  |  |  | Candled fuse |  |  | 2 | Mike from CFA reported that a small grassfire had started around the base of a pole. He stated that a fuse had dropped down and started the fire. The CFA were onsite at the time of the report. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire at incident location. There were no injuries reported. | Powder filled | 2 | 2 | 2 |  | WPD014 | moisture ingress | Grassfire | 42769.0264 | 1 | Small: 10 - 1000 sq.m | 5707 | Roadway |  | 20170302PWA_06 | Infrastructure (network-based) | -38.3093 | 144.2721 | 1 | Powercor | Report | 6993 | 0.017613 | 22kV AC | Avalon Airport | 3217 | Freshwater Creek | Fuse
Service Crew cut away the damaged area of the conductor and re-terminated into a new Pit Connector. Crew found no other damage. Crew fitted an extension to the pit to raise the height to the revised level | 39 JEDDA STREET, BELL POST HILL VIC 3215 | 32077785 | Unauthorised work;Unauthorised access | [5 empty] | 2 | concreter reported he received a shock from a service pit. On arrival the LEI and crew identified that a LV conductor in the pit had been damaged when the concreter had attempted to fit another section of service pit to raise the surface level of the pit. There was not fire or third party damages reported. | Services cable;Services pit | 0 | 0 | 0 |  | GL015 | Interference | Minor shock;Damage to network assets | 42562.6285 |  |  | 5711 | Roadway |  | 20170306PWA_02 | Infrastructure (network-based) | -38.0989 | 144.3297 | 1 | Powercor | Report | 12439 | 0.016668 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | Other
On arrival crew carried out repairs | 217 DARLINGTON-CAMPERDOWN ROAD, GNOTUK VIC 3260 | 30272856 | Working too close to overhead lines | [5 empty] | 1 | A customer reported a tipper had struck and brought down 2 wires at the incident location. On arrival the crew found that a struck the 22kV conductors, resulting in them breaking and falling to ground. Protection operated. There was no ground fire, reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CDN006 | Tipper operating near overhead conductor | Loss of supply;No Go Zone (contact) | 42797.3931 |  |  | 5712 |  |  | 20170306PWA_03 | Infrastructure (network-based) | -38.1893 | 143.1107 | 1 | Powercor | Report | 7001 | 0.024936 | 22kV AC | Warrnambool Airport Ndb | 3260 | Gnotuk | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. Local DAO notified. CFA on site. The crew attended to isolate HV fuses of the transformer to make safe. LV Krone box was replaced with a new Krone FSD. Overhead LV was re-terminated and supply restored to customers. | LAGOONA, 204 NAUGHTIN ROAD, BOORHAMAN VIC 3678 | 5103424 |  |  |  | Overheated connection |  |  | 2 | IMS 226737. A small grass fire within area surrounding substation pole (LIS 5103424). LV fuse box (Krone Box) found burning on pole (LIS 5103424). Melted plastic (from the Krone Box) was found at the base of the substation pole. | Connection box | 0 | 0 | 0 |  | wn3 | LV FSD failed. | Grassfire | 42797.4792 | 1 | Small: 10 - 1000 sq.m | 5714 | Agricultural |  | 20170306SPN_01 | Infrastructure (network-based) | -36.2373 | 146.2735 | 1 | AusNet Services Distribution | Report | 7956 | 0.035512 | Low voltage AC (<1kV) | Wangaratta Aero | 3678 | Boorhaman | Fuse
On arrival crew carried out repairs | 13 MONTGOMERY ROAD, YARROWEYAH VIC 3644 | 33082438 |  | Lightning |  |  |  |  | 2 | Report from CFA pole fire at the corner of Kokoda and Montgomery Roads YARROWEYAH. Crew attended and found road verge on fire and into landowners property, Crew on investigation believe a lightning strike on concrete pole # 171 Yarroweyah Line was the cause. As a result of the fire poles 170 and 169 of the Yarroweyah Line required replacement. Some property damage, loss of fencing and hay bales, 2 Powercor Poles requiring replacement fire area covered 600 Metres by 30 Metres approximately. No injuries reported | Pole (concrete) | 2 | 2 | 2 |  | NKA005 | lightning strike in vicinity of pole | Grassfire | 43072.666 | 0 | Medium: 1000 sq.m - 10 ha | 5758 | Roadway |  | 20170314PWA_05 | Infrastructure (network-based) | -35.9673 | 145.5595 | 1 | Powercor | Report | 7064 | 0.016219 | 22kV AC | Shepparton Airport | 3644 | Yarroweyah | Lightning
On arrival crew carried out repairs | 116 DARWIN ROAD, ROBINVALE VIC 3549 | 33064684 |  |  |  | Overheated connection |  |  | 1 | Report from REC that there was a cable down on the road verge and no supply in the area, cable reported to be broken between pole 11 and pole 12 at the incident location. Crew attended and found HV 3/2.75 Steel Cable had parted at cable sleeve . A burn area on the ground of 3 Metres by 3 Metres was evident, No property damage and No injuries reported | Conductor (bare) | 2 | 2 | 2 |  | RVL004 | connection failure at splice | Grassfire | 43011.7896 | 1 | Localised: less than 10 sq.m | 5759 | Agricultural |  | 20170314PWA_06 | Infrastructure (network-based) | -34.6136 | 142.7503 | 1 | Powercor | Report | 7066 | 0.023936 | 22kV AC | Mildura Airport | 3549 | Robinvale | Conductor
Crew attended site. Damaged conductor, cross arms and insulators repaired. | 362 PEACOCKS ROAD, BUANGOR VIC 3375 | 30323366 | Working too close to overhead lines | [5 empty] | 1 | Vicfire and Police reported an excavator has contacted HV O/H line at the incident location. Upon arrival, the attending crew found that the HV conductors had been contacted by the excavator and damage was caused to network assets. No injuries, fire or damage to the third party assets found. The protection operated. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | BAS011 | Interference | Loss of supply;Damage to network assets | 14/03/2017 11:21 |  |  | 5766 | Agricultural |  | 20170316PWA_01 | Infrastructure (network-based) | -37.3411 | 143.1874 | 1 | Powercor | Report | 7080 | 0.0005 | 22kV AC | Ballarat Aerodrome | 3375 | Buangor | Vehicle
CEOT dispatched a fault crew and a AusNet Services' LEI to make safe, investigate and repair. Supply isolated and made safe. Downer fault crew replaced the HV crossarm on pole 1205187. LEIs disconnected affected properties prior to LV supply being restored on circuit. LEIs then reconnected affected properties. Downer replaced damaged meters where required. LEIs issued Advice to Customer forms to those customers with damage to electrical installations and appliances. | 9 COLEMAN STREET, HEATHMONT VIC 3135 | 1205187 |  | Fallen |  | Fatigue |  | Phase to phase | 1 | IMS 226918. Initial reports of a switchboard fire, later it was discovered a tree branch over LV mains and then reported a broken HV crossarm. Final report: HV crossarm on pole 1205187 broke resulting in HV conductor contacting the LV conductor below. Feeder RWT22 initially tripped and then had a reclose. This caused a HV Injection to occur. | Crossarm (wood);Switchboard;Customer installation | 0 | 0 | 0 |  | rwt22 | Broken HV crossarm. | HV injection | 15/03/2017 15:05 |  |  | 5764 | Residential |  | 20170316SPN_01 | Infrastructure (network-based) | -37.8245 | 145.2482 | 1 | AusNet Services Distribution | Report | 7075 | 0.032647 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3135 | Heathmont | Trees
A faults crew attended and replaced the damaged white phase LV bridge with a copper to aluminium bridge fitted to a 'D' clamp. | STATION STREET, CHELSEA VIC 3196 | 8817371 |  |  |  | Electrical breakdown;Overheated connection |  |  | 2 | Constable Matt Whinchello advised that a passerby saw the powerlines arcing near the bus stop at the Chelsea Railway Station and there was burn marks on the passersby car. During warm conditions, the white phase LV ampact connection had been burning out on pole number LIS 8817371 which is a tee-off pole on the corner of Station and Blantyre Streets. Hot molten aluminium fell from the failed connection onto vehicles parked underneath the pole. The cause of the connection failure was a probable loose or overheated connection. | Dropper/bridge | 0 | 0 | 0 |  |  | The cause of the connection failure was a probable loose or overheated connection. | Vehicle | 42981.5625 | 1 | Negligible: no ground fire | 5763 | Roadway |  | 20170316UTD_01 | Infrastructure (network-based) | -38.0525 | 145.1165 | 1 | United Energy Distribution | Report | 7072 | 0.0045162 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | AF Other
CEOT dispatched a fault crew to isolate, make safe and repair. The crew attended and isolated supply to a sparking HV isolator. Observation by fault crew that isolator which had been sparking appeared not to be aligned straight and that other isolators were straight. Fire was self extinguishing. | 69 NAR NAR GOON ROAD, NAR NAR GOON VIC 3812 | 517611 |  |  |  | Mechanical breakdown |  |  | 2 | IMS 226971. Report of sparks from pole. Burnt out Line side HV isolator on ACR has caused a small grass fire at base of pole. Closed BW1232B (Bypass Switch) and Opened In's and Out's on ACR. HV Blade Isolator needs to be changed at later date. G&B crew required. | Disconnector/isolator | 0 | 0 | 0 |  | PHM14 | Burnt out line side of a HV blade isolator mounted on a steel crossarm on a concrete pole resulting in hot particles falling to the ground starting a very small grass fire at base of the pole. Mechanical failure of switch â€“ the isolator had been sparking and appeared not to be aligned straight. | Grassfire | 18/03/2017 1:20 | 1 | Localised: less than 10 sq.m | 5776 | Industrial |  | 20170319SPN_01 | Infrastructure (network-based) | -38.0701 | 145.5722 | 1 | AusNet Services Distribution | Report | 11254 | 0.029887 | 22kV AC | Moorabbin Airport | 3812 | Nar Nar Goon | AF Other
Site isolated and made safe. Access permit was issued and repairs completed by Jemena work party, which re-made and cleaned connection to bushing, then installed new bushing cover. All other connections were checked and considered okay. | 131 SOMERTON ROAD, CAMPBELLFIELD VIC 3061 |  |  |  |  | Defective component;Electrical breakdown;Overheated connection |  |  | 1 | MFB attended a reported fire at the rear of a factory at Somerton-Dennis #1 substation. The road side phase HV bushing was hot and bushing cover has melted. There was no evidence of fire or burning at ground level. | Transformer | 0 | 0 | 0 |  |  | Bushing hot and cover melted; appeared to be caused by loose connection | Melting or smoking only | 20/03/2017 9:10 |  |  | 5779 | Industrial |  | 20170320JEM_01 | Infrastructure (network-based) | -37.6419 | 144.9371 | 1 | Jemena | Report | 7100 | 0.0075035 | 22kV AC | Essendon Airport | 3061 | Campbellfield | AF Other
On arrival crew replaced Surge diverter | 89 MARQUANDS ROAD, TRUGANINA VIC 3029 | 30238362 |  |  |  | Electrical breakdown |  |  | 2 | A Customer reported a loud bang in his street and what looked like a burnt insulator at the base of a pole. Powercor fault crew leader was directed to check the incident as part of a line patrol for a feeder outage on a separate feeder. The Powercor crew attended the site and noted a damaged surge diverter and a small burnt patch on the nature strip beneath a HV cable head at the incident location. The burnt patch measured approx. 400mm x 400mm. There was no reported injuries or third party property damage. | Surge diverter | 2 | 2 | 2 |  | LV002 | Surge diverter ruptured at time of adjacent feeder auto reclose | Grassfire | 27/02/2017 20:12 | 1 | Localised: less than 10 sq.m | 5780 | Roadway |  | 20170320PWA_02 | Infrastructure (network-based) | -37.845 | 144.7276 | 1 | Powercor | Report | 7101 | 0.0078287 | 22kV AC | Laverton Raaf | 3029 | Truganina | AF Other
On arrival crew carried out repairs | 601 NULLAWIL LALBERT ROAD, KALPIENUNG VIC 3529 | 33015899 |  |  |  | Overheated connection |  |  | 2 | VicFire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had caught on fire, molten plastic fell to the ground but no ground fire resulted. Fire self extinguished prior to CFA arriving. There were no reported injuries, no third party damage, no protection operated. | Connection box | 2 | 2 | 2 |  | CTN003 | Box totally destroyed unable to determine cause | Pole-top fire | 28/02/2017 21:00 | 1 | Negligible: no ground fire | 5781 | Agricultural |  | 20170320PWA_03 | Infrastructure (network-based) | -35.8091 | 143.2528 | 1 | Powercor | Report | 7102 | 0.039381 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3529 | Kalpienung | Pole
The crew made the site safe, and replaced the pole. | 211 THWAITES ROAD, WINSLOW VIC 3281 | 33099951 |  |  |  | Leakage |  |  | 2 | The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt through under the king bolt, attached to the crossarm for the HV fuses. The pole was severely damaged and almost burnt through. There was no ground fire, reported injuries or third party property damage. | Dropper/bridge | 2 | 2 | 2 |  | KRT012 | Excessive leakage current | Pole-top fire | 42858.441 | 1 | Negligible: no ground fire | 5782 | Roadway |  | 20170320PWA_04 | Infrastructure (network-based) | -38.2556 | 142.4384 | 1 | Powercor | Report | 7103 | 0.041104 | 22kV AC | Warrnambool Airport Ndb | 3281 | Winslow | Pole
On arrival crew isolated supply for REC | 27 FERGUSON ROAD, ARARAT VIC 3377 | 32115273 |  |  |  | Fault on customer installation |  |  | 2 | Customer called to advise 3 black boxes in metering cabinet had melted at the site location. A crew attended and found the white phase fuse loose and had overheated. Crew isolated supply to the cabinet and an REC attended and replace the fuse and holder. Supply was then restored to the cabinet. There were no shocks, injuries or third party damage. | Customer installation | 2 | 2 | 2 |  | ART034 | Loose connection in customers instalation | Loss of supply | 42889.3799 |  |  | 5783 | Commercial |  | 20170320PWA_05 | Infrastructure (network-based) | -37.2644 | 142.918 | 1 | Powercor | Report | 7106 | 0.021532 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | AF Other
On arrival crew carried out repairs | 208 ARCHER STREET, SHEPPARTON VIC 3630 | 33088586 | Vehicle | [5 empty] | 2 | A passer-by reported a truck has taken down a wire at the incident location. Upon arrival the crew found that the service had been brought down by the truck. There were no injuries or fire or third party property damage. | Service conductor | 2 | 2 | 2 |  | STN012 | Truck struck conductor | Loss of supply;Damage to network assets | 27/02/2017 13:47 |  |  | 5792 | Roadway |  | 20170321PWA_08 | Infrastructure (network-based) | -36.3937 | 145.4104 | 1 | Powercor | Report | 7115 | 0.036119 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
On arrival CitiPower faults crew replaced the pole and provided a defect notice to the affected customers No 26, 28 and 30 McLean Street. | 28 MCLEAN STREET, BRUNSWICK WEST VIC 3055 | 30351065 | Vehicle | [5 empty] | 2 | The MFB called CitiPower to report that a pole had fallen on a house. CitiPower faults crew attended 28 McLean St, Brunswick to find and LV service pole had snapped after a truck had made contact with the attached Optus cable over the road. As a result pole LIS-52373 snapped and made contact with a parked car. The LV service cable and Optus cable was torn from the fascia of No.28 and made further damage to the faÃ§ade of the front of the building. The truck driver did not stop but was later stopped at another location by Victoria Police. Victoria Police have been contact to gain drivers details. There was no fire, shocks or reported injuries There was third party damage to a parked vehicle and house poa's. | Service conductor;Pole (wood) | 2 | 2 | 2 |  | NS010 | Truck striking optus cable and services | Loss of supply;Damage to network assets | 42738.2278 |  |  | 5793 | Roadway |  | 20170321PWA_09 | Infrastructure (network-based) | -37.7545 | 144.9384 | 1 | CitiPower | Report | 17443 | 0.029502 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Vehicle
On arrival crew carried out repairs | 21 BOLTE DRIVE, TRUGANINA VIC 3029 | 30335938 | Working too close to underground cables | [5 empty] | 2 | A contractor advised an excavator has dug up an UG cable at the incident location. Upon arrival, the Powercor crew noticed that a part of lighting LV UG cable, conduit between two lighting poles had been damaged. There was no fire or reported injuries. | Cable | 2 | 2 | 2 |  | LV002 | Roadside earthworks | Damage to network assets | 42919.434 |  |  | 5806 |  |  | 20170322PWA_09 | Infrastructure (network-based) | -37.821 | 144.7072 | 1 | Powercor | Report | 8048 | 0.015508 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Dug up
The crew made repairs and supply was restored. | 10 WALNUT ROAD, BALWYN NORTH VIC 3104 | 30186214 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that he has exposed a conduit at the incident location. On arrival the fault crew found that the contractor whilst working to install a gas main in the footpath reserve had contacted and damaged a low voltage underground main on the supply side of the pit to 10 Walnut Road. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | WD022 | Contractor installing gas main | Loss of supply;No Go Zone (contact) | 15/03/2017 8:10 |  |  | 5841 | Roadway |  | 20170329PWA_06 | Infrastructure (network-based) | -37.7918 | 145.0898 | 1 | CitiPower | Report | 7177 | 0.02652 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
On arrival crew completed repairs | 1 HOLBROOK CRESCENT, BRUNSWICK WEST VIC 3055 | 30155519 | Copper theft | [5 empty] | 2 | Crew reported that wires have been tampered with at the incident location. On arrival the fault crew found that the low voltage earth had been stolen from the substation (Wattle Valley-Hooper AS) at the incident location. There was no ground fire and no injury as a result of this incident. | Pole mounted | 2 | 2 | 2 |  | WB013 | copper theft | Damage to network assets | 16/03/2017 9:30 |  |  | 5842 | Roadway |  | 20170329PWA_07 | Infrastructure (network-based) | -37.7692 | 144.9394 | 1 | CitiPower | Report | 7178 | 0.032543 | Earthing cable | Essendon Airport | 3055 | Brunswick West | Other
On arrival crew carried out repairs | 40-48 PARK STREET, SOUTH MELBOURNE VIC 3205 | CP0155783 | Vandalism;Copper theft | [5 empty] | 1 | A customer reported an outage at the incident location. Upon arrival, the Citipower fault crew found that the indoor substation entrance door had been damaged. A bolt cutter was found attached to the 11kv dropper cable on the transformer, there had been an attempt to cut the HV cable. The protection operated. There was no evidence of injuries or fire found. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | SO018 | Attempted copper theft | Loss of supply;Damage to network assets | 30/03/2017 8:21 |  |  | 5856 | Commercial |  | 20170330PWA_01 | Infrastructure (network-based) | -37.8324 | 144.9693 | 1 | CitiPower | Report | 12117 | 0.020516 | 11kV AC | Essendon Airport | 3205 | South Melbourne | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | BENNET STREET, DANDENONG VIC 3175 |  |  | Wind |  | HV injection |  |  | 1 | At 1331hrs on 27/03/2017, 22kV ACR DN8237 located in Railway Parade, reclosed to lockout affecting 598 customers. During strong winds and rain, a large gum tree located at the entrance to the Dandenong Showgrounds broke and fell over the HV and LV conductors bringing them down to the ground. Electrical infrastructure was damaged and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Greaves 1- Bennet" and "Greaves 2- Bennet"" substations. The LEI confirmed a high voltage injection occurred (KEY 1701) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | NP 36 | Vegetation: Trees Incident | HV injection;Loss of supply | 28/03/2017 13:31 |  |  | 5854 | Roadway |  | 20170330UTD_01 | Infrastructure (network-based) | -37.9851 | 145.1999 | 1 | United Energy Distribution | Report | 7192 | 0.02191 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the crossarm replacement and conductor repairs were completed under Access Authority conditions prior to supply being restored. | STEPHENSONS ROAD, MOUNT WAVERLEY VIC 3149 | 603284 |  | Wind |  | Overheated connection |  |  | 1 | At 1538hrs on 27/03/2017, 22kV feeder EB 22 circuit breaker reclosed to lockout affecting 1336 customers. Reported property damage. Police have advised as part of the EB22 feeder fault, an overhead conductor fell on a car In Stephensons Road, Mount Waverley opposite Mount Waverley railway station. Car occupants were inside the car and then drove off. The police provided details of car to the ZNX Field Operator. During strong winds and rain, the HV blue phase aluminium ampact bail connection failed at pole No. LIS located on the corner of Stephenson Road and Miller Crescent (tee-off to Mount Waverley Vic Rail) that caused the overhead conductor to make contact with a passing vehicle that drove off. The police officer from the Oakleigh police station obtained details and provided them to the First Responder. The event was reported to ESV with reference number 7118378 provided. It was unknown the amount of damage that was sustained to the vehicle. | Conductor (bare);Aluminium;Dropper/bridge | 0 | 0 | 0 |  | EB 22 | Connection failure. | Loss of supply | 27/03/2017 13:38 |  |  | 5855 | Roadway |  | 20170330UTD_02 | Infrastructure (network-based) | -37.8751 | 145.129 | 1 | United Energy Distribution | Report | 7193 | 0.030082 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Other
On arrival crew carried out repairs | 3493 HATTAH-ROBINVALE ROAD, LIPAROO VIC 3549 | 32139293 |  | Precipitation |  | Leakage |  |  | 2 | CFA reported pole fire at 3493 Hattah-Robinvale Rd Liparoo. On arrival, crew found cross-arm had fire on the footpath side of it. No injuries, no ground fire, no third party damage. | Pole (wood) | 2 | 2 | 2 |  | WMN013 | Excessive leakage current | Pole-top fire;Damage to network assets | 22/03/2017 0:50 | 1 | Negligible: no ground fire | 5871 | Roadway |  | 20170403PWA_03 | Infrastructure (network-based) | -34.7863 | 142.626 | 1 | Powercor | Report | 7217 | 0.0081852 | 22kV AC | Mildura Airport | 3493 | Liparoo | Crossarm
Requested operator of EWP to return to ground level. Advised operator that a Qualified Spotter must be used and that 3000mm clearance to powerlines to be maintained. | 3 HOWARD STREET, WEST MELBOURNE VIC 3003 | 30182601 | Working too close to overhead lines | [5 empty] | 2 | Citipower worker attended site to assess scaffolding requirements and identified large mobile work platform working in vicinity of bare ow voltage overhead conductor. | Conductor (bare) | 0 | 0 | 0 |  | BQ047 | Potential Breach of No Go Zone | No Go Zone (no contact) | 42798.5528 |  |  | 5874 | Construction |  | 20170403PWA_04 | Infrastructure (network-based) | -37.807 | 144.9532 | 1 | CitiPower | Report | 8023 | 0.023024 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
Supply was disconnected and crew replaced two-phase service. Dummy fuse inserted at point of attachment. | 150 DALLAS DRIVE, DALLAS VIC 3047 |  |  |  |  | Defective component |  |  | 2 | Neutral screen service blew at roller clamp termination and came down, then set grass alight. | Neutral screen;Connector/termination | 0 | 0 | 0 |  |  | This fire incident was the result of sparks emitted when a neutral screen service roller clamp termination failed | Grassfire | 42738.4792 | 1 | Localised: less than 10 sq.m | 5890 | Residential |  | 20170406JEM_01 | Infrastructure (customer connection) | -37.6699 | 144.9379 | 1 | Jemena | Report | 7242 | 0.01683 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Dallas | Connection
Site made safe and temporary repairs made to neutral conductor Neutral conductor subsequently repaired correctly and conductors re-sagged | 304 LOWER HEIDELBERG ROAD, IVANHOE EAST VIC 3079 |  | Vehicle |  |  | Conductor clashing |  |  | 1 | Truck hit Optus cable at the corner of Lower Heidelberg Rd and Bourke Rod North, causing clashing between HV conductors, which in turned resulted in HV bridges to burn off and a minor grass fire. No photo is available for this fire start incident. | Conductor (bare);Communication cable/equipment;Dropper/bridge | 0 | 0 | 0 |  | HB24 | Third party truck impact with Optus cable resulted in HV conductors clashing and HV bridges burning off. | Grassfire | 15/02/2016 11:50 | 1 | Localised: less than 10 sq.m | 5892 | Residential |  | 20170406JEM_02 | Infrastructure (network-based) | -37.7705 | 145.0631 | 1 | Jemena | Report | 8424 | 0.037597 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe East | Vehicle
Conductor was currently hanging safely. HV tie and HV crossarm have been replaced under access permit by Jemena faults crew. | 96 NORTH STREET, HADFIELD VIC 3046 | Pole no. A045338 |  |  |  | Defective component |  |  | 2 | Broken HV tie caused the HV conductor to come off and contact the street light. The HV conductor is hanging in the air above the street light on the pole. The molten parts of the street light also started a small grass fire at the base of the pole. | Insulator tie wires/connections;Public lighting | 0 | 0 | 0 |  | PV23 | The road side phase HV conductor has a broken HV tie. | Grassfire | 26/10/2016 13:35 | 1 | Localised: less than 10 sq.m | 5895 | Residential |  | 20170406JEM_03 | Infrastructure (network-based) | -37.7045 | 144.9401 | 1 | Jemena | Report | 12711 | 0.039359 | 11kV AC | Essendon Airport | 3046 | Hadfield | AF Other
Jemena's public lighting contractor has attended site to repair street light pole and replaced street light. | 339 GILBERT ROAD, PRESTON VIC 3072 | Pole no. A015139 |  |  |  | Defective component |  |  | 2 | Street light failed, disconnected and caught fire. Street light type: HP sodium (150W), mount type: bracket No photo is available for this fire start incident. | Public lighting;Pole (steel) | 0 | 0 | 0 |  | CS03 | Street light failure | Pole-top fire | 21/04/2016 2:37 | 1 | Negligible: no ground fire | 5898 | Residential |  | 20170406JEM_04 | Infrastructure (network-based) | -37.7385 | 144.9898 | 1 | Jemena | Report | 8426 | 0.01209 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | AF Other
On arrival crew carried out repairs | 2995 PRINCES HIGHWAY, WINCHELSEA VIC 3241 | 30332470 | Working too close to overhead lines | [5 empty] | 1 | The site superintendent (Luke Denman 0407855418) reported that a tip truck had contacted an electrical wire at the incident location. On arrival the crew found a tipper attached to the truck had contacted a 22KV conductor. The truck was on site but the driver had left the scene when the crew arrived. The truck Tyres were damaged. There was no fire or reported injuries to the driver and no other third party damage. | Conductor (bare) | 2 | 2 | 2 |  | WIN011 | Tipper struck conductors | Loss of supply;No Go Zone (contact) | 42739.3986 |  |  | 5891 | Public space |  | 20170406PWA_01 | Infrastructure (network-based) | -38.2476 | 143.9764 | 1 | Powercor | Report | 7243 | 0.036118 | 22kV AC | Avalon Airport | 3241 | Winchelsea | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew changed the damaged Krone box with a new Krone box. | COWES CHILDRENS HUB, 177 SETTLEMENT ROAD, COWES VIC 3922 | 2803645 |  |  |  | Overheated connection |  |  | 2 | IMS 226862. A Krone box (FSD) fire was reported by the fire brigade. No ground fire occurred. The cause of the fire was the burnt out Krone box. There was molten plastic at the base of the pole on the footpath and small section on the grass. Approximately 0.5 sq.m of grass was charred from the molten plastic. CAM# 2803645. | Connection box | 0 | 0 | 0 |  | PHI13 | FSD caught fire causing molten plastic material to fall to the ground. | Plant/equipment | 43011.4375 | 1 | Negligible: no ground fire | 5894 | Roadway |  | 20170406SPN_01 | Infrastructure (network-based) | -38.4563 | 145.2426 | 1 | AusNet Services Distribution | Report | 11255 | 0.032922 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Cowes | AF Other
On arrival crew carried repairs | 355 ORRONG ROAD, ST KILDA EAST VIC 3183 | 30219097 | Vehicle | [5 empty] | 2 | A Report from the MFB notified CitiPower that wires were down at the incident locationt. Upon arrival the CitiPower crew was notified by residents that a truck had made contact with the Low Voltage service to 355 Orrong Rd and did not stop. When the CitiPower crew arrive the found the LV cross arm has snapped and the road side LV conductor has come away from the cross arm and the overhead service was on the ground removed from the service pole. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Service conductor;Crossarm (wood) | 2 | 2 | 2 |  | AR10 | Unknown vehicle struck service line | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/03/2017 18:08 |  |  | 5903 | Roadway |  | 20170407PWA_05 | Infrastructure (network-based) | -37.8609 | 145.0101 | 1 | CitiPower | Report | 7261 | 0.035277 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | St Kilda East | Vehicle
On arrival crew carried out repairs Transformer was replaced and environmental cleanup carried out, | 495 OCONNORS ROAD, WERRIBEE SOUTH VIC 3030 | 32170730 | Working too close to underground cables | [5 empty] | 2 | A passer-by reported that a lawn mower has struck a low voltage cable and the transformer is leaking oil at the incident location. On arrival the fault crew found that a council worker (Wyndham Council) had been mowing near the substation when his lawn mower contacted / snagged the low voltage substation earth. The earth pulled on the bushing of the transformer breaking the bushing and causing the transformer to begin leaking oil, two meters of earth cable was pulled away from the ground. Further it was determined that the low voltage earth which had been buried at the required depth had been exposed when the council installed a spoon drain a couple of years earlier. This exposed earth was subsequently contacted by the mower. There was no ground fire and no injury as a result of this incident. | Earth;Pole mounted | 2 | 1 | 2 |  | WBE034 | Lawn mover entangled with earth cable | Loss of supply;Damage to network assets | 17/03/2017 10:49 |  |  | 5904 | Roadway |  | 20170407PWA_06 | Infrastructure (network-based) | -37.9603 | 144.6963 | 1 | Powercor | Report | 7262 | 0.02076 | Earthing cable | Laverton Raaf | 3030 | Werribee South | Other
On arrival crew carried out repairs | 243 BRAYS ROAD, ROSS CREEK VIC 3351 | 33007975 | Copper theft | [5 empty] | 2 | A contract employee called to advise earth cables were missing from a pole at the incident location. On arrival the crew found that both earth cables had been stolen from the pole. The crew replaced stolen earth cables. No protection operated. There were no reported injuries or shocks. | Earth | 2 | 2 | 2 |  | BAS022 | cable theft | Damage to network assets | 29/03/2017 12:10 |  |  | 5905 | Roadway |  | 20170407PWA_07 | Infrastructure (network-based) | -37.6497 | 143.7973 | 1 | Powercor | Report | 7263 | 0.037069 | Earthing cable | Ballarat Aerodrome | 3351 | Ross Creek | Other
On arrival crew carried out repairs | 13 BOND STREET, TALBOT VIC 3371 | 32027019 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Site manager reported wire down at the incident location. On arrival the crew found that a Loader had struck a VicRail owned pole, both causing the pole to lean & the neutral screened service (PAL) cable at incident location to fail mid span. | Service conductor | 2 | 2 | 2 |  | MRO007 | Loader struck pole | Loss of supply | 42739.6944 |  |  | 5908 | Public space |  | 20170411PWA_02 | Infrastructure (network-based) | -37.1771 | 143.7055 | 1 | Powercor | Report | 7267 | 0.019448 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3371 | Talbot | Vehicle
EIO attended and advises 'electric shock' was REC receiving burns from electricity splash over when working on switchboard. Ambulance, and Fire Brigade were on site, as well as Worksafe and ESV. Fault crew attended and disconnected supply at sub pole out front. Defect #J09678 issued on customer switchboard. | 34-38 FREIGHT DRIVE, SOMERTON VIC 3062 |  |  |  |  | Fault on customer installation |  |  | 2 | LEIW (Khushroo) was working at the main switchboard. His main task was to disconnect redundant cabling from within wall(s) that were to be demolished. While working at the main switchboard, a flashover occurred that had resulted in an ionisation of the atmosphere immediately within the vicinity of the working area. The flashover made contact with Khushrooâ€™s clothing and burnt his shirt off of his body. Khushroo sustained severe burns as a result and was taken to hospital via ambulance. As a result of the short or flashover within the main switchboard, the blue phase fuse blew at the substation supplying the property. The white phase lost effective contact and became open-circuited as a result of pitted arced contacts. The red phase remained supplying the installation, however all three hinged fused contacted had sustained pitted arced contacts. Upon ESV in attendance testing the installation, they confirmed that the PSC via the red phase to neutral was 3.31KA. The voltage supply at the top of the main switch on the red phase was 245VAC. The fault loop (Neutral impedance) was well below 0.1?. LEI arranged for fault crew to attend, isolate supply and issue defect notice for an REC to rectify arc damaged main switchboard before supply is to be restored. | Customer installation | 2 | 2 | 2 |  |  | Customers switchboard. | Medical attention (first aid/doctor/hospital) | 13/04/2017 13:21 |  |  | 5922 | Commercial |  | 20170413JEM_02 | Infrastructure (network-based) | -37.6419 | 144.9642 | 1 | Jemena | Report | 7283 | 0.0086215 | Low voltage AC (<1kV) | Essendon Airport | 3062 | Somerton | Other
On arrival crew carried out repairs | 32 INVERLOCHY STREET, ANGLESEA VIC 3230 | 33042041 |  |  |  | Electrical breakdown |  |  | 2 | The crew were conducting some switching for operations. When they closed Switch 20175 , the crew noticed an explosion in the distance. Upon arrival, the crew found that transformer, Treatment Works 14, had exploded and was on fire. The CFA extinguished the fire. The crew advised that oil had hit the ground and small ground fires had occurred. The Powercor Environmental Group was made aware of the situation. Soil samples were taken and sent off for testing. Veolia was arranged to dispose of the contaminated soil. There were no reported injuries or third party damage. | Pole mounted | 1 | 1 | 2 |  | WPD021 | Transformer failure - cause undetermined | Loss of supply;Grassfire;Plant/equipment | 43073.1 | 1 | Localised: less than 10 sq.m | 5914 | Commercial |  | 20170413PWA_01 | Infrastructure (network-based) | -38.4049 | 144.1988 | 1 | Powercor | Report | 7275 | 0.036701 | 22kV AC | Avalon Airport | 3230 | Anglesea | Other
On arrival crew carried out repairs | 16 ADAMSON ROAD, ECHUCA VIC 3564 | 32184201 |  | Animal |  |  |  |  | 1 | CFA reported wires down and they were controlling a small grass fire at the incident location. The crew found a broken HV termination Xarm which caused a 150m x 100m grass fire at the incident location. There were no reported injuries, no 3rd party damage for the incident. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | ECA012 | Crossarm failure | Grassfire | 43073.6493 | 1 | Medium: 1000 sq.m - 10 ha | 5924 | Agricultural |  | 20170418PWA_01 | Infrastructure (network-based) | -36.1825 | 144.7303 | 1 | Powercor | Report | 7285 | 0.021435 | 22kV AC | Bendigo Airport | 3564 | Echuca | Crossarm
On arrival crew carried out repairs | 3203 LAKE CHARM-QUAMBATOOK ROAD, LAKE CHARM VIC 3581 | 30235186 |  |  |  | Leakage |  |  | 2 | Customer reported wires down and pole fire at the incident location. On arrival the crew found a pole fire had caused a small ground fire resulting in approximately 2m x 3m of grass being burnt. There were no reported injuries, no 3rd party damage, for the incident. | Pole (wood) | 2 | 2 | 2 |  | KGT004 | excessive leakage current | Pole-top fire;Grassfire | 42982.8299 | 1 | Localised: less than 10 sq.m | 5925 | Agricultural |  | 20170418PWA_02 | Infrastructure (network-based) | -35.6262 | 143.793 | 1 | Powercor | Report | 7286 | 0.033753 | 22kV AC | Swan Hill Aerodrome | 3203 | Lake Charm | Pole
On arrival crew carried out repairs | 1 TWELFTH STREET, MILDURA VIC 3500 | 32150522 |  |  |  | Leakage |  |  | 2 | A passer-by informed that a loud bang, sparking and smoking at the incident location. On arrival the crew found that a Pole Fire had occurred. Note: At the time of the incident no HVI found. There was no ground fire or injury. CFA attended. | Crossarm (wood) | 2 | 2 | 2 |  | MDA031 | excessive leakage current | Pole-top fire | 20/04/2017 13:43 | 1 | Negligible: no ground fire | 5957 | Roadway |  | 20170426PWA_03 | Infrastructure (network-based) | -34.1992 | 142.165 | 1 | Powercor | Report | 7327 | 0.04011 | 22kV AC | Mildura Airport | 3500 | Mildura | Pole
On arrival crew carried out repairs | CALDER HIGHWAY, DUMOSA VIC 3527 | 32024287 |  |  |  | Leakage |  |  | 2 | CFA reported Pole Fire on the Calder Highway between the towns of Demosa and Nullawil. Crew attended and opened off ACR for isolation and replaced HV intermediate crossarm. No ground fire, no property damage, no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | CTN003 | Excessive leakage current | Pole-top fire | 20/04/2017 17:58 | 1 | Negligible: no ground fire | 5958 | Roadway |  | 20170426PWA_04 | Infrastructure (network-based) | -35.9131 | 143.2266 | 1 | Powercor | Report | 7328 | 0.0067315 | 22kV AC | Swan Hill Aerodrome | 3527 | Dumosa | Pole
Underground group requested to make the supply to the site safe. The cable has been capped and sealed. The area around the repair has been secured by barriers. John (Cervello / JOV PTY LTD) notified (26.4.2017 @ 02:27hours) low voltage cable on site is â€œaliveâ€ no work to proceed until supply abolished. | 42-44 MANNINGHAM STREET, PARKVILLE VIC 3052 | 30212688 | Unauthorised work | [5 empty] | 2 | Reporte that a building has been demolished and a live underground cable has been damaged by the demolition company at the incident location. On arrival the fault crew found that a building was being demolished, the supply to the building had not been abolished and a live low voltage underground cable had been exposed and damaged at the incident location. The demolition company alleges that they were informed by the property owner that the supply had been abolished late in 2016 and were given the go ahead to demolish the building. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | LS012 | Demolition Works | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/04/2017 11:00 |  |  | 5962 | Residential |  | 20170427PWA_01 | Infrastructure (network-based) | -37.7875 | 144.9423 | 1 | CitiPower | Report | 7333 | 0.038238 | Low voltage AC (<1kV) | Essendon Airport | 3052 | Parkville | Dug up
Emergency high voltage switching was completed and the repairs completed under Access Authority conditions before supply was restored. Work Safe attended the site and began an investigation. ESV were also advised of the event. | 19 IRVING AVENUE, BOX HILL VIC 3128 | 7037062 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | At 1315hrs on 18/04/2017, ACR BH7611 located in Station Street reclosed to lockout affecting 1111 customers interrupted initially for ACR BH7611 protection operation. A NGZ breach occurred following a crane operated by Liberty Cranes making contact with the 22kV overhead conductors at a construction site outside 19 Irving Road, Box Hill whilst lifting a steel girder into place. The crane made contact with the red phase HV conductor that sustained damage and was required to be sleeved. No injuries were sustained or damage occurred to the crane. | Conductor (bare) | 0 | 0 | 0 |  | DC 06 | A crane load made contact with the 22kV overhead conductors at a construction site outside 19 Irving Avenue, Box Hill. In summary, No Go Zone assessments were completed as follows and the Permit to Work had expired. - Garry Harding (ZNX) first attended site on the 25/5/2016 and issued PTW U21258 for basement works only. - Re-attended on 14/09/2016 and issued PTW U21493 for construction and crane work. This PTW expired on the 14/12/2016 and was not renewed. - ZNX attended the site on 26/04/2017 and issued a new PTW U2295 that expires on 26/07/2017. | No Go Zone (contact) | 18/04/2017 13:15 |  |  | 5980 | Construction |  | 20170430UTD_05 | Infrastructure (network-based) | -37.8159 | 145.1212 | 1 | United Energy Distribution | Report | 12329 | 0.038869 | 22kV AC | Moorabbin Airport | 3128 | Box Hill | Vehicle
On arrival crew carried out repairs | UNIT 1 119 WINFIELD ROAD, BALWYN NORTH VIC 3104 | 30179454 | Copper theft | [5 empty] | 2 | Registered Electrical Contractor reported that cable has been stolen from the incident location. On arrival the fault crew found that about 1.5m of 3phase, 35mm2 copper low voltage underground cable had been stolen from the incident location. The cable had been rolled up and left at the pole end pending connection to fuses on the pole which supply a pit servicing four new units at the incident location. No cable was stolen from the pit. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | WD032 | Cable theft | Damage to network assets | 28/04/2017 13:00 |  |  | 5981 | Roadway |  | 20170501PWA_01 | Infrastructure (network-based) | -37.7909 | 145.1028 | 1 | CitiPower | Report | 7352 | 0.029987 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
On arrival crew carried out repairs | 473 ALBERT STREET, EAST MELBOURNE VIC 3002 | 30206483 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that they have dug up a underground cable at the incident location. On arrival the fault crew found that they have hit a underground 16mmÂ² 4/c service cable. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | MP049 | Excavation works | Loss of supply;Damage to network assets | 27/04/2017 12:37 |  |  | 5983 | Commercial |  | 20170501PWA_02 | Infrastructure (network-based) | -37.8097 | 144.9747 | 1 | CitiPower | Report | 17441 | 0.012861 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Dug up
On arrival crew carried out repairs | TREKARDO PARK BALLARAT SOCCER CLUB, 507 PLEASANT STREET S, REDAN VIC 3350 | 30000081 | Vehicle | [5 empty] | 2 | CFA reports a car into a pole at the incident location. On arrival the crew found car had struck a pole, resulting in a fatality to the driver. Police, Ambulance, SES and CFA attended. No protection operated. The pole was replaced. There were no reported shocks or ground fire start. | Pole (wood) | 2 | 2 | 2 |  | BAS014 | Vehicle struck pole | Damage to network assets | 42740.5854 |  |  | 5989 | Roadway |  | 20170502PWA_02 | Infrastructure (network-based) | -37.571 | 143.8372 | 1 | Powercor | Report | 12109 | 0.013867 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Redan | Vehicle
On arrival crew carried out repairs | 350 MITCHELL ROAD, KIALLA VIC 3631 | 32188231 | Working too close to overhead lines | [5 empty] | 1 | A customer reported a power outage. A crew patrolled the line and found a excavator had contacted the SWER O/H line and broke the conductor, dropping it to the ground. Protection operated. There were no reported shocks, injuries or ground fire start. | Conductor (bare) | 2 | 2 | 2 |  | STN021 | Excavator hit line | Loss of supply;No Go Zone (contact) | 42799.4042 |  |  | 5992 | Agricultural |  | 20170504PWA_03 | Infrastructure (network-based) | -36.4571 | 145.4177 | 1 | Powercor | Report | 7370 | 0.021628 | 12.7kV AC (SWER) | Shepparton Airport | 3631 | Kialla | Vehicle
Under investigation | 176 SWANN DRIVE, DERRIMUT VIC 3030 |  |  |  |  | Incorrect design | Unknown work practice factor |  | 1 | An electrical tester was proving the operation of a push button switch on a newly installed 66kV circuit breaker when his hand contacted a micro-switch. The micro-switch controls the light within the cabinet and was actuated by opening the cabinet door. A minor electric shock was received. | Any other type | 0 | 0 | 0 |  |  | Inadvertent contact | Minor shock | 42830.375 |  |  | 6004 | Construction |  | 20170508PWA_05 | Infrastructure (network-based) | -37.8014 | 144.7732 | 1 | Powercor | Report | 8109 | 0.010188 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Derrimut | Other
Fault truck called to investigate and make safe - DAO and ESV advised. Crew isolated the supply, issued permit and replaced the junction box to restore supply. | 61 TANJIL RIVER ROAD, TANJIL SOUTH VIC 3825 | 2201134 |  |  |  | Overheated connection |  |  | 2 | IMS 226876. Customer called claiming there was a fire on a substation pole. When fault crew arrived on site they found a junction box on the pole had failed and caught on fire. Fire was extinguished on arrival and small patch of grass approximately 1 metre square was burnt. Please note - the initial report from CEOT was a fire on sub pole. No report of a ground fire, asset fire only so therefore no Schedule 1 report was entered into OSIRIS as only a Schedule 2 report was required. CEOT did though fax a Schedule 1 report to ESV as their standard process. | Connection box | 0 | 0 | 0 |  | moe21 | Cause could not be determined but typical causes are high impedance connections or electrical overload. | Grassfire | 13/03/2017 7:40 | 1 | Localised: less than 10 sq.m | 6006 | Agricultural |  | 20170508SPN_01 | Infrastructure (network-based) | -38.1207 | 146.2715 | 1 | AusNet Services Distribution | Report | 7386 | 0.0039306 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Tanjil South | Connection
Made safe and removed service and meter. | 11 ROBINSON STREET, JACANA VIC 3047 |  | Unauthorised access | [5 empty] | 2 | A Zinfra crew was sent out to do a service order abolishment of an existing overhead service and meter to an existing house and a new connection for an overhead BTS pole. Upon arrival the crew discovered that the overhead service and meter were already relocated to the BTS. | Aluminium twisted (XLPE);Smart meter | 2 | 2 | 2 |  |  | Unknown party removed and disconnected service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42983.4389 |  |  | 6014 |  |  | 20170509JEM_01 | Infrastructure (network-based) | -37.686 | 144.9121 | 1 | Jemena | Report | 7394 | 0.035483 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Jacana | Other
CEOT dispatched a faults crew and an AusNet Services' LEI to make safe, investigate and repair. Pre-rectification test results: An initial NST test was performed which failed. Voltage from an independent earth to the street light pole was measured at 225 Volts. IR of street light circuit was measured at zero MOhms A-E which is a fail. What was rectification? The identified faulty active conductor of the public lighting cable was removed and this connection was repaired. After-rectification test results: A final NST test was performed which failed. Neutral impedance was measured at 1.3. The Polarity was correct, the cable size and the long route length distance was determined to be the reason for the circuit neutral impedance being above 1. The voltage from an independent earth to the point of contact (the street light pole) was measured at 0.7 Volts which is considered safe. An IR test of the lighting circuit was measured at 75 MOhms which is a pass. A Continuity test was conducted on the street lighting circuit which passed. Any other test results? An earth fault loop test of the supply to the metallic street light pole was measured at 300. Rewireable fuse with 8-10A fuse wire was used. The following is additional information provided to ESV to assist in understanding the issues involved. This is in the form of an action item raised in IMS by Glenn Davidson on Robert Prestidge, Site Supervisor, Traralgon depot. Rob has set an action reply due date of 31 July. Rob will need to liaise with AusNet Services' Standards section and also the Work Practices section to assist and seek information in addressing the following points: "The following information is extracted from the attached incident report from the attending AusNet Services' LEI. Can you please comment on and decide if we need to take any actions on these points raised by the LEI. Can an insulated cover be inserted in this pole's termination opening and is the pole earthed (MEN) as per our Standard Installations Manual? I would appreciate some feedback. Please provide your answers and any actions taken in the Required Actions field below. Many thanks Glenn Information extracted for LEI's report: * LED light fitting has no cable retention capabilities, allowing single insulated cable to fall back into the pole piecing the insulation. * No check test preformed when light fitting replaced. (comment by Glenn Davidson:- there is currently no check test for public lighting testing and the issue is being discussed at the VESI ISCT&Pcommittee level whether or not it is required). * No MEN connection at pole or insulated covers on active or neutral bars. (If MEN connection had been made â€“ 225V / 1.3 = 173A â€“ 8-10A fuse protection would have operated. No MEN connection from Earth fault loop value. 225V / 300 = 0.75A â€“ too low to operate protective device). * New outgoing underground lighting cable installed DEC 2016 to feed failed street lights further along the circuit. Unknown if any testing was done on that street light pole at that time." For further information, please see attached photos of the street light pole. | 11 ANTARES AVENUE, SALE VIC 3850 | 2507322 |  |  |  | Defective component |  | Phase to phase | 2 | IMS 226991. Mr Speed was washing his car on the nature strip outside his house when he received a tingle off the street light pole. Mr Speed regarded the shock as slight comparable to a telephone shock (ex Telstra employee). The cause was found to be a piercing in the insulation of the street light active conductor 75mm from the termination of the LED light fitting onto the metallic pole, causing the street light to become live. | Public lighting | 0 | 0 | 0 |  | sle11 | Damaged insulation on lighting active conductor made contact with metallic street light pole. | Minor shock | 20/03/2017 15:30 |  |  | 6015 | Residential |  | 20170509SPN_02 | Infrastructure (network-based) | -38.1095 | 147.0874 | 1 | AusNet Services Distribution | Report | 12358 | 0.017322 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | AF Other
A CitiPower crew attended this site to remove / make safe the low voltage supply | 511-521 KING STREET, WEST MELBOURNE VIC 3003 | 30189038 | Unauthorised work;Unauthorised access | [5 empty] | 2 | Fletcher Coon Jackson (CitiPower employee) reported that a developer has demolished a building at the incident location on or before the 9.2.2017 leaving behind â€œLIVEâ€ low voltage assets. Scheduled date for CitiPower to abolish these assets: 16.2.2017. A CitiPower crew attended this site to remove / make safe the low voltage supply which had been left protruding from the ground with the â€œLIVEâ€ electrical wires dangling from the metal conduit which was supporting a plastic distribution box. There was no ground fire and no injury as a result of this incident. | Services cable;Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | VM026 | Demolition works prior to abolishment of supply | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42980.4951 |  |  | 5682 | Commercial |  | 20170227PWA_06 | Infrastructure (network-based) | -37.8079 | 144.9511 | 1 | CitiPower | Report | 6960 | 0.022441 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. Downer requested an AusNet Services Vegetation & Easements (V&E) officer attend the site to speak to the private contractor regarding their options. The V&E officer explained to the private contractor that they were breaching the No Go Zone Rules by removing branches over and adjacent to the 22kV conductors. The private contractor was told to cease work and it could only be completed under shutdown conditions. The private contractor was referred to Extec Services to arrange for a shutdown to complete the works. | 28 CARDIGAN ROAD, MOOROOLBARK VIC 3138 | 1015329 | Working too close to overhead lines;Unauthorised work | Within clearances |  |  |  | Phase to earth | 1 | IMS 226693. LD6003 tripped on SEF (F10-9184-r) - report of private tree contractor dropping branch on/through network lines, 1x 22kV line down between Lis 1015329 - 1015330. A third party tree contractor was removing a pine tree that was overhanging 22kV conductors on private property. During the course of the operation the private climbing party lost control of a cut branch which landed on the 22kV conductor causing one phase to fail mid-span and fall to ground. Tree clearer's details: Richard McLeod, Blue Chip Tree Services, telephone 0400 427409. | Conductor (bare) | 0 | 0 | 0 |  | ldl24 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 42738.4653 |  |  | 5696 | Residential |  | 20170301SPN_04 | Infrastructure (network-based) | -37.7884 | 145.3205 | 1 | AusNet Services Distribution | Report | 12353 | 0.032498 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | Trees
On arrival crew confirmed no conductor damage | 63 GODDARD ROAD, KYABRAM VIC 3620 | 32186923 | Working too close to overhead lines | [5 empty] | 1 | A customer reported a contractor hit power line and also power outage at the incident location. Upon arrival, the Powercor crew found that a truck mounted crane had flicked the 22kV line. The protection operated. No damage on the HV conductors but small flash marks can be seen. There were no injuries, fire or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | KYM003 | crane contacted conductor | Loss of supply;No Go Zone (contact) | 28/02/2017 12:59 |  |  | 5699 | Roadway |  | 20170302PWA_01 | Infrastructure (network-based) | -36.2921 | 145.0679 | 1 | Powercor | Report | 8047 | 0.024132 | 22kV AC | Shepparton Airport | 3620 | Kyabram | Vehicle
As the pole had sustained substantial damage it was replaced after all investigations had taken place. | 70 HOPPERS LANE, WERRIBEE SOUTH VIC 3030 | 32170030 | Vehicle | [5 empty] | 2 | MFB reported car hit pole at the intersection of Duncans Rd and Hoppers Lane Werribee South. The vehicle was reported as travelling in a southerly direction and lost control while overtaking another vehicle and collided with the pole. The force of the impact was severe. The pole had snapped and shifted at ground level, however the HV & LV Conductors remained in place being held on by the insulators, thus there was no ground fire. The driver and sole occupant of the vehicle, a male, died at the scene. All emergency services were on site including MFB, SES, Police and Ambulance. | Pole (wood) | 2 | 2 | 2 |  | WBE034 | Vehicle incident | Damage to network assets | 42828.5243 |  |  | 5710 | Roadway |  | 20170306PWA_01 | Infrastructure (network-based) | -37.9179 | 144.7021 | 1 | Powercor | Report | 6999 | 0.026199 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Vehicle
Crew isolated supply and REC attended to restore supply. | 187 IRAAK LAKE ROAD, IRAAK VIC 3494 | 30098846 |  |  |  | Fault on customer installation |  |  | 2 | CFA reported pole fire/grass fire at the above location. A crew attended and found the fuse box at the customerâ€™s POA had shorted and had caused a small grass fire. There was no injuries. | Customer installation | 2 | 2 | 2 |  | RCT014 | Fault on customers FOLCB | Grassfire | 42828.7694 | 0 | Localised: less than 10 sq.m | 5721 | Agricultural |  | 20170307PWA_01 | Infrastructure (network-based) | -34.4103 | 142.3158 | 1 | Powercor | Report | 7016 | 0.018775 | Low voltage AC (<1kV) | Mildura Airport | 3494 | Iraak | Fuse
On arrival crew carried out repairs | 1224 SHINNICKS ROAD, NUMURKAH VIC 3636 | 33087082 |  |  |  | Unknown technical factor |  |  | 2 | CFA reported grass fire at incident location CFA were in attendance prior to crew arrival and extinguished fire. No shock, no third party damage, no injuries were sustained. | EDO fuse | 2 | 2 | 2 |  | NKA006 | Fuse operation, no further details found | Grassfire | 42828.909 | 1 | Medium: 1000 sq.m - 10 ha | 5722 | Roadway |  | 20170307PWA_02 | Infrastructure (network-based) | -36.0354 | 145.4034 | 1 | Powercor | Report | 7018 | 0.038082 | 22kV AC | Shepparton Airport | 3636 | Numurkah | Fuse
On arrival crew carried out repairs | 199 REES ROAD, MELTON SOUTH VIC 3338 | 30306398 | Copper theft | [5 empty] | 2 | A Powercor employee reported cut away cables on a pole and at the incident location. Upon arrival, the fault crew found that the earthing cable on the pole had been stolen. There were no reported injuries or other damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | theft | Damage to network assets | 16/02/2017 13:18 |  |  | 5723 | Agricultural |  | 20170307PWA_03 | Infrastructure (network-based) | -37.7213 | 144.561 | 1 | Powercor | Report | 7019 | 0.012203 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Work has been directed to stop and the area protected by temporary fencing. The contractor has been instructed to contact Powercor Customer Compliance team. | 85 DUNNINGS ROAD, POINT COOK VIC 3030 | 31036638 | Working too close to underground cables | [5 empty] | 2 | A call was received requesting Powercor to attend and relocate the Powercor assets at the incident location as the assets interfere with the road expansion work which is being done by the contractor. Upon arrival, the fault crew found that the HV and LV UG cable conduits exposed and a conduit is slightly damaged. There was no visible damage to the electrical cables. There was no fire, injuries or third party property damage. | Cable | 2 | 2 | 2 |  | LV008 | Excavation works | No Go Zone (contact) | 16/02/2017 12:24 |  |  | 5725 | Roadway |  | 20170308PWA_01 | Infrastructure (network-based) | -37.8864 | 144.7465 | 1 | Powercor | Report | 7021 | 0.034519 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew carried out repairs | 129 KOROIT-WOOLSTHORPE ROAD, KOROIT VIC 3282 | 33102607 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that they had contacted an U/G cable at the above location. A crew attended and found that during the installation of a pair of gas main conduits, an U/G lv service had been dragged out of the trench. The contractor advises that they had completed a dial before you dig, had identified and exposed the U/G conduit. A NGZ permit was on issue. The 2 gas pipes had been install in the trench under the lv conduit and while pulling the 2 gas pipe thru the trench, the pipe came out of the trench, contacting the lv U/G conduit, bending it up out of the trench. Supply to the premise was not interrupted. There were no shocks, injuries, third party damage or ground fire start. | Services cable | 2 | 2 | 2 |  | KRT013 | disturbed cable during gas installation | No Go Zone (contact) | 17/02/2017 14:55 |  |  | 5727 | Residential |  | 20170308PWA_02 | Infrastructure (network-based) | -38.2804 | 142.3687 | 1 | Powercor | Report | 7023 | 0.040432 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3282 | Koroit | Other
On arrival crew carried out repairs | 12 MARKET ROAD, SUNSHINE VIC 3020 | 30106124 | Copper theft | [5 empty] | 2 | Miles (Powercor employee) reported that copper earths have been stolen from the incident location. On arrival the fault crew found that copper earths have been stolen from the Third-Market ground substation. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | SSE034 | cable theft | Damage to network assets | 17/02/2017 12:09 |  |  | 5728 | Public space |  | 20170308PWA_03 | Infrastructure (network-based) | -37.7996 | 144.839 | 1 | Powercor | Report | 7024 | 0.002831 | Earthing cable | Essendon Airport | 3020 | Sunshine | Other
On arrival crew carried out repairs | 98 CENTRAL KIALLA ROAD, KIALLA VIC 3631 | 32191637 |  |  |  | Overheated connection |  |  | 2 | Customer reported that his fuse had blown and meter panel was blackened and fuse glowing. On arrival crew found that the fuse had overheated and melted and appeared to have a bad connection on the line side. Customer was still on supply, Crew advised that damage to switchboard was minimal. No damage to house, no ground fire, no injuries. | Meter board (including fuses) | 2 | 2 | 2 |  | STN021 | Overheated connection in meter board fuse | Melting or smoking only | 20/02/2017 20:27 |  |  | 5730 | Residential |  | 20170308PWA_04 | Infrastructure (network-based) | -36.4499 | 145.4316 | 1 | Powercor | Report | 7026 | 0.017899 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Kialla | Fuse
On arrival crew carried out repairs | 25 MANZEENE AVENUE, LARA VIC 3212 | 32067790 | Working too close to underground cables | [5 empty] | 2 | Contractor reported that they have contacted a low voltage underground cable at the incident location. On arrival the fault crew found contractors were excavating a trench in the vicinity of Powercor low voltage underground cables. They used an excavator to remove a large rock when the rock became dislodged the crew sighted the cable and conduit which were installed inside a bore through a large rock at the incident location. Power flickered in the house but remained on. MOCâ€™s drawings on site. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | FNS021 | Removal of rock from trench | No Go Zone (contact);Damage to network assets | 23/02/2017 10:31 |  |  | 5740 | Roadway |  | 20170309PWA_01 | Infrastructure (network-based) | -38.019 | 144.3805 | 1 | Powercor | Report | 7037 | 0.04084 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Dug up
On arrival crew carried out repairs. | 638-688 GREIGS ROAD, ROCKBANK VIC 3335 | 33102697 | Working too close to underground cables | [5 empty] | 2 | An excavation contractor installing a water main in the nature strip has struck an LV service cable crossing Greigs Rd at the incident location. The Contractor had undertaken Dial before You Dig enquiries and had documents on site, but there was no reference to this cable crossing in the responses received. The LV cable sustained some external damage to its sheath, but the cable remained on supply. There were no reported injuries or ground fire start. | Services cable | 2 | 2 | 2 |  | MLN011 | Contractor hit cable | No Go Zone (contact);Damage to network assets | 23/02/2017 13:11 |  |  | 5741 | Roadway |  | 20170309PWA_02 | Infrastructure (network-based) | -37.7436 | 144.6345 | 1 | Powercor | Report | 7038 | 0.014027 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
On arrival crew cut away tree and carried out repairs to conductor | 202 HARBOURS ROAD, YENDON VIC 3352 | 32002591 |  | Fallen |  |  |  |  | 1 | CFA called to advise a tree had pulled down a wire and started a grass fire at the above location. On arrival the crew found a tree had contacted 1 phase of a single phase 22kV line and broke the conductor, resulting in the conductor falling to the ground and starting a grass fire on public property. The CFA attended and extinguished the ground fire. Protection operated at Eureka P97A ACR. There were no shocks, injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | BAS023 | Vegetation: Trees Incident | Grassfire | 42950.5437 | 1 | Small: 10 - 1000 sq.m | 5742 | Roadway |  | 20170309PWA_03 | Infrastructure (network-based) | -37.6544 | 143.9726 | 1 | Powercor | Report | 7043 | 0.040888 | 22kV AC | Ballarat Aerodrome | 3352 | Yendon | Trees
On arrival crew confirmed isolation and arranged for repairs to take place. | 40-52 MCARTHURS ROAD, ALTONA NORTH VIC 3025 | 32164556 | Vandalism;Copper theft | [5 empty] | 2 | Powercor Report Room noted that a number of industrial customers had lost supply, (â€¦via AMI Power down) at incident location. Affected Customers were all fed from â€œMcArthurs 32-Chambersâ€ ground-type substation. A Powercor fault crew was dispatched to establish the cause of the outage. Upon arrival Powercor crew found that vacant factory premises at 40-52 McArthurs Rd, Altona North had sustained a break-in. The substation fence perimeter had been breached, and a HV switch handle had been vandalized in the process of unauthorized isolation of the substation transformer and LV substation circuits. An inspection of the factory site noted evidence of copper theft on the customerâ€™s installation. No protection operated. There were no reported injuries or ground fire start. | Earth/earthing;Dropper/bridge | 2 | 2 | 2 |  | BLT017 | Vandalism and cable theft | Loss of supply;Damage to network assets | 25/02/2017 22:45 |  |  | 5743 | Industrial |  | 20170309PWA_04 | Infrastructure (network-based) | -37.8349 | 144.8405 | 1 | Powercor | Report | 7044 | 0.037192 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3025 | Altona North | AF Other
CEOT dispatched fault crew to make safe and investigate. CEOT also advised the local DAO. Crew isolated supply and made safe. Crew replaced the damaged 500 kVA transformer with up to date animal/bird proofing and restored supply. | 235 BALD HILL ROAD, PAKENHAM VIC 3810 | 524590 |  | Bird |  |  |  | Phase to earth | 1 | IMS 226815. reported in vicinity of pole #524590 at the South East Water's Pakenham Recycled Storage water Reservoir. AusNet Services' local DAO onsite. Grass fire in the vicinity of substation pole LIS 524590, approximately 70m x 28m in size due to a bird touching live parts of the transformer. It was a very hot dry day with gusty Easterly winds which fanned the fire up an embankment. The fire burnt itself out due to a gravel track and a dam in the way of more fuel. Blown HV bushing on transformer. HV fuse operated. | Pole mounted;Transformer | 0 | 0 | 0 |  | phm12 | Bird Incident | Grassfire | 42950.5625 | 1 | Small: 10 - 1000 sq.m | 5748 | Industrial |  | 20170309SPN_01 | Infrastructure (network-based) | -38.0903 | 145.5077 | 1 | AusNet Services Distribution | Report | 7051 | 0.011104 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | Animal
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Crew on site have reported possibly caused by a helicopter. Final report: Crew isolated the fault and restrung the 22kV conductor then restored supply. | 1755 MCDONALDS TRACK, THORPDALE VIC 3835 | 5744869 | Manned aircraft | [5 empty] | 1 | IMS 226843. Initial report: Resident reported wire down. Final report: Pole 39 LIS #5744869 WINDERLICH SPUR MOE31. 3 phase termination substation pole. Cable size 118 ACSR. Helicopter was flying very low to spray potatoes and made contact with one of the Blue phase 22kV conductor. Company/owner of helicopters â€“ Country Helicopters. www.countryhelicopters.com.au. Registration number VH-JIU. No injuries sustained. | Conductor (bare) | 0 | 0 | 0 |  | moe22 | A low flying crop spraying helicopter contacted the Blue phase HV conductor. | Loss of supply;No Go Zone (contact) | 42981.5951 |  |  | 5749 | Agricultural |  | 20170309SPN_02 | Infrastructure (network-based) | -38.3048 | 146.2138 | 1 | AusNet Services Distribution | Report | 7053 | 0.016441 | 22kV AC | Morwell (Latrobe Valley Airport) | 3835 | Thorpdale | Other
A faults crew attended and proceeded to replace the damaged FOLCB and was restored upon completion. | 695 BONEO ROAD, BONEO VIC 3939 | 1312279 |  |  |  | Overheated connection |  |  | 2 | CFA onsite advised of a grass fire caused by a fuse blowing. A 40sqm grass fire was reported at the base of pole No. LIS 1312279 located outside 695 Boneo Road that was promptly extinguished by the CFA. The cause was a burnt out red phase connection at a FOLCB and the suspected cause was a loose connection with molten metal falling into the dry grass below the pole starting the grass fire. | Aluminium twisted (grey);Connection box | 0 | 0 | 0 |  |  | The suspected cause was a loose connection. | Grassfire | 42858.625 | 1 | Localised: less than 10 sq.m | 5738 | Roadway |  | 20170309UTD_01 | Infrastructure (network-based) | -38.4215 | 144.8875 | 1 | United Energy Distribution | Report | 7035 | 0.01274 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Boneo | Connection
On arrival crew inspected conductors for damage. An LEI inspected for HV injection (non found) | 43 GREAVES STREET S, WERRIBEE VIC 3030 | 30105854 | Vehicle | [5 empty] | 0 | Vic Police phoned in to advise of a wire down at the cnr of Hodges St & Greaves St Werribee. Upon arrival the crew had found that an unknown vehicle, possibly a large truck, had hit the Optus Cable at the incident location, this has resulted in the Optus Catenary Flicking into the HV & LV Conductors above, causing sparking and splash marks on the HV Conductors and Neutral of the LV Conductors. There was no reported HVI, this was confirmed by the LEI, who attended. There was no fallen electrical cables as a result of this incident. There was no fires or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBE024 | Unknown vehicle hit OPTUS cable | Loss of supply;Significant disruption to the community;Damage to network assets | 43011.6535 |  |  | 5755 | Roadway |  | 20170314PWA_03 | Infrastructure (network-based) | -37.9094 | 144.6563 | 1 | Powercor | Report | 7061 | 0.029942 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival crew carried out repairs | 494 MUCKLEFORD-WALMER ROAD, MUCKLEFORD VIC 3451 | 32044587 |  | Lightning |  |  |  |  | 1 | CFA reported cable on the ground grass smoldering at incident location. Crew attended and found HV conductor 3/2.75 Galvanised Steel Conductor had failed believed to be caused by lightning strike. An area of 8 Metres by 2 Metres was burnt on the road verge. No property damage and No injuries reported | Conductor (bare) | 2 | 2 | 2 |  | CMN004 | Lightning strike | Grassfire | 43072.3069 | 1 | Small: 10 - 1000 sq.m | 5761 | Roadway |  | 20170315PWA_01 | Infrastructure (network-based) | -37.0495 | 144.1474 | 1 | Powercor | Report | 8396 | 0.0081516 | 22kV AC | Bendigo Airport | 3451 | Muckleford | Lightning
crew attended. referred to ESV | 34 FERRARS PLACE, SOUTH MELBOURNE VIC 3205 | 30171120 | Working too close to overhead lines | [5 empty] | 2 | Crew advises scaffolding erected against energised service and FOLCB. site previously advised on 15/02/2017 that isolation would be required. | Service conductor;Customer installation | 0 | 0 | 0 |  | AP015 | Interference - clearance not maintained | No Go Zone (no contact) | 17/03/2017 13:41 |  |  | 5773 | Residential |  | 20170317PWA_02 | Infrastructure (network-based) | -37.8402 | 144.9593 | 2 | CitiPower | Report | 7093 | 0.030256 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Other
On arrival crew isolated supply and carried out repairs | ALSTONVALE COURT, EAST BENDIGO VIC 3550 | 31037843 |  | Lightning |  | Corrosion |  |  | 1 | Vic Fire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo. On arrival the crew found one of the HV cable head joint terminations had failed and a fire occurred at the base of the pole approx. 25 sq. meters in area. The weather was overcast and humid with storms in the vicinity. There was no reported injuries or third party property damage. | Cable;Dropper/bridge | 2 | 2 | 2 |  | EHK021 | Cable head joint failed | Grassfire | 20/03/2017 19:11 | 1 | Small: 10 - 1000 sq.m | 5785 |  |  | 20170321PWA_01 | Infrastructure (network-based) | -36.7496 | 144.3211 | 1 | Powercor | Report | 7108 | 0.01848 | 22kV AC | Bendigo Airport | 3550 | East Bendigo | Connection
On arrival crew inspected site, no damage found | MCPHEE ROAD, IRYMPLE VIC 3498 | 32148440 |  |  |  | Unknown technical factor |  |  | 1 | Customer reported pole on fire at base of pole. On arrival, crew found 2 separate spot fires (5-10 square meters) at bottom of 2 pole substations within 200m of each other. Customer had extinguished the fire, no CFA attendance. One section fuse operated, there was no evidence of failed assets at either pole. There were no reported injuries, minor property damage. | Pole mounted | 2 | 2 | 2 |  | RCT021 | No cause for fire could be found | Loss of supply;Grassfire | 19/03/2017 16:26 | 1 | Small: 10 - 1000 sq.m | 5790 | Agricultural |  | 20170321PWA_06 | Infrastructure (network-based) | -34.2705 | 142.172 | 1 | Powercor | Report | 7113 | 0.021478 | 22kV AC | Mildura Airport | 3498 | Irymple | Pole
On arrival crew carried out repairs. | 102 OAKWOOD ROAD, ALBANVALE VIC 3021 | 30120236 | Vehicle | [5 empty] | 2 | Vic fire reported that a truck has contacted and brought down wires at the incident location. On arrival the fault crew found that a tip truck had left the work site. The driver having forgotten to stow his raised tipper which snagged the overhead pay TV and service wires at the incident location. Vic fire reported that a truck has contacted and brought down wires at the incident location. On arrival the fault crew found that a tip truck had left the work site. The driver having forgotten to stow his raised tipper which snagged the overhead pay TV and service wires at the incident location. Vic fire reported that a truck has contacted and brought down wires at the incident location. On arrival the fault crew found that a tip truck had left the work site. The driver having forgotten to stow his raised tipper which snagged the overhead pay TV and service wires at the incident location. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | SA007 | Failure to lower tipper | Loss of supply;Damage to network assets | 27/02/2017 9:37 |  |  | 5791 | Roadway |  | 20170321PWA_07 | Infrastructure (network-based) | -37.7511 | 144.7688 | 1 | Powercor | Report | 7114 | 0.030917 | Low voltage AC (<1kV) | Laverton Raaf | 3021 | Albanvale | Vehicle
Substation isolated, a defect notice was issued | 110 DOHERTYS ROAD, LAVERTON NORTH VIC 3026 | 33076596 | Building too close or within the No Go Zone | [5 empty] | 2 | Powercor was contacted with a request for assistance to isolate a substation, at an industrial incinerator complex at 110 Dohertys Rd Laverton North. A fire had occurred within the customer installation of the premises earlier in the day. A Powercor crew attended the site, but were unable to readily perform the switching required. Powercor fault crew leader noted that access to the pole type substation was impeded by a structure that had been constructed around it. It was noted that electrical and physical clearances between the pole substation and the encircling structure had also been breached. The fault crew were instructed to disconnect customer until unauthorised structure is removed from the vicinity of the pole type substation so that access and required clearances are restored. A Defect Notice was issued and an LEI attendance was requested. There were no ground fires or reported injuries. | Pole mounted | 2 | 2 | 2 |  | LVN031 | Unauthorised barriers placed around susbstation | No Go Zone (no contact) | 42738.666 |  |  | 5794 | Industrial |  | 20170322PWA_01 | Infrastructure (network-based) | -37.8283 | 144.7915 | 1 | Powercor | Report | 7118 | 0.03735 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3026 | Laverton North | Other
Crew advised that the Service Cable was redundant, therefore they decided to cut away and remove the LV Cable at ground level. | 429-443 FAULKNERS ROAD, MOUNT COTTRELL VIC 3024 | 33072601 | Copper theft | [5 empty] | 2 | Chris advised UG cable at incident location has been vandalised. Upon arrival the crew found that an unknown person had tied a rope around an abandoned UG Service Cable and attempted to pull it out of the ground. There was no fire, injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN011 | Attempted cable theft | Damage to network assets | 42797.7625 |  |  | 5795 | Roadway |  | 20170322PWA_02 | Infrastructure (network-based) | -37.7753 | 144.6214 | 1 | Powercor | Report | 7119 | 0.032719 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival crew carried out repairs | 231-319 FAULKNERS ROAD, MOUNT COTTRELL VIC 3024 | 33073470 | Copper theft | [5 empty] | 2 | The crew advised they have found that an unknown person had cut away and stolen the LV Earths from ground level to a height of approximately 3 metres up the pole at the incident location. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 42797.7625 |  |  | 5796 | Roadway |  | 20170322PWA_03 | Infrastructure (network-based) | -37.7609 | 144.6288 | 1 | Powercor | Report | 7120 | 0.038611 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival crew isolated supply and commenced repairs | 56 MARINE PARADE, ABBOTSFORD VIC 3067 | 30170972 |  | Fire |  |  |  |  | 2 | Fault crew responded to a call by the MFB, a fire had caused damaged to CitiPower assets at the incident location. On arrival the fault crew found that a contractor while installing a new sewer had bored into a gas main which ignited and burnt the low voltage underground service on the nearby pole. The contractor Jack Mclean received burns to his face and hands and was taken to hospital. | Services cable | 2 | 2 | 2 |  | CW009 | 3rd party struck gas main | Significant disruption to the community;Damage to network assets | 23/02/2017 18:00 |  |  | 5797 | Roadway |  | 20170322PWA_04 | Infrastructure (network-based) | -37.8031 | 145 | 1 | CitiPower | Report | 7123 | 0.010762 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | Dug up
The fence and gate temporary repaired and permanent repairs have been arranged. Cleaning of the area is underway. The security company has been requested to increase the patrols on both DA and FB ZSSâ€™s. | 424-432 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 |  | Vandalism;Copper theft | [6 empty] | A Powercor employee has received a phone call reporting break in at the incident location (DA Zone Substation). The attended crew found that the thieves damaged the entrance door and also a fence panel and entered to the control room and distribution sub. All locker doors were opened and attempted copper theft from an old two disconnected distribution transformers. The LV bushing of a transformer damaged causing oil leak into the cement floor. A minor damage has been done to the other transformer. The site made safe and repairs have been arranged. The thieves left tools/equipment inside. There were no reported injuries or fire. | Zone substation | 2 | 2 | 2 |  |  | attempted copper theft | Damage to network assets | 42918.6097 |  |  | 5807 | Industrial |  | 20170322PWA_10 | Infrastructure (network-based) | -37.8088 | 144.9328 | 1 | CitiPower | Report | 7135 | 0.025521 | Not applicable | Essendon Airport | 3003 | West Melbourne | Other
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 250w HPS lantern from the pole in the centre medium strip. A 50amp fuse had operated that was replaced to restore supply to a number of street lights in the vicinity. A new order was created for the replacement of the defective lantern. | 745 PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 8805944 |  |  |  | Electrical breakdown |  |  | 1 | CFA are on site and report a pole fire opposite 810-818 Princes Highway, Springvale. A 250w HPS lantern on pole No. LIS 8805944 located outside 745 Princes Highway caught fire and self-extinguished. The cause was unknown but most likely a loose connection that overheated may have been the cause. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated may have been the cause. | Plant/equipment | 20/03/2017 20:00 | 1 | Negligible: no ground fire | 5800 | Roadway |  | 20170322UTD_01 | Infrastructure (network-based) | -37.939 | 145.1624 | 1 | United Energy Distribution | Report | 7125 | 0.040958 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | AF Other
Low voltage isolator opened to make safe. Crew replaced 3 phase fuse mains junction box and restored supply at 1610. | 2-8 BULLA ROAD, BULLA VIC 3428 |  |  |  |  | Age |  |  | 2 | A fuse mains junction box on a substation pole was reported by MFB to be sparking. However, there was no evidence of ground fire or any other fire start. Therefore, by AER definition below, this incident is not considered to be a reportable F-factor fire start. | Connection box | 0 | 0 | 0 |  |  | Fuse mains junction box on substation pole was aged and deteriorated. | Plant/equipment | 25/03/2017 13:28 | 0 | Negligible: no ground fire | 5818 | Peri-urban |  | 20170325JEM_03 | Infrastructure (network-based) | -37.6405 | 144.8154 | 1 | Jemena | Report | 7149 | 0.034034 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Fuse
On arrival crew commenced repairs A LEI attended on site to verify any HVIâ€™s and confirmed that a HVI did occur, affecting numerous customers. | 76 MARION STREET, ALTONA NORTH VIC 3025 | 30105507 |  | Humidity;Fallen |  |  |  |  | 1 | A report was received from a customer that they heard a loud bang and saw sparks coming from the pole across the road. Upon arrival the fault crew found that a large branch from a gum tree located within adjacent reserve broke and fell across the HV conductors, resulting in the HV being pushed down into the LV below. The conductors remained in place. There were no reported injuries or fire to report. | Conductor (bare) | 2 | 2 | 2 |  | BLT017 | Vegetation: Trees Incident | HV injection;Loss of supply | 26/03/2017 19:19 |  |  | 5820 | Public space |  | 20170327PWA_02 | Infrastructure (network-based) | -37.8351 | 144.8515 | 1 | Powercor | Report | 7151 | 0.022506 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3025 | Altona North | Trees
The PCA HV Operator informed the Control Room. Repairs to the fence where completed | 163 ANDERSON ROAD, SUNSHINE VIC 3020 |  | Vandalism;Copper theft | [5 empty] | 2 | After attending SSE Zone Sub due to a number of faults on Sunday 12/03/2017 at approximately midday, a PCA HV Operator noticed that part of the barbed wire fence on the Western Perimeter of SSE Zone Sub (close to the southern corner) had been cut away. He did a quick walk around of the Zone Sub Yard and advised that it appeared as though nothing had been taken. The only damage he could visibly see was the copper bonding from the fire hydrant to the fire box had been pulled out of the ground and attempted to be stolen, however nothing was actually taken or removed from the Zone Sub-Yard. | Zone substation | 2 | 2 | 2 |  |  | suspected attempted copper theft | Less than $50k damage;Damage to network assets | 43072.5813 |  |  | 5821 | Industrial |  | 20170327PWA_03 | Infrastructure (network-based) | -37.7796 | 144.8281 | 1 | Powercor | Report | 7152 | 0.0021146 | Earthing cable | Essendon Airport | 3020 | Sunshine | Other
On arrival crew carried out inspection of site | 715 COLAC-LAVERS HILL ROAD, BARONGAROOK VIC 3249 | 33039891 |  | Blown branch/vegetation |  |  |  |  | 2 | Vic Fire reported a ground fire at the incident location. On arrival the crew found that a grassfire of approx. 1,000m2 in size had ignited beneath the 22kV conductors at the incident location. There was a reclose of the CLC006 feeder CB recorded at approx. 10:42am. Inspections of the HV conductor in the area by the attending crew were unable to identify a cause for the grassfire, however it was noted that strong winds were present, and several pieces of bark were scattered on the ground in the area. There was no other reported third party damage or any injuries. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | No direct cause found | Grassfire | 27/03/2017 10:48 | 1 | Small: 10 - 1000 sq.m | 5828 | Public space |  | 20170328PWA_06 | Infrastructure (network-based) | -38.4295 | 143.5778 | 1 | Powercor | Report | 7161 | 0.010014 | 22kV AC | Ballarat Aerodrome | 3249 | Barongarook | Trees
No Go Zone assessor attended site on 20 March 2017 and installed four flags on the HV overhead line. There was no one in attendance. The property appears to be vacant as very little usage recorded on the meter. | 1320 MICKLEHAM ROAD, CRAIGIEBURN VIC 3064 |  | Building too close or within the No Go Zone | [5 empty] | 2 | A Jemena fault crew attended a fault with 3 x 6K boric acid fuses found blown at a tee off to MICKLEHAM RD-P14E2. There was no physical damage to the overhead lines and no one was on site at the time of visit. There is building material stockpiled adjacent to the high voltage (HV) overhead lines. The cause is a suspected line strike by machinery due to the close location of construction equipment to line (e.g scaffolding/timber/junk). The fault crew measured from the top of one of the piles and it is less then 3m to the HV overhead line. | Conductor (bare) | 0 | 0 | 0 |  | COO-11 | The property owner is in breach of the NGZâ€™s limits of approach as the containers are too close to the HV overhead lines. | No Go Zone (no contact) | 14/03/2017 10:35 |  |  | 5846 | Peri-urban |  | 20170329JEM_01 | Infrastructure (network-based) | -37.6036 | 144.8836 | 1 | Jemena | Report | 7182 | 0.011051 | 22kV AC | Melbourne Airport | 3064 | Craigieburn | Vehicle
On arrival crew carried out repairs | 590 INKERMAN ROAD, CAULFIELD NORTH VIC 3161 | 30219414 |  |  |  | Unknown technical factor |  |  | 2 | A Customer, Ursula Lever, phoned in to advise that the a pole mounted box has caught fire and dropped to the ground, still smoking, and a possible wire down.. Upon arrival the CitiPower faults crew found that the LV FOLCB supplying 590 & 590A Inkerman Rd, Caulfield North had caught fire and melted to the ground. There was no ground fire, injuries or third party damage | Connection box | 2 | 2 | 2 |  | EL011 | due to damage no cause identified | Pole-top fire;Loss of supply | 19/03/2017 14:01 | 1 | Negligible: no ground fire | 5866 | Roadway |  | 20170331PWA_04 | Infrastructure (network-based) | -37.8681 | 145.0143 | 1 | CitiPower | Report | 7210 | 0.014354 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Pole
The faults crew opened HV fuses at DN0209 and the HV underground cable isolated to allow the HV red phase elbow to be re-secured to the transformer. The faults crew replaced the HV red phase 31.5amp powder filled fuse and restored supply. The substation fence was fixed temporary with permanent repairs to be completed on 31/03/2017. | WEDGEWOOD ROAD, HALLAM VIC 3803 |  | Copper theft | [5 empty] | 1 | A REC attended a dim lights call out at 27 Wedgewood Road and measured 180v between the red phase and neutral. Also identified 240v between the white phase and neutral and blue and neutral is 75v. REC has isolated supply at the main switch for safety. A faults truck attended and identified the red phase 31.5amp powder filled fuse had operated at "Wedgewood - T4 Princess" ground type substation. The cause was unknown persons had attempted to remove the 22kV red phase elbow from the transformer in what appears to have been an attempted copper theft earlier that morning that caused dim lights to customers supplied from the street circuit. Milk crates were found within the ground type substation enclosure with the fence cut open. It was unknown if any injuries were sustained. | Equipment;Outdoor | 0 | 0 | 0 |  | DN 21 | Suspected copper theft from ground type substation. | No Go Zone (contact) | 30/03/2017 8:15 |  |  | 5862 | Industrial |  | 20170331UTD_01 | Infrastructure (network-based) | -38.0072 | 145.256 | 1 | United Energy Distribution | Report | 7206 | 0.0020602 | 22kV AC | Moorabbin Airport | 3803 | Hallam | Other
On arrival crew arranged repairs | 3906 CALDER HIGHWAY, BRIDGEWATER VIC 3516 | 30017992 |  |  |  | Leakage |  |  | 2 | Vicfire advised a pole fire at the incident location. Fire had been extinguished upon crew arrival. Upon arrival noted burning to the pole and 2 small patches of grass at the base of the pole. There were no injuries, loss or damage to third party property. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | BETS-CTN | Excessive leakage current | Pole-top fire;Grassfire | 30/03/2017 1:00 | 1 | Localised: less than 10 sq.m | 5868 | Roadway |  | 20170403PWA_01 | Infrastructure (network-based) | -36.5926 | 143.9241 | 1 | Powercor | Report | 7212 | 0.039416 | 22kV AC | Bendigo Airport | 3906 | Bridgewater | Pole
On arrival crew carried out repairs. | 16 HOBBS ROAD, WYNDHAM VALE VIC 3024 | 32177760 | Unknown external/community factor | [5 empty] | 1 | A Powercor crew attended before 17:00 hrs and found a 22kV Boric Acid spur line fuse had operated at LIS 211268 in Wollahra Rise. The crew were unable to find a cause for the fuse operation. At 17:18 Following customer calls the Powercor crew re-attended, and discovered that a second HV fuse had operated. After further line Patrol crew found that an overhead steel 22kV conductor appeared damaged between LIS 200527 and LIS 200528. The land beneath the line is being re-developed from grazing land to residential estates, as part of this development the overhead lines will ultimately be placed underground. There were a number of excavators operating across the area. A number of inquiries were made on site with plant operators, there was no information forthcoming regarding any potential contact of the overhead conductors. On detailed examination the Powercor crew found that 2 strands of one of the 3/2.75 steel conductors had been damaged. There was no injuries reported, no fire or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE014 | Probable contact by unidentified excavator | Damage to network assets | 42739.7208 |  |  | 5870 | Construction |  | 20170403PWA_02 | Infrastructure (network-based) | -37.8676 | 144.61 | 1 | Powercor | Report | 7216 | 0.040698 | 22kV AC | Laverton Raaf | 3024 | Wyndham Vale | Conductor
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe and investigate. NST test at pole passed and NST test at premises failed. Inspection of the overhead service cable revealed that it had sustained damage, been previously repaired with heat shrink. Further investigation revealed the repair had been unsuccessful and the neutral had corroded off. It was also noted that there was a tree growing close to the service cable. The Linesman noted this and it was defected. The overhead service cable was replaced with a new XLPE type service cable. Further tests conducted: NST tests, Polarity tests OK. Customer's main earth conductor resistance < 0.5 Ohm, OK. Carried out tests at customer's switchboard and neutral test / NST test OK. Linesman to follow up on the tests clearing away from the service cable on the customer's property. | 53 BUCKLEY STREET, SALE VIC 3850 | 2504970 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 226660. Both the injured persons were lightly dressed doing household activities when touching the taps in either the bathroom or kitchen felt tingles from the taps. They informed the Real Estate Agent who engaged REC Jones Electrical who sent Electricians to attend. The Electrician carried out tests and obtained readings of 9 Volts AC to an independent earth. | Service conductor | 0 | 0 | 0 |  | sle14 | The outer insulation of the service cable neutral conductor was damaged and the conductor was corroded through. | Minor shock | 28/02/2017 17:00 |  |  | 5881 | Residential |  | 20170404SPN_03 | Infrastructure (network-based) | -38.095 | 147.0784 | 1 | AusNet Services Distribution | Report | 7230 | 0.00048264 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | OH Cable
On arrival crew carried out repairs | 119 HANNS ROAD, SEA LAKE VIC 3533 | 32156368 |  |  |  | Leakage |  |  | 1 | following on from reports of no supply in the Sea Lake area, A line patrol found a SWER pole top fire at the incident location. There was no ground fire, reported injuries or third party property damage, | Pole (wood) | 2 | 2 | 2 |  | CTN003 | Excessive leakage current | Pole-top fire;Loss of supply | 42888.3014 | 1 | Negligible: no ground fire | 5882 | Agricultural |  | 20170405PWA_01 | Infrastructure (network-based) | -35.5015 | 143.0315 | 1 | Powercor | Report | 7232 | 0.0099896 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3533 | Sea Lake | Pole
On arrival crew carried out repairs | 2753 HAMILTON HIGHWAY, CARAMUT VIC 3274 | 30042625 |  |  |  | Leakage |  |  | 1 | Following customer calls, a pole fire was located at P261 of the Penshurst line. The HV crossarm burnt through causing conductors to fall onto T/off conductors. There was no ground fire, reported injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | TRG002 | Excessive leakage current | Pole-top fire | 16/02/2017 1:47 | 1 | Negligible: no ground fire | 5883 | Roadway |  | 20170405PWA_02 | Infrastructure (network-based) | -37.9322 | 142.4948 | 1 | Powercor | Report | 7233 | 0.028622 | 22kV AC | Warrnambool Airport Ndb | 3274 | Caramut | Pole
Crew replaced blue phase service box transformer isolator and fire report number 04564 raised | 20 HILLCREST DRIVE, LANGWARRIN VIC 3910 |  |  |  |  | Overheated connection |  |  | 1 | At 1830hrs on 3/4/17 customer reported burn marks on pole and molten plastic on ground. Crew arrived onsite at 2011hrs and replaced blue phase service box transformer isolator | Disconnector/isolator | 0 | 0 | 0 |  | LWN 23 | Connection failure | Melting or smoking only | 42798.7715 |  |  | 5884 | Roadway |  | 20170405UTD_01 | Infrastructure (network-based) | -38.161 | 145.2103 | 1 | United Energy Distribution | Report | 7235 | 0.020661 | Low voltage AC (<1kV) | Moorabbin Airport | 3910 | Langwarrin | AF Other
New Connection Crew arrived onsite for Truck Appointment to upgrade from single phase to three phase to find a live lv service hanging off the supply pole. Crew immediately isolated supply to service hanging on pole and then undertook upgrade of supply from single phase to three phase. Site left safe. | 13 DALY AVENUE, RYE VIC 3941 |  | Unauthorised work;Caused by REC/contractor |  |  |  | Incorrect electrical isolation and/or permits |  | 2 | New Connection Crew arrived onsite for Truck Appointment to upgrade from single phase to three phase to find a live lv service hanging off the supply pole. Crew approached REC and asked if he had removed the service and hung it on the pole, to which he replied â€œyesâ€ and â€œwhat's the problem?â€ Crew immediately isolated supply and then undertook upgrade of supply from single phase to three phase. Site left safe. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | RBD 14 | It appears the REC wanted us to attend the single appointment â€“ Upgrading the 3Ph supply and reconnecting upon completion. This at a minimum should have been booked for a disconnect and reconnect appointment. Not withstanding the obvious Public Safety Risk â€“ The conductive pole and just a bit of tape over the end of the service ends which are at head height. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42829.3535 |  |  | 5889 | Residential |  | 20170406UTD_01 | Infrastructure (network-based) | -38.3738 | 144.8347 | 1 | United Energy Distribution | Report | 7240 | 0.029866 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | Rye | Other
LEI investigated Supply left off due to no access for testing (deceased estate) ESV advised and are investigating | 9 MALIN STREET, KEW VIC 3101 | 30169258 |  |  |  |  | Not followed |  | 2 | Following on from replacement of a pole a Citipower Linesmen reported an energised neutral / earthing system incident at the POA service box on the premise of 9 Malin St Kew . It was reported , a water pipe below the customerâ€™s property was made live and acted like a heat sink. This excess heat burnt insulation in the house. There was no reported injuries or shock. | Service conductor;Customer installation | 2 | 2 | 2 |  | L002 | Human error, wiring fitted into incorrect terminal at supply point on fascia | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43043.75 |  |  | 5909 | Residential |  | 20170412PWA_01 | Infrastructure (network-based) | -37.8145 | 145.0443 | 1 | CitiPower | Report | 12453 | 0.022774 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | AF Other
The LEI tested all customer connections and confirmed no damage to customer property. Field crews carried out required repairs | LORNE COLLEGE, 18 SMITH STREET, LORNE VIC 3232 | 30064045 |  | Wind;Fallen |  |  |  |  | 2 | The Crew were dispatched to investigate wires down and possible HVI incident in Grove Rd, Lorne. Attending crew found that a tree had fallen onto a span at the incident location. The HV then hit the ground and left small burn marks on the grass. It is suspected that there was also a HVI with the HV making contact with the bare LV. There was no third party damage or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | CLC005 | Vegetation: Trees Incident | Loss of supply;Grassfire | 43012.2812 | 1 | Localised: less than 10 sq.m | 5910 | Public space |  | 20170412PWA_02 | Infrastructure (network-based) | -38.5398 | 143.9738 | 1 | Powercor | Report | 7270 | 0.0076655 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3232 | Lorne | Trees
On arrival crew commenced repairs | 31 KOSSATZ ROAD, NETHERBY VIC 3418 | 32105633 |  | Fire |  |  |  |  | 1 | Customer rang to advise pole laying in paddock and no supply. Crew attended and found pole burnt off at base following land owner complete ling stubble burn off in paddock earlier that day. Protection operated. There were no reported shocks or injuries. | Pole (wood) | 2 | 2 | 2 |  | NHL016 | Stubble burn off | Loss of supply | 42859.5597 |  |  | 5912 | Agricultural |  | 20170412PWA_04 | Infrastructure (network-based) | -36.0926 | 141.6583 | 1 | Powercor | Report | 7308 | 0.024487 | 12.7kV AC (SWER) | Horsham Aerodrome | 3418 | Netherby | Other
The crew was instructed to complete this abolishment | 6 WALLACE STREET, BRUNSWICK WEST VIC 3055 | 30155576 | Unauthorised work;Unauthorised access | [5 empty] | 2 | Our crew was sent to an abolishment this morning where this is what was found on arrival Even though the crew was unable to locate the meter (crew suspect meter was damaged and removed during the demolition works) we could not leave the site in this condition!! The deteriorated open wire service was hanging approx. 2.5M high above the footpath There was no fire or reported injuries. | Service conductor | 2 | 2 | 2 |  | WB011 | Interference with service and meters | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43073.7083 |  |  | 5930 | Residential |  | 20170418PWA_07 | Infrastructure (network-based) | -37.7635 | 144.9461 | 1 | CitiPower | Report | 7291 | 0.021071 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Other
On arrival crew carried out repairs | 76 OLD DOOKIE ROAD, SHEPPARTON VIC 3630 | 33089832 |  |  |  | Overheated connection |  |  | 2 | Fire reported a Pole Fire at the incident location. On arrival the crew found the FSD unit to be overloaded and burnt out. There were no reported injuries, no 3rd party damage, no ground fire for the incident. | Connection box | 2 | 2 | 2 |  | STN024 | Unable to confirm due to damage | Pole-top fire | 43043.2667 | 1 | Negligible: no ground fire | 5932 | Roadway |  | 20170418PWA_08 | Infrastructure (network-based) | -36.3778 | 145.4248 | 1 | Powercor | Report | 7293 | 0.033557 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Fuse
On arrival crew carried out repairs | 17 ELM GROVE, RICHMOND VIC 3121 | 30193326 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | The MFB reported a wire had been brought down by a truck. A crew attended and found a crane truck had struck and broken a service cable to 17/19 Elm Grove. The trucks crane was not fully retracted when the incident occurred. No damage to customers point of attachment but a light on the supply pole was damaged and is listed for replacement. There was no fire, no shocks, injuries or 3rd party propery damage. | Service conductor | 2 | 2 | 2 |  | NR006 | Truck crane not stowed correctly | Loss of supply | 42920.5972 |  |  | 5936 | Roadway |  | 20170419PWA_04 | Infrastructure (network-based) | -37.8244 | 144.9998 | 1 | CitiPower | Report | 7297 | 0.017867 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. | 57 PAYNTER ROAD, NEERIM JUNCTION VIC 3832 |  |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 227473. Customer reported part supply failure. An AusNet Services' fault crew attended and found a candled 6k EDO fuse. No ground fire occurred. | EDO fuse | 0 | 0 | 0 |  | wgl24 | Candled EDO fuse tube. | Other electricity related | 43043.6076 | 1 | Negligible: no ground fire | 5940 | Agricultural |  | 20170420SPN_01 | Infrastructure (network-based) | -37.9278 | 145.9492 | 1 | AusNet Services Distribution | Report | 7303 | 0.016958 | 22kV AC | Morwell (Latrobe Valley Airport) | 3832 | Neerim Junction | Fuse
Initial report: CEOT dispatched a fault crew and an AusNet Services' LEI to make safe, investigate and carry out any necessary repairs. Final report: Fault crew and an AusNet Services' LEI attended to make safe, investigate and carry out necessary repairs. The supply was still connected, but customers were complaining of erratic supply with lights dimming and electrical equipment failures. Pre-rectification test results: Initial NST test performed which failed. Substation isolated for high neutral impedance. Addition LEIâ€™s were called in for support. What was rectification? 88 Customers' installations were isolated at their SPDs (service protection devices). Neutral connection repaired and a hinged isolator was replaced with a new hinged isolator after heat effected damage to the substation isolator. After-rectification test results: Final NST test performed which passed. Installations were individually inspected for damage, tested and power restored where access was provided. Where installation damage was found a Customer Claim form was filled out and damaged equipment isolated. Defect Notices (NCIDs) were issued where POAs were inaccessible. Electrical installation without access were left off supply with a contact form left in the meter boxes. | 37 PLOVER STREET, COWES VIC 3922 | 28062700 |  |  |  | Overheated connection |  |  | 2 | IMS 227542. Initial report: Possible injection, customers' complained of damage within properties. Final report: A single LV neutral connection clamp joining substation "PHILLIP JUSTICE" 92128062700 with a Copper conductor to the overhead AL ABC distribution system failed causing high LV volts through customers' installations in Ti Tree Drive, Settlement Road, Plover Street, Justice Road, and Churchill Drive, Cowes. Many of the installations requiring appliance technicians and electricians to repair damaged electrical items and electrical fittings. (Split System A/C, dishwashers, fridges, and LED lights, etc.). An actual HV injection did not occur. Please refer to the Cause tab for further details. | Connector/termination | 0 | 0 | 0 |  | phi11 | The substation's sole LV neutral connection clamp became faulty which resulted in a high impedance neutral fault at the substation source resulting in high volts on the reticulation network impressed across customer's electrical installations which are connected to the distribution network in a Star configuration, thus depending on the electrical loads present at any given time on customer's installations will determine the voltage present at each Point Of Supply (e.g. some properties will have higher LV volts than others and the installations with higher volts may suffer damage to appliances). The generated heat of the faulty neutral connection also damaged the substation's LV hinged isolator. HV assets were not involved. An actual HV injection did not occur. | Less than $50k damage | 16/04/2017 14:55 |  |  | 5941 | Residential |  | 20170420SPN_02 | Infrastructure (network-based) | -38.4585 | 145.2116 | 1 | AusNet Services Distribution | Report | 12357 | 0.020949 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3922 | Cowes | Connection
On arrival crew carried out repairs | 6172 ARARAT-ST ARNAUD ROAD, BEAZLEYS BRIDGE VIC 3477 | 32025009 |  | Fire |  |  |  |  | 2 | Customer called Powercor to advise that he had been burning off crop stubble. The burn had gotten out of control and had burnt down a Powercor pole at the incident location. There were no reported injuries | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | CTN006 | Farmer Burning off stubble | Damage to network assets | 18/04/2017 3:24 |  |  | 5944 | Agricultural |  | 20170421PWA_02 | Infrastructure (network-based) | -36.6986 | 143.1691 | 1 | Powercor | Report | 7311 | 0.010164 | 12.7kV AC (SWER) | Horsham Aerodrome | 3477 | Beazleys Bridge | Other
On arrival crew carried out repairs | 122 JAMOUNEAU STREET, WARRACKNABEAL VIC 3393 | 32097104 |  |  |  | Mechanical breakdown |  |  | 2 | A customer reported a wire to the house had broken and burn marks on ground where it landed. A crew attended and found the service to the premises had burnt off at the roller clamp at the house end . The service fell to the ground, resulting is a small ground fire. No CFA attended. There were no shocks, injuries or 3rd party damage. | Service conductor;Neutral screen | 2 | 2 | 2 |  | HSM005 | Service ruptured at roller clamp | Grassfire | 21/04/2017 12:08 | 1 | Localised: less than 10 sq.m | 5946 | Residential |  | 20170421PWA_03 | Infrastructure (network-based) | -36.2628 | 142.3934 | 1 | Powercor | Report | 7313 | 0.0072859 | Low voltage AC (<1kV) | Horsham Aerodrome | 3393 | Warracknabeal | OH Cable
Emergency high voltage switching took place after the red phase HV Boric Acid fuse was found to be candling at BH1074 in Joyce Street. The faults crew proceeded to replaced the red phase Boric Acid fuse unit under Access Permit conditions and supply was restored to normal on completion. | 170 CENTRAL ROAD, NUNAWADING VIC 3131 |  |  |  |  | Candled fuse |  |  | 1 | Caller reports the power went off for a few seconds and there is a fire on the pole located outside 170 Central Road and a thumping noise coming from it. There are lots of sparks and hissing but the power is now okay. At 12.15AM on 14/04/2017, ACR BH7287 on 22kV feeder NW21 located in Central Road opened and successfully reclosed and held. | Boric acid | 0 | 0 | 0 |  | NW21 | The red phase HV Boric Acid fuse was found to be candling. | Pole-top fire | 14/04/2017 0:15 | 1 | Negligible: no ground fire | 5951 | Roadway |  | 20170425UTD_05 | Infrastructure (network-based) | -37.825 | 145.169 | 1 | United Energy Distribution | Report | 7318 | 0.010834 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Pole
Substation isolated and assets to be removed. | 25-29 PARAMOUNT ROAD, WEST FOOTSCRAY VIC 3012 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Unaouthorised access to Substation (Paramount 25- Somerville no.2 S/S) via customers warehouse. Unknown person forced substation doors open. Copper cables and bus bar stolen. | Copper;Indoor | 2 | 2 | 0 |  |  | Unauthorised access to substation (forced doors open) and theft of copper cables and busbar. | Damage to network assets | 20/04/2017 14:00 |  |  | 5961 | Industrial |  | 20170427JEM_02 | Infrastructure (network-based) | -37.8073 | 144.8615 | 1 | Jemena | Report | 7331 | 0.021559 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3012 | West Footscray | Other
On arrival crew carried out repairs | 32 VAUXHALL ROAD, NORTHCOTE VIC 3070 | 30188494 |  | Lightning |  |  |  |  | 2 | A customer reported that a pole struck by lightning at the incident location. Upon arrival the CitiPower crew found that a damaged pole and also HVI to customersâ€™ equipment. There were no injuries or fire. | Pole (wood) | 2 | 2 | 2 |  | NC002 | Lightning strike | HV injection;Loss of supply | 26/04/2017 10:46 |  |  | 5963 | Roadway |  | 20170427PWA_02 | Infrastructure (network-based) | -37.776 | 145.0122 | 1 | CitiPower | Report | 7334 | 0.010023 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Lightning
On arrival crew carried out repairs | 1751 KERANG-MURRABIT ROAD, CAPELS CROSSING VIC 3579 | 32030269 |  |  |  | Leakage |  |  | 2 | CFA reported Pole Fire APPROX 600-700 metres SOUTH of intersection of Kerang - Murrabit Road and Guilmartin Road Capels Crossing. Crew attended and assessed the partially burnt HV intermediate crossarm where the insulator pin had fallen through. No ground fire, no property damage, no reported injuries. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | KGT003 | Excessive leakage current | Pole-top fire | 20/04/2017 18:34 | 1 | Negligible: no ground fire | 5964 | Roadway |  | 20170427PWA_03 | Infrastructure (network-based) | -35.6015 | 143.9345 | 1 | Powercor | Report | 7335 | 0.019205 | 22kV AC | Swan Hill Aerodrome | 3579 | Capels Crossing | Pole
A faults truck attended and isolated supply at pole No. LIS 3302271. A defect notice was issued to the Body Corporate for a burnt out LV isolator and consumers cables within the pillar and they are arranging for a REC to complete the rectification work at the earliest opportunity. | 49 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | 3302271 |  |  |  | Overheated connection |  |  | 2 | CFA state there is a fire in a 1m x 1m electricity box. During damp conditions with early morning rain, a fault occurred in a LV pillar that supplies 12 units at 49 Nepean Highway, Aspendale that caused a small grass fire. The most likely cause was an overheated connection within the pillar. | LV Pillar | 0 | 0 | 0 |  |  | The most likely cause was a loose connection within the pillar that overheated. | Grassfire | 25/04/2017 7:45 | 1 | Localised: less than 10 sq.m | 5979 | Residential |  | 20170430UTD_04 | Infrastructure (network-based) | -38.0162 | 145.0935 | 1 | United Energy Distribution | Report | 7350 | 0.020054 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | AF Other
On arrival crew commenced repairs. LEIâ€™s were on site to inspect and test the premises for suspected high voltage injection, no damage found. | 140-164 FORREST STREET, ARDEER VIC 3022 | 30112203 | Vehicle | [5 empty] | 1 | A passer-by reported that a car has struck a pole adjacent to the incident location. Due to the force of the impact the outer phase aluminum ties broke allowing the outer phase high voltage conductors to fall onto the low voltage circuit below. High voltage injection possible and possible damage to 105 customers supplied from the North-Suspension substation. There was no ground fire and no injury as a result of this incident. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SU015 | Vehicle accident | Loss of supply;Damage to network assets | 42830.5312 |  |  | 5995 | Roadway |  | 20170505PWA_01 | Infrastructure (network-based) | -37.783 | 144.8058 | 1 | Powercor | Report | 7373 | 0.00079514 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3022 | Ardeer | Vehicle
On arrival crew carried out repairs. | 100 POINT COOK HOMESTEAD ROAD, POINT COOK VIC 3030 | 30337265 | Working too close to underground cables | [6 empty] | A contractor advised an excavator has dug up an UG cable at the incident location. Upon arrival, the Powercor crew noticed that a Kiosk earthing cable had been damaged. There was no fire, no injuries or third party property damage. | Earth | 2 | 2 | 2 |  | LV004 | Contractor excavating near Kiosk substation | No Go Zone (contact);Damage to network assets | 42771.5708 |  |  | 6016 | Public space |  | 20170509PWA_02 | Infrastructure (network-based) | -37.9159 | 144.7648 | 1 | Powercor | Report | 7396 | 0.038516 | Earthing cable | Laverton Raaf | 3030 | Point Cook | Dug up
ON arrival crew carried out repairs | 16 MERTON STREET, ALTONA MEADOWS VIC 3028 | 30106401 | Copper theft | [5 empty] | 2 | A passer-by reported cable has been stolen from a high voltage gas switch at the incident location. On arrival the fault crew found that a section of copper earthing about six meters long had been stolen from the gas switch at the incident location. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LVN022 | Cable theft | Damage to network assets | 28/04/2017 8:40 |  |  | 6019 | Roadway |  | 20170509PWA_03 | Infrastructure (network-based) | -37.864 | 144.7784 | 1 | Powercor | Report | 7399 | 0.017848 | Earthing cable | Laverton Raaf | 3028 | Altona Meadows | Other
On arrival crew carried out repairs | 724 GLENFERRIE ROAD, HAWTHORN VIC 3122 | 30196546 |  |  |  | Overheated connection |  |  | 2 | MFB reported a pole fire at the incident location. On arrival the crew found that a Low Voltage Insulated Piercing Connector (IPC) at incident location had burnt out. There was no ground fire and no reported injuries nor third party property damage. | Connector/termination | 2 | 2 | 2 |  | L002 | Overheated IPC connection | Melting or smoking only | 22/04/2017 9:57 |  |  | 6024 | Roadway |  | 20170510PWA_04 | Infrastructure (network-based) | -37.8196 | 145.0361 | 1 | CitiPower | Report | 7404 | 0.035799 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Connection
On arrival crew carried out repairs | 80 WOODS ROAD, TRUGANINA VIC 3029 | 30119602 | Copper theft | [5 empty] | 2 | Due to an unrelated report where a customer was experiencing power supplies issues, when the fault crew arrived to investigate the supply issues, they identified that the same pole type substation supplying the customer at had at some point prior had the HV earth stolen from the pole. Approximately 10m of 70mm HV earth was stolen. There were no reported shocks, injuries, fire or third party damage as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LV002 | Theft of cable | Damage to network assets | 42891.5465 |  |  | 6027 | Roadway |  | 20170510PWA_05 | Infrastructure (network-based) | -37.8317 | 144.7204 | 1 | Powercor | Report | 7407 | 0.02448 | Earthing cable | Laverton Raaf | 3029 | Truganina | Other
A faults crew isolated and supply and a construction crew were required to replace two bays of LVABC. Emergency low voltage switching was completed to restore supply to customers supplied from "Osborne-Clarkes" substation with the krone switch at pole number LIS 1102022 closed and LV bridges broken at the tee-off pole on the corner of Osborne Drive at pole number 1101987. Two bays of LVABC was replaced and supply restored to normal upon completion to customers in Clarkes Avenue. | 31 CLARKES AVENUE, MOUNT MARTHA VIC 3934 | 1102020 |  |  |  | Electrical breakdown |  |  | 2 | Pole fire per CFA. A low voltage pole type junction box had caught fire and melted at pole number LIS 1102022 located near 31 Clarkes Avenue and the CFA were in attendance. The LVABC attached to the concrete pole was damaged and was required to be replaced. The cause of the fault was unknown and no photos were taken by the crew. | Connection box | 0 | 0 | 0 |  |  | The cause of the fault was undetermined and further investigation is required. | Pole-top fire | 42862.7354 | 1 | Negligible: no ground fire | 6281 | Roadway |  | 20170724UTD_02 | Infrastructure (network-based) | -38.2533 | 145.0307 | 1 | United Energy Distribution | Report | 12935 | 0.029928 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | Pole
On arrival crew carried out repairs | 238 PALMERSTON STREET, CARLTON VIC 3053 | 30212995 | Working too close to underground cables | [6 empty] | Contactor (DKM Earthworks) reported that they have contacted an underground cable at the incident location. On arrival the undergrounds fault crew found the contractor had contacted and damaged a low voltage underground main during excavation works to repair a water main at the incident location. The contractor had the required MOCâ€™s and dial before you dig plans which they failed to read correctly resulting in destructive digging which damaged the cable. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | BQ012 | Destructive excavation | Loss of supply;No Go Zone (contact);Damage to network assets | 28/06/2017 12:15 |  |  | 6298 | Roadway |  | 20170726PWA_04 | Infrastructure (network-based) | -37.7958 | 144.9667 | 1 | CitiPower | Report | 7763 | 0.00076273 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Dug up
Crew isolated the cable and completed repairs. | 19-27 KIALLA LAKES DRIVE, KIALLA VIC 3631 | 33096928 | Working too close to underground cables | [5 empty] | 1 | A customer reports a loss of supply and a contractor has dug up cable in middle of road at the above address. A crew attended and found a boring contractor installing a new gas main had struck and damaged an U/G LV main in street. There were no reported shocks, injuries or fire start. | Cable | 2 | 2 | 2 |  | STN012 | Contractor installing gas main | Loss of supply;No Go Zone (contact);Damage to network assets | 29/06/2017 12:03 |  |  | 6299 | Roadway |  | 20170726PWA_05 | Infrastructure (network-based) | -36.4136 | 145.3958 | 1 | Powercor | Report | 7765 | 0.021422 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Kialla | Dug up
The crew made the site safe and issued a defect notice. | 11-13 KIRKDALE STREET, BRUNSWICK EAST VIC 3057 | 30157707 | Vehicle | [5 empty] | 2 | A customer advised a truck has flicked a service line at the incident location. Upon arrival the CitiPower crew found a service hanging low and the POA had been damaged. No other damage reported. There was no fire or injuries reported | Service conductor | 2 | 2 | 2 |  | BK009 | Truck struck service line | Loss of supply;Damage to network assets | 42832.4806 |  |  | 6303 | Residential |  | 20170726PWA_09 | Infrastructure (network-based) | -37.7698 | 144.9813 | 1 | CitiPower | Report | 7769 | 0.010772 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Vehicle
On arrival crew inspected conductors for damage - non found | 13 QUANDONG STREET, LASCELLES VIC 3487 | 30100939 | Working too close to overhead lines | [5 empty] | 1 | Powercor fault crew attending an outage (OYN05 feeder) found that HV conductors flicked by unknown vehicle near the incident location. No damage on the conductors has been found. There was no Vehicle present at the site. The vicinity of the power line is being used by unknown third party for dumping soil. No injuries or fire reported. | Conductor (bare) | 2 | 2 | 2 |  | OYN005 | Unknown tipper struck conductor | Loss of supply | 27/07/2017 13:29 |  |  | 6315 | Public space |  | 20170728PWA_02 | Infrastructure (network-based) | -35.6056 | 142.581 | 1 | Powercor | Report | 7782 | 0.031274 | 22kV AC | Swan Hill Aerodrome | 3487 | Lascelles | Vehicle
Area made safe and LV conductors re-sleeved and rehung. Replaced red and white phase isolators. | 21 BAIRD STREET, MAIDSTONE VIC 3012 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Bare overhead LV conductor (red and neutral phases) fell to ground as a result of tree branch contact caused by strong winds | Conductor (bare) | 0 | 0 | 0 |  | FW17 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/07/2017 10:57 |  |  | 6322 | Residential |  | 20170729JEM_02 | Infrastructure (network-based) | -37.7896 | 144.8728 | 1 | Jemena | Report | 7789 | 0.027464 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | Trees
Area isolated for crews to conduct repairs to pole and LV conductors. | 832-838 HIGH STREET, RESERVOIR VIC 3073 | Pole no. A037721 | Vehicle | [5 empty] | 1 | Bare LV conductors on the ground as a result of truck hitting pole i.e. vehicle impact pole. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | CN11 | Vehicle (truck) impact pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/07/2017 11:46 |  |  | 6333 | Roadway |  | 20170731JEM_02 | Infrastructure (network-based) | -37.7225 | 145.0069 | 1 | Jemena | Report | 7805 | 0.025203 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Vehicle
Inspector confirmed HVI. The service trucks isolated damaged properties and damaged street light cabling. The west end of circuit was not affected by HVI and was re-enrgised. Customers on the east circuit were isolated and after repairs were completed the LV supply was energised. Isolated customers were tested and damaged meters were replaced where required. | 32-34 ST GEORGES ROAD, BEACONSFIELD UPPER VIC 3808 |  |  | Blown branch/vegetation |  |  |  |  | 2 | IMS 229470-An electrical inspector was called to attend possible HVI. This was confirmed from damage to a street light and customer properties that were checked. A limb had fallen from a tree on the property at 32 St Georges Rd Beaconsfield Upper and caused a HV injection with the red phase LV conductor. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | HV injection | 30/07/2017 7:38 |  |  | 6330 | Residential |  | 20170731SPN_03 | Infrastructure (network-based) | -38.0001 | 145.4055 | 1 | AusNet Services Distribution | Report | 8120 | 0.022395 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3808 | Beaconsfield Upper | Trees
Site made safe - crew isolated affected area. Jemena crew carried out repairs to LV conductor and replaced LV bridge. | CHINGFORD STREET, FAIRFIELD VIC 3078 |  |  | Wind |  | Conductor clashing |  |  | 1 | Strong winds caused LV conductors to clash resulting in bare LV conductor on ground (cornerr Chingford & Perry). | Conductor (bare) | 0 | 0 | 0 |  |  | Conductors clashing due to high winds. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/07/2017 18:10 |  |  | 6342 |  |  | 20170802JEM_01 | Infrastructure (network-based) | -37.7699 | 145.0251 | 1 | Jemena | Report | 7974 | 0.0192 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Fairfield | Other
Crew found that xlpe leads were on fire at LIS 2207558 on S/S WELLPO (MWTS-LGA3).Fire was out when crew attended Crew opened HV fuse and CFA extinguished fire. Crew found 7/104 dropper lead had been burnt. Construction crew replaced 7/104 droppers with XLPE droppers and restored supply. | 1159 MORWELL-THORPDALE ROAD, THORPDALE VIC 3835 | 2207558 |  |  |  | Defective component |  |  | 2 | IMS 229555. Fire Brigade report of pole fire @ 1159 Morwell Thorpdale Rd | Transformer | 0 | 1 | 0 |  | MOE31 | Defective dropper. | Pole-top fire | 42774.2361 | 1 | Negligible: no ground fire | 6351 | Agricultural |  | 20170803SPN_01 | Infrastructure (network-based) | -38.2885 | 146.1889 | 1 | AusNet Services Distribution | Report | 7831 | 0.019682 | 22kV AC | Morwell (Latrobe Valley Airport) | 3835 | Thorpdale | Conductor
Area isolated for crews to conduct repairs. Pole replaced and LV conductors repaired. | GLENROY ROAD, GLENROY VIC 3046 |  | Vehicle | [5 empty] | 2 | Vehicle hit pole (pole no. A050603) cnr Glenroy Rd & Leonard St Glenroy causing overhead LV conductor to fall on ground. | Conductor (bare);Pole (wood);Crossarm (wood) | 2 | 0 | 2 |  |  | Vehicle hit pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42955.5694 |  |  | 6380 | Residential |  | 20170808JEM_04 | Infrastructure (network-based) | -37.7062 | 144.9295 | 1 | Jemena | Report | 7864 | 0.023205 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Vehicle
On arrival crew carried out repairs and issued a defect notice to customer for POA repairs | 6 HENDRY STREET, SUNSHINE WEST VIC 3020 | 32164349 | Vehicle | [6 empty] | A Council employee informed a garbage truck has clipped a service cable at the incident location. Upon arrival the crew found that the 3Ph service cable had been damaged along with the customerâ€™s POA. There were no injuries or fire. | Service conductor;Customer installation | 2 | 2 | 2 |  | SSE014 | Garbage truck emptying bin | Damage to network assets | 42743.3694 |  |  | 6400 | Roadway |  | 20170811PWA_03 | Infrastructure (network-based) | -37.7869 | 144.8164 | 1 | Powercor | Report | 7888 | 0.032162 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
Jemena dispatched Network Operator to attend site and made safe. Conductor repaired on Sunday 13 August 2017. ESV contacted, reference no: 8016049 | 13 JUNCTION STREET, NEWPORT VIC 3015 | Pole no. A023693 |  | Within clearances |  |  |  |  | 1 | Tree clearing contractor removing cypress tree for construction developer, lost control of tree trunk and made contact with live bare HV conductors, causing white phase HV bridge to fail at pole no. A023693 Photo attachment has been included in the "Notes and Findings" sections | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | NT03 | Vegetation: Trees Incident | Loss of supply | 43077.7153 |  |  | 6404 | Residential |  | 20170814JEM_01 | Infrastructure (network-based) | -37.8358 | 144.8809 | 1 | Jemena | Report | 7900 | 0.039237 | 22kV AC | Essendon Airport | 3015 | Newport | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 351 NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 3308862 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 2152hrs on 11/08/2017, 22kV feeder ACR FS8164 located in Merewether Avenue reclosed to lockout affecting 584 customers. At the same time, 22kV feeder FTN14 circuit breaker successfully reclosed and held. Emergency services advised of a car into a pole outside 351 Nepean Highway, Frankston. A vehicle has struck the HV/LV tee-off pole (LIS No. 3308862) to "Officeworks-Nepean" substation located outside 351 Nepean Highway, Frankston that caused HV/LV mid-span conductors to clash. Following the conductors clashing, splash marks were identified on the HV conductors after they made contact with the LV conductors. The faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Bragge-Merewether" substation. The LEI confirmed a high voltage injection occurred (MOR 1701) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | FTN 14 | A vehicle has struck the HV/LV tee-off pole to "Officeworks-Nepean" substation located outside 351 Nepean Highway, Frankston that caused HV/LV mid-span conductors to clash and a HVI was later confirmed. | HV injection;Loss of supply | 43047.9111 |  |  | 6407 | Roadway |  | 20170814UTD_04 | Infrastructure (network-based) | -38.1355 | 145.1247 | 1 | United Energy Distribution | Report | 7895 | 0.00043634 | 22kV AC | Moorabbin Airport | 3199 | Frankston | Vehicle
During patrol of feeder PV14, Jemena crew found a tree branch had contacted the red and white phases of overhead HV conductors. Tree branch was very small and not related to any observed defect or decay. | 13 CENTREWAY, GLENROY VIC 3046 | Pole no. A093554 |  | Wind;MEC |  |  |  |  | 1 | Small tree branch failed and fell onto HV conductor. Refer to photos and JEN fault investigation form (attached in Notes and Findings) for details. There was some blackening of failed tree branch, but no fire start. | Conductor (bare) | 0 | 0 | 0 |  | PV14 | Vegetation: Trees Incident | Singeing or local charring/blackening only | 16/08/2017 9:24 |  |  | 6417 | Residential |  | 20170816JEM_01 | Infrastructure (network-based) | -37.7057 | 144.905 | 1 | Jemena | Report | 7908 | 0.027869 | 11kV AC | Essendon Airport | 3046 | Glenroy | Trees
Crew replaced EDO tube and restored supply. No evidence of fire on the ground. The EDO unit has been scheduled to be replaced with BA. | 19 HAKEA COURT, GLENGARRY NORTH VIC 3854 | 2602078 |  |  |  | Candled fuse |  |  | 0 | IMS228880 - fault crew called to all supply failure and found a EDO tube burnt, broken in half. | EDO fuse | 0 | 0 | 0 |  | TGN31 | EDO fuse tube burnt off | Pole-top fire;Loss of supply | 42742.559 | 1 | Negligible: no ground fire | 6438 | Forest - native (not park) |  | 20170824SPN_01 | Infrastructure (network-based) | -38.0962 | 146.5474 | 1 | AusNet Services Distribution | Report | 8326 | 0.024208 | 22kV AC | Morwell (Latrobe Valley Airport) | 3854 | Glengarry North | Fuse
Site made safe. burnt FOLCB replaced. | 80 BLUE RIDGE ROAD, DEWHURST VIC 3808 | 521902 |  |  |  | Defective component;Overheated connection |  |  | 0 | IMS228875 - pole fire reported by CFA. Crew sent to make safe. found the FOLCB melted. No fire or flame observed, melted plastic at the base of pole per photos attached in tab 7. | Connection box | 0 | 0 | 0 |  | BWN14 | suspected loose connection within the FOLCB | Pole-top fire;Melting or smoking only | 42742.6507 | 1 | Negligible: no ground fire | 6439 | Residential |  | 20170824SPN_02 | Infrastructure (network-based) | -37.9859 | 145.4647 | 1 | AusNet Services Distribution | Report | 7965 | 0.037981 | Low voltage AC (<1kV) | Moorabbin Airport | 3808 | Dewhurst | Connection
ENO investigated and isolated affected area for repairs to be made. | 217 REX ROAD, CAMPBELLFIELD VIC 3061 |  | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | ST34 Fdr CB Opened to Lockout - Truck transporting forklift made contact with ariel earth cable, flicking it it into overhead high voltage conductors. | Conductor (bare) | 0 | 0 | 0 |  |  | Oversized load vehicle encroaching clearances as per Green Book made contact with aerial earth. Vehicle impact caused aerial earth to break, which then made contact with centre phase overhead conductor. | No Go Zone (contact) | 25/08/2017 10:22 |  |  | 6443 |  |  | 20170825JEM_01 | Infrastructure (network-based) | -37.6524 | 144.9659 | 1 | Jemena | Report | 7970 | 0.029372 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Vehicle
Isolated the area to make safe. Krone boxes and switches have been replaced within 24 hours. | 1 ROGERS STREET, COBURG VIC 3058 |  |  |  |  | Overheated connection |  |  | 2 | East and west circuit Krone boxes melted at Rogers-Ross pole-mounted substation (pole no. A070535) Photo is unavailable for this event. | Disconnector/isolator;Connection box | 0 | 0 | 0 |  | CS13 | Overheated connection | Melting or smoking only | 30/08/2017 18:35 |  |  | 6463 | Residential |  | 20170830JEM_01 | Infrastructure (network-based) | -37.7357 | 144.966 | 1 | Jemena | Report | 8287 | 0.0017766 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Connection
On arrival crew isolated supply and commenced repairs | 71 ROUSE STREET, PORT MELBOURNE VIC 3207 | 35242860 | Working too close to underground cables | [5 empty] | 1 | Citipower fault crew attending an outage (AP014 feeder) found that an UG HV cable had been damaged at the incident locationd. The damage was done by a contractors carrying out horizontal boring operations. MOCS 12335826 and PTW 045651 & 2 on issue. There was no fire or reported injuries. | Cable | 2 | 2 | 2 |  | AP014 | Horizontal boring operations | Loss of supply;No Go Zone (contact) | 29/08/2017 9:38 |  |  | 6458 | Roadway |  | 20170830PWA_04 | Infrastructure (network-based) | -37.8439 | 144.9421 | 1 | CitiPower | Report | 8001 | 0.0054965 | 11kV AC | Essendon Airport | 3207 | Port Melbourne | Dug up
Isolated and made safe. AusNet DSO sent to inspect the site. Found the excavator operator pulled the cable up which dragged the elbows off the transformer tripping the line. The line appears to have tripped before he cut through it with the excavator, no obvious flash marks on the bucket but some on the transformer (ground type substation). the section of line supplying the quarry remains switched off pending repair (Quarry has own generator). | 452 TYERS-WALHALLA ROAD, TYERS VIC 3844 | 2720375 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS229722 - Quarry operator dug up 22KV underground cable by excavator ex Switch 5677989. ACR went to lock out sensing the fault. Isolated and made safe. | Cable | 0 | 0 | 0 |  | TGN31 | excavation | No Go Zone (contact) | 43047.6604 |  |  | 6462 |  |  | 20170830SPN_04 | Infrastructure (network-based) | -38.1249 | 146.4681 | 1 | AusNet Services Distribution | Report | 8040 | 0.0005162 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Tyers | Dug up
A faults truck was dispatched once again and removed the old single phase service for safety and 45m x three phase service is required for the reconnection. There was no one in attendance and the residence is empty as the renovation is taking place. The REC will be advised of the correct process and the reconnection will take place after the REC arranges a truck appointment. As the REC has interfered with the meter and has caused a number of site visits by United Energy employees and representatives, it was seen warranted to notify ESV of the interference. | 30 CLAUSCEN STREET, TEMPLESTOWE LOWER VIC 3107 |  | Unauthorised work | [5 empty] | 2 | 4 Aug - AMI meter No. 1115436 stopped communicating at 2.17PM. ~12 Aug - Note placed in systems stating that a REC had enquired about a supply upgrade. 15 Aug - Meter technician sent to investigate the cause of the non-communicating meter. He attended the site and found that a renovation was underway and the meter had been removed and couldn't be found anywhere at the property. He was approached by a builder who rang the REC and the technician discussed what had occurred. The REC told him the meter box was damaged and unsafe and he'd removed the meter and service fuse at the POA. This meter has stopped communicating since 4/8/17 and since then he has not notified anyone. The REC also mentioned that he's raised a mains upgrade request over a week ago for the premise from single phase to three phase. The technician checked the "damaged" meter box that looked fine with the existing meter box in place with a new paint job. Back in the office, the technician could not find any requests in United Energy systems for any upgrades and suspected the REC wasn't telling the truth and was trying to cut corners. 22 Aug - 10.58AM Builder called and advised the meter panel and meter were accidently damaged during renovations and the REC has made safe. The called advised he didn't have the REC or CES details but wanted the supply upgrade to be reconnected. A faults truck was sent to check for safety and everything was safe. 22 Aug - 4.13PM REC No. 22618 rang the United Energy faults and emergencies call centre advising that Prescribed CES No. 123033787 has been provided following LEI M. Gauci (Licence No. 980648) sign off and the site is ready for the supply reconnection after the upgrade to three phase and the CES will be left in the meter panel. | Smart meter | 0 | 0 | 0 |  |  | The REC has interfered with the meter prior to a supply upgrade and sought a reconnection through attendance by a faults truck. | No Go Zone (contact) | 15/08/2017 10:00 |  |  | 6465 | Residential |  | 20170831UTD_02 | Infrastructure (network-based) | -37.7644 | 145.1152 | 1 | United Energy Distribution | Report | 8070 | 0.0095579 | Low voltage AC (<1kV) | Essendon Airport | 3107 | Templestowe Lower | Other
Site made safe and fault crew replaced HV earthing cable. | 538 MELTON HIGHWAY, SYDENHAM VIC 3037 | Pole no. A005948 | Copper theft | [5 empty] | 2 | Jemena operator patrolling a feeder fault found HV earthing cable missing from cable head pole no. A005948 between ground level and 3 to 4 metres from the ground. No risk to public safety. | Copper;Earth/earthing | 0 | 0 | 0 |  | SHM21 | HV earth cable stolen from cable head pole no. A005948. | Damage to network assets | 42775.2181 |  |  | 6473 | Roadway |  | 20170902JEM_01 | Infrastructure (network-based) | -37.694 | 144.7629 | 1 | Jemena | Report | 8087 | 0.027404 | 22kV AC | Melbourne Airport | 3037 | Sydenham | Other
Dispatched fault crew to isolate make safe investigate and repair. | 1900 BONANG ROAD, DELEGATE RIVER VIC 3888 | 5768315 |  | Wind;Fallen |  |  |  | Phase to earth |  | IMS230123 - Report of wire down in paddock and a small fire 50x60 meters in the vicinity of wire down reported by CFA | Conductor (bare) | 0 | 0 | 0 |  | BM8B31 | Vegetation: Trees Incident | Grassfire | 42803.5868 | 1 | Medium: 1000 sq.m - 10 ha | 6481 | Agricultural |  | 20170904SPN_01 | Infrastructure (network-based) | -37.0607 | 148.8014 | 1 | AusNet Services Distribution | Report | 8096 | 0.015304 | 22kV AC | Gabo Island Lighthouse | 3888 | Delegate River | Trees
The faults crew attended and dropped the single phase overhead service from pole No. LIS 1303725 and issued a defect notice. The faults crew also left a card with the defect notice stating that photos were taken and will be passed on to ESV as live (covered) wires could have been touched by a member of the public. 29/08/2017 - REC No. 20077 (Marcus 0419 309 112) provided Prescribed CES No. 15437822 after he installed a new FMJB and meter board. A faults truck attended and reconnected the single phase XLPE overhead service and re-installed the existing meter in the new meter box. Installation tests were completed and supply was left on. | 10 WALBROOK ROAD, RYE VIC 3941 | 1303275 | Unauthorised work;Caused by REC/contractor | [5 empty] | 2 | Caller (0419 309 112) is reporting the overhead fuse box at the POA is hanging down but still connected by the cable. 28/08/2017 - The premise is under renovation and the REC has unmounted the FMJB at the POA and then stated it was unsafe to arrange for a faults truck to attend and issue a defect notice to avoid the costs associated with a truck appointment. | Service conductor;Aluminium twisted (XLPE);Smart meter | 0 | 0 | 0 |  |  | The premise is under renovation and the REC has unmounted the FMJB at the POA and then stated it was unsafe. Live (covered) wires could have been touched by a member of the public. | No Go Zone (contact);Damage to network assets | 28/08/2017 14:00 |  |  | 6479 | Residential |  | 20170904UTD_05 | Infrastructure (network-based) | -38.376 | 144.7917 | 1 | United Energy Distribution | Report | 8093 | 0.041076 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Other
On arrival crew carried out repairs | 123 MERRIVALE DRIVE, WARRNAMBOOL VIC 3280 | 30136387 | Vehicle | [6 empty] | It was reported a vehicle hit and bought down a powerline at the incident location. On arrival the crew found that a Low Voltage (service had been hit by a truck , resulting in it breaking and coming to ground. There was no reported fire, no reported injuries or other third party property damage. | Service conductor | 2 | 2 | 2 |  | WBL004 | Truck struck service | Loss of supply;Damage to network assets | 18/08/2017 13:41 |  |  | 6493 | Roadway |  | 20170907PWA_01 | Infrastructure (network-based) | -38.3793 | 142.4594 | 1 | Powercor | Report | 8116 | 0.0053472 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
On arrival crew isolated supply and carried our repairs | 156 LOWER DARLINGTON ROAD, DUVERNEY VIC 3323 | 30055834 |  | Lightning |  | Corrosion;Mechanical breakdown |  |  | 1 | Powercor was contacted by a customer reporting conductor has hit the ground. A crew was dispatched to investigate. On arrival, the crew found that 4 spans of SWER conductor were on the ground between Pole 6 and Pole 11 DUVERNEY spur. The break occurred mid span between Pole 10 and Pole 11. There was no fire, no reported injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | CLC003 | Past lightning damage indicated by crew | Loss of supply | 16/08/2017 13:21 |  |  | 6499 | Agricultural |  | 20170908PWA_02 | Infrastructure (network-based) | -38.0244 | 143.564 | 1 | Powercor | Report | 8264 | 0.0048032 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3323 | Duverney | Conductor
On arrival crew isolated supply and commenced repairs | LEURA LEE, 2976 PRINCES HIGHWAY, PORT FAIRY VIC 3284 | 30135294 |  |  |  | Corrosion |  |  |  | The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt and the CFA had extinguished it. The centre phase tie had broken allowing conduction to fall onto cross arm. There was no ground fire, no injuries or third party property damage There were no photos taken at the incident site. | Crossarm (wood) | 2 | 2 | 2 |  | KRT013 | Broken HV Tie | Pole-top fire | 20/08/2017 7:36 | 1 | Negligible: no ground fire | 6500 | Roadway |  | 20170908PWA_03 | Infrastructure (network-based) | -38.3834 | 142.1691 | 1 | Powercor | Report | 8133 | 0.014866 | 22kV AC | Warrnambool Airport Ndb | 3284 | Port Fairy | Pole
A faults truck attended and ensured the failed Capacitor Bank was isolated and the crew will advise the depot to have the Capacitor Bank replaced. | 114 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7050090 |  |  |  | Fatigue |  |  | 1 | Pole fire per MFB outside the cemetery and they are on their way. At 7.29PM on 31/08/2017, Capacitor Bank "Burwood-Millicent" installed on pole No. LIS 7050090 outside the Reece Hardware store exploded/faulted that resulted in the three Boric Acid fuses operating. The timber pole was slightly burnt adjacent to the star point connections and the cause of the fault was unknown. | Any other type | 1 | 1 | 0 |  | BW 22 | At the time of the fault, the cause was unknown. | Pole-top fire | 31/08/2017 19:29 | 1 | Negligible: no ground fire | 6496 | Roadway |  | 20170908UTD_01 | Infrastructure (network-based) | -37.8508 | 145.0999 | 1 | United Energy Distribution | Report | 12954 | 0.011968 | 11kV AC | Moorabbin Airport | 3125 | Burwood | AF Other
10 x 3 phase industrial/commercial properties on circuit isolated. Techsafe inspector onsite and confirmed high voltage injection incident. Fault crew assisted to disconnect customer premises for inspector to check for damage. All distribution metering equipment and installation switchboards and appliances at accessible properties were inspected for evidence of damage and reconnected. Damage cards were issued as required. | 348 ARDEN STREET, KENSINGTON VIC 3031 |  |  | Wind |  | Conductor clashing |  |  | 2 | LV street lighting circuit came into contact with 66kV conductors above during high winds. Blue phase of the LV affected. TechSafe EIO incident report is attached in "Notes & Findings" section. | Conductor (bare);Conductor (insulated) | 0 | 0 | 0 |  | FT06 | High winds caused street light service to clash with 66KV line. | HV injection;Less than $50k damage | 18/09/2017 12:37 |  |  | 6520 | Commercial |  | 20170918JEM_05 | Infrastructure (network-based) | -37.7993 | 144.9354 | 1 | Jemena | Report | 8302 | 0.027171 | Low voltage AC (<1kV);66kV AC | Essendon Airport | 3031 | Kensington | Other
Crew disconnected the overhead service to the BTS. | 126 RENNIE STREET, COBURG VIC 3058 |  | Unauthorised access | [5 empty] | 2 | Unknown persons relocated an overhead service from residential dwelling to a BTS. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Unknown persons relocated overhead service to BTS. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/09/2017 12:04 |  |  | 6521 |  |  | 20170919JEM_01 | Infrastructure (network-based) | -37.7518 | 144.9777 | 1 | Jemena | Report | 8162 | 0.022544 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
The crew made the site safe, the meter panel and associated equipment was replaced and supply was restored. | 420 THWAITES ROAD, WINSLOW VIC 3281 | 32195765 |  |  |  | Corrosion |  |  |  | The CFA reported a fire in the meter board at their dairy at the incident location. On arrival the Electrical Inspector found that a Low Voltage fuse/s has failed and caused the meter panel including the meter to catch fire. There was no ground fire. No third party damage and no injury was reported. | Smart meter;Meter board (including fuses) | 2 | 2 | 2 |  | KRT012 | Overheated connection | Meter board | 17/09/2017 8:57 | 1 | Negligible: no ground fire | 6536 | Industrial |  | 20170926PWA_05 | Infrastructure (network-based) | -38.2526 | 142.4165 | 1 | Powercor | Report | 8184 | 0.040887 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3281 | Winslow | Fuse
Advised Tom Mahony not to work within 2000mm of cables, install barriers and signage to ensure. CitiPower processing Sag / Sway and Asset Relocation required to achieve clearances | 38 LYNDHURST STREET, RICHMOND VIC 3121 | 30192370 | Building too close or within the No Go Zone | [5 empty] | 2 | Builder requested site visit to confirm clearances present. Citipower representative found Residential Building extension framework pushed up to approx. 700mm adjacent to low voltage conductors between Lis 279 & 280 on Abinger St frontage. | Conductor (bare) | 0 | 0 | 0 |  | NR022 | Interference - building too close to line | No Go Zone (no contact) | 42924.6403 |  |  | 6544 | Residential |  | 20170927PWA_05 | Infrastructure (network-based) | -37.8201 | 145.0004 | 1 | CitiPower | Report | 8192 | 0.040697 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Other
Reported as breach | 114 HODDLE STREET, ABBOTSFORD VIC 3067 | 30167852 | Building too close or within the No Go Zone | [5 empty] | 2 | CitiPower identified that a scaffold had been dismantled in contravention of the instructions in the issued permit to work | Service conductor | 0 | 0 | 0 |  | CW009 | Non compliance to permit conditions | No Go Zone (no contact) | 14/08/2017 14:34 |  |  | 6552 | Construction |  | 20170927PWA_11 | Infrastructure (network-based) | -37.8049 | 144.9925 | 1 | CitiPower | Report | 8200 | 0.014159 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | Other
Crew Isolated supply to make repairs to damaged cable, after visual inspection individual cores re-insulated and outer insulation re-sealed. Supply restored no cable joints required. | 1133 MALDON-NEWSTEAD ROAD, MALDON VIC 3463 | 33025178 | Working too close to underground cables | [6 empty] | A Central Power Crew attended and found directional bore unit had damaged LV 120mm sa x Underground Cable conduit at the incident location. MOCS onsite but details not noted. No Fire, No personal damage or shocks reported. | Cable | 2 | 2 | 2 |  | CMN004 | Directional boring | Damage to network assets | 42775.4736 |  |  | 6555 | Public space |  | 20170928PWA_03 | Infrastructure (network-based) | -37.0146 | 144.0641 | 1 | Powercor | Report | 8205 | 0.018185 | Low voltage AC (<1kV) | Bendigo Airport | 3463 | Maldon | Dug up
Upon inspection crew found that there had been a flashover behind meter this had caused blackening of the meter board and the wiring, this was only superficial. The installation inspected by LEI. Supply was restored to the customer | 108 HIGH STREET, WEDDERBURN VIC 3518 | 30019975 |  | Bird |  |  |  |  | 2 | Customer called to advise no supply and blackened meter. There was no other damage to assets or private property. | Connection to meter;Customer installation | 2 | 2 | 2 |  | CTN002 | Suspected the cause was due to a build-up of small ants under the meter cover which resulted in a flashover. | Loss of supply;Singeing or local charring/blackening only | 43016.3958 |  |  | 6564 | Residential |  | 20171003PWA_02 | Infrastructure (network-based) | -36.4149 | 143.6107 | 1 | Powercor | Report | 8214 | 0.012069 | Low voltage AC (<1kV) | Bendigo Airport | 3518 | Wedderburn | Animal
On arrival crew isolated supply and carried out repairs. | 6 KAWANA COURT, HOPPERS CROSSING VIC 3029 | 30119260 | Vehicle | [6 empty] | A customer advised a truck has dislodged a service wire at the incident location. There was no injuries or fire. | Service conductor | 2 | 2 | 2 |  | LV001 | Truck struck service line | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 14/09/2017 13:15 |  |  | 6567 | Residential |  | 20171003PWA_04 | Infrastructure (network-based) | -37.8576 | 144.6825 | 1 | Powercor | Report | 8217 | 0.0017569 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Vehicle
The attending faults crew isolated and replaced the damaged FOLCB and the neutral LV pin and insulator that was damaged as a result of the fire. Supply was restored to the affected customers upon completion. The faults crew were unable to replace the overhead service to number 7 as the POA is obstructed by the veranda. A defect notice was issued advising that a REC is required to complete repairs before supply can be restored. 29/09/2017 - REC No. 24897 provided non-prescribed CES No. 231203553 after the veranda was removed and the service hook relocated to allow unhindered access to the POA. A new single phase service was installed and supply reconnected following the completion of installation tests. | 8 TADJI STREET, SORRENTO VIC 3943 | 1306299 |  | Precipitation |  | Corrosion |  |  | 2 | Caller reports the top of the pole is on fire outside 8 Tadjui Street and the CFA haven't been called. During cool and damp conditions, a three phase FOLCB installed on an LV ABC intermediate pole No. LIS 1306299 located outside 8 Tadji Street, Sorrento caught on fire and melted due to probable corrosion as the pole is situated a short distance from Port Phillip Bay. The FOLCB ignited that caused debris to fall to the ground but no ground fire started. | Connection box | 0 | 0 | 0 |  |  | Probable corrosion as the pole is situated a short distance from Port Phillip Bay. | Pole-top fire | 28/09/2017 13:37 | 1 | Negligible: no ground fire | 6566 | Roadway |  | 20171003UTD_03 | Infrastructure (network-based) | -38.3547 | 144.7599 | 1 | United Energy Distribution | Report | 12955 | 0.038234 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Pole
The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the Fused Overhead Mains Connection Box and completed an NST test which confirmed a Pass result. | 13 NICHOLSON STREET, WARRNAMBOOL VIC 3280 | 33101725 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Lyn Wilson was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WBL008 | corroded service connection | Minor shock | 31/08/2017 0:00 |  |  | 6590 | Residential |  | 20171004PWA_07 | Infrastructure (network-based) | -38.389 | 142.499 | 1 | Powercor | Report | 8242 | 0.00514 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
HV supply to isolated | 383 BOUNDARY ROAD, TRUGANINA VIC 3029 | 30244411 | Copper theft | [5 empty] | 2 | Operator was accessing control box at Boundary 105 HV Capacitor for planned works from a pup ladder. Operator experienced a tingle when contacting the control box. Upon closer inspection it was identified that the earth on the structure had been cut and stolen. | Earth/earthing | 0 | 0 | 0 |  | LVN024 | Suspected -Stray potential due to undetected stolen earthing cable. | Minor shock;Damage to network assets | 42926.3458 |  |  | 6606 | Roadway |  | 20171010PWA_01 | Infrastructure (network-based) | -37.8119 | 144.7639 | 1 | Powercor | Report | 8266 | 0.0092037 | Control circuit;Other | Laverton Raaf | 3029 | Truganina | Other
A faults crew promptly attended and isolated supply to the transformer and the CFA were on site and extinguished the fire. Repairs were completed to the electrical infrastructure and supply restored upon completion. | 1 SOUTH BOUNDARY ROAD E, SOMERVILLE VIC 3912 | 9498509) |  | Prone to deposition of faecal matter |  | Moisture ingress;Fatigue |  |  | 1 | At 1042hrs on 05/10/2017, 22kV ACR FS7877 located in Government Road opened to lockout as the reclose function was suppressed with live line sequence enabled for Application No. 111929 as a Downer glove and barrier crew were installing armour rods, vibration dampers and bushing covers on LWN 21. A stay wire rod rusted below ground level and subsequently pulled out of the ground that caused the substation pole (LIS No. 9498509) to slightly lean in the soft ground and the stay wire to make contact with a lightning arrestor at "Mealy-South Boundary" pole type substation. Tracking occurred that caused a small smouldering fire between the inside of the timber pole to the HV earth on the outside of the pole. | Guy wire;Outdoor | 0 | 0 | 0 |  | LWN 21 | The cause was attributed to the pole type substation being located near a water facility in a paddock for cows with substantial effluent surrounding the pole area. In addition, a large amount of cow hair was found on the stay wire and it appeared the cows had been rubbing on the stay wire. | Pole-top fire | 42865.4458 | 1 | Negligible: no ground fire | 6610 | Agricultural |  | 20171012UTD_01 | Infrastructure (network-based) | -38.2231 | 145.2488 | 1 | United Energy Distribution | Report | 8272 | 0.03714 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Animal
crew attended and replaced cross arm | 29 HIGHVIEW ROAD, BALWYN NORTH VIC 3104 | 30179954 |  |  |  | Rot |  |  | 1 | A customer reported arcing sound and loud bang from a pole out the front of their property. On arrival the crew found that the wooden HV Cross-Arm had broken and a HV conductor had contacted the LV bare conductor causing HV injection. | Conductor (bare) | 0 | 0 | 0 |  | WD011 | deteriorated cross arm | HV injection;Loss of supply | 43049.9514 |  |  | 6614 | Residential |  | 20171013PWA_01 | Infrastructure (network-based) | -37.7813 | 145.08 | 1 | CitiPower | Report | 8279 | 0.028475 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3104 | Balwyn North | Crossarm
High voltage injection suspected but no damage found (over 100 customers checked). Crew carried out repairs to conductors. | 39 KEES ROAD, LARA VIC 3212 | 30071450 |  | Fallen;Council |  |  |  |  | 1 | Local resident (Maria) reported that a tree branch has fallen across the high voltage overhead line one phase has broken and a small ground fire at the incident location. On arrival the fault crew found that a branch from a large tree towering over the line had broken off, falling onto the high voltage overhead breaking the outer phase conductor which then fell onto the low voltage circuit below. There was no injury as result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | FNS012 | Vegetation: Trees Incident | Loss of supply;Grassfire | 18/10/2017 13:20 | 1 | Localised: less than 10 sq.m | 6619 | Roadway |  | 20171019PWA_01 | Infrastructure (network-based) | -38.0187 | 144.3918 | 1 | Powercor | Report | 12587 | 0.020738 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3212 | Lara | Trees
A REC replaced the burnt out consumers mains box at the POA and contacted the United Energy faults and emergencies call centre for a reconnection. A faults truck attended and found the old single phase consumers mains box with live service tails still hanging by the drip loop and a new mains box installed on the facia board. The two man crew had concerns the REC had completed the work unsafely and suggested that ESV are advised. They proceeded to reconnect the customer and took photos and advised their supervisor. | 3 FINTONIA ROAD, NOBLE PARK VIC 3174 |  | Caused by REC/contractor |  |  | Fault on customer installation |  |  | 2 | 3.42PM - AMI meter at the property communicated a last gasp. 5.55PM REC 13777 advised the customer contacted him for an all supply failure and the REC identified the consumers mains box was burnt out at the POA. REC advised that he unscrewed the defective mains box and installed a new one in its place. Wires are still connected to the old box and he has left non prescribed CES 509613794 on site. | Service conductor | 0 | 0 | 0 |  |  | REC infringement with live overhead service cable (interference with assets). | No Go Zone (contact) | 13/10/2017 17:55 |  |  | 6628 | Residential |  | 20171023UTD_01 | Infrastructure (network-based) | -37.9658 | 145.185 | 1 | United Energy Distribution | Report | 8305 | 0.0040764 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Other
Site made safe. Pole replaced and new conductor run. | 102 BARRY ROAD, CAMPBELLFIELD VIC 3061 | A041818 | Vehicle | [5 empty] | 2 | Long oversized truck with trailer contacted pole guy wire and snapped top of pole. This resulted in HV bare conductors on the ground. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Truck impacted pole guy wire with enough force to snap the top off the pole. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43018.1514 |  |  | 6633 | Roadway |  | 20171024JEM_01 | Infrastructure (network-based) | -37.668 | 144.9676 | 1 | Jemena | Report | 8333 | 0.008184 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Vehicle
On arrival crew carried out repairs | 438-456 BALLARAT ROAD, SUNSHINE NORTH VIC 3020 | 30120176 |  | Wind |  | Conductor clashing |  |  | 1 | The control room reported that a HV wire was down between Ballarat West-Moreland & Ballarat-Harvester substations . On arrival the attending crew found that a high voltage conductor was laying on the ground over the road, the HV conductor had broken near the connector dropper assembly of a non-switched cable head at pole LIS-017831. Protection operated as expected There was no fire, injuries or third property damage. | Conductor (bare) | 2 | 2 | 2 |  | SSE032 | Attributed to conductor movement during high wind event | Loss of supply | 23/09/2017 23:42 |  |  | 6635 | Roadway |  | 20171024PWA_01 | Infrastructure (network-based) | -37.7777 | 144.8367 | 1 | Powercor | Report | 8319 | 0.023735 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Other
On arrival the crew carried out repairs | 54 FINDLAY STREET, STRATHMERTON VIC 3641 | 32181172 | Working too close to overhead lines | [6 empty] | An company employee from NGH Earthmoving reported the service wire across from the school had been hit and broken in half at the incident location. There was no other reported third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | NKA003 | Excavator struck service | Loss of supply;Damage to network assets | 28/09/2017 14:00 |  |  | 6640 | Roadway |  | 20171025PWA_02 | Infrastructure (network-based) | -35.9244 | 145.4779 | 1 | Powercor | Report | 8324 | 0.034235 | Low voltage AC (<1kV) | Shepparton Airport | 3641 | Strathmerton | Dug up
On arrival crew carried out repairs | 1-11 LARNEUK STREET, NORTH SHORE VIC 3214 | 32080982 | Vehicle | [5 empty] | 2 | A customer reported that a truck has struck a wire and the wire has broken and on the ground at the incident location. On arrival the crew found that a tip Truck) was exiting the site and contacted an LV service cable causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | CRO022 | Tip Truck Struck service line | Loss of supply;Damage to network assets | 42835.509 |  |  | 6642 | Roadway |  | 20171025PWA_04 | Infrastructure (network-based) | -38.0954 | 144.3675 | 1 | Powercor | Report | 8327 | 0.018233 | Low voltage AC (<1kV) | Avalon Airport | 3214 | North Shore | Vehicle
The crew made the site safe, and replaced the pole. | MALLEE HIGHWAY, OUYEN VIC 3490 | 32153108 |  |  |  | Leakage |  |  | 2 | A customer (Andrew) reported a pole down at the incident location. On arrival the crew found that a pole fire the pole appears to have burnt from the base upward and was laying on the ground. The crew also reported there was no ground fire. Third party damage in the form of a dead sheep was found by the crew. No injury was reported. | Pole (wood) | 2 | 2 | 2 |  | OYN003 | Excessive leakage current | Pole-top fire;Fatality of livestock, pet or companion animal | 13/10/2017 9:40 | 1 | Negligible: no ground fire | 6653 | Agricultural |  | 20171030PWA_02 | Infrastructure (network-based) | -35.0522 | 142.5048 | 1 | Powercor | Report | 8339 | 0.020905 | 22kV AC | Mildura Airport | 3490 | Ouyen | Pole
The pole was replaced, conductors were repaired and supply was restored. | BALLARAT-DAYLESFORD ROAD, NEWLYN VIC 3364 | 30356218 | Vehicle | [5 empty] | 1 | A report was received from Vic Pol that a car had hit a pole in Ballarat-Daylesford Road Dean. On arrival the crew found that a car had hit Dean Pole 35. The impact resulted in the pole breaking in half and also caused the HV conductors to break and come to rest on the ground. The driver only sustained minor injuries and was taken to hospital for checks. There was no shock or fire | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | BAN008 | Vehicle struck pole | Loss of supply;Damage to network assets | 42988.809 |  |  | 6656 | Roadway |  | 20171031PWA_02 | Infrastructure (network-based) | -37.4456 | 143.9814 | 1 | Powercor | Report | 8343 | 0.011272 | 22kV AC | Ballarat Aerodrome | 3364 | Newlyn | Vehicle
Supply was isolated at "Howard-Cole" substation and the white and blue phase LV conductors were repaired with supply restored upon completion. An investigation commenced to determine why the LV fuses failed to operate at the time of the fault. The investigation revealed there were 315amp DIN fuses installed and the conductors involved are 19/3.25 AAC and 192m in length from the 315kVA "Howard Cole" pole substation. According to the Design Standard, the 315amp LV fuses should operate up to 290m in length. At the location of the fault, approximately 10m of the felled blue phase conductor was laying partly on concrete and grass. The cause of the fuses to operate was therefore inconclusive and the faults crew returned the following day to determine if any LV parallels were installed but the circuit was found to be normal. | 11 HOWARD STREET, GLEN IRIS VIC 3146 | 2310568 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 0 | Caller reports a pole and wires down in Howard Road, Glen Iris and emergency services are on their way. A truck operator working for Lombardi Concreting has raised his tip truck into the LV conductors and contacted the white and blue phase LV conductors outside 11 Howard Street causing the blue phase conductor to fall to the ground. The LV fuses at the east circuit from "Howard-Cole" substation failed to operate and the conductor remained live on the ground. There was no poles on the ground as indicated in the initial customer calls and no injuries received. | Conductor (bare) | 0 | 0 | 0 |  |  | A truck operator working for Lombardi Concreting has raised his tip truck into the LV conductors. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/10/2017 12:35 |  |  | 6671 | Roadway |  | 20171103UTD_02 | Infrastructure (network-based) | -37.8552 | 145.0652 | 1 | United Energy Distribution | Report | 9745 | 0.020919 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor of a Neutral Screened O/H Service Cable as the cause of the high impedance associated with the return path of the neutral current. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Aluminium Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 2 42 FIFTH STREET, NICHOLS POINT VIC 3501 | 32140931 |  |  |  | Corrosion |  | Phase to earth | 2 | Miss Ebony Greenhill was in the Bathroom showering at the time she received an electric shock when she simultaneously contacted the metallic water tap with her right hand and her bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | MDA024 | Corroded neutral service connection | Minor shock | 23/09/2017 8:00 |  |  | 6687 | Residential |  | 20171109PWA_05 | Infrastructure (customer connection) | -34.2022 | 142.193 | 1 | Powercor | Report | 8377 | 0.035992 | Low voltage AC (<1kV) | Mildura Airport | 3501 | Nichols Point | Connection
Electrical inspector attended site, isolated property and waited for operator to return to restore the LV before further assessing for any equipment damage as a result of high voltage injection. Supply was restored after Electrical inspector assessed that it was safe to restore supply. | 90 MT RIDLEY ROAD, MICKLEHAM VIC 3064 | Pole no. A006039 |  | Animal |  | HV injection |  |  | 1 | Centre phase HV fuse unit blew at pole number A006039. Street light mounted to same pole had blown. The one customer connected to the LV from the pole (Yarra Valley Water) had sustained damage from high voltage injection. Equipment with sustained damage include several surge arrestors, phase monitoring relay, telemetry radio and loop isolators. TechSafe report attached in "Notes & Findings" section. | Boric acid | 0 | 0 | 0 |  | KLO22 | Animal Incident | HV injection | 43019.2347 |  |  | 6691 | Peri-urban |  | 20171110JEM_01 | Infrastructure (network-based) | -37.5688 | 144.9343 | 1 | Jemena | Report | 8488 | 0.0090937 | 22kV AC | Melbourne Airport | 3064 | Mickleham | Conductor
Voltage test with an independent earth and various parts of the electrical installation including the Powercor assets, revealed a severely corroded service connector (including neutral service conductor) at the pole end. Existing service re-terminated into new service connectors at pole end by Powercor faults truck. NST test at customers POA by Faults Crew passed OK. NST test at customers main Switchboard by CTA passed OK. No stray voltages detected by CTA. | 5 OLD MIDLAND HIGHWAY, MOUNT ROWAN VIC 3352 | 33006679 |  |  |  | Corrosion |  | Phase to earth | 2 | Liliah received an electric shock whilst she was siting in the bath and simultaneously contacting the water taps with her wet hands. | Service conductor | 2 | 2 | 2 |  | BAN009 | Corroded service connection | Minor shock | 26/09/2017 10:00 |  |  | 6688 | Residential |  | 20171110PWA_01 | Infrastructure (network-based) | -37.5134 | 143.8473 | 1 | Powercor | Report | 8400 | 0.0077095 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Connection
On arrival crew extinguished fire and made site safe | 541 W SCHULTZ ROAD, HAMILTON VIC 3300 | 33058168 |  | Bird |  |  |  |  | 1 | A Powercor crew were patrolling following a 66kV fault, and reported a fire at the incident location. On arrival the crew found that an Ibis had caused a flashover on a 66kV pole and fallen to the ground starting a grassfire of approx. 200m2 of mostly road reserve, with a small area of private land burnt and minor fence damage. The crew extinguished the fire, the CFA did not attend. There were no injuries or other damage reported. | Conductor (bare) | 2 | 2 | 2 |  | NRB - HTN | Bird Incident | Grassfire | 43050.4535 | 1 | Small: 10 - 1000 sq.m | 6697 |  |  | 20171113PWA_04 | Infrastructure (network-based) | -37.7586 | 142.1122 | 1 | Powercor | Report | 8414 | 0.026306 | 66kV AC | Hamilton Airport | 3300 | Hamilton | Animal
Crew made site safe and removed the offending umbrella from the high voltage conductors. The high voltage conductors were upgraded and replaced. | 6 MARAMA STREET, COBURG NORTH VIC 3058 |  | Unknown external/community factor;Blown detritus | Wind |  |  |  |  | 1 | An umbrella blew into high voltage conductors causing them to fall to the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Jemena work crew found umbrella in the HV conductors. Unknown third party or wind caused an umbrella to contact/go into HV conductors. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/11/2017 18:03 |  |  | 6701 | Roadway |  | 20171114JEM_01 | Infrastructure (network-based) | -37.7199 | 144.9588 | 1 | Jemena | Report | 9803 | 0.02695 | 22kV AC | Essendon Airport | 3058 | Coburg North | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded U/G Service Neutral Conductor termination at the Connection Box located at the Reticulation Pole. The Powercor Fault Crew replaced the Connection Box at the O/H Reticulation Pole, re-terminated the Underground Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 8 KORONG COURT, CLIFTON SPRINGS VIC 3222 | 30058425 |  |  |  | Corrosion |  | Phase to earth |  | Mr Brandon Aird (Plumber) was installing metallic ductwork underneath the house when he received an electric shock as he made simultaneous contact with his hand on the conductive Hot Water Pipe and his body in contact with the damp ground. | Connection box | 2 | 2 | 2 |  | DDL022 | Corroded neutral in connection box | Minor shock | 42987.5007 |  |  | 6704 | Residential |  | 20171114PWA_01 | Infrastructure (network-based) | -38.1567 | 144.5503 | 1 | Powercor | Report | 8590 | 0.026829 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | Connection
Crew found birds nest on sw BW237 has caused a fire and burnt out all 6 LA's. No fire occurred on the ground. LA's now removed and both feeders restored. New LA's required at a later date. No relevant photos. | 108-110 ROBJANT STREET, HAMPTON PARK VIC 3976 | 505186 |  | Bird |  |  |  |  | 2 | IMS 230821 - Bird nest caused fire on top of the gas switch open point BW2237. | Disconnector/isolator | 0 | 0 | 0 |  | HPK23 | Bird Incident | Pole-top fire | 19/10/2017 11:17 | 1 | Negligible: no ground fire | 6708 | Residential |  | 20171114SPN_03 | Infrastructure (network-based) | -38.037 | 145.249 | 1 | AusNet Services Distribution | Report | 15190 | 0.027808 | 22kV AC | Moorabbin Airport | 3976 | Hampton Park | Animal
On arrival crew confirmed site safe and commenced repairs | 62 FITZGERALD ROAD, LAVERTON NORTH VIC 3026 | 33074960 | Working too close to overhead lines | [5 empty] | 1 | Report received that an excavator had hit a pole on the north side of the Federation Trail, at the back of the Onesteel recycling facility in Fitzgerald Rd, Laverton North. Upon arrival the fault crew found that the excavator which was operating and moving around the scrap metal yard had contacted and hooked up the supervisory cable spanning between LIS-29740 and LIS-29741. Being dark, the excavator operator may not have noticed that contact was made with the supervisory cable, and therefore continued in his forward direction, which resulted in the 66kV anchor pole at LIS-29740 moving within the ground from its base, and nearly coming to ground due to the supervisory cable remaining hooked up as the excavator continued in a forward direction. This also resulted in the 66kV conductors between the two poles almost coming to ground, at which time it was identified that the excavator operator had made contact with our assets. There was no contact by plant with the 66kv conductors. Marker buoys are also installed along this span to warn plant operators of the line. There was no fire, no reported injuries or third party property damage. | Communication cable/equipment | 2 | 2 | 2 |  | ATS SCI | Excavator contacted supervisory cable | No Go Zone (contact);Damage to network assets | 19/10/2017 20:29 |  |  | 6714 | Industrial |  | 20171117PWA_01 | Infrastructure (network-based) | -37.8332 | 144.7847 | 1 | Powercor | Report | 8446 | 0.031674 | Supervisory cable;Other | Laverton Raaf | 3026 | Laverton North | Vehicle
A LEI and faults truck attended and isolated the underground supply to the property at the underground electricity pit supplied from pole No. LIS 7029132. The underground cable route label in the meter enclosure was in poor condition but showed the cable adjacent the fence line and an inspection of the cable depth found it was buried at 460mm. A defect notice was issued to the customer and a REC was to attend and complete the cable repairs before the electricity supply can be restored. Worksafe were advised but did not class this as a notification event and didn't attend. | 120A WOODHOUSE GROVE, BOX HILL NORTH VIC 3129 | 7029132 | Working too close to underground cables |  |  | Fault on customer installation |  | Phase to earth | 2 | Caller advised the underground cable in the front yard of the premise (near the gas meter) was hit with a crow bar. The worker received an electric shock and was taken to hospital in an ambulance. An employee of Allgas Plumbing was excavating by hand below an existing gas meter to allow a new gas lead in to be installed. During his work he was using a 6 foot crow bar and penetrated the underground consumers mains within the property and received an electric shock. The Allgas crew ensured the victim was okay and there was no need for first aid, but an ambulance was called and he was checked out by paramedics and transported to Box Hill hospital for observation. United Energy was notified and a faults truck sent to isolate the damaged underground consumers mains. * United Energy notified Energy Safe Victoria via Loc Vuong as the incident phone line rang out on two occasions. | Customer installation | 0 | 0 | 0 |  |  | The employee was excavating by hand below an existing gas meter to allow a new gas lead in to be installed using a 6 foot crow bar when he penetrated the underground consumers mains cable and received an electric shock to his hand. | Minor shock;Medical attention (first aid/doctor/hospital) | 14/11/2017 8:38 |  |  | 6720 | Residential |  | 20171117UTD_03 | Infrastructure (network-based) | -37.8024 | 145.1304 | 1 | United Energy Distribution | Report | 8454 | 0.027361 | Low voltage AC (<1kV) | Moorabbin Airport | 3129 | Box Hill North | Dug up
Site made safe, both high and low voltage switches opened. Defect notice issued to customer. | 68-72 MCARTHURS ROAD, ALTONA NORTH VIC 3025 | 32164586 | Copper theft | [6 empty] | A R.E.C (Vito Serratore, mobile: 0418518484) reports that this factory has been burgled and all copper cables and bus bars have been cut and removed all the way back to the substation. Supply lost to factory. There was no fire or reported injuries | Pole mounted | 2 | 2 | 2 |  | BLT017 | Theft | Loss of supply;Damage to network assets | 13/10/2017 13:00 |  |  | 6740 | Industrial |  | 20171122PWA_02 | Infrastructure (network-based) | -37.8346 | 144.8375 | 1 | Powercor | Report | 8480 | 0.025492 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3025 | Altona North | Other
Section was isolated and repairs initiated by Jemena work party. | 91-109 ESSEX STREET, WEST FOOTSCRAY VIC 3012 |  | Recreation - Helium (party) balloons |  |  |  |  | Phase to phase | 1 | Feeder FW17 unsuccessful reclose. Evidence of splashing across the HV fuse units and the LV bus at pole substation Blandford-Essex. Closer inspection found evidence of metallic balloons and streamers. Section was isolated and repairs initiated by Jemena work party. Molten debris fell onto parked car causing damage to paintwork and sunroof. Photos attached in "Notes & Findings" section. | Conductor (bare);Boric acid | 0 | 0 | 0 |  | FW17 | Evidence of splashing across the HV fuse units and the LV Bus at Blandford-Essex substation. Metallic balloons came in contact with HV feeder FW17 at pole substation BLANDFORD-ESSEX. | Loss of supply;Less than $50k damage | 23/11/2017 10:49 |  |  | 6751 | Public space |  | 20171123JEM_02 | Infrastructure (network-based) | -37.7937 | 144.8768 | 1 | Jemena | Report | 8493 | 0.022633 | 22kV AC | Essendon Airport | 3012 | West Footscray | Other
SIte visited 19/10/2017 | 16 BERRY STREET, CLIFTON HILL VIC 3068 | 30169046 | Building too close or within the No Go Zone | [6 empty] | Scaffold erected in breach of VESI Guidelines. -Building appears non-compliant to Table 313. -Builder advised by Work Safe to contact Citipower re Scaffold erected. -Builder advised Work Safe inspector had approved Scaffold to Work Safe requirements but Citipower needed to approve. | Conductor (bare) | 2 | 2 | 2 |  | F029 | No go zone breach | No Go Zone (no contact) | 19/10/2017 0:00 |  |  | 6757 | Commercial |  | 20171124PWA_01 | Infrastructure (network-based) | -37.7895 | 144.9977 | 1 | CitiPower | Report | 9703 | 0.017442 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Clifton Hill | Other
Jemena crew arrived on site, isolated supply and replaced pole on the same day as incident | HEIDELBERG FOOTBALL CLUB, 5 BEVERLEY ROAD, HEIDELBERG VIC 3084 | Pole no. A115292 | Vehicle | [5 empty] | 2 | Car hit pole no. A115292 resulting in live bare LV wires down Pole is damaged and requires replacement | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | HB23 | Car hit pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/11/2017 10:26 |  |  | 6763 | Roadway |  | 20171127JEM_02 | Infrastructure (network-based) | -37.7558 | 145.073 | 1 | Jemena | Report | 8510 | 0.033627 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Heidelberg | Vehicle
On arrival crew isolated supply and commenced repairs | 1175 ROSEBERY-RAINBOW ROAD, BEULAH VIC 3395 | 32109148 |  | Within clearances |  |  |  |  | 1 | A Powercor LSA crew attended a reported fire at the incident location. On arrival the crew found that a cactus bush centre runner had caused a HV conductor to break and fall to the ground starting a grassfire of approx 100 acres of private grass land. The CFA extinguished the fire. There were no reported injuries or other damage. | Conductor (bare) | 2 | 2 | 2 |  | HSM003 | vegetation encroachment | Grassfire | 26/11/2017 16:30 | 1 | Large: more than 10 ha | 6766 | Agricultural |  | 20171127PWA_03 | Infrastructure (network-based) | -35.8524 | 142.2908 | 1 | Powercor | Report | 8518 | 0.022963 | 12.7kV AC (SWER) | Horsham Aerodrome | 3395 | Beulah | Trees
Emergency switching was completed to minimise the number of customers affected and the neutral connection was reconnected at the pole type substation under Access Authority conditions. | CENTRE ROAD, BENTLEIGH EAST VIC 3165 |  |  |  |  | HV injection;Not built/maintained to design | Poor workmanship |  | 2 | The United Energy AMI team advised of voltage issues in Agnes Street, Bentleigh East and have requested a faults crew to attend immediately. A new pole type substation named "Centre- Alexander" was installed approximately 18 months ago but for various reasons wasn't commissioned and placed into service at this time. 16/08/2017 - Application No. 109856A was created for Zinfra First Responders to commission the new "Centre-Alexandra" pole type substation and close the east circuit LV fuses and create a new open point for the west circuit after the temporary LV bridging is removed. Following the completion of the pole type substation commissioning, the main neutral connection become detached from the neutral plate at the pole type substation that caused the voltage to rise on the north circuit affecting customers who reside in Agnes and Malane Streets. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the north circuit of "Centre-Alexandra" substation. The LEI confirmed a high voltage injection occurred (CLA 1702) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (insulated);Equipment;Pole mounted | 0 | 0 | 0 |  | OR 24 | Neutral connection failure at the pole type substation. | HV injection | 16/08/2017 15:00 |  |  | 6451 | Roadway |  | 20170829UTD_02 | Infrastructure (network-based) | -37.9206 | 145.0541 | 1 | United Energy Distribution | Report | 8153 | 0.0003669 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Connection
On arrival crew isolated supply and carried out repairs REC for the railways to co-ordinate reconnection of the underpass lighting. | 56 LYNCH STREET, HAWTHORN VIC 3122 | 30181091 | Vehicle | [6 empty] | MFB reported a garbage truck pulled down service at Lynch St Cnr Golding St Hawthorn . On arrival the crew a two core XLPE service cable partially on the ground and partially upon the side mirror of a parked car. | Service conductor | 2 | 2 | 2 |  | CL013 | Garbage truck | Loss of supply;Damage to network assets | 43047.3396 |  |  | 6455 | Public space |  | 20170830PWA_01 | Infrastructure (network-based) | -37.8215 | 145.0306 | 1 | CitiPower | Report | 7986 | 0.0077199 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Vehicle
Fault crew attended site. Overhead conductor was dead when fault crew arrived, conductor was removed from the road with HV stick and site made safe. Conductor was repaired, erected and supply restored to the HV line. | 8500 BASS HIGHWAY, LEONGATHA SOUTH VIC 3953 | 2011054 |  |  |  | Overheated connection |  | Phase to earth | 0 | IMS229723 - Single phase HV conductor found across road on the ground, sparking. HV tie on the North side of the single phase intermediate structure had failed and conductor have broken after making contact to pole 2011054 | Conductor (bare) | 0 | 0 | 0 |  | LGA23 | broken tie caused the conductor in contact with the pole under high wind and resultant arcing. | Loss of supply | 43047.9715 |  |  | 6461 |  |  | 20170830SPN_03 | Infrastructure (network-based) | -38.4969 | 145.9232 | 1 | AusNet Services Distribution | Report | 8039 | 0.019525 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Leongatha South | Conductor
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 250w HPS lantern from the steel tramways pole. A new order was created for the replacement of the defective lantern. A blue Toyota Corolla (Rego WGW 965) was parked underneath the street light that sustained minor damage to the paint work as burning plastic fell from the burning lantern head. | 229 BALACLAVA ROAD, CAULFIELD NORTH VIC 3161 | 2334727 |  | Bird |  | Electrical breakdown |  |  | 2 | Warren from Citipower Dispatch advised they received a call from the fire brigade stating a light on a power pole is on fire in front of 229 Balaclava Road. The fire brigade are presently on site. A 250w HPS lantern on pole No. LIS 2334727 located outside 229 Balaclava Road, Caulfield North caught fire and was extinguished by the MFB. The cause was a birds nest inside the street light head that caught on fire. | Public lighting | 0 | 0 | 0 |  |  | Bird Incident | Plant/equipment | 20/08/2017 21:20 | 1 | Negligible: no ground fire | 6464 | Roadway |  | 20170831UTD_01 | Infrastructure (network-based) | -37.8729 | 145.0254 | 1 | United Energy Distribution | Report | 12952 | 0.0012963 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the HV infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 650 SOUTH ROAD, MOORABBIN VIC 3189 | 1816898 |  | Alive;Property owner/customer |  | Conductor clashing |  |  | 1 | At 0919hrs on 27/08/2017, 22kV feeder HT 09 circuit breaker reclosed to lockout affecting 167 customers. A gum tree branch from a tree inside "Melbourne's Cheapest Cars" located at 650 South Road, Moorabbin near the corner of Alex Avenue broke and fell over the HV conductors causing the footpath side HV conductor to break between pole numbers 1816897 and 1816898 and contact the LV conductors below. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Alex-South" substation. The LEI confirmed a high voltage injection occurred (CLA 1703) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | HT 09 | Vegetation: Trees Incident | HV injection;Loss of supply | 27/08/2017 9:19 |  |  | 6472 | Roadway |  | 20170831UTD_05 | Infrastructure (network-based) | -37.9378 | 145.0703 | 1 | United Energy Distribution | Report | 8084 | 0.024427 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Trees
Jemena crew checked crossarm on pole no. A016943 and determined that no further action was required. 4 x 3 phase services which were blown at mains box were were reterminated, tested and connected. | 10 SUMMIT DRIVE, EAGLEMONT VIC 3084 | A016943 |  |  |  | Overheated connection |  |  | 2 | LV ABC and mains box blew at pole no. A016943 Melted mains box was examined and there was no evidence of fire in surrounding vegetation or infrastructure which can be directly attributed to the melted material. No photo was available for this incident. | Conductor (ABC);Connection box | 0 | 0 | 0 |  | HB15 | 4 x overhead services blown at mains box at pole end | Melting or smoking only | 42775.391 |  |  | 6474 | Residential |  | 20170902JEM_02 | Infrastructure (network-based) | -37.7669 | 145.0629 | 1 | Jemena | Report | 8289 | 0.012947 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Eaglemont | OH Cable
replaced fuse and tube; fitted stinger cover on HV droppers. | 1549 ARCADIA TWO CHAIN ROAD, MIEPOLL VIC 3666 | 3904466 |  |  |  | Candled fuse |  |  | 0 | IMS230120 - EDO fuse tube burnt; fault crew found EDO fuse tube burnt and reportedly dead cockatoo at the base of the pole. No fire on the ground. | EDO fuse | 0 | 0 | 0 |  | BN1 | Bird Incident | Pole-top fire | 42775.2743 | 1 | Negligible: no ground fire | 6482 | Agricultural |  | 20170904SPN_02 | Infrastructure (network-based) | -36.6643 | 145.4701 | 1 | AusNet Services Distribution | Report | 8099 | 0.023997 | 22kV AC | Shepparton Airport | 3666 | Miepoll | Animal
Police were notified and attended site with details of the stolen items provided in the police report. Q-main were immediately organized for the repairs of the security fence. | HAMMOND ROAD, DANDENONG VIC 3175 |  | Unauthorised access;Copper theft | [5 empty] | 2 | When the field crew arrived on site, they identified the contractors site containers had been broken into and tools and equipment were stolen. Upon regular security inspections when the crew arrived on site, it was discovered the fence on the west side of the zone substation had been tampered with. A further inspection was made on the work site and it was identified that both the Zinfra and civil contractors on site containers was broken into and a number of items were removed from site including copper cables, power and hand tools. | Cable;Copper;Zone substation | 0 | 0 | 0 |  | DSH | Security breach at DSH zone substation. | No Go Zone (contact) | 42771.3125 |  |  | 6491 | Other | Zone substation | 20170906UTD_02 | Infrastructure (network-based) | -38.0139 | 145.2055 | 1 | United Energy Distribution | Report | 8124 | 0.025029 | 66kV AC | Moorabbin Airport | 3175 | Dandenong | Other
On arrival crew commenced repairs | 20 STURT STREET, BALLARAT CENTRAL VIC 3350 | 32010097 | Vehicle | [6 empty] | A customer has reported a truck has hit the service line at the incident location. On arrival the crew found that a Low Voltage service had been hit by a truck resulting in it breaking and coming to ground. There were no reported injuries, fire and minor third party damage. | Service conductor | 2 | 2 | 2 |  | BAN013 | Waste management truck | Loss of supply;Damage to network assets | 19/08/2017 7:01 |  |  | 6494 | Roadway |  | 20170907PWA_02 | Infrastructure (network-based) | -37.5616 | 143.8602 | 1 | Powercor | Report | 8121 | 0.011847 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat Central | Vehicle
On arrival crew isolated supply and commenced repairs. LEI engaged to check HVI's | 124 PRINCESS STREET, KEW VIC 3101 | 30301319 | Vehicle | [5 empty] | 1 | The MFB reported that a car had collided with a 66KV sub transmission pole at the incident location. The MFB left but were called back minutes later as the 66KV was tracking onto the LV crossarm straps. On Arrival the CitiPower faults crew found the pole has splintered and the centre phase 66KV insulator had snapped and come away from the cross arm. A HV injection occurred into the LV and the Q019 feeder protection operated. The car and driver had left the scene with Victoria Police to follow up with a police report. There was no fire or reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | RTS-CW Q019 | Vehicle collided with pole | HV injection;Loss of supply | 42895.8431 |  |  | 6495 | Roadway |  | 20170908PWA_01 | Infrastructure (network-based) | -37.7994 | 145.0304 | 1 | CitiPower | Report | 8123 | 0.017494 | Low voltage AC (<1kV);22kV AC;66kV AC | Essendon Airport | 3101 | Kew | Vehicle
Jemena crew made area safe and replaced damaged cable. | 11 LEAMINGTON STREET, RESERVOIR VIC 3073 |  | Copper theft | [5 empty] | 2 | Customer reports underground supply cable has been ripped out of pole and wires exposed. Jemena crew arrived on site to find underground cable has had copper stolen. | Services cable;Copper | 2 | 2 | 2 |  |  | Copper theft by unknown person. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43048.6889 |  |  | 6504 | Roadway |  | 20170911JEM_01 | Infrastructure (network-based) | -37.7132 | 145.0068 | 1 | Jemena | Report | 8293 | 0.010257 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Crew attended and carried out repairs | 4818 HENTY HIGHWAY, MYAMYN VIC 3304 | 33058882 | Vehicle | [5 empty] | 1 | Vicfire reported a 2 vehicle collision brought down power lines and started a grass fire at the incident location. On arrival the crew found that a truck had veered off the road to miss another vehicle hitting the pole and the HV conductors had started multiple small fires (approx. 5m2 in total). Hamilton Police were also in attendance and reported no injuries. | Pole (concrete) | 0 | 0 | 0 |  | HYT011 | Motor Vehicle Collision | Loss of supply;Grassfire;Damage to network assets | 43048.6799 | 1 | Localised: less than 10 sq.m | 6507 | Agricultural |  | 20170912PWA_03 | Infrastructure (network-based) | -37.971 | 141.7321 | 1 | Powercor | Report | 8143 | 0.031891 | 22kV AC | Portland (Cashmore Airport) | 3304 | Myamyn | Vehicle
De-energised overhead, replaced BA fuse and patrolled section of lines downstream. | 1965 OLD SALE ROAD, SHADY CREEK VIC 3821 | 2706751 |  |  |  | Candled fuse |  |  | 1 | IMS230207 - candled BA fuse at WL045 and burn marks at base of pole 2706751 about 1 meter in circumference. | Boric acid | 0 | 0 | 0 |  | WGL24 | BA fuse candling | Loss of supply;Grassfire | 42925.7083 | 1 | Localised: less than 10 sq.m | 6510 | Roadway |  | 20170912SPN_01 | Infrastructure (network-based) | -38.0996 | 146.0322 | 1 | AusNet Services Distribution | Report | 12844 | 0.015466 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Shady Creek | Fuse
A LEI and faults truck attended and the LEI tested the installation and no faults could be identified. A NST was completed that passed. The faults crew checked the connections in the pole end after 1.5v was measured on the neutral and 3.6v when load was applied. The faults crew re-terminated neutral connections at pole No. LIS 2326031 and at the pit as the neutral joint in the pit showed evidence of water ingress. Upon completion the LEI measured the voltage on the neutral had reduced to 0.8v. | UNIT 2 16 FENTON STREET, HUNTINGDALE VIC 3166 | 2326031 |  | Precipitation |  | Corrosion;Neutral fault |  | Phase to earth | 2 | A REC reported the customer had voltage issues and he believes it could be a crook neutral at the pole end. In addition, the customer has received electric shocks from the sink and stove but doesn't have the dimming of lights. The occupier had been receiving electric shocks from the sink and stove and contacted the United Energy faults and emergencies call centre after a REC had checked the installation and suggested the cause was a faulty neutral connection at the pole end. | Connector/termination | 0 | 0 | 0 |  |  | The faults crew re-terminated neutral connections at pole No. LIS 2326031 and at the pit as the neutral joint in the pit showed evidence of water ingress. | Minor shock | 42864.5694 |  |  | 6511 | Residential |  | 20170913UTD_01 | Infrastructure (network-based) | -37.9069 | 145.111 | 1 | United Energy Distribution | Report | 8150 | 0.018212 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Huntingdale | Connection
Site made safe and repairs made to HV conductor Supply restored | 25 STUBBS STREET, KENSINGTON VIC 3031 |  |  |  |  | Electrical breakdown |  |  | 1 | HV overhead conductor heading south of cable head pole no. A030872 broke and fell to ground due to fault current, resulting in loss of supply. Photos attached in "Notes & Findings" section. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | FT14 | Connector mechanical failure due to AMPACT failure at cable head pole no. A030872. The AMPACT connector in use was confirmed to be correct for the application on site, taking into account all relevant details (conductor types and sizes, manufacturer specifications, etc.) | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/08/2017 4:50 |  |  | 6514 | Roadway |  | 20170915JEM_01 | Infrastructure (network-based) | -37.7912 | 144.9358 | 1 | Jemena | Report | 8172 | 0.040282 | 11kV AC | Essendon Airport | 3031 | Kensington | Connection
The crew isolated supply and installed a new cross-arm on a raiser bracket. | SPENCER ROAD, TARRONE VIC 3283 | 30144811 |  |  |  | Leakage |  |  |  | Person driving past reported a pole fire. On arrival the crew found that the High Voltage cross arm on pole 1 had burnt. There was no reported ground fire, injury or shocks. (no photos available at time of report) | Crossarm (wood) | 2 | 2 | 2 |  | KRT013 | Excessive leakage current | Pole-top fire | 25/09/2017 4:41 | 1 | Negligible: no ground fire | 6535 | Roadway |  | 20170926PWA_04 | Infrastructure (network-based) | -38.2794 | 142.2056 | 1 | Powercor | Report | 8183 | 0.019951 | 22kV AC | Warrnambool Airport Ndb | 3283 | Tarrone | Pole
On arrival crew isolated supply and carried out repairs | 2 THE ESPLANADE, PORTARLINGTON VIC 3223 | 32070587 |  |  |  | Overheated connection |  |  |  | CFA reported a pole fire at the incident location On arrival the crew found that fuse box, LV droppers and conduit had melted due to an overheated connection. The CFA told the crew they had extinguished a fire prior to their arrival and only melted plastic on the ground. No ground fire, no injuries, no third party damage. | Connection box | 2 | 2 | 2 |  | DDL021 | Unable to determine due to damage | Pole-top fire;Loss of supply | 43017.8792 | 1 | Negligible: no ground fire | 6537 | Roadway |  | 20170926PWA_06 | Infrastructure (network-based) | -38.1136 | 144.6576 | 1 | Powercor | Report | 8185 | 0.032249 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Portarlington | Connection
CitiPower officer attending requested the Scaffold be made non accessible and for the customer to apply on line for a site visit. | 27 CANTERBURY ROAD, TOORAK VIC 3142 | 30279072 | Building too close or within the No Go Zone | [5 empty] | 2 | CitiPower No Go Zone officer detected a scaffold has been erected close to Low voltage service cables and non standard visual warning devices had been installed by persons unknown. The service cable had also been secured to the scaffold with duct tape. No injury or third party damages reported. | Conductor (insulated) | 0 | 0 | 0 |  | TK025 | interference / unauthorised access | No Go Zone (contact) | 42956.5826 |  |  | 6545 | Construction |  | 20170927PWA_06 | Infrastructure (network-based) | -37.847 | 145.0095 | 1 | CitiPower | Report | 8193 | 0.040603 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Other
Crew reported for follow up | 56 LIMA STREET, ST ALBANS VIC 3021 | 33074956 | Unauthorised access | [5 empty] | 2 | Metering and servicing crew attended premises in preparation for a scheduled appointment. On arrival the crew identified that the meter had been removed and left stowed in an inappropriate manner. | Smart meter;Meter board (including fuses) | 0 | 0 | 0 |  | SU012 | Interference by REC | No Go Zone (no contact) | 42864.375 |  |  | 6549 | Residential |  | 20170927PWA_08 | Infrastructure (network-based) | -37.7568 | 144.8017 | 1 | Powercor | Report | 8197 | 0.031096 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Other
The crew replaced the stolen earths with new earths (approximately 4 meters of copper used). | 89-95 BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30249820 | Copper theft | [6 empty] | Powercor contact centre received a report of stolen copper earths at the incident location. On arrival the fault crew found that the low voltage earth had been stolen from the substation. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | SU034 | Copper theft | Damage to network assets | 42744.4583 |  |  | 6551 | Public space |  | 20170927PWA_10 | Infrastructure (network-based) | -37.8145 | 144.7999 | 1 | Powercor | Report | 8199 | 0.035256 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
Details captured, site being monitored by CitiPower No Go Zone group. Clearance from erected scaffold adequate. | 83B EASEY STREET, COLLINGWOOD VIC 3066 | 30172014 | Building too close or within the No Go Zone | [5 empty] | 2 | CitiPower No Go Zone officer identified that scaffolding had been erected in vicinity of an energised High voltage line. | Conductor (bare);Aluminium twisted (XLPE) | 0 | 0 | 0 |  | CW009 | Non compliance to instructions issued by CitiPower | No Go Zone (no contact) | 14/08/2017 9:00 |  |  | 6553 | Construction |  | 20170928PWA_01 | Infrastructure (network-based) | -37.7982 | 144.9896 | 1 | CitiPower | Report | 8201 | 0.015086 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3066 | Collingwood | Other
The crew replaced the severed service with a new service. | 17 PROVOST STREET, NORTH MELBOURNE VIC 3051 | 30182769 | Vehicle | [6 empty] | A customer reported that a garbage truck has contacted the service at the incident location. â€œHalf is on the ground the other half is on a parked car.â€ On arrival the fault crew found that a garbage truck had contacted the service and it had been severed service was resting on a car and the ground, no damage to POA. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | VM004 | Garbage truck struck service | Loss of supply;Damage to network assets | 42834.4757 |  |  | 6554 | Roadway |  | 20170928PWA_02 | Infrastructure (network-based) | -37.8022 | 144.9472 | 1 | CitiPower | Report | 8202 | 0.0018877 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Vehicle
The crew replaced the stolen earth with new. | 307 DOHERTYS ROAD, TRUGANINA VIC 3029 | 33074060 | Copper theft | [6 empty] | A powercor employee reported that the low voltage earth has been stolen from the incident location. On arrival the fault crew found that the earth had been cut away from the pole substation about four meters of copper removed. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LVN024 | copper theft | Damage to network assets | 42864.3931 |  |  | 6558 | Public space |  | 20170928PWA_06 | Infrastructure (network-based) | -37.8264 | 144.7631 | 1 | Powercor | Report | 8207 | 0.033796 | Earthing cable | Laverton Raaf | 3029 | Truganina | Other
On arrival crew isolated supply and arranged for repairs to be made. | 120 LIEBIG STREET, WARRNAMBOOL VIC 3280 | 33097885 | Working too close to underground cables | [5 empty] | 1 | A customer reported that they had damaged LV U/G cable at the incident location. On arrival the crew found that an excavator doing streetscape works had dug up and cut through LV cable with an auger attachment. LV fuses blew and a shop owner made the excavator operator aware of the loss of supply. DBYD documents were onsite, number was not obtained. There was no fire , injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBL008 | Streetscape works | Loss of supply | 13/09/2017 16:20 |  |  | 6565 | Commercial |  | 20171003PWA_03 | Infrastructure (network-based) | -38.3833 | 142.4843 | 1 | Powercor | Report | 8215 | 0.032622 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Dug up
On arrival crew carried out the required repairs | 32-38 BURNS ROAD, ALTONA VIC 3018 | 30226121 | Copper theft | [6 empty] | A Powercor employee reported copper earth missing from a pole substation. A crew attended and found that HV and LV cable earths were cut and removed from the pole. No shock, injuries or third party damage. | Earth | 2 | 2 | 2 |  | AC031 | Copper theft | Damage to network assets | 17/09/2017 11:24 |  |  | 6568 | Public space |  | 20171003PWA_05 | Infrastructure (network-based) | -37.8493 | 144.7897 | 1 | Powercor | Report | 8218 | 0.01313 | Earthing cable | Laverton Raaf | 3018 | Altona | Other
Fault Crew checked all service connections,02/09/17 CTA tested property and completed all reqâ€™d VESI tests Fault crew replaced existing service with new and check all connections, 04/09/17 CTA retested property and completed all reqâ€™d VESI tests | 8 QUERCUS COURT, CAMBERWELL VIC 3124 | 30174013 |  |  |  | Corrosion |  | Phase to earth |  | Brian reported he received electric shock when she made simultaneous contact between the metallic kitchen sink tap with one hand and the metallic kitchen sink with his other. | Connection box | 2 | 2 | 2 |  | RD010 | Loose connection at FOLCB | Minor shock | 31/08/2017 10:00 |  |  | 6589 | Residential |  | 20171004PWA_06 | Infrastructure (customer connection) | -37.8495 | 145.0893 | 1 | CitiPower | Report | 8288 | 0.02899 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Connection
On arrival crew isolated supply and carried out repairs | 335 FORD ROAD, GRAHAMVALE VIC 3631 | 33096629 |  |  |  | Corrosion |  |  |  | A customer reported a fire on the pole at the incident location. On arrival the crew found that a neutral connection in a crossarm mounted junction box had overheated. Hot debris fell to the ground causing a grassfire of approx. 1m x 2m= 2m2 on the roadside. The crew also stated that the customer had to replace a damaged power circuit breaker on their switchboard. The initial report stated that the customer had sustained damage to some equipment, however this could not be verified. There were no injuries reported. | Connection box | 2 | 2 | 2 |  | SHN024 | Overheated connection | Grassfire | 42835.4785 | 1 | Localised: less than 10 sq.m | 6594 | Roadway |  | 20171005PWA_01 | Infrastructure (network-based) | -36.3474 | 145.4395 | 1 | Powercor | Report | 8247 | 0.018458 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Grahamvale | Crossarm
Zinfra compliance officer removed the service fuse from the FOLCB on the BTS pole and issued a level 1 defect. Faults crew then disconnected the overhead service. | 336 BUCKLEY STREET, ESSENDON VIC 3040 |  | Unauthorised work | [5 empty] | 2 | 1 illegally connected Builders Temporary Supply (BTS) pole where the overhead services have been relocated from an existing residential dwelling to an unsafe non compliant BTS pole by on authorized Jemena personal and without a prescribed CES. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Unknown unauthorised third party relocated live service line to a BTS. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42988.4285 |  |  | 6598 | Residential |  | 20171009JEM_01 | Infrastructure (network-based) | -37.7543 | 144.8947 | 1 | Jemena | Report | 8252 | 0.036957 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | AF Other
Crew attended | 21 CORNISH AVENUE, TRESCO VIC 3583 | 30247555 |  | Bird | [5 empty] | Powercor received report of a fire. Fire was out on when crew attended onsite. Cause unable to be confirmed, however it is suspected that the fire started at the HV Underground Cable Head Pole and was possibly a bird flashover | Dropper/bridge | 0 | 0 | 0 |  | KGT004 | Bird Incident | Grassfire | 42926.6097 | 1 | Small: 10 - 1000 sq.m | 6602 | Roadway |  | 20171009PWA_03 | Infrastructure (network-based) | -35.502 | 143.672 | 1 | Powercor | Report | 8259 | 0.018204 | 22kV AC | Swan Hill Aerodrome | 3583 | Tresco | Animal
Line isolated and conductor repaired | 11 GEAR AVENUE, MOUNT HELEN VIC 3350 | 32001267 |  |  |  | Not built/maintained to design |  |  | 1 | Customers reported dim lights at the incident location. On arrival the crew found that a conductor had broken resulting in the conductor falling to the ground. There was no ground fire. There were no reported shocks, injuries or third party property damages. | Conductor (bare) | 0 | 0 | 0 |  | BAS013 | conductor condition | Loss of supply | 43018.2806 |  |  | 6607 | Roadway |  | 20171011PWA_01 | Infrastructure (network-based) | -37.6306 | 143.9026 | 1 | Powercor | Report | 11278 | 0.025729 | 22kV AC | Ballarat Aerodrome | 3350 | Mount Helen | Conductor
A LEI and faults crew attended and the LEI removed the fuse cartridge near pole number LIS 1823140 after viewing the cut to the pole guard on the timber public light pole. The immediate area was tested to ensure that no hazards remained and the LEI confirmed the damaged underground cable had been isolated. The fuse cartridge in the pillar that supplied the light pole had been removed and it was confirmed the fuse had operated due to the fault. The faults crew disconnected the and capped the underground cables to ensure it couldn't be energised by normal means and resealed the pillar. A further follow up is required to remove the timber pole. A review of our records indicated that a truck appointment occurred on 03/10/2017 arranged by REC Adam to relocate the existing consumers mains and metering to the new toilet block. | JETTY ROAD, SANDRINGHAM VIC 3191 | 9296902 | Working too close to underground cables;Caused by REC/contractor |  |  |  |  | Phase to earth | 1 | Caller reports that someone has received an electric shock from underground cables while demolishing a toilet block on Jetty Road, Sandringham. Worksafe and ESV are going to the site to investigate. Earlier this month, an unknown person apparently tested a live underground cable with a volt stick and then proceeded to use a grinder to cut through a pole guard and conduit into a live neutral screened cable attached to pole No. LIS 9296902. The active and neutral conductors shorted out and caused a fuse cartridge to operate that was located in a nearby pillar. It's believed that no electric shock nor any flash burns received to the person using the grinder. There are no records to indicate that United Energy had been advised of the event that occurred earlier this month. | Services cable;Copper | 0 | 0 | 0 |  |  | Using a grinder to cut through a live underground cable attached to the timber pole. | No Go Zone (contact) | 18/10/2017 10:05 |  |  | 6621 | Construction |  | 20171020UTD_01 | Infrastructure (network-based) | -37.9458 | 144.9975 | 1 | United Energy Distribution | Report | 8297 | 0.020302 | Low voltage AC (<1kV) | Moorabbin Airport | 3191 | Sandringham | Other
On arrival crew carried out repairs. | 14 HOPETOUN ROAD, WARRNAMBOOL VIC 3280 | 30238319 | Vehicle | [5 empty] | 2 | A customer reported that a truck has struck a wire and the wire has broken and was on the ground at the incident location. On arrival the crew found that a waste collection truck was exiting a driveway and contacted an LV service cable causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | WBL006 | Garbage truck exiting driveway | Loss of supply;Damage to network assets | 42776.5188 |  |  | 6641 | Residential |  | 20171025PWA_03 | Infrastructure (network-based) | -38.3694 | 142.4736 | 1 | Powercor | Report | 8325 | 0.0033924 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
Area made safe for crews to repair conductor. | 10 EDEN COURT, ASCOT VALE VIC 3032 |  |  | Wind |  | Conductor clashing |  |  | 2 | LV conductor clashing due to strong wind, resulting in LV conductor on the ground. | Conductor (bare) | 2 | 2 | 0 |  |  | Conductor clashing due to strong wind. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/10/2017 7:08 |  |  | 6647 |  |  | 20171027JEM_01 | Infrastructure (network-based) | -37.7722 | 144.9015 | 1 | Jemena | Report | 8332 | 0.033428 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Lightning
Fire burnt approx. 20m x 20m. pole was checked ok and the line stayed energised | 36 COBAINS ROAD, BUNDALAGUAH VIC 3851 | 2511666 |  | Bird |  |  |  |  | 1 | IMS 230896 - fault crew noted grass fire on side of the road. called CFA to attend and extinguished the fire. | Conductor (bare) | 0 | 0 | 0 |  | MFA23 | Bird Incident | Grassfire | 24/10/2017 11:40 | 1 | Small: 10 - 1000 sq.m | 6665 | Agricultural |  | 20171102SPN_02 | Infrastructure (network-based) | -38.017 | 147.0048 | 1 | AusNet Services Distribution | Report | 8353 | 0.0020081 | 22kV AC | Morwell (Latrobe Valley Airport) | 3851 | Bundalaguah | Animal
Fault crew found excavator had come into contact with 1ph neutral screen service at a property being demolished. Jemena crew dropped service and removed meter because the same excavator was demolishing this house and would come into contact with the service again. Crew obtained excavator details. Anthill Excavations: 0422274002, Truck registration: XAL-245. No photos available. | 36 CONGRAM STREET, BROADMEADOWS VIC 3047 |  | Crane, excavator or other construction/farming equipment | [6 empty] | Excavator came into contact with overhead service at property being demolishing. | Service conductor | 2 | 2 | 2 |  | BMS12 | Excavator came into contact with overhead service line. | No Go Zone (contact) | 42805.4319 |  |  | 6669 | Residential |  | 20171103JEM_01 | Infrastructure (network-based) | -37.6884 | 144.9315 | 1 | Jemena | Report | 9794 | 0.025485 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Vehicle
On arrival crew isolated supply and carried out repairs. | 18 HEATHER STREET, HAMLYN HEIGHTS VIC 3215 | 30074807 |  |  |  | Unknown technical factor |  |  |  | A customer reported a pole fire at the incident location. Crew Located Burnt out FSD. Report from customers there had been a fire, but out there was no ground fire, no injuries or third party property damage. No photos taken | Connection box | 2 | 2 | 2 |  | GL013 | Cause not established - Item not retained | Pole-top fire | 43049.8507 | 1 | Negligible: no ground fire | 6670 | Roadway |  | 20171103PWA_03 | Infrastructure (network-based) | -38.1197 | 144.3271 | 1 | Powercor | Report | 8358 | 0.022755 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | Pole
The 15amp blue phase HV fuse was replaced and supply restored to customers in the area. | 26 ENTALLY DRIVE, WHEELERS HILL VIC 3150 | 200667 |  | Precipitation |  | Fatigue |  |  | 2 | The MFB report wires are down in Entally Drive and callers in the area are reporting dim lights. The blue phase 22kV 15amp Powder Filled Fuse candled at "Entally-View Mount" pole type substation that caused a loss of supply and dim lights to customers in the vicinity. There were no wires down as reported by the MFB. Pole No. LIS 0607733. | Powder filled | 0 | 0 | 0 |  | MGE 34 | The cause of the fuse to candle was unknown but the weather was drizzling at the time. | Pole-top fire | 42927.5076 | 1 | Negligible: no ground fire | 6679 | Roadway |  | 20171108UTD_02 | Infrastructure (network-based) | -37.9028 | 145.1773 | 1 | United Energy Distribution | Report | 12960 | 0.02201 | 22kV AC | Moorabbin Airport | 3150 | Wheelers Hill | Fuse
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole, which was identified as the cause of the high impedance associated with the return path for the neutral current. The attending Powercor Fault Crew replaced the existing O/H Service Cable between the Reticulation Pole and the Service Pole supplying 210, 212 and 214 Walker Street and to the Customerâ€™s POA at 214 Walker Street and completed an NST Test at all installations which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 210 WALKER STREET, BALLARAT NORTH VIC 3350 | 30261982 |  |  |  | Corrosion |  | Phase to earth | 2 | Ms Suzie Zhang was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal shower taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | BAN015 | Corroded service connection | Minor shock | 20/09/2017 16:30 |  |  | 6686 | Residential |  | 20171109PWA_04 | Infrastructure (network-based) | -37.5429 | 143.8725 | 1 | Powercor | Report | 8376 | 0.033734 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat North | Connection
Dispatched crew. Crew found HV earth on the wood sub pole had come adrift from the pole as the staples had fallen out which caused the HV earth to rest against a 240V LV isolator on the supply side, causing 240V to feed into the HV earth. The crew moved the HV earth off the LV isolator and reattached it to the pole . | 74 MOONDARRA ROAD, MOONDARRA VIC 3825 | 2200339 |  |  |  | Earth fault |  | Phase to earth | 2 | IMS 230337 - Customer reported dog appeared to get shock from near sub pole | Disconnector/isolator;Pole mounted;Earth/earthing | 0 | 0 | 0 |  | MOE14 | broken earth | Shock to livestock, pet or companion animal | 16/09/2017 8:57 |  |  | 6685 | Agricultural |  | 20171109SPN_01 | Infrastructure (network-based) | -38.0241 | 146.3649 | 1 | AusNet Services Distribution | Report | 8599 | 0.021157 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Moondarra | AF Other
On arrival crew carried out repairs | 134 VINES ROAD, HAMLYN HEIGHTS VIC 3215 | 32080104 |  |  |  | Electrical breakdown |  |  | 2 | Vicfire reported a fire at the incident location. On arrival the crew found that a neutral screen service cable had failed at the house end roller termination, resulting in blackening of the POA area and the live service cable falling to the ground. The service cable falling to the ground in turn resulted in a small fire in a garden bed in the front yard of the house. There were no injuries or other damage reported. | Service conductor | 2 | 2 | 2 |  | GL013 | Service cable damaged at Roller Clamp | Grassfire | 43050.4417 | 1 | Localised: less than 10 sq.m | 6696 | Residential |  | 20171113PWA_03 | Infrastructure (network-based) | -38.1163 | 144.3289 | 1 | Powercor | Report | 8410 | 0.029219 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | OH Cable
An electrical inspector was dispatched and carried out NST testing which failed due to high neutral impedance. The electrical inspector checked the substation and discovered the door was not secured because the lock had been drilled out. A visual inspection inside the substation revealed that the LV neutral conductor had been cut. The electrical inspector isolated the street circuit and informed the report room. Jemena service crews were dispatched to repair damaged LV neutral conductor. | 30 FOX HOLLOW DRIVE, SUNBURY VIC 3429 |  | Vandalism | [6 empty] | Following an all supply fail report at around 6am, a crew was dispatched to the Fox Hollow-Watsons kiosk substation and found what appeared to be a tripped LV circuit breaker which they re-energised. Immediately afterwards, the owner of no. 30 Fox Hollow Drive realised that her electrical equipment was emitting smoke and malfunctioning. The owner immediately turned the power off at her switchboard and contacted Jemena. The owner at no. 35 Fox Hollow Drive also reported that power circuits had tripped. TechSafe report (containing photos) attached in "Notes and Findings" section | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | SHM11 | Vandals had cut LV neutral conductor in kiosk substation at Fox Follows-Watsons, possibly trying to steal copper cable before discovering it was aluminium Vandals had also drilled a hole in lock to access kiosk substation | Less than $50k damage;Damage to network assets | 15/11/2017 5:50 |  |  | 6711 | Roadway |  | 20171115JEM_02 | Infrastructure (network-based) | -37.613 | 144.7325 | 1 | Jemena | Report | 9805 | 0.0043773 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew carried out repairs | 1808 MOUNT MACEDON ROAD, WOODEND VIC 3442 | 31006854 |  |  |  | Insulator |  |  | 1 | Emergency Services informed a pole fire at the incident location. On arrival the crew found that a HV conductor came off from damaged insulator and sitting on the cross arm and the arm smoking. There was no ground fire, third party damage or injury. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | WND012 | insulator top dislodged | Pole-top fire | 16/11/2017 14:36 | 1 | Negligible: no ground fire | 6716 | Roadway |  | 20171117PWA_02 | Infrastructure (network-based) | -37.3617 | 144.5509 | 1 | Powercor | Report | 9807 | 0.0068866 | 22kV AC | Melbourne Airport | 3442 | Woodend | Conductor
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The pole junction box was removed and replaced with IPCs. | 165 BUNYIP RIVER ROAD, NAR NAR GOON VIC 3812 | 512440 |  |  |  | Mechanical breakdown |  |  | 2 | IMS 231255 - Fire brigade reported a pole fire. The Attending AusNet Services' fault crew found a burnt out junction box on the pole. No fire on the ground or the pole. It appears the service cable hook has failed resulting in the pole junction box being dislodged from the pole and holding the customer's service cable. | Connection box | 0 | 0 | 0 |  | phm33 | Burnt out pole junction box. | Other electricity related | 16/11/2017 18:33 | 1 | Negligible: no ground fire | 6715 | Agricultural |  | 20171117SPN_01 | Infrastructure (network-based) | -38.1512 | 145.5778 | 1 | AusNet Services Distribution | Report | 9806 | 0.03967 | Low voltage AC (<1kV) | Moorabbin Airport | 3812 | Nar Nar Goon | AF Other
CEOT dispatched a fault crew who isolated, made safe and carried out repairs. For remedial measures AusNet Services' has in place a steel conductor replacement program. | 68 IRELANDS ROAD, TOORA VIC 3962 | 2022759 |  | Lightning |  | Corrosion |  | Phase to earth | 1 | IMS 231270 - A HV steel conductor broken mid-span at Lis 2022759. The HV conductor fell to the ground. Electrical protection operated - 2 x HV fuses were blown. There were reports of a lightning strike in the vicinity. The attending fault crew commented that the conductor was rusty and possibly the lightning strike caused the conductor to break. It is believed it was possible that the HV conductor on the ground was alive due to backfeed via downstream substation transformer windings. | Conductor (bare) | 0 | 0 | 0 |  | FTR21 | Rusty conductor and lightning strike. | Loss of supply | 16/11/2017 18:53 |  |  | 6728 | Roadway |  | 20171120SPN_01 | Infrastructure (network-based) | -38.6792 | 146.3209 | 1 | AusNet Services Distribution | Report | 8464 | 0.040426 | 22kV AC | Morwell (Latrobe Valley Airport) | 3962 | Toora | Conductor
Upon arrival crew isolated supply to the known undergrounds in the area. Non-invasive hydro excavation was used to expose the cable to facilitate repairs. The section of LV service cable was protected by corrugated conduit. | 41 PARK ROAD, MARYBOROUGH VIC 3465 | 60254524 | Working too close to underground cables | [5 empty] | 2 | Central Goldfields Shire employee called to inform that upon setting up an RACV event at Lions Reserve, a tent peg had been observed sparking. There was no fire, no reported injuries or third party property damage | Services cable | 2 | 2 | 2 |  | MRO004 | Tent peg driven into Underground | Loss of supply;No Go Zone (contact);Damage to network assets | 18/11/2017 10:27 |  |  | 6732 | Public space |  | 20171121PWA_01 | Infrastructure (network-based) | -37.04 | 143.7408 | 1 | Powercor | Report | 8468 | 0.0030301 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | Other
CEOT dispatched a fault crew to make safe and investigate. The Fire Brigade attended and extinguished the fire. The fault crew disconnected the overhead service cable. The customer's REC installed a new POA/mains box (FOLCB). An AusNet Services' crew attended and reconnected supply with a COES number 627042520. | 21 DILOP DRIVE, EPPING VIC 3076 | 931457 |  |  |  | Fault on customer installation |  |  |  | IMS 231289. Emergency Services called reporting fire at building junction box. The failure of the customer's unmetered consumer's mains caused a fire at the FOLCB at the Point of Supply. The service cable was still attached and did not drop. The service cable was not damaged. The side of the building was also burnt. | Customer installation | 0 | 0 | 0 |  | epg23 | The customer's unmetered consumer's mains caused a fire at the FOLCB at the Point of Supply. | Property | 20/11/2017 14:20 | 0 | Negligible: no ground fire | 6734 | Industrial |  | 20171121SPN_01 | Infrastructure (network-based) | -37.6433 | 145.0175 | 1 | AusNet Services Distribution | Report | 8472 | 0.038514 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | AF Other
Checked over on site and taken to Swan Hill hospital on Splatt Street, Swan Hill to undergo medical assessment | 7 MEMORIAL DRIVE, SWAN HILL VIC 3585 | 33104909 |  |  |  |  | Not followed;Inappropriate tools/plant/equipment;Failure to use correct PPE |  | 2 | An employee was wiring behind a panel within Swan Hill ZSS and made contact with a bare stud and received an electric shock.Â The shock was felt from the back of his right hand, where he had made contact to his little finger on his left hand. | Zone substation | 2 | 2 | 2 |  | SHL001 | Work method used, Inadequate covering and PPE | Minor shock | 21/11/2017 14:30 |  |  | 6737 | Other | Zone substation | 20171122PWA_01 | Infrastructure (network-based) | -35.3453 | 143.5227 | 1 | Powercor | Report | 12274 | 0.026086 | Voltage regulating and Tap changer control circuitry;Low voltage AC (<1kV);Other | Swan Hill Aerodrome | 3585 | Swan Hill | Other
On arrival crew isolated supply and arranged repairs. | 420 ST KILDA ROAD, MELBOURNE VIC 3004 | 30194306 |  |  |  | Corrosion;Overheated connection |  |  |  | MFB reported a smoking pole at the incident location. Upon arrival, the Powercor crew found that the overheated junction box on the steel P/L pole melted and cable insulation failed livening up the pole. There were no injuries, third party damages or ground fire. | Connection box;Pole (steel) | 2 | 2 | 2 |  | MP036 | Moisture ingress causing corrosion | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Melting or smoking only | 43079.6111 |  |  | 6743 | Roadway |  | 20171122PWA_03 | Infrastructure (network-based) | -37.8361 | 144.975 | 1 | CitiPower | Report | 9700 | 0.0034132 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Connection
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | CENTRAL PARK ROAD, MALVERN EAST VIC 3145 | 2318679 |  | Lightning |  |  |  |  | 2 | Caller reports lightning has hit a pole and number 12 and 14 Central Park Road have lost their electricity supply. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, customers in Central Park Road lost their electricity supply after lightning struck pole No. LIS 2318679. Several AMI meters were damaged and required replacement whilst other occupiers advised the faults crew they had damaged appliances. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Westgarth-Central Park" substation. The LEI confirmed a high voltage injection occurred (BWD 1702) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Pole (wood) | 0 | 0 | 0 |  | CFD 16 | Lightning struck a United Energy LV pole. | Damage to network assets | 18/11/2017 17:15 |  |  | 6738 | Residential |  | 20171122UTD_01 | Infrastructure (network-based) | -37.868 | 145.0412 | 1 | United Energy Distribution | Report | 8478 | 0.036701 | 11kV AC | Moorabbin Airport | 3145 | Malvern East | Lightning
Site made safe and LV conductor repaired | 388 GILBERT ROAD, PRESTON VIC 3072 | 10053904 |  |  | Neutral | Defective component |  |  | 2 | Report of sparking powerline running parrallel to street, burnt and down over the road. Fargo sleeve has failed resulting in dead side of LV conductor falling to the ground. This incident is not considered a bare conductor failure as per ESV reporting guidelines. LV conductor has been repaired and re-sleeved. | Conductor (bare) | 0 | 0 | 0 |  | CN0-008 | Fargo sleeve has failed resulting LV conductor falling to the ground. LV conductor has been repaired and re-sleeved. | Loss of supply | 22/11/2017 16:15 |  |  | 6750 | Residential |  | 20171123JEM_01 | Infrastructure (network-based) | -37.7358 | 144.9906 | 1 | Jemena | Report | 8491 | 0.00014468 | 11kV AC | Essendon Airport | 3072 | Preston | AF Other
On arrival crew isolated supply As a result of the vehicle impact the substation had to be replaced. | 1 VERONA AVENUE, TARNEIT VIC 3029 | 35264672 | Vehicle | [5 empty] | 1 | Customer reported car hit pole at the incident location. On arrival the crew found serious multiple vehicle accident and one of the vehicle had hit the Sayers â€“ Verona 315kVA Kiosk substation causing major damage to the substation starting fire and oil leak as a result of the vehicle impact. No oil loss into any nearby drains. Ground fire at the base of the kiosk (small area), possible third party property damage to the fence adjacent to the substation due to fire and smoke. The occupants of the vehicle were taken to hospital prior to the fault crew arriving at the scene. | Pad mounted equipment/kiosk | 2 | 1 | 2 |  | LV001 | Vehicle collision | Loss of supply;Significant disruption to the community;Grassfire;Damage to network assets | 25/11/2017 19:11 | 1 | Localised: less than 10 sq.m | 6764 | Roadway |  | 20171127PWA_02 | Infrastructure (network-based) | -37.8473 | 144.6798 | 1 | Powercor | Report | 8513 | 0.01326 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3029 | Tarneit | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out repairs. HV EDO fuse was removed and replaced. | 197 CUNNINGHAM ROAD, SWAN REACH VIC 3903 | 1911236 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 230961. Candling EDO fuse tube at LIS 1911236. Fuse found to be candling when fault crew attended. There was no evidence of a ground fire. | EDO fuse | 0 | 0 | 0 |  | BDL41 | Burnt EDO fuse tube. | Other electricity related | 27/10/2017 20:30 | 1 | Negligible: no ground fire | 6769 | Agricultural |  | 20171128SPN_01 | Infrastructure (network-based) | -37.7982 | 147.879 | 1 | AusNet Services Distribution | Report | 12845 | 0.020139 | 22kV AC | Bairnsdale Airport | 3903 | Swan Reach | Fuse
On arrival crew carried out repairs | BOILINGDOWNS, 1366 MIDLAND HIGHWAY, GHERINGHAP VIC 3331 | 30266389 |  |  |  | Overheated connection |  |  | 1 | Emergency services reported conductor down across the road at the incident location. Attending crew found the red phase of steel conductor had broken between P71 (LIS-59813) and P1 (LIS-747554) resulting in a small ground fire/burns to the ground. There was no third party damage or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | GL015 | overheated connection | Grassfire | 28/11/2017 2:51 | 1 | Localised: less than 10 sq.m | 6783 | Roadway |  | 20171129PWA_01 | Infrastructure (network-based) | -38.071 | 144.2279 | 1 | Powercor | Report | 8540 | 0.017376 | 22kV AC | Avalon Airport | 3331 | Gheringhap | Connection
Initial report: CEOT dispatched a fault crew to make safe and carry out necessary repairs. Fault truck attended. The fire was out on arrival of the fault crew. The fire size was approximately 2ft x 2ft. CEOT advised the local DAO to investigate the incident. ESV advised. Transformer isolated. Main line supply restored. Final report from attending DAO: When conducting the fire report, the customer was off supply. The fuses located at switch LDL099 fuses were dropped when I arrived. No other additional information to report. | 90 MONBULK-SEVILLE ROAD, WANDIN EAST VIC 3139 | 1012337 |  |  |  | Electrical breakdown |  |  | 1 | IMS 231451. Initial report: A Transformer faulted which caused oil to spill out then caught fire. The HV fuse was found hung-up and failed to operate which tripped the line upstream. Final report: Report from the DAO: Attended site and there was a pole fire at BIDPO#102337. The pole was a HV Termination pole with an existing 50kVA pole type substation located on it. The substation was fuseless. (See photos attached). The fire was out when I attended site. The result of the fire was caused by the Substation transformer failing and oil leaking out of the tank. This resulted in a fire. There was evidence of a small fire located around the pole, however it was measured at 0.5m wide and 0.5m in length. There was no other damage to any other surrounding assets. The pole was scorched, however there was not enough damage to the asset to deem it unserviceable. The oil also leaked onto the ground and this spread approx. 2x3m in length. There was no damage to the customer's private property. The base of the pole was all grass & shrubbery. There was no damage to the customers private property. The base of the pole was all grass & shrubbery. | Pole mounted | 0 | 0 | 0 |  | ldl13 | Transformer internal fault. Oil leak - Mechanical damage (leaking gasket/broken bushing etc.). | Grassfire | 28/11/2017 13:45 | 1 | Localised: less than 10 sq.m | 6784 | Agricultural |  | 20171129SPN_01 | Infrastructure (network-based) | -37.8277 | 145.4528 | 1 | AusNet Services Distribution | Report | 10929 | 0.012216 | 22kV AC | Moorabbin Airport | 3139 | Wandin East | AF Other
replaced 1x 15E BA fuse. no ground fire found. | 8 FERN GULLY ROAD, COCKATOO VIC 3781 | 417489 |  |  |  | Candled fuse |  |  | 2 | IMS 230730 - fault truck dispatched and found candled BA fuse | Boric acid | 0 | 0 | 0 |  | BGE22 | candled fuse no photo available | Pole-top fire | 43079.7361 | 1 | Negligible: no ground fire | 6786 |  |  | 20171129SPN_03 | Infrastructure (network-based) | -37.9469 | 145.4881 | 1 | AusNet Services Distribution | Report | 12825 | 0.0045394 | 22kV AC | Moorabbin Airport | 3781 | Cockatoo | Fuse
Made safe and repairs made | 7-9 MEPHAN STREET, FOOTSCRAY VIC 3011 |  | Copper theft | [5 empty] | 2 | Earth stolen from a pole A036948 CHP to MEPHAN 9-GORDON | Copper;Earth;Earth/earthing | 0 | 0 | 0 |  |  | Copper earth cable stolen by unknown persons | Damage to network assets | 30/11/2017 17:30 |  |  | 6799 | Industrial |  | 20171130JEM_03 | Infrastructure (network-based) | -37.7868 | 144.8873 | 1 | Jemena | Report | 8565 | 0.017708 | Earthing cable | Essendon Airport | 3011 | Footscray | Other
CEOT dispatched a fault crew to make safe, and carry out necessary repairs. CEOT notified the local DAO to investigate the incident. ESV advised. CFA attended and extinguished the fire. CHP terminations replaced. | 1079 PLENTY ROAD, SOUTH MORANG VIC 3752 | 917432 |  |  |  | Electrical breakdown |  | Phase to phase |  | IMS 231481. Initial report:Pole fire @ lis#917432 at underground Cable Head Pole in an electricity easement. Grass fire in the area of approximate size 50m x 20m. Note - the provided address is the closest address in Plenty Rd to the CHP in question. Final report: DAO received a call from CEOT at approx.16.45, regarding a pole fire on BIDPO#917432. There was no fire on site when the DAO arrived. Pole #917432 is a HV 22kVA cable head pole. All phases (RWB 3x240 sq.mm) were burnt out above the heat shrink wrap on the cable head structure. The underground conductor was visible upon site inspection. The fire had also scorched the top of the pole, however the damage was not significant enough to deem it unserviceable. The melting and fire that was on the cable had caused a significant fire on the ground. This fire was measured at 5m in width and 60m in length. Due to the location, there was no damage to property or any other AusNet Services' assets. The fire was no threat to surrounding properties. No injuries occurred. Area was extremely dry, which contributed to the spreading of the grass fire. No wind at the time enabled the fire to be put out before it spread. No other asset damage occurred. | Pole (wood);Cable | 0 | 0 | 0 |  | drn11 | Underground asset failure - fault at the Cable Head Pole (CHP). | Grassfire | 29/11/2017 14:45 | 1 | Small: 10 - 1000 sq.m | 6791 | Other | Electricity easement | 20171130SPN_01 | Infrastructure (network-based) | -37.631 | 145.0959 | 1 | AusNet Services Distribution | Report | 8552 | 0.00064005 | 22kV AC | Essendon Airport | 3752 | South Morang | UG Cable
Attending electrical inspector isolated all properties and while service crews replaced the crossarm and carried out repairs. Once repairs were completed, the LV circuit was re energised and all accessible distribution metering equipment and customer switchboards and installations were inspected for damage before being reconnected to supply and damage notices issued. | 87 LINCOLN DRIVE, KEILOR EAST VIC 3033 |  |  |  |  | Rot |  |  | 1 | 66kV crossarm failed due to deterioration/rot. Causing the 66kV conductor falling into the LV conductor causing a High Voltage Injection. | Conductor (bare);Crossarm (wood);Aluminium | 0 | 2 | 0 |  |  | 66kV crossarm failed due to deterioration / rot resulting in a high voltage injection. | HV injection;Loss of supply | 42778.4201 |  |  | 6806 | Residential |  | 20171202JEM_03 | Infrastructure (network-based) | -37.7423 | 144.8671 | 1 | Jemena | Report | 8573 | 0.0273 | 66kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
LEI inspected installation and found no damage had been caused. | 166 PUMPS ROAD, RED CLIFFS VIC 3496 | 33064221 |  | Lightning |  |  |  |  | 1 | Report of lightning strike at the incident location. On arrival the crew found there had been a lighting strike to centre phase of RCTS-MBN 66/22KV had caused a small 300mm x 300mm grass fire around the earth stake of the customer installation. There were no reported shocks or injuries. | Pole (concrete);Customer installation | 2 | 2 | 2 |  | RCTS MBN 66kv | Lightning strike | Grassfire | 28/11/2017 18:26 | 1 | Localised: less than 10 sq.m | 6809 | Agricultural |  | 20171204PWA_02 | Infrastructure (network-based) | -34.299 | 142.2209 | 1 | Powercor | Report | 13081 | 0.017368 | Low voltage AC (<1kV);66kV AC | Mildura Airport | 3496 | Red Cliffs | Lightning
CEOT dispatched a fault crew to make safe and carry out necessary repairs. CEOT advised the local DAO to investigate the incident. Attending fault crew reported to the DAO and CEOT that there was evidence of a small fire. | 82 STONELEIGH ROAD, MANSFIELD VIC 3722 | 3918752 |  | Bird |  |  |  | Phase to earth | 1 | IMS 231500. CEOT received a pole fire reported from Vic Fire. A bird was found at the base of the concrete pole and there was a small grass fire of 1m x 1 m in size. 2 x HV Boric Acid fuses had operated. CFA attended prior to the arrival of AusNet Services' fault crew. | Boric acid;Pole (concrete) | 0 | 0 | 0 |  | msd1 | Bird Incident | Grassfire | 30/11/2017 21:17 | 1 | Localised: less than 10 sq.m | 6813 | Agricultural |  | 20171204SPN_02 | Infrastructure (network-based) | -37.0641 | 146.0755 | 1 | AusNet Services Distribution | Report | 10916 | 0.023356 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 2A KLAUER STREET, SEAFORD VIC 3198 | 3306551 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 1811hrs on 23/11/2017, 66kV feeder CRM-FTN-LWN circuit breaker successfully reclosed and held. At the same time 22kV feeder FTN 13 circuit breaker reclosed to lockout affecting 1852 customers. Emergency services have advised a car has hit a pole and knocked it down at the corner of Klauer Street and Frankston-Dandenong Road. A vehicle struck 66/22kV and LV pole (LIS No. 3306551) in Klauer Street west of Frankston-Dandenong Road causing it to snap and the HV/LV mid-span conductors to clash. Following the conductors clashing, splash marks were identified on the HV conductors after they made contact with the LV conductors and the faults crew requested a LEI attend as a HVI was suspected to customers supplied from "FTN DNG-Klauer" substation. The LEI confirmed a high voltage injection occurred (MOR 1702) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | 66kV CRM-FTN-LWN and FTN 13 | A vehicle struck 66/22kV and LV pole No. LIS No. 3306551 in Klauer Street, Seaford. | HV injection;Loss of supply | 23/11/2017 18:11 |  |  | 6818 | Roadway |  | 20171204UTD_04 | Infrastructure (network-based) | -38.1195 | 145.1459 | 1 | United Energy Distribution | Report | 8588 | 0.0026273 | Low voltage AC (<1kV);22kV AC;66kV AC | Moorabbin Airport | 3198 | Seaford | Vehicle
On arrival crew assessed damage and arranged repairs | 410 VICTORIA ROAD, TALLYGAROOPNA VIC 3634 | 33090222 |  | Bird |  |  |  |  | 1 | Following the recent storm events and a reclose on the SHTS-NKA No 2 line, a crew was asked to patrol 20 poles either side of the distance to fault that was recorded in the fault log. At P 109 SHTS-NKA No 1 line the crew found that a bird had flashed over an insulator, it had come to ground and started a ground fire of approximately 40 m X 6 m. No third party damage or injury was reported. | Conductor (bare) | 2 | 2 | 2 |  | SHTS NKA 2 SHN11 | Bird Incident | Grassfire | 42837.8208 | 1 | Small: 10 - 1000 sq.m | 6820 | Roadway |  | 20171205PWA_02 | Infrastructure (network-based) | -36.239 | 145.4651 | 1 | Powercor | Report | 8596 | 0.0062685 | 22kV AC;66kV AC | Shepparton Airport | 3634 | Tallygaroopna | Animal
Section was isolated and made safe. | 100 OLYMPIA STREET, TOTTENHAM VIC 3012 | Pole no. A033114 |  |  |  | Rot | Followed but inappropriate |  | 1 | HV Cable Head Termination Pole A033114 (which contained a 22kV switch and cable termination) failed due to rot. During restoration works, as the faults crew was applying earths to the adjacent Intermediate Tee off Pole A033113 for the access permit to replace Pole A033114, pole A033113 also failed just below ground line. For details of this pole failure, refer to OSIRIS incident report 20180710JEM_02. A copy of the investigation report is attached in the "Notes & Findings" section. | Conductor (bare);Pole (wood);Cable;Aluminium;Disconnector/isolator;Connector/termination | 1 | 0 | 0 |  | TH12 | Animal Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42778.3597 |  |  | 6824 | Industrial |  | 20171206JEM_02 | Infrastructure (network-based) | -37.8046 | 144.857 | 1 | Jemena | Report | 12268 | 0.0058368 | 22kV AC | Essendon Airport | 3012 | Tottenham | Pole
The faults crew isolated supply at the pole end (pole No. LIS 7058846) and a defect notice issued to the customer advising that a REC is required to inspect and repair the damaged meter panel following the lightning strike. 25/11/2017 - LEI Danny Morgan attended and completed Prescribed CES No. 15671066 after the REC replaced the damaged meter panel. The faults crew re-attended and installed a new meter and reconnected supply following the completion of installation tests that confirmed the fault had been rectified. | 6 CYPRESS AVENUE, TEMPLESTOWE LOWER VIC 3107 | 7058846 |  | Lightning |  | HV injection;Fault on customer installation |  |  | 2 | Customer called to advise that a large red spark emitted from the POA and they have lost their electricity supply. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, a single customer that resides at 6 Cypress Avenue advised that lightning struck the point of attachment. A faults truck attended and requested that a LEI attend as a HVI was suspected as the meter has melted to the meter panel. The LEI confirmed a high voltage injection occurred (BWD 1706) affecting the customer. | Smart meter;Meter board (including fuses) | 0 | 0 | 0 |  |  | Lightning strike at the POA. | HV injection;Melting or smoking only | 24/11/2017 20:22 |  |  | 6823 | Residential |  | 20171206UTD_02 | Infrastructure (network-based) | -37.768 | 145.1219 | 1 | United Energy Distribution | Report | 8600 | 0.030869 | Lightning;Other | Moorabbin Airport | 3107 | Templestowe Lower | Lightning
The line crew advised the control room (CEOT), checked HV Fuse at DON MONDA substation then HE021. Restored supply at 1147hrs. In the planning stage and site assessment of this task, HV suppression was considered and deemed not necessary as a control by supervisor when scoping works as new LVABC was being run under existing LV Open Wire conductors. During the investigation it was identified that the Ventia employee has not secured the roller and rope successfully whilst holding the LVABC clear of the slack bay of LV open wire. The rope has slipped and let go causing the LVABC to spring upwards and clash with the slack bay of LV open wire.Based on the available evidence identified through the ICAM process, it is most plausible that the individual has not followed due process by incorrectly securing the handline to roller. The individual is well trained in the task and has completed this task on numerous occasions. | 300 DON ROAD, BADGER CREEK VIC 3777 | 1402802 |  |  |  |  | Not followed;Poor or no communication;Poor workmanship | Phase to phase | 1 | IMS 227120. At approximately 11.05am a Line crew was installing new 150 mm sq. LVABC from pole CAM# 1402792 to pole CAM# 1402845 on Hannover Road, Healesville, utilising winder unit and rope. Due to existing LV open wire conductors being strung slack in the first span into Hannover Rd between pole CAM# 1402792 and pole CAM# 1402840, the crew installed a roller attached with a handline in the middle of this span to ensure new LVABC was kept clear of existing LV open wire whilst new LVABC was being run. As new LVABC was being pulled in, via the winder unit, the rope holding this roller in position to the new LVABC has slipped and let go. This has caused the rope hauling the new LVABC to flick up and hit the spreader on the LV open wire resulting in the LV conductors clashing. The White Phase HV fuse at HE021 (25E) blew as a result. No Ventia employees were injured because of this event and there was no risk to any members of the public. This incident is reported under the category of reduction of electrical safety and uncontrolled release of LV conductor. | Conductor (ABC);Conductor (bare) | 0 | 0 | 0 |  | wyk24 | The Ventia employee did not secured the roller and rope successfully whilst holding the LVABC clear of the slack bay of LV open wire. The rope has slipped and let go causing the LVABC to spring upwards and clash with the slack bay of LV open wire. | Loss of supply | 27/03/2017 11:10 |  |  | 6022 | Residential |  | 20170510SPN_01 | Infrastructure (network-based) | -37.6735 | 145.5392 | 1 | AusNet Services Distribution | Report | 7402 | 0.028161 | Low voltage AC (<1kV) | Moorabbin Airport | 3777 | Badger Creek | Other
Ground cover reinstated | 33 WILLIAMS LANDING BOULEVARD, WILLIAMS LANDING VIC 3027 | 30316494 | Working too close to underground cables | [5 empty] | 2 | An audit found a breach of no go zone near a HV UG power line at the incident location. Powercor staff investigated the site and found the HV and LV cables had been uncovered in one place,. Other areas had been excavated and steel rods have been driven. There have been no applications made through DBYD or Permit to work . No cable damage has been identified. No fire, outages or injuries reported. | Cable | 2 | 2 | 2 |  | LV007 | Unauthorized excavation work | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43013.3333 |  |  | 6035 | Public space |  | 20170512PWA_01 | Infrastructure (network-based) | -37.862 | 144.7536 | 1 | Powercor | Report | 7417 | 0.032564 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3027 | Williams Landing | Other
Feeder section was isolated and HV crossarm was replaced on the same day under HV permit. | 46 LACKENHEATH DRIVE, TULLAMARINE VIC 3043 | A045824 |  |  |  | Leakage |  |  | 2 | Evidence of charring at HV intermediate crossarm, which was half burnt through. No interruption to customer supply. No photo was available. | Crossarm (wood) | 0 | 0 | 0 |  | AW14 | Pole top fire due to tracking | Pole-top fire | 19/05/2017 13:13 | 1 | Negligible: no ground fire | 6058 | Residential |  | 20170519JEM_01 | Infrastructure (network-based) | -37.6961 | 144.8854 | 1 | Jemena | Report | 7446 | 0.035191 | 22kV AC | Essendon Airport | 3043 | Tullamarine | Crossarm
Crew attended and isolated supply from service pit | 13 HALL STREET, LORNE VIC 3232 | 30338895 | Unauthorised work | [5 empty] | 1 | Line crew were sent to abolish a premises. On arrival they found that the meter was lying on the ground and the house had been removed. The underground supply was tested and found to be de-energised. It was subsequently found that a 50 amp fuse on the supply pole had operated. There was no indication on site regarding who was responsible for the demolition. Supply isolated at pit. There was no injuries or ground fire. | Services cable;Connection to meter | 0 | 0 | 0 |  | CLC005 | Interference | Loss of supply | 22/05/2017 10:00 |  |  | 6060 | Residential |  | 20170523PWA_02 | Infrastructure (network-based) | -38.527 | 143.983 | 1 | Powercor | Report | 7448 | 0.0057917 | Low voltage AC (<1kV) | Avalon Airport | 3232 | Lorne | Other
On arrival crew carried out repairs | 3600 HATTAH-ROBINVALE ROAD, WEMEN VIC 3549 | 32141418 | Vehicle | [5 empty] | 2 | Vic Roads reported one of their vehicles hit and bought down power lines while dumping road fill at the incident location. On arrival the crew found that a Low Voltage (LV) service had been hit by a truck, resulting in it hanging low across the road. There were no reported injuries or other third part damage. | Services cable | 2 | 2 | 2 |  | WMN013 | Truck struck service line | Loss of supply;Damage to network assets | 43044.4049 |  |  | 6076 |  |  | 20170526PWA_02 | Infrastructure (network-based) | -34.7808 | 142.6393 | 1 | Powercor | Report | 7469 | 0.033162 | Low voltage AC (<1kV) | Mildura Airport | 3600 | Wemen | Vehicle
On arrival crew carried out repairs | 309 GUYS HILL ROAD, STRATHFIELDSAYE VIC 3551 | 33034052 | Working too close to underground cables | [5 empty] | 2 | A customer reports excavating and breaking a earth cable at the above location. A crew attended and found a substation earth cable had been excavated and broken. No protection operated. There were no reported shocks, injuries or ground fire start. | Earth/earthing | 2 | 2 | 2 |  | BGO013 | Excavation work for footpath | No Go Zone (contact);Damage to network assets | 19/05/2017 9:39 |  |  | 6088 | Public space |  | 20170529PWA_07 | Infrastructure (network-based) | -36.8113 | 144.3426 | 1 | Powercor | Report | 7481 | 0.001765 | Earthing cable | Bendigo Airport | 3551 | Strathfieldsaye | Dug up
CEOT dispatched a fault crew to make safe, investigate and arrange repair. The fault crew found that the light head on street light pole had caught fire. The fault crew isolated the supply at the pit. A new INCD was raised which was sent to the public lighting contractor to replace the street light lantern head. The lantern was replaced. | 755 PRINCES HIGHWAY, BERWICK VIC 3806 | 5765423 |  |  |  | Electrical breakdown |  |  | 2 | IMS 227798. CEOT received INCD from Fire Brigade for fire at pole. An attending AusNet Services fault crew found that a major road 2009 250 Watt HPS street lantern had suffered an internal meltdown. | Public lighting | 0 | 0 | 0 |  | BWN13 | The actual cause was not established. Most likely caused by overheating of the lantern's internal components. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors.) | Other electricity related | 42983.8472 | 1 | Negligible: no ground fire | 6081 | Roadway |  | 20170529SPN_01 | Infrastructure (network-based) | -38.0314 | 145.3417 | 1 | AusNet Services Distribution | Report | 11257 | 0.027836 | Low voltage AC (<1kV) | Moorabbin Airport | 3806 | Berwick | AF Other
CEOT dispatched a fault crew to make safe and investigate and arrange for any necessary repairs. The site where the irrigator sprinkler made contact with the overhead HV conductor was measured at 5 metres ground clearance, which was between poles 4 and 5 (2201062) Daw spur. The line was inspected by the Survey team and found the conductor to be below sag of AusNet Services' drawing EVX18/50 between these 2 poles. A construction crew re-sagged the cable between poles 3 (2201059) and 5 (2201062) Daw spur to EVX18/50 to gain a clearance of 7.0 meters at site where cable was low. Checked overhead conductors - no damage found. Action raised on AusNet Services' Technical Assessment Team Lead to review asset previous inspection details. Action raised on AusNet Services' Asset Maintenance & Support Manager to investigate electrical protection configuration and settings. | 254 MOE-WILLOW GROVE ROAD, TANJIL SOUTH VIC 3825 | 2201019 | Working too close to overhead lines |  |  |  |  | Phase to earth | 0 | IMS 228131. Customer's irrigation sprinkler made contact with HV overhead in paddock at pole 4 Daw spur 2201061. Customer name BS & SM Tabuteau, phone 0413215908. No Injuries occurred. Line protection did not operate and there was no supply outage. | Conductor (bare) | 0 | 0 | 0 |  | moe21 | Irrigation sprinkler made contact with overhead HV conductor. | No Go Zone (contact) | 29/05/2017 10:35 |  |  | 6089 | Agricultural |  | 20170529SPN_04 | Infrastructure (network-based) | -38.1189 | 146.253 | 1 | AusNet Services Distribution | Report | 12361 | 0.010449 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Tanjil South | Vehicle
On arrival crew isolated supply and carried out repairs | 368 DEAKIN AVENUE, MILDURA VIC 3500 | 32141697 |  |  |  | Overheated connection |  |  | 2 | CFA reported switch board fire, at the incident location. On arrival the crew found meter board had been fire damaged as the result of a fuse base failure, There were no reported injuries | Meter board (including fuses) | 2 | 2 | 2 |  | MDA033 | Overheated connection | Meter board | 43013.9847 | 1 | Negligible: no ground fire | 6112 | Residential |  | 20170601PWA_06 | Infrastructure (network-based) | -34.2036 | 142.1408 | 1 | Powercor | Report | 7511 | 0.011314 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Fuse
On arrival crew carried out repairs | 1060 MITCHELL ROAD, KIALLA EAST VIC 3631 | 30329181 |  | Bird |  |  |  |  | 1 | Customers advised fuses down and dim lights. On arrival the crew found a bird clashed the conductors, one conductor on ground and second frayed right in middle of bay, grass fire limited to small spots where conductor was laying on ground, There were no reported injuries, no property damage for the incident. | Conductor (bare) | 2 | 2 | 2 |  | STN011 | Bird Incident | Grassfire | 42921.8319 | 1 | Localised: less than 10 sq.m | 6117 | Agricultural |  | 20170605PWA_01 | Infrastructure (network-based) | -36.4567 | 145.4978 | 1 | Powercor | Report | 8076 | 0.011363 | 22kV AC | Shepparton Airport | 3631 | Kialla East | Animal
On arrival crew carried out repairs | 7 LIGHTBODYS ROAD, PORTLAND VIC 3305 | 30089611 | Working too close to overhead lines | [5 empty] | 1 | The control room reported feeder CB of PLD003 had operated and the feeder was off supply. Shortly after, a report was made to Powercor advising of a tip truck making contact with overhead High Voltage wires at the incident location. It appeared that the truck driver had tipped the truck rear trailer up underneath the line. The crew reported that the truck driver did experience a small tingle but no injuries. Paramedics assessed him onsite but he did not require any further treatment. No ground fire identified. | Conductor (bare) | 2 | 2 | 2 |  | PLD003 | tip truck contacted line | Minor shock;Loss of supply;Damage to network assets | 42922.9556 |  |  | 6130 | Roadway |  | 20170609PWA_01 | Infrastructure (network-based) | -38.322 | 141.5671 | 1 | Powercor | Report | 7536 | 0.014094 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
Ropes removed whilst CitiPower officer was on site and advised to keep clear. | 277R BRUNSWICK STREET, FITZROY VIC 3065 | 30168901 | Working too close to overhead lines | [5 empty] | 2 | CitiPower officer attended site and found that Abseilers had placed ropes over insulated 240 volt Service Cable running along facade of multi storey building. No damage or injury. | Services cable | 0 | 0 | 0 |  | CW013 | Interference | No Go Zone (no contact) | 42861.5 |  |  | 6133 | Residential |  | 20170609PWA_02 | Infrastructure (network-based) | -37.7989 | 144.9782 | 1 | CitiPower | Report | 7539 | 0.026633 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Other
On arrival crew carried out repairs | STATION STREET, WOORINEN SOUTH VIC 3588 | 32159753 | Vehicle | [5 empty] | 2 | Fire Brigade and Customer advised of car into pole, at the incident location. On arrival the crew found a damaged concrete service pole leaning at 45 degrees , service cable and junction box damaged. There were no reported property damage, report of injured passenger in car. | Service conductor;Pole (concrete) | 2 | 2 | 2 |  | SHL004 | Vehicle collided with pole | Loss of supply;Damage to network assets | 42983.9771 |  |  | 6157 |  |  | 20170614PWA_02 | Infrastructure (network-based) | -35.2917 | 143.4481 | 1 | Powercor | Report | 7567 | 0.036528 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3588 | Woorinen South | Vehicle
CEOT dispatched a field crew to investigate and they discovered a candling EDO fuse.The fuse tube was burnt in half but still in the fuse holder. No ground fire present. The crew replaced the fuse holder and fuse link. | 72 PALMERS ROAD, LAKES ENTRANCE VIC 3909 | 1902525 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 228272. Customer reported sparking wires & flames from pole on cnr Golflinks Rd and Sea Lakes Rd, Lakes Entrance. An AusNet Services fault crew attended pole substation McColley-Palmer and found a EDO fuse tube had burnt in half. No ground fire occurred. | EDO fuse | 0 | 0 | 0 |  | BDL41 | EDO fuse tube burnt. | Other electricity related | 31/05/2017 21:10 | 1 | Negligible: no ground fire | 6156 | Residential |  | 20170614SPN_01 | Infrastructure (network-based) | -37.8704 | 148.0084 | 1 | AusNet Services Distribution | Report | 11260 | 0.011859 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | Fuse
Operator attended site, completed isolations and restored supply. Fault crew completed repairs to overhead conductor. | 120-200 ROSAMOND ROAD, MARIBYRNONG VIC 3032 |  | Vehicle | [5 empty] | 1 | MFB reported sparking wires on pole number A037434. A vehicle has hit the overhead service running across Rosamond Road and caused the HV overhead conductors to clash, bringing down the white phase. | Conductor (bare) | 0 | 0 | 0 |  | YVE23 | Vehicle impact on overhead line | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/06/2017 14:23 |  |  | 6165 | Roadway |  | 20170615JEM_01 | Infrastructure (network-based) | -37.7729 | 144.8864 | 1 | Jemena | Report | 7577 | 0.018012 | 22kV AC | Essendon Airport | 3032 | Maribyrnong | Vehicle
On arrival crew carried out repairs | 8 CELLANA COURT, PORTLAND VIC 3305 | 30093294 | Vehicle | [5 empty] | 2 | A customer reports a high load had struck the wire to the building at the above location. A crew attended and found a service cable to the building had been struck and damaged. There were no reported shocks, injuries or ground fire start. | Service conductor | 2 | 2 | 2 |  | PLD006 | Truck exhaust struck service | Loss of supply;Damage to network assets | 30/05/2017 12:08 |  |  | 6161 | Construction |  | 20170615PWA_01 | Infrastructure (network-based) | -38.3648 | 141.6231 | 1 | Powercor | Report | 7571 | 0.030801 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out or arrange for any necessary repairs to be done. | 33 YARRAM-MORWELL ROAD, YARRAM VIC 3971 | 2622116 | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | IMS 228521. CEOT received call from a customer that truck had hit a service cable. An AusNet Services' fault crew attended and found that a tip truck with a raised tipper tray had contacted overhead HV conductor. A tip truck that had its tray lifted came into contact with the HV conductor. The actual location was on the customer's private drive way that was gravel. The height measured after the incident was 6.6m. The conductor was 3/2.75 steel, and the contact was almost mid span with the span to be estimated approx. 250m in distance. The closest CAM# is 2622116. The driver was not at the site when AusNet Services crew arrived. | Conductor (bare) | 0 | 0 | 0 |  | ftr21 | Tipper truck tray made contact with overhead HV conductor. | No Go Zone (contact) | 14/06/2017 8:40 |  |  | 6162 | Agricultural |  | 20170615SPN_01 | Infrastructure (network-based) | -38.5529 | 146.6505 | 1 | AusNet Services Distribution | Report | 7573 | 0.027769 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Yarram | Vehicle
On arrival crew carried out repairs | 45 KENSINGTON ROAD, SOUTH YARRA VIC 3141 | 30216509 |  |  |  | Overheated connection |  |  | 2 | MFB reported light pole on fire and sparks hitting the ground at the above incident location. On arrival, the crew found an IPC (insulation piercing connector) overheated and melted away onto the ground. There was no ground fire nor third party damaged. There were no reported injuries. No images captured by CitiPower. | Conductor (insulated) | 2 | 2 | 2 |  | TK009 | connection failure | Melting or smoking only | 28/05/2017 18:38 |  |  | 6174 |  |  | 20170619PWA_03 | Infrastructure (network-based) | -37.8366 | 145.0014 | 1 | CitiPower | Report | 12459 | 0.015083 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Connection
The faults crew replaced the copper transformer earth cable and re-installed the timber cover guards at pole No. LIS 1103759. | 1675 STUMPY GULLY ROAD, MOOROODUC VIC 3933 | 1103759 | Copper theft | [5 empty] | 2 | Copper Theft - Copper transformer earth cable was stolen outside 1675 Stumby Gully Road, Somerville. A Select Solutions Asset Inspector identified the copper transformer earth cable was stolen from substation pole "Stumpy G P7-Eramosa" substation located outside 1675 Stumpy Gully Road, Somerville. | Conductor (bare);Copper;Earth/earthing | 0 | 0 | 0 |  | MTN 22 | Unknown persons stole the copper earth cable from a substation pole. | Damage to network assets | 19/06/2017 8:00 |  |  | 6170 | Agricultural |  | 20170619UTD_03 | Infrastructure (network-based) | -38.2242 | 145.1348 | 1 | United Energy Distribution | Report | 7582 | 0.040595 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Other
On arrival crew carried out repairs | 222-224 PELHAM STREET, MELBOURNE VIC 3000 | 30183613 | Working too close to underground cables | [5 empty] | 1 | During excavation or a gas main an excavator trenching east along Pelham st contacted EW conduits Conduit broken and LV steel wire armoured mains damaged. DBYD documentation and plans on site. There was no fire, injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BQ014 | Excavation near cable | Loss of supply;No Go Zone (contact);Damage to network assets | 42741.5625 |  |  | 6181 | Roadway |  | 20170620PWA_01 | Infrastructure (network-based) | -37.8019 | 144.9585 | 1 | CitiPower | Report | 7597 | 0.028407 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew carried out repairs | 12 MCIVOR ROAD, ST ALBANS VIC 3021 | 30148854 | Vehicle | [5 empty] | 2 | There was a report from Vic Fire that of a passing unidentified truck has struck he service cable at the incident location. Upon arrival the crew found that the service cable has been hit by an unknown truck travelling in a northerly direction along Erica Avenue. The service cable was lying in the front nature strip at the incident location with the other end lying on the road. The force of the service cable being pulled north has caused considerable damage to the POA & roof / roof tiles of #12 McIvor Road, St Albans 3021. There were no reported shockâ€™s, injuries or fire. | Service conductor | 2 | 2 | 2 |  | SA007 | Unknown truck struck service | Loss of supply;Damage to network assets | 42771.8722 |  |  | 6182 | Roadway |  | 20170620PWA_02 | Infrastructure (network-based) | -37.742 | 144.8031 | 1 | Powercor | Report | 7598 | 0.02126 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Vehicle
Electrical network operator switched and issued access permit for repairs to broken LV crossarm and HV dropper at fuse units by Jemena Fault Crew. LV bus and HV overhead was isolated to make safe and repairs initiated by Jemena work party. Supply was restored via LV at 0039. | 15 ARGYLE STREET, RESERVOIR VIC 3073 |  |  |  |  | Mechanical breakdown |  |  | 1 | LV subpole crossarm broke and caused the LV conductor to clash with HV dropper at fuse units, resulting in a flashover and pole top fire. | Conductor (ABC);Crossarm (wood);Dropper/bridge | 0 | 0 | 0 |  | TT3 | LV crossarm broke and caused the LV conductor to clash with HV dropper. | Pole-top fire | 20/06/2017 23:00 | 1 | Negligible: no ground fire | 6183 | Residential |  | 20170621JEM_01 | Infrastructure (network-based) | -37.704 | 145.0249 | 1 | Jemena | Report | 7600 | 0.029626 | 22kV AC | Essendon Airport | 3073 | Reservoir | Crossarm
Razor wire re-instated, most remaining cable drums (in the open) removed to Tullamarine store and a few drums placed in an on-site container. General clean-up was carried out for open and public visible areas of all materials, even empty drums. Wilson Security has been informed of site break-in and asked when the last patrol of site was performed to gauge intrusion period. They are engaged to perform 3x night patrols with additional weekend day patrol. Incident will be reported to Victoria Police after stolen cable value is estimated. | 44 MOORE ROAD, AIRPORT WEST VIC 3042 |  | Copper theft | [5 empty] | 2 | Airport West zone substation was broken-in at night. The intruders cut the razor wire, then cut the main gate lock from inside and let their trailer in. Six cable drums were stolen. Field crew first person on site discovered front gate wide open at approximately 7am, padlock shank cut. Construction Manager assessed the site at 7.25AM same day. | Zone substation | 2 | 2 | 2 |  |  | Copper theft | Damage to network assets | 22/06/2017 7:25 |  |  | 6196 | Industrial |  | 20170626JEM_01 | Infrastructure (network-based) | -37.7162 | 144.8858 | 1 | Jemena | Report | 7617 | 0.038794 | Not applicable | Essendon Airport | 3042 | Airport West | Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 3 Volts no load to 8 Volts maximum load. Service crew discovered the corrosion and deterioration of the neutral screen conductor termination at the take-off box on the Powercor pole. The crew installed a new ABC service and performed NST at the POA with a pass result recorded. | UNIT 4 63 CALDER STREET, MANIFOLD HEIGHTS VIC 3218 | 31035059 |  |  |  | Corrosion |  | Phase to earth | 2 | Laurence was standing in the shower, having a shower, when he felt a tingle to his left hand when adjusting the shower tap. | Service conductor;Connection box | 2 | 2 | 2 |  | GL012 | Corrossion of connections in Pole Junction box | Minor shock | 31/05/2017 19:00 |  |  | 6194 | Residential |  | 20170626PWA_02 | Infrastructure (network-based) | -38.144 | 144.3296 | 1 | Powercor | Report | 17439 | 0.038648 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Manifold Heights | Connection
Crew attended, cleared conductor from vehicle and restored to top of poles. | 909 NAREEN ROAD, NAREEN VIC 3315 | 32126288 | Vehicle | [5 empty] | 1 | The customer reported a wire off pole and over a truck at the incident location. On arrival the crew found that the SWER conductor had fallen on a log truck and the truck drove off pulling down 5 bays of conductor before stopping. The log loader used to load the truck was next to the track which the conductor was over but neither vehicle showed signs of electrical contact. Vehicle operators stated they didnâ€™t notice the conductor had fallen or any contact with it when loading. Danger signs for the line were in place, with one fallen over near the log loader. No injuries were reported. No ground fire. No third party damage. Protection systems operated as expected. | Conductor (bare) | 0 | 0 | 0 |  | HTN006 | Most probable is vehicle impact with pole | Loss of supply | 25/06/2017 12:56 |  |  | 6195 | Forest - plantation |  | 20170626PWA_03 | Infrastructure (network-based) | -37.4448 | 141.5841 | 1 | Powercor | Report | 7801 | 0.031557 | 12.7kV AC (SWER) | Hamilton Airport | 3315 | Nareen | Vehicle
AusNet Crew leader spoke to 3rd party onsite - Ross Jarvis, Director of Jarvis Norwood Construction who owns the crane involved. The crane was traveling with boom raised, the crane operator was unaware he had struck the overhead conductor, operator cited poor visibility. LV conductors were tested and found alive on ground. No LV fuses were blown at Sub that supplied the LV which was located 6 bays away. LV conductors were isolated by breaking bridges on LIS No 2501720. New LV conductor 4 x 7/300ACC was replaced between LIS No 2501720 and 2501721 LV supply restored and NST test conducted. All customers back on supply. Height of LV Conductor before incident unknown. Height of replaced LV conductor 6.2 metres from ground. A request has been made to the local Delivery Manager to forward a No-Go Zone breach letter to the offending party. | 6 PARK STREET, SALE VIC 3850 | 2501720 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 2 | IMS228384 - A crane hit and took LV conductors down at Park St Sale. 1 bay of Low voltage overhead conductor bought to ground by the crane. Near Bridge construction site. The operator was traveling with boom raised and cited no/poor visibility. LV Conductors damaged - 4 x 064 copper bare conductor - between LIS no 2501720 and 2501721HV Inter - LV termination. Nil Injury. | Conductor (bare) | 0 | 0 | 0 |  | SLE 11 | Crane boom contacted LV condutor | No Go Zone (contact) | 42922.3958 |  |  | 6197 | Commercial |  | 20170626SPN_01 | Infrastructure (network-based) | -38.1126 | 147.061 | 1 | AusNet Services Distribution | Report | 7618 | 0.030456 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | Vehicle
On arrival crew carried out repairs. A defect notice was issued to customer to repair POA | 271 PLANTATION ROAD, CORIO VIC 3214 | 30292453 | Vehicle | [5 empty] | 2 | A customer advised that a garbage truck had hit the service last Friday but power was not interrupted. Upon arrival the crew found that the service and the POA had been damaged. No details forthcoming about the vehicle. There was no fire or injuries. | Service conductor | 2 | 2 | 2 |  | CRO013 | Unknown vehicle struck service | Damage to network assets | 42922.4556 |  |  | 6206 | Residential |  | 20170629PWA_01 | Infrastructure (network-based) | -38.0648 | 144.3421 | 1 | Powercor | Report | 7639 | 0.041569 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded / burnt Neutral Screen Conductor of an O/H Aluminium Neutral Screened Service Cable. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. | 4 TUDBALL COURT, BACCHUS MARSH VIC 3340 | 32172575 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Hayden Watt-Beckhurst was in the front garden washing his hands when he received an electric shock as he made simultaneous contact with his hand on the front external Garden Tap while standing on the wet ground washing his hands | Service conductor | 2 | 2 | 2 |  | BMH004 | Corroded service neutral | Minor shock | 19/05/2017 14:00 |  |  | 6208 | Residential |  | 20170629PWA_03 | Infrastructure (network-based) | -37.6696 | 144.4349 | 1 | Powercor | Report | 7641 | 0.0069711 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Bacchus Marsh | OH Cable
on arrival crew isolated site to clean up and restoration of installation. | 2 WALCHS ROAD, NORTH SHORE VIC 3214 | 30070111 | Copper theft | [5 empty] | 2 | A customer reported an attempted theft at the above location. A crew attended and found the spare customer mains in the substation site had been tampered with. The crew isolated the site to allow access. No protection operated. There were no reported shocks, injuries, third party damage or fire start. | Customer installation | 2 | 2 | 2 |  | CRO032 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/06/2017 14:41 |  |  | 6218 | Industrial |  | 20170630PWA_01 | Infrastructure (network-based) | -38.0936 | 144.3738 | 1 | Powercor | Report | 7681 | 0.0040093 | Low voltage AC (<1kV) | Avalon Airport | 3214 | North Shore | Other
Crew attended and replaced connection between LVABC and bare conductor | 140 THE PARADE, OCEAN GROVE VIC 3226 | 31011583 |  |  |  | Overheated connection |  |  | 2 | A passer-by reported flames coming from the pole at the incident location and had called the CFA. The attending crew found that an IPC on a bare conductor interface had failed and fallen to the ground. | Conductor (ABC);Conductor (bare) | 0 | 0 | 0 |  | DDL011 | overheated connection, unable to determine if loose | Loss of supply;Melting or smoking only | 42773.7639 |  |  | 6227 | Roadway |  | 20170706PWA_01 | Infrastructure (network-based) | -38.2668 | 144.5308 | 1 | Powercor | Report | 7666 | 0.0028669 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
CEOT sent crew to investigate. Found CapBank Can was leaking and had small fire. Isolated and put out with CO2 extinguisher from outside the fence. Spill kit pads used to soak up liquid. Management Advised. Investigation completed. The No.2A Cap Bank has been isolated and the failed capacitor is scheduled to be replaced. | 61 GLENFERN ROAD, FERNTREE GULLY VIC 3156 | 1302470 |  |  |  | capacitor can insulation breakdown;Other |  |  | 1 | IMS 229035. On the 6/07/2017 at 08:31hrs the No2A 22kV Cap Bank CB closed by its VAR controller. A short time later the FGY 22kV Feeders indicated intermittent Phase-Neutral Amps of various magnitudes via SCADA. At 08:49hrs, the FGY22 Feeder CB tripped, reclosed and tripped. The DFA on FGY22 triggered and sectionalised a fault below switch BG874 and restored supply to the remainder of the feeder. Supply was interrupted to 1,009 customers. The first responder reported smoke coming from the No2A Cap Bank cabinet and a small fire was observed on one of the capacitor units that was quickly put out with a CO2 fire extinguisher. The small fire was contained within the metal cabinet where the capacitor can sits. | Zone substation | 0 | 1 | 0 |  | FGY22 | Investigation completed with following findings: The root cause of the intermittent internal capacitor can failure is believed to be due to insulation failure between capacitor foils within the can. Intermittent nature of the capacitor fault does not last long enough to trigger the circuit breaker to trip. The non-operation of the No2 Cap Bank protection relay was confirmed to be correct and as expected for an intermittent type fault. The Cap Bank protection relay was subsequently tested and found to operate as designed. | Loss of supply;Plant/equipment | 42893.3674 | 1 | Negligible: no ground fire | 6231 | Other | Zone Substation | 20170706SPN_03 | Infrastructure (network-based) | -37.8935 | 145.2921 | 1 | AusNet Services Distribution | Report | 12824 | 0.023248 | 22kV AC | Moorabbin Airport | 3156 | Ferntree Gully | AF Other
On arrival crew commenced repairs. | ALEXANDRA AVENUE, MELBOURNE VIC 3004 | 30244109 | Working too close to underground cables | [5 empty] | 2 | Contractor reported that they have damaged a cable at the incident location. On arrival the fault crew found that a contractor installing conduits for Vic Roads had bored into a low voltage underground cable (public lighting) at the incident location. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | MP001 | Contractor installing conduits | Damage to network assets | 42984.8535 |  |  | 6234 | Public space |  | 20170710PWA_01 | Infrastructure (network-based) | -37.8234 | 144.9762 | 1 | CitiPower | Report | 7675 | 0.016141 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Dug up
On arrival crew carried out repairs | 2-4 57 CARDIGAN STREET, CARLTON VIC 3053 | 30211827 |  |  |  | Overheated connection |  |  | 2 | A customer reported that power has been lost and there is a burning smell coming from behind the meter at the incident location. On arrival the fault crew found that the white and blue phase conductors had shorted out inside a connection box causing arcing, sparking and melting of insulation at the incident location. There was no fire and no injury as a result of this incident. | Connection box | 2 | 2 | 2 |  | BQ015 | overheated connection | Melting or smoking only | 15/06/2017 12:13 |  |  | 6236 | Residential |  | 20170712PWA_01 | Infrastructure (customer connection) | -37.8054 | 144.9644 | 1 | CitiPower | Report | 7691 | 0.012566 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Connection
The first responder arrived on site proceeded to open the switch to make site safe. Subsequently fault crew has installed a termination clamp. | 180 MONOMEITH ROAD, MONOMEITH VIC 3984 | 513162 |  |  |  | Corrosion;Mechanical breakdown |  | Phase to earth | 0 | IMS229089 - Incorrect AMPAC bail was installed on corroded 3/12 steel conductor which caused the 22kV bare conductor to break and fell on the ground, live and backfeeding. | Conductor (bare) | 0 | 0 | 0 |  | LLG11 | Incorrect AMPAC bail was installed on corroded 3/12 steel conductor which caused the 22kV bare conductor to break | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42985.7125 |  |  | 6243 |  |  | 20170713SPN_01 | Infrastructure (network-based) | -38.2169 | 145.5291 | 1 | AusNet Services Distribution | Report | 7910 | 0.028586 | 22kV AC | Moorabbin Airport | 3984 | Monomeith | AF Other
The fire choke was pushed back to its hinged position(it was stuck) using an operating stick. The bottom half of the fuse tube was removed, a new fuse tube inserted and supply restored. | 234 WATERS LANE, COLAC COLAC VIC 3707 | 5215357 |  |  |  | Defective component;Candled fuse |  | Phase to phase | 0 | IMS 229085 - Linesmen attended a no supply report at "Colac 10E" substation. On arrival they found the top half of an EDO fuse tube on the ground at the base of the pole and the bottom half of the tube still hanging in the fuse unit at the top of the pole. The pole is a concrete pole fitted with hinged fire choke type EDO units. The fire choke was still in its normal position, it had not swung open and the fuse tube was resting against it. It was raining at the time and there was no evidence of a fire on the ground. | EDO fuse | 0 | 0 | 0 |  | WOTS24 | EDO fuse tube malfunction resulted in fuse candling | Other electricity related | 42954.3167 | 1 | Negligible: no ground fire | 6246 | Agricultural |  | 20170713SPN_02 | Infrastructure (network-based) | -36.2312 | 147.8491 | 1 | AusNet Services Distribution | Report | 12813 | 0.015679 | 22kV AC | Wangaratta Aero | 3707 | Colac Colac | AF Other
Supply to area interrupted. Crew carried out repairs when safe to do so | 344 GLENELG HIGHWAY, HAMILTON VIC 3300 | 32135990 | Unknown external/community factor | [5 empty] | 2 | A boat factory business known as â€œRadleys of Hamiltonâ€ suffered a significant fire when it was reported on site that a worker had accidental started a fire in the workshop. Heat from the fire resulted in the Red Phase Aluminum Low Voltage mains conductor, located in the street, failing mid span and falling to ground. The fire was reported as being quiet large and CFA crews were fighting the fire in proximity to live HV and LV conductors. In consideration of safety to CFA crews and other emergency services, Powercor crews undertook HV switching to isolate supply to the surrounding area. This affected supply to approximately 2,400 customers. | Conductor (bare) | 2 | 2 | 2 |  | HTN004 | external fire in factory | Loss of supply;Significant disruption to the community | 13/07/2017 15:50 |  |  | 6258 | Industrial |  | 20170717PWA_01 | Infrastructure (network-based) | -37.7222 | 141.9927 | 1 | Powercor | Report | 7712 | 0.013713 | Low voltage AC (<1kV);22kV AC | Hamilton Airport | 3300 | Hamilton | Other
On arrival crew carried out repairs | 17 CORRIGAN STREET, WARRNAMBOOL VIC 3280 | 35319621 | Working too close to underground cables | [5 empty] | 1 | A Downer employee reported they had hit an UG cable at the incident location. On arrival the crew found that an under road boring machine had struck a 240V UG mains cable. The work crew had a blanket Permit To Work for the area #46258, and told the Powercor crew who attended that they had identified the location of the cable prior to commencing to bore. There was no other reported third party damage or any injuries. | Cable | 2 | 2 | 2 |  | WBL005 | Contractor struck cable | Loss of supply;No Go Zone (contact) | 23/06/2017 11:54 |  |  | 6259 | Roadway |  | 20170717PWA_02 | Infrastructure (network-based) | -38.3598 | 142.5012 | 1 | Powercor | Report | 7713 | 0.022398 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Dug up
On arrival crew carried out repairs. REC repaired mains box | 18 LAWRENCE STREET, CASTLEMAINE VIC 3450 | 30037417 | Vehicle | [5 empty] | 2 | A customer reports a delivery truck has pulled down the service to the house at the above address. A crew attended and found the service had been pulled off the point of attachment on the building. The delivery truck was not onsite when the crew attended. The service cable had pulled off the building and was laying on driveway alive. There were no reported shocks, injuries or fire start. | Service conductor | 2 | 2 | 2 |  | CMN001 | Vehicle struck service | Loss of supply;Damage to network assets | 23/06/2017 12:20 |  |  | 6260 | Roadway |  | 20170717PWA_03 | Infrastructure (network-based) | -37.076 | 144.2081 | 1 | Powercor | Report | 7714 | 0.0361 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Vehicle
On arrival crew commenced repairs | 475 BELLARINE HIGHWAY, MOOLAP VIC 3224 | 32070833 | Vehicle | [5 empty] | 1 | A passer-by (Mrs Wendy Ogilvie) reported that a car has crashed into the pole outside 475 Bellarine Highway corner of Kancy Street. Pole is broken at base and is resting on the car. Occupant no longer in the vehicle. Pole is leaning out towards the highway and wires are still attached at pole ends but very tight at the incident location. On arrival the fault crew found that a car had collided with and broke the pole at its base, pole being supported by the overhead conductors at the incident location. There was no ground fire as a result of this incident. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | GLE024 | Vehicle collided with pole | Loss of supply;Damage to network assets | 23/06/2017 13:00 |  |  | 6261 | Roadway |  | 20170717PWA_04 | Infrastructure (network-based) | -38.182 | 144.4352 | 1 | Powercor | Report | 7716 | 0.027479 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3224 | Moolap | Vehicle
A faults truck attended to check the integrity of the pole and found the car had struck the underground cable guard that caused minor fire damage to the underground cabling near the top of the pole stake when the underground cable was squashed that caused a minor phase to phase flashover. Minor repairs were completed and the pole will be programmed for replacement within 30 days. | 278 BEACH ROAD, BLACK ROCK VIC 3193 | 1817994 | Vehicle | [5 empty] | 2 | Per MFB - Pole fire. A vehicle contacted a staked LV intermediate pole (LIS No. 1817994) located outside 278 Beach Road, Black Rock that caused a pole fire to occur. The MFB were in attendance but the fire self extinguished prior to their attendance. | Pole (wood);Cable | 0 | 0 | 0 |  |  | A vehicle contacted an LV intermediate pole and the underground cable was squashed that caused a flashover and burns to the pole. Photos were taken but were not available when the report was submitted. | Pole-top fire | 25/06/2017 13:15 | 1 | Negligible: no ground fire | 6272 | Roadway |  | 20170721UTD_04 | Infrastructure (network-based) | -37.9732 | 145.0143 | 1 | United Energy Distribution | Report | 7873 | 0.031992 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Black Rock | Vehicle
The site was defected, the service and meters were removed. | 61 CUTHBERT STREET, BROADMEADOWS VIC 3047 |  | Unauthorised access | [5 empty] | 2 | Whilst crews were working at the 61 Cuthbert St, Broadmeadows, completing a pole to pit installation, the crew noticed a suspicious looking BTS with a grey twist service connected to it. | Service conductor;Aluminium twisted (grey);Smart meter | 0 | 0 | 0 |  |  | The property owner was on site and advised his name was "John" and he was the "Owner". When the compliance officer asked him who did the connection he said "the abolishment guy" and when the compliance officer asked who is the abolishment guy he replied "Roman, do you know Roman?". He then went on to say that "the overhead service was connected to the old house" | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/07/2017 16:39 |  |  | 6278 | Residential |  | 20170724JEM_01 | Infrastructure (network-based) | -37.6847 | 144.9303 | 1 | Jemena | Report | 7735 | 0.00026968 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Other
On arrival crew commenced repairs HVI Damage being assessed | 203 ALMA ROAD, ST KILDA EAST VIC 3183 | 30219544 | Working too close to overhead lines | [6 empty] | CitiPower fault crew attending an outage (BC013 feeder) found a scissor lift made contact with LV/HV lines at the incident location. The lift first contacted the LV and then flicked on to the HV conductors. No injuries or fire found. There was HVI but the damages have not been assessed yet. Work Safe and ESV informed. | Conductor (bare) | 2 | 2 | 2 |  | BC013 | Scissor lift contacted LV | HV injection;No Go Zone (contact);Damage to network assets | 25/07/2017 14:27 |  |  | 6293 | Public space |  | 20170726PWA_01 | Infrastructure (network-based) | -37.8633 | 145.0053 | 1 | CitiPower | Report | 7756 | 0.037288 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3183 | St Kilda East | Vehicle
On arrival crew carried out initial repairs. | 3076 MERIDIAN ROAD, MERRINEE VIC 3496 | 32141660 |  | Bird | [5 empty] | Emergency Services reported a grass fire at the incident location. Upon arrival, the Powercor crew found that a bird flashover between HV flex and steel crossarm . No other obvious damage on network assets found. There was a small grass fire, no injuries reported. | Dropper/bridge | 2 | 2 | 2 |  | RCT023 | Bird Incident | Grassfire | 25/07/2017 11:49 | 1 | Small: 10 - 1000 sq.m | 6295 | Agricultural |  | 20170726PWA_02 | Infrastructure (network-based) | -34.3597 | 141.9798 | 1 | Powercor | Report | 7759 | 0.0082836 | 22kV AC | Mildura Airport | 3076 | Merrinee | Animal
On arrival crew carried out repairs | 167 STATION ROAD, DEER PARK VIC 3023 | 30115143 |  |  |  | Corrosion |  |  | 2 | Powercor was contacted by customers indicating no supply. It was discovered that at the incident location, the road-side LV phase conductor had separated into two pieces between an LV insulating piercing connector and a copper to Aluminium tee clamp. The live side of the LV conductor remained in the air, restrained by the coiled line tie on the crossarm LV insulator. The Powercor crew found an LV conductor on the ground in the Station Rd., median strip, this span of LV conductor that fell to the ground was de-energized by the break. There were no reported injuries. There were no reports of ground fire. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | SU022 | corroded connection | Loss of supply | 42742.1403 |  |  | 6302 | Public space |  | 20170726PWA_08 | Infrastructure (network-based) | -37.7584 | 144.7765 | 1 | Powercor | Report | 7768 | 0.01238 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Connection
Crew called CEOT and confirmed no one was hurt. Conductor was isolated and made safe. The work crew under EAP repaired the line and restored the line after it was fixed. Investigator reviewed previous asset (aerial) inspection record (May 17) and photo assessment which found no defects then, concluded it was localised corrosion of the conductor that could not be picked up by visual assessment, and cleared the G&B crew the likelihood of incorrect working method. Photos attached in tab 7. An suggestion to improve assessment quality using thermal inspection is being discussed. | 609 TARRA VALLEY ROAD, DEVON NORTH VIC 3971 | 2610764 |  |  |  | Corrosion |  | Phase to earth | 0 | IMS 229609. At Lis 2610764 3/12 steel conductor broke from load side of pole. G&B crew working on NEMS 340314 fitting vibration dampers. The conductor broke under the existing armour rod during installation - 3/12 steel conductor was old but no visible cavity or damage was noticed and the work was minimal, hence the crew proceeded after work assessed as safe to progress. No protection operated. | Conductor (bare) | 0 | 0 | 0 |  | ftr12 | Localised corrosion of the steel conductor. | Loss of supply | 21/07/2017 11:05 |  |  | 6297 | Agricultural |  | 20170726SPN_01 | Infrastructure (network-based) | -38.5199 | 146.6577 | 1 | AusNet Services Distribution | Report | 7949 | 0.038801 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Devon North | Conductor
Jemena emergency response team and MFB attended incident to extinguish fire. Jemena fault crew isolated supply from Krone switch at pole no. A0109445 to services pit. The underground LV cable and service pit have both been replaced. | 4 LIVINGSTONE STREET, IVANHOE VIC 3079 | Pole no. A109445 |  |  |  | Defective component |  |  | 2 | Service pit in laneway off Kenilworth Parade was reported by MFB to be "smoking". Underground LV cable was found by Jemena fault crew to be burnt. Photo in relation to this incident is not available | Cable;Services pit | 0 | 0 | 0 |  | FF90 | Underground LV cable fault | Other electricity related | 25/07/2017 11:17 | 1 | Negligible: no ground fire | 6310 | Residential |  | 20170727JEM_01 | Infrastructure (network-based) | -37.7687 | 145.0411 | 1 | Jemena | Report | 12945 | 0.018316 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | UG Cable
On arrival crew isolated supply and carried out repairs. | UNIT 1 267 CURETON AVENUE, MILDURA VIC 3500 | 33062567 | Vehicle | [6 empty] | Emergency services reported wires sparking at roundabout after a truck had pulled a three phase twisted service down at the incident location. Upon arrival the crew found that three actives had been pulled to the ground and were sparking and the neutral had been pulled through the neutral clamps at the POAâ€™s slightly. The vehicle and driver details are unknown There were no reported injuries or third party damage. | Service conductor | 2 | 2 | 2 |  | MBN023 | Truck struck service line | Loss of supply;Damage to network assets | 42801.65 |  |  | 6307 | Roadway |  | 20170727PWA_03 | Infrastructure (network-based) | -34.1722 | 142.1579 | 1 | Powercor | Report | 7773 | 0.037034 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Vehicle
Upon reinstatement crew fitted a raiser bracket on the crossarm. The REC relocated the POA to an undamaged section of facia. | 30 ROSS STREET, TATURA VIC 3616 | 32186826 | Vehicle | [6 empty] | Customer reported an unknown truck had struck the overhead service supplying her premise and that the power was off at the incident location. Customer rang back a second time to advise the service was down across the road & was also resting on top of the neighbours vehicle. The service had been torn away at the customers end, damaging the facia. Customer was arranging an REC to carry out repairs, crew disconnected service pending repairs. There was no ground fire, no reported injuries, no 3rd party damage | Service conductor | 2 | 2 | 2 |  | MNA014 | Unknown vehicle struck service | Loss of supply;Damage to network assets | 42985.2764 |  |  | 6320 | Roadway |  | 20170728PWA_06 | Infrastructure (network-based) | -36.4378 | 145.2229 | 1 | Powercor | Report | 7787 | 0.016194 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Tatura | Vehicle
On arrival crew carried out repairs | 1 INDUSTRIAL AVENUE, HOPPERS CROSSING VIC 3029 | 30115749 |  |  |  | Leakage |  |  |  | A customer informed a broken insulator on the ground and the wire resting on cross arm at the incident location. On arrival the Powercor crew found that a Pole Fire had occurred. There was no ground fire, no reported injuries or third party damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | LV005 | Excessive leakage current | Pole-top fire | 14/07/2017 9:29 | 1 | Negligible: no ground fire | 6327 | Public space |  | 20170731PWA_02 | Infrastructure (network-based) | -37.8692 | 144.7252 | 1 | Powercor | Report | 7794 | 0.040753 | 22kV AC | Laverton Raaf | 3029 | Hoppers Crossing | Pole
On arrival crew carried out repairs | 115 SALMON STREET, PORT MELBOURNE VIC 3207 | 30218476 |  |  |  | Unknown technical factor |  |  |  | MFB reported a fire on building wall at the incident location. Upon arrival, the CitiPower crew found that the 3Ph meter board caught fire. T There were no injuries, third party damages or ground fire. | Meter board (including fuses) | 2 | 2 | 2 |  | PM004 | Due to damage unable to determine | Meter board | 14/07/2017 13:42 | 1 | Negligible: no ground fire | 6332 | Commercial |  | 20170731PWA_03 | Infrastructure (network-based) | -37.8289 | 144.9228 | 1 | CitiPower | Report | 7804 | 0.038443 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | AF Other
On arrival crew isolated line and replaced cross-arm | 30 HABELS ROAD, YULECART VIC 3301 | 30090144 |  |  |  | Mechanical breakdown |  |  |  | Hamilton Police reported a vehicle had hit a low conductor Habels Rd cnr McKellars Rd, Yulecart. The crew attended and found that a crossarm had broken and the HV conductor had been struck by a vehicle. There was no fire or reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | HTN002 | Broken crossarm | Loss of supply;Less than $50k damage | 29/07/2017 17:00 |  |  | 6334 | Roadway |  | 20170731PWA_04 | Infrastructure (network-based) | -37.7477 | 141.9095 | 1 | Powercor | Report | 7807 | 0.03695 | 22kV AC | Hamilton Airport | 3301 | Yulecart | Vehicle
Dispatched Inspector Ben Airey to isolate make safe and investigate. On arrival crew observed extensive damage to the pole mount transformer had occurred following a sever thunderstorm went through the area. The transformer was removed and replaced by the line crew. Installation inspector called to site to conducted and inspection of the electrical assets. customer issued with defect notice and advised to engage an REC to rectify damage to switchboard. Two power sub circuits were isolated and made safe after one RCD failed to reset and the other failed to operate within the correct time frame >300ms. No report of system induced HVI. | 50 HAYES ROAD, NEWBOROUGH VIC 3825 | 2201519 |  | Lightning |  |  |  |  | 1 | IMS 229410. Customer called with Appliance Damage , Customer part of Fault report from 25th Lightning strike on line causing blown transformer and three fuses to blow on Switch. INCD Number 145371-r. | Pole mounted | 0 | 1 | 0 |  | moe14 | Given the extensive damage to the transformer and that the incident happened during a severe thunderstorm cause of the damage is consistent with a lightning strike. The lightning strike produced a HV injection causing a single phase 22 kV 25kVA substation to explode, splitting it in half. The HV Protection (2 x 6A boraic acid HV fuses) blew along with the LV Protection fuses. Parts of the substation were found upto 50m away. The sole installation supplied off the transformer was 135 Hayes Road, Newborough which received a voltage injection resulting in significant appliance and installation damage. Customer issued with defect notice and advised to engage an REC to rectify damage to shed switchboard. Two power sub circuits were isolated and made safe after one RCD failed to reset and the other failed to operate within the correct time frame >300ms. | Less than $50k damage;Damage to network assets | 26/07/2017 7:50 |  |  | 6328 | Residential |  | 20170731SPN_01 | Infrastructure (network-based) | -38.1653 | 146.2937 | 1 | AusNet Services Distribution | Report | 13621 | 0.0084502 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Newborough | Lightning
Fault truck organised to investigate and repair. Inspector organised and attended to identify/isolate/inspect affected properties. Fault crew proceeded to isolate the Ballintine St spur line at tee pole 3908988 and FDR BN006 was restored at approx. 17.30hrs. CEOT arranged for an electrical inspector to attend due to the high voltage contact with the low voltage circuit between poles 3909048 and 3909047. Repairs took place and the high voltage line was repaired and re-energised. On advice from the electrical inspector in attendance , all customers on the blue phase were identified and isolated and then substations â€œBALLINTINE-NICHOLSONâ€ and â€œBALLINTINE-JENSENâ€ were re-energised. No damage found on installations connected to the â€œBALLINTINE-NICHOLSONâ€ substation and all customers were re-energised. Some damage found on installations connected to the blue phase of the â€œBALLINTINE-JENSENâ€ substation â€“ blue phase customers remained isolated overnight until additional electrical inspection staff could be made available to assist with testing and restoration. Friday 28th July â€“ Electrical inspectors arrived at approx. 2.30pm and undertook visual inspections of the remaining installations â€“ resulting in the replacement of 4 electrical meters. | 29 BALLINTINE STREET, BENALLA VIC 3672 | 3909048 | Vandalism |  |  | HV injection |  | Phase to phase | 2 | IMS229440 - two High Voltage phases of 19/3.25 AAC conductor on the east side of pole 3909048 had fallen through the low voltage conductors , FDR BN006 CB tripped, the dead conductor was on the ground. 137 customers were off supply. | Conductor (bare);Pole mounted | 0 | 1 | 0 |  | BN6 | HV conductor fallen on LV circuit | HV injection;Loss of supply;Less than $50k damage | 27/07/2017 15:50 |  |  | 6329 | Residential |  | 20170731SPN_02 | Infrastructure (network-based) | -36.5592 | 145.9586 | 1 | AusNet Services Distribution | Report | 13622 | 0.016516 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3672 | Benalla | Conductor
The crew made the site safe. | 407 ST KILDA ROAD, MELBOURNE VIC 3000 | 30196345 | Unauthorised work | [6 empty] | A contractor advised an UG cable dug up at the incident location. Upon arrival, the Powercor crew found that a P/L service had been cut. The worker reported a minor shock and he was later cleared by a doctor. Worksafe attended incident site There was no fire or third party property damage. | Services cable | 2 | 2 | 2 |  | FR016 | Interference | Minor shock | 42862.4167 |  |  | 6338 | Roadway |  | 20170801PWA_01 | Infrastructure (network-based) | -37.8362 | 144.9761 | 1 | CitiPower | Report | 7824 | 0.0025938 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
A crew attended and repaired the earth. | 65 CAMPASPE WAY, POINT COOK VIC 3030 | 30109201 | Copper theft | [5 empty] | 2 | Asset Inspector reported a stolen HV earth from pole at incident location. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | LV004 | Copper theft | Damage to network assets | 43076.5729 |  |  | 6343 | Public space |  | 20170802PWA_03 | Infrastructure (network-based) | -37.8789 | 144.7194 | 1 | Powercor | Report | 7818 | 0.00087269 | Earthing cable | Laverton Raaf | 3030 | Point Cook | Other
The crew took photos of the infringement and notified their supervisor. | 4 POWYS DRIVE, BEAUMARIS VIC 3193 |  | Unauthorised work | [5 empty] | 2 | A Downer meter and servicing crew had a job to dress up a new pole to pit underground service outside 4 Powys Drive, Beaumaris and identified the overhead service supplying number four was very slack and investigated the cause. The meter and servicing crew identified that it appeared unknown persons had relocated the overhead single phase XLPE service from a raiser bracket at the POA and re-attached the service to an adjacent piece of timber for unknown reasons. A review of United Energy records shows no requests for any crews attendance has been requested. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Unknown persons have relocated the single phase overhead service. | No Go Zone (contact) | 42743.3542 |  |  | 6340 | Residential |  | 20170802UTD_01 | Infrastructure (network-based) | -37.9858 | 145.0456 | 2 | United Energy Distribution | Report | 7815 | 0.018789 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Beaumaris | Other
Service was reconnected and supply restored. | 38 MILLER STREET, ESSENDON VIC 3040 |  | Working too close to overhead lines | [5 empty] | 2 | Excavator hit (insulated) service line. This caused the service line to detach from pole and fall to the ground. | Service conductor | 0 | 0 | 0 |  |  | Excavator working too close to the service line. | No Go Zone (contact) | 42801.4444 |  |  | 6358 | Residential |  | 20170803JEM_05 | Infrastructure (network-based) | -37.7535 | 144.9091 | 1 | Jemena | Report | 7840 | 0.0384 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Vehicle
The underground faults crew have repaired the cable supply restored. | 16 ROBE STREET, ST KILDA VIC 3182 | 30212125 | Working too close to underground cables | [5 empty] | 1 | A contractor reports contacting an underground cable at the incident location. On arrival the fault crew found contractors repairing a damaged sewer had contacted a low voltage underground cable with their excavator. Damage to the cable caused a low voltage fuse to operate which cleared the fault. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | SK013 | Contractor excavation | Loss of supply;No Go Zone (contact);Damage to network assets | 15/07/2017 10:19 |  |  | 6359 | Public space |  | 20170803PWA_04 | Infrastructure (network-based) | -37.8643 | 144.9784 | 1 | CitiPower | Report | 7841 | 0.00081944 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Dug up
On arrival crew isolated supply and carried out repairs | 74 BRIDGE STREET, NORTHCOTE VIC 3070 | 30187103 | Vehicle | [6 empty] | A customer advised a service cable lying on a car at the incident location. Upon arrival CitiPower crew found that the LV service cable pulled down by an unknown vehicle and the fallen cable was lying on a parked car. No damage on the car observed by the crew. There was no fire or injuries | Service conductor | 2 | 2 | 2 |  | NC001 | Unknown vehicle struck service | Loss of supply;Damage to network assets | 17/07/2017 9:47 |  |  | 6360 | Roadway |  | 20170803PWA_05 | Infrastructure (network-based) | -37.7783 | 144.9957 | 1 | CitiPower | Report | 7843 | 0.030978 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
On arrival crew isolated supply and carried out repairs. | 38 HONOUR AVENUE, WYNDHAM VALE VIC 3024 | 32163152 | Vehicle | [6 empty] | Emergency Services reported wires down at the incident location. Upon arrival, the crew found that an unknown vehicle had hit the Optus cable and had taken down the red phase LV conductor to the ground along with it. There was no fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE031 | Unknown vehicle struck optus cable | Loss of supply;Damage to network assets | 21/07/2017 17:34 |  |  | 6371 | Roadway |  | 20170807PWA_02 | Infrastructure (network-based) | -37.8932 | 144.6231 | 1 | Powercor | Report | 7855 | 0.0047176 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
On arrival crew replaced meter. supply left off and customer issued with defect notice to have house wiring inspected. | 10 DERRIMUT ROAD, HOPPERS CROSSING VIC 3029 | 32172839 | Vandalism | [6 empty] | Customer reported that the meter has been previously hit and damaged by intruders with an axe, and no power coming from meter. There was no fire or injuries. | Smart meter;Customer installation | 2 | 2 | 2 |  | WBE013 | Vandalism | Loss of supply;Damage to network assets | 20/07/2017 21:35 |  |  | 6372 | Residential |  | 20170807PWA_03 | Infrastructure (network-based) | -37.8909 | 144.681 | 1 | Powercor | Report | 7856 | 0.033179 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Other
CFA attended to small fire which was contained to transformer. Crew isolated and made site safe. Crew then replaced fuse and removed birds nest. Transformer functionality was not affected by fire. | 330 MT RIDLEY ROAD, MICKLEHAM VIC 3064 | 10200106 |  | Bird |  |  |  | Phase to phase | 1 | Birds nest located on top of pole transformer (pole no. A145352) caught fire and caused centre phase HV fuse to operate. | Pole mounted | 0 | 1 | 0 |  | KLO22 | Bird Incident | Pole-top fire | 42924.7653 | 1 | Negligible: no ground fire | 6374 | Residential |  | 20170808JEM_01 | Infrastructure (network-based) | -37.5663 | 144.9155 | 1 | Jemena | Report | 13015 | 0.031108 | 22kV AC | Melbourne Airport | 3064 | Mickleham | Animal
The attending faults crew isolated and replaced the damaged FOLCB and the neutral LV pin and insulator that was damaged as a result of the fire. Supply was restored to the affected customers upon completion. | 298 HOTHAM ROAD, PORTSEA VIC 3944 | 1307139 |  |  |  | Corrosion |  |  | 2 | Per CFA - pole fire 50m from the corner of Hotham Road and Franklin Street on the Bay side. During cool and damp conditions, a three phase FOLCB installed on an LV intermediate crossarm at pole No. LIS 1307139 located near the corner of Hotham Road and Franklin Street was burnt out due to probable corrosion as the pole is situated a short distance from Port Phillip Bay. The FOLCB ignited that caused a fire on the LV intermediate cross arm that self extinguished. | Connection box | 0 | 0 | 0 |  |  | The probable cause was due to corrosion as the pole is situated a short distance from Port Phillip Bay. | Pole-top fire | 42954.7347 | 1 | Negligible: no ground fire | 6384 | Roadway |  | 20170809UTD_02 | Infrastructure (network-based) | -38.3312 | 144.7143 | 1 | United Energy Distribution | Report | 12949 | 0.037439 | Low voltage AC (<1kV) | Avalon Airport | 3944 | Portsea | Crossarm
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Fault crew attended, made safe and replaced the Boric Acid 6k fuse element and fuse tube. | 66 TAP TAP ROAD, JACK RIVER VIC 3971 | 2622133 |  |  |  | Candled fuse |  |  | 2 | IMS 226904. Boric Acid HV 6k fuse candled. The fuse tube candled but both ends stayed up. There was no visible fire anywhere at the base of the pole CAM# 2622133, O'Neill P19. Note by Glenn Davidson: This incident was entered into IMS selecting a Pole Fire tab only but the Electrical tab should have also been selected. As a result it was late in identifying this incident for entering into OSIRIS. I have advised the local Field Delivery Manager of this issue. Please note that our CEOT (Control Room) did fax a Schedule 1 report to ESV. We apologise for this. Fuse tube candled at both ends | Boric acid | 0 | 0 | 0 |  |  | Candled BA fuse tube. | Other electricity related | 15/03/2017 6:55 | 1 | Negligible: no ground fire | 6025 | Agricultural |  | 20170510SPN_02 | Infrastructure (network-based) | -38.5879 | 146.5609 | 1 | AusNet Services Distribution | Report | 12359 | 0.014837 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Jack River | Fuse
Temporary repairs to fence & razor wire. | 44 MOORE ROAD, AIRPORT WEST VIC 3042 |  | Unauthorised access | [5 empty] | 2 | Fence cut to gain entry to zone substation (ZSS) AW via adjacent property (West side). Fence hole created allowed access to front area of Substation (non-operational area). Second access point into ZSS was, again, from adjacent property. Intruders stacked pallets upright against fence to use as ladders, unfixed razor wire and moved razor wire to one side then Jumped down into site. Nothing was stolen. | Zone substation | 2 | 2 | 2 |  |  | Unauthorised access by burglar. | Less than $50k damage | 42740.3333 |  |  | 6047 | Industrial |  | 20170515JEM_05 | Infrastructure (network-based) | -37.7162 | 144.8858 | 1 | Jemena | Report | 7431 | 0.010122 | 22kV AC | Essendon Airport | 3042 | Airport West | Other
On arrival crew carried out repairs | 326 HEATH ROAD, CASHMORE VIC 3305 | 32128364 |  |  |  | Overheated connection |  |  | 2 | A customer reports a power outage at the above location. A crew attended and found a pole mounted fuse box had over heated and started a pole fire. No CFA attended. There were no reported shocks, injuries or ground fire start. | Connection box | 2 | 2 | 2 |  | PLD003 | unable to determine cause due to damage | Pole-top fire;Loss of supply | 43074.2826 | 1 | Negligible: no ground fire | 6041 | Agricultural |  | 20170515PWA_01 | Infrastructure (network-based) | -38.3141 | 141.5295 | 1 | Powercor | Report | 7423 | 0.028542 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Cashmore | Fuse
Crew attended and removed span of conductor. conductor to be reinstated at later date | 58 HIGHETT STREET, RICHMOND VIC 3121 | 30185275 |  | Within clearances |  |  |  |  | 2 | A passer-by reported that there is a conductor hanging above the footpath at the incident location. On arrival the fault crew found that a low voltage mains conductor had parted mid-span with both ends hanging above the footpath. | Conductor (bare) | 0 | 0 | 0 |  | NR015 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/05/2017 8:03 |  |  | 6042 | Residential |  | 20170515PWA_02 | Infrastructure (network-based) | -37.8153 | 144.9933 | 1 | CitiPower | Report | 7499 | 0.011317 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Conductor
As the house has been almost completely demolished, the faults crew removed the single phase XLPE overhead service from pole No. LIS 1815122, took photos and forwarded them to their supervisor. The site was left safe after the demolition works created an unsafe situation for the general public and themselves. | 14 FAIRVIEW AVENUE, CHELTENHAM VIC 3192 | 1815122 | Working too close to overhead lines | [5 empty] | 2 | Wire down - Caller has reported the line from the pole to the house has fallen after the POA was ripped off the facia board. The property is de-energised and vacant. A ZNX faults crew attended the site following a report of a wire down that was reported by Ryan 0419 885 816. When they arrived on site, they found the house was in the process of being demolished and the meters were missing from the site. The single phase XLPE overhead service remained attached to the POA on the facia board which was laying alive on the ground. The Resource Co-ordinator reviewed notes for the account and the requestor was advised on 16/05/2017 the abolishment would be completed next week. No electric shocks or serious damage was sustained. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | The house was in the process of being demolished and the fascia board was felled with the live single phase service remaining attached. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/05/2017 11:00 |  |  | 6056 | Residential |  | 20170518UTD_03 | Infrastructure (network-based) | -37.9574 | 145.0655 | 1 | United Energy Distribution | Report | 7443 | 0.041289 | Low voltage AC (<1kV) | Moorabbin Airport | 3192 | Cheltenham | Other
The crew placed a crane to hold the pole and ensure the pole was secure. A member of the crew stayed overnight on site. After contractor backfilled the trench area between the steel shoring and the pole (1.8m from the pole), as requested by CPL, the Powercor crew re-instated the pole. | 31 WHITEHILL AVENUE, SUNSHINE NORTH VIC 3020 | 33071369 | Working too close to overhead lines | [5 empty] | 2 | Customer (Robert) from MODERN CARPORTS (VIC) PTY LTD, reported that there is some road works going on around the area and near pole LIS-26903 at the intersection of Whitehall and Knight roads. Upon arrival, the crew found that there were some excavation works along Whitehill Avenue. Pole was leaning about 10Â° towards the building line and it looked like the road excavation had loosen the soil surrounding the pole, the concrete kerb in front of the pole was loose and had slightly moved.. Contractor had a permit to work which specified no excavation deeper that 1800mm within 1500mm of poles, the excavation was only 1.2m from the pole at the Kerb level. There was no Fire, injuries or third party property damage. | Pole (concrete) | 2 | 2 | 2 |  | SSE012 | Road excavation works | Damage to network assets | 15/05/2017 15:56 |  |  | 6057 | Roadway |  | 20170519PWA_01 | Infrastructure (network-based) | -37.7548 | 144.8367 | 1 | Powercor | Report | 7445 | 0.024465 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Other
On arrival crew completed repairs | 2146 GISBORNE ROAD, COIMADAI VIC 3340 | 32167656 | Vehicle | [5 empty] | 2 | Emergency Services reported a cable on the ground at the incident location. Upon arrival, the crew found that a HV conductor had been brought down by an unknown vehicle. There was evidence of a small grass fire. There were no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BMH006 | Unknown vehicle struck conductor | Loss of supply;Grassfire | 23/05/2017 11:58 | 1 | Localised: less than 10 sq.m | 6062 | Roadway |  | 20170524PWA_01 | Infrastructure (network-based) | -37.5955 | 144.4636 | 1 | Powercor | Report | 7450 | 0.0048113 | 22kV AC | Melbourne Airport | 3340 | Coimadai | Vehicle
The crew repaired the cable and sealed its end before burying it at the prescribed depth. Information regarding the cable route details have been forwarded for record updated to show repairs undertaken. | 52 SOUTH WHARF DRIVE, DOCKLANDS VIC 3008 | 30286496 | Working too close to underground cables | [5 empty] | 2 | A contractor reported that a bobcat has damaged an underground cable at the incident location. On arrival the fault crew found an unidentified low voltage cable end had been left out of the ground with a bollard placed over it. The operator in the process of spreading topsoil at the worsksite made contact with the bollard under which the underground cable was located, sparking and arcing occurred. The fault crew were unable to determine when and who left the cable in this condition. There were no reported injuries, no fire or third party property damage. | Services cable | 2 | 2 | 2 |  | FB004 | Bobcat disturbed cable | Damage to network assets | 15/05/2017 12:05 |  |  | 6063 | Commercial |  | 20170524PWA_02 | Infrastructure (network-based) | -37.8225 | 144.938 | 1 | CitiPower | Report | 7451 | 0.026947 | Low voltage AC (<1kV) | Essendon Airport | 3008 | Docklands | Dug up
Citi-Power fault crew isolated supply to the building, site made safe. Three meters were extensively damaged and have been replaced. All the ceramic fuse units and there links were also replaced A plumber was on site and replaced three gas meters. | 18 ROBE STREET, ST KILDA VIC 3182 | 30212170 | Vandalism | [5 empty] | 2 | The MFB reported that a person has vandalised assets at the incident location. On arrival the fault crew found that a drug effected person has attacked / vandalised the common meter board and gas meters with an old pedestal fan at the incident location. There was no fire and no injury as a result of this incident. | Smart meter;Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | SK013 | Vandalism | Loss of supply;Damage to network assets | 16/05/2017 17:55 |  |  | 6078 | Residential |  | 20170529PWA_01 | Infrastructure (network-based) | -37.8642 | 144.9785 | 1 | CitiPower | Report | 7471 | 0.007287 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Other
On arrival crew carried out repairs | 3803 COBDEN-WARRNAMBOOL ROAD, NARINGAL VIC 3277 | 32194437 |  |  |  | Overheated connection |  |  | 2 | CFA reports a fire on a pole at the above location. A crew attended and found a fuse box had over heated and melted. The resulting falling debris started a grass fire at the base of the pole of approx. 1m/Sq. There were no reported shocks, injuries or third party damage. | Connection box | 2 | 2 | 2 |  | WBL002 | Unable to determine cause due to damage. | Grassfire | 42741.375 | 1 | Localised: less than 10 sq.m | 6106 | Roadway |  | 20170601PWA_01 | Infrastructure (network-based) | -38.3962 | 142.6917 | 1 | Powercor | Report | 12455 | 0.029096 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3803 | Naringal | Fuse
On arrival crew isolated supply | 760 GERANG-GLENLEE ROAD, GERANG GERUNG VIC 3418 | 30082574 |  |  |  | Fault on customer installation |  |  | 2 | Emergency Services reported that a fuse box not attached to the house was on fire at the incident location. On arrival the crew found that a Meter box, which also contained the customerâ€™s switchboard was mounted to a private pole on the customerâ€™s property. The meter board, meters and switch board had all been totally destroyed by the fire, the cause of which could not be determined due to the damage. The fire caused melted plastic and debris to fall to the ground, however the debris landed on short green grass and there was no ground fire, no reported third party damage or any injuries. | Customer installation | 2 | 2 | 2 |  | NHL015 | Not apparent due to damage | Loss of supply;Meter board | 25/05/2017 15:27 | 1 | Negligible: no ground fire | 6111 | Agricultural |  | 20170601PWA_05 | Infrastructure (network-based) | -36.3085 | 141.8728 | 1 | Powercor | Report | 12457 | 0.0017234 | Low voltage AC (<1kV) | Horsham Aerodrome | 3418 | Gerang Gerung | AF Other
CEOT dispatched a fault crew to make safe, investigate and arrange repairs. The CFA had put out the fire prior to the fault crew attending. The light head had definitely melted and a lot of water was around the base of pole 1902475 from the CFA extinguishing the fire. The fault crew disconnect the supply at the base of the light pole and made safe. The light head was still secure and left in place for replacement by the public lighting contractor. A request was raised for Electrix to replace the street lantern with a new fitting. | 685 PRINCES HIGHWAY, LAKES ENTRANCE VIC 3909 | 1902475 |  |  |  | Electrical breakdown |  |  | 2 | IMS 228117. CEOT received a report of a pole fire at pole LIS 1902475. A fire occurred in the head of a street light fitting on a main road light pole. The light pole location was at approximately 685 Princes Hwy. | Public lighting | 0 | 0 | 0 |  | BDL41 | Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors. | Other electricity related | 17/05/2017 17:55 | 1 | Negligible: no ground fire | 6105 | Commercial |  | 20170601SPN_01 | Infrastructure (network-based) | -37.877 | 148.003 | 1 | AusNet Services Distribution | Report | 11259 | 0.011733 | Low voltage AC (<1kV) | Bairnsdale Airport | 3909 | Lakes Entrance | AF Other
Made safe and removed service and meter. | 4 MAGDALA AVENUE, STRATHMORE VIC 3041 |  | Unauthorised access | [5 empty] | 2 | A Zinfra crew was sent out to upgrade an overhead service to 3 phases. Upon arrival the crew discovered that the overhead service and meter were already relocated to the BTS. | Aluminium twisted (XLPE);Smart meter | 2 | 2 | 2 |  |  | Unknown party removed and disconnected service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42772.3958 |  |  | 6116 | Residential |  | 20170605JEM_01 | Infrastructure (network-based) | -37.7412 | 144.914 | 1 | Jemena | Report | 7516 | 0.0033171 | Low voltage AC (<1kV) | Essendon Airport | 3041 | Strathmore | Other
On arrival crew completed repairs. A defect notice was issued for POA repairs | 52-64 KNOX STREET, NUMURKAH VIC 3636 | 32180494 | Vehicle | [5 empty] | 2 | Mr Rick informed a truck has pulled down a service at the incident location. Upon arrival the Powercor crew found that the service cable on the ground. There were no injuries or fire. | Service conductor | 2 | 2 | 2 |  | NKA004 | Truck struck service | Loss of supply | 25/05/2017 11:13 |  |  | 6123 | Roadway |  | 20170605PWA_07 | Infrastructure (network-based) | -36.0922 | 145.4395 | 1 | Powercor | Report | 7525 | 0.030402 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Vehicle
Crew attended and replaced pole | 20 DORRINGTON ROAD, GLENLEE VIC 3418 | 32104727 | Vehicle | [5 empty] | 1 | A customer reported no supply at the incident location. On arrival the crew found that a tractor had struck a SWER intermediate pole in a paddock while plowing, knocking the pole over. The SWER conductor contacted the ground resulting in a grassfire of approx. 15m x 20m= 300m2 in a stubble paddock. Protection operated. There was no other reported third party damage or injuries. | Pole (wood) | 0 | 0 | 0 |  | NHL015 | Agricultural vehicle collided with pole | Loss of supply;Grassfire;Damage to network assets | 42861.5021 | 1 | Small: 10 - 1000 sq.m | 6124 | Agricultural |  | 20170606PWA_01 | Infrastructure (network-based) | -36.1858 | 141.7931 | 1 | Powercor | Report | 7527 | 0.027959 | 12.7kV AC (SWER) | Horsham Aerodrome | 3418 | Glenlee | Vehicle
On arrival crew carried out repairs | 23 KOORINGA WAY, PORT MELBOURNE VIC 3207 | 30200663 | Contact from third-party infrastructure;Other | [5 empty] | 1 | Citipower fault crew attending an outage found that a rusted sewer venting pipe has fallen on to HV conductors at the incident location. No third party damages, fire or injuries were reported. | Conductor (bare) | 2 | 2 | 2 |  | FB020 | Sewer vent pipe fell over and contacted line | Damage to network assets | 42892.4354 |  |  | 6125 | Public space |  | 20170606PWA_02 | Infrastructure (network-based) | -37.8343 | 144.9069 | 1 | CitiPower | Report | 7529 | 0.028645 | 11kV AC | Essendon Airport | 3207 | Port Melbourne | Other
Area was barricaded and relevant cables were isolated in underground pit. | 9 PIONEER STREET, CRAIGIEBURN VIC 3064 |  | Working too close to underground cables | [6 empty] | Unkown person broke conduit for underground cable resulting in exposed cables on nature strip. | Cable | 2 | 2 | 2 |  |  | Unkown person broke conduit for underground cable resulting in exposed cables on nature strip. | No Go Zone (no contact) | 31/05/2017 12:41 |  |  | 6126 | Residential |  | 20170608JEM_01 | Infrastructure (network-based) | -37.5883 | 144.8932 | 1 | Jemena | Report | 7530 | 0.033047 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
LV overhead conductor was isolated and repairs initiated by Jemena faults crew. HV feeder back bone was inspected, patrolled and cleared. | 57 DONCASTER STREET, ASCOT VALE VIC 3032 |  | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Truck mounted crane struck the LV overhead at the corner of Doncaster St and Stanford St. Insulated low voltage overhead conductor fell onto the ground. High voltage overhead clashed at this location causing a successful reclose on feeder. The high voltage overhead clash may have been caused by the vehicle impact on the LV overhead conductor which shook the overall structure of the assets. | Conductor (ABC);Conductor (bare) | 0 | 0 | 0 |  | ES22 | Truck mounted crane was driven with boom not fully stowed and made contact with LV overhead conductor. It was not in operating mode at the time it made contact with LV overhead conductor. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42953.4903 |  |  | 6128 | Residential |  | 20170608JEM_02 | Infrastructure (network-based) | -37.7782 | 144.9038 | 1 | Jemena | Report | 12402 | 0.0077616 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3032 | Ascot Vale | Vehicle
CEOT dispatched a fault crew to isolate, make safe and arrange for necessary repairs to the overhead HV conductor and the damaged service cables. AusNet Services' subcontractor, Extec Services P/L also attended the incident site. A construction crew attended and repaired the HV conductor, repaired/replaced several service cables and restored supply. | 59 CAMERON WAY, PAKENHAM VIC 3810 | BW2709 | Working too close to overhead lines | [5 empty] | 1 | IMS 227939. A tipper truck with the tipper raised, ran through overhead service cables. One of the service cables flicked up into one of the HV phases and created scorch marks. The scorched HV conductor was deemed OK to remain up in position, but repairs were required to be undertaken at a later date. The HV line was immediately de-energised by the feeder CB tripping open while its auto-reclose was suppressed. | Conductor (bare);Service conductor | 0 | 0 | 0 |  | phm31 | A tipper truck with its tipper tray in the raised position drove through several overhead services cables causing one service cable to contact the above HV bare conductor resulting in damage to the conductor and feeder protection to operate. The driver is not known. | No Go Zone (contact) | 17/05/2017 8:35 |  |  | 6127 | Residential |  | 20170608SPN_01 | Infrastructure (network-based) | -38.0782 | 145.5005 | 1 | AusNet Services Distribution | Report | 12362 | 0.018529 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3810 | Pakenham | Vehicle
A faults truck attended and the REC advised that an electric shock had also been received by the occupier. A LEI was called to investigate and the owner when questioned advised that no electric shock had been received but the lights had been dimming. The LEI measured 1.5v on the earthing system that was constant with the fuse in and removed at the POA. All installation tests and a NST passed and the faults crew proceeded to check all neutral connections and no faults were identified. The owner was instructed to contact United Energy if any problems continued. There was no evidence of faulty internal wiring. | 169 BAXTER-TOORADIN ROAD, BAXTER VIC 3911 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | REC called and stated the switchboard is live as the consumers mains are feeding directly to the main switch before the meter. He's unable to isolate to make safe and tradesmen remain on site. The occupier contacted a REC to investigate the cause of flickering and dimming lights. | No failed asset | 0 | 0 | 0 |  |  | No cause was identified as no electric shock was received. | Minor shock | 42861.4583 |  |  | 6131 | Residential |  | 20170609UTD_01 | Infrastructure (network-based) | -38.1972 | 145.1687 | 2 | United Energy Distribution | Report | 7537 | 0.018956 | Low voltage AC (<1kV) | Moorabbin Airport | 3911 | Baxter | Other
The attending faults crew isolated the damaged cables that supplied a vacant unit at the rear of the shop. The faults crew found the workers had no Permit To Work with the faÃ§ade mounted LVABC remaining alive. The faults crew informed the owner not to allow anyone back onto the roof until a Permit To Work was obtained for the No Go Zone activities. The crew took photos and advised their supervisor. | 229 POINT NEPEAN ROAD, DROMANA VIC 3936 | 9824810 | Working too close to overhead lines | [6 empty] | REC called to report that onsite workers have struck the active and neutral before the mains box. The wires were hi by a grinder and did spark when to was struck. Workers are onsite and have parked their truck outside the shop. Onsite workers have cut copper conductors between the LVABC and the consumers MJB whilst working on the shop front roof. The worker used a concrete saw as he cut through the facade when the accident happened. Fortunately, no injury was sustained as he stood on the metal roof with water running. | Conductor (insulated);Customer installation | 0 | 0 | 0 |  |  | Onsite workers have cut a copper conductor between the LVABC and the consumers MJB whilst working on the shop front roof. | No Go Zone (contact) | 42892.7917 |  |  | 6136 | Commercial |  | 20170613UTD_01 | Infrastructure (network-based) | -38.3329 | 144.9649 | 1 | United Energy Distribution | Report | 7542 | 0.037407 | Low voltage AC (<1kV) | Moorabbin Airport | 3936 | Dromana | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a load imbalance at the Sub-station, causing a rise in voltage of 4.9 Volts on the neutral reticulation and O/H Neutral Service Conductor and between the points of contact. The attending Powercor Fault Crew broke, cleaned and remade all connections of the Two Wire O/H Twisted Service Cable and completed an NST Test, which confirmed a Pass result. | 12 SINCLAIR STREET, COLAC VIC 3250 | 32066882 |  |  |  | Out of balance load |  | Phase to earth | 2 | Mr Aaron Crabbe was in the Kitchen washing dishes when he received an electric shock as he made simultaneous contact with his hands when he operated the Hot Water Tap while his other hand was in contact with the metallic sink. | Service conductor | 2 | 2 | 2 |  | CLC002 | load imbalance at the Sub-station | Minor shock | 20/01/2017 13:00 |  |  | 6176 | Residential |  | 20170619PWA_05 | Infrastructure (network-based) | -38.3305 | 143.5732 | 1 | Powercor | Report | 12460 | 0.0020845 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | AF Other
The faults crew replaced the copper transformer earth cable and re-installed the timber cover guards at pole No. LIS 9868567. | GAMBLE ROAD, SKYE VIC 3977 | 9868567 | Copper theft | [5 empty] | 2 | Caller reports wire hanging down approximately two meters down from the substation and can be touched on the corner of Gamble Road and Selwyn Court, Skye. A passerby reported the copper transformer earth cable was stolen from "Gamble-Selwyn" pole type substation and a section was left hanging. | Cable;Copper;Earth/earthing | 0 | 0 | 0 |  | FTN 25 | Unknown persons stole the copper earth cable from a substation pole. | Damage to network assets | 19/06/2017 14:30 |  |  | 6180 | Roadway |  | 20170620UTD_01 | Infrastructure (network-based) | -38.1141 | 145.2015 | 1 | United Energy Distribution | Report | 7596 | 0.031922 | 22kV AC | Moorabbin Airport | 3977 | Skye | Other
On arrival crew carried out repairs | 7 FARRELL AVENUE, CASTLEMAINE VIC 3450 | 30037938 | Vehicle | [5 empty] | 1 | While emptying garbage bins, a garbage truck has become entangled with the Low voltage conductors at the incident location On arrival the Powercor crew found that the LV conductors clashed causing minor damage to the conductors. There was no fire, injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CMN001 | Emptying Bins near conductors | Loss of supply;No Go Zone (contact) | 42861.5479 |  |  | 6189 | Roadway |  | 20170622PWA_01 | Infrastructure (network-based) | -37.0729 | 144.225 | 1 | Powercor | Report | 7607 | 0.00045255 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Vehicle
On arrival crew carried out repairs | 19 CORELLA ROAD, SUNSHINE WEST VIC 3020 | 30114027 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A contractor advised that while delivering gravel to their road works, a tip truck has struck and brought down the service cable at the incident location. There was no fire, injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | SU035 | tipping operations | Loss of supply;No Go Zone (contact) | 42892.4313 |  |  | 6190 | Roadway |  | 20170622PWA_02 | Infrastructure (network-based) | -37.7951 | 144.8044 | 1 | Powercor | Report | 7608 | 0.027679 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
On arrival crew could not determine cause of ground fire or find evidence of flashover. Followup raised to further examine connections. | 100C STALEY ROAD, WEMEN VIC 3549 | 32143194 |  |  |  | Unknown technical factor |  |  | 2 | Customer started their pump remotely and then went to check it started. Found small grass fire beneath the transformer and extinguished. No loss of supply no feeder operation, no evidence onsite of an animal. Area burnt on road verge 6metres by 3 metres, report made to ESV. There were no reported shocks, injuries. | Pole mounted | 2 | 2 | 2 |  | WMN013 | No cause found | Grassfire | 24/06/2017 14:05 | 0 | Small: 10 - 1000 sq.m | 6198 | Roadway |  | 20170627PWA_01 | Infrastructure (network-based) | -34.7394 | 142.6607 | 1 | Powercor | Report | 8431 | 0.025106 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3549 | Wemen | AF Other
On arrival crew carried out repairs | 828 GEELONG ROAD, CANADIAN VIC 3350 | 33109488 |  |  |  | Overheated connection |  |  | 2 | Vicfire reported a street light pole on fire at the incident location. Upon arrival the Powercor crew found that the street light lantern had been damaged as a result of excessive heat. No other damages reported. There was no ground fire and no injuries | Public lighting | 2 | 2 | 2 |  | BAS013 | Unable to determine due to damage | Melting or smoking only | 42772.7542 |  |  | 6200 | Roadway |  | 20170627PWA_02 | Infrastructure (network-based) | -37.5886 | 143.8664 | 1 | Powercor | Report | 7628 | 0.00037153 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Canadian | AF Other
CEOT dispatched a fault crew and an Operator to attend the fault. The CFA extinguished the fire of approximately 40m x 3m area. Line crew re strung and sleeved conductor and restored supply. The DAO was also dispatched to investigate and take relevant photos.observed 1 x 3/12 conductors on the ground centre phase and dead pelican onsite - burnt grass on Road reserve -CFA /Police onsite. | 834 BUNDALAGUAH ROAD, BUNDALAGUAH VIC 3851 | 2508411 |  | Bird |  |  |  | Phase to earth |  | IMS 228743. CEOT received a report from a passer-by that a power line was down and of a possible fire. 3/12 steel conductor broken 2 x 40 BA fuses blown at SW5611446 | Conductor (bare) | 0 | 0 | 0 |  | MFA23 | Bird Incident | Loss of supply;Grassfire | 25/06/2017 17:02 | 1 | Small: 10 - 1000 sq.m | 6199 | Agricultural |  | 20170627SPN_01 | Infrastructure (network-based) | -38.0293 | 146.9846 | 1 | AusNet Services Distribution | Report | 11279 | 0.03745 | 22kV AC | Morwell (Latrobe Valley Airport) | 3851 | Bundalaguah | Animal
150 HPS street light head caught fire. MFB had put fire out when Jemena crew arrived. Jemena crew disconnected supply and removed streetlight head. Streetlight has been disconnected and head renived, A notification has been raised for the street light to be replaced. | 399 MURRAY ROAD, PRESTON VIC 3072 |  |  |  |  | Defective component |  |  | 2 | A passerby reported glow / fire on streetlight arm of pole outside property. Report from MFB: Street light pole fire. Light type is Mercury Vapour (RATING: 400W) 150 High Pressure Sodium (HPS) A photo for this incident is not available. | Pole top;Public lighting | 0 | 0 | 0 |  | CN08 | Failure of street light. | Pole-top fire | 25/06/2017 17:58 | 1 | Negligible: no ground fire | 6205 | Residential |  | 20170629JEM_01 | Infrastructure (network-based) | -37.7371 | 144.9931 | 1 | Jemena | Report | 7752 | 0.010206 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | AF Other
The crew made the service cable safe and left customer off supply for REC to make repairs. | 260 MARSHALLS LANE, BEREMBOKE VIC 3342 | 32176707 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [6 empty] | The customers REC advised that an excavator has pulled down the service wire at the incident location. Upon arrival the Powercor crew found that the service cable had been pulled down between the pole and customers FOLCB. No other damage reported. There was no ground fire and no injuries | Service conductor | 2 | 2 | 2 |  | BMH003 | excavator struck service | Loss of supply;No Go Zone (contact) | 42922.6861 |  |  | 6211 | Agricultural |  | 20170629PWA_06 | Infrastructure (network-based) | -37.8112 | 144.2314 | 1 | Powercor | Report | 7644 | 0.032171 | Low voltage AC (<1kV) | Avalon Airport | 3342 | Beremboke | Vehicle
On arrival crew carried out repairs. | 1047 BUNGAREE-CRESWICK ROAD, BUNGAREE VIC 3352 | 32001030 | Copper theft | [5 empty] | 2 | An inspector reports a missing earth cable on a pole at the above location. A crew attended and found the low voltage earth cable on the pole missing. There were no reported shocks, injuries, third party damage or fire start. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | Copper theft | Damage to network assets | 42953.6958 |  |  | 6213 | Roadway |  | 20170629PWA_08 | Infrastructure (network-based) | -37.5538 | 143.9934 | 1 | Powercor | Report | 7647 | 0.022476 | Earthing cable | Ballarat Aerodrome | 3352 | Bungaree | Other
On arrival the crew disconnected supply and issued a defect notice | 9 WOORITE PLACE, WYNDHAM VALE VIC 3024 | 30103023 |  |  |  | Unknown technical factor |  |  | 2 | Emergency services reported a house fire at the incident location. On arrival, the Powercor crew found that the customerâ€™s fuse board and the meter caught fire at the incident location. There were no injuries | Switchboard;Customer installation | 2 | 2 | 2 |  | WBE031 | Due to Damage cause unable to be determined | Meter board | 27/06/2017 8:44 | 0 | Negligible: no ground fire | 6214 | Residential |  | 20170629PWA_09 | Infrastructure (network-based) | -37.8973 | 144.6251 | 1 | Powercor | Report | 7650 | 0.028366 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | AF Other
Jemena Works Practices was notified on 29/06/2017 and attended on site for investigation. On arrival the site had already been back-filled and made safe by the developer. Jemena Works Practices representative has made contact with the third party electrical contract to verify if they had an NGZ permit on issue on that site. Their response was no. | 13 LAVINIA STREET, GREENVALE VIC 3059 | Mietta Lavinia substation | Building too close or within the No Go Zone;Working too close to underground cables;Unauthorised access | [5 empty] | 2 | During the thermal survey/inspection of COO 011 conducted by Select Solutions, it was found that a contestable works electrical (Option 2) third-party contractor had breached No Go Zone rule by excavating existing Jemena's electrical infrastructure and assets on an future land development. The third-party contractor left site exposed overnight in preparation to conduct their works for the following morning. Photos (as part the thermal inspection report) have been attached in Section 7 (Notes & Findings) of this OSIRIS report. Information and contact details of third-party contractor have been included in Additional Information under Section 7. | Cable;Pad mounted equipment/kiosk | 2 | 2 | 2 |  | COO 011 | Project manager and electrical contractor did not follow the No Go Zone rules and regulations | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/06/2017 15:30 |  |  | 6216 | Residential |  | 20170630JEM_01 | Infrastructure (network-based) | -37.6176 | 144.8867 | 1 | Jemena | Report | 7753 | 0.021819 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3059 | Greenvale | Dug up
Site made safe. Tree branch was removed from HV overhead conductor, which was checked and cleared for any damage. Supply restored. | 94 BARRY ROAD, CAMPBELLFIELD VIC 3061 | Pole no. A025000 |  | Blown branch/vegetation | Highly unlikely |  |  | Phase to phase | 1 | MFB reported an explosion sound at the corner of Barry Road and Mason Street, Campbellfield. BD16 feeder reclosed and opened to lockout. Jemena network operator advised a 30mm tree branch high up in tree canopy tore off during strong winds and landed across three phases of HV overhead conductor. Tree branch caught fire when it contacted HV conductor. No other damage to network assets was identified. Photos are attached in the "Notes & Findings" section of this report. | Conductor (bare) | 0 | 0 | 0 |  | BD16 | Vegetation: Trees Incident | Other vegetation | 13/07/2017 8:57 | 1 | Negligible: no ground fire | 6240 | Industrial |  | 20170713JEM_01 | Infrastructure (network-based) | -37.6684 | 144.9683 | 1 | Jemena | Report | 12944 | 0.007566 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Trees
ON arrival crew carried out repairs | 433 ORMOND ROAD, SPRINGBANK VIC 3352 | 30007510 | Copper theft | [5 empty] | 2 | A pole inspector reported an missing earth cable at the above location. A crew attended and found the high voltage earth cable missing from the pole. There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | copper theft | Damage to network assets | 16/06/2017 14:29 |  |  | 6247 | Roadway |  | 20170713PWA_05 | Infrastructure (network-based) | -37.5161 | 144.0577 | 1 | Powercor | Report | 7699 | 0.025314 | Earthing cable | Ballarat Aerodrome | 3352 | Springbank | Other
On arrival crew carried out repairs | 403 RIVERSDALE ROAD, HAWTHORN EAST VIC 3123 | 30202208 |  |  |  | Corrosion |  |  | 2 | MFB reported a pole fire at the incident location. Upon arrival, the Powercor crew found that an overheated termination ignited the junction box on the pole. There were no injuries, third party damages or ground fire. | Connection box | 2 | 2 | 2 |  | CL023 | Overheated connection | Pole-top fire | 30/06/2017 12:42 | 1 | Negligible: no ground fire | 6249 | Roadway |  | 20170713PWA_07 | Infrastructure (network-based) | -37.8308 | 145.0529 | 1 | CitiPower | Report | 7825 | 0.01565 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Connection
The crew made safe, isolated the area, replaced the damaged poles and restored supply. Three homes had damage to their fasciaâ€™s. R.E.Câ€™s repaired this damage. The defect notices removed and supply restored. | 19-23 GREAVES STREET S, WERRIBEE VIC 3030 | 30102850 | Vehicle | [5 empty] | 2 | The MFB reported that an excavator has contacted wires and a pole is leaning at the incident location. On arrival the fault crew found that an excavator being transported on a flatbed (excavator bucket arm had not been fully lowered, had snagged the Optus catenary wire and a low voltage 35mm2 four core XPLE conductors. These in turn pulled over one pole which failed at its base. A second pole was leaning towards the road. Both poles were replaced. The 35mm2, 4 core XLPE across the road was also replaced. There was no ground fire and no injury as a result of this incident. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | WBE024 | Overheight load struck conductors | Loss of supply;Damage to network assets | 15/06/2017 23:30 |  |  | 6254 | Roadway |  | 20170714PWA_05 | Infrastructure (network-based) | -37.9079 | 144.655 | 1 | Powercor | Report | 7707 | 0.015325 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
Operator isolated area and issued Access Permit to conduct repairs to HV conductor. | 2 KING STREET, AIRPORT WEST VIC 3042 |  |  | Bird |  |  |  |  | 1 | Bird's nest across phases on Ganged Flicker Blade switch 22106 in king street, west of matthews street, between feeders AW1 and AW5. HV conductor subsequently found by electrical network operator on ground on matthews street on tee to mcintosh street. | Conductor (bare) | 0 | 0 | 0 |  | AW05 | Bird Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/07/2017 6:20 |  |  | 6268 | Industrial |  | 20170719JEM_01 | Infrastructure (network-based) | -37.7236 | 144.8909 | 1 | Jemena | Report | 7725 | 0.021708 | 22kV AC | Essendon Airport | 3042 | Airport West | Animal
Due to damage to the substation, the low voltage supply will be removed and all equipment will be isolated from all supply points. | 40-52 MCARTHURS ROAD, ALTONA NORTH VIC 3025 | 32164551 | Copper theft | [5 empty] | 2 | A representative for this site advises that unauthorised persons have gained access to the ground substation and low voltage switch-room at the incident location. On arrival at site the crew found that one of the transformerâ€™s had had its lid removed and the copper core has been removed. One third of the oil contents of this transformer (1000kVA) have been released onto the ground. The other transformer also 1000kVA had its lid partially removed in preparation for theft of its core. Due to previous theft attempts only one LV circuit was energised. The owner of the site has recently requested an abolishment of supply to this substation There was no ground fire and no injury as a result of this incident. | Transformer | 2 | 1 | 2 |  | BLTS017 | copper theft | Damage to network assets | 26/06/2017 0:00 |  |  | 6287 | Industrial |  | 20170724PWA_03 | Infrastructure (network-based) | -37.8349 | 144.8405 | 1 | Powercor | Report | 7745 | 0.028015 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
The Downer underground supervisor communicated to the contractor to cease work in the vicinity of the HV cable until further clarification was provided from Downer or United Energy. The Downer underground supervisor determined that a underground cable jointer was required to repair the damaged cable. Works were completed to repair the cable, sand and slab and backfill to make safe until further repairs to the conduit can be completed. | 1 SOUTHPARK CLOSE, KEYSBOROUGH VIC 3173 |  | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Caller reports that excavator has busted an underground conduit and the outer black sheath outside 1 Southpark Close, Keysborough. The crew will remain on site. A third party contractor using an excavator made contact with a HV underground conduit and cable during sewerage excavation work. A contractor to Elite Property Group was performing excavating works to connect to a sewer. In the process of performing these works, it appears the excavator has damaged a HV underground cable. A Downer fault crew was dispatched to site and upon arrival found the affected area had been barricaded, presumable by the 3rd party contractor. The fault crew observed that the top layer of conduit had been damaged / removed and the bottom layer of conduit housing the HV cable was cracked and damaged. This included the 22KV cable being damaged through to the 1st sheath of cable and showing signs of damage (scratches) to the 2nd sheath. No injuries were sustained. | Cable | 0 | 0 | 0 |  | NP 14 | An excavator made contact with a HV underground conduit and cable during sewerage excavation work. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42742.5625 |  |  | 6280 | Roadway |  | 20170724UTD_01 | Infrastructure (network-based) | -37.9861 | 145.1472 | 1 | United Energy Distribution | Report | 7737 | 0.0014537 | 22kV AC | Moorabbin Airport | 3173 | Keysborough | Dug up
On arrival crew carried out repairs | 45 VICTORIA STREET, BRUNSWICK EAST VIC 3057 | 30155665 |  |  |  | Overheated connection |  |  |  | MFB reported a fire at incident location. CitiPower faults was dispatched to investigate. On arrival the crew found an IPC burnt however found no evidence of fire on the ground, pole or crossarm. It was believed the event at the incident location was due to a was due to a loose connection resulting in overheating. There was no fire , no reported injuries or third party property damage. | Connector/termination | 2 | 2 | 2 |  | BK022 | Overheated connection | Loss of supply;Singeing or local charring/blackening only | 42742.6417 |  |  | 6308 | Public space |  | 20170727PWA_04 | Infrastructure (network-based) | -37.7687 | 144.9791 | 1 | CitiPower | Report | 7826 | 0.013405 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Connection
Site made safe and area isolated for Jemena crews to conduct repair and replacement of LV overhead conductor. Supply restored @ 17:48 after repairs were carried out. | 111 ST ELMO ROAD, IVANHOE VIC 3079 |  | Crane, excavator or other construction/farming equipment | Within clearances |  |  |  |  | 2 | Demolition company working on site knocked a tree, resulting in a tree branch coming into contact with LV conductors which fell to the ground | Conductor (bare) | 0 | 0 | 0 |  | EP36 | Vegetation: Trees Incident | Loss of supply | 42774.4917 |  |  | 6347 | Residential |  | 20170802JEM_02 | Infrastructure (network-based) | -37.7578 | 145.0469 | 1 | Jemena | Report | 7822 | 0.011983 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Trees
Fault crew attended site and found a krone box had failed and caught on fire. No damage to building or structures below from the fire. new krone box was erected and 160Amp LV fuse installed. Krone box also supplied two neighbouring shops via a junction box. Supply restored to all three premises. | 2 BAIR STREET, LEONGATHA VIC 3953 | 2003702 |  |  |  | Electrical overload;Overheated connection |  |  | 1 | IMS 229563 - FIRE reported at McCartins pub at cables outside building. fault crew dispatched to make site safe. | Services cable;Connection box | 0 | 0 | 0 |  | LGA22 | There were no visible causes for krone box failing. Probable high customer volts or/and poor connection. | Pole-top fire | 42774.7743 | 1 | Negligible: no ground fire | 6352 | Commercial |  | 20170803SPN_02 | Infrastructure (network-based) | -38.4768 | 145.9462 | 1 | AusNet Services Distribution | Report | 8085 | 0.022736 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha | Pole
Faults crew replaced HV earth and cover guard on pole no. A052713 | 201 SUNSHINE ROAD, TOTTENHAM VIC 3012 | pole no. A052713 | Copper theft | [5 empty] | 2 | Jemena fault crew found HV earth wire damaged on switch pole A052713 Most likely cause of damage is copper theft. The date of copper theft is unknown. | Disconnector/isolator;Earth/earthing | 0 | 0 | 0 |  | TH12 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42833.3854 |  |  | 6363 | Industrial |  | 20170804JEM_01 | Infrastructure (network-based) | -37.7991 | 144.8579 | 1 | Jemena | Report | 7846 | 0.038873 | 22kV AC | Essendon Airport | 3012 | Tottenham | Other
On arrival crew isolated supply and carried out repairs | SOUTHSIDE BUSINESS PARK PROPOSED, 93-119 KAVANAGH STREET, SOUTHBANK VIC 3006 | 30173519 | Working too close to underground cables | [5 empty] | 1 | A CitiPower underground fault crew were investigating cause for a feeder outage and found damage to an underground cable consistent with a third party contact at the incident location. It was appeared that contractors doing drainage works in the vicinity had damaged the cable. The SB 22 11kV tripped to lock out as a result of this damage at 10:54 on the 12.7.2017. The contractor who caused the damage did not contact CitiPower. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | SB022 | Excavation works | No Go Zone (contact);Damage to network assets | 43076.4542 |  |  | 6361 | Public space |  | 20170804PWA_01 | Infrastructure (network-based) | -37.8256 | 144.9629 | 1 | CitiPower | Report | 7844 | 0.016587 | 11kV AC | Essendon Airport | 3006 | Southbank | Dug up
A faults crew attended and there were no workers onsite. The fuses at the POA had previously been removed but no carriers were inserted. The single phase meter was found to be hanging upside down and the switchboard and associated wiring had been partially removed. The faults crew isolated the supply at pole number LIS 0612188, inserted dummy fuses at the POA and issued a defect notice that was left in the meter position. They took photos and notified their supervisor. The following morning, an unknown caller advised of a truck hitting a wire at this property. Another faults crew attended and found an Optus communication conductor on the ground after it was felled by unknown persons. | 37 WESTALL ROAD, CLAYTON SOUTH VIC 3169 | 612188 | Vandalism | [5 empty] | 2 | Occupier of number 39 reports there is a sparking power line near the POA. The home is presently a vacant premise. The timber home appears to be partially demolished and a caller rang earlier in the evening advising of a sparking POA. The faults crew suspected the requestor was trying to have the electricity supply abolished as opposed to going through the correct process. | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Probable demolishing company had removed supply and was trying to have the overhead service and meter removed to allow the abolishment of the timber home. | No Go Zone (contact) | 42774.8542 |  |  | 6370 | Residential |  | 20170807UTD_01 | Infrastructure (network-based) | -37.9443 | 145.1394 | 0 | United Energy Distribution | Report | 7854 | 0.02544 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Other
The site was made safe and the LV service was repaired. | 4720 MIDLAND HIGHWAY, GIRGARRE EAST VIC 3616 | 30138921 | Working too close to underground cables | [6 empty] | The Project Engineer (Jason Brown) reported one of their contractors had hit an underground LV cable with an excavator. This was done while excavating for road works. On arrival the crew found that a Low Voltage (LV) UG had been damaged by the contractor. There were no reported injuries or other third part damage. | Services cable | 2 | 2 | 2 |  | SHP014 | Roadside excavation | Damage to network assets | 21/07/2017 12:35 |  |  | 6386 |  |  | 20170809PWA_01 | Infrastructure (network-based) | -36.4311 | 145.1016 | 1 | Powercor | Report | 7870 | 0.04078 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Girgarre East | Dug up
The attending faults crew isolated and replaced the damaged FOLCB and reconnected supply to the affected customers. | 19 ROSSERDALE CRESCENT, MOUNT ELIZA VIC 3930 | 3313863 |  |  |  | Overheated connection |  |  | 2 | Emergency services advise a transformer is on fire. During cool and damp conditions, a three phase FOLCB containing an underground cable on the LV pole No. LIS 3313863 located outside 20 Rosserdale Crescent, Mount Eliza was burnt out due to probable overload. | Connection box | 0 | 0 | 0 |  |  | The cause was probable overload that caused a overheated connection. | Pole-top fire | 42893.2069 | 1 | Negligible: no ground fire | 6383 | Roadway |  | 20170809UTD_01 | Infrastructure (network-based) | -38.1765 | 145.0807 | 1 | United Energy Distribution | Report | 12936 | 0.019708 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Connection
A LEI and faults crew attended and there was initially some confusion as both the customer and the vegetation workers advised the LEI that both parties received shocks. It was confirmed during these discussions that no electric shock was received. The LEI tested the pole and surrounding metallic objects including the pole guard and no voltages were present. The LEI observed that water was leaking out of the conduit within the pole guard and appeared to be coming from a pit on the opposite side of the road which was at a higher level than the base of the pole. Sand had also been washed into the pit from the property side of the pit. Water then flowed down the conduit to the base of the pole where it exited the conduit. The LEI advised the UE Resource Coordinator that a underground faults crew would be required to repair the conduit to prevent the water exiting at the base of the pole. | 390 BALDRYS ROAD, MAIN RIDGE VIC 3928 | 1308687 |  |  |  | Moisture ingress |  | Phase to earth | 2 | A vegetation crew were working in the vicinity and a customer advised them that an electric shock had been received from a pole. A customer advised a UE subcontracting vegetation crew who were cutting trees in the area, that an electric shock had been received from pole number LIS 1308687 located outside 390 Baldrys Road. | Pole (wood);Services cable | 0 | 0 | 0 |  |  | Testing confirmed that no electric shock was sustained. | Minor shock | 42986.3819 |  |  | 6399 | Residential |  | 20170811UTD_01 | Infrastructure (network-based) | -38.4061 | 144.9548 | 2 | United Energy Distribution | Report | 7887 | 0.0051204 | Low voltage AC (<1kV) | Moorabbin Airport | 3928 | Main Ridge | Other
A faults truck attended and made the site safe after a LV FOLCB containing underground cables caught fire. 7 customers were supplied from the pole and overhead services to 27,28 and 32 were cut clear and underground supplies to 30A, 30B, 31 and 31B isolated after they were fire damaged following the initial fire. The cause was suspected to be from overload or a loose connection and the possum cause was never confirmed. A day faults crew attended and completed repairs and replaced the damaged electrical infrastructure. A REC was also required on site as damage was identified at 27 London Street after a defect notice was issued. The REC made the repairs at the POA and provided non-prescribed CES 629532142 upon completion. A fire report was completed by the crew with photos taken after a burnt section of grassed area was identified at the base of the pole as a result of molten plastic falling during the fire. | UNIT 2 29 LONDON STREET, BENTLEIGH VIC 3204 | 1802621 |  |  |  | Electrical overload;Overheated connection |  |  | 2 | The MFB states there is a pole fire outside 29 London Street, Bentleigh and the initial cause was a possum at pole number 1802621. | Services cable;Connection box | 0 | 0 | 0 |  |  | Animal Incident | Grassfire | 43047.1333 | 1 | Localised: less than 10 sq.m | 6401 | Residential |  | 20170811UTD_02 | Infrastructure (network-based) | -37.9242 | 145.044 | 1 | United Energy Distribution | Report | 12950 | 0.01736 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Bentleigh | Connection
On arrival crew isolated supply and commenced repairs | 4 VALLEY MEWS, WYNDHAM VALE VIC 3024 | 30320417 |  |  |  | Electrical breakdown |  |  | 1 | Powercor was contacted by several customers indicating no supply. On arrival, the crew found that the LV fuse board of the Kiosk substation â€˜VALLEY-GREENSâ€™ had caught fire due to an overheating fault. The fire was contained inside the kiosk substation and extinguished by itself. There were no injuries or third party property damage. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | WBE023 | underground cable damage leading to overheating | Plant/equipment | 42802.7854 | 1 | Negligible: no ground fire | 6420 | Public space |  | 20170817PWA_01 | Infrastructure (network-based) | -37.8881 | 144.618 | 1 | Powercor | Report | 12579 | 0.0066354 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | UG Cable
On arrival Crew replaced PE cell. Lantern still serviceable. | 3A HUME STREET, ARMADALE VIC 3143 | 30166655 |  |  |  | Overheated connection |  |  |  | MFB reports a pole fire at the above address. A crew attended and found a PE cell in a 80 MV public light had over heated and caught fire. MFB where onsite and extinguished fire. . No ground fire start. . There were no reported shocks, injuries or 3rd party damage. | Public lighting | 2 | 2 | 2 |  | AR011 | PE cell overheated | Pole-top fire | 42833.2722 | 1 | Negligible: no ground fire | 6423 | Public space |  | 20170817PWA_02 | Infrastructure (network-based) | -37.8569 | 145.021 | 1 | CitiPower | Report | 13695 | 0.033667 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | AF Other
On arrival the crew made the site safe and issued a defect to customer to repair POA | 7 EWING STREET, BRUNSWICK VIC 3056 | 30158576 | Vehicle | [6 empty] | A customer advised a truck has brought down a service line at the incident location. Upon arrival the CitiPower crew found that the service had been damaged along with the POA. T | Service conductor;Customer installation | 2 | 2 | 2 |  | C022 | Truck struck service line | Loss of supply | 42924.4806 |  |  | 6424 | Roadway |  | 20170817PWA_03 | Infrastructure (network-based) | -37.7772 | 144.9667 | 1 | CitiPower | Report | 7933 | 0.035207 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
On arrival crew isolated supply and carried out repairs | 2 BRADBURYS LANE, HORSHAM VIC 3400 | 30260985 |  |  |  | Unknown technical factor |  |  |  | Vic Fire reported an overhead service cable on fire at the incident location. On arrival the crew found that the LV Fused Mains Box connected to the overhead service had been on fire The LV Fused mains Box had melted, and parts had fallen to the ground. There was no ground fire or any other damage caused by this incident. | Connection box | 2 | 2 | 2 |  | HSM010 | Due to damage cause could not be determined | Loss of supply;Other electricity related | 15/08/2017 18:24 | 1 | Negligible: no ground fire | 6447 | Commercial |  | 20170828PWA_01 | Infrastructure (network-based) | -36.7138 | 142.1991 | 1 | Powercor | Report | 7977 | 0.036859 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Pole
The crew made the site safe and repairs arranged. | 121 PIONEER DRIVE, ROCKBANK VIC 3335 | 30342708 | Working too close to underground cables | [6 empty] | A contractor advised an UG cable dug up at the incident location. Upon arrival, the Powercor crew noticed that a main service cable and the UG pit had been dug up by the contractor. There were no injuries or fire. | Cable;Services pit | 2 | 2 | 2 |  | MLN021 | Excavations in housing estate | Loss of supply;No Go Zone (contact);Damage to network assets | 16/08/2017 9:40 |  |  | 6448 |  |  | 20170829PWA_01 | Infrastructure (network-based) | -37.7269 | 144.6661 | 1 | Powercor | Report | 7978 | 0.0099653 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
The site was made safe and the LV Public lighting cable was repaired. It was also noted by the crew, that the â€œDial before you dig" map did not appear to show this cable. | 18 DEAKIN AVENUE, MILDURA VIC 3500 | 33066148 | Working too close to underground cables | [6 empty] | An REC (Luke 0419 340 929) called to say Lower Murray Water had hit an underground cable while excavating in the nature strip. On arrival the crew found that a Low Voltage Public lighting circuit had been damaged by the excavator. There were no reported injuries or other third part damage. . | Services cable | 2 | 2 | 2 |  | MDA031 | Excavation near cable | No Go Zone (contact) | 15/08/2017 8:27 |  |  | 6449 | Public space |  | 20170829PWA_02 | Infrastructure (network-based) | -34.1841 | 142.164 | 1 | Powercor | Report | 8100 | 0.039575 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Dug up
Attending crew made the site safe, arranged traffic control, re-sleeved conductor and repaired conductor connections. (Notification reference number 10271728, PM order reference number 5151618.) | 10 HOLMES ROAD, MOONEE PONDS VIC 3039 | 10572069 (LV conductor asset number) |  |  |  | Mechanical breakdown |  |  | 1 | Blue phase, footpath side LV conductor failed at split bolt clamp connection between poles A109279 and A109280 (N/O point - De-energised conductor). The failure point was on the east side of pole A109279. | Conductor (bare) | 0 | 0 | 0 |  | ES24 | LV conductor had failed at split bolt clamp between poles A109279 & A109280. | Loss of supply | 42834.4896 |  |  | 6480 | Roadway |  | 20170904JEM_01 | Infrastructure (network-based) | -37.7664 | 144.9189 | 1 | Jemena | Report | 8094 | 0.0064317 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Connection
Site made safe. Police and fire bridge attended site Jemena crew replaced copper earth and cover guard on pole no. A052901 | QUARRY ROAD, TOTTENHAM VIC 3012 | A052901 | Copper theft | [5 empty] | 2 | 1.2metres of copper bare conductor (HV earthing) was removed from pole no. A052901. There was no supply interruption to customers and it appears that removal of the HV earthing was done a while ago. The initial report of HV conductors on the ground was unsubstantiated. | Pole (wood);Copper | 0 | 0 | 0 |  | TH12 | Copper theft | Damage to network assets | 42864.4222 |  |  | 6486 | Industrial |  | 20170905JEM_02 | Infrastructure (network-based) | -37.7992 | 144.8535 | 1 | Jemena | Report | 8292 | 0.023942 | 22kV AC | Essendon Airport | 3012 | Tottenham | Other
Police were notified but chose not to attend. Once again, Q-main were organized for the repair of the damaged security fence. | HAMMOND ROAD, DANDENONG VIC 3175 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Breach in the security fence at DSH zone substation was discovered on the western side. Upon arrival, the field crew noticed the fence on the western side of the zone substation had been tampered with. A further inspection was made at the work site and found nothing was stolen but slight damage occurred to two control cable drums. There were three recent security breaches at DSH (Dandenong South) zone substation as follows: 2 May 2017 2 August 2017 8 August 2017 Please refer to the "Additional Information" field at the rear of this report. | Cable;Copper;Zone substation | 0 | 0 | 0 |  | DSH | Security breach at DSH zone substation. | Damage to network assets | 42774.5833 |  |  | 6492 | Other | Zone substation | 20170906UTD_03 | Infrastructure (network-based) | -38.0138 | 145.2055 | 1 | United Energy Distribution | Report | 8126 | 0.01005 | 66kV AC | Moorabbin Airport | 3175 | Dandenong | Other
The faults truck attended and completed a tong test at pole No. LIS 2319946 and identified there was no current on the white and blue phases. As the shop trader was not in attendance and the meter enclosure was accessible, the faults crew investigated and determined that a bypass had been established. They identified the customer had removed then mains from the line side of his main switch at the meter position and installed new white and blue phase mains from the load side of the meter board fuses and connected them to the main switch thus bypassing the meter on the white and blue phases. The three phase supply was isolated above the shops veranda and a defect notice was left at the site advising the shop trader that the electricity supply would not be restored until rectification was completed by a REC and a prescribed CES obtained. The crew took photos of the bypass and forwarded to the United Energy metering team. 7 Sept - REC No. 24997 (Peter 0402 424 549) removed the meter bypass conductors and prescribed CES No. 404100542 was provided after LEI Andrew Carter attended the site. A faults crew attended after the bypass had been removed and reconnected supply by inserting three fuse cartridges above the veranda and supply was left on after the completion of installation tests. The United Energy metering team are to determine if the costs associated with the meter bypass fraud and attendance by faults crews will be invoiced to the shop trader. | 81 MACKIE ROAD, BENTLEIGH EAST VIC 3165 | 2319946 | Theft;Unauthorised work;Unauthorised access |  |  | Fault on customer installation |  |  | 2 | The United Energy metering team suspect the shop trader at 81 Mackie Road has now bypassed the meter. As a result, no current is recorded by the meter on the white and blue phases and the bypass occurs at the same time as the meter reports a power failure. This site has had the meter tampered with on multiple occasions and ESV has been notified and investigated previously - refer to 20161222UTD_04 from December 2016. The shop trader at this location has a history of electricity theft and a trouble order was created for a faults truck to attend the site and to determine if a meter bypass or tampering has occurred as there are unusual meter communications being recorded. | Switchboard;Connection to meter | 0 | 0 | 0 |  |  | Electricity theft occurred after a meter bypass and illegal wiring had been installed. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42895.6875 |  |  | 6498 | Commercial |  | 20170908UTD_02 | Infrastructure (network-based) | -37.9153 | 145.0745 | 1 | United Energy Distribution | Report | 8131 | 0.029176 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 26 FRANKLIN ROAD, DONCASTER EAST VIC 3109 | 7062538 |  | Lightning |  | HV injection |  |  | 2 | At 1634hrs on 25/11/2017, 22kV feeder DC 10 and 66kV feeder TSTS-DC No. 2 -circuit breakers successfully reclosed and held. There was lightning in the area at the time. Following a storm that struck Melbourne at approximately 4.30PM on 25/11/2017, customers in Franklin Road lost their electricity supply after lightning struck a HV/LV concrete pole No. LIS 7062538. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the east circuit of "Franklin-Leeds" substation. The lightning struck a HV spur fusing pole DT7140 and damaged the red phase HV conductor and a three phase FOLCB that supplied an underground cable. The red and white 315amp LV fuses operated at "Franklin-Leeds" substation and the LEI's investigation revealed that almost property connected to the red and white phases sustained appliance damage including three meters. The LEI confirmed a high voltage injection occurred (BWD 1707) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | 22kV DC10 and 66kV TSTS-DC No. 2 | Lightning struck HV/LV concrete pole No. LIS 7062538. | HV injection;Loss of supply | 25/11/2017 16:34 |  |  | 6770 | Residential |  | 20171128UTD_01 | Infrastructure (network-based) | -37.7896 | 145.1557 | 1 | United Energy Distribution | Report | 8529 | 0.021907 | 22kV AC | Moorabbin Airport | 3109 | Doncaster East | Lightning
On arrival crew isolated supply and carried out repairs. | 70 LITTLES LANE, TERANG VIC 3264 | 30047390 | Working too close to overhead lines | [5 empty] | 1 | A Powercor fault crew attending an outage on TRG02 found that a Drilling Rig contacted HV conductors at the incident location. Protection operated (line auto reclosed). A conductor fell (between LIS409782 and 401917) on to a shed and it was alive due to back feed from the nearest pole substation. No one injured but the machine operator (Adrian Oehlmann) has been taken to hospital as a precaution. There was no fire. | Conductor (bare) | 2 | 2 | 2 |  | TRG002 | Drilling rig contacted overhead conductor | Loss of supply;No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/11/2017 10:12 |  |  | 6788 | Agricultural |  | 20171129PWA_02 | Infrastructure (network-based) | -38.2294 | 142.9288 | 1 | Powercor | Report | 8558 | 0.027553 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Vehicle
Site made safe and repaired. | FOOTSCRAY SOCIETY AGED, 25 MEPHAN STREET, FOOTSCRAY VIC 3011 |  | Copper theft | [5 empty] | 2 | Unknown persons stolen copper earths from a pole A122890 (Cable Head Pole (CHP) to Mephan-Rosamond kiosk substation | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper earth cables stolen by unknown persons | Damage to network assets | 30/11/2017 17:30 |  |  | 6798 | Residential |  | 20171130JEM_02 | Infrastructure (network-based) | -37.7866 | 144.8849 | 1 | Jemena | Report | 8564 | 0.014774 | Earthing cable | Essendon Airport | 3011 | Footscray | Other
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT also notified the local DAO to investigate the incident. Crew replaced the EDO fuse. | 55 WHITELAWS TRACK, CALLIGNEE VIC 3844 | 2605775 |  | Bird | [5 empty] | IMS 231480. According to the caller reporting the fault a fuse dropped at a service pole. Bracket was on fire but now is out according to the caller. The attending fault crew reported that a bird had flown in to a HV EDO 6k fuse unit on a concrete substation pole and there was a small fire (1m x 1m) at the base of the pole. The local DAO arrived on site to find a recently deceased bird on the ground in the burnt area. Only bracken fern was burnt. No damage to owner's property. Photos taken show Substation pole, deceased bird and burnt area. | EDO fuse | 0 | 0 | 0 |  | tgn23 | Bird Incident | Grassfire | 29/11/2017 16:05 | 1 | Localised: less than 10 sq.m | 6793 | Residential |  | 20171130SPN_02 | Infrastructure (network-based) | -38.2947 | 146.5981 | 1 | AusNet Services Distribution | Report | 8554 | 0.010118 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Callignee | Animal
On arrival crew isolated supply and carried out repairs. | 1335 BOOTHROYDS ROAD, NUMURKAH VIC 3636 | 32186418 |  | Fallen |  |  |  |  | 1 | Vic Fire rang to advise of a grass fire at the incident location. On arrival the crew found a tree had fallen onto service line straining connections in fuse box, this in turn caused arcing resulting in a grass fire of approx. 0.5HA. A Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries. | Service conductor | 2 | 2 | 2 |  | NKA006 | Vegetation: Trees Incident | Loss of supply;Grassfire | 28/11/2017 15:45 | 1 | Small: 10 - 1000 sq.m | 6807 | Roadway |  | 20171204PWA_01 | Infrastructure (network-based) | -36.0201 | 145.3861 | 1 | Powercor | Report | 8574 | 0.010241 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Trees
Secured the ACR from closing. Assessed the protection targets received from ACRC conducted a thorough line inspection which revealed no other faults. Contacted Emergency Services for any accident or incident reports in the area. Ensured all people were clear from the line. Re-energised the line. CFA attended site and extinguished grass fire within approx. 1hr of incident, police also attended incident to investigate and record details of truck driver responsible for incident. Once area was made safe, AusNet Services' crew attended site to asses damage to electrical assets and to determine if line was safe to be re-energised. Only superficial damage (burn mark) on conductors found, operators advised that line was safe to be re-energised. AusNet Services' network representatives then arrived on site to conduct an investigation into incident and to record all damage caused both to electrical assets, and property. Details of driver responsibly provided by CFA investigator as they were leaving site as we arrived. | ROSEDALE FARM, 729 AERODROME ROAD, AVENEL VIC 3664 | 4706126 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 231422. ACR SE14614 Tripped and locked out. After inspection it was found that a customer opposite 729 Aerodrome Rd, between poles Lis 4705578 and 47006126, caused his vehicle to make contact with the live overhead 22kv conductors. The contact caused a flash which in turn ignited the grass. No damage was reported to the CEOT. After dumping a load of gravel/sand within the property approx. 20m East of the existing 22,000 volt overhead electrical conductors, the driver of the tipper trailer proceeded to drive away from the dumped load and towards the overhead conductors with the trailer still raised. The front of the raised trailer then made contact with the closest overhead conductor, then the second overhead conductor, causing an electrical fault, and also causing a grass fire in the surrounding area. The fire caused by this incident caused approx. 5000 sq.m of grass to be burnt out within the property with no stock, building or asset damage caused. Both Police and CFA attended the incident but had left site prior to AusNet Services arriving on site to investigate as fire was extinguished and made safe prior to our arrival. | Conductor (bare) | 0 | 0 | 0 |  | smr8 | A tip truck trailer made contact with overhead 22kV line. | Grassfire;No Go Zone (contact) | 27/11/2017 11:16 | 1 | Localised: less than 10 sq.m | 6812 | Agricultural |  | 20171204SPN_01 | Infrastructure (network-based) | -36.898 | 145.2127 | 1 | AusNet Services Distribution | Report | 10899 | 0.0099271 | 22kV AC | Mangalore Airport | 3664 | Avenel | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box on the Reticulation Pole . The attending Powercor Fault Crew replaced the Pole Top Connection Box at the Reticulation Pole and re-terminated the O/H Service Neutral Cable and completed an NST test which confirmed a Pass result. | 13 MOONAH AVENUE, NELSON VIC 3292 | 30142192 |  |  |  | Corrosion |  | Phase to earth |  | Mr Paul Brown was washing his hands in the Kitchen Sink when he received an electric shock as he made simultaneous contact with his hands between the Kitchen Taps and the metallic Kitchen Sink. | Connector/termination;Connection box | 2 | 2 | 2 |  | ETSA001 | Corroded neutral connection | Minor shock | 17/10/2017 9:30 |  |  | 6819 | Roadway |  | 20171205PWA_01 | Infrastructure (network-based) | -38.0425 | 141.0058 | 1 | Powercor | Report | 17366 | 0.017664 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3292 | Nelson | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged electrical infrastructure was replaced under Access Authority conditions. | ELIZABETH AVENUE, CAPEL SOUND VIC 3940 | 1300184 |  |  |  | Defective component |  |  | 0 | Fire authority reported a pole fire in Elizabeth Avenue near the corner of Eastbourne Road. A copper to aluminium ampact connection failed at HV/LV strain pole LIS No. 1300184 located on the corner of Elizabeth Street and the Broadway. This caused the helical termination to fail resulting in the red phase HV conductor to fall to the ground alive and the stage 1 and 2 BUEF protection to operate at RBD Zone Substation before the RBD23 feeder earth fault protection. No high voltage injection or damage was sustained although burn marks were created on the grass below where the conductor fell. | Connector/termination | 0 | 0 | 0 |  | RBD 23 | A copper to aluminium ampact connection failed at a HV/LV strain pole. | Grassfire | 24/11/2017 6:53 | 1 | Localised: less than 10 sq.m | 6822 | Roadway |  | 20171206UTD_01 | Infrastructure (network-based) | -38.3686 | 144.8718 | 1 | United Energy Distribution | Report | 12961 | 0.0030602 | 22kV AC | Moorabbin Airport | 3940 | Capel Sound | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged electrical infrastructure was replaced under Access Authority conditions. The pole was straightened and supply restored upon completion. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 678 NEPEAN HIGHWAY, CARRUM VIC 3197 | 3303240 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | 2.00AM - 22kV feeder CRM22 circuit breaker successfully reclosed and held. 2.50AM - Emergency high voltage switching was completed after a car had made contact with a HV tee-off / LV intermediate timber pole. A vehicle struck pole LIS No. 3303240 located outside 678 Nepean Highway Carrum that caused the HV/LV mid-span conductors to clash. Following the conductors clashing, splash marks were identified on the HV conductors after they made contact with the LV conductors and the faults crew requested a LEI attend as a HVI was suspected to customers supplied from "Progress-Nepean" substation. The LEI confirmed a high voltage injection occurred (MOR 1703) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | CRM 22 | A vehicle struck a HV/LV pole that caused the HV/LV mid-span conductors to clash and a HVI to occur. | HV injection;Loss of supply | 42806.0833 |  |  | 6842 | Residential |  | 20171211UTD_03 | Infrastructure (network-based) | -38.0796 | 145.123 | 1 | United Energy Distribution | Report | 8623 | 0.011053 | 22kV AC | Moorabbin Airport | 3197 | Carrum | Vehicle
MFB attended site. Site made safe and tramways de-energised their traction lines so that Jemena assets do not fall into tramways' DC supplies Temporary repairs were then conducted using live line techniques. The following is a list of repairs carried out at the time of writing: â€¢ Pole A050803 Gaffney Street 1 pole West of Sydney Rd - Replace damaged HV strain crossarm with new Sl 24 Steel - Install new HV isolators â€¢ Pole A034846 Murray Road East of Sydney Rd HV inter pole - Replace existing HV crossarm with new Assin 2.6 steel â€¢ Pole A050810 Gaffney Street 2 pole West of Sydney Rd Hv inter with isolators and Cable Head Pole - Replace existing wooden crossarm with new Sl 24 - Replace existing Hv isolators with new â€¢ Replace bay of .1,5 copper conductor from pole A050803 to pole A050810 â€¢ Follow up works still to be carried out is to repair HV cable at pole A050810 | 39 GAFFNEY STREET, COBURG VIC 3058 | pole no. A050803 |  |  |  | Rot |  |  | 1 | Live HV conductor fell to ground across foothpath due to failure of HV crossarm. The footpath side phase of the HV strain insulator's eye bolt pulling through the HV crossarm. The resultant shock load to HV isolator 13876 has caused the HV isolator insulator to break. As a result, the HV conductor fell to the ground whilst still alive and being fed by the Delta windings of the Distribution Transformers downstream of this location. East side of HV isolators have remaining HV overhead conductor hanging over Tramways traction DC cables on Sydney Rd. Protection operated as per design and no injuries were sustained by any Jemena staff, contractors or members of the public Failed wooden HV crossarm has been replaced with a steel HV crossarm. Unfortunately, no photos are available for this incident. | Conductor (bare);Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | CS13 | HV crossarm failure due to rot. The wooden HV crossarm was last inspected in 2016 and did not have any maintenance notifications raised against it until the incident occurred | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/12/2017 11:34 |  |  | 7851 | Roadway |  | 20171213JEM_01 | Infrastructure (network-based) | -37.734 | 144.9636 | 1 | Jemena | Report | 10901 | 0.015972 | 22kV AC | Essendon Airport | 3058 | Coburg | Crossarm
On arrival crew isolated supply to allow REC to complete repairs | 496 BLIND CREEK ROAD, MITCHELL PARK VIC 3355 | 30004172 | Vehicle | [6 empty] | A customer reported that a passing truck had struck the service cable at the incident location. On arrival the crew found that a high load had struck and pulled down the service cable to the premises, causing damage to the cable and the customer building. There were no reported shocks, injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | BAS011 | Unknown vehicle struck service | Damage to network assets | 24/10/2017 12:36 |  |  | 7853 | Roadway |  | 20171213PWA_02 | Infrastructure (network-based) | -37.5119 | 143.7577 | 1 | Powercor | Report | 9635 | 0.037196 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Mitchell Park | Vehicle
CEOT dispatched a fault crew to make safe and carry out necessary repairs. The fault crew repaired the damage overhead conductor. There are other trees alongside a water course which due to recent rain has affected their root systems which are being checked by AusNet Services' Vegetation group. Vegetation is predominately dry woodland species and highly susceptible to fire. | 154 GOLD MEMORIAL ROAD, WARRANDYTE VIC 3113 | 1224905 |  | Precipitation;Fallen |  |  |  | Phase to earth | 1 | IMS 231784. A large gum tree fell from across Gold Memorial Road across the high voltage line between poles 1205294 and 1224905. One 3/12 steel overhead HV conductor fell to the ground causing a small grass fire which was extinguished by the CFA. The feeder CB tripped to lockout. The tree in question is outside of the vegetation clearance space. | Conductor (bare) | 0 | 0 | 0 |  | rwn33 | Vegetation: Trees Incident | Grassfire | 42990.5479 | 1 | Localised: less than 10 sq.m | 7850 | Roadway |  | 20171213SPN_01 | Infrastructure (network-based) | -37.7568 | 145.2258 | 1 | AusNet Services Distribution | Report | 12821 | 0.034391 | 22kV AC | Moorabbin Airport | 3113 | Warrandyte | Trees
There are concerns with the disregard for safe working practices in accordance with established work practices the Jaguar REC's had and proceeded to work unsafely in close proximity to live electrical infrastructure with incorrect PPE for the tasks being completed. | 230 HAMMOND ROAD, DANDENONG SOUTH VIC 3175 |  | Unauthorised access;Caused by REC/contractor | [5 empty] | 2 | Chris Hargraves from Jaguar Electrics had arranged for 2 truck appointments to enable a supply upgrade to take place. As part of the work supply had to be isolated, but unfortunately, the customer didnâ€™t want to come off supply for half the day. Downer arranged for a safety observer and a Permit to Work to be issued the day prior to the planned truck appointment (08/12/2017) at no cost to Jaguar Electrics to lessen the interruption time for the customer. A Downer employee was driving past (06/12/2017) and noticed Jaguar Electrics representatives commencing work at the United Energy pillar and demanded they stop trying to break into pillar to install the consumers cabling while the pillar was alive with no safety observer present. This was disappointing and created an unsafe situation as Downer had worked with the REC to assist the supply upgrade that consisted of installing the new consumers mains and lugging off at the LV pillar. | LV Pillar | 0 | 0 | 0 |  |  | Vandalism and unauthorised access into a live LV pillar by a REC. | No Go Zone (contact);Damage to network assets | 42898.4375 |  |  | 7848 | Industrial |  | 20171213UTD_02 | Infrastructure (network-based) | -38.0182 | 145.2045 | 2 | United Energy Distribution | Report | 9629 | 0.02251 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Other
The crew made the site safe, and replaced the service. | 3 JENKINS STREET, CHARLTON VIC 3525 | 30021640 |  |  |  | Corrosion |  |  |  | The customer reported a wire down that had started a small fire at the incident location. On arrival the crew found that an LV neutral screened service cable had faulted. It caused a ground fire of approximately 2m X 2m. No damage or injury was reported. | Service conductor | 2 | 2 | 2 |  | CTN005 | Mechanical failure | Grassfire | 13/12/2017 13:15 | 1 | Localised: less than 10 sq.m | 7864 | Residential |  | 20171214PWA_04 | Infrastructure (network-based) | -36.2728 | 143.3582 | 1 | Powercor | Report | 9651 | 0.00056019 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3525 | Charlton | OH Cable
On arrival crew carried out repairs | 686-718 LEAKES ROAD, BONNIE BROOK VIC 3335 | 30258182 | Copper theft | [6 empty] | A Powercor contractor reported a copper theft at the incident location. Upon arrival, the Powercor crew found that the earthing cable on the sub pole had been stolen There was no fire, injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 24/10/2017 15:38 |  |  | 7868 | Roadway |  | 20171214PWA_06 | Infrastructure (network-based) | -37.6972 | 144.6584 | 1 | Powercor | Report | 9655 | 0.017684 | Earthing cable | Melbourne Airport | 3335 | Bonnie Brook | Other
Crew have isolated the area, â€œsite made siteâ€. Due to damage sustained the pole is being replaced. | 264 JOHNSTON STREET, FITZROY VIC 3065 | 30172751 | Vehicle | [6 empty] | The MFB reported that a car has collided with a pole at the incident location, conductors are down on the ground and resting across a parked car. On arrival the fault crew found that the lady driver appears to have had a heart attack and has driven her car into a pole at speed. The cross arm has been broken and low voltage mains are on the ground. Two low voltage fuses in the substation have operated but third phase â€œALIVEâ€ on the ground at the incident location. There was no fire. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | CW012 | Vehicle struck pole | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42805.5271 |  |  | 7873 |  |  | 20171215PWA_03 | Infrastructure (network-based) | -37.799 | 144.9839 | 1 | CitiPower | Report | 9660 | 0.036509 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Vehicle
On arrival crew completed isolation and made site safe. | 2 WRIGHT STREET, SUNSHINE VIC 3020 | 32168865 | Copper theft | [6 empty] | A Powercor employee found vandalised pole at the incident location. Upon arrival, the Powercor fault crew found that the HV O/H conductors and UG cable cut away. This is a vacant property that belongs to a HV customer, Grain Elevators. This time, thieves cut the OH conductors of two bays and approx. 6m of 22kV UG cables on the CHP have been stolen. | Conductor (bare);Cable | 2 | 2 | 2 |  | SSE034 | vandalism - copper theft | Damage to network assets | 23/10/2017 14:09 |  |  | 7877 | Industrial |  | 20171215PWA_05 | Infrastructure (network-based) | -37.7966 | 144.8382 | 1 | Powercor | Report | 9666 | 0.0013866 | 22kV AC | Essendon Airport | 3020 | Sunshine | Other
CEOT dispatched a fault crew to isolate supply, make safe and arrange for repairs. Supply isolated and conductors repaired. Downer overhead crew dispatched to repair fault. | 575 BRIDGE INN ROAD, MERNDA VIC 3754 | 917516 |  |  |  | Age;Corrosion |  | Phase to earth | 1 | IMS 231699. Initial report: 2x2m burn marks found on the ground due to LV conductor breakage at LIS# 917561. Final report: A LV white phase 7/0.64 copper conductor appeared to have broken mid-span between poles #917516 & 917515. The DAO could not see any specific cause for the break, but suspected it to be due to its age with prior sleeving repairs done on the conductor and adjacent conductors. The DAO could not see any fire marks as a result of the conductor failure with the break occurring above a tar road and nor were there any at fire marks at base of pole #917516 where sparks from LV phase to phase short circuit fault current would have occurred. The fallen conductor was barricaded with Police warning tape. The DAO could also not see any property damage on his arrival. The attending Downer linesman advised that he and the crew noticed small burn marks on the ground not at the conductor down location but at the nearby substation pole supplying the overhead LV conductor circuit, where a LV crossarm fuse for this LV conductor blew due the fault. It is considered that hot particles from the operating of the LV fuse fell to the ground at the base of the substation pole and caused this small grass fire (approximately 2m x 2m in size. The CFA attended. | Conductor (bare) | 0 | 0 | 0 |  | DRN12 | Broken LV copper conductor. | Grassfire | 14/12/2017 11:14 | 1 | Localised: less than 10 sq.m | 7875 | Residential |  | 20171215SPN_01 | Infrastructure (network-based) | -37.6007 | 145.0979 | 1 | AusNet Services Distribution | Report | 12848 | 0.024815 | Low voltage AC (<1kV) | Essendon Airport | 3754 | Mernda | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 8B RAILWAY AVENUE, OAKLEIGH VIC 3166 | 2325346 |  |  |  | Conductor clashing;Electrical overload |  |  | 1 | At 2212hrs on 14/12/2017, 66kV feeder OE-CDA opened auto with no auto reclose. At the same time, 11kV feeder OE04 and ACR OA8108 both had successful recloses. The feeders were patrolled and the zone substation exit isolators on the OE04 CHP had a blown off bridge on the red phase and was arcing and sparking. This fault appeared to be the cause of the 66kV reclose as the line runs directly above the HV isolators on the same pole. 2350hrs - The United Energy Network Control Centre attempted to restore the 66kV feeder OE-CDA via CB C at CDA and the feeder CB tripped again. The crew who were in attendance found the 66kV and 11KV conductors wrapped together between pole No. LIS 2333277 and 2333278 in Railway Avenue. As the crew patrolled the 11kV feeder approximately 5 minutes after the earlier fault, a 3 sqm fire had started in sword grass underneath "Railway P1W-Warner' pole type substation that was quickly extinguished by the crew with a fire extinguisher. The fire was caused when the 11kV red phase powder filled fuse unit failed and the top contact of the fuse clamp fell into the grass below. The 11kV 500kVA transformer at the pole type substation at pole number LIS 2325346 was fused with 56amp powder filled fuses that require replacement. The Live Line clamps to the fuse unites were lifted and stowed and the substation placed under LV parallel. | Connector/termination | 1 | 0 | 0 |  | OE 04 11kV | The 66kV and 11KV conductors wrapped together in Railway Avenue. | Loss of supply;Grassfire | 14/12/2017 22:34 | 1 | Localised: less than 10 sq.m | 7881 | Roadway |  | 20171215UTD_01 | Infrastructure (network-based) | -37.91 | 145.1019 | 1 | United Energy Distribution | Report | 12967 | 0.0027095 | 11kV AC | Moorabbin Airport | 3166 | Oakleigh | AF Other
On arrival crew isolated supply and carried out repairs. The customer engaged an REC to make repairs to the building | 509 WALLACEDALE-BYADUK ROAD, WALLACEDALE VIC 3303 | 30087571 |  | Fallen | [5 empty] | A customer reported that a tree had struck the service cable at the incident location. On arrival the crew found that a tree had struck and pulled down the service cable to the incident location, causing damage to the cable and the customer building. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | HTN002 | Vegetation: Trees Incident | Loss of supply;Less than $50k damage | 25/10/2017 8:01 |  |  | 7887 | Agricultural |  | 20171218PWA_01 | Infrastructure (network-based) | -37.9232 | 141.8424 | 1 | Powercor | Report | 9676 | 0.0092662 | Low voltage AC (<1kV) | Hamilton Airport | 3303 | Wallacedale | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral and Active Conductor terminations at the Pole Top Connection Box located on the Reticulation Transformer Pole, The attending Powercor Fault Crew replaced the Faulty O/H Service Cable at the Pole Top Connection Box and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 126 CORANGAMITE LAKE ROAD, COLAC WEST VIC 3250 | 30051081 |  |  |  | Corrosion |  | Phase to earth |  | Ms Graham was washing mud from hands and feet at an external garden tap when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and her bare feet while standing on the wet ground. | Service conductor;Connection box | 2 | 2 | 2 |  | CLC004 | Corroded connection in pole junction box | Minor shock | 42988.5833 |  |  | 7892 | Roadway |  | 20171218PWA_06 | Infrastructure (network-based) | -38.3229 | 143.5314 | 1 | Powercor | Report | 9689 | 0.039803 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac West | Connection
The crew isolated supply to the circuit and completed repairs. | 110-116 MURRAY STREET, COLAC VIC 3250 | 34028809 | Working too close to underground cables | [6 empty] | A customer rang to advise the traffic lights on the Cnr of Murray and Gellibrand Stâ€™s, Colac where not operating. A crew attended and found an underground boring contractor operating onsite had struck an underground low voltage mains at the intersection. No protection operated. The contractor had completed a dial before you dig and had plans onsite but had not read the plans correctly and not expected a cable to be laid under the existing pit. There was no ground fire start. There were no reported shocks or injuries. | Services cable | 2 | 2 | 2 |  | CLC002 | Directional boring | Loss of supply;Damage to network assets | 26/10/2017 13:24 |  |  | 7901 |  |  | 20171218PWA_11 | Infrastructure (network-based) | -38.3398 | 143.5872 | 1 | Powercor | Report | 12078 | 0.023939 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | Dug up
Truck driver remained in vehicle until crew had made site safe. Crew isolated and left 2 shops off overnight. Pole and services replaced | 98 KNOX STREET, NUMURKAH VIC 3636 | 33083547 | Vehicle | [6 empty] | CFA reported truck has hit overhead wires and wires down on truck. On arrival, crew found a concrete LV service pole that had snapped and the twisted LV service on a B double truck. Information that the crew obtained from the site is that a B double truck had gone down a street that could not be exited at the end and, while trying to exit the street, caught the LV road crossing between the two trailers which in turn caused the concrete service pole to snap. No injuries, no ground fire, no third party damage. | Service conductor;Pole (concrete) | 2 | 2 | 2 |  | NKA004 | Truck entangled in services | Loss of supply;Damage to network assets | 30/10/2017 17:45 |  |  | 7906 | Roadway |  | 20171219PWA_02 | Infrastructure (network-based) | -36.0923 | 145.4324 | 1 | Powercor | Report | 9705 | 0.036436 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Vehicle
Crew have replaced/repaired the earth cables. | 90 MURRAY ROAD, THORNHILL PARK VIC 3335 | 30108502 | Copper theft | [6 empty] | Rod, from ELECTRIX reported HV earth stolen from a pole substation. A crew attended and found that HV cable earths were cut and removed from pole LIS-111656. No shock, injuries or third party damage. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper Theft | Damage to network assets | 42746.7729 |  |  | 7912 | Roadway |  | 20171219PWA_05 | Infrastructure (network-based) | -37.7165 | 144.632 | 1 | Powercor | Report | 9718 | 0.027948 | Earthing cable | Laverton Raaf | 3335 | Thornhill Park | Other
The crew replaced the service cable. | 6 PAULS CRESCENT, WENDOUREE VIC 3355 | 32008355 |  |  |  | Corrosion |  |  |  | Vic fire rang to advise a wire was on fire and down on the ground at the above incident location. A crew attended and found a neutral screen service cable to 6 Paul Crescent, Wendouree had burnt thru at the roller clamp on the pole end and fallen to the ground. There were no reported shocks or injuries. No ground fire start or evidence of fire | Service conductor | 2 | 2 | 2 |  | BAN004 | insulation failure | Loss of supply;Melting or smoking only;Damage to network assets | 42746.6889 |  |  | 7914 | Roadway |  | 20171219PWA_07 | Infrastructure (network-based) | -37.5335 | 143.8408 | 1 | Powercor | Report | 13485 | 0.0044306 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | OH Cable
CEOT dispatched a fault crew to make safe, isolate and arrange for necessary repairs. Electrical Access Permits were Issued for works on HV and LV cables. EAPs were Cancelled on completion of repair works. Sanction For Testing application was Receipted and Relinquished following tests and cables were deemed fit for service. Downer have repaired the HV and LV. For rectification works 10 metres of 185 sq.mm 3 core AL conductor XLPE HV cable and 2 HV straight joints plus 5 metres of 185 sq. mm sq.mm 4 core AL conductor XLPE LV cable and 2 straight LV joints were installed. AusNet Services' damage recoverable section to initiate recoverable costs. Boring contractor's details are: GC Plumbwise, telephone 0411 701705. | 52 LINACRE DRIVE, BUNDOORA VIC 3083 | 5710461 | Working too close to underground cables |  |  |  |  | Phase to phase | 1 | IMS 231767. Initial Report: A plumbing contractor operating an underground boring machine caused the borer machine to hit an underground HV cable causing the feeder to trip. Final report: A plumbing contractor operating an underground boring machine caused the borer machine to hit an underground HV cable and an underground LV cable, causing the feeder ACR to trip. The borer machine also hit underground Telstra cables. 60 customers off supply. | Cable | 0 | 0 | 0 |  | wt13 | An underground boring machine made contact with underground HV and LV cables. | Loss of supply;No Go Zone (contact) | 18/12/2017 13:54 |  |  | 7905 | Residential |  | 20171219SPN_01 | Infrastructure (network-based) | -37.6858 | 145.0781 | 1 | AusNet Services Distribution | Report | 10958 | 0.034032 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3083 | Bundoora | Dug up
The site was made safe and the LV service was replaced. | 10 LYNTON CRESCENT, KYABRAM VIC 3620 | 33096116 | Vehicle | [6 empty] | Boral Asphalt reported one of their vehicles hit and bought down powerlines at the incident location. On arrival the crew found that a Low Voltage (LV) service had been hit by a truck, resulting in it coming to ground. here were no reported injuries or other third paryt damage. | Service conductor | 2 | 2 | 2 |  | KYM002 | Truck contacted service line | Loss of supply;Damage to network assets | 43019.5111 |  |  | 7933 | Roadway |  | 20171220PWA_06 | Infrastructure (network-based) | -36.3062 | 145.0482 | 1 | Powercor | Report | 9744 | 1.7361e-05 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Kyabram | Vehicle
On arrival crew isolated supply and carried out repairs | 1578 MOUNT TERRICK ROAD, ROSLYNMEAD VIC 3564 | 32181340 |  | Blown branch/vegetation | [5 empty] | The CFA reported a grass fire at the incident location. On arrival the crew found that a tree had come over causing an LV service to come to ground and short out on a steel fence post, which in turn caused a ground fire of approximately 10m X 10m at the incident location. Damage was reported to the grassland only, no injury was reported | Service conductor | 2 | 2 | 2 |  | ECA012 | Wind and storm event | Grassfire | 20/12/2017 10:35 | 1 | Small: 10 - 1000 sq.m | 7939 | Agricultural |  | 20171221PWA_03 | Infrastructure (network-based) | -36.1294 | 144.5527 | 1 | Powercor | Report | 9756 | 0.023604 | Low voltage AC (<1kV) | Bendigo Airport | 3564 | Roslynmead | Trees
On arrival crew commenced repairs | 585 JENNINGS HILL ROAD, SUTTON GRANGE VIC 3448 | 33029021 |  | Blown branch/vegetation |  |  |  |  | 1 | Crew attended to find cable down between pole # 9 and pole # 10 Sutton Grange East Spur where an epicormics attached limb had dislodged and was blown across the HV Conductors . Estimated 50 acres of property burnt. No injuries, No reported shocks. | Conductor (bare) | 2 | 2 | 2 |  | CMN003 | Limb had dislodged in severe windstorm | Grassfire | 20/12/2017 17:50 | 1 | Large: more than 10 ha | 7943 | Agricultural |  | 20171222PWA_02 | Infrastructure (network-based) | -36.9944 | 144.3838 | 1 | Powercor | Report | 11017 | 0.0024757 | 22kV AC | Bendigo Airport | 3448 | Sutton Grange | Trees
The site was made safe and the HV conductor was repaired. | 50 PITMANS ROAD, GYMBOWEN VIC 3401 | 32101886 | Vehicle | [5 empty] | 1 | A customer (Mathew Gabbe) called to say a tip truck had contacted the overhead line at the incident location and left site. No details of the truck or driver were available. On arrival the crew found that a HV conductor had been contacted and had damaged strands near LIS 23222. There were no reported injuries or other third part ydamage. | Conductor (bare) | 2 | 2 | 2 |  | HSM004 | Unknown truck hit conductor | Damage to network assets | 21/12/2017 12:01 |  |  | 7947 |  |  | 20171222PWA_04 | Infrastructure (network-based) | -36.7235 | 141.6145 | 1 | Powercor | Report | 9769 | 0.041029 | 22kV AC | Horsham Aerodrome | 3401 | Gymbowen | Vehicle
A faults crew attended and safely replaced the copper earth cable at the substation. | 32 BARRY STREET, SEAFORD VIC 3198 | 3309758 | Copper theft | [5 empty] | 2 | Caller reports the copper wire has been cut from the pole adjacent his property. The wire is exposed and there is no arcing or sparking. A 2.5m length of copper earth cable has been cut and removed by unknown person/s from "Barry-Fellowes" pole type substation - pole No. LIS 3309758. | Earth/earthing | 0 | 0 | 0 |  |  | Stolen copper earth cable from "Barry-Fellowes" pole type substation. | Damage to network assets | 22/12/2017 13:30 |  |  | 7953 | Roadway |  | 20171227UTD_02 | Infrastructure (network-based) | -38.1138 | 145.1481 | 1 | United Energy Distribution | Report | 9776 | 0.028184 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Other
crew attended and rep[laced fused mains box | GARVAN PARK, 340 AVOCA-BEALIBA ROAD, RATHSCAR WEST VIC 3465 | 30020147 |  |  |  | Overheated connection |  |  | 1 | VicFire Reported grass fire around the base of wood pole. The attending powercor crew found that a low voltage fuse box had malfunctioned. | Any other type | 0 | 0 | 0 |  | MRO008 | connection malfunction | Grassfire | 26/12/2017 21:14 | 1 | Small: 10 - 1000 sq.m | 7962 | Roadway |  | 20180102PWA_03 | Infrastructure (customer connection) | -37.0377 | 143.4785 | 1 | Powercor | Report | 9790 | 0.031363 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Rathscar West | Connection
Crew attended and replaced fuse tube | 105 RIFLE BUTTS ROAD, LANDSBOROUGH VIC 3384 | 33050264 |  |  |  | Fuse failed to eject |  |  | 1 | Customer called to advise of a fire start at the above address. A crew attended and found a HV fuse tube malfunctioned, dropping hot material onto the ground, starting a ground fire of approx. 20m x 10m in area on private property. Customer extinguished fire | EDO fuse | 0 | 0 | 0 |  | STL007 | EDO fuse malfunction | Grassfire | 30/12/2017 14:35 | 1 | Small: 10 - 1000 sq.m | 7968 |  |  | 20180102PWA_09 | Infrastructure (network-based) | -37.0138 | 143.1182 | 1 | Powercor | Report | 9804 | 0.024176 | 22kV AC | Ballarat Aerodrome | 3384 | Landsborough | Fuse
Small fire (30cm x 30cm) at POA at 27 Drayton caused form HVI blowing up POI Select inspectors onsite completing meter changes and testing. 2x >20m tall thin pine trees taken down by tree clearing crew to avoid future recurrence. | 2-4 DRAYTON CRESCENT, PARK ORCHARDS VIC 3114 | 1205256 |  | Fallen |  |  |  | Phase to phase | 1 | IMS 231822 - feeder tripped. DAO onsite. Large tree (>20m tall) 5m from HV/LV Line fell over and brought HV down into LV causing HVI. 2x Bays HV/LV on ground and asset damaged (X-Arms, poles shaken etc). | Conductor (bare) | 0 | 0 | 0 |  | RWN26 | Vegetation: Trees Incident | HV injection;Loss of supply;Other electricity related | 27/12/2017 11:58 | 1 | Localised: less than 10 sq.m | 7958 | Residential |  | 20180102SPN_03 | Infrastructure (network-based) | -37.7819 | 145.2096 | 1 | AusNet Services Distribution | Report | 12816 | 0.028529 | 22kV AC | Moorabbin Airport | 3114 | Park Orchards | Trees
On arrival crew isolated supply and carried out repairs | 1 WERONA ROAD, FAIRHAVEN VIC 3231 | 33041158 |  |  |  | Electrical overload;Overheated connection |  |  |  | Vicfire reported a small grass fire at Fairhaven. On arrival the Powercor crew found the fire had been extinguished by local residents. An area of grass some 5 by 5 metres at the base of the substation pole was burnt. A ruptured copper to aluminium tee clamp connection was subsequently found and repaired. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | WPD014 | Ruptured copper to aluminium tee clamp connection | Grassfire | 43252.6111 | 1 | Small: 10 - 1000 sq.m | 7980 | Public space |  | 20180108PWA_02 | Infrastructure (network-based) | -38.466 | 144.0813 | 1 | Powercor | Report | 9828 | 0.011279 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Fairhaven | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. This included 11 80w MV lanterns on the circuit that were connected to the red phase. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 54 BOWEN STREET, MALVERN EAST VIC 3145 | 2315712 |  | Blown branch/vegetation |  | Conductor clashing;HV injection |  |  | 1 | At 1756hrs on 06/01/2017, 11kV feeder EM 02 circuit breaker reclosed to lockout affecting 644 customers. During strong winds, a large tree branch from a customers gum tree located in the front yard of 54 Bowen Street contacted the 11kV conductors that resulted in a HV conductor to contact the LV conductors below near pole No. LIS 2315712. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the west circuit of "Fenwick-Chadstone" substation. The LEI confirmed a high voltage injection occurred (BWD 1801) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | EM 02 | Vegetation: Trees Incident | HV injection;Loss of supply | 43252.7472 |  |  | 7975 | Residential |  | 20180108UTD_02 | Infrastructure (network-based) | -37.8831 | 145.0779 | 1 | United Energy Distribution | Report | 9821 | 0.033192 | 11kV AC | Moorabbin Airport | 3145 | Malvern East | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an Open Circuit O/H Service Neutral Conductor where terminated at the FOLCB located at the Customerâ€™s POA. The attending Powercor Fault Crew reterminated the O/H Service Neutral Conductor at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result following installation of a new FOLCB by REC. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 13 ARGYLE ROAD, MARYBOROUGH VIC 3465 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Ian Hughes was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metallic Shower Taps and his bare feet while standing on the wet shower base. | Service conductor;Customer installation | 2 | 2 | 2 |  |  | Corroded connection in customers FOLCB | Minor shock | 13/11/2017 4:30 |  |  | 8983 | Residential |  | 20180109PWA_01 | Infrastructure (customer connection) | -37.0505 | 143.7457 | 1 | Powercor | Report | 10891 | 0.021392 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | Connection
Site observed to be safe. Developer in negotiation regarding other non compliance with the project ( Stonehill Stage 7B) | 1 CALDERWOOD ROAD, MADDINGLEY VIC 3340 | [5 empty] | Ineffective planning/procedures/processes |  |  | Auditor Observed a Low voltage Pit which had previously been detailed as being non compliant had been lowered without a Permit to work being applied for. There was no injuries or third party property damage. | Services pit | 2 | 2 | 2 |  |  | Interference with service pit by non qualified person | No Go Zone (no contact) | 42959.6667 |  |  | 8985 | Public space |  | 20180109PWA_03 | Infrastructure (network-based) | -37.6831 | 144.4175 | 1 | Powercor | Report | 10835 | 0.010091 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Other
The faults crew proceeded to replace the FOLCB on pole No. LIS 3314469 and supply was restored to the customers upon completion. | 14 KOORNALLA CRESCENT, MOUNT ELIZA VIC 3930 | 3314469 |  |  |  | Overheated connection |  |  | 2 | Caller Brian (9787 6130) called to report of a pole on fire in front of the property with sparking, flames and smoke evident. A pole mounted three phase FOLCB that contained an underground service that supplied 5 and 7 Koornalla Crescent caught on fire and proceeded to self-extinguish. The cause was unknown but most likely a loose connection that overheated. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. | Pole-top fire | 17/12/2017 20:58 | 1 | Negligible: no ground fire | 7983 | Roadway |  | 20180109UTD_01 | Infrastructure (network-based) | -38.183 | 145.0758 | 1 | United Energy Distribution | Report | 12968 | 0.02528 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Connection
The crew removed branches, replaced fuses and restored supply. | 1181 CALDER HIGHWAY, MARONG VIC 3515 | 30147096 |  | Blown branch/vegetation |  |  |  |  | 1 | During high winds tree branch's were blown onto HV conductors starting a small grass fire at the incident location. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | BET006 | Wind blown debris from outside clearance space struck line. | Grassfire | 43252.6618 | 1 | Small: 10 - 1000 sq.m | 8994 | Agricultural |  | 20180110PWA_01 | Infrastructure (network-based) | -36.7386 | 144.1577 | 1 | Powercor | Report | 13704 | 0.040814 | 22kV AC | Bendigo Airport | 3515 | Marong | Trees
On arrival crew carried out repairs and restored supply. | 1 KOSTADT STREET, NATHALIA VIC 3638 | 33079710 |  |  |  | Fuse failed to eject |  |  |  | An EDO Candled and burnt in Half at the incident location. There was no ground fire, no reported injuries or third party property damage. No photos available | EDO fuse | 2 | 2 | 2 |  | NKA002 | Unconfirmed, probable fuse maloperation | Pole-top fire;Hung-up fuse only | 43282.1257 | 1 | Negligible: no ground fire | 8996 | Roadway |  | 20180110PWA_03 | Infrastructure (network-based) | -36.0511 | 145.2058 | 1 | Powercor | Report | 10851 | 0.032105 | 22kV AC | Shepparton Airport | 3638 | Nathalia | Fuse
The crew made safe, replacing pole & transformer. | MURRAY VALLEY HIGHWAY, KERANG VIC 3579 | 32029791 |  | Lightning |  |  |  |  | 1 | Vic Fire reported pole fire at the incident location. On arrival the crew found a pole had been struck by lightning causing the transformer to fail and ignited a small grass fire. 10m x 10m. There were no reported shocks or injuries. | Pole (wood);Pole mounted | 2 | 2 | 2 |  | KGT003 | Lightning strike | Grassfire | 43313.8257 | 1 | Small: 10 - 1000 sq.m | 9007 | Roadway |  | 20180111PWA_03 | Infrastructure (network-based) | -35.7633 | 143.9315 | 1 | Powercor | Report | 10873 | 0.032189 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | Lightning
Supply isolated. Repairs/replacement organised | 129A THE AVENUE, SUNSHINE WEST VIC 3020 | Pa0119174 |  |  |  | Electrical breakdown;Overheated connection |  |  | 1 | Customer reported a transformer fire at the incident location. On arrival the crew found that a kiosk substation had caught fire, resulting in a fire behind the closed doors of the kiosk substation. Protection operated. There were no reported injuries, no shocks, no ground fire, no HVI. The fence adjacent to the kiosk damaged due to the fire. | Disconnector/isolator;Pad mounted equipment/kiosk | 2 | 1 | 2 |  | SU035 | Internal fault | Plant/equipment | 43252.8229 | 1 | Negligible: no ground fire | 9010 | Public space |  | 20180111PWA_05 | Infrastructure (network-based) | -37.7991 | 144.8046 | 1 | Powercor | Report | 10880 | 0.0059028 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | OH Cable
In order to complete the repair the transformer was isolated on both HV and LV sides. The original neutral copper dropper (70 mm) was replaced by 120 mm copper dropper. The new dropper was connected to the overhead LV neutral reticulated conductor using a Parallel Groove (PG) clamp. A LV spreader has also been installed. Jemena faults crew requested Tech Safe Compliance / Electrical to attend the site to effect the restoration of supply to customer premises following the repair of the neutral dropper. Jemena Network Operations and Control (NOC) were advised that a large number of customers had appliances damaged and NOC activated the Emergency Management Team (EMT) to deal with influx of customer inquiries on the 12 January 2018. Jemenaâ€™s Claims and Recoverable Works engaged Sphere Electrical Contractors to attend and assist customers with any required repairs to their installation and appliances. The substation was re-instated into service at approximately 00:01 hrs (AEDT) on 12 January 2018 however no customers were reconnected until confirmed to be safe by Tech Safe Compliance / Electrical. Power was restored to majority of customers by approximately 16:00 hrs (AEDT) on the 12 January 2018 with few customers remaining off supply until it was determined safe to reconnect. A formal risk assessment has been conducted to identify and consider any additional controls (listed below) which can be put in place to prevent a recurrence i. Conduct analysis of additional AMI data, when it is available later in 2018 ii. Consider installing data recording (all parameters including load) equipment for new substations (possible additional control raised in risk assessment, due date to be decided if it is decided to be implemented) iii. If the date of tree removal is available, investigate the effect on HV and if the event was recorded. In addition, consider rate of change of voltage if there is any detectable signature in the HV waveform (feasibility of action dependent on whether date of tree removal can be discovered) Pending actions are as follows: 1. Arrange a thermographic survey of Barrington-Parnell substation and adjacent substations (30 April 2018) 2. Arrange a meeting with Hume City Council to discuss tree removal outside 30 Barrington Crescent during 2017 of which Jemena was not informed and for which no permit applications were submitted (30 June 2018) i. Brief the council on impacts of this incident and try to get council to acknowledge the risks of tree removal in the vicinity of powerlines and follow protocols for tree removal / vegetation management ii. Try to find out from Hume Council exactly when the tree was cut 3. Consider implementing 5 minute smart metre data collection across network, which will enable monitoring of neutral impedances at customer premises which will help identify broken neutrals, and complete the field tests for phase detection using smart meters (31 December 2018) | 35 BARRINGTON CRESCENT, GLADSTONE PARK VIC 3043 |  |  | Fallen;Council |  | Conductor clashing;Neutral fault |  |  | 1 | On 11 January 2018 a customer contacted Jemena at 18:04 hrs (AEDT) to advise of the intermittent loss of supply occurring approximately five times over a 30 minute period. Jemena smart meter data supports the customer observation of the intermittent power loss. The commencement time of this event is approximately 17:26 hrs (AEDT) on 11 January 2018. Jemena crew attended the site at approximately 20:20 hrs (AEDT) and disconnected all supply from Barrington-Parnell distribution substation. The crew identified that transformer LV neutral dropper was broken. The LV neutral dropper is used to connect the overhead LV reticulated neutral conductor to the neutral bushing of the transformer (Barrington-Parnell substation) burnt off. The dropper burnt off close to the D-Loop (split bolt) clamp at the point where the conductor is dropping (bending) and continues to connect with transformer neutral bushing and transformer LV earth conductor. As a result of the neutral connection failure the transformer neutral (star point) remained connected to the substation CMEN. However, the aluminium overhead reticulated mains neutral was isolated from the CMEN star point of the transformer. This created a condition where customers experienced over and under voltages which were observed as intermittent interruption to power supply. Over voltage caused damage to customer appliances at approximately 50% of the 98 residential properties supplied from Barrington-Parnell substation. Although the exact root cause of the incident could not be determined, available evidence suggests that tree clearing conducted by a third party is the probable cause of the dropper failure. NearMap photos have been attached in the "Notes & Findings" section. Note that Jemena will not be providing the investigation report in its entirety as it was prepared under professional legal privilege. Please refer to an email sent to Rob Oldfield on 9 March 2018 and email correspondence with Greg Sieburn on this matter, which are attached in the Notes & Findings section. | Conductor (bare);Copper;Pole mounted;Customer installation;Dropper/bridge | 0 | 0 | 0 |  | AW02 | Vegetation: Trees Incident | Loss of supply;More than $50k damage;Melting or smoking only | 43405.2535 |  |  | 9012 | Residential |  | 20180112JEM_01 | Infrastructure (network-based) | -37.6896 | 144.8934 | 1 | Jemena | Report | 13400 | 0.0047465 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Gladstone Park | Trees
Initial Report: made safe, investigating. Final report: CEOT dispatched a fault crew to make safe, investigate and arrange for any necessary repairs. BG548 to BG717 de-energised. Tree branch was removed under EAP. Crew replaced Red and White phase 50E Boric Acid fuses at BG113. CEOT also dispatched a LEI to check for any HVI damage - no damage occurred. | 137 WOORI YALLOCK ROAD, COCKATOO VIC 3781 | 420317 |  | Fallen;MEC |  |  |  | Phase to phase | 1 | IMS231978 - Initial Report: Tree on HV & LV reported by Emergency Authorities. Small fire at ground level extinguished by CFA. Final Report: No ground fire evident, resident reports that the CFA extinguished embers from a branch that caught fire, it had fallen and was resting on the conductors. A large branch failed from a large gum tree approximately 30m high that overhangs all phases of HV and LV conductors (3 spans). Decay and discolouration from an old wound was evident at the point of failure that was approximately 9m above the conductors. LBRA fire zone. The private tree is classed as a hazardous tree with AusNet Services' having responsibility for vegetation clearances. The tree branches were not located inside the clearance space. Electrical protection operated. Recloser trip and HV fuses operated. | Conductor (bare) | 0 | 0 | 0 |  | BGE22 | Vegetation: Trees Incident | Grassfire | 43435.2653 | 1 | Localised: less than 10 sq.m | 9020 | Residential |  | 20180112SPN_01 | Infrastructure (network-based) | -37.9251 | 145.4974 | 1 | AusNet Services Distribution | Report | 10902 | 0.028328 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3781 | Cockatoo | Trees
The faults crew replaced the copper earth cable and re-installed the timber cover guards at pole No. LIS 3309535. | 20 MORETON STREET, FRANKSTON NORTH VIC 3200 | 3309535 | Copper theft | [5 empty] | 2 | Caller reports the earth lead that runs down the pole has been cut at pole 3309535. The wood on the pole has also been removed. A customer contacted the United Energy faults and emergencies call centre advising that copper cabling had been stolen from the pole. The faults crew attended and found that unknown persons had stolen the copper earth cable from the HV/LV pole outside 20 Moreton Street, Frankston North. The cable was removed along with the timber cover guard. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown persons stole copper earth cable. | Damage to network assets | 43405.3646 |  |  | 9017 | Roadway |  | 20180112UTD_03 | Infrastructure (network-based) | -38.1196 | 145.1545 | 1 | United Energy Distribution | Report | 10888 | 0.037711 | 22kV AC | Moorabbin Airport | 3200 | Frankston North | Other
On arrival crew carried out repairs. LEI attended to asses HVI Damage | 54 FEDERATION STREET, PATCHEWOLLOCK VIC 3491 | 32151382 |  |  |  | Leakage |  |  | 1 | Customers reported all supply fail and hearing nearby fire sirens at incident location. On arrival the crew found that a HV strain cross-arm had burnt through on P124 Patchewollock line on the footpath side causing HV conductor to fall onto the LV circuit below. CFA in attendance, to extinguish the cross-arm fire, but also the air conditioning unit in the adjacent Town Hall building which the embers from the burning cross-arm are believed to have entered, CFA have had to remove the evaporative unit to douse the roof cavity to extinguish the fire in the roof of the structure LEI advised damage due to HVI relatively minor. There were no reported injuries, go ground fire. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | OYN005 | Excessive Leakage current | Pole-top fire;HV injection;Loss of supply;Significant disruption to the community | 13/01/2018 17:40 | 1 | Negligible: no ground fire | 9024 | Roadway |  | 20180115PWA_02 | Infrastructure (network-based) | -35.3834 | 142.1875 | 1 | Powercor | Report | 10896 | 0.034322 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3491 | Patchewollock | Crossarm
CEOT dispatched a fault crew to make safe and carry out / arrange for any necessary repairs. The crew found that the transformer was most likely hit by lightning. CEOT also requested an AusNet Services' LEI to attend to investigate. The LEI attended on Sunday and confirmed HVI damage to customers' appliances but the revenue meters were OK. 20kVA transformer was replaced with a 25kVA transformer. Also required 3 metres of HV dropper and HV and LV bushing caps. | 955 ARTHURS CREEK ROAD, ARTHURS CREEK VIC 3099 | 926007 |  | Lightning |  |  |  |  | 1 | IMS 231997. Report of All Supply Failures and appliances damaged. A SWER transformer (20kVA) was blown, most likely as a result of a lightning strike which resulted in HVI damage to properties. 955 Arthurs Creek Rd: ceiling fan, computer, TVx2, Playstation, DVD player, water fall, pump, Ioniser box, sprinkler pump, Bluetooth speaker, microwave, kitchen Fridge, Lounge TV, home phone. 945 Arthurs Creek Rd: Did not sustain too much damage, a double adaptor surge alert and some blown light fitings only. | Pole mounted | 0 | 0 | 0 |  | DRN14 | Lightning strike to substation transformer. | HV injection | 13/01/2018 20:49 |  |  | 9023 | Residential |  | 20180115SPN_01 | Infrastructure (network-based) | -37.5778 | 145.1965 | 1 | AusNet Services Distribution | Report | 10897 | 0.030426 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3099 | Arthurs Creek | Lightning
Capacitor replaced. | 4077 MURRAY VALLEY HIGHWAY, PIANGIL VIC 3597 | 30100069 |  | Lightning |  |  |  |  | 1 | Emergency Services reported a pole fire at the incident location. Upon arrival, the Powercor crew found 100*20 Sqm grass fire. There was a report of capacitor unit and transformer sparking at the incident location. The protection operated. CFA attended. There were no injuries. | Equipment;Transformer | 2 | 1 | 2 |  | SHL002 | There was a lightning storm in the area On review of available information it appears that there was a lightning strike in the vicinity. | Grassfire | 15/01/2018 11:03 | 1 | Medium: 1000 sq.m - 10 ha | 9032 | Agricultural |  | 20180116PWA_01 | Infrastructure (network-based) | -35.0681 | 143.3355 | 1 | Powercor | Report | 12013 | 0.028005 | 22kV AC | Swan Hill Aerodrome | 3597 | Piangil | Lightning
CEOT dispatched a fault crew to repair/make safe. CEOT also notified the local DAO to investigate the incident. Report from attending DAO: Arrived at site, took photos of the burnt area at both structures/pole at either end of the span that had failed and the area of grass that had been burnt and made notes on weather conditions. | 100 MCILWAINE STREET, MEENIYAN VIC 3956 | 2001927 |  |  |  | Corrosion |  | Phase to earth |  | IMS 232036. Conductor came down cnr Ross St. Grass fire observed at location. Report from the attending DAO: Attended site at the CNR of McIlwaine St, Ross St and Martians Rd Meeniyan. 1 phase on the south side phase of 3 phase HV conductors between poles 28001927 and 28010196 was on the ground across McIlwaine St and also in the paddock that runs parallel with Martins Rd. Conductor did not appear to have been frayed at either end of the break as per attached photos. Conductors was touching the ground in the area of a grass fire approximately 8 sq.metres in size with very minor damage to customer's property. | Conductor (bare) | 0 | 0 | 0 |  | lga14 | HV conductor on ground. Some signs of corrosion. | Grassfire | 15/01/2018 17:08 | 1 | Localised: less than 10 sq.m | 9033 | Agricultural |  | 20180116SPN_01 | Infrastructure (network-based) | -38.5868 | 146.0136 | 1 | AusNet Services Distribution | Report | 11515 | 0.0081539 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Meeniyan | Conductor
On arrival crew isolated supply and carried out repairs. | 400 BRISBANE RANGES ROAD, MOUNT WALLACE VIC 3342 | 31025054 |  |  |  | Leakage |  |  | 1 | Emergency Services informed a fallen transformer on fire. On arrival the crew found that a Pole Fire had occurred at the incident location. The top part of this swer pole burnt through and fell on to ground. There was no ground fire ,no injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | BMH003 | Excessive leakage current | Pole-top fire | 29/11/2017 8:49 | 1 | Negligible: no ground fire | 9041 | Roadway |  | 20180117PWA_03 | Infrastructure (network-based) | -37.7613 | 144.2488 | 1 | Powercor | Report | 10933 | 0.010953 | 12.7kV AC (SWER) | Avalon Airport | 3342 | Mount Wallace | Pole
The crew replaced the overheated connection. | 57 BUNGAREE-WALLACE ROAD, BUNGAREE VIC 3352 | 32000693 |  |  |  | Overheated connection |  |  |  | VicFire reported a fire start in proximity of a Powercor asset at the incident location. A crew attended but were unable to identify possible cause of fire start. CFA attended and extinguished ground fire of approx. 20m x 10m in area. A crew attended the following day and identified an overheated connection. There were no reported shocks, injuries or third party property damages. | Dropper/bridge | 2 | 2 | 2 |  | BAN011 | Overheated connection | Grassfire | 16/01/2018 21:26 | 1 | Small: 10 - 1000 sq.m | 9046 | Roadway |  | 20180118PWA_01 | Infrastructure (network-based) | -37.5556 | 143.973 | 1 | Powercor | Report | 10939 | 0.033172 | 22kV AC | Ballarat Aerodrome | 3352 | Bungaree | Connection
Voltage tests between an independent earth and various points on the pole, including the distribution cabling from the pit identified a voltage of 225 Volts on the load side of the Neutral Conductor at the Terminal Strip as well as the MEN earth conductor. The attending Powercor Fault Crew checked the condition of all conductors and disconnected the U/G Cable from the pit to make safe while the LEIW re-terminated the earthing system conductors in the correct manner and replaced the two Din Mounted Terminal Strips which had an MEN Link installed within the Street Light Pole Structure. | 23 FIREBRACE STREET, HORSHAM VIC 3400 | 35231949 |  |  |  | Earth fault | Unknown work practice factor | Phase to earth | 2 | The Electrical Contractor, Mr Joel Dymke was attempting to install a Din Mounted Fuse assembly within a Street Lighting Pole Structure terminal strip, when he inadvertently disconnected the MEN earth from the pole , the back of his hand came in contact with this earth cable and resulted in a mild electric shock. There was no fire or third party property damage. | Services cable | 2 | 2 | 2 |  | HSM010 | This condition caused current to flow through the ineffective link within the Din Rails Terminal Strips to the disconnected MEN conductor, resulting in the conductor being energised at 225 Volts to earth. | Minor shock | 21/11/2017 10:30 |  |  | 6828 | Public space |  | 20171207PWA_01 | Infrastructure (network-based) | -36.7129 | 142.1996 | 1 | Powercor | Report | 8605 | 0.00015394 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged electrical infrastructure was replaced under Access Authority conditions. | 60 NORTH ROAD, BRIGHTON VIC 3186 | 2304847 | Vehicle | [5 empty] | 1 | At 2326hrs on 02/03/2017, 11kV feeder NB 22 circuit breaker reclosed to lockout affecting 165 customers. A vehicle struck a HV intermediate CHP (LIS No. 2304847) located outside 60 North Road Brighton that caused a HV tie to break and the conductor to rest on the steel HV crossarm causing a pole fire to occur. The HV underground cable supplied "North-New" Indoor substation and sustained damage requiring repairs to be completed. | Conductor (bare);Insulator tie wires/connections | 0 | 0 | 0 |  | NB 22 | A vehicle struck a HV intermediate pole that resulted in a tie breaking and the HV conductor to fall onto the steel crossarm. | Pole-top fire | 42778.9764 | 1 | Negligible: no ground fire | 6841 | Residential |  | 20171211UTD_02 | Infrastructure (network-based) | -37.8987 | 144.995 | 1 | United Energy Distribution | Report | 8622 | 0.020149 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | NORCAL ROAD, NUNAWADING VIC 3131 | 7034951 |  | Lightning |  | HV injection |  |  | 1 | At 1647hrs on 07/12/2017, 22kV feeder NW 33 circuit breaker reclosed to lockout affecting 2351 customers. Following a storm that struck Melbourne at approximately 4.30PM on 07/12/2017, it appeared that lightning struck a HV/LV manual gas switch installed at pole No. LIS 7034951 located in Norcal Road resulting in HV conductors to come down on both sides of the switch. The transformer at Norcal- North Station" substation had badly burnt HV bushings and requires replacement. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from Norcal-North Station" substation. The LEI confirmed a high voltage injection occurred (BWD 1708) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. In addition, vehicles parked under the pole were damaged by debris when the lightning struck the United Energy overhead infrastructure. | Conductor (bare);Any other type | 0 | 0 | 0 |  | NW 33 | During storm activity, lightning struck UE overhead infrastructure. | HV injection;Loss of supply | 42928.6993 |  |  | 6847 | Residential |  | 20171212UTD_04 | Infrastructure (network-based) | -37.82 | 145.1812 | 1 | United Energy Distribution | Report | 8628 | 0.018388 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Lightning
The substation crew advised their supervisor of the breach and the unsafe activities completed by the REC. The crew updated the circuit breaker in the pillar following the organisations safe work methods and safely re-secured the LV pillar. | 37 LAKEWOOD BOULEVARD, CARRUM DOWNS VIC 3201 |  | Vandalism;Unauthorised access;Caused by REC/contractor | [5 empty] | 2 | The Downer meter and servicing supervisor had requested a substation crew to attend 37 Lakewood Boulevard to upgrade the circuit breaker in the pillar from 100amps to 160amps in preparation for a supply upgrade. Upon arrival, the Downer substation crew found the REC had broken into the live LV pillar to run the underground consumers mains cable inside the pillar. This is a breach of No Go Zone framework and the REC should not have broken into the live pillar without a spotter or attempting to have gone through the correct processes. The REC left the pillar unsecured and therefore any members of the general public could have accessed the live electrical infrastructure. The REC's details are listed in the 'other information' tab. | LV Pillar | 0 | 0 | 0 |  |  | Vandalism and unauthorised access into a live LV pillar by a REC. | No Go Zone (contact);Damage to network assets | 42778.375 |  |  | 6848 | Roadway |  | 20171213UTD_01 | Infrastructure (network-based) | -38.0925 | 145.1578 | 1 | United Energy Distribution | Report | 8629 | 0.034172 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Other
The faults crew replaced the copper earth cable and re-installed the timber cover guards at pole No. LIS 3308443. | 256 FRANKSTON-DANDENONG ROAD, SEAFORD VIC 3198 | 3308443 | Copper theft | [5 empty] | 2 | Caller advised the pole at the front of the property is unstable and a piece of wood has come away from the base of it and some wires are now exposed. A customer contacted the United Energy faults and emergencies call centre advising that copper cabling had been exposed at the base of the pole. The faults crew attended and found that approximately 2.5m of 0.1 copper cable had been stolen from the HV cable head pole outside 256 Frankston-Dandenong Road with the cable cut just above the wooden cover guard. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown persons have stolen a HV CHP copper earth cable. | Damage to network assets | 42959.5833 |  |  | 7849 | Roadway |  | 20171213UTD_03 | Infrastructure (network-based) | -38.1219 | 145.1432 | 1 | United Energy Distribution | Report | 9630 | 0.010491 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Other
On arrival crew isolated supply and commenced repairs | 394-422 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | 30197524 | Vehicle | [6 empty] | At a truck â€˜car parkâ€™. MFB advised a truck had brought down a pole with LV service cable at the incident location. Upon arrival the CitiPower crew found that the truck was reversing in the car park when it hit the pole, bringing it down. There were no injuries or fire. | Service conductor;Pole (wood) | 2 | 2 | 2 |  | WG012 | Vehicle struck pole | Loss of supply;Damage to network assets | 24/10/2017 22:34 |  |  | 7867 | Roadway |  | 20171214PWA_05 | Infrastructure (network-based) | -37.809 | 144.9345 | 1 | CitiPower | Report | 9654 | 0.010483 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Vehicle
The crew isolated the cable and it was replaced. The customer engaged an REC to make repairs to the building. | 34 LANGSTAFFE DRIVE, WENDOUREE VIC 3355 | 30001312 | Vehicle | [6 empty] | A customer rang to advise an truck had pulled down the service cable to their building. A crew attended and found an truck had struck and pulled down the service wire to 34 Langstaffe Dr. The cable was alive on the ground. There was no ground fire start. There were no reported shocks or injuries. | Service conductor | 2 | 2 | 2 |  | BAN003 | Truck struck service | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/10/2017 15:35 |  |  | 7869 | Roadway |  | 20171214PWA_07 | Infrastructure (network-based) | -37.5208 | 143.8306 | 1 | Powercor | Report | 9656 | 0.027606 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | Vehicle
Site made safe. Earths replaced. | 42 ZAKWELL COURT, COOLAROO VIC 3048 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Unknown person(s) accessed (unauthorsied) the zone substation at Coolaroo. They removed / stole copper earths from within the switchyard. | Disconnector/isolator;Earth;Zone substation | 0 | 0 | 0 |  |  | Unknown person(s) cut hole in security fence / gate and stole copper earths. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/12/2017 13:31 |  |  | 7880 | Industrial |  | 20171215JEM_03 | Infrastructure (network-based) | -37.6422 | 144.934 | 1 | Jemena | Report | 9669 | 0.035694 | Earthing cable | Essendon Airport | 3048 | Coolaroo | Other
The site was made safe. The Powercor crew insulated the bare ends of the LV cables in the LV pit. An electrical Defect Notice was issued to the site contractor/account holder. The residence was left off supply. | 1259-1283 LEAKES ROAD, ROCKBANK VIC 3335 | 30108640 | Copper theft | [6 empty] | Powercor was contacted by a site contractor at approx. 10:44am on Tuesday 7/11/17 indicating no LV supply. Upon attendance, the Powercor crew noted damage to an external customer metering cabinet at an un-occupied residence at 1259 Leakes Road, Rockbank The former property is in the process of redevelopment into a housing estate. The customer metering cabinet was also acting as a Temporary Builders Supply to a developer construction compound on the site. The Powercor crew noted that: - the Powercor Electricity meter and Customerâ€™s metering panel were not present at the site. - The 3 core, 16mm2 LV service cable/customer mains interface in an LV underground service pit at the Leakes Rd frontage of the property had been cut. - The consumer LV mains between the LV pit and the Customerâ€™s metering panel appeared to have been forcefully withdrawn from its conduit and was not present. - the remnant, LV cable tails present in the LV pit were still alive and un-capped. There was no fire or reported injuries. | Services cable;Services pit;Customer installation | 2 | 2 | 2 |  | MLN021 | Copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42927.4472 |  |  | 7874 |  |  | 20171215PWA_04 | Infrastructure (network-based) | -37.7344 | 144.6524 | 1 | Powercor | Report | 9661 | 0.0060475 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew confirmed site safe - no damage to assets | GEODETIC ROAD N, CARAG CARAG VIC 3623 | 30255374 |  | Bird |  |  |  |  | 1 | Crew attended to find small ground fire had been extinguished by local farmer on road verge area burnt 150metres by 6metres. Starling birds had caused a flashover on the concrete pole steel crossarm ACR structure, starting a small grass fire. No property damage, No injuries, No reported shocks. | ACR/OCR | 2 | 2 | 2 |  | SHP021 | Bird Incident | Grassfire | 14/12/2017 17:38 | 1 | Small: 10 - 1000 sq.m | 7878 | Roadway |  | 20171215PWA_06 | Infrastructure (network-based) | -36.5448 | 144.9319 | 1 | Powercor | Report | 9667 | 0.011575 | 22kV AC | Mangalore Airport | 3623 | Carag Carag | Animal
The site was made safe and the LV service was removed. The house was left off supply and a defect notice issued, until an REC can attend to fix the customer side damage. | 54 ROADKNIGHT STREET, BIRREGURRA VIC 3242 | 30055649 | Vehicle | [6 empty] | A nearby customer reported a vehicle hit and bought down powerlines at the incident location. On arrival the crew found that a Low Voltage service had been hit by a truck, resulting in it coming to ground. Damage to the customers POA and mains was reported by the linesmen. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | CLC007 | Unknown vehicle struck service line | Loss of supply | 26/10/2017 18:24 |  |  | 7894 | Residential |  | 20171218PWA_07 | Infrastructure (network-based) | -38.3349 | 143.7839 | 1 | Powercor | Report | 9690 | 0.013435 | Low voltage AC (<1kV) | Avalon Airport | 3242 | Birregurra | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Service Conductor at the Flat Clamp termination located at the Service Pole. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 211 THIRTEENTH STREET, MILDURA VIC 3500 | 33061046 |  |  |  | Corrosion |  | Phase to earth |  | Mr Ashley Yates was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | MDA032 | Corroded O/H Neutral Service Conductor at the Flat Clamp termination located at the Service Pole. | Minor shock | 43018.375 |  |  | 7899 | Residential |  | 20171218PWA_09 | Infrastructure (network-based) | -34.1865 | 142.1463 | 1 | Powercor | Report | 9737 | 0.025751 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | OH Cable
On arrival crew made site safe and issue a defect for customer to carry out repairs | 40 DUNNS ROAD, WERRIBEE SOUTH VIC 3030 | 32172110 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer advised a tractor has pulled down a wire at the incident location. Upon arrival the Powercor crew found that the service and fuse box had been damaged and the wire lying on the ground. There were no injuries or fire. | Service conductor | 2 | 2 | 2 |  | WBE034 | Believed tractor struck service No vehicle found onsite | Loss of supply;Damage to network assets | 26/10/2017 15:21 |  |  | 7900 |  |  | 20171218PWA_10 | Infrastructure (network-based) | -37.93 | 144.7204 | 1 | Powercor | Report | 9696 | 0.011595 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Vehicle
A faults crew promptly attended and the LV krone box was replaced along with a length of 3 phase cable up to the overhead reticulation. Supply was restored after a 315amp fuse was replaced at "Fourth-Station" substation that had operated due to the fault. The LEI was in attendance and tested the affected properties. | 186 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | 3302395 |  |  |  | Overheated connection |  |  | 1 | The fire authority advised of a pole fire in Nepean Highway near Park Lane. Refer also to OSIRIS report 20171218UTD_02 for an electric shock received due to this fault. During extremely warm conditions, a krone box installed on pole No. LIS 3302395 caught fire opposite 186 Nepean Highway. The cause was attributed to a probable loose connection that possibly overheated. In addition, the location is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. No photos were taken at the time of the event. | Conductor (ABC);Services cable;Connector/termination | 0 | 0 | 0 |  |  | The cause was attributed to a probable loose connection that possibly overheated. In addition, the location is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. | Pole-top fire;Loss of supply | 13/12/2017 17:55 | 1 | Negligible: no ground fire | 7897 | Residential |  | 20171218UTD_04 | Infrastructure (network-based) | -38.0312 | 145.1039 | 1 | United Energy Distribution | Report | 12966 | 0.007691 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | Connection
The crew made the site safe and reported that repair work will be organized for the next day as additional resources and equipment is required. | 37 ALBEMARLE STREET, WILLIAMSTOWN NORTH VIC 3016 | 30111818 | Copper theft | [6 empty] | The property owner â€˜Joâ€™ called to report that a cable has been taken from across the road, the galvanised cover panel had been taken off the pole and the cable had been stolen. Upon arrival the fault crew found that the cover guard at pole LIS-2665, protecting the recently installed underground service had been removed and the underground service cable had been stolen (approx. route length 32m). The installation was not in service and was awaiting the customer connection request. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Services cable | 2 | 2 | 2 |  | BLT022 | Copper theft | Damage to network assets | 31/10/2017 17:02 |  |  | 7911 |  |  | 20171219PWA_04 | Infrastructure (network-based) | -37.8508 | 144.8624 | 1 | Powercor | Report | 9717 | 0.022029 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown North | Other
The faults crew repaired the severed cable and supply was restored. | 651-669 LONSDALE STREET, MELBOURNE VIC 3000 | 30185006 | Working too close to underground cables | [6 empty] | A contractor reported that they have damaged an underground cable at the incident location. On arrival the fault crew found that a low voltage underground cable had been severed by an excavator doing preparation work for a shaft excavation at the incident location. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | JA018 | Excavating too close to cable. DBYD/MOCS (Sequence #) 65818970. Excavator driver knew the cable was in the area but failed to ensure cable was not damaged. Destructive equipment used, excavator. | Loss of supply;No Go Zone (contact) | 43019.2083 |  |  | 7931 | Roadway |  | 20171220PWA_05 | Infrastructure (network-based) | -37.8151 | 144.9525 | 1 | CitiPower | Report | 9742 | 0.016253 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew isolated supply and commenced repairs. | 170 BOUNDARY ROAD, SHEPPARTON EAST VIC 3631 | 33088169 |  | Blown branch/vegetation |  |  |  |  | 1 | Following numerous customer calls during and extensive storm front ( Lightning, rain and high winds) a crew attended to find a conductor on the ground at the incident location. There was no evidence of a ground fire, no injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | STN024 | Extensive storm front, high winds and rain | Loss of supply;Damage to network assets | 19/12/2017 19:09 |  |  | 7938 | Roadway |  | 20171221PWA_02 | Infrastructure (network-based) | -36.3911 | 145.4981 | 1 | Powercor | Report | 9754 | 0.0040498 | 22kV AC | Shepparton Airport | 3631 | Shepparton East | Lightning
CEOT dispatched a fault crew to make safe and carry out any necessary repairs to the network. The crew isolated supply and made safe. CEOT also requested an AusNet Services' LEI to attend to investigate and check for property damage. LEI attended site and checked all properties on LV circuit. House isolated at FOLCB. LV circuit energised by Electrix. NST test performed. Crews reinstated fallen overhead conductors and replaced damaged metering. Supply restored. | 11 GRETA ROAD, WANGARATTA VIC 3677 | 5103007 |  | Wind |  |  |  | Phase to phase | 1 | IMS 231791. Initial report: Under incd-34955-s possible HVI ex LV of "GRETA BOWSER" S/S. Final report: During a storm event a tree fell into overhead HV and LV conductors causing a HVI. Conductors were on the ground. Feeder CB operated. Some damage sustained to metering and there were tripped circuit breaker switches at customers' premises. No other reported damage to customers' installations. | Pole mounted | 0 | 0 | 0 |  | wn1 | Vegetation: Trees Incident | HV injection | 20/12/2017 19:59 |  |  | 7935 | Residential |  | 20171221SPN_01 | Infrastructure (network-based) | -36.3629 | 146.3157 | 1 | AusNet Services Distribution | Report | 9749 | 0.018456 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3677 | Wangaratta | Trees
The faults crew removed the single phase overhead service for safety but meter numbers 1269243 and 1250691 were left on site. | 102 RAE AVENUE, EDITHVALE VIC 3196 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Caller reporting there is a shed and the power line going to the shed is arcing but no fire is evident. Caller says the house is demolished but for some reason the wire has not been removed. Business name is P L P Contracting P/L. A house was being demolished and it appeared the excavator undertaking this work has deliberately struck the POA to cause a fault to avoid the costs for an abolishment and to expedite the removal of the overhead supply. No abolishment request had been received by United Energy. | Service conductor | 0 | 0 | 0 |  |  | House was being demolished and no request for the removal of electricity assets had been received by United Energy. | No Go Zone (contact) | 20/12/2017 12:15 |  |  | 7934 | Residential |  | 20171221UTD_01 | Infrastructure (network-based) | -38.0331 | 145.1163 | 1 | United Energy Distribution | Report | 9747 | 0.023766 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Edithvale | Other
On arrival crew inspected structure for damage | RIPPLE VALE, 4100 CAPE OTWAY ROAD, BIRREGURRA VIC 3242 | 32062882 |  | Blown branch/vegetation |  |  |  |  | 1 | Customer reported a whirly wind had blown straw onto power lines at the incident location. On arrival the crew found that the straw had caused a flash over which in turn started a ground fire at the base of Ingleby P12 (LIS-7534) (approx. 16m2 in total). The fire self-extinguished due to the moist ground. A successful reclose occurred on the upstream ACR (@1703hrs). No injuries, no third party damage reported. | Conductor (bare) | 2 | 2 | 2 |  | WIN011 | Wind blown straw in extreme winds | Grassfire | 21/12/2017 19:10 | 1 | Small: 10 - 1000 sq.m | 7946 | Roadway |  | 20171222PWA_03 | Infrastructure (network-based) | -38.3385 | 143.8244 | 1 | Powercor | Report | 9767 | 0.034049 | 22kV AC | Avalon Airport | 3242 | Birregurra | Other
Crew attended, branch had cleared on arrival, Supply restored | 1229 CALDER HIGHWAY, MARONG VIC 3515 | 30147098 |  | Blown branch/vegetation |  |  |  |  | 1 | VicFire Reported a grass fire near the intersection of Allies st Marong. Attending crew found branch had contacted HV and high voltage fuses had operated | Dropper/bridge | 0 | 0 | 0 |  | BET001 | airborne vegetation | Grassfire | 22/12/2017 16:12 | 1 | Localised: less than 10 sq.m | 7961 | Roadway |  | 20180102PWA_02 | Infrastructure (network-based) | -36.7383 | 144.1552 | 1 | Powercor | Report | 11289 | 0.0042419 | 22kV AC | Bendigo Airport | 3515 | Marong | Trees
Crew attended and closely inspected assets | 85 GIBBS STREET, MILDURA VIC 3500 | 33064015 |  | Bird |  |  |  |  | 1 | Powercor crew were patrolling line after reclose and found small fire in the vicinity of the line. | Conductor (bare) | 0 | 0 | 0 |  | MBN012 | Bird Incident | Grassfire | 26/12/2017 13:36 | 1 | Small: 10 - 1000 sq.m | 7963 | Roadway |  | 20180102PWA_04 | Infrastructure (network-based) | -34.1901 | 142.0963 | 1 | Powercor | Report | 9792 | 0.017075 | 22kV AC;66kV AC | Mildura Airport | 3500 | Mildura | Animal
Fault Crew attended fire at base of pole , EDO type fuse replaced. | 235 GRAVEL PIT ROAD, WANGARATTA SOUTH VIC 3678 | 5121021 |  |  |  | Candled fuse |  |  | 2 | IMS 231819 - EDO fuse candled. Grass fire observed at the pole base. | EDO fuse | 0 | 0 | 0 |  | WN4 | EDO fuse candling | Grassfire | 26/12/2017 14:30 | 1 | Small: 10 - 1000 sq.m | 7954 | Agricultural |  | 20180102SPN_01 | Infrastructure (network-based) | -36.3822 | 146.2583 | 1 | AusNet Services Distribution | Report | 9778 | 0.010432 | 22kV AC | Wangaratta Aero | 3678 | Wangaratta South | Fuse
Fault crew dispatched to make safe and invetigation A grass fire (3x8m) has occurred at the base of Pole. A dead / charred bird is lying at the edge of the burnt area. There is burn marks visible on the centre phase bridging insulator and cover. See attached photos of the scene / damage. | 675 TRARALGON-MAFFRA ROAD, GLENGARRY VIC 3854 | 2601158 |  | Bird |  |  |  |  | 1 | IMS 231820 - Reported sparking and grass fire in area . Fire was extinguished by CFA | Dropper/bridge | 0 | 0 | 0 |  | TGN31 | Bird Incident | Grassfire | 27/12/2017 11:35 | 1 | Small: 10 - 1000 sq.m | 7955 | Agricultural |  | 20180102SPN_02 | Infrastructure (network-based) | -38.134 | 146.5579 | 1 | AusNet Services Distribution | Report | 9779 | 0.01789 | 22kV AC | Morwell (Latrobe Valley Airport) | 3854 | Glengarry | Animal
Crew attended and replaced pole | 600 GRUBB ROAD, WALLINGTON VIC 3222 | 30069061 | Vehicle | [5 empty] | 1 | Powercor received notification from the Police and members of the public advising of a vehicle accident in Grubb Rd, Wallington. Near the Portarlington Rd intersection Powercor crew arrived on site and found a vehicle engulfed in flames and Pole down on the ground. Nearby roadside vegetation had also ignited (30x4m) | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | DDL011 | Motor vehicle impact | Significant disruption to the community;Vehicle | 43132.2924 | 0 | Small: 10 - 1000 sq.m | 7969 | Roadway |  | 20180103PWA_01 | Infrastructure (network-based) | -38.2002 | 144.5468 | 1 | Powercor | Report | 9809 | 0.0048866 | 22kV AC | Avalon Airport | 3222 | Wallington | Vehicle
On arrival crew inspected site for damage 2 spans of conductor subsequently replaced | 36 WALLACES LANE, GLENORMISTON SOUTH VIC 3265 | 30049396 |  | Wind |  | Conductor clashing |  |  | 1 | A ground fire occurred at the incident location. A the fire area was indicated to be 31Ha and one unoccupied house was destroyed. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG001 | conductor clashing | Grassfire | 43252.6215 | 1 | Large: more than 10 ha | 7979 | Agricultural |  | 20180108PWA_01 | Infrastructure (network-based) | -38.1736 | 142.9659 | 1 | Powercor | Report | 9826 | 0.038385 | 22kV AC | Warrnambool Airport Ndb | 3265 | Glenormiston South | Conductor
A faults crew attended and replaced the defective single phase neutral screened service with a XLPE type. Supply was restored upon the completion of installation tests. | 3 UNION GROVE, SPRINGVALE VIC 3171 | 613560 |  |  |  | Electrical breakdown |  |  | 2 | Caller reports a wire down and is touchable. The wire has detached from the house after an explosion and caught fire that caused charring of the front lawn. During hot warm conditions, a single phase neutral screened service failed at the roller clamp and fell to the ground. Molten metal from the service caused a small 2sqm grass fire on the front lawn that self extinguished. | Service conductor | 0 | 0 | 0 |  |  | The single phase neutral screened service failed at the roller clamp. | Grassfire | 43221.7035 | 1 | Localised: less than 10 sq.m | 7974 | Residential |  | 20180108UTD_01 | Infrastructure (customer connection) | -37.9527 | 145.1535 | 1 | United Energy Distribution | Report | 12973 | 0.0020208 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Connection
The Jemena electrical network operator assessed the situation and made the site safe, then contacted the Jemena control room to dispatch JEN fault crew to make repairs to the line. | 31 SUNSHINE ROAD, WEST FOOTSCRAY VIC 3012 |  |  |  |  | Mechanical overload | Poor or no communication | Three phase | 1 | On Wednesday 25 October 2017 at approximately 06.09am, FW 16 circuit breaker had experienced reclose and open to lockout at Footscray West substation. On further investigation initiated by Jemena control room, a Network Operator was dispatched to patrol 22kV FW FDR 16 line to identify any cause that may have affected the line. While the electrical network operator was patrolling the line, he identified centre phase HV conductor at the temporary mid-span isolators had fallen to ground on the north side of Sunshine road, between pole numbers A052684 and A052685. | Conductor (bare);Disconnector/isolator | 0 | 0 | 0 |  | FW16 | Upon closer examination, the electrical network operator identified that the northern side of the 22kV FW FDR 16 line had burn off marks on the load side of the mid-span isolators. The failure of the mid-span isolator connection caused the conductor to make ground contact. History of mid-span isolators (MSI's): 1.On Saturday 06th June, 2015, Glove and Barrier 4 crew had been planned to execute switching Application 64178 (copy attached in Notes and Findings section), which requires a set of MSIâ€™s to be installed on the northside of Sunshine Rd West Footscray, between pole number A052684 and A052685. The MSIâ€™s had been installed for plan outage that had been scheduled for Sunday 07th June 2015, to isolate 22KV FDR FW16 for the commissioning of Sunshine-Meadow Lea Substation. 2. On Sunday 13th September 2015, MSIâ€™s northside of Sunshine Rd West Footscray, between pole number A052684 and A052685, have to be utilised to isolate Sunshine-Meadow Lea Substation as per switching application 65226 (copy attached in Notes and Findings section) for the purpose of No Go Zone permit that required to be issued to third party building contractors to re-caulk Sunshine-Meadow Lea Substation Internal walls with full supervision of JEN operator. 3. On 20th January, 17th February and 17th March 2016, JEN Control Room had identified on their Asset Performance spreadsheet under Section Abnormal tab that the MSIâ€™s northside of Sunshine Rd West Footscray, between pole number A052684 and A052685 had been in service over 3 months. Control and Dispatch Team Leader had notified Live Line Team Leader of the outstanding date which the MSIâ€™s had been installed and no longer are required which they need to be removed from the network and the conductors to be re-instated. Live Line team leader had responded to with no knowledge of the ownership and which group was the initial installer of the MSIâ€™s. 4. On Wednesday, 25th October 2017 at approximately 06.09am, FW 16 Circuit Breaker (CB) had experience reclose and Open to Lockout at Footscray West Zone substation. Findings: 1. Glove and Barrier 4 crew and High Voltage No Go Zone team, had failed to identify the status, ownership and maintenance of the MSIâ€™s of the use for their two separate jobs. 2. All parties had failed to comply with Jemena Live Line Manual, Document No.: ELE MA 0005 Version: 2, Section 18. MSI Maintenance and Installation. Corrective actions: Work Practices to establish process and reinforce the Live Line Manual, Document No.: ELE MA 0005 Version: 2, Section 18. MSI Maintenance and Installation with the all internal and external stakeholders. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/10/2017 6:09 |  |  | 7984 | Commercial |  | 20180109JEM_01 | Infrastructure (network-based) | -37.8009 | 144.8728 | 1 | Jemena | Report | 10849 | 0.041605 | 22kV AC | Essendon Airport | 3012 | West Footscray | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a broken (Open Circuit) O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA, The attending Powercor Fault Crew reterminated the broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 6 ARUNGA AVENUE, NORLANE VIC 3214 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Pratik Lohiya was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Taps and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Broken neutral at POA | Minor shock | 13/11/2017 8:00 |  |  | 8984 | Residential |  | 20180109PWA_02 | Infrastructure (network-based) | -38.0966 | 144.3542 | 1 | Powercor | Report | 10833 | 0.00027778 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | OH Cable
The site was made safe and the SWER pole was replaced. | 587 MCNICOLS ROAD, TOWANINNY SOUTH VIC 3527 | 30378334 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Rifa Salutary reported one of their vehicles hit and bought down a pole at the incident location. On arrival the crew found that a SWER pole had been bought to ground by a telehandler. There were no reported injuries or other third part damage. There was no fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | CTN003 | Tractor struck pole | Loss of supply;Damage to network assets | 43019.4472 |  |  | 8989 | Agricultural |  | 20180109PWA_04 | Infrastructure (network-based) | -35.9149 | 143.3501 | 1 | Powercor | Report | 10840 | 0.010287 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3527 | Towaninny South | Vehicle
The padlock was replaced and the yard adjacent to the zone substation safely secured. The lock outer cover guard has also been removed and will be replaced at the earliest opportunity. | GILBY ROAD, MOUNT WAVERLEY VIC 3149 |  | Vandalism;Theft;Unauthorised access | [5 empty] | 2 | A First Responder attended NO (Notting Hill) Zone substation and identified an attempted unauthorised entry had been made into the adjacent storage area. The padlock at the yard adjacent to the NO Zone Substation located in an industrial area on the corner of Gilby and Lionel Roads had almost been cut through by unknown persons. They had obtained access by unknown means into the yard that contained two containers of materials and tools and were trying to get out in a probable attempted theft of materials and/or copper. | Zone substation | 0 | 0 | 0 |  |  | Probable attempted theft of materials and/or copper. | Damage to network assets | 43344.3333 |  |  | 8986 | Industrial |  | 20180109UTD_02 | Infrastructure (network-based) | -37.8972 | 145.137 | 1 | United Energy Distribution | Report | 10836 | 0.0035012 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Other
The crew made safe/trimmed trees and restored supply | 358 RESTDOWN ROAD, ROCHESTER VIC 3561 | 32184954 |  | Within clearances | [5 empty] | CFA reported a small grass fire at the incident location. On arrival the crew found at mid span from LIS 17037 trees making contact to HV resulting in a grass fire of approx. 100m x 100m, with damage to fencing & machinery. . There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | SHP012 | Vegetation contact with HV | Grassfire | 43252.8097 | 1 | Medium: 1000 sq.m - 10 ha | 8995 | Roadway |  | 20180110PWA_02 | Infrastructure (network-based) | -36.3384 | 144.6735 | 1 | Powercor | Report | 10848 | 0.0021065 | 22kV AC | Bendigo Airport | 3561 | Rochester | Trees
Fire extinguished Pole replaced, supply restored | BOLTON-KOOLOONONG ROAD, BOLTON VIC 3546 | 32149634 |  | Lightning |  |  |  |  | 1 | Customer reported outage. Crew attended and found SWER pole had been struck by lightning and had burnt through at the base, falling to ground. There was a resulting ground fire start around the base of the pole of approx. 6mx6m. There were no reported shocks or injuries. | Pole (wood) | 2 | 2 | 2 |  | BBD014 | Lightning strike on pole | Grassfire | 43313.9444 | 1 | Localised: less than 10 sq.m | 8999 | Agricultural |  | 20180110PWA_04 | Infrastructure (network-based) | -34.8861 | 143.1272 | 1 | Powercor | Report | 10856 | 0.021464 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3546 | Bolton | Lightning
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The crew replaced the damaged overhead neutral screen service cable with a new XLPE type service cable. The customer's REC/Electrician replaced the FMB at the POA at the same time due to damage. All tests and checks were conducted and passed after the above items were completed. | 67 BEACH PARADE, SANDY POINT VIC 3959 | 2023367 |  | Animal |  |  |  | Phase to earth | 2 | IMS 231437. Customer received tingles from a tap. A possum caused damage to the overhead neutral screen service cable. | Service conductor | 0 | 0 | 0 |  | ftr21 | Animal Incident | Minor shock | 27/11/2017 15:25 |  |  | 9009 | Residential |  | 20180111SPN_05 | Infrastructure (network-based) | -38.828 | 146.1203 | 1 | AusNet Services Distribution | Report | 10876 | 0.010457 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3959 | Sandy Point | Animal
CEOT dispatched a fault crew to make safe and carry out necessary repairs. Crew isolated, made safe and replaced EDO fuse tube and link. ZA 90 day Notification is raised in SAP to replace both hung-up EDO's with BA fuse units as per policy 64-2009. | 20 BUTTERWORTHS ROAD, STONY CREEK VIC 3957 | 2013243 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 231444.1x 6A EDO fuse hung-up and candled @ lis #2013243, no ground fire, ncf. | EDO fuse | 0 | 0 | 0 |  | LGA13 | EDO fuse tube candled. | Other electricity related | 28/11/2017 6:31 | 1 | Negligible: no ground fire | 9011 | Agricultural |  | 20180111SPN_06 | Infrastructure (network-based) | -38.5513 | 146.1263 | 1 | AusNet Services Distribution | Report | 12847 | 0.026907 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3957 | Stony Creek | Fuse
On arrival crew isolated supply and carried out repairs. | 24 VISTA DRIVE, MELTON VIC 3337 | 32178447 |  | Wind | [5 empty] | Report received from residents that a tent/gazebo had blown onto the wires outside their property, causing sparks. Upon arrival the fault crew found that a lightweight portable gazebo had in fact been swept up by the wind and blown into the open wire LV conductors. This caused the sparking and shorting between circuits which was reported by the residents, and eventually led to the red phase and neutral conductor to break mid span and come to ground, causing a small grass fire of (3m2) in the nature strip in front of 24 Vista Drive. The MFB were also in attendance and the small grass fire was extinguished. There was no reported third party property damage. No shock or injuries to report. | Conductor (bare) | 2 | 2 | 2 |  | MLN022 | Gazebo blown into line | Loss of supply;Grassfire | 43405.6937 | 1 | Localised: less than 10 sq.m | 9018 | Roadway |  | 20180112PWA_03 | Infrastructure (network-based) | -37.682 | 144.5755 | 1 | Powercor | Report | 10903 | 0.025584 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Other
A faults truck attended and replaced the white phase 10amp HV EDO fuse and tube that had been candling. The fuse was replaced and supply restored to approximately 12 customers. | 69 CARRATHOOL AVENUE, ROSEBUD VIC 3939 | 1311457 |  | Humidity |  | Fatigue |  |  | 2 | Per CFA - junction box on fire in Duells Road near the corner of Carathool Avenue. A HV fuse candled at the HV spur fusing (RB 0157) in Carathhool Ave , Rosebud following a report from the CFA. | EDO fuse | 0 | 0 | 0 |  | RBD 12 | A HV fuse candled. | Pole-top fire | 43435.1653 | 1 | Negligible: no ground fire | 9019 | Residential |  | 20180112UTD_04 | Infrastructure (network-based) | -38.3869 | 144.9313 | 1 | United Energy Distribution | Report | 12976 | 0.015333 | 22kV AC | Moorabbin Airport | 3939 | Rosebud | Fuse
Substation isolated and site made safe. Oil spill cleaned up. Jemena Works Practices and HSE teams advised of incident. | 1-19 GRAINGERS ROAD, WEST FOOTSCRAY VIC 3012 |  | Copper theft | [5 empty] | 2 | Copper theft at Grainger Colours & Chemical substation On attendance HV Switch #10538 was closed, HV droppers and transformer bushings must have been cut live Photos have been attached in Notes & Findings section. | Copper;Transformer | 0 | 1 | 0 |  | FW08 | Copper theft | Damage to network assets | 15/01/2018 15:00 |  |  | 9031 | Industrial |  | 20180115JEM_01 | Infrastructure (network-based) | -37.8027 | 144.8807 | 1 | Jemena | Report | 10912 | 0.029076 | 22kV AC | Essendon Airport | 3012 | West Footscray | Other
On arrival crew carried out repairs. | 1020 LILFORD ROAD, GILLIESTON VIC 3616 | 30128571 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and rest on the cross arm. CFA extinguished the cross-arm fire, a controlled interruption on SHTS-KYM #1 was required. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | SHTS KYM 1 | Excessive leakage current | Pole-top fire | 43435.9125 | 1 | Negligible: no ground fire | 9025 | Roadway |  | 20180115PWA_03 | Infrastructure (network-based) | -36.3431 | 145.1995 | 1 | Powercor | Report | 10898 | 0.008588 | 66kV AC | Shepparton Airport | 3616 | Gillieston | Crossarm
CEOT dispatched a fault crew to isolate, make safe and to carry out necessary repairs. CEOT also notified the local Duty Availability Officer (DAO) to investigate the incident. Necessary repairs made. | 105 KNIGHTS ROAD, LONGWARRY VIC 3816 | 2716128 |  |  |  | Overheated connection |  |  | 2 | IMS 231507. CFA called CEOT there was smoke and flames from a pole in a paddock. No fire on the ground. A pole junction box was burnt out on the pole. No other damage occurred. | Connection box | 0 | 0 | 0 |  | wgl12 | Cause not identified but most likely due to high impedance fault. | Other electricity related | 42778.8187 | 1 | Negligible: no ground fire | 9037 | Agricultural |  | 20180116SPN_02 | Infrastructure (network-based) | -38.1334 | 145.7372 | 1 | AusNet Services Distribution | Report | 10925 | 0.028439 | Low voltage AC (<1kV) | Moorabbin Airport | 3816 | Longwarry | Connection
On arrival crew isolated supply and carried out repairs | 1580 TATURA-UNDERA ROAD, UNDERA VIC 3629 | 33096503 |  | Fallen | [5 empty] | CFA reported a grass fire caused by tree over powerlines at the incident location. On arrival the crew found that tree branch approximately 15M in length from outside the clearance space had failed and fallen over one phase of a 3 phase spur line. The conductor struck the fence igniting 2 ground fires 300 metres apart (140x 10 & 70 x 10 mtrs) . The conductor remained suspended in free air still alive. There were no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | KYM003 | Vegetation: Trees Incident | Grassfire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/01/2018 16:52 | 1 | Medium: 1000 sq.m - 10 ha | 9040 | Agricultural |  | 20180117PWA_02 | Infrastructure (network-based) | -36.2978 | 145.2231 | 1 | Powercor | Report | 10932 | 0.0097685 | 22kV AC | Shepparton Airport | 3629 | Undera | Trees
On arrival crew isolated supply and carried out repairs. | 8 TORITTA WAY, TRUGANINA VIC 3029 | 30239859 | Vehicle | [5 empty] | 1 | A customer advised a pillar box has been hit by a car at the incident location. The customer also reported the box on fire, which was extinguished by persons unknown. Upon arrival, the Powercor crew found that the UG pillar had been run over by a vehicle causing a small fire. There were no injuries or third party property damage | LV Pillar | 2 | 2 | 2 |  | LV002 | Vehicle struck pillar | Plant/equipment | 17/01/2018 9:38 | 1 | Negligible: no ground fire | 9044 | Roadway |  | 20180117PWA_04 | Infrastructure (network-based) | -37.8467 | 144.7245 | 1 | Powercor | Report | 10936 | 0.027334 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Vehicle
CEOT dispatched a fault crew to isolate, make safe, investigate and arrange for a replacement street light. The street light was isolated by faults crew. The street light lantern was replaced. | 7 UNION ROAD, WANDIN NORTH VIC 3139 | 1002142 |  |  |  | Electrical breakdown |  |  | 2 | IMS 231520. Street light fire per CFA. A 400 Watt Mercury Vapour streetlight had burnt out and the control box had blackened. No fire on the ground. | Public lighting | 0 | 0 | 0 |  | ldl23 | Burnt out street light fitting. The damage was contained within the light head. | Other electricity related | 42837.4826 | 1 | Negligible: no ground fire | 9042 | Residential |  | 20180117SPN_01 | Infrastructure (network-based) | -37.7813 | 145.428 | 1 | AusNet Services Distribution | Report | 10934 | 0.0021273 | Low voltage AC (<1kV) | Moorabbin Airport | 3139 | Wandin North | AF Other
Crew attended no operations on the network no loss of supply Reported to Vegetation Manager who arranged for the trees in all three spans to be cut. | MYWEE ROAD, STRATHMERTON VIC 3641 | 30124251 |  | Within clearances | [5 empty] | Customer Chris Scott at 50 Mywee Road Strathmerton call that trees were in contact with HV and had started a grass fire in Roadside Vegetation Plantation. Approximately 110 metres by 22 metres and another small 10 metres by 10 metres grass fire in road verge and into customers property. Property damage was some fencing and irrigation pipes. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | NKA003 | Vegetation in clearance space | Grassfire | 20/01/2018 17:43 | 1 | Medium: 1000 sq.m - 10 ha | 9065 | Roadway |  | 20180122PWA_04 | Infrastructure (network-based) | -35.9252 | 145.4945 | 1 | Powercor | Report | 10975 | 0.0099803 | 22kV AC | Shepparton Airport | 3641 | Strathmerton | Trees
On arrival crew isolated supply and arranged repairs to underground cable. | 120 SUGARLOAF ROAD, AXEDALE VIC 3551 | 30266277 |  |  |  | Unknown technical factor |  |  | 1 | HV Underground cable failed above ground on concrete termination pole and caught on fire. There was a small ground fire. There was no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BET005 | No cause identified to date | Pole-top fire;Grassfire | 19/01/2018 20:04 | 1 | Localised: less than 10 sq.m | 9071 | Agricultural |  | 20180122PWA_06 | Infrastructure (network-based) | -36.7724 | 144.4958 | 1 | Powercor | Report | 10982 | 0.0094271 | 22kV AC | Bendigo Airport | 3551 | Axedale | UG Cable
CEOT dispatched a fault crew to make safe, investigate and arrange for repairs. The fire was extinguished when the fault crew arrived and made safe. A construction crew replaced the LV fused isolator. Supply was restored. CEOT also notified the local DAO to investigate. | 1 PLEASANT VIEW COURT, DIAMOND CREEK VIC 3089 | 924181 |  |  |  | Overheated connection |  |  | 0 | IMS 232087. Initial report: Burnt out Blue phase isolator on LIS 924181. Fire size 8 sq. metres. Final report: CFA reported a small 8 sq. metre ground fire which had been extinguished. The attending fault crew found the Blue phase low voltage fuse isolator had been burnt out which would have caused the fire. The LV connection was hot. LV fuse did not operate. | Disconnector/isolator | 0 | 0 | 0 |  | ELM32 | Hot connections at crossarm mounted LV fuse isolator. | Loss of supply;Grassfire | 19/01/2018 18:37 | 1 | Localised: less than 10 sq.m | 9069 | Residential |  | 20180122SPN_02 | Infrastructure (network-based) | -37.6787 | 145.1446 | 1 | AusNet Services Distribution | Report | 12853 | 0.038245 | Low voltage AC (<1kV) | Essendon Airport | 3089 | Diamond Creek | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 1177 NORTH ROAD, OAKLEIGH VIC 3166 | 2326221 |  |  |  | Electrical breakdown |  |  | 1 | At 0025hrs on 18/01/2018, 11kV feeder OE 04 circuit breaker reclosed to lockout affecting 2663 customers. A faults crew patrolled the feeder and identified the centre phase 11kV HV conductor on the ground in North Road at the corner of Abbeygate Street between pole No. LIS 2324790 and 2324791. The cause was a copper to aluminium ampact connection failure at pole number LIS 2324790 with secondary damage as a result of fault current at switch OA 0028 where a PG clamp connection failed on the centre phase at the south side of the switch and finally, the road side HV connection failed on the load side of switch OA2970 at pole No. LIS 2326221 where the ampact connection failed. There was evidence of splash marks on the LV conductors in North Road near Abbeygate Street and a LEI was dispatched to investigate any possible high voltage injection. The LEI checked properties in the area and no damage was identified. There was also scorch marks on the nature strip caused by molten metal falling into the dry grass below at the time of the fault. | Connector/termination | 0 | 0 | 0 |  | OE 04 | A failed HV ampact connection was the initial cause. | Grassfire | 18/01/2018 0:26 | 1 | Localised: less than 10 sq.m | 9066 | Roadway |  | 20180122UTD_02 | Infrastructure (network-based) | -37.9101 | 145.0919 | 1 | United Energy Distribution | Report | 12977 | 0.032394 | 11kV AC | Moorabbin Airport | 3166 | Oakleigh | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Fused Overhead Mains Connection Box at the Customerâ€™s Point of Attachment, The attending Powercor (Downer LSA) Fault Crew reterminated the existing O/H Service Cable at the Fused Overhead Mains Connection Box and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 82 EDGAR STREET, HEYWOOD VIC 3304 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Craig Searle was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Services cable | 2 | 2 | 2 |  |  | Corroded connection at FOLCB | Minor shock | 29/11/2017 0:00 |  |  | 9082 |  |  | 20180123PWA_06 | Infrastructure (customer connection) | -38.1304 | 141.6301 | 1 | Powercor | Report | 10999 | 0.0077604 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3304 | Heywood | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Crew on arrival observed LV fuse mains box burnt on pole and small burnt area at base of pole. Fire extinguished by CFA. Burnt grass area, no other damage. LV fuse main box replaced. | 60 YASMIN DRIVE, HERNES OAK VIC 3825 | 2208544 |  |  |  | Overheated connection |  |  | 2 | IMS 232114. Fire about 2x2 metres square in size located at base of pole. Fault on LV fuse mains box on underground service to property. Burnt out LV fuse mains box. | Any other type | 0 | 0 | 0 |  | moe31 | Burnt out LV fuse Mains box. High impedance fault. | Grassfire | 23/01/2018 2:00 | 1 | Localised: less than 10 sq.m | 9074 | Residential |  | 20180123SPN_01 | Infrastructure (network-based) | -38.2338 | 146.2922 | 1 | AusNet Services Distribution | Report | 10986 | 0.024953 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Hernes Oak | Fuse
Transformer was isolated (LV & HV) and HV earth wire was replaced under access permit. | 10 OLD RIDDELL ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Jemena electrical network operator was on patrol following a successful reclose of feeder circuit breaker and found the white phase HV boric acid fuse operated at Riddell Road-P55 pole-mounted substation. On further inspection, it was found that the copper HV earth wire had been cut away and stolen. Photos have been attached in the "Notes and Findings" section. | Copper;Boric acid;Pole mounted;Earth/earthing | 2 | 2 | 2 |  | SBY11 | Copper theft by unknown parties | Damage to network assets | 27/01/2018 13:13 |  |  | 9099 | Agricultural |  | 20180124JEM_02 | Infrastructure (network-based) | -37.554 | 144.698 | 1 | Jemena | Report | 11018 | 0.03816 | 22kV AC | Melbourne Airport | 3429 | Sunbury | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole The attending Powercor Fault Crew replaced the existing O/H Service Cable to the Pole Top Connection Box and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 28 FURNESS STREET, KANGAROO FLAT VIC 3555 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Tori White was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metal Shower Tap and her bare feet while standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  |  | corroded connection | Minor shock | 13/11/2017 10:30 |  |  | 9087 | Residential |  | 20180124PWA_04 | Infrastructure (network-based) | -36.8179 | 144.2344 | 1 | Powercor | Report | 11005 | 0.011861 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Kangaroo Flat | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination located at the Reticulation Pole The attending Powercor Fault Crew disconnected and remade the O/H Service Neutral Conductor termination at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 69 FRASER CRESCENT, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Mrs Tessa Vaux-Miller was in the Bathroom having a shower when she received an electric shock as she made simultaneous contact between her hands on the metallic Shower Tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded neutral connection | Minor shock | 42989.8125 |  |  | 9094 | Residential |  | 20180124PWA_11 | Infrastructure (network-based) | -38.2593 | 144.5191 | 1 | Powercor | Report | 11012 | 0.011112 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination and burnt FOLCB located at the Customers POA, The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result following replacement of the FOLCB by the attending REC. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 34 HIGHMONT DRIVE, BELMONT VIC 3216 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Winston was washing mud from her hands at an external garden tap when she received an electric shock as she made simultaneous contact with one hand on the metal tap and her bare feet while standing on the wet ground | Service conductor;Customer installation | 2 | 2 | 2 |  |  | corroded neutral at FOLCB | Minor shock | 31/10/2017 9:00 |  |  | 9098 | Residential |  | 20180124PWA_14 | Infrastructure (customer connection) | -38.1907 | 144.3321 | 1 | Powercor | Report | 11063 | 0.03248 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
On arrival crew carried out repairs | 123 CURLEWIS STREET, SWAN HILL VIC 3585 | 32158229 |  |  |  | Fuse failed to eject;Candled fuse |  |  |  | VicFire reported a pole fire at the incident location. On arrival, crew found that a candled fuse hanging up on SW#34828. There were no injuries and ground fire. | EDO fuse | 2 | 2 | 2 |  | SHL008 | Hung up EDO fuse | Pole-top fire | 22/01/2018 2:34 | 1 | Negligible: no ground fire | 9105 | Roadway |  | 20180125PWA_02 | Infrastructure (network-based) | -35.3393 | 143.561 | 1 | Powercor | Report | 11026 | 0.0185 | 22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Fuse
The crew isolated the transformer and installed a new substation earth under access permit. | 136 MAKLAND DRIVE, DERRIMUT VIC 3030 | 30244819 | Copper theft | [6 empty] | Powercor personnel noted a missing/stolen earth at LIS 726292 opposite 136 Makland Drive Derrimut. This pole supports Makland-Castro P2, 100kVA pole type substation. The earth appeared to have been cut and removed from ground line to a high point about the transformer tank. There were no reported injuries. There were no reports of ground fire. | Earth/earthing | 2 | 2 | 2 |  | SU023 | Copper theft | Damage to network assets | 24/11/2017 22:40 |  |  | 9109 | Roadway |  | 20180125PWA_04 | Infrastructure (network-based) | -37.7905 | 144.775 | 1 | Powercor | Report | 11030 | 0.028204 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
Initial Report: CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. CEOT also notified the local DAO to investigate. Final Report: CFA attended. Fault crew replaced bridges on pole 2010941. | 965 KOONWARRA-INVERLOCH ROAD, LEONGATHA SOUTH VIC 3953 | 2010941 |  |  |  | Corrosion;Overheated connection |  |  |  | IMS 232136. Initial Report: Customer reports sparking and arcing pole at rear of property. CEOT Dispatch received a call from Vic Fires also saying grass fire in vicinity of pole at 9:45. Final Report: It would appear the PG clamps on the HV bridges (3-3/2.75 st/gz) were corroded and loose which may have lead to arcing which resulted in a grass fire of 16 sq. metres in size. | Pole (wood) | 0 | 0 | 0 |  | lga23 | Corroded and loose PG clamps on bridges lead to arcing. | Grassfire | 24/01/2018 20:19 | 1 | Small: 10 - 1000 sq.m | 9102 | Agricultural |  | 20180125SPN_01 | Infrastructure (network-based) | -38.575 | 145.8443 | 1 | AusNet Services Distribution | Report | 11575 | 0.032507 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Leongatha South | Connection
A faults truck attended and removed the overhead service to 37 Grandview Avenue and issued a defect notice to the occupier as repairs are required to be completed by a REC before supply can be restored. | 37 GRANDVIEW AVENUE, GLEN IRIS VIC 3146 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  | Conductor clashing |  |  | 1 | Customers supplied from "Norwood-Mills" substation reported a loss of their electricity supply. A Nationwide Demolition work crew were working at 39 Grandview Avenue when an excavator contacted the overhead service that supplied 37 Grandview Avenue damaging the overhead two phase service and POA. In addition, the LV white phase 315amp fuse operated at the east circuit of "Norwood-Mills" substation following conductor clashing in the overhead reticulation after the pole was shaken. No shocks or injuries were received. | Service conductor;Aluminium | 0 | 0 | 0 |  |  | A Nationwide Demolition work crew were working at 39 Grandview Avenue when an excavator contacted the overhead service that supplied 37 Grandview Avenue. | Loss of supply;No Go Zone (contact);Damage to network assets | 24/01/2018 13:30 |  |  | 9112 | Residential |  | 20180125UTD_03 | Infrastructure (network-based) | -37.8523 | 145.0838 | 1 | United Energy Distribution | Report | 11033 | 0.03222 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an Open Circuit U/G Supply Neutral Conductor in the Underground Reticulation Service Pit. The attending Powercor Fault Crew reterminated the Powercor U/G Service Neutral Conductor in the Service Pit and completed an NST which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 532-536 FOURTEENTH STREET, MILDURA VIC 3500 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr Pat Woollard was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Services cable | 2 | 2 | 2 |  |  | Loose neutral connection | Minor shock | 26/11/2017 9:00 |  |  | 9133 | Residential |  | 20180129PWA_05 | Infrastructure (network-based) | -34.2121 | 142.1637 | 1 | Powercor | Report | 11059 | 0.0083808 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Connection
On arrival crew inspected assets and restored supply | 13 LANGSHAW STREET, ALTONA NORTH VIC 3025 | 32163566 | Vehicle | [5 empty] | 1 | A passer-by advised a truck has hit a wire at the incident location. Upon arrival the Powercor crew found that a communication cable tangled with the LV conductors. Protection operated . T No injuries or fire reported. | Conductor (bare) | 2 | 2 | 2 |  | BLT020 | Truck struck communication cable | Loss of supply | 42898.5875 |  |  | 9136 | Roadway |  | 20180129PWA_07 | Infrastructure (network-based) | -37.8259 | 144.8477 | 1 | Powercor | Report | 11062 | 0.0024861 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | ELEY ROAD, BLACKBURN SOUTH VIC 3130 |  |  | Heat |  | Neutral fault |  |  | 2 | Callers supplied from "Eley-Grange" substation advised of appliance damage following a supply outage. During very warm conditions, customers supplied from "Eley-Grange" pole type substation sustained appliance damage after the neutral connection failed at the 22kV 315kVA transformer. Customers in the area advised the faults crew of damage to appliances prior to the outage and the faults crew requested that a LEI attend to investigate as a HVI was suspected. The LEI confirmed a high voltage injection occurred (BWD 1702) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment | Conductor (insulated);Connector/termination;Transformer | 0 | 0 | 0 |  | EB 14 | failed neutral connection to the 22kV transformer at "Eley-Grange" pole type substation. | HV injection | 27/01/2018 19:00 |  |  | 9131 |  |  | 20180129UTD_02 | Infrastructure (network-based) | -37.8473 | 145.1467 | 1 | United Energy Distribution | Report | 11057 | 0.012725 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn South | Connection
Voltage tests between an independent earth and various parts of the installation passed. NST tests at installation switchboard and neighbouring property switchboard also returned a pass result. A visual inspection of the incoming neutral screen supply cable showed noticeable signs of wear and damage. Jemena lines crew to replace neutral screened service to the property. All tests carried out, PASS results obtained. | 7 JUDITH STREET, KEILOR EAST VIC 3033 |  |  |  |  | Age |  |  | 2 | Customer received minor shock from outdoor tap whilst touching the tap with his hand and simultaneously standing on the dry ground with rubber souled shoes. | Service conductor | 2 | 2 | 2 |  |  | No cause found. Suspect it was due to the neutral screened service which crew replaced. Refer to Techsafe report for more details. | Minor shock | 30/01/2018 17:48 |  |  | 9153 |  |  | 20180130JEM_03 | Infrastructure (network-based) | -37.7465 | 144.8781 | 1 | Jemena | Report | 11623 | 0.0037303 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | OH Cable
The faults crew isolated the neutral screen service and the site was made safe. They checked the person who received the electric shock and recommended that he seek a medical examination following the electric shock being received but he stated to the crew that it wasnâ€™t a â€œbig shockâ€, as the live service conductor only brushed the back of his hand. The faults crew proceeded to replace the overhead service to 58 with a XLPE type and supply was left on following the completion of installation tests. | 58 GOODWIN STREET, BLACKBURN VIC 3130 | 7033518 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 2 | Customer reports that an overhead electricity line going to 58 Goodwin Street has been pulled from the POA and the cable is hanging in the front yard of 56 Goodwin Street. The caller was from 54 Goodwin Street and states the cable was pulled down by an excavator. The Zinfra faults crew arrived on site at 9.00AM to find the neutral screen service cable from pole number LIS 7033518 that supplied 58 Goodwin Street remained alive and was taped up at the base of the pole after being felled by an excavator working at a home abolishment at 56 Goodwin Street. The crew spoke to the workers and identified the overhead service cable was pulled down by an excavator working at the site. The workers advised the crew that a resident at 54 Goodwin Street was the person who taped up the broken service to the base of the pole and had received an electrical shock to the hand. Details of those involved were captured by the faults crew and United Energy notified ESV and was provided with reference number 7980346. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | The single phase neutral screen cable was struck by a large excavator. | Minor shock | 42955.3681 |  |  | 6385 | Residential |  | 20170809UTD_03 | Infrastructure (network-based) | -37.8167 | 145.1632 | 1 | United Energy Distribution | Report | 7869 | 0.037093 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | Vehicle
On arrival the crew made the site safe, as the cable is no longer required a Fault Followup raised to remove the cable. | ALEXANDRA AVENUE, MELBOURNE VIC 3004 | 30179748 | Working too close to underground cables | [6 empty] | A contractor advised an excavator has dug up an UG cable at the incident location. Upon arrival, the crew noticed that a service cable had been damaged at the west side of the bridge. There were no injuries or fire. | Services cable | 2 | 2 | 2 |  | MP036 | Excavation Works | No Go Zone (contact);Damage to network assets | 25/07/2017 7:00 |  |  | 6389 |  |  | 20170810PWA_01 | Infrastructure (network-based) | -37.823 | 144.9763 | 1 | CitiPower | Report | 7875 | 0.0066678 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Dug up
ESV attended the site and carried investigations with the assistance of Citipower Information was given by fellow workers. | 334 CITY ROAD, SOUTHBANK VIC 3006 | 30166924 |  |  |  |  | Unknown work practice factor | Phase to phase | 1 | Dean was attempting to install a C/Breaker into a distribution switchboard , Switchboard was live at the time of the incident. Dean Contacted phase to phase resulting in Dean receiving flash burns to his arms and face. Protection within the Citipower S/Station was deployed. No shock was received ESV attended the site and carried investigations with the assistance of Citipower | Customer installation | 2 | 2 | 2 |  | AP001 | Attempting to install a C/Breaker into a distribution switchboard | Medical attention (first aid/doctor/hospital) | 19/07/2017 15:00 |  |  | 6391 | Commercial |  | 20170810PWA_02 | Infrastructure (network-based) | -37.8279 | 144.9575 | 1 | CitiPower | Report | 7879 | 0.025402 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | Other
Site made safe and Jemena crew isolated Govan-Stanlake substation for repairs. Transformer and wiring replaced. | 18 STANLAKE STREET, FOOTSCRAY VIC 3011 | A032340 | Copper theft | [5 empty] | 1 | MFB reported a possible tree fire caused by Jemena assets, including customers reporting "All Supply failures" fed out of Govan-Stanlake single pole-mounted substation. Attending crew found red phase LV tail from transformer bushing to isolator had failed. Jemena crew did not find evidence of a fire. Whilst onsite, Jemena faults crew also found HV and LV earths on the transformer were missing and concluded that they have most likely been stolen. It was not possible to identify when exactly the theft took place. | Pole mounted;Connector/termination;Earth/earthing | 0 | 0 | 0 |  | FW04 | Copper theft | Damage to network assets | 43016.7604 |  |  | 6396 | Residential |  | 20170811JEM_02 | Infrastructure (network-based) | -37.7919 | 144.8837 | 1 | Jemena | Report | 8154 | 0.0083588 | 22kV AC | Essendon Airport | 3011 | Footscray | Other
Supply was disconnected and made safe. | 44 & 48 VOLGA STREET, HADFIELD VIC 3046 |  | Unauthorised work | [5 empty] | 2 | 2 illegally connected Builders Temporary Supply (BTS) poles where the overhead services have been relocated from a demolished residential homes to an unsafe non compliant BTS pole by non authorized Jemena personal and without a prescribed CES. | Service conductor;Aluminium twisted (XLPE);Smart meter | 2 | 2 | 2 |  |  | Unknown third party illegally connected BTS poles to overhead service. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/08/2017 12:06 |  |  | 6410 |  |  | 20170814JEM_02 | Infrastructure (network-based) | -37.7055 | 144.9414 | 1 | Jemena | Report | 7899 | 0.038039 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
The crew replaced the damaged cable and repaired the hole in the conduit. | 26 LIDDY STREET, KENSINGTON VIC 3031 | 30184254 | Working too close to underground cables | [6 empty] | A customer reported loss of power to their home at 28 Liddy St, Kensington. On arrival the underground fault crew found a damaged conduit and underground mains cable supplying 28 Liddy Street. It appears that the damage had been caused by Telstra technicians / contractors who had installed a Telstra pit directly above the damaged area. The Telstra pit has been insitu for some time before the damage caused a fault and loss of supply to 28 Liddy Street. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | FT013 | Unknown party installed communication pit above cable | Loss of supply;No Go Zone (contact);Damage to network assets | 28/07/2017 18:36 |  |  | 6405 | Public space |  | 20170814PWA_01 | Infrastructure (network-based) | -37.7896 | 144.9258 | 1 | CitiPower | Report | 7893 | 0.020649 | Low voltage AC (<1kV) | Essendon Airport | 3031 | Kensington | Other
On arrival crew isolated supply and carried out repairs | 11 HEYINGTON PLACE, KENNINGTON VIC 3550 | 34001771 | Working too close to underground cables | [6 empty] | A contractor reported a manually operated Jack hammer has hit an UG cable at the incident location. Upon arrival, the Powercor crew noticed that an UG LV mains had been damaged. There were no injuries or fire. | Cable | 2 | 2 | 2 |  | BET005 | Excavation works | No Go Zone (contact);Damage to network assets | 42743.4125 |  |  | 6408 | Public space |  | 20170814PWA_02 | Infrastructure (network-based) | -36.7633 | 144.3049 | 1 | Powercor | Report | 7896 | 0.027991 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Kennington | Dug up
A faults truck attended and found the timber residence has been partially demolished. The timber home is fenced off with a crane in the front yard. The appears the house is ready for demolishment and there are no workers in attendance when the faults crew attended. The crew contacted their supervisor and United Energy and received instructions to remove the single phase grey twisted service and meter as the home could be demolished as soon as Monday. The crew took photos and forwarded them to their Supervisor and United Energy as ESV will be informed of the safety infringement. | 1009 HEATHERTON ROAD, NOBLE PARK VIC 3174 | 632836 | Working too close to overhead lines;Unauthorised work | [5 empty] | 2 | A passerby (0481 281 055) advised there is a cable laying across the front yard of this premise. An unknown caller advised of a overhead service laying alive on the ground. It appears the vacant timber home has been partially demolished with the single phase supply remaining connected. During the demolition preparation works, the facia board has been partially removed thatâ€™s caused the overhead service to be low. In addition, the active conductor has been removed from the active link at the meter board that remained live as the service fuse was still in at the POA. A review of the account notes in United Energy systems shows that an abolishment request hasn't been received. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | The vacant timber home has been partially demolished and during the preparation works, the facia board has been partially removed thatâ€™s caused the overhead service to be low. | No Go Zone (contact) | 43047.7396 |  |  | 6402 | Residential |  | 20170814UTD_01 | Infrastructure (network-based) | -37.9636 | 145.1629 | 1 | United Energy Distribution | Report | 7890 | 0.038918 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Other
A LEI and faults truck attended and suspected the pit connections were required to be re-terminated and the three phase pole mounted FOLCB at pole number LIS No. 3315865 also required replacement. There appeared to be damaged insulation on the red phase of the underground service cable. The underground cables were re-terminated in the pit following the FOLCB replacement and the LEI tested the installation confirming the fault had been rectified. | 16 GULLS WAY, FRANKSTON SOUTH VIC 3199 | 3315865 |  |  |  | Electrical breakdown |  | Phase to earth | 2 | REC called to advise of a part supply failure at the property. The REC suggested to check the pit as he received a slight tingle from the service line and the customer heard a load bang. The REC will remain on site. A REC (James Marc Electrical Contractor) was called after a customer had a part supply failure at the property. The REC (Licence No. 12252) received a slight electric shock to his hand when checking the cables in the pit and contacted the United Energy faults and emergencies call centre. | Services cable;Copper | 0 | 0 | 0 |  |  | Damaged insulation on the red phase of the underground service cable within the service pit. | Minor shock | 42774.4792 |  |  | 6403 | Residential |  | 20170814UTD_02 | Infrastructure (network-based) | -38.1628 | 145.0993 | 1 | United Energy Distribution | Report | 7891 | 0.010841 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston South | Other
LV leads have been replaced. | 25 MAST GULLY ROAD, UPWEY VIC 3158 | 1314427 |  |  |  | Age;Corrosion;Overheated connection |  | Phase to phase | 1 | IMS 228541- LV droppers burnt out. Crew attended and CFA was on site. Crew found burnt out LV leads 95mm. No trace of fire or scorching marks found on ground. | Dropper/bridge | 0 | 0 | 0 |  | UWY1 | could not be ascertained - potentially a combination of load, age and corrosion. | Pole-top fire | 15/06/2017 16:35 | 1 | Negligible: no ground fire | 6419 | Residential |  | 20170817SPN_01 | Infrastructure (network-based) | -37.8989 | 145.3325 | 1 | AusNet Services Distribution | Report | 7916 | 0.036488 | Low voltage AC (<1kV) | Moorabbin Airport | 3158 | Upwey | Conductor
Site made safe with fuse replaced. | 3770 GRAND RIDGE ROAD, MIRBOO NORTH VIC 3871 | 2002648 |  |  |  | Fuse failed to eject |  |  | 2 | IMS228816 - 6amp EDO Fuse on a single phase switch hung up on a single phase line, the unit was held up and did not fall to the ground. No fire or burnt grass. | EDO fuse | 0 | 0 | 0 |  | LGA11 | EDO fuse hung up. | Loss of supply | 28/06/2017 9:19 |  |  | 6421 | Agricultural |  | 20170817SPN_02 | Infrastructure (network-based) | -38.3826 | 146.1159 | 1 | AusNet Services Distribution | Report | 8381 | 0.0092431 | 22kV AC | Morwell (Latrobe Valley Airport) | 3770 | Mirboo North | Fuse
On arrival crew isolated supply and replaced pole and services | 406-408 EAGLEHAWK ROAD, EAGLEHAWK VIC 3556 | 32030457 | Vehicle | [6 empty] | Police called that a car had hit a pole and reporting wires down. The vehicle had struck a pole and had shifted it 2m in the ground upon impact. The driver/s of the vehicle has left the scene before police had arrived. Services disconnected from the pole by the impact. There was no fire. | Service conductor;Pole (concrete) | 2 | 2 | 2 |  | EHK031 | Vehicle struck pole | Loss of supply;Damage to network assets | 42802.8715 |  |  | 6426 | Roadway |  | 20170818PWA_02 | Infrastructure (network-based) | -36.721 | 144.2571 | 1 | Powercor | Report | 7935 | 0.017218 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Eaglehawk | Vehicle
On arrival crew isolated supply and commenced repairs. | 130 DOURO STREET, NORTH GEELONG VIC 3215 | 30072254 | Vehicle | [5 empty] | 1 | A Powercor fault crew reported a truck has contacted a pole at the incident location. On arrival the fault crew found a LV conductor was on the ground, There was a simultaneous HV feeder reclose, no evidence on site of HVI. The vehicle left the scene. There was no fire, injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | GB031 | Vehicle contacting pole | Loss of supply;Damage to network assets | 42924.4715 |  |  | 6427 | Roadway |  | 20170818PWA_03 | Infrastructure (network-based) | -38.1129 | 144.3497 | 1 | Powercor | Report | 7937 | 0.029597 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3215 | North Geelong | Vehicle
Cable isolated and CitiPower conducted investigation | 119 BRUNSWICK ROAD, BRUNSWICK VIC 3056 | 30159582 | Working too close to underground cables | [5 empty] | 1 | Contractor cut energized high voltage cable with power saw whilst removing out of service cables from excavation in order to install conduit pit for tramway upgrade. Consequent outage effected approximately 600 customers. There was no injury, fire or third party damage. | Cable | 0 | 0 | 0 |  | WB010 | Interference | Loss of supply | 16/08/2017 15:58 |  |  | 6435 | Roadway |  | 20170822PWA_01 | Infrastructure (network-based) | -37.7779 | 144.9693 | 1 | CitiPower | Report | 12087 | 0.013236 | 6.6kV AC | Essendon Airport | 3056 | Brunswick | Other
The customer advised the crew to abolish and remove the meter box and cables as they are demolishing the whole site. The crew decommissioned the meter box and removed meter and cables onsite. | 8 OTTAWA ROAD, TOORAK VIC 3142 | 30233744 | Unauthorised access | [6 empty] | Customer reported an excavator had hit the meter box at above incident location. On arrival, the crew reported an excavator did contacted the meter box and moved the LV cables. There was no fire or reported injuries. | Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | AR005 | Building demolition works | No Go Zone (contact) | 26/07/2017 14:45 |  |  | 6442 | Residential |  | 20170825PWA_02 | Infrastructure (network-based) | -37.8464 | 145.0206 | 1 | CitiPower | Report | 7969 | 0.040441 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Vehicle
Isolated at 1312536. Fault crew attended on the same day and replaced the head of the street light. | CAR YARD, 1097 BURWOOD HIGHWAY, FERNTREE GULLY VIC 3156 | 1312538 |  |  |  | Defective component |  |  |  | IMS 229982- Report of street lighting pole fire at the corner of Selman Ave & Burwood Hwy received. Site visit conducted. On Pole#1312538 the street light PE cell had failed and caught fire. Call was recorded on the 25th of August. No damage to surrounding area, the fire was contained in the head of the street light. | Public lighting | 0 | 0 | 0 |  | FGY23 | Vegetation: Trees Incident | Pole-top fire | 25/08/2017 19:27 | 1 | Negligible: no ground fire | 6454 | Commercial |  | 20170830SPN_01 | Infrastructure (network-based) | -37.8884 | 145.2952 | 1 | AusNet Services Distribution | Report | 15187 | 0.018735 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Ferntree Gully | AF Other
Spoke to factory owner. Obtained the driver's detail: John Payne 0428576423 Inspected the site - burn mark under the truck - no fire or injury reported. Inspected HV conductors from EPV - minor damage to HV conductor (broken strands). Fitted splices on the stranded conductor. Supply restored. | 52 BUCKLER ROAD, NORTH WANGARATTA VIC 3678 | 5652722 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS229714 - a tip truck was unloading chicken manure in the yard at the back of a factory when contact was made with HV line Between LIS# 5652722 & # 5652723 . Spur fuse blown. | Conductor (bare) | 0 | 0 | 0 |  | WN3 | tip truck in contact with conductor when unloading | Loss of supply;No Go Zone (contact) | 43047.4528 |  |  | 6459 | Industrial |  | 20170830SPN_02 | Infrastructure (network-based) | -36.331 | 146.3709 | 1 | AusNet Services Distribution | Report | 8025 | 0.020105 | 22kV AC | Wangaratta Aero | 3678 | North Wangaratta | Vehicle
section isolated and made safe. conductor repaired and supply restored on the same day. | 500 SOLDIERS ROAD, CLYDE NORTH VIC 3978 | 502470 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | IMS 229693 - Excavator hit 22kV overhead conductor and brought it down. No person injured. | Conductor (bare) | 0 | 0 | 0 |  | CLN23 | no go zone breach | Loss of supply;No Go Zone (contact) | 43016.375 |  |  | 6470 | Agricultural |  | 20170831SPN_02 | Infrastructure (network-based) | -38.0842 | 145.3627 | 1 | AusNet Services Distribution | Report | 13407 | 0.020086 | 22kV AC | Moorabbin Airport | 3978 | Clyde North | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the HV crossarm replacement was completed under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 28 SPRINGFIELD ROAD, BLACKBURN VIC 3130 | 639431 |  |  |  | Age;HV injection |  |  | 1 | At 1325hrs on 24/08/2017, ACR BH7317 located in Primrose Street reclosed to lockout affecting 77 customers. The MFB advised of a broken crossarm near the corner of Springfield Road and Beverley Crescent. A HV spur fusing strain crossarm (BH7148) broke outside 28 Springfield Road at pole No. LIS 0639431 and the blue phase HV disc insulator pulled through the HV crossarm and the HV conductor made brief contact with the LV conductors below. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the north circuit of "Bordeaux-Beverley" substation. The LEI confirmed a high voltage injection occurred (BWD 1701) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | DC 08 | Broken HV strain crossarm most likely due to deterioration. | HV injection;Loss of supply | 24/08/2017 13:25 |  |  | 6466 | Roadway |  | 20170831UTD_03 | Infrastructure (network-based) | -37.8098 | 145.1447 | 1 | United Energy Distribution | Report | 8077 | 0.026841 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Crossarm
The Victoria Police was notified and a police report completed with details of the security breach and theft at the zone substation. | HAMMOND ROAD, DANDENONG SOUTH VIC 3175 |  | Unauthorised access;Copper theft | [5 empty] | 2 | A Zinfra substation crew arrived at DSH (Dandenong South) zone substation to continue with construction activities and observed there was a breach in the security fence in the south east corner from the adjacent property. The substation crew found that copper control cables installed to the new plant were cut and removed by unknown persons. | Cable;Copper;Zone substation | 0 | 0 | 0 |  | DSH | Security breach at DSH zone substation. | Damage to network assets | 42955.3125 |  |  | 6475 | Other | Zone substation | 20170904UTD_01 | Infrastructure (network-based) | -38.0141 | 145.2064 | 1 | United Energy Distribution | Report | 8125 | 0.032591 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Other
The pole type substation was isolated and the electric fence tape removed. At 2310hrs, "Madden-Pine" substation was re-energised and a 160amp service fuse replaced at pole No. LIS 1814312 along with a 315amp HRC fuse on the blue phase at "Madden-Pine" substation. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 29 PINE LANE, HEATHERTON VIC 3202 | 1824451 |  |  |  | HV injection |  |  | 1 | At 1638hrs on 27/08/2017, 66kV feeder HTS-KBH circuit breaker reclosed to lockout but no customers were affected. The 66kV feeder was patrolled and a piece of electric fence tape approximately 2m in length over the centre phase insulator near 29 Pine Lane at pole No. LIS 1824451. There was no wind at the time of the fault and a high voltage injection was suspected and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Madden-Pine" substation. The LEI confirmed a high voltage injection occurred (CLA 1704) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | HTS-KBH | A piece of electric fence tape approximately 2m in length was found on the centre phase insulator near 29 Pine Lane. | HV injection;Loss of supply | 27/08/2017 16:38 |  |  | 6476 | Residential |  | 20170904UTD_02 | Infrastructure (network-based) | -37.9593 | 145.0975 | 1 | United Energy Distribution | Report | 8090 | 0.020929 | 66kV AC | Moorabbin Airport | 3202 | Heatherton | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the HV conductors were repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | TALBOT AVENUE, BENTLEIGH VIC 3204 | 1804436 |  |  |  | HV injection;Electrical breakdown |  |  | 1 | At 2225hrs on 28/08/2017, 11kV feeder BT 06 circuit breaker reclosed to lockout affecting 469 customers. A possum got across the 11kV red and white phase conductors on the HV/LV tee-off pole on the corner of Talbot and Tovan Akas Avenues, Bentleigh. The fault current caused HV ampact connections to fail on the corner of Talbot Avenue and Brewer Road at pole No. LIS 1804461and the red and white phase HV conductors fall to the ground making brief contact with the red phase LV conductor below. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the west circuit of "Clairmont-Brewer" substation. The LEI confirmed a high voltage injection occurred (CLA 1705) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | BT 06 | Animal Incident | HV injection;Loss of supply | 28/08/2017 22:25 |  |  | 6477 | Roadway |  | 20170904UTD_03 | Infrastructure (network-based) | -37.9212 | 145.0282 | 1 | United Energy Distribution | Report | 8091 | 0.003353 | 11kV AC | Moorabbin Airport | 3204 | Bentleigh | Animal
The faults crew replaced the copper transformer earth cable and re-installed the timber cover guards at pole No. LIS 7058387. | MACROBERTSON STREET, TEMPLESTOWE LOWER VIC 3107 | 7058387 | Copper theft | [5 empty] | 2 | Copper Theft - Copper transformer earth cable was stolen from "MacRobertson-High" substation. A Select Solutions Asset Inspector identified that unknown persons had stolen the copper transformer earth cable from "MacRobertson-High" pole type substation. | Earth/earthing | 0 | 0 | 0 |  | BU 09 | Unknown persons had stolen the copper transformer earth cable from "MacRobertson-High" pole type substation. | Damage to network assets | 28/08/2017 12:30 |  |  | 6478 | Roadway |  | 20170904UTD_04 | Infrastructure (network-based) | -37.7598 | 145.1185 | 1 | United Energy Distribution | Report | 8092 | 0.017036 | 22kV AC | Essendon Airport | 3107 | Templestowe Lower | Other
Isolated at transformer. made safe - Inspector following up to check for any customer side damage - replaced fused junction box on pole. no photo available | 45 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909 | 1902793 |  | Prone to salt deposition | [5 empty] | IMS230171 - fuse box on pole caught fire - no ground fire @lis 1902793 | Connection box | 0 | 0 | 0 |  | NLA34 | likely caused by polluted insulator (salt ) | Pole-top fire | 42834.9958 | 1 | Negligible: no ground fire | 6488 | Roadway |  | 20170905SPN_03 | Infrastructure (network-based) | -37.8608 | 148.0347 | 1 | AusNet Services Distribution | Report | 8317 | 0.025657 | Low voltage AC (<1kV) | Bairnsdale Airport | 3909 | Lake Bunga | Fuse
Crew attended, made safe and completed repairs LEI attended to assess HV Injection damage | 17 SHANNON AVENUE, HAMLYN HEIGHTS VIC 3215 | 32075999 |  | Animal |  |  |  |  | 1 | A customer reported hearing loud explosions and power going off and back on again. On arrival the crew found that a possum had contacted a HV line resulting the a helical termination parting and the HV conductor contacting the low voltage circuit. Feeder protection operated. There were no fires or injuries reported. A number of premises sustained HV injection damage | Conductor (bare) | 0 | 0 | 0 |  | GL021 | Animal Incident | Loss of supply;More than $50k damage | 43017.1354 |  |  | 6505 | Residential |  | 20170912PWA_01 | Infrastructure (network-based) | -38.1286 | 144.3386 | 1 | Powercor | Report | 8139 | 0.011284 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3215 | Hamlyn Heights | Animal
Site made safe and driver assisted from vehicle | 97 CASHMORE ROAD, PORTLAND VIC 3305 | 32134313 | Working too close to overhead lines | [5 empty] | 1 | A customer reported employee driven boom into power line at the incident location. On arrival the crew found that a log loader was in contact with the HV and had brought down conductors Observers had seen the truck make contact and told the employee to stay in the truck until crew arrived. There were no fires or injuries reported. HV protection operated | Conductor (bare) | 0 | 0 | 0 |  | PLD002 | Interference | Loss of supply;No Go Zone (contact) | 43048.6479 |  |  | 6506 | Industrial |  | 20170912PWA_02 | Infrastructure (network-based) | -38.3217 | 141.5855 | 1 | Powercor | Report | 8141 | 0.020043 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
A faults crew attended and there was no evidence of any attempted copper cable theft and no damage to the substation. A new padlock was installed and the kiosk substation was safely secured. | MANNINGHAM ROAD, BULLEEN VIC 3105 | 7069495 | Unauthorised access | [5 empty] | 2 | Caller reports the 2.5 tonne kiosk substation in Manningham Road outside the Bulleen Heights School has the padlock removed and the handle looks like its in the open position. The school is located opposite Ayr Street. Kiosk substation "Manningham N221 - Ayr" had been opened by unknown persons after the padlock had been removed. The kiosk padmount substation is located within the grounds of Bulleen Heights School in Manningham Road. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | BU 10 | Unknown person removed the padlock and opened the kiosk substation door. Do damage or injuries were sustained. | Damage to network assets | 14/09/2017 7:20 |  |  | 6515 | Roadway |  | 20170915UTD_01 | Infrastructure (network-based) | -37.7723 | 145.1047 | 1 | United Energy Distribution | Report | 8156 | 0.025572 | 22kV AC | Essendon Airport | 3105 | Bulleen | Other
JEN field crew attended the incident, made safe, sleeved conductor and restored supply. | 8 GREGORY COURT, SUNBURY VIC 3429 | SAP equipment no. 10694630 |  | Wind |  | Mechanical breakdown |  |  | 2 | A LV overhead conductor (2nd footpath phase) broke mid span (at the LV spreader) and consequently fell to the ground. A customer had reported loss of supply and wire down on the ground. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | SBY33 | The cause of the LV overhead conductor failure is unknown. Site visit and on-site evidence did not conclusively identify the root cause of the incident. Although this section of conductor crosses a road, there was no clear evidence of vehicle impact and this was therefore not reported as a "external impact" event. Contributing factors were strong gust winds on the day of the incident, an unclipped conductor from an LV spreader and pre-existing damage on the conductor not identified in the previous inspection. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/09/2017 5:10 |  |  | 6516 | Residential |  | 20170918JEM_01 | Infrastructure (network-based) | -37.5839 | 144.7095 | 1 | Jemena | Report | 8157 | 0.035471 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Conductor
Faults crew disconnected the unauthorised and illegal service. | 30-32 CARLISLE STREET, PRESTON VIC 3072 |  | Unauthorised work;Unauthorised access | [5 empty] | 2 | Unknown persons relocated an overhead service from a residential dwelling to a BTS. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Unknown persons relocated an overhead service. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/09/2017 11:46 |  |  | 6518 | Residential |  | 20170918JEM_03 | Infrastructure (network-based) | -37.7523 | 145.0089 | 1 | Jemena | Report | 8159 | 0.025396 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
The employee has immediately seized work and bought down the EWP to its resting place and contacted JEN Control room. The employee was shaken from the incident but there has been no injuries to the work party or the general public. Jemena fault crew attended the site at 10.00am, assessed the situation and made safe. Jemena crew restore the damaged conductor by sleaving method and restored customer supply. As this work was neither for or by Jemena personnel or contractors, Jemena will not conduct a formal investigation. Third party contractor is investigating the incident and its expected to submit a full incident report to Hobson Bay City Council. | 93 RAILWAY PLACE, WILLIAMSTOWN VIC 3016 |  | Caused by REC/contractor | Council |  |  |  |  | 1 | A third party tree clearing company carrying out works for Hobson Bay City Council at the corner of Railway Place and Charles Street, Williamstown, made contact with JEN Low Voltage assets while clearing tree branches around JEN overhead mains. Active Tree Services had been instructed to setup their worksite at pole no. A024344, north side of Charles St, Williamstown, to prune vegetation around JEN Assets. One employee had entered the EWP with his Pole Chainsaw resting across the rim of the bucket with each end of the chainsaw pole outreached on each side of the EWP. The employee had raised his boom of the EWP to the designated height, and started slewing across to reach his destination with the focus on the live LV conductors in front of him. As he was approaching his work zone with the focus on the LV conductors in front of him, he has misjudged his chainsaw pole resting across the rim of the EWP and the chainsawâ€™s head became in contact with the Blue and White phase bare copper LV Conductors that were alive. Once the metal chainsaw head had made contact, the blue phase bare LV conductor has dropped on the ground and broken contact from the chainsawâ€™s head. | Conductor (bare) | 0 | 0 | 0 |  | NT15 | Contributing factors identified by initial interview: â€¢ The work party had appointed a spotter to watch the works being carried out by the employee in the EWP, but was not fully observant / failed to do so due to the fact the observer was also conducting other works in the preparation of the task. â€¢ Employee in the EWP had failed to wait till the spotter has his full attention towards the task carried out in the EWP. â€¢ The work party had failed to comply with Safe Approach Distances (SAD). | Loss of supply;Damage to network assets | 18/09/2017 9:52 |  |  | 6519 | Residential |  | 20170918JEM_04 | Infrastructure (network-based) | -37.8607 | 144.8915 | 1 | Jemena | Report | 8307 | 0.0037384 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Other
On arrival crew confirmed isolations. Multiple emergency agencies on site. Pole was supported to enable emergency service to carry out their work. Pole replaced | 6981 MURRAY VALLEY HIGHWAY, WYUNA VIC 3620 | 30124023 | Vehicle | [5 empty] | 1 | Dispatch called NAO to report a car had hit a pole and people were trapped on the corner of the Murray Valley Highway and Scobie Rd â€“ Tongala. It appeared that a two car collision had taken place with an elderly couple in one car ( possibly deceased) and another car containing multiple occupants some of whom were treated at the scene. The pole was fractured at ground level. There was no fire, two reported fatalities and damage to two vehicles. The fatalities related to the vehicle accident and were not electrically caused. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | KYM004 | Vehicle collision | Loss of supply;Not involving electrocution;Damage to network assets | 42987.3521 |  |  | 6523 |  |  | 20170920PWA_01 | Infrastructure (network-based) | -36.199 | 145.0055 | 1 | Powercor | Report | 8164 | 0.027719 | 22kV AC | Shepparton Airport | 3620 | Wyuna | Vehicle
Controller directed the fault crew to isolate the circuit to make safe. Repairs were complete on the same day under an EAP. | 205 NINE MILE ROAD, TYNONG VIC 3813 | 514944 |  |  |  | Fatigue |  | Phase to earth | 0 | IMS 230332- Report of cable off a pole by passerby, faultcrew dispatched to site and confirmed that 1 phase of copper LV was on ground from Lis 514944, no LV fuses had blown to clear the fault therefore the conductor was alive on the ground. | Conductor (bare) | 0 | 0 | 0 |  | PHM14 | fatigued line. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/09/2017 7:24 |  |  | 6538 | Agricultural |  | 20170926SPN_01 | Infrastructure (network-based) | -38.1034 | 145.6219 | 1 | AusNet Services Distribution | Report | 8186 | 0.021619 | Low voltage AC (<1kV) | Moorabbin Airport | 3813 | Tynong | OH Cable
Jemena crew made site safe and repaired white phase LV conductor. | 62 BECKET STREET N, GLENROY VIC 3046 |  | Vehicle | [6 empty] | Truck hit white phase overhead LV conductor resulting in LV conductor on ground. | Conductor (bare) | 0 | 2 | 2 |  |  | Truck clipped overhead line and caused it to fall to ground. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/09/2017 12:36 |  |  | 6548 | Roadway |  | 20170927JEM_02 | Infrastructure (network-based) | -37.6963 | 144.9127 | 1 | Jemena | Report | 9641 | 0.020861 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Vehicle
On arrival crew made safe and carried out repairs. | 65 MUNDY STREET, GEELONG VIC 3220 | 32076772 | Working too close to underground cables | [6 empty] | Collin (City of Greater Geelong) reported a crew have exposed a cable while they were working with an excavator at the incident location. Upon arrival, the Powercor crew noticed an UG earthing cable that connected to the HV switch had been dug up in the nature strip. There was no evidence of injuries or fire or third party property damage.. | Earth | 2 | 2 | 2 |  | GLE032 | Council roadworks | Damage to network assets | 29/08/2017 9:40 |  |  | 6546 | Public space |  | 20170927PWA_07 | Infrastructure (network-based) | -38.1584 | 144.3635 | 1 | Powercor | Report | 8194 | 0.030959 | Earthing cable | Avalon Airport | 3220 | Geelong | Dug up
On arrival crew made safe and carried out repairs. | SAYERS ROAD, LAVERTON VIC 3028 | 30244154 | Copper theft | [6 empty] | A contractor reported a copper theft at the incident location. Upon arrival, the Powercor fault crew found that 3m of copper earthing cable had been cut away. No other damage identified. There were no reported injuries, fire or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | LV006 | Copper theft | Damage to network assets | 28/08/2017 17:58 |  |  | 6550 | Public space |  | 20170927PWA_09 | Infrastructure (network-based) | -37.8554 | 144.762 | 1 | Powercor | Report | 8198 | 0.0094479 | Earthing cable | Laverton Raaf | 3028 | Laverton | Other
On arrival crew isolated supply and carried out repairs. | BUNDARA, 692 DINYARRAK ROAD, LILLIMUR VIC 3420 | 33047492 |  | Fallen;MEC |  |  |  |  | 1 | CFA reported a fire at the incident location. On arrival, the crew found that a tree branch (from outside the clearance space) had fallen across an adjacent 22kV line resulting in a ground fire (Approx. 50m x 25m) in paddock. Protection operated. There were no reported shocks, injuries or 3rd party damage. | Conductor (bare) | 2 | 2 | 2 |  | NHL031 | Vegetation: Trees Incident | Grassfire | 28/09/2017 16:16 | 1 | Medium: 1000 sq.m - 10 ha | 6559 | Agricultural |  | 20171002PWA_01 | Infrastructure (network-based) | -36.3066 | 141.0659 | 1 | Powercor | Report | 12589 | 0.0027164 | 22kV AC | Horsham Aerodrome | 3420 | Lillimur | Trees
On arrival crew carried out repairs | 12 HOTHAM STREET, LAKE WENDOUREE VIC 3350 | 30355647 | Vehicle | [6 empty] | Vic Fire reported a car had hit a pole at incident location. On arrival the crew found that the pole had snapped at the base with the car on site, The police reported that the number plates are stolen . Add other relevant details in here: | Pole (wood) | 2 | 2 | 2 |  | BAN005 | Vehicle incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42987.3576 |  |  | 6562 | Roadway |  | 20171003PWA_01 | Infrastructure (network-based) | -37.5525 | 143.8478 | 1 | Powercor | Report | 8212 | 0.0054803 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Lake Wendouree | Vehicle
Crew have replaced/repaired the earth cables. | 48-54 BURNS ROAD, ALTONA VIC 3018 | 30226125 | Copper theft | [6 empty] | A Powercor employee reported copper earth missing from a HV switch pole. A crew attended and found that cable earths were cut and removed from the pole. Police have been notified. No shock, injuries or third party damage. | Earth | 2 | 2 | 2 |  | AC031 | Copper theft | Damage to network assets | 17/09/2017 11:24 |  |  | 6569 | Public space |  | 20171003PWA_06 | Infrastructure (network-based) | -37.851 | 144.7893 | 1 | Powercor | Report | 8219 | 0.017398 | Earthing cable | Laverton Raaf | 3018 | Altona | Other
On arrival crew isolated supply and carried out repairs | HOLLANDS TRACK, AVOCA VIC 3467 | 31003249 |  | Wind |  |  |  |  | 1 | ACR tripped and crew were asked to perform patrol. Crew found copper conductor down between pole 315 and 316 in a paddock. There were no injuries, no ground fire, minor third party damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO008 | Crew did not find any immediate cause of the broken conductor. | Loss of supply | 17/09/2017 7:39 |  |  | 6570 | Agricultural |  | 20171003PWA_07 | Infrastructure (network-based) | -37.1216 | 143.4437 | 1 | Powercor | Report | 8222 | 0.038976 | 22kV AC | Ballarat Aerodrome | 3467 | Avoca | Conductor
On arrival crew isolated supply and completed repairs. | 68 KERANG-QUAMBATOOK ROAD, KERANG VIC 3579 | 33108359 |  |  |  | Mechanical breakdown |  |  |  | Call to report sparking at the top of the insulators on an HV switch at incident location. Upon arrival crew noted that there was considerable sparking on the boundary side insulator of switch. There was no other damage to assets or private property. ESV NOT# N/A There were no reported injuries or third party damage. | Disconnector/isolator | 2 | 2 | 2 |  | KGT004 | connection loose | Melting or smoking only;Damage to network assets | 43078.791 |  |  | 6571 | Public space |  | 20171003PWA_08 | Infrastructure (network-based) | -35.7331 | 143.8915 | 1 | Powercor | Report | 8223 | 0.0052569 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable which was identified as the cause of the high impedance within the neutral service conductor. The attending Citipower Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 35 PARKVILLE STREET, BURNLEY VIC 3121 | 30191944 |  |  |  | Corrosion |  | Phase to earth |  | Ms Joanna Spiez was taking a shower when she received an electric shock as she made simultaneous contact between her hands on the shower taps and her feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | TK001 | Corroded service cable | Minor shock | 31/08/2017 18:30 |  |  | 6580 | Residential |  | 20171003PWA_16 | Infrastructure (network-based) | -37.8286 | 145.0115 | 1 | CitiPower | Report | 8232 | 0.026758 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Burnley | OH Cable
Crew repaired earth | 324 SOMERVILLE ROAD, KINGSVILLE VIC 3012 |  | Copper theft | [5 empty] | 2 | Earth stolen from a switch | Copper | 2 | 2 | 2 |  | FW04 | Copper cable stolen by unknown person(s) | Damage to network assets | 42835.3132 |  |  | 6584 | Roadway |  | 20171004JEM_02 | Infrastructure (network-based) | -37.8115 | 144.8731 | 1 | Jemena | Report | 8236 | 0.028138 | Earthing cable | Essendon Airport | 3012 | Kingsville | Other
Remaining standing trees cut and line restored | 304 ANNYA ROAD, MILLTOWN VIC 3304 | 33055450 |  | Alive;Fallen;Property owner/customer |  |  |  |  | 1 | Customer reported tree had brought down power lines across road. On arrival the crew found that one of the trees on the fringe of a recently harvested plantation had fallen and brought down 4 spans of SWER conductor. The crew isolated supply and reinstated the conductor after the remaining standing plantation trees were cut. | Conductor (bare) | 0 | 0 | 0 |  | HYT011 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 29/09/2017 10:16 |  |  | 6592 | Forest - plantation |  | 20171004PWA_09 | Infrastructure (network-based) | -38.0335 | 141.6656 | 1 | Powercor | Report | 12590 | 0.02756 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3304 | Milltown | Trees
On arrival crew checked conductors and carried out repairs | 5 UNDERBOOL SOUTH ROAD, UNDERBOOL VIC 3509 | 33067224 | Working too close to overhead lines | [5 empty] | 1 | Following an outage on Underbool P428 ACR, a member of the public reported directly to the fault crew that a truck had hit the HV conductors just past the ACR. On arrival the crew found that a Tipper Truck had been tipping bark at the incident location, when the top of the tipper contacted the 22kV overhead conductors between P428 & P428A Murrayville Line. The crew also stated that the driver of the truck didnâ€™t appear to have any injuries, but appeared dazed and was attended to by ambulance officers, and later taken to Mildura Hospital for observation. The truck sustained damage to the front tyres and the crew reported that the front wheel bearings were also damaged. Worksafe were to attend later in the day. There were no other injuries or damage reported. | Conductor (bare) | 2 | 2 | 2 |  | OYN001 | Tipper contacted conductors | Loss of supply;Medical attention (first aid/doctor/hospital);No Go Zone (contact) | 42865.5278 |  |  | 6595 |  |  | 20171006PWA_01 | Infrastructure (network-based) | -35.1701 | 141.8044 | 1 | Powercor | Report | 9818 | 0.039265 | 22kV AC | Mildura Airport | 3509 | Underbool | Vehicle
Crew attended m made safe and undertook repairs to damaged conductor | 10440 PRINCES HIGHWAY, ALLANSFORD VIC 3277 | 31030223 |  |  |  | Corrosion |  |  | 1 | Powercor received a call from VicFire reporting â€œsparking wiresâ€ at warrnambool. When crews arrived on site they found CFA crews in attendance and they had extinguished a number of spot fires, approx. 5m x 80m along the Princes Hwy, approx. 1.2km east of Staffords Rd. The cause of the fires appeared to be a broken 22kV conductor | Conductor (bare) | 0 | 0 | 0 |  | WBL002 | Conductor parted at joint | Grassfire | 42926.9104 | 1 | Small: 10 - 1000 sq.m | 6600 | Roadway |  | 20171009PWA_01 | Infrastructure (network-based) | -38.3881 | 142.5652 | 1 | Powercor | Report | 8255 | 0.026281 | 22kV AC | Warrnambool Airport Ndb | 3277 | Allansford | Conductor
crew attended, made safe and undertook repairs | BANNOCKBURN-SHELFORD ROAD, BANNOCKBURN VIC 3331 | 30231988 |  | Fallen;MEC |  |  |  |  | 1 | On Sun 8 Oct 2017 at 11:49am, Powercor received a call from VicFire reporting a wire down at LIS989876 with a small grass fire When crews arrived at the incident site, they found a broken tree branch across the 22kV HV overhead conductors. A small ground fire (2m x 2m) near the base of the pole had been extinguished by the CFA. The tree was part of the Bannockburn Recreation Reserve. No conductors fell to ground. No other third party property damage was reported. No injuries were reported. | Conductor (bare) | 0 | 0 | 0 |  | GL012 | Vegetation | Grassfire | 42957.4924 | 1 | Localised: less than 10 sq.m | 6601 | Public space |  | 20171009PWA_02 | Infrastructure (network-based) | -38.047 | 144.1417 | 1 | Powercor | Report | 8257 | 0.00081481 | 22kV AC | Avalon Airport | 3331 | Bannockburn | Trees
Crew attended and replaced cross-arm | 27-29 CORACK ROAD, DONALD VIC 3480 | 32019143 |  | Precipitation;Prone to dust deposition |  | Leakage |  |  | 1 | Numerous customers reported no supply . Crew attended to find end of HV Cross-arm had burnt off and HV insulator was resting on LV cross-arm. | Crossarm (wood) | 0 | 0 | 0 |  | CTN006 | Dust pollution and moisture | Pole-top fire;Loss of supply | 42988.5389 | 1 | Negligible: no ground fire | 6608 | Agricultural |  | 20171011PWA_02 | Infrastructure (network-based) | -36.3582 | 142.9911 | 1 | Powercor | Report | 12279 | 0.0032222 | 22kV AC | Horsham Aerodrome | 3480 | Donald | Crossarm
Crew attended and completed repairs | VERE STREET, COLLINGWOOD VIC 3066 | 30173750 | Working too close to underground cables | [5 empty] | 1 | Citipower fault crew attending an outage found an UG HV cable had been damaged. The damage was done by a contractor while he was excavating the area for construction of Collingwood College playground. | Cable | 0 | 0 | 0 |  | CW014 | Interference | Loss of supply;Damage to network assets | 43018.3993 |  |  | 6616 |  |  | 20171013PWA_02 | Infrastructure (network-based) | -37.8025 | 144.9916 | 1 | CitiPower | Report | 12088 | 0.00018056 | 11kV AC | Essendon Airport | 3066 | Collingwood | Dug up
Emergency high voltage switching was completed and the electrical infrastructure repaired under electrical access permit conditions. Supply was restored upon completion. | 56 NEPEAN HIGHWAY, MENTONE VIC 3194 | 1822129 |  |  |  | Electrical breakdown |  |  | 0 | AT 0157hrs on 19/10/2017, 11kV feeder M23 circuit breaker successfully reclosed and held. The white phase HV conductor failed mid span at a sleeve on the corner of Nepean Highway and Flinders Street that caused the HV conductor to fall onto the LV crossarm. A HVI was suspected to customers in the vicinity and a was LEI dispatched to investigate and it was later confirmed that a HVI did not occur. Molten metal fell into a garden bed below and started a very small fire at the BP service station that was quickly extinguished. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | M23 | A HV conductor failed at a sleeve midspan on the corner of Nepean Highway and Flinders Street. | Grassfire | 19/10/2017 1:57 | 1 | Localised: less than 10 sq.m | 6622 | Roadway |  | 20171020UTD_02 | Infrastructure (network-based) | -37.9773 | 145.0666 | 1 | United Energy Distribution | Report | 12957 | 0.037198 | 11kV AC | Moorabbin Airport | 3194 | Mentone | Conductor
A faults truck attended and found the white phase HV fuse had candled at Bangholme-Hammond" capacitor bank. The pole mounted vacuum switch appeared to be damaged and the faults crew left the capacitor bank isolated. | 97-105 BANGHOLME ROAD, BANGHOLME VIC 3175 | 206462 |  |  |  | Candled fuse |  |  | 1 | A pole fire was reported at pole No. LIS 0623176 located at "Bangholme-Hammond" capacitor bank installed on DVY34 22kV feeder. There was no ground fire. | Boric acid | 0 | 0 | 0 |  | DVY34 | The pole mounted vacuum switch appeared to be damaged and may have been the most likely cause. | Pole-top fire | 19/10/2017 11:01 | 1 | Negligible: no ground fire | 6625 | Roadway |  | 20171020UTD_03 | Infrastructure (network-based) | -38.0381 | 145.1987 | 1 | United Energy Distribution | Report | 12958 | 0.019924 | 22kV AC | Moorabbin Airport | 3175 | Bangholme | Pole
Crew dispatched to investigate : 22kV Blade isolator failed with fixed jaw burnt out. fire extinguished upon crew arrival. observed 29x 6m marks of grass fire near asset BD020 P#1604421. Nearby fence posts were damaged with scorch marks. (see attached photos) Crew replaced the single blade 22KV isolator. | 1881 GREAT ALPINE ROAD, WISELEIGH VIC 3885 | 1604421 |  |  |  | Mechanical breakdown |  |  | 0 | IMS 230752 - Emergency services reported fire. Fault crew dispatched. | Disconnector/isolator | 0 | 1 | 0 |  | BDL8 | 22kV Blade isolator failed with fixed jaw burnt out. | Grassfire | 15/10/2017 10:00 | 1 | Small: 10 - 1000 sq.m | 6627 | Agricultural |  | 20171023SPN_01 | Infrastructure (network-based) | -37.7244 | 147.8012 | 1 | AusNet Services Distribution | Report | 8304 | 0.018506 | 22kV AC | Bairnsdale Airport | 3885 | Wiseleigh | AF Other
issued to crew to make safe and investigate - large limb of a tree fell on the line, damaged insulator or/and dislodged the conductor causing leakage concentration on T off xarm king bolt caused pole fire and the pole top broke. Photos attached pole being replaced. | 128 MCFEES ROAD, RHYLL VIC 3923 | 2805565 |  | Blown branch/vegetation |  |  |  |  | 0 | IMS 230386 - pole caught fire and snapped at top due to large limb hitting cable. | Conductor (bare);Pole (wood);Crossarm (steel) | 0 | 0 | 0 |  | PHI11 | vegetation contact | Pole-top fire;Loss of supply | 19/09/2017 8:32 | 1 | Negligible: no ground fire | 6634 | Agricultural |  | 20171024SPN_01 | Infrastructure (network-based) | -38.4936 | 145.2965 | 1 | AusNet Services Distribution | Report | 8443 | 0.0012859 | 22kV AC | Moorabbin Airport | 3923 | Rhyll | Trees
On arrival crew replaced poles and services | 18 JAMES STREET, NORTHCOTE VIC 3070 | 30356213 | Vehicle | [6 empty] | A customer in James Street, Northcote, reported truck hit and bought down multiple service wires at the incident location. On arrival the crew found that an earthmoving machine on a truck had hit cable TV lines. It dragged the cable TV with it and caused a CitiPower pole to snap and also several Low Voltage (LV) services broke. There were no reported injuries or other third party damage. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | NC001 | Truck hit cable TV cables | Loss of supply;Damage to network assets | 28/09/2017 14:21 |  |  | 6645 | Roadway |  | 20171027PWA_01 | Infrastructure (network-based) | -37.775 | 144.9952 | 1 | CitiPower | Report | 8330 | 0.010622 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Vehicle
On arrival crew carried out repairs | 473-481 KARADOC AVENUE, NICHOLS POINT VIC 3501 | 30095498 |  |  |  | Leakage |  |  | 1 | Following reports of dim lights Crossarm fire located on pole 8 Karadoc Ave. There was no ground fire, no reported injuries or third party property damage. No photo of incident site available. | Crossarm (wood) | 2 | 2 | 2 |  | RCT011 | excessive leakage current | Pole-top fire | 43049.6646 | 1 | Negligible: no ground fire | 6666 | Roadway |  | 20171103PWA_01 | Infrastructure (network-based) | -34.2099 | 142.1916 | 1 | Powercor | Report | 8354 | 0.0015475 | 22kV AC | Mildura Airport | 3501 | Nichols Point | Pole
On arrival crew carried out repairs | 2805 OLD MELBOURNE ROAD, DUNNSTOWN VIC 3352 | 33006274 |  |  |  | Corrosion |  |  |  | A Fault crew attending following a reported outage and found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | EDO fuse | 2 | 2 | 2 |  | BAS023 | Hung up fuse | Pole-top fire;Hung-up fuse only | 43049.7785 | 1 | Negligible: no ground fire | 6667 | Roadway |  | 20171103PWA_02 | Infrastructure (network-based) | -37.5897 | 143.9645 | 1 | Powercor | Report | 8355 | 0.037573 | 22kV AC | Ballarat Aerodrome | 3352 | Dunnstown | Fuse
On arrival crew isolated supply and carried out repairs | ATHORN ROAD, WOORINEN VIC 3589 | 31022238 |  |  |  | Leakage |  |  | 1 | Passing truck driver adv crossarm rotten, has broken and wires hanging low with insulator off beam, not within reachable height but a breeze could cause wires to make contact with pole. On arrival crew found there had been a crossarm fire and end was burnt off crossarm. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 43079.2979 | 1 | Negligible: no ground fire | 6673 | Roadway |  | 20171103PWA_04 | Infrastructure (network-based) | -35.249 | 143.4722 | 1 | Powercor | Report | 8361 | 0.022016 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 28 COOPER AVENUE, GLEN WAVERLEY VIC 3150 | 608953 |  | Precipitation |  | Leakage |  |  | 1 | At 1104hrs on 07/11/2017, 22kV feeder MGE 34 circuit breaker reclosed to lockout affecting 621 customers. The MFB reported a pole fire with HV conductors fallen onto the LV conductors. During light drizzly weather, a cross arm fire occurred on a HV strain pole located outside 28 Cooper Avenue, Glen Waverley that has burnt through the upper part of the HV/LV pole and requires replacement. The HV crossarm burnt through and a HV conductor fell and made contact with the LV below and a high voltage injection was suspected to customers supplied from the west circuit of "Cooper-Whites" substation. A LEI attended and confirmed a high voltage injection did not occur | Crossarm (wood) | 0 | 0 | 0 |  | MGE 34 | The crossarm fire occurred during drizzly weather and tracking was the probable cause. | Pole-top fire | 42927.4611 | 1 | Negligible: no ground fire | 6678 | Roadway |  | 20171108UTD_01 | Infrastructure (network-based) | -37.8993 | 145.1725 | 1 | United Energy Distribution | Report | 12959 | 0.040354 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Pole
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor at the Split Bolt Clamp termination at the Reticulation Pole, which was identified as the cause of the high impedance associated with the return path for the neutral current. The attending Powercor Fault Crew replaced the Single Phase O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 4 GRAHAM STREET, KANGAROO FLAT VIC 3555 | 33013968 |  |  |  | Corrosion |  | Phase to earth | 2 | Mrs Shirley Hibbert was standing at the Kitchen sink when she received an electric shock as she made simultaneous contact between her hands on the Hot Water Tap and the metallic Kitchen sink. | Service conductor | 2 | 2 | 2 |  | BET004 | corroded service connection | Minor shock | 43017.75 |  |  | 6682 | Residential |  | 20171109PWA_01 | Infrastructure (network-based) | -36.7908 | 144.246 | 1 | Powercor | Report | 8371 | 0.031487 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Kangaroo Flat | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor of an O/H Neutral Screened Service Cable, which was identified as the cause of the high impedance associated with the return path for the neutral current. The attending Powercor Fault Crew replaced the Single Phase O/H Neutral Screened Copper Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 12 PERTOBE LANE, WARRNAMBOOL VIC 3280 | 31029408 |  |  |  | Corrosion |  | Phase to earth | 2 | Mr Robert Wallace was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hands on the shower taps and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WBL004 | Corroded service neutral connection | Minor shock | 16/09/2017 0:00 |  |  | 6683 | Residential |  | 20171109PWA_02 | Infrastructure (customer connection) | -38.3917 | 142.4671 | 1 | Powercor | Report | 8372 | 0.0093981 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
The attending Powercor Fault Crew disconnected the damaged Underground Consumers Mains Conductors at the Electricity Supply Pit to enable repairs by an REC/LEIW. | 28 RICHARD DRIVE, LARA VIC 3212 | 30308742 | Working too close to underground cables |  |  |  |  | Phase to earth | 2 | Mr Barry Macdonald (Gardening Contractor) attended the premises at 28 Richard Drive Lara to install a front boundary fence. Mr Macdonald was operating a Post Hole Digging Machine adjacent to the Electricity Supply Pit when he heard a loud bang. Mr Macdonald reached down into the post hole to clear away dirt, when he felt what he described as a minor electric shock. | Services cable | 2 | 2 | 2 |  | FNS012 | Post hole digging | Minor shock | 23/09/2017 11:00 |  |  | 6684 | Public space |  | 20171109PWA_03 | Infrastructure (network-based) | -38.0291 | 144.3929 | 1 | Powercor | Report | 8374 | 0.041583 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Dug up
On arrival crew carried out repairs. | 109 DOYLES ROAD, GRAHAMVALE VIC 3631 | 33092008 |  | Bird |  |  |  |  | 1 | Crew attended to find small ground fire had been extinguished by Vic Fire on road verge. Evidence of a dead crow at the base of the pole. Feeder CB STN024 operated just prior to report from Vic Fire. There were no injuries or third party property damage. | Crossarm (steel);Pole (concrete) | 2 | 2 | 2 |  | STN024 | Bird Incident | Grassfire | 42989.8215 | 1 | Localised: less than 10 sq.m | 6690 | Roadway |  | 20171110PWA_03 | Infrastructure (network-based) | -36.3755 | 145.4319 | 1 | Powercor | Report | 8402 | 0.024591 | 22kV AC | Shepparton Airport | 3631 | Grahamvale | Animal
On arrival crew carried out repairs | 437 LANDRIGAN ROAD, CARISBROOK VIC 3464 | 33011414 |  |  |  | Overheated connection |  |  | 2 | Crew attended to find a connection between bare LV Mains and Service Connection Junction Box had Burnt off on the red phase. A small ground fire on the road verge area resulted. This fire was extinguished by Fire agency . There was no property damage, No injuries or reported shocks. | Conductor (bare);Dropper/bridge | 2 | 2 | 2 |  | MRO007 | Malfunction of Electrical connection | Grassfire | 43080.4993 | 1 | Small: 10 - 1000 sq.m | 6694 | Roadway |  | 20171113PWA_02 | Infrastructure (network-based) | -37.0884 | 143.7976 | 1 | Powercor | Report | 8407 | 0.001816 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3464 | Carisbrook | Connection
On arrival, the fault crew had assessed the damage, made the site safe and carried out repairs to the damaged LV conductors between pole numbers A008464 and A008463 with sleeve, also repaired blue phase conductor at 55 Wood Street, Ascot Vale and also restored customers' outage on that circuit. Once the fault investigation was completed, the fault crew noticed that the roof plumber installing roof sheet and facers from a scaffold that was erected on a building construction site at 55 Wood Street, Ascot Vale. The fault crew approached the roof plumbers and questioned if the fault had something to do with roof installation works that they were carrying out, but the roof plumbers had denied that they had involvement with the fault. The fault crew could not see any other evidence that the roof plumbers had any involvement to the fault. On Friday 24 November 2017, Jemena Works Practices attended site to investigate further and make sure that the site is safe for the public and to check for any other hazards. Findings on site: 1. The site had been made safe 2. The building construction site was shut and there was any evidence of any work being carried out 3. The scaffold erected at the building site appears to be compliant with No Go Zone guidelines 4. There is no NGZ permit issued on this site | 55 WOODS STREET, ASCOT VALE VIC 3032 |  |  | Wind | [5 empty] | Jemena overhead fault crew was dispatched to white phase low voltage conductor down between pole numbers A008464 and A008463, with damage also to the blue phase conductor at 55 Wood Street, Ascot Vale. | Conductor (bare) | 0 | 0 | 0 |  | ES22 | Incident occurred adjacent to a building site where workmen were installing tin roof sheeting in windy conditions, although any involvement related to this incident was denied by the workmen. | Loss of supply | 14/11/2017 7:41 |  |  | 6702 | Residential |  | 20171114JEM_02 | Infrastructure (network-based) | -37.7746 | 144.9018 | 1 | Jemena | Report | 8432 | 0.020332 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Other
crew attended and commenced repairs | 41-47 ROSENEATH STREET, NORTH GEELONG VIC 3215 | 32081845 | Working too close to overhead lines | [5 empty] | 1 | A contractor reported that a scissor lift has inadvertently contacted overhead lines at the incident location. On arrival the fault crew found that a contractor was repairing the scissor lift which was located under the high voltage overhead line, not being fully aware of the high voltage line above. The contractor raised the lift which contacted the live overhead line. This caused arcing between line and scissor lift, the overhead power line broke falling onto the ground starting a small fire at the incident location. MFB crews arrived on site and a small fire was extinguished. (1m by 0.5m). The operator of the lift appeared to be uninjured, he was advised to seek medical attention. | Conductor (bare) | 2 | 2 | 2 |  | GB031 | Interference - Scissor Lift operator struck HV | Loss of supply;Grassfire | 17/11/2017 10:17 | 1 | Localised: less than 10 sq.m | 6719 | Commercial |  | 20171117PWA_03 | Infrastructure (network-based) | -38.1197 | 144.3492 | 1 | Powercor | Report | 8453 | 0.036597 | 22kV AC | Avalon Airport | 3215 | North Geelong | Other
Customer reported a failure of supply on the 14th August. Fault crews were dispatched and on arrival at RAU 6 single phase substation found an EDO fuse tube burnt in half, with the top section on the ground and the bottom section hanging down in the fuse carrier. Note the fuse carriers have fixed fire chokes and are unsuitable for a concrete pole. There was no evidence of any fire at the base of the pole. The bottom section of HV EDO tube removed from fuse carrier. Both fuse tubes were replaced and supply restored. An investigation of the AMI smart meter for the site revealed that the EDO fuse link likely blew and had remained arcing when supply failed. Moisture ingress had been identified in both fuse tubes earlier and a notification had been raised on the 18/8/2017 as a 90 day item to replace the Fuse Carriers with Boric Acid fuses. | 445 UP RIVER ROAD, CARLYLE VIC 3685 | 5209079 |  |  |  | Moisture ingress;Fuse failed to eject | Inappropriate tools/plant/equipment |  | 0 | IMS229737 - Customer call with no supply , fault crew found Hung Up 6K EDO fuse blown, No fire on ground and no fire on pole. | EDO fuse | 0 | 0 | 0 |  | BWA23 | EDO fuse hung up - moisture ingress and incorrect type (fixed fire chokes) previously fitted. | Pole-top fire | 14/08/2017 10:53 | 1 | Negligible: no ground fire | 6502 | Roadway |  | 20170911SPN_01 | Infrastructure (network-based) | -36.0001 | 146.4948 | 1 | AusNet Services Distribution | Report | 8136 | 0.041657 | 22kV AC | Wangaratta Aero | 3685 | Carlyle | Fuse
fuse link and fuse tube replaced and the supply restored. | 501 RUSHOLME ROAD, TARRAWINGEE VIC 3678 | 5111668 |  | Bird |  | Candled fuse |  |  | 0 | IMS229279- Customer reported light inside house flickering. Fault crew attended site and found a dead bird, HV EDO fuse candled. No ground fire observed. | EDO fuse | 0 | 0 | 0 |  | WN5 | Bird Incident | Pole-top fire | 19/07/2017 10:06 | 1 | Negligible: no ground fire | 6503 | Residential |  | 20170911SPN_02 | Infrastructure (network-based) | -36.365 | 146.4858 | 1 | AusNet Services Distribution | Report | 8137 | 0.026953 | 22kV AC | Wangaratta Aero | 3678 | Tarrawingee | Animal
A faults crew attended and the fire was extinguished after the crew arrived and no fire was sighted. The burnt out three phase FOLCB was replaced by the crew and supply restored upon completion. | 16 WILLIAMS GROVE, BONBEACH VIC 3196 | 3303133 |  |  |  | Overheated connection |  |  | 2 | Per fire brigade - distribution box on pole number 3306133 is on fire and the fire authority are on site. A birds nest inside a three phase FOLCB at pole No. LIS 3303133 located opposite 13 Williams Grove that supplied an underground supply to units 1 and 2, 13 Williams Grove caught on fire. The pole is located near Port Phillip Bay that may have also contributed to the fault. | Connection box | 0 | 0 | 0 |  | CRM 22 | Bird Incident | Pole-top fire | 19/08/2017 11:25 | 1 | Negligible: no ground fire | 6508 | Roadway |  | 20170912UTD_01 | Infrastructure (network-based) | -38.0627 | 145.1176 | 1 | United Energy Distribution | Report | 12951 | 0.015381 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Bonbeach | Animal
Magpies had been constructing a birds nest made of bits of wire on the top of the transformer at "Ordish N80-82 Cahill" pole type substation at pole number LIS 3425946 located near 82 Ordish Road that momentarily caught fire. The pole fire had been extinguished prior to the faults crew arrival. | 80-82 ORDISH ROAD, DANDENONG SOUTH VIC 3175 | 3425946 |  | Bird |  | Leakage |  |  | 2 | CFA report of a pole fire in Ordish Road. Magpies had been constructing a birds nest made of bits of wire on the top of the transformer at "Ordish N80-82 Cahill" pole type substation at pole number LIS 3425946 located near 82 Ordish Road that momentarily caught fire. The pole fire had been extinguished prior to the faults crew arrival. | Pole mounted | 0 | 0 | 0 |  | DSH 33 | Bird Incident | Pole-top fire | 24/08/2017 6:07 | 1 | Negligible: no ground fire | 6509 | Roadway |  | 20170912UTD_02 | Infrastructure (network-based) | -38.0236 | 145.1924 | 1 | United Energy Distribution | Report | 12953 | 0.018744 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Animal
The steel public lighting pole was removed from the road and details of the affected vehicle owners were captured and provided to the United Energy customer relations availability officer. When the traffic subsided, the faults crew returned and picked up the fallen steel public lighting pole and returned it to the depot. A new trouble order was created for the public lighting poles replacement and the United Energy Asset Inspection Planner commenced an investigation to the cause of the pole to fail. | MANNINGHAM ROAD, BULLEEN VIC 3105 | 9868619 |  |  |  | Mechanical breakdown |  |  | 2 | Emergency services advise that a steel street light pole has fallen near 2 Manningham Road, Bulleen. A 11m steel slip base public lighting pole (LIS No. 9868619) with a double spigot bracket attached installed in the centre medium strip, fall and made contact with two vehicles stopped at the traffic lights causing slight damage. ESV were notified of the event and United Energy were provided with ESV reference No. 8219521. | Public lighting;Pole (steel) | 0 | 0 | 0 |  |  | The United Energy Asset Inspection Planner commenced an investigation to the cause of the pole to fail. | Significant disruption to the community | 13/09/2017 16:45 |  |  | 6513 | Roadway |  | 20170914UTD_01 | Infrastructure (network-based) | -37.7605 | 145.0814 | 1 | United Energy Distribution | Report | 8152 | 0.028909 | Low voltage AC (<1kV) | Essendon Airport | 3105 | Bulleen | AF Other
Feeder patrols initiated. Supply restored when fault detected and removed. | 181 LANGRIDGE STREET, ABBOTSFORD VIC 3067 | 30221828 | Blown detritus | Wind |  |  |  |  | 1 | All supply lost to North Richmond Zone Substation (NR). Note: Substation was on single contingency due to work being undertaken at the station. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | B-NR | Vegetation: Trees Incident | Loss of supply;Significant disruption to the community | 23/09/2017 11:12 |  |  | 6532 | Public space |  | 20170926PWA_01 | Infrastructure (network-based) | -37.8074 | 144.9924 | 1 | CitiPower | Report | 9815 | 0.011558 | 66kV AC | Essendon Airport | 3067 | Abbotsford | Other
On arrival crew isolated supply and carried out repairs | 791 WENTWORTH ROAD, YELTA VIC 3505 | 32150293 |  |  |  | Leakage |  |  |  | CFA Comms reported wires sparking at incident location. On arrival crew found HV intermediate cross arm that had caught fire but has since extinguished. There was no ground fire, no injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MBN013 | Excessive leakage current | Pole-top fire | 18/09/2017 19:44 | 1 | Negligible: no ground fire | 6533 | Roadway |  | 20170926PWA_02 | Infrastructure (network-based) | -34.1283 | 142.0081 | 1 | Powercor | Report | 8306 | 0.0065104 | 22kV AC | Mildura Airport | 3505 | Yelta | Crossarm
On arrival crew isolated supply and carried out repairs | 128 FIFTH STREET, MERBEIN VIC 3505 | 32142995 |  |  |  | Leakage |  |  |  | CFA Comms reported pole fire at 128 Fifth St Merbein. On arrival crew found HV cross arm that had caught fire but had extinguished. There was no ground fire, No injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MBN014 | Excessive leakage current | Pole-top fire | 18/09/2017 18:57 | 1 | Negligible: no ground fire | 6534 | Roadway |  | 20170926PWA_03 | Infrastructure (network-based) | -34.1814 | 142.056 | 1 | Powercor | Report | 8182 | 0.021837 | 22kV AC | Mildura Airport | 3505 | Merbein | Pole
The crew disconnected and isolated the damaged service cable and issued a defect notice. | 14 SIMMIE STREET, SUNSHINE WEST VIC 3020 | 30107312 | Vehicle | [6 empty] | Vic Fire reported a wire down and sparking at incident location. The crew advised that upon attending site, they had discovered the Service Cable running across Simmie Street to the POA at the Greek Orthodox Church , had been hit by an unknown truck and was lying on the road. The truck had also pulled down the Optus CATV and Telstra Cable to 14 Simmie Street and had also damaged the POA. A new service cable could not been run and re-connected at the time, due to the substantial damage to the POA, customer advised to organize REC to repair POA. There were no reported shockâ€™s, injuries or fire. | Service conductor | 2 | 2 | 2 |  | SSE014 | Unknown vehicle struck service cable | Loss of supply;Damage to network assets | 24/08/2017 18:41 |  |  | 6540 | Commercial |  | 20170927PWA_01 | Infrastructure (network-based) | -37.7897 | 144.8172 | 1 | Powercor | Report | 8188 | 0.021209 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
Supply was left off. A fault follow up has been arranged for a Powercor contractor to install a new LV U/G and pit to resupply park. | CHAPEL STREET, WEDDERBURN VIC 3518 | 32020379 | Working too close to underground cables | [6 empty] | A contractor reported that the backhoe on their site dug up an underground service cable at the incident location. On arrival the crew found that a contractor was operating a backhoe and dug up an underground LV service cable causing damage to the cable. There were no reported injuries or third party property damages. | Services cable | 2 | 2 | 2 |  | CTN002 | Streetscape works | Loss of supply;Damage to network assets | 31/08/2017 13:15 |  |  | 6556 |  |  | 20170928PWA_04 | Infrastructure (network-based) | -36.4182 | 143.6134 | 1 | Powercor | Report | 8204 | 0.041109 | Low voltage AC (<1kV) | Bendigo Airport | 3518 | Wedderburn | Dug up
Repairs to the stolen copper HV Earth, approx. 25m where completed. | 79-83 CHERRY LANE, LAVERTON NORTH VIC 3026 | 32173184 | Copper theft | [6 empty] | Field crew reported stolen earth at LIS 827425 and gas switch 22395, pole located near 79-83 Cherry Lane Laverton North 3026. On arrival the Ardeer Faults crew had found that a length of 25m HV Earth had been cut away, removed and stolen at Pole LIS 827425 and gas switch 22395, and also damaged LV Aluminium cable. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | LVN033 | Copper theft | Damage to network assets | 42803.6056 |  |  | 6557 | Public space |  | 20170928PWA_05 | Infrastructure (network-based) | -37.836 | 144.7993 | 1 | Powercor | Report | 8206 | 0.011188 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Other
On arrival crew carried out repairs. | 58 WATSONS ROAD, NEWCOMB VIC 3219 | 30075685 | Vehicle | [6 empty] | The customer at the incident address reported a neighbours vehicles hit and bought down their service wire. On arrival the crew found that a service had been hit by the neighbours truck (While accessing his driveway), resulting in it being bought to ground. There were no reported fire, injuries or other third party damage. | Service conductor | 2 | 2 | 2 |  | GLE031 | Truck hit service | Loss of supply;Damage to network assets | 17/09/2017 16:27 |  |  | 6573 | Roadway |  | 20171003PWA_10 | Infrastructure (network-based) | -38.1651 | 144.3907 | 1 | Powercor | Report | 8225 | 0.016782 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Newcomb | Vehicle
On arrival crew isolated supply and carried out repairs. | 17 TRENERRY CRESCENT, ABBOTSFORD VIC 3067 | 30173169 |  |  |  | Electrical breakdown |  |  |  | A customer reported that there was an explosion and a flash and they have part supply at the incident location. On arrival the fault crew found that a low voltage termination box had faulted causing rupturing of the pitch filled termination, debris was thrown from the faulted equipment with one large piece hit a car causing minor damage to it. There was no pole fire or ground fire and no injury as a result of this incident. | Connection box | 1 | 2 | 2 |  | CW009 | unable to establish | Loss of supply;Damage to network assets | 22/09/2017 11:37 |  |  | 6574 | Roadway |  | 20171003PWA_11 | Infrastructure (network-based) | -37.7993 | 144.9995 | 1 | CitiPower | Report | 8226 | 0.014231 | Low voltage AC (<1kV) | Essendon Airport | 3067 | Abbotsford | AF Other
The faults crew replaced the copper transformer earth cable and re-installed the timber cover guards at pole No. LIS 8815698. | HOMEWOOD ROAD, CRANBOURNE SOUTH VIC 3977 | 8815698 | Copper theft | [5 empty] | 2 | Caller reports that a neutral conductor has been removed from the pole. A passerby identified the copper transformer earth cable was stolen from substation pole "Homewood P5 - Pearce" located near 32 Homewood Road, Cranbourne and contacted the United Energy faults and emergencies call centre. | Conductor (bare);Copper | 0 | 0 | 0 |  | LWN 31 | The copper transformer earth cable was stolen from substation pole "Homewood P5 - Pearce". | Damage to network assets | 28/09/2017 10:00 |  |  | 6563 | Roadway |  | 20171003UTD_02 | Infrastructure (network-based) | -38.1599 | 145.2373 | 1 | United Energy Distribution | Report | 8213 | 0.0091644 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne South | Other
Emergency high voltage switching was completed to minimise the number of customers affected. A faults truck attended and commenced the rectification work at the HV underground cable at the CHP to "Warner-Southern Pool" indoor substation with stinger covering installed on the droppers at pole No. LIS 2317554. A construction crew were called and repaired and re-sagged the overhead conductors in Alamain Avenue before completing further repairs, including the installation of HV spreaders on the overhead conductors at the railway crossing. | WARNER AVENUE, ASHBURTON VIC 3147 | 2317554 |  |  |  | Conductor clashing;Electrical breakdown |  |  | 1 | At 0539hrs on 02/10/2017, 11kV feeders EM 05 and EM 07 circuit breakers reclosed to lockout affecting 2896 customers. A possum flashed over the HV underground cable at the CHP to "Warner-Southern Pool" indoor substation. Secondary damage occurred attributed to fault current as follows: 1. Alamein Avenue corner of Warner Avenue as the red phase tee-off ampact connection failed that caused the intermediate conductor to fall to the ground. 2. Ashburn Grove at HV switch OA0059 where the blue phase connection to the switch failed and the HV switch requires replacement; and 3. West of the EM railway tie station where the EM 05 and EM 07 HV overhead conductors clashed that caused the white phase overhead conductor to fall onto the Vic Rail DC supply near pole No. LIS 8803390. The bay of conductors that crosses the railway line requires replacement due to the damage caused by clashing and the amount of sleeves installed. No HVI or major damage occurred where the DC traction conductors back energised the white phase AC conductor. There was an unconfirmed report of a Vic Rail train with a faulty motor. | Conductor (bare);Traction lines;Any other type;Dropper/bridge | 0 | 0 | 0 |  | EM 05 and EM 07 | Animal Incident | Loss of supply | 42776.2354 |  |  | 6577 | Roadway |  | 20171003UTD_04 | Infrastructure (network-based) | -37.8673 | 145.0856 | 1 | United Energy Distribution | Report | 8229 | 0.021483 | 11kV AC | Moorabbin Airport | 3147 | Ashburton | Animal
The 100amp porcelain fuse carrier was replaced and supply restored upon completion of installation tests. | 130 MITFORD STREET, ELWOOD VIC 3184 | 2332245 |  |  |  | Fatigue;Overheated connection |  |  | 2 | Caller advised the box outside had a cracking noise and sounded like it was shorting out for about 30 seconds before it caught on fire and had smoke coming from it. Smoke and fire have since stopped but they have lost their electricity supply. A 100amp porcelain fuse carrier was burnt out at the unit development in Mitford Street, Elwood. It appeared arcing was evident but there was no evidence of a fire when the faults crew attended. | Any other type | 0 | 0 | 0 |  |  | The cause was attributed to deterioration caused by a probable loose connection that created an overheated connection. | Other electricity related | 42745.816 | 1 | Negligible: no ground fire | 6611 | Residential |  | 20171012UTD_02 | Infrastructure (network-based) | -37.8806 | 144.9873 | 1 | United Energy Distribution | Report | 12956 | 0.021612 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | Connection
A faults crew attended and isolated supply to the South East Water Pump Station at pole number LIS 1300273 and identified the white and blue phase 100amp HRC fuses had operated. The damaged underground cable was repaired and supply restored upon completion. | 26 COLCHESTER ROAD, CAPEL SOUND VIC 3940 | 1300273 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Caller advised that a conduit has been hit with an excavator. Cable has been exposed and no electric shocks have been received. A third party civil contractor working for South East Water has made contact with a LV cable supplying the South East Water Pump Station. When questioned, JHL Civil Contractors believed that a Permit to Work wasn't required for work near the underground cable and they had obtained DBYD plans. No electric shocks or damage to plant was sustained. | Services cable;Copper | 0 | 0 | 0 |  |  | Excavating in close proximity to a live low voltage underground cable. | No Go Zone (contact) | 43079.6042 |  |  | 6613 | Roadway |  | 20171013UTD_01 | Infrastructure (network-based) | -38.3797 | 144.8829 | 1 | United Energy Distribution | Report | 8277 | 0.01323 | Low voltage AC (<1kV) | Moorabbin Airport | 3940 | Capel Sound | Dug up
A faults crew attended and replaced the damaged single phase overhead service and issued a defect notice to the occupier for the damaged POA. Upon completion, the installation was tested and left on supply. | 55 BELLEVUE AVENUE, DONCASTER EAST VIC 3109 | 7071051 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | AMI meter technicians have identified that meter number 518633 located at 55 Bellevue Avenue, Doncaster East is reporting under voltage events. Please check service cable connections at pole number LIS 7071051 and the POA for neutral issues. An unknown demolition crew has made contact with the XLPE overhead service that supplies 55 Bellevue Avenue and left it in a situation with no neutral at the pole end and lying on the temporary metal fencing. No shocks or injuries were received. | Service conductor | 0 | 0 | 0 |  |  | An unknown demolition crew has made contact with the XLPE overhead service . | No Go Zone (contact) | 43079.3889 |  |  | 6617 | Residential |  | 20171016UTD_01 | Infrastructure (network-based) | -37.7834 | 145.1694 | 1 | United Energy Distribution | Report | 8284 | 0.029069 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Other
Jemena crew found large excavator directly under the overhead HV conductor digging a trench for pipes. Jemena crew advised the machine operator to cease work immediately due to encroaching his Safe Approach Distance (SAD) to the HV O/H with his mobile plant. Jemena crew confirmed the work party did not have NGZ VESI permit and had failed to comply with SAD. Work party was advised to remove themselves from the area and to apply for NGZ permit to work. | 45-165 OLD SYDNEY ROAD, MICKLEHAM VIC 3064 |  | Working too close to overhead lines | [5 empty] | 1 | Large (approximately 20t) excavator made contact with overhead HV conductor whilst digging a trench for sewer pipes. See attached photo for splash weld mark on top of the excavator boom. Responsible third party details have been included in the "Other information sources", however the name and contact details of the excavator operator was not taken. The work party consisted of Winslow constructors (Client) and Yarra Valley Excavation (contractor). | Conductor (bare);Steel | 0 | 0 | 0 |  | COO11 | The work party did not have No Go Zone VESI Permit and failed to comply with Safe Approach Distances (SAD) | No Go Zone (contact) | 20/10/2017 15:02 |  |  | 6624 | Agricultural |  | 20171020JEM_01 | Infrastructure (network-based) | -37.535 | 144.8693 | 1 | Jemena | Report | 9725 | 0.037155 | 22kV AC | Melbourne Airport | 3064 | Mickleham | Vehicle
CEOT dispatched a crew sent to investigate. The crew isolated supply from BW1084. The crew found HV Elbows on switchgear were on fire. No damage was caused beside the HV switchgear. | 46 MARINER CLOSE, CRANBOURNE NORTH VIC 3977 | 594816 |  |  |  | Unknown technical factor |  |  | 2 | IMS 230654 - Received INCD from Fire Service saying smoke coming from Kiosk transformer. HV elbows on fire @ Mariner-Godwin kiosk substation. Unknown cause of the fire and damage to switchgear. CFA reported temperatures during the fire at 280 degrees C. | Pad mounted equipment/kiosk | 0 | 1 | 0 |  | CRE23 | The root cause could not be determined. | Plant/equipment | 42957.6687 | 1 | Negligible: no ground fire | 6620 | Residential |  | 20171020SPN_01 | Infrastructure (network-based) | -38.0775 | 145.2859 | 1 | AusNet Services Distribution | Report | 12890 | 0.013198 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne North | AF Other
Successful reclose on the TTS-EP sub transmission 66KV line. A network operator was then dispatched to patrol the line and identified a third party civil contractor carrying out civil works underneath Jemena's 66kv line at a private industrial property at 4 Dalton Rd, Thomastown. The Jemena Network Operator assessed the situation and made the site safe. They then contacted the Jemena Control Room to dispatch JEN fault crew to make repairs to the line (see photo IMG20171023115326). Jemena control room reported incident to ESV via phone (reference #8473724) on the day incident occurred. The details of the excavator operator or site supervisor were not available. In relation to cost recovery for damage done, Jemena has sent letters to the responsible third party (Leoâ€™s Concreting Company) but has yet to receive a response. Jemena has not followed up with the responsible third party in this instance in regards to NGZ compliance education. | 4 DALTON ROAD, THOMASTOWN VIC 3074 |  | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Third party excavator's boom made contact with JEN Sub transmission TTS-EP 66kV line conductor and damaged the overhead conductor (see IMG_4220 and IMG4224). The excavator operator had initially denied involvement in the incident, but subsequently admitted to the incident after being presented with evidence by Jemenaâ€™s network operator. | Conductor (bare) | 0 | 0 | 0 |  | TTS-EP | The work party operating the excavator did not have a No Go Zone VESI Permit and had failed to comply with Safe Approach Distances (SAD). The work party had also failed to identify all overhead electrical assets within their work zone. A potential contributing factor that was observed was the additional soil on site that altered the ground level (See photo IMG_4223). | No Go Zone (contact) | 21/10/2017 9:18 |  |  | 6626 | Industrial |  | 20171021JEM_01 | Infrastructure (network-based) | -37.6958 | 145.0242 | 1 | Jemena | Report | 9716 | 0.014138 | 66kV AC | Essendon Airport | 3074 | Thomastown | Vehicle
BA fuse was replaced. no photo was taken. | 590 INVERLOCH-KONGWAK ROAD, WATTLE BANK VIC 3995 | 5656096 |  |  |  | Candled fuse |  |  | 0 | IMS 230177 - 6K BA fuse was reported burnt out. crew on site observed no fire on ground. fuse candled. | Boric acid | 0 | 0 | 0 |  | WGI22 | BA fuse candled. | Pole-top fire | 42864.6271 | 1 | Negligible: no ground fire | 6629 | Agricultural |  | 20171023SPN_02 | Infrastructure (network-based) | -38.5648 | 145.6968 | 1 | AusNet Services Distribution | Report | 8308 | 0.012933 | 22kV AC | Moorabbin Airport | 3995 | Wattle Bank | Fuse
Crew sent to make safe and investigate - found broken LV open wire 064 copper cable failed and fell to the ground. conductor and grass fire at base of pole Fire was approx. 15 x 4 mtrs . The cable appears to have failed due to a poor IPC connection on the open wire connecting a 95mm ABC service. Heat generated from the poor connection caused the cable to fail and fall to the ground. The hot partials of the IPC and or copper cable could have made contact with the ground. | 311 YAN YEAN ROAD, PLENTY VIC 3090 | 926107 |  |  |  | Defective component;Mechanical breakdown |  | Phase to earth | 0 | IMS 230242- Received incident report for Grass Fire and wire down below transformer on corner Sutherland Rd and Yan Yean Rd. | Copper;Connector/termination | 0 | 0 | 0 |  | ELM15 | Heat generated from the poor connection caused the cable to fail and fall to the ground. The hot particles of the IPC and/ or copper cable could have made contact with the ground. no photo is available. | Loss of supply;Grassfire | 43048.7819 | 1 | Small: 10 - 1000 sq.m | 6630 | Roadway |  | 20171023SPN_03 | Infrastructure (network-based) | -37.6554 | 145.1238 | 1 | AusNet Services Distribution | Report | 8310 | 0.030906 | Low voltage AC (<1kV) | Essendon Airport | 3090 | Plenty | Connection
On arrival crew carried out repairs | 833 KENLEY ROAD, KENLEY VIC 3597 | 32150173 | Working too close to underground cables | [5 empty] | 2 | A contractor (Jonathan Chislett) called to say he had exposed an earthing wire while scraping dirt with a backhoe in the vicinity of the earth. On arrival the crew found that a substation earth had been exposed. There was no fire, reported injuries or other third party damage. | Earth/earthing | 2 | 2 | 2 |  | BBD021 | Scrapping ground in vicinity of substation | Damage to network assets | 21/09/2017 11:19 |  |  | 6636 | Agricultural |  | 20171024PWA_02 | Infrastructure (network-based) | -34.855 | 143.3405 | 1 | Powercor | Report | 8316 | 0.0095104 | Earthing cable | Swan Hill Aerodrome | 3597 | Kenley | Dug up
On arrival the crew found that the LV UG cable was not damaged as stated. The crew noted that the large sign had been taken down in close proximity to a 66kV Line without any permit to work apparently being issued. The site supervisor told the crew that they will be digging footings and erecting a new sign at the site. The crew instructed the site supervisor that a permit to work would be required due to the proximity to the HV conductors, both overhead and underground in the vicinity | 154 RAGLAN PARADE, WARRNAMBOOL VIC 3280 | 41078802 | Working too close to overhead lines |  |  |  | Ineffective planning/procedures/processes |  | 2 | An Electrician reported that a crane was putting up a new sign at the incident location, and that the conduit was damaged and the cable was exposed. On arrival the crew found that the LV UG cable was not damaged, and that the Electrician had used the incident reporting process to expedite an abolishment of supply to the sign. The crew also stated that this was not the first time this REC had used this method to expedite our attendance at a work site. There was no fire, no exposed electrical equipment on site. There were no reported injuries or third party property damage. | Services cable;Customer installation | 2 | 2 | 2 |  | WBL003 | Misrepresentation of situation regarding cable damage Potential no go zone breaches | No Go Zone (no contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/10/2017 9:30 |  |  | 6643 | Commercial |  | 20171026PWA_01 | Infrastructure (network-based) | -38.3825 | 142.5211 | 1 | Powercor | Report | 8328 | 0.0030914 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Other
On arrival crew carried out repairs. | 23 KELPIE BOULEVARD, CURLEWIS VIC 3222 | 30299130 | Working too close to underground cables | [6 empty] | An excavator operator reported that he had dug up an UG cable at the incident location. On arrival the crew found that an excavator had dug up a 185mm LV UG cable insulated end in a new estate. There was no other reported damage or any injuries. | Cable | 2 | 2 | 2 |  | DDL014 | excavator operation | Damage to network assets | 42835.6618 |  |  | 6644 | Public space |  | 20171026PWA_02 | Infrastructure (network-based) | -38.1751 | 144.5487 | 1 | Powercor | Report | 8329 | 0.037317 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Curlewis | Dug up
On arrival crew carried out repairs | 7 HAROLD COURT, LITTLE RIVER VIC 3211 | 33040949 |  |  |  | Overheated connection |  |  | 1 | Vicfire reported a fire at this address. On arrival the crew found that a fused Overhead line connector box had failed. The falling ash and debris fell to ground without causing a ground fire. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | FNS022 | insufficient remains to accurately determine cause. | Pole-top fire;Loss of supply | 14/10/2017 1:52 | 1 | Negligible: no ground fire | 6651 | Public space |  | 20171030PWA_01 | Infrastructure (network-based) | -37.9634 | 144.5052 | 1 | Powercor | Report | 8337 | 0.024927 | Low voltage AC (<1kV) | Avalon Airport | 3211 | Little River | Connection
On arrival the crew cleared the tree and completed repairs. Boric acid fuse unit replaced | 2 EASY STREET, INVERMAY PARK VIC 3350 | 33005393 |  | Blown branch/vegetation |  | Fuse failed to eject |  |  | 1 | A customer rang to advise a tree had fallen over the line. A crew attended and found a tree had fallen across the high voltage line between P1 and P2 in Taylor court, Invermay, bringing one conductor to the ground. Conductor did not break. (initiating event) This initiated a small ground fire near # 2 Easy street that is attributed to a high voltage fuse mal-operating under the current from the tree contact fault. ( subsequent and primary reportable event) There was no ground fire start at the location of the tree contact. There were no reported shocks or injuries. | Conductor (bare);Boric acid | 2 | 2 | 2 |  | BAN007 | Vegetation: Trees Incident | Loss of supply;Grassfire | 29/10/2017 15:48 | 1 | Localised: less than 10 sq.m | 6655 | Public space |  | 20171031PWA_01 | Infrastructure (network-based) | -37.5258 | 143.866 | 1 | Powercor | Report | 15126 | 0.010699 | 22kV AC | Ballarat Aerodrome | 3350 | Invermay Park | Trees
Attending Jemena crew made area safe. No damage was caused to point of attachment or customer's service line. | 30A ADELAIDE STREET, FOOTSCRAY VIC 3011 | Pole no. A064775 |  |  |  | Fault on customer installation |  |  | 2 | Optus cable fault caused optus cable to come into contact with overhead LV conductor and create a spark. Spark resulted in a small fire at the fence/grass area at residential property (refer to attached photos in "Notes & Findings" section of this report). | Conductor (bare);Communication cable/equipment | 0 | 0 | 0 |  | FE09 | Optus cable came into contact with overhead LV conductor and create a spark which resulted in a small fire. | Grassfire | 29/10/2017 16:40 | 1 | Localised: less than 10 sq.m | 6658 | Residential |  | 20171101JEM_01 | Infrastructure (network-based) | -37.7954 | 144.8874 | 1 | Jemena | Report | 12947 | 0.019994 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Conductor
On arrival crew carried out repairs | 63 BOWLANDS ROAD, LEITCHVILLE VIC 3567 | 32038108 |  | Lightning |  |  |  |  | 1 | Powercor fault crew reported ground fire(s) associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total. There were no reported injuries or 3rd party damage. | Conductor (bare) | 0 | 0 | 0 |  | CHA003 | Lightning strike causing flashover | Grassfire | 24/12/2016 11:59 | 1 | Localised: less than 10 sq.m | 6660 | Roadway |  | 20171102PWA_01 | Infrastructure (network-based) | -35.8124 | 144.2144 | 1 | Powercor | Report | 8413 | 0.016389 | 22kV AC | Swan Hill Aerodrome | 3567 | Leitchville | Lightning
Crew isolated supply and made repairs | 1 SUSAN STREET, IRONBARK VIC 3550 | 33021007 |  | Bird |  | Electrical breakdown |  | Phase to earth |  | CFA reported a grass fire caused by Powercor assets at the incident location. Fault crew had just attended bird flashover @ Wood street when this report was received, after investigation crew found evidence of arcing on a PG clamp at P46 Happy Valley believed to have a high impedance connection which arced when it was subjected to fault current associated with the wood street event, this location being on the same feeder between the terminal station and the fault location. | Conductor (bare) | 0 | 0 | 0 |  | BET002 | Bird Incident | Grassfire | 25/01/2017 17:34 | 1 | Localised: less than 10 sq.m | 6661 |  |  | 20171102PWA_02 | Infrastructure (network-based) | -36.7557 | 144.2609 | 1 | Powercor | Report | 8412 | 0.015293 | 22kV AC | Bendigo Airport | 3550 | Ironbark | Animal
Emergency high voltage switching was completed and the HV strain crossarm replaced under Access Authority conditions after the damaged pole top was cut off. | 22 HUMPHRIES ROAD, MOUNT ELIZA VIC 3930 | 3314196 |  | Precipitation |  | Electrical breakdown |  |  | 2 | Pole fire per emergency services. Following light drizzly rain, a pole fire occurred at the HV strain crossarm at pole No. LIS 3314196 located in Humphries Road, Mount Eliza which is located a short distance away from Port Phillip Bay. The 22kV strain crossarm had polymeric insulators that were most likely tracking that caused the HV crossarm to burn. | Pole (wood);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | FSH 13 | The 22kV strain crossarm had polymeric insulators that were most likely tracking in the light drizzle. | Pole-top fire | 42896.1847 | 1 | Negligible: no ground fire | 6668 | Roadway |  | 20171103UTD_01 | Infrastructure (network-based) | -38.171 | 145.1058 | 1 | United Energy Distribution | Report | 8356 | 0.022328 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Crossarm
White bus fuse was blown and all installations on the affected circuit were inspected by Techsafe inspector for damage. Area isolated for crews to conduct repairs - damage pole was replaced before installations were reconnected. | 38 DEMPSTER STREET, WEST FOOTSCRAY VIC 3012 | A150256 | Vehicle | [5 empty] | 1 | Truck hit pole no. A150256 in front of property. Pole snapped approximated 2 metres from ground and LV crossarm also snapped. HV cable came off insulator and came into contact with LV cables, resulting in a high voltage injection. Numbers 28 and 38 Dempster Street sustained damage to appliances. TechSafe report attached in "Notes & Findings" section. | Conductor (bare);Pole (wood) | 0 | 2 | 0 |  | TH11 | Truck hit pole no. A150256 | HV injection | 42897.3958 |  |  | 6676 | Residential |  | 20171106JEM_02 | Infrastructure (network-based) | -37.8026 | 144.8615 | 1 | Jemena | Report | 8399 | 0.00024884 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3012 | West Footscray | Vehicle
On arrival crew carried out repairs | 15 AVOCAT AVENUE N, RED CLIFFS VIC 3496 | 32141274 |  |  |  | Leakage |  |  |  | Pole fire found on Avocat Sewerage 6. Conductors down in tree, Tree on fire HV And LV crossarms replaced. There was no ground fire, no reported injuries or third party property damage. No photos of incident taken | Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire;Other vegetation | 25/10/2017 3:51 | 1 | Negligible: no ground fire | 6677 |  |  | 20171108PWA_01 | Infrastructure (network-based) | -34.3 | 142.1852 | 1 | Powercor | Report | 15127 | 0.018486 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3496 | Red Cliffs | Trees
The fault location was excavated and cabling repaired | IMMIGRATION MUSEUM, 400-424 FLINDERS STREET, MELBOURNE VIC 3000 | 30313734 | Working too close to underground cables | [5 empty] | 1 | JA5 11kv Feeder tripped to lockout. A patrol of the cable route found a storm water pit was recently constructed over cabling and HV cable damaged had occurred. There was no fire, no injuries or third party property damage. | Cable | 2 | 2 | 2 |  | JA5 | Excavation near underground cable | Loss of supply;Damage to network assets | 30/10/2017 21:03 |  |  | 6680 | Roadway |  | 20171108PWA_02 | Infrastructure (network-based) | -37.8193 | 144.9605 | 1 | CitiPower | Report | 8370 | 0.03222 | 11kV AC | Essendon Airport | 3000 | Melbourne | Dug up
Crew made site safe Attending TechSafe inspector completed a walk through and damage assessment of all accessible installations on Stradishall Way and Lackenheath Drive that were affected and found no evidence of a high voltage injection. The contactor box for street light circuit mounted on the pole in Lackenheath Drive had noticeable signs of smoke and damage. Once linesmen had completed works on the switch wire and street lighting circuit, the TechSafe inspector advised the report room and service crews that the LV circuits were safe to re-energise. | 2 LACKENHEATH DRIVE, TULLAMARINE VIC 3043 |  |  | Wind |  |  |  |  | 2 | LV switch wire came into contact with HV lines due to windy conditions, resulting in loss of supply to about 60 customers. The switch wire was down and there were noticeable signs or arcing to the white phase HV conductor. The TechSafe inspector concluded that a high voltage injection had occurred to the switch wire only and did not affect any installations. TechSafe report is attached in the "Notes & Findings" section. | Conductor (bare) | 2 | 2 | 2 |  | AW14 | Windy conditions were the mostly like cause | Loss of supply | 13/11/2017 14:07 |  |  | 6699 | Residential |  | 20171113JEM_01 | Infrastructure (network-based) | -37.6941 | 144.8817 | 1 | Jemena | Report | 8495 | 0.020524 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Lightning
LEI dispatched. Test found 100V on the earth bar. supply isolated until fault truck called and replaced the service further proceeded to test at internal switchboard - all tests passed: NST â€“ pass Loop - .3ohm PSC 806amps Earth to water pipe .06ohm | 40 MCIVER STREET, FERNTREE GULLY VIC 3156 | 1322374 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 230121 - customer reported dim lights and a tingle off front garden tap. | Neutral screen | 0 | 0 | 0 |  | FGY31 | Supply neutral broke away in neutral screen - neutral fault | Minor shock | 42775.7604 |  |  | 6695 | Residential |  | 20171113SPN_01 | Infrastructure (customer connection) | -37.8957 | 145.29 | 1 | AusNet Services Distribution | Report | 8420 | 0.012837 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Ferntree Gully | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The local DOA & ESV were advised. CFA and police were on site when the DAO arrived on site. The fire was under control and only one section remained alight. The CFA were awaiting the all clear to extinguish the fire as the conductor was on the ground. The fault crew arrived and made the conductor safe. The CFA extinguished the fire and left the site. The fault crew reinstated the SWER conductor, but could not get the remaining works completed as they ran out of hours. The crew returned the next day and restored supply at approximately 13:00. | 1447 LILLIPUT-NORONG ROAD, NORONG VIC 3682 | 5235554 |  | Fallen |  |  |  | Phase to earth | 1 | IMS 231154 - At approximately 19:07 on the 10/11/17, a fire was called in by a customer at Lilliput-Norong Road, Norong. A tree on the customer's property fell over and contacted the overhead SWER line. The fallen tree caused the SWER line to break and fall to the ground resulting in a medium crop fire in the vicinity. MAHONGA ISO ACR reclosed twice and went to lockout. 29 NMI's off supply until approximately 1300 on 12/11/17. CFA on site and extinguished the fire. | Conductor (bare) | 0 | 0 | 0 |  | wn3 | Vegetation: Trees Incident | Loss of supply;Grassfire | 43019.8444 | 1 | Medium: 1000 sq.m - 10 ha | 6703 | Agricultural |  | 20171114SPN_01 | Infrastructure (network-based) | -36.0952 | 146.3253 | 1 | AusNet Services Distribution | Report | 8437 | 0.0002581 | 12.7kV AC (SWER) | Wangaratta Aero | 3682 | Norong | Trees
Crew dispatched to investigate. Likely a pelican flew into live 22kV overhead conductors with its wide wing span causing a 22kV phase to phase flashover that caused 22kV EPG32 CB Feeder trip, with hot molten aluminium metal from the 22kV 3-6/1/.093 ACSR conductors falling on grass starting 2 separate fires, 1 approx 5mx5m, midspan between poles #914097 & 914098 where pelican made conductor contact and another fire approx. 15m x30m around base of pole #914098 that may have been larger due to possible live fallen conductor making contact with a metal fence. photos per attachment. | QUARRY ROAD, EPPING VIC 3076 | 914098 |  | Bird |  | Conductor clashing |  | Phase to earth | 1 | IMS 230893 - pelican hit 22 kv conductor, caused feeding circuit breaker to open, fire in vicinity of pole near dead pelican. | Conductor (bare) | 0 | 0 | 0 |  | EPG32 | Bird Incident | Grassfire | 24/10/2017 10:15 | 1 | Small: 10 - 1000 sq.m | 6707 | Other | quarry hills park | 20171114SPN_02 | Infrastructure (network-based) | -37.6369 | 145.0462 | 1 | AusNet Services Distribution | Report | 8438 | 0.0393 | 22kV AC | Essendon Airport | 3076 | Epping | Animal
The Jemena compliance officer forced work to stop, made the BTS safe and notified Jemena control room of the activities with Work Practices to further follow up of the breach. Supply was not connected to the BTS. Jemena Work Practices notified the builder to remove the BTS and structure and relocate with in the buildings property with the guidance of Jemena No Go Assessor and provide the builder with NGZ report. | 1 DEIDRE COURT, AIRPORT WEST VIC 3042 |  | Building too close or within the No Go Zone | [5 empty] | 2 | BTS pole within 1.3 metres of Low Voltage open wire conductors. BTS structure had no supply, was directly inline with Jemena electricity poles and installed within the easement of Jemena's corridor on the nature strip. | Customer appliance | 2 | 2 | 2 |  |  | The Builder was not compliant with the NGZ guidelines clearances. There was no NGZ permit on Issue to the builder or REC. | No Go Zone (no contact) | 20/11/2017 15:03 |  |  | 6727 |  |  | 20171120JEM_01 | Infrastructure (network-based) | -37.725 | 144.8727 | 2 | Jemena | Report | 8462 | 0.023269 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Airport West | Other
Made safe and replace earth cable | 26 SARAH STREET, CAMPBELLFIELD VIC 3061 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stole copper earth cable from switch pole. | Copper;Earth | 2 | 2 | 2 |  |  | Unknown person(s) stole earth cable from the pole | Damage to network assets | 20/11/2017 11:13 |  |  | 6730 | Industrial |  | 20171120JEM_03 | Infrastructure (network-based) | -37.6711 | 144.9717 | 1 | Jemena | Report | 8466 | 0.0073507 | Earthing cable | Essendon Airport | 3061 | Campbellfield | Other
On arrival crew carried out repairs | 186 FYANS STREET, SOUTH GEELONG VIC 3220 | 32069759 |  | Bird |  | Overheated connection |  |  | 1 | A bird flashover occurred at pole adjacent to 170 fryans st ( Lis 17498) Due to fault current there was a flashover at an isolator pole( Lis 17264) which caused a ground fire due to fallen debris. There were no reported injuries or third party property damage. | Disconnector/isolator | 2 | 2 | 2 |  | GLE033 | Electrical flashover and resultant fault current | Grassfire | 22/11/2017 14:41 | 1 | Localised: less than 10 sq.m | 6749 | Roadway |  | 20171123PWA_01 | Infrastructure (network-based) | -38.1667 | 144.3704 | 1 | Powercor | Report | 8492 | 0.030359 | 22kV AC | Avalon Airport | 3220 | South Geelong | Animal
On arrival crew carried out repairs | 381 CHURCHILL ROAD, YARROWEYAH VIC 3644 | 32185760 |  | Bird |  |  |  |  | 1 | VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on open point switch pole, causing the bird to fall to the ground resulting in a ground fire on road reserve. There were no reported injuries. | Disconnector/isolator | 2 | 2 | 2 |  | CME015 | Bird Incident | Grassfire | 22/11/2017 14:17 | 1 | Small: 10 - 1000 sq.m | 6753 | Roadway |  | 20171123PWA_02 | Infrastructure (network-based) | -35.9555 | 145.5677 | 1 | Powercor | Report | 8496 | 0.030922 | 22kV AC | Shepparton Airport | 3644 | Yarroweyah | Animal
CEOT dispatched a fault crew to make safe, isolate and carry out any necessary repairs. CEOT also notified the local DAO to investigate. An AusNet Services' LEI attended to investigate and check for HVI damage. After investigation the LEI determined it was a suspected HVI due to the burnt Neutral conductor. Crew reconnected supply after the LEI checked the factories for any damage. Closed LV fuses at the substation after crew were given the OK by the LEI. | 211 SETTLEMENT ROAD, THOMASTOWN VIC 3074 | 910963 |  | Wind |  |  |  | Phase to phase | 1 | IMS 231316. TT12 feeder had reclose. Emergency switching operation to remove a cafÃ© umbrella which blew onto adjacent HV line. Possible HV injection occurred. APEX SETTLEMENT Substation - isolated LV for Ausnet Services' LEI to investigate for any property damage to customers' electrical installations. Burn marks were sighted on Neutral. | Conductor (bare) | 0 | 0 | 0 |  | tt12 | An umbrella blew up onto overhead HV line. | HV injection | 21/11/2017 14:55 |  |  | 6754 | Industrial |  | 20171123SPN_02 | Infrastructure (network-based) | -37.6945 | 145.0347 | 1 | AusNet Services Distribution | Report | 8499 | 0.029841 | 22kV AC | Essendon Airport | 3074 | Thomastown | Other
COET dispatched a fault crew to make safe, investigate and carry out any necessary repairs. An Underground crew were requested to trace the underground service cable for 35 Lorimers Lane. CEOT also notified the local DAO to investigate the incident. The Underground crew discovered that the underground service was an old style installation where in fact the customer's underground consumer's mains, being of single insulated building wire enclosed in a conduit, was installed from the premises, across the property boundary to the AusNet Services' pole located in the road reserve. The consumer's mains cables went straight through the pit with no electrical connection at this POS. This supply arrangement is no longer allowed. The old pit was an old earthenware type pit which was buried and a fault in the single insulated cables was found between the service pit and the pole, adjacent to the pit.. The Underground crew installed a new service pit at the property boundary, a new Underground 4 core 16 sq.mm service cable from the pole to the new pit and replaced the damaged SPD (FOLCB) at the pole end with a new SPD fuse unit. Supply was subsequently restored to the customer's premises. | 35 LORIMERS LANE, DIXONS CREEK VIC 3775 | 1007063 |  |  |  | Electrical breakdown |  | Phase to phase | 1 | IMS 231317. A supply fail reported at 35 Lorimers Lane, Dixon Creek. The attending fault crew found a blown LV fuse at the substation transformer, 3rd morning in a row. The crew suspected it was due to electrical overload so they upgraded the LV fuses to 125 Amps. This immediately blew the LV fuse next pole up, LIS 1007063. When the LV fuses blew, there was a grassfire below of an approximate size of 1 square metre. Suspected an underground service cable fault for 35 Lorimers Lane, Dixons Creek. An Underground crew were requested to attend site to trace the underground service cable as the fault crew could not locate the service pit for this premises. Supply left off for this premises. | Cable | 0 | 0 | 0 |  | ldl14 | Underground service cable fault. | Grassfire | 21/11/2017 7:20 | 1 | Localised: less than 10 sq.m | 6755 | Agricultural |  | 20171123SPN_03 | Infrastructure (network-based) | -37.6066 | 145.4127 | 1 | AusNet Services Distribution | Report | 8501 | 0.036487 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Dixons Creek | UG Cable
CEOT dispatched a fault crew to make safe and carry out necessary repairs. CEOT also notified the local DAO. The grass fire was out when the fault crew was on site. The crew IPC'd the street light connection onto an existing XLPE service cable on the same pole and therefore a new service cable for the street light was not required. All hardware associated with the old street light service cable has been removed. | 20 UPPER YARRA DAM ROAD, REEFTON VIC 3799 | 1409238 |  |  |  | Defective component |  | Phase to earth |  | IMS231367. Reported power line down and small grass fire. Fire was approximately 4.5m x 1.8m. The fire self extinguished when the service cable hit the ground. A single phase 2 wire neutral screen service cable burned through at the wrap-on termination at the street light pole end. The service cable only supplied a street light. | Service conductor | 0 | 0 | 0 |  | WYK13 | Street light service cable fell to ground due to burnt through wrap-on preform termination. | Grassfire | 22/11/2017 18:30 | 1 | Localised: less than 10 sq.m | 6756 | Agricultural |  | 20171123SPN_04 | Infrastructure (network-based) | -37.6743 | 145.8604 | 1 | AusNet Services Distribution | Report | 12846 | 8.3333e-05 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3799 | Reefton | OH Cable
CEOT dispatched a fault crew to isolate substation. Also LEI Bill Rounds requested to attend to check properties for any property damages. Supply isolated at the FOLCB at the POA (by pulling fuses). LEI arranged for service crews to replace damaged revenue meters. Customers where issued defects notices (NCIDs) where required and advised to engaged a REC to rectify damage. Customers where issued damage reports where required. Red Phase isolator replaced. | 58-60 MERRILL CRESCENT, WARRANWOOD VIC 3134 | 1208046 |  | Lightning | [5 empty] | IMS 231399. Confirmed injection due to lightning. Revenue meters blank but has power. Power to main switch but CB won't hold. Red Phase ISOL burnt out. AusNet Services' LEI found HVI injection damage on a number of properties. | Disconnector/isolator;Customer installation | 0 | 0 | 0 |  | rwn22 | Lightning strike. | HV injection | 25/11/2017 5:55 |  |  | 6765 | Residential |  | 20171127SPN_01 | Infrastructure (network-based) | -37.7703 | 145.2601 | 1 | AusNet Services Distribution | Report | 8516 | 0.017709 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3134 | Warranwood | Lightning
CEOT dispatched a fault crew to make safe and carry out any necessary repairs. The fault crew attended investigated and took photographs. CEOT also requested the local DAO to investigate the incident. The crew ascertained that no damage was caused to AusNet Services' network assets. The supply was not interrupted. No details on the truck. Crew rolled up Telstra cable to pole to make safe. | 152 ELDER STREET, GREENSBOROUGH VIC 3088 | 928045 | Working too close to overhead lines | [6 empty] | IMS 231318. A truck contacted Telstra assets at this location, pulling them down and flicking them into AusNet Services' overhead LV assets resulting in a LV injection into the Telstra assets. A fire of size 1 sq. metre was reported near a Telstra pit. | Conductor (bare) | 0 | 0 | 1 | Telstra | wt15 | A truck contacted Telstra overhead assets which caused them to make contact with AusNet Services' overhead LV distribution conductors. | Property | 21/11/2017 10:15 | 1 | Localised: less than 10 sq.m | 6767 | Residential |  | 20171127SPN_02 | Infrastructure (network-based) | -37.7167 | 145.0989 | 1 | AusNet Services Distribution | Report | 8519 | 0.0338 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | Vehicle
CTA and faults crew isolated building service feeding vandalised building at 60 Buckhurst St. Nothing could be found in the immediate vicinity of where the woman was found that would explain here receiving an electric shock. | 19 GLADSTONE STREET, SOUTH MELBOURNE VIC 3205 |  | Copper theft | [5 empty] | 2 | MFB reported finding a woman on the footpath with apparent burns to her right forearm. when crew arrived, the woman had been taken by ambulance to an undisclosed hospital. The womanâ€™s name was Helen Hughes. She was reportedly vague about where she received the burn and described it as being received â€˜brushing against somethingâ€™. She was found outside the display suite on the footpath (see photos). She was apparently squatting inside the disused display suite and numerous tools were present in the room she was squatting in. The MFB officers were not convinced of where she actually received the â€˜shockâ€™. How the display suite was originally supplied is not clear and consumerâ€™s mains had been removed. Tests were carried out at various points of the display suite (DB and exposed metallic strapping etc) using an independent earth and no voltage could be detected. The large abandoned building next door had signs of forced entry and the MFB suspected she may have in fact come from that building. CTA and faults crew inspected the building under the escort of the police and found that the building appeared to be in the process of having copper stripped. The building service from the substation had been cut and taped and was still alive (cables were about 4m up in the air and appeared to have been cut some time ago). | Customer installation | 0 | 0 | 0 |  |  | probable interference -attempted copper theft | Medical attention (first aid/doctor/hospital) | 16/10/2017 10:30 |  |  | 6792 | Roadway |  | 20171130PWA_01 | Infrastructure (network-based) | -37.8288 | 144.9521 | 1 | CitiPower | Report | 8551 | 0.0088403 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Other
Crew attended. vegetation management in progress | 380 ERREYS ROAD, COBRICO VIC 3266 | 30305107 |  | Within clearances |  |  |  |  | 1 | Crew patrolling line in response to a feeder outage found vegetation had contacted the line resulting in some singing of the vegetation | Conductor (bare) | 0 | 0 | 0 |  | TRG003 | Vegetation encroachment | Other vegetation | 29/11/2017 13:57 | 1 | Negligible: no ground fire | 6795 | Roadway |  | 20171130PWA_02 | Infrastructure (network-based) | -38.3033 | 142.9942 | 1 | Powercor | Report | 8560 | 0.038947 | 22kV AC | Warrnambool Airport Ndb | 3266 | Cobrico | Trees
Crew attended and replaced LV fused isolator | 83 MILLAWA AVENUE, ST ALBANS VIC 3021 | 31024776 |  |  |  | Overheated connection |  |  | 1 | Vic Fire rang to advise fuse has blown and caused grass fire at the incident location. On arrival the crew found at the cnr of Biggs St and Millawa Ave, St Albans on LIS 8958 red phase LV fused isolator had failed dropping debris on the ground resulting in a grass fire of approx. 2m X 10m on road reserve. A Fire crew attended and extinguished the fire. | Any other type | 0 | 0 | 0 |  | SA005 | Connection failure | Grassfire | 29/11/2017 20:05 | 1 | Small: 10 - 1000 sq.m | 6796 | Roadway |  | 20171130PWA_03 | Infrastructure (network-based) | -37.7378 | 144.8074 | 1 | Powercor | Report | 8562 | 0.0084086 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Fuse
Immediate actions: As advised by Principal Engineer, all ABM Installations for 220kV & 66kV L90 relays powercycled to reset the Seal In function. IMS raised. Discussed with all parties to avoid future similar incidents. ? Teleconference with Principal Engineer PC & A, Commissioning In Charge, Testing Engineer, DSP Design Engineer to discuss the reasons behind the incident and to avoid future occurence of similar incident. Recommendations to prevent recurrence: CBF Supv Alarm to be configured to a spare LED. CT also to be shorted to block current into relay. Powercycle the relay once tested. | 347 MARY STREET, RICHMOND VIC 3121 | [5 empty] | Inappropriate tools/plant/equipment |  |  | IMS 231320. This incident is reported to ESV under "significant disruption to the community occurs". At RTS, on Tuesday 21st November 2017, at 13:23Hrs, New No3 66kV BUS Tripped. A loss of 12MW was reported due to the TRIP incident. No personal Injury occurred. Following FDRs Tripped: 1. SUB FR1 FDR. 2. SUB SK FDR. 3. B3 TRANS. 4. SUB FR No2 FDR. 5. New 2-3 66kV BUS TIE CB. 6. New 3-4 66kV BUS TIE CB. With reference to the Tripping Incident at BTS on 06/06/2017 at 11:42 hours (No.2 220kV Bus tripped by CB Fail Protection of No.2 Transformer Group No.2 Bus CB), Installation of ABM (Active Burden Module) was recommended at RTS by Protection & Control Asset Management in order to avoid such Tripping Incident. At RTS on Tuesday 21st November 2017, while installing and testing of ABMs in 66kV Protection & Control Panel No. G6 - FR3 FDR (New No4 66kV BUS) the following events happened. (SCADA Time): 12:23:43.714 - FR1 Y CBF Trip â€“ ON. 12:23:27.743 â€“ New No3 66kV Bus Y BP Trip â€“ ON. The reason for CBF Trip was analysed after consultation with Principal Engineer PC & A, it was confirmed the CBF settings of GE L90 relay along with the methodology of Testing the CBF function after installation of ABM module caused the Tripping. Informed TOC the reason for tripping and the New No3 66kV BUS was normalised at 12:38:13. Significant contributing factors identified are: â€¢ Relay Settings-CBF Initiate Seal In Function. â€¢ No indication of CBF Supervision pick up. â€¢ Heavy Load on FR1 caused Current Element of relay pick up. â€¢ BF1 â€“ Seal In Function is ON. â€¢ Methodology of Testing CBF function after installing ABMs. The issue associated with the incident that, if corrected, could have prevented the incident from occurring or would have significantly reduced the consequences are: â€¢ If CBF Supervision Pick up LED Indication was available, Tester would have noticed. â€¢ During Installation & Testing of ABM, If current to the relay was blocked before Initiating the CBF function, relay supervision will not pick up. | Terminal substation | 0 | 0 | 0 |  |  | Please see the incident details included in the Incident tab / Description of Event. | Loss of supply | 21/11/2017 13:23 |  |  | 6794 | Other | Terminal Station | 20171130SPN_03 | Infrastructure (network-based) | -37.831 | 145.0004 | 2 | AusNet Services Transmission | Report | 9726 | 0.029015 | 66kV AC | Essendon Airport | 3121 | Richmond | AF Other
Site made safe, security fenced / gate temporary repaired. Earths replaced. | 42 ZAKWELL COURT, COOLAROO VIC 3048 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Unknown person(s) accessed (unauthorsied) the zone substation at Coolaroo via a hole they created. They removed gate lock and stole copper earths from within the switchyard. | Disconnector/isolator;Earth;Zone substation | 2 | 2 | 2 |  | Coolaroo Zone Substation | Unknown person(s) cut hole in security fence / gate and stole copper earths. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 42867.625 |  |  | 6821 | Industrial |  | 20171206JEM_01 | Infrastructure (network-based) | -37.6424 | 144.9337 | 1 | Jemena | Report | 8597 | 0.012242 | Earthing cable | Essendon Airport | 3048 | Coolaroo | Other
CEOT dispatched a fault crew to make safe and carry out any necessary repairs. The local DOA was also dispatched to investigate the incident. The DAO attended the site and found that 1 Phase of the 2 Wire HV line was under height at 4.97m from the ground. The other phase was 7.0 m from the ground. Small scorch marks were observed on the ground near a gravel pile under the HV line believed to be from the truck's tyres. The Downer fault crew arrived on-site to re-string the conductor and place the HV line back into service. | 29 GLENBURNIE AVENUE, HEATHCOTE JUNCTION VIC 3758 | 912280 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 231045. Reports of low overhead HV conductor between poles LIS# 912280 & 929684 allegedly due to being contacted by a Tip Truck dumping gravel on the road reserve (as reported by customers). SW# 881097 had a HV Fuse blown. No details of the tip truck are available. | Conductor (bare) | 0 | 0 | 0 |  | klo14 | Tip truck tray made contact with overhead HV conductor. | No Go Zone (contact) | 42777.5465 |  |  | 6829 | Residential |  | 20171207SPN_01 | Infrastructure (network-based) | -37.3748 | 145.0328 | 1 | AusNet Services Distribution | Report | 8606 | 0.035345 | 22kV AC | Wallan (Kilmore Gap) | 3758 | Heathcote Junction | Vehicle
Crew attended and made safe Referred to worksafe | 993 BURKE ROAD, CAMBERWELL VIC 3124 | 30194930 | Unauthorised work | [5 empty] | 2 | A company employee informed that a live meter is on the ground at the incident location. Upon arrival, a Citipower inspector found that the service wire and the meter on the ground and it was live. The crew made the place safe. WorkSafe informed. | Service conductor;Meter board (including fuses) | 0 | 0 | 0 |  | L014 | Interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42867.4528 |  |  | 6837 | Residential |  | 20171208PWA_01 | Infrastructure (network-based) | -37.823 | 145.0581 | 1 | CitiPower | Report | 8617 | 0.021574 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Other
On arrival crew carried out repairs | 75 NEALIE STREET, CARDROSS VIC 3496 | 33062189 |  |  |  | Unknown technical factor |  |  | 2 | Customer reported a â€œpole fireâ€ and grass fire caused by Powercor assets at the incident location. On arrival the crew found that a FOLCB on a concrete pole had failed and ignited, the molten material falling to the ground and igniting a small area of grass at the base of the pole approximately 3m x 1m in size. CFA attended & extinguished the fire. There were no reported injuries, no 3rd party damage. | Connection box | 2 | 2 | 2 |  | RCT023 | Insufficient remains to determine cause | Grassfire | 43020.4479 | 1 | Localised: less than 10 sq.m | 6844 | Roadway |  | 20171212PWA_01 | Infrastructure (network-based) | -34.3072 | 142.1563 | 1 | Powercor | Report | 8625 | 0.036903 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Cardross | Pole
On arrival crew isolated supply and carried out repairs | 10 FAIRWAY DRIVE, LARA VIC 3212 | 33044395 |  |  |  | Electrical breakdown |  |  |  | The CFA reported a pole had caused grass fire at the incident location. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire around substation pole 2 Fairway Drive (LIS-59510). The roadside lightning arrestor on the pole was broken in half but remained attached to the pole. The roadside HV powder filled fuse had operated and fallen to the ground. The fire, totalling approximately 3m x 5m had been extinguished by the CFA and nearby resident. The Definitive cause of the fire is unknown, however it seems that fallen debris from either the blown powder filled fuse or the broken lightning arrestor may have been the ignition source. Appropriate isolations were made and the site was made safe, the fault was handed to the day time crew for final repairs. 1 customer was left off supply for the remainder of the night. | Powder filled;Surge diverter | 2 | 2 | 2 |  | FNS011 | Surge diverter malfunction | Grassfire | 18/01/2018 23:47 | 1 | Small: 10 - 1000 sq.m | 9062 | Roadway |  | 20180122PWA_03 | Infrastructure (network-based) | -38.0233 | 144.3654 | 1 | Powercor | Report | 10969 | 0.040372 | 22kV AC | Avalon Airport | 3212 | Lara | Fuse
On arrival crew isolated supply and carried out repairs | 107 JACARANDA STREET, RED CLIFFS VIC 3496 | 32140300 |  |  |  | Mechanical breakdown |  |  |  | Customer reported wire down at premise starting a small grass fire. Crew attended and found Black XLPE service mains cable had failed at the Point of Attachment and had fallen onto concrete footpath and scorched ground. There were no reported shocks or injuries or damages. | Service conductor | 2 | 2 | 2 |  | RCT023 | Service cable failed at point of attachment | Grassfire | 19/01/2018 18:49 | 1 | Localised: less than 10 sq.m | 9068 | Roadway |  | 20180122PWA_05 | Infrastructure (network-based) | -34.3127 | 142.1865 | 1 | Powercor | Report | 11567 | 0.03466 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | OH Cable
CEOT dispatched a fault crew to isolate, make safe and carry out/arrange for necessary repairs. As soon as reports of a car was involved, AusNet Services immediately de-energised area. When fault crew arrived isolated and made safe. An AusNet Services' LEI attended and reported there were no signs of HVI damage. | 10 NEVILLE STREET, COCKATOO VIC 3781 | 417268 |  | Fallen |  |  |  |  | 1 | IMS 232090. Initial report: Reports of tree branch on fire @ LIS #417268. On arrival crew found 1 ph of HV open wire on the deck over car. Car was parked with no-one inside. No ground fire. 1X fuse blown @ SW #BG503. Final report: A Large branch failed from a large gum tree approx. 30m high that overhangs all phases of HV and LV conductors (both LV and HV have 3 spans). Decay and discolouration from an old wound was evident at the point of failure that was approx. 9m above the conductors. 902 customers were affected or taken off supply by the incident. The tree was owned and located within private property. | Conductor (bare) | 0 | 0 | 0 |  | BGE22 | Vegetation: Trees Incident | Loss of supply;Other vegetation | 20/01/2018 21:20 | 1 | Negligible: no ground fire | 9058 | Residential |  | 20180122SPN_01 | Infrastructure (network-based) | -37.937 | 145.4888 | 1 | AusNet Services Distribution | Report | 11569 | 0.039664 | 22kV AC | Moorabbin Airport | 3781 | Cockatoo | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions prior to the supply being restored. | 45 WELLINGTON AVENUE, BLACKBURN VIC 3130 | 7037553 |  | Blown branch/vegetation |  | Electrical breakdown |  |  | 1 | At 1456hrs on 19/01/2018, 22kV feeder NW 21 circuit breaker reclosed to lockout affecting 592 customers. A tree branch from a private tree located at 6 Lake Road north/east of LIS No. 7029960 near Wellington Street and fell across the white and blue phase HV overhead conductors. Further faults were caused by fault current as follows: 1. White phase HV conductor on the ground in Central Road at pole No. LIS 7037841 2. White phase ampact connection was burnt off at Railway Road, 1 pole east of George Street at pole No. LIS 7018936 3. Red phase helical termination failed at the polymeric insulator in Almar Street opposite Sandy Street and finally 4. Blue phase ampact connection failure at pole No. LIS 7037553 that was found during the emergency HV switching. Molten metal from the HV clashing in Lake Road near Wellington Street fell into dry grass and leaves next to a paling fence near 45 Wellington Avenue and caused the timber fence to slightly burn that was estimated to be 3m x .03m. Photos are attached showing the slightly damaged fence. | Connector/termination | 0 | 0 | 0 |  | NW 21 | Vegetation: Trees Incident | Grassfire | 19/01/2018 14:56 | 1 | Localised: less than 10 sq.m | 9070 | Roadway |  | 20180122UTD_04 | Infrastructure (network-based) | -37.8239 | 145.1573 | 1 | United Energy Distribution | Report | 12981 | 0.033333 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 24 DEVON STREET, HAMLYN HEIGHTS VIC 3215 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Kathleen Patricia was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metal Shower Rose and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded service conductor | Minor shock | 42989 |  |  | 9080 | Residential |  | 20180123PWA_05 | Infrastructure (network-based) | -38.1156 | 144.3266 | 1 | Powercor | Report | 10998 | 0.020323 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | OH Cable
On arrival crew carried out required repairs | 70 MURRAY STREET, PIANGIL VIC 3597 | 30147267 |  |  |  | Unknown technical factor |  |  |  | Crew attended to find Junction Box had burnt out between Gang Operated LV Switch and customer Underground Mains. R No Ground Fire , No property damage, No injuries, No reported shocks. | Connection box | 2 | 2 | 2 |  | SHL002 | Unable to determine due to damage | Pole-top fire | 14/11/2017 5:11 | 1 | Negligible: no ground fire | 9083 | Agricultural |  | 20180123PWA_07 | Infrastructure (network-based) | -35.0515 | 143.3166 | 1 | Powercor | Report | 11001 | 0.025542 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3597 | Piangil | Connection
The faults crew installed some stinger insulation onto the electrolysis cable to make the site safe. No further follow up action was required following the LV fuse replacement at "FTN DNG-N88 Stephens" substation. | 90A FRANKSTON-DANDENONG ROAD, DANDENONG SOUTH VIC 3175 | 211770 |  |  |  | Conductor clashing |  |  | 1 | Customers supplied from "FTN DNG-N88 Stephens" substation advised of a loss of their electricity supply. The white phase LV conductor attached to pole No. LIS 0635472 located on the corner of Frankston-Dandenong Road near the Dandenong bypass, made contact with the electrolysis cable and clashing occurred with molten metal dropping into the grass below and a small 1sqm fire to start. | Conductor (bare) | 0 | 0 | 0 |  | DSH 32 | The white phase LV conductor made contact with the electrolysis cable and clashing occurred. Due to the type of HV / LV construction on the pole, the electrolysis cable was attached to the LV crossarm. | Grassfire | 22/01/2018 15:27 | 1 | Localised: less than 10 sq.m | 9079 | Roadway |  | 20180123UTD_01 | Infrastructure (network-based) | -38.0088 | 145.2157 | 1 | United Energy Distribution | Report | 12982 | 0.016624 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Conductor
Site made safe and all locks replaced. Supply restored to customer at 09:25 | MARIBYRNONG RIVER BIKE TRAIL, 71-89 HOBSONS ROAD, KENSINGTON VIC 3031 | HOBSONS-SMITHFIELD | Vandalism | [5 empty] | 2 | John from Hacer Group called to advise that Jemena kiosk substation has been broken into and supply has been lost. On arrival, Jemena network operator found both distribution key locks have been cut off. Street circuit fuses and customer circuit fuses found open. No copper or any electrical equipment was damaged or stolen. Incident location is a construction site for high rise apartments. Photos have been attached in the "Notes & Findings" section. | Transformer | 0 | 1 | 0 |  | FT04 | Vandalism | Damage to network assets | 21/01/2018 2:30 |  |  | 9095 | Construction |  | 20180124JEM_01 | Infrastructure (network-based) | -37.7965 | 144.9159 | 1 | Jemena | Report | 11013 | 0.011575 | Not applicable | Essendon Airport | 3031 | Kensington | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB, The attending Powercor Fault Crew replaced the existing Three Phase O/H Aluminium Neutral Screened Service Cable with a new 4 Wire ABC Service Cable and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 5 238 DEAKIN AVENUE, MILDURA VIC 3500 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Carolyn Arbuckle was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic shower taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 24/10/2017 7:30 |  |  | 9088 | Residential |  | 20180124PWA_05 | Infrastructure (customer connection) | -34.1942 | 142.1522 | 1 | Powercor | Report | 11006 | 0.03161 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Connection
On arrival, the ENO assessed the LV switchboard at the indoor substation and identified a 3 phase fuse failure on the LV street circuit. The ENO made the LV street circuit safe, isolated supply and contacted the Jemena control room to dispatch JEN underground crew to test the LV circuit and make repairs to damaged underground cable. The underground fault crew attended the site at approximately 18:00. They identified the path of JEN easement and applied their test equipiment to the LV street circuit to trace the source of failure. It was identified that the fault was right under the retaining wall post which has been installed on top of Jemena HV and LV assets, with fresh concrete in the hole where the post was installed to rest. The crew then excavated and exposed the damaged LV underground circuit, made repairs to the underground cable and restored the customer's power supply. The Works Practices teams also attended the location for a follow-up on the incident. ESV was informed via phone, reference number 9163718 | 48 BOX FOREST ROAD, GLENROY VIC 3046 |  | Working too close to underground cables | [5 empty] | 2 | Jemena electrical network operator (ENO) was dispatched to Box Forrest - Yooralla indoor distribution substation (located at Ilim College, 45-50 Box Forest Road, Glenroy) to attend to the customer's complaint of loss of power supply to the school. It was found that a fencing contractor engaged by the school to construct works over JEN easement, had crushed concrete cover slab which in turn impacted Jemena LV underground cable. Photos have been attached in the "Notes and Findings" section. For more information, please contact Nick Mateski of Jemena Works Practices on 0417339536 | Cable | 0 | 0 | 0 |  | PV24 | No Go Zone infringement Factors identified by the Works Practices initial attendance on site: â€¢ The work party did not have No Go Zone VESI Permit â€¢ Damage to the underground cable was made by excavating the post hole with pick attachment to the boom and lifted without any knowledge or awareness â€¢ The fencing contractor may have tried to cover up or repair the damage by using duct tape without knowledge of the high electric shock risk. As per the description provided by the underground faults crew who attended the repairs, evidence was not quarantined. â€¢ The work party had failed to comply with Safe Approach Distances | No Go Zone (contact) | 23/01/2018 15:20 |  |  | 9101 | Commercial |  | 20180125JEM_01 | Infrastructure (network-based) | -37.704 | 144.9565 | 1 | Jemena | Report | 11520 | 0.029279 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3046 | Glenroy | Dug up
On arrival crew carried out repairs | 34 CASTRO WAY, DERRIMUT VIC 3030 | 30244799 | Copper theft | [6 empty] | Upon attendance, the Powercor crew noted that a HV earth forming part of a 22kV cable head termination had been cut and stolen. The earth appeared to have been cut with an axe at ground line. The earth appeared to have been cut high up on the pole behind the HV cable trifurcation point. (approx. 7m above ground.) There were no reported injuries. There were no reports of ground fire. | Earth/earthing | 2 | 2 | 2 |  | SU013 | Copper theft | Damage to network assets | 24/11/2017 17:11 |  |  | 9108 | Roadway |  | 20180125PWA_03 | Infrastructure (network-based) | -37.7914 | 144.7751 | 1 | Powercor | Report | 11029 | 0.028455 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply and carried out repairs | 29A ADELAIDE STREET, ARMADALE VIC 3143 | 30166035 | Working too close to overhead lines | [6 empty] | A gardener has advised she accidentally cut the service wire while trimming the hedges at the incident location. Upon arrival, the crew found that service wire was clean cut. There was no fir, no reported injuries or other damage. | Service conductor | 2 | 2 | 2 |  | AR003 | Service cut during hedge trimming | Loss of supply;Damage to network assets | 23/11/2017 15:46 |  |  | 9110 |  |  | 20180125PWA_05 | Infrastructure (network-based) | -37.8536 | 145.0282 | 1 | CitiPower | Report | 11031 | 0.028775 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | Other
The attending LEI identified Overhead neutral Screened Service and customer F.O.L.C.B to be badly deteriorated and unserviceable. Jemena lines crew re-serviced the property and left the site safe and disconnected. A defect was issued to the customer for replacement of customer owned F.O.L.C.B. The installation was left OFF supply. | 2 KIATA COURT, COOLAROO VIC 3048 |  |  |  |  | Fault on customer installation |  |  | 2 | Customer received an electric shock whilst making simultaneous contact with the metallic taps in his shower and wet floor. | Customer installation | 2 | 2 | 2 |  |  | The attending LEI identified Overhead neutral Screened Service and customer F.O.L.C.B to be badly deteriorated and unserviceable. | Minor shock | 27/01/2018 15:02 |  |  | 9120 | Residential |  | 20180128JEM_02 | Infrastructure (network-based) | -37.6579 | 144.9309 | 1 | Jemena | Report | 11041 | 0.030287 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Coolaroo | OH Cable
On arrival crew cut back vegetation and inspected assets for damage. | 129 CURRELLS ROAD, PORT CAMPBELL VIC 3269 | 30045051 |  | Within clearances | [5 empty] | The CFA reported a grass fire which had possibly started due to vegetation contact at the incident location. A crew was dispatched to investigate. On arrival crew observed 10x 6 mtr of road reserve had been burnt, this was extinguished prior to their arrival. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG003 | Vegetation contact with conductors | Grassfire | 28/01/2018 14:24 | 1 | Small: 10 - 1000 sq.m | 9125 |  |  | 20180129PWA_01 | Infrastructure (network-based) | -38.603 | 143.0163 | 1 | Powercor | Report | 11053 | 0.021644 | 22kV AC | Warrnambool Airport Ndb | 3269 | Port Campbell | Trees
On arrival crew isolated supply and carried out repairs. | 512 ERRARD STREET S, BALLARAT CENTRAL VIC 3350 | 30013213 | Working too close to overhead lines | [6 empty] | A customer reported that the tip truck had contacted the service cable at the incident location. On arrival the crew found that a contractor ( DMH Sand and Soil â€“ Ph 03 5335 8353 ) had been operating an tipper and contacted a LV service cable causing damage to the cable. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | BAS013 | Tip truck hit service while unloading soil | Loss of supply;Damage to network assets | 42837.3986 |  |  | 9135 | Roadway |  | 20180129PWA_06 | Infrastructure (network-based) | -37.5726 | 143.8467 | 1 | Powercor | Report | 11061 | 0.036725 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat Central | Vehicle
CEOT dispatched a fault crew to isolate, make safe and repair. Supply isolated and made safe. CEOT also notified the local DAO to investigate the incident. ESV notified. HV insulator replaced and HV conductor reattached. Pole-tops and conductors each side of incident pole checked for damage. All OK and supply restored same day. | 201 YABBA ROAD, TALLANGATTA EAST VIC 3700 | 5211158 |  |  |  | Insulator |  | Phase to earth | 1 | IMS 232160. Under INCD-163546-r @ LIS #5211158 HV insulator broken, conductor sagged to ground. Fire in the vicinity of approximately 575 sq.m in size. ACR tripped to lockout. | Insulators | 0 | 0 | 0 |  | wots24 | Broken HV insulator. | Grassfire | 28/01/2018 13:05 | 1 | Small: 10 - 1000 sq.m | 9122 | Agricultural |  | 20180129SPN_01 | Infrastructure (network-based) | -36.2218 | 147.2584 | 1 | AusNet Services Distribution | Report | 11600 | 0.034294 | 22kV AC | Wangaratta Aero | 3700 | Tallangatta East | AF Other
On arrival crew isolated supply and carried out repairs | 31 BENNETT ROAD, HORSHAM VIC 3400 | 32090515 | Working too close to overhead lines | [6 empty] | A council worker reported the service wire to a house had been struck by a backhoe and hanging low at the incident location. On arrival the crew found that a backhoe being driven by a council worker had struck the service cable above the nature strip, causing it to break in the middle and fall to the ground. There was no reported fire, third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | HSM010 | Backhoe operations | Loss of supply;Damage to network assets | 13/12/2017 8:24 |  |  | 9145 | Roadway |  | 20180130PWA_05 | Infrastructure (network-based) | -36.7225 | 142.1872 | 1 | Powercor | Report | 11075 | 0.014738 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Vehicle
On arrival crew isolated supply and carried out repairs | 34 BENTLEY STREET, WILLIAMSTOWN NORTH VIC 3016 | 30113429 | Vehicle | [6 empty] | Powercor was contacted by a customer indicating loss of supply at their address on Thursday 14/12/2017 at 16:20 hrs. The customer also indicated that there was a broken wire on the ground and another hanging low in the air outside their premise. The 4c x 25 overhead service cable had been sliced into two pieces and the ends were on the ground. There were no reported injuries. There were no reports of ground fire. | Service conductor | 2 | 2 | 2 |  | BLT030 | Appears truck mounted cran hit o/h service conductor | Loss of supply;Damage to network assets | 14/12/2017 16:20 |  |  | 9147 | Roadway |  | 20180130PWA_07 | Infrastructure (network-based) | -37.8505 | 144.8604 | 1 | Powercor | Report | 11077 | 0.030094 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown North | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. The crew attended and found a pole box melted @ lis#2809269 and a 2m x 2m grass fire at the base of the pole. CEOT also advised the local DAO to investigate. ESV called. Repairs carried out by fault crew. | 430 KOETSVELDT ROAD, RYANSTON VIC 3992 | 2809269 |  |  |  | Overheated connection |  |  |  | IMS232174. Customer reported to CEOT that they had dropped a phase. A pole mounted FOLCB caught fire with the molten plastic falling to the ground causing a 4 sq.metre area burnt at the base of the pole. | Connection box | 0 | 0 | 0 |  | WGI22 | Pole mounted FOLCB caught fire. High impedance fault. | Grassfire | 29/01/2018 5:35 | 1 | Localised: less than 10 sq.m | 9137 | Agricultural |  | 20180130SPN_01 | Infrastructure (network-based) | -38.508 | 145.5922 | 1 | AusNet Services Distribution | Report | 12854 | 0.040756 | Low voltage AC (<1kV) | Moorabbin Airport | 3992 | Ryanston | Connection
CEOT dispatched a fault crew to isolate, make safe and repair. CEOT also notified the local DAO to investigate. The fault crew made the site safe, replaced 2 off 12k BA fuses and restored supply to customers. The BA fuses did not drop out which caused the CB to trip. | 910 PRINCES HIGHWAY, NICHOLSON VIC 3882 | 1611151 |  | Bird |  |  |  | Phase to earth |  | IMS 232190. BDL6 22kV CB tripped and Reclosed. Reports of no power in Nicholson Court by customers. Reports of a fire in the area. Attending fault crew found a burnt bird at the base of the pole. A small burnt out area at the base of the pole in the pigface plant. Fire was approximately 3m x 0.5m in size plus a few other very small burnt areas. Total burnt area about 3 sq. metres. | Boric acid | 0 | 0 | 0 |  | bdl6 | Bird Incident | Grassfire | 30/01/2018 1:42 | 1 | Localised: less than 10 sq.m | 9140 | Residential |  | 20180130SPN_03 | Infrastructure (network-based) | -37.8173 | 147.7373 | 1 | AusNet Services Distribution | Report | 11070 | 0.025009 | 22kV AC | Bairnsdale Airport | 3882 | Nicholson | Animal
Voltage tests detected a voltage rise of 230 Volts between the metallic gutter and the metallic step ladder. Subsequent tests detected a 230 Volt rise between the raiser bracket, metallic guttering and an independent earth. The service anchor was found to have cut into the active conductor of the service cable at the poa dog bone bracket. Powercor linesman replaced the service & the service bracket and the CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 7 HAKEA COURT, WERRIBEE VIC 3030 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Sue received an electric shock when she simultaneously contacted the metallic gutter with one hand and the metal step ladder with the other hand. | Service conductor | 2 | 2 | 2 |  |  | The service anchor was found to have cut into the active conductor of the service cable at the poa dog bone bracket. | Minor shock | 27/11/2017 9:30 |  |  | 9158 | Residential |  | 20180131PWA_05 | Infrastructure (network-based) | -37.8891 | 144.6661 | 1 | Powercor | Report | 11089 | 0.012773 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | AF Other
A LEI and faults truck attended and completed voltage tests between an independent earth and the water tap along with the neutral bar at the main switchboard and recorded a voltage of 36v under load. The connections were checked by the faults crew at the POA and pole ends that revealed a severely corroded copper neutral screen at the pole end. The defective copper neutral screen service was replaced with a XLPE type and supply restored after installation tests confirmed the fault had been rectified. | 62 AINTREE ROAD, GLEN IRIS VIC 3146 | 2316683 |  | Heat |  | Electrical breakdown |  | Phase to earth | 2 | Owner of the property received a shock from the taps and called a REC and his boss contacted United Energy. The REC believed the neighbour has the same issue but cannot confirm. The occupier received electric shocks from the rear garden water taps and contacted a REC to investigate the cause. The REC completed installation tests and believed the issue is from the street and contacted the United Energy faults and emergencies call centre. | Service conductor;Copper;Neutral screen | 0 | 0 | 0 |  |  | Defective copper neutral screened service. | Minor shock | 29/01/2018 13:00 |  |  | 9166 | Residential |  | 20180131UTD_01 | Infrastructure (network-based) | -37.8544 | 145.0444 | 1 | United Energy Distribution | Report | 11097 | 0.0078403 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | OH Cable
Fault truck remade neutral connection at pole end CTA re-tested property, all required VESI tests passed | 581 SYDNEY ROAD, BRUNSWICK VIC 3056 |  |  |  |  | Corrosion |  | Phase to earth |  | Lucas was connecting a gas cooking appliance when he received an electric shock when he made simultaneous contact between the metallic cooking appliance with one hand and the metallic gas pipe with his other hand. | Service conductor | 2 | 2 | 2 |  |  | corroded neutral connection | Minor shock | 19/12/2017 11:30 |  |  | 9178 | Residential |  | 20180201PWA_02 | Infrastructure (network-based) | -37.7635 | 144.9626 | 1 | CitiPower | Report | 11111 | 0.0027465 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
Crew advised the service cable was coiled on the pole ready to be connected (at a future date) but unfortunately was stolen last night. | 21 WARBURTON ROAD, CAMBERWELL VIC 3124 |  | Copper theft | [6 empty] | Resident reported vandalism and stolen wires on a pole outside the above incident location. On arrival, the crew found that the underground copper service cable from pole LIS 12009 to service pit adjacent to 18 Warburton Road, Camberwell, had been stolen. The police have been notified of the thefts. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Services cable | 2 | 2 | 2 |  |  | Copper theft | Damage to network assets | 26/12/2017 8:13 |  |  | 9181 | Roadway |  | 20180201PWA_04 | Infrastructure (network-based) | -37.826 | 145.0709 | 1 | CitiPower | Report | 11114 | 0.012381 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole, The attending Powercor Fault Crew re-terminated the existing O/H Service Cable at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 399 WILTONS ROAD, MEPUNGA WEST VIC 3277 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Troy Anderson (Plumbing Contractor) was repairing a Bore Pump when he received an electric shock as he made simultaneous contact between one hand on the metallic Bore Pump Motor and the other hand on the metal frame of an adjacent Water Tank. | Service conductor | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 19/12/2017 13:00 |  |  | 9190 | Agricultural |  | 20180201PWA_10 | Infrastructure (network-based) | -38.4291 | 142.6647 | 1 | Powercor | Report | 11123 | 0.032925 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3277 | Mepunga West | Connection
CEOT dispatched a fault crew to isolate, make safe and arrange for repairs. The fault crew found a street light head had caught fire. The supply to light was isolated and site made safe. The faulty street light lantern was replaced. | 25 MAGID DRIVE, NARRE WARREN VIC 3805 | 593824 |  |  |  | Electrical breakdown |  |  | 2 | IMS 231963. CEOT received a report of a street light fire. A 150 Watt HPS lantern over heated due to internal capacitor and starter (ignitor) fault. Fire confined to lantern itself. | Public lighting | 0 | 0 | 0 |  | hpk12 | HPS street lantern head caught fire due to faulty capacitor. | Other electricity related | 13/12/2017 21:46 | 1 | Negligible: no ground fire | 9191 | Public space |  | 20180201SPN_01 | Infrastructure (network-based) | -38.0183 | 145.2999 | 1 | AusNet Services Distribution | Report | 12815 | 0.032566 | Low voltage AC (<1kV) | Moorabbin Airport | 3805 | Narre Warren | AF Other
A LEI and faults truck attended and initial tests indicated a voltage of 2 volts between an independent earth to the shower taps as well as the customers earthing system. Further tests had the NST passing and network analyses showing no abnormal results, even when a larger load was introduced. Further investigation and inspection by the fault crew at the POA and pole ends identified a corroded neutral connection at the pole end to the overhead reticulation. The faults crew proceeded to replace the single phase grey twisted service with a ZLPE type and the LEI completed installation tests that confirmed the fault had been rectified. | 2 SINCLAIR AVENUE, RYE VIC 3941 | 1301685 |  | Heat |  | Corrosion;Neutral fault |  | Phase to earth | 2 | REC is reporting an electric shock was received from the shower taps for the past week. The REC believes there is a problem in the street and the customer has stopped using the two showers. The occupiers received electric shocks to their hands as they made simultaneous contact with the shower taps while standing on the wet shower base and contacted a REC to investigate the cause. The REC completed installation tests and believed the issue is with the reticulation and contacted the United Energy faults and emergencies call centre. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | Faulty pole end neutral connection. The pole is located in close proximity to Port Phillip Bay may have been a contributing factor. | Minor shock | 25/01/2018 14:30 |  |  | 9179 | Residential |  | 20180201UTD_01 | Infrastructure (network-based) | -38.3736 | 144.8206 | 1 | United Energy Distribution | Report | 11112 | 0.0058981 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | Rye | Connection
Emergency LV switching was completed and the damaged LV pillar replaced by a Zinfra underground faults crew. Supply was restored to the area after LV fuses were replaced at "Stradbroke-Ascot" substation. | 46 ASCOT DRIVE, NOBLE PARK NORTH VIC 3174 | 8809817 (Closest) |  | Heat |  | Overheated connection |  |  | 1 | Per MFB - Pole fire. During warm conditions, a LV pillar located on the corner of 44 and 46 Ascot Drive caught fire and damaged a small portion of the timber fence that separates the two properties. The cause was attributed to a loose connection that overheated which caused internal dry grass and debris to catch on fire. | LV Pillar | 0 | 0 | 0 |  |  | The cause was attributed to a loose connection that overheated which caused internal dry grass and debris to catch on fire. | Property | 26/01/2018 4:27 | 1 | Localised: less than 10 sq.m | 9185 | Residential |  | 20180201UTD_03 | Infrastructure (network-based) | -37.9403 | 145.1874 | 1 | United Energy Distribution | Report | 12986 | 0.037185 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park North | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. Crew temporarily bridged out LV isolator on the White phase. Construction crew required to replace the Krone box (FSD). | 32 VICTORIA STREET, RINGWOOD EAST VIC 3135 | 1217471 |  |  |  | Overheated connection |  |  | 2 | IMS 232095 - Fire brigade reported pole fire. Fault crew found a burnt out White phase fuse isolator (FSD). Parts of LV isolator found on the ground. No ground fire started. | Any other type;Disconnector/isolator | 0 | 0 | 0 |  | rwt32 | Burnt out LV FSD Krone box. | Loss of supply;Plant/equipment | 21/01/2018 22:46 | 1 | Negligible: no ground fire | 9197 | Residential |  | 20180202SPN_01 | Infrastructure (network-based) | -37.814 | 145.2542 | 1 | AusNet Services Distribution | Report | 11131 | 0.030924 | Low voltage AC (<1kV) | Moorabbin Airport | 3135 | Ringwood East | Fuse
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the â€˜Simpy Crimpâ€™ adjacent to the FOLCB located at the Customerâ€™s POA, The attending Powercor Fault Crew replaced the Simpy Crimp and re-terminated the existing O/H Service Cable at the Customerâ€™s POA and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1 BAILEY STREET, CALIFORNIA GULLY VIC 3556 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Jenifer Sharpe was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact between one hand on the kitchen tap and the other hand on the metal sink. | Service conductor | 2 | 2 | 2 |  |  | loose connection | Minor shock | 20/12/2017 12:00 |  |  | 9201 | Residential |  | 20180205PWA_03 | Infrastructure (customer connection) | -36.7342 | 144.2502 | 1 | Powercor | Report | 11135 | 7.1759e-05 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | California Gully | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole, The attending Powercor Fault Crew replaced the existing O/H Service Cable from the Pole Top Connection Box to the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 6 BAKER STREET, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Ali Shambrook was in the rear yard operating the External Garden Tap when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the wet lawn. | Service conductor;Connection box | 2 | 2 | 2 |  |  | loose connection | Minor shock | 27/12/2017 17:30 |  |  | 9204 | Residential |  | 20180205PWA_06 | Infrastructure (network-based) | -38.2696 | 144.5148 | 1 | Powercor | Report | 11138 | 0.037347 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
On arrival crew inspected HV for damage and organised repairs | 1 PERTOBE ROAD, WARRNAMBOOL VIC 3280 | 32197532 | Blown detritus | Wind |  |  |  |  | 1 | Report received from customers that a gazebo had blown onto the wires outside Caravan Park, causing sparks. Upon arrival the fault crew found that a lightweight gazebo had in fact been swept up by the wind and blown into the HV line causing the HV line outage. There were no injuries, HVI or fire. | Conductor (bare) | 2 | 2 | 2 |  | WBL008 | Wind blew Gazebo onto line | Damage to network assets | 43435.5215 |  |  | 9218 | Commercial |  | 20180205PWA_19 | Infrastructure (network-based) | -38.3962 | 142.4724 | 1 | Powercor | Report | 11508 | 0.0024711 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Other
fault crew attended and confirmed fault was caused by tracking on the insulators. Pole and insulators changed. no fire on the ground. | METROPOLITAN RING ROAD, FAWKNER VIC 3060 | 5642607 |  |  |  | Leakage |  |  | 1 | IMS 231993 - pole fire reported on a subtransmission pole on the Metropolitan Ring Road. | Pole (wood);Insulators | 0 | 2 | 0 |  | SMTS-KMS 66kV | insulator tracking | Pole-top fire | 43435.6847 | 1 | Negligible: no ground fire | 9224 | Roadway |  | 20180205SPN_01 | Infrastructure (network-based) | -37.6918 | 144.9605 | 1 | AusNet Services Distribution | Report | 12852 | 0.034387 | 66kV AC | Essendon Airport | 3060 | Fawkner | AF Other
The HV intermediate cross arm was replaced under glove and barrier techniques. | 125-135 ROOKS ROAD, NUNAWADING VIC 3131 | 7031360 |  | Precipitation |  | Leakage |  |  | 2 | Caller reports there is a broken cross arm after a pole fire. The insulator is hanging and it requires urgent attention. Following light drizzly rain after a dry spell, a HV cross arm fire occurred on a HV/LV tee-off pole (LIS No. 7031360) located outside 125 Rooks Road, Nunawading on the corner of Beech Street. | Crossarm (wood) | 0 | 0 | 0 |  | RWT 24 | The HV insulators were an older brown fog type that may have tracked at the time of the pole fire after a spell of warm weather. | Pole-top fire | 30/01/2018 8:40 | 1 | Negligible: no ground fire | 9223 | Residential |  | 20180205UTD_04 | Infrastructure (network-based) | -37.8305 | 145.1871 | 1 | United Energy Distribution | Report | 11626 | 0.033582 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Crossarm
On arrival crew isolated supply and carried out repairs. | 116 HUTCHINS LANE, KOTUPNA VIC 3638 | 32193175 |  | Fallen;MEC |  |  |  |  | 1 | Vicfire reported grassfire started by a HV conductor falling to within private property, emergency services on site. Upon arrival crew found that the fire had been extinguished and that the CFA were still onsite. It was observed that a branch had struck the conductor, bringing it to ground igniting a grass fire. There was no private property damage sustained , no injuries, no reported shocks. | Conductor (bare) | 2 | 2 | 2 |  | KYM004 | vegetation limb striking conductor | Grassfire | 43161.5007 | 1 | Medium: 1000 sq.m - 10 ha | 9225 | Agricultural |  | 20180206PWA_01 | Infrastructure (network-based) | -36.1298 | 145.0425 | 1 | Powercor | Report | 11160 | 0.039235 | 22kV AC | Shepparton Airport | 3638 | Kotupna | Trees
Crew attended to make safe, damaged public light pole removed. low voltage supply isolated. | 8 SEPARATION STREET, NORTH GEELONG VIC 3215 | 35210470 | Vehicle | [6 empty] | mergency Services Victoria reported that a large truck had collided with a public light pole at the incident location. On arrival the fault crew found that a truck carrying a load of live chickens had lost control and brought down a public light pole in Separation St, Geelong North near the bridge. A number of chickens had escaped their pens and were running around on the road causing traffic chaos. Police, MFB, Channel 10 and SES in attendance. There was no ground fire and no injury as a result of this incident. Reported due to Media interest. | Pole (steel) | 2 | 2 | 2 |  |  | Truck incident | Significant disruption to the community;Damage to network assets | 15/01/2018 12:00 |  |  | 9234 | Roadway |  | 20180208PWA_01 | Infrastructure (network-based) | -38.1116 | 144.3515 | 1 | Powercor | Report | 11170 | 0.031317 | Low voltage AC (<1kV) | Avalon Airport | 3215 | North Geelong | Vehicle
On arrival the fault crew found that the live cable on the truck and damaged to the network assets Crew isolated supply and carried out repairs | 13-15 BRIGHTON STREET, RICHMOND VIC 3121 | 30188911 | Vehicle | [6 empty] | Mike from MFB reported a truck has reversed into a pole, wires down and broken cross arm at the incident location. On arrival the fault crew found that the live cable on the truck and damaged to the network assets. There were no injuries or fire. | Pole (wood) | 2 | 2 | 2 |  | R024 | Truck hit pole | Loss of supply;Damage to network assets | 17/01/2018 12:06 |  |  | 9239 | Roadway |  | 20180208PWA_06 | Infrastructure (network-based) | -37.8266 | 145.0003 | 1 | CitiPower | Report | 11176 | 0.018905 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Vehicle
CEOT dispatched a fault crew to the area and found the driver of the truck which struck the pole was no longer on site. The fault crew was then instructed to make the area safe. After making the area safe the crew waited on site for the truck to be safely removed from the site. The crew then replaced the pole and restored supply. | 623 PRINCES HIGHWAY, MONTGOMERY VIC 3851 | 2503929 | Vehicle |  |  |  |  | Phase to earth | 1 | IMS 232309. A truck hit a pole, lis 2503929, carrying 22kV conductors. The conductors fell on the truck and the line tripped off from the SLE32 CB. The truck had left site before the fault crew arrived, truck/driver details unknown and not available | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  | SLE32 | Truck contacted an AusNet Services pole located on the road reserve. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43283.2257 |  |  | 9243 | Agricultural |  | 20180208SPN_02 | Infrastructure (network-based) | -38.0565 | 147.0682 | 1 | AusNet Services Distribution | Report | 11640 | 0.0066273 | 22kV AC | Bairnsdale Airport | 3851 | Montgomery | Vehicle
CEOT DISPATCHED A FAULT CREW TO ISOLATE, MAKE SAFE AND INVESTIGATE. CREW MADE SAFE AND SUPPLY TO MACHINARY ISOLATED. Crew arrived on-site to find sprinkler had come in contact with 22kV overhead conductor - it appears the sprinkler struck the outer phase conductor and dragged the phase onto the centre phase causing line to trip Crew measured the conductor height and confirmed it was 6.75 metres off the ground where sprinkler struck (note sprinkler pivot /A frame that made contact was 6.7 metre). Weather was quite warm, 37 degrees C and when crew arrived the temperature had drop reducing sag. This sprinkler has been travelling this path for 10 years with no known incidents. The crew re-sagged the span making clearance to ground where the sprinkler contacted it to 8.6 metres based recommended sag as per plan. Note Span is 300 metres long of 3/12 steel 3 phase. | 287B LITTLE PLAIN ROAD, VALENCIA CREEK VIC 3860 | 2513344 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232326. FARMING WATERING MACHINE HAS COME IN CONTACT WITH HV LINE BETWEEN 2513346 AND 2513344. | Conductor (bare) | 0 | 0 | 0 |  | mfa21 | FARM IRRIGATION MACHINE CONTACTED OVERHEAD HV LINE. | No Go Zone (contact) | 43283.6576 |  |  | 9246 | Agricultural |  | 20180208SPN_04 | Infrastructure (network-based) | -37.8083 | 146.9577 | 1 | AusNet Services Distribution | Report | 11187 | 0.018872 | 22kV AC | Bairnsdale Airport | 3860 | Valencia Creek | Vehicle
On arrival crew inspected assets - No damage sustained | 72 BAMAWM ROAD, BAMAWM EXTENSION VIC 3564 | 33084014 |  | Bird |  |  |  |  | 1 | Emergency services reported grass fire possibly started by Powercor assets, requested Powercor attend. Upon arrival crew found that there had been a flashover on the t-off arm on P153 BAMAWM RD LIS-28004. Crew recovered remains of bird from the arm. The bird had flashed across the 5 shed bridging insulator on the t-off arm. No damage to private assets or Powercor assets was sustained. | Conductor (bare);Crossarm (steel);Insulators | 2 | 2 | 2 |  | ECA012 | Bird Incident | Grassfire | 43283.9431 | 1 | Small: 10 - 1000 sq.m | 9248 | Roadway |  | 20180209PWA_01 | Infrastructure (network-based) | -36.2061 | 144.6169 | 1 | Powercor | Report | 11190 | 0.0043461 | 22kV AC | Bendigo Airport | 3564 | Bamawm Extension | Animal
The incident was caused due to a break in the insulation of the 2 wire twisted grey service termination clamp (dog bone) at the POA house end. The internal metal of the hook in the dog bone had penetrated the active conductor of the service, which in turn had the raiser bracket live at 245 Volts. Suspect damage to dog bone caused by recent council pruning of large trees above and around the service at the front of the house. CTA/LEI instructed fault crew to check the 2 wire twisted grey service termination at the POA on the house. Dog bone insulation was broken and the internal metal of the hook in the dog bone had penetrated the active conductor of the service. Crew removed the existing service and replaced with new 2 wire ABC. They performed NST of the new O/H service with pass result recorded. | 23 WAVERLEY AVENUE, LORNE VIC 3232 |  |  |  |  | Corrosion |  | Phase to earth |  | Robin was standing on an aluminium ladder cleaning the roof guttering of the house. He received a serious shock when holding onto the service raiser bracket of the house with his left hand and his right hand came in contact with the metal roof guttering of the house. His weight pulled the gutter forward which touched the raiser bracket, causing a large flash, and released him from contact with the bracket and gutter and he fell approximately a metre to the ground. | Service conductor | 2 | 2 | 2 |  |  | Vegetation: Trees Incident | Medical attention (first aid/doctor/hospital) | 22/12/2017 10:30 |  |  | 9255 | Residential |  | 20180209PWA_08 | Infrastructure (network-based) | -38.5327 | 143.9726 | 1 | Powercor | Report | 11197 | 0.0049248 | Low voltage AC (<1kV) | Avalon Airport | 3232 | Lorne | Trees
On arrival crew isolated supply and carried out repairs. | 1359 DOHERTYS ROAD, MOUNT COTTRELL VIC 3024 | 31022976 | Copper theft | [6 empty] | Upon attendance, the Powercor crew noted that the LV earth appeared to have been cut and stolen from the substation assembly. There was no fire or reported injuries | Earth/earthing | 2 | 2 | 2 |  | LV002 | Copper theft | Damage to network assets | 25/01/2018 23:25 |  |  | 9257 | Roadway |  | 20180209PWA_10 | Infrastructure (network-based) | -37.8153 | 144.6548 | 1 | Powercor | Report | 11199 | 0.022339 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
Site made safe and fuses replaced. Jemena re-strained white phase conductor to clear access in driveway. Jemena vegetation management contractor has liaised with local council to trim the tree branch. The Council Arborist has also been advised that there are several trees in Grange and Oak Streets that are within the clearance space. The Council Arborist (Mick Miggiani â€“ Moonee Valley) has committed to inspecting and taking action on these trees. | 32 GRANGE ROAD, AIRPORT WEST VIC 3042 |  |  | Within clearances |  | Conductor clashing |  |  | 2 | Council tree branches (fast growing juvenile eucalypts) rubbing through LV conductor and windy conditions caused conductor clashing, which subsequently resulted in the LV conductor hanging at a severely reduced clearance and running through council tree branches. This prevented entry and exit of vehicles from driveway and loss of supply to customer. | Conductor (bare) | 0 | 0 | 0 |  | AW07 | Vegetation: Trees Incident | Loss of supply | 43375.6521 |  |  | 9260 | Roadway |  | 20180210JEM_01 | Infrastructure (network-based) | -37.7314 | 144.8838 | 1 | Jemena | Report | 12014 | 0.02444 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Airport West | Conductor
Upon arrival at the site, the crew identified that the building was partly demolished, the overhead service supply was of the hook from the building attachment and the fused overhead line connection box (FOLCB) was severely damaged. Jemena crew did not find any customers or personnel on site. Jemena crew had made the property safe by disconnecting and removing the overhead service line and leaving the smart meter in the customer meter box. | 6 DUNN STREET, BROADMEADOWS VIC 3047 |  | Working too close to overhead lines;Unauthorised work | [5 empty] | 2 | Excavator at demolition site clipped LV service and pulled down service line (See TE 160330). | Service conductor | 0 | 0 | 0 |  | BMS23 | Excavator clipped and pulled down service line during demolition works. This customer had lodged an abolishment request to Jemena. The initial date booked for abolishment was 16th Feb 2018 (Jemena reference ID: 000072954). | No Go Zone (contact) | 43436.3896 |  |  | 9279 | Residential |  | 20180212JEM_03 | Infrastructure (network-based) | -37.6927 | 144.9188 | 1 | Jemena | Report | 11224 | 0.026353 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Vehicle
n arrival crew isolated supply to allow customers REC to carry out repairs. | 64 WHITTAKERS LANE, RIDDELLS CREEK VIC 3431 | 32046597 |  |  |  | Fault on customer installation |  |  |  | Customer reported an LV service is down over the roadway due to a private pole failing at the incident location. On arrival the crew found that a wood private pole had failed at ground level, pole was heavily rotted at ground level and was supporting a service approximately 35m in length across the roadway. There was no fire or reported injuries. | Service conductor | 2 | 2 | 2 |  | GSB012 | Customer private pole failed | Loss of supply | 43406.6743 |  |  | 9276 | Roadway |  | 20180212PWA_05 | Infrastructure (network-based) | -37.456 | 144.6737 | 1 | Powercor | Report | 11221 | 0.034134 | Low voltage AC (<1kV) | Melbourne Airport | 3431 | Riddells Creek | Pole
On arrival crew isolated supply and commenced repairs. LEI arranged to check for HVI | 17 MURCHISON STREET, TARADALE VIC 3447 | 30035668 |  | Wind;Fallen | [5 empty] | SES reports, HV wire down tree fell on conductor, #17 MURCHISON ST â€“ TARADALE VIC,3447 Upon arrival crew found that a tree had fallen between P25 and P26 ( bringing the boundary side HV phase over the LV. There was suspected HVI to a number of installations. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CMN001 | WInd storm | HV injection;Loss of supply;Damage to network assets | 43375.6889 |  |  | 9288 | Roadway |  | 20180214PWA_03 | Infrastructure (network-based) | -37.14 | 144.3493 | 1 | Powercor | Report | 11674 | 0.011272 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3447 | Taradale | Trees
On arrival crew carried out repairs | 74 BELVOIR PARK ROAD, RAVENSWOOD VIC 3453 | 32014982 |  |  |  | Leakage |  |  |  | A customer reported sparking at top of pole behind their house. Upon arrival @21:30:00 crew found that a BA fuse had candled on the T/Pole at the incident location. There was no ground fire, no injuries or third party property damage. | Boric acid | 2 | 2 | 2 |  | BET004 | Unable to determine | Pole-top fire;Loss of supply;Hung-up fuse only | 13/02/2018 20:43 | 1 | Negligible: no ground fire | 9290 | Agricultural |  | 20180214PWA_05 | Infrastructure (network-based) | -36.8565 | 144.1998 | 1 | Powercor | Report | 11280 | 0.0092512 | 22kV AC | Bendigo Airport | 3453 | Ravenswood | Fuse
LEI Enzo Toressan 0417 108 361 on 14/02/2018 @ 18:09. LEI advised that he attended No. 47 and inspected everything and everything seemed to be OK. He spoke to the factory workers at No. 47 and was not sure if they received a shock, he advised that he will be preparing an Electrical incident Report for the reported shock. He also attended No. 52-58 across the road and everything also appeared to be OK. On arrival crew inspected assets repaired damage to HV bridge. | UNIT 1 63-69 PIPE ROAD, LAVERTON NORTH VIC 3026 | 32174820 | Blown detritus | Wind |  |  |  |  | 1 | The customer/owner at No. 47 Pipe Rd, Laverton North on 14/02/2018 @ 15:23 has advised:- KARATONGA UNIT TRUST, workmen on roof next door have dropped insulation onto wires causing power outage in street . Upon arrival the PCA Operator has advised that workers working on the roof of No.63-69 Pipe Rd, Laverton North (west of No. 47 Pipe Rd next door) have stripped back the existing roof, sheeted lengths of tin and sisalation paper, and the resultant wind has dragged the sisalation paper off the roof and towards into the HV OH Line to the east, around the proximity of LIS-12493, this has resulted in a fault on SU034 feeder CB. Subsequently due to this fault the HV Tee-Off bridges at Pole LIS-12446-7728 Pipe Rd cnr Raymond Rd have burnt off. Workers at 47 Pipe Rd felt tingles through the factory floor - no one hurt but some workers have headaches - factory is International Skin and Hides - Pat # 0433 888 120 | Conductor (bare) | 2 | 2 | 2 |  | SU034 | Workers adjacent to HV removing sisalation which was caught by wind | Loss of supply;No Go Zone (contact) | 14/02/2018 15:23 |  |  | 9308 | Industrial |  | 20180215PWA_05 | Infrastructure (network-based) | -37.8239 | 144.8075 | 1 | Powercor | Report | 11684 | 0.025002 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Other
The crew made the site safe, and replaced the crossarm. | 1901 PORTLAND-NELSON ROAD, GORAE WEST VIC 3305 | 32129434 |  |  |  | Leakage |  |  |  | The CFA reported a grass fire at the incident location. On arrival the crew found that a crossarm had caught fire which also resulted in a ground fire at the incident location. The ground fire was spread across approximately 1.5 acres. Damage was reported to the grassland only, no injury was reported. | Crossarm (wood) | 2 | 2 | 2 |  | PLD003 | Excessive leakage current | Grassfire | 15/02/2018 13:15 | 1 | Medium: 1000 sq.m - 10 ha | 9313 |  |  | 20180216PWA_02 | Infrastructure (network-based) | -38.2322 | 141.4497 | 1 | Powercor | Report | 11309 | 0.021725 | 22kV AC | Portland (Cashmore Airport) | 3305 | Gorae West | Crossarm
Crew attended and replaced FOLCB, | TORGANNAH ROAD, KOONOOMOO VIC 3644 | 32181198 |  |  |  | Overheated connection |  |  |  | CFA reported a grass fire near Powercor assets at the incident location. On arrival the crew found that a LV fuse unit overheated, dropping burning materials to the ground and igniting a grass fire around the base of the substation pole, approximately 10 metres square was burnt. | Any other type | 0 | 0 | 0 |  | NKA005 | overheated connection | Grassfire | 17/02/2018 17:22 | 1 | Localised: less than 10 sq.m | 9333 | Agricultural |  | 20180220PWA_02 | Infrastructure (network-based) | -35.8634 | 145.5872 | 1 | Powercor | Report | 11333 | 0.036286 | Low voltage AC (<1kV) | Shepparton Airport | 3644 | Koonoomoo | Fuse
Crew attended and made safe Call centre operator called to follow up condition, after discussion call centre operator called ambulance to take Mr Davies for a precautionary assessment at hospital. | CEMETARY ROAD W, PARKVILLE VIC 3054 | 30205090 |  | Within clearances |  |  |  |  | 2 | CitiPower received a message form a member of the public who advised he had been hit by an overhead conductor. The pedestrian, Stephen Davies, mentioned the cable was hit by a tree branch, which created some sparks, then broke the conductor which hit heâ€™s upper arm/tricep and resulted in some pain and tingling in heâ€™s fingers. The attending CitiPower Faults crew found the open wire Neutral conductor between on the corner of College Crescent and Cemetery Rd had come away from LIS-81327 and was on the ground. The neutral conductor was not found to be in contact with any of the active phases on arrival. | Conductor (bare) | 0 | 0 | 0 |  | VM030 | Vegetation contact with overhead line resulted in clashing | Medical attention (first aid/doctor/hospital) | 19/02/2018 17:40 |  |  | 9335 | Public space |  | 20180220PWA_04 | Infrastructure (network-based) | -37.7916 | 144.9611 | 1 | CitiPower | Report | 12872 | 0.038612 | Low voltage AC (<1kV) | Essendon Airport | 3054 | Parkville | Trees
On arrival crew made site safe and inspected pole connections. No damage identified, no items repaired or replaced. | 45 DUNKELD-CAVENDISH ROAD, DUNKELD VIC 3294 | 33058547 |  |  |  | Unknown technical factor |  |  |  | The CFA reported a grass fire at the incident location. On arrival the crew found that a grass fire (10x10m) had been extinguished by the CFA. Fire started at the base of the pole, flash marks observed on the LV cross arm bracket and service attachment. No damage, no injuries were reported. | Pole (concrete) | 2 | 2 | 2 |  | HTN005 | No cause found | Grassfire | 20/02/2018 23:48 | 1 | Small: 10 - 1000 sq.m | 9340 | Agricultural |  | 20180221PWA_02 | Infrastructure (network-based) | -37.654 | 142.3065 | 1 | Powercor | Report | 11802 | 0.040267 | 22kV AC | Hamilton Airport | 3294 | Dunkeld | Crossarm
CEOT dispatched a fault crew to make safe, isolate supply, investigate and carry out/arrange for necessary repairs. The fire was reported to emergency services. Crew isolated electricity supply and made safe and carried out necessary repairs restoring conductors. | 86 KILLARA ROAD, COLDSTREAM VIC 3770 | 1009667 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 232489. Initial Report: INCD-165602-r. Tree brought HV down and caused 50m x 15m ground fire. Final Report: Tree branch fell over and lowered High Voltage conductor close to ground. Caused 50 x 15m fire. Tree report - tree outside of clear space - extremely strong easterly wind gust has caused a limb to fail out of a Candlebark gum (E. rubida). The limb has caught on the line and subsequent contact has caused foliage to ignite with the embers falling to the ground starting a small grass fire. Report from attending DAO: Electrical Network representatives attended site at 11.05am on 20/02/2018 & spoke with lady owner who advised that a strong easterly wind blew in on the evening of 19/02/2018 causing a large limb from a gum tree to break away & fall over overhead 22kV 1Ã¸ 3/12 Steel Conductor. Visible burn marks on O/H conductor were observed and it is alleged that the branch has hit both O/H conductors. Customer stated that the conductors did not break but were hanging very low causing arcing between the conductors, tree branch & very dry grass which caused a fire. The fire spread in a westerly to north westerly direction. Fire size approximately 50mx15m. Tree had been removed & conductors were back in the air at time of site visit. The fire site was approximately 25% inside the span between BIDPO 1009667 & BIDPO 1009668. Fire was on the 25% side of BIDPO 1009667. Electrical protection operated - 2 x 25 E HV fuses operated. | Conductor (bare) | 0 | 0 | 0 |  | ldl23 | Vegetation: Trees Incident | Grassfire | 19/02/2018 19:00 | 1 | Small: 10 - 1000 sq.m | 9337 | Agricultural |  | 20180221SPN_01 | Infrastructure (network-based) | -37.7236 | 145.4038 | 1 | AusNet Services Distribution | Report | 11340 | 0.0038715 | 22kV AC | Moorabbin Airport | 3770 | Coldstream | Trees
The section was isolated to conduct repairs, the crew replaced the section of overhead conductor from the underground termination to the mains including the connectors as the entire section of conductor had melted due to the hot connection. | 59-61 TRADE PLACE, COBURG NORTH VIC 3058 | 10050522 |  |  |  | Overheated connection |  |  | 2 | A hot connection between the dropper and underground cable termination (North side phase on pole A066643) resulted in molten conductor from the cable head contacting the grass below igniting an approximate 30sq metre grass fire below. Operator and Lineworker attended site after fire had been extinguished. | Aluminium;Dropper/bridge | 0 | 0 | 0 |  | CN2 | The fault was due to a hot connection between the dropper and underground cable termination. As a result molten conductor from the cable head contacted the grass below igniting an approximate 30sq metre grass fire below. See attached pictures. | Grassfire | 22/02/2018 13:12 | 1 | Small: 10 - 1000 sq.m | 9346 | Industrial |  | 20180222JEM_02 | Infrastructure (network-based) | -37.7242 | 144.9692 | 1 | Jemena | Report | 11670 | 0.0009838 | 22kV AC | Essendon Airport | 3058 | Coburg North | Conductor
On arrival the crew made the site safe, and the HV fuse was replaced. | 679 GLENELG HIGHWAY, SMYTHES CREEK VIC 3351 | 33000200 |  |  |  | Candled fuse |  |  |  | A number of customers reported voltage issues beyond P1 Bells Road, Smythes Creek. On arrival the crew found a HV boric acid fuse had hung up and burnt through. This caused a ground fire in two spots of approximately 1m square and 2m square. Damage was reported to the grassland only, no injury was reported. | Boric acid | 2 | 2 | 2 |  | BAS021 | corroded fuse | Grassfire | 22/02/2018 9:56 | 1 | Localised: less than 10 sq.m | 9351 | Roadway |  | 20180223PWA_04 | Infrastructure (network-based) | -37.5971 | 143.7686 | 1 | Powercor | Report | 11360 | 0.036133 | 22kV AC | Ballarat Aerodrome | 3351 | Smythes Creek | Fuse
On arrival crew isolated supply and carried out repairs. | 144 WESTBOURNE GROVE, NORTHCOTE VIC 3070 | 30186813 |  |  |  | Overheated connection |  |  |  | MFB reported pole fire at the above incident location. On arrival, the crew found that a LV fuse switch disconnect unit had overheated and melted. There were no reported shockâ€™s, injuries, fire or damaged to third party as a result of this incident. | Disconnector/isolator | 2 | 2 | 2 |  | NC001 | Corrossion | Melting or smoking only | 43283.8833 |  |  | 9355 | Roadway |  | 20180223PWA_07 | Infrastructure (network-based) | -37.7746 | 144.9972 | 1 | CitiPower | Report | 11364 | 0.02651 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Fuse
Crew isolated the pole in the pit and carried out repairs. | 25 CURTIS AVENUE, SUNBURY VIC 3429 |  | Vehicle | [6 empty] | Zinfra crew have found a pole (A137134) has been knocked over by a vehicle. Crew could hear the arcing and upon investigation found that the pole was alive. TE# 160921 | Public lighting | 0 | 0 | 0 |  |  | A pole (A137134) was knocked over by a vehicle. No details of vehicle were available. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/02/2018 11:00 |  |  | 9361 |  |  | 20180226JEM_01 | Infrastructure (network-based) | -37.5753 | 144.7477 | 1 | Jemena | Report | 11370 | 0.031185 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Vehicle
On arrival crew isolated supply. Due to damage to the customerâ€™s POA the crew removed the service and issued a defect notice. | 83 TANNER STREET, BREAKWATER VIC 3219 | 30076735 | Vehicle | [6 empty] | A customer reported that a truck has torn down an insulated service at the incident location. On arrival the fault crew found that a large truck has snagged and pulled down the service at the incident location, the driver had remained in his vehicle due to concerns the vehicle maybe â€œALIVEâ€. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  | GLE021 | Truck struck service line. | Loss of supply;Damage to network assets | 14/02/2018 13:30 |  |  | 9380 | Roadway |  | 20180226PWA_06 | Infrastructure (network-based) | -38.1863 | 144.3688 | 1 | Powercor | Report | 11398 | 0.026326 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Breakwater | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. The crew made safe, isolated and carried out repairs. Supply restored. | 90 JUPITER BOULEVARD, VENUS BAY VIC 3956 | 2804943 |  |  |  | Overheated connection |  |  | 2 | IMS 232547. Attending fault crew reported a fused mains box (FOLCB) on pole caught fire. Melted plastic fell to the ground. COET advised that a small ground fire of size 1 sq. metre occurred at the base of the pole. The crew advised it was the AusNet FOLCB that caused the fire however it was burnt to the point of no recognition to determine what the cause may have been. It is considered to be a high impedance connection issue resulting in a overheated connection. | Any other type;Connection box | 0 | 0 | 0 |  | wgi14 | The root cause not determined but considered to be an overheated connection at FOLCB. | Grassfire | 23/02/2018 21:57 | 1 | Localised: less than 10 sq.m | 9366 | Residential |  | 20180226SPN_02 | Infrastructure (network-based) | -38.7041 | 145.8193 | 1 | AusNet Services Distribution | Report | 12830 | 0.013074 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3956 | Venus Bay | Fuse
On arrival crew carried out asset inspection and arranged for insulator replacement | 385 SHEPPARTON-ZEERUST ROAD, ZEERUST VIC 3634 | 33093573 |  | Bird | [5 empty] | Vic Fire reported grass fire at base of pole 84. On arrival the crew found evidence of a flashover on a 22kV insulator that has had damage to one of the sheds on the insulator which will need to be replaced. Crew found a â€œraven or crowâ€ at base of pole that was burnt along with approx. 100m x 5m of burnt grass in road reserve. Also a small amount of damage was noticed on the fence adjacent to the road reserve. No shock or injuries. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | SHN011 | Bird Incident | Grassfire | 29/01/2018 15:30 | 1 | Small: 10 - 1000 sq.m | 9149 | Roadway |  | 20180130PWA_08 | Infrastructure (network-based) | -36.292 | 145.3993 | 1 | Powercor | Report | 15129 | 0.00030671 | 22kV AC | Shepparton Airport | 3634 | Zeerust | Animal
Initial Report: CEOT dispatched a fault crew to make safe, investigate and repair. CEOT also dispatched an AusNet Services' LEI to attend to investigate customers' premises for damages. A HVI was confirmed by the attending LEI. PENTLOWE IRELAND substation. Neutral tail burnt off at substation. Crew replaced neutral lead at transformer. Final Report by attending AusNet Services' LEI: LEI was called to attend site after customer reported appliances exploding and smoking. LEI attended site 5.30 am on 29-01-18. Substation was still energised. LEI tested switchboard at no. 51 Ireland Ave. Results: active to independent earth - 402 Volts. LEI proceeded to isolate properties and isolate LV fuses at substation. LEI proceeded to isolate all properties on the circuit (approx. 70 properties). The fault crew found a corroded neutral cable at substation. The fault crew replaced the neutral cable and re-energised substation. Each property was then tested and returned to supply. Damage reports were compiled for all affected properties. | 62 IRELAND AVENUE, WANTIRNA SOUTH VIC 3152 | 1218438 |  |  |  | Corrosion;Overheated connection |  |  |  | IMS 232179. Initial Report: Various customers reporting high volts, smell of smoke inside, and appliances not working. Final Report: The high volts on the customers' electrical installations was caused by a corroded neutral cable at the substation. | Pole mounted | 0 | 0 | 0 |  | bra11 | Burnt off neutral cable at the substation. | HV injection | 28/01/2018 21:28 |  |  | 9138 | Residential |  | 20180130SPN_02 | Infrastructure (network-based) | -37.8586 | 145.2498 | 1 | AusNet Services Distribution | Report | 11068 | 0.014735 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna South | AF Other
The damaged Optus cable was made safe and the faults crew replaced a damaged meter at 65 Dunlavin Avenue. A LEI investigated the amount of damage that occurred to customers appliances and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | PAGE STREET, MITCHAM VIC 3132 |  |  | Lightning |  | HV injection |  |  | 1 | The customer heard a very loud explosion in the street and found there is a cable down in front of the premise. Customers supplied from "Dunlavin-Page" substation advised they have lost their electricity supply. Lightning struck an Optus cable and burnt it down. A voltage was sent through the Optus cable strand and a number of fuses cartridges at the consumers POA operated as a result. Customers who reside in Page Street and Knightsbridge Avenue advised of possible appliance damage and the faults crew requested that a LEI attend to investigate as a HVI was suspected. The LEI confirmed a high voltage injection occurred (BWD 1703) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Communication cable/equipment | 0 | 0 | 0 |  |  | Lightning struck an Optus communication cable and caused damage to customers appliances as the steel strand is bonded to the United Energy neutral conductor. | HV injection | 29/01/2018 21:00 |  |  | 9141 | Roadway |  | 20180130UTD_01 | Infrastructure (network-based) | -37.8141 | 145.1857 | 1 | United Energy Distribution | Report | 11071 | 0.018887 | Low voltage AC (<1kV) | Moorabbin Airport | 3132 | Mitcham | Lightning
On arrival crew isolated supply and carried out repairs | 94 WESTLAKE DRIVE, MELTON WEST VIC 3337 | 34031832 |  |  |  | Unknown technical factor |  |  |  | Customer reported a fire incident at an LV pillar in front of No. 94 Westlake Drive Melton 3337. The fire brigade was called and attended to the fire. There were no reported injuries. There was no ground fire. | LV Pillar | 2 | 2 | 2 |  | MLN022 | overheated connection | Plant/equipment | 29/01/2018 19:45 | 1 | Negligible: no ground fire | 9155 | Roadway |  | 20180131PWA_02 | Infrastructure (network-based) | -37.6757 | 144.544 | 1 | Powercor | Report | 11085 | 0.040909 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Connection
Crew Isolated supply and made repairs to damaged cable after visual inspection individual cores re-insulated and outer insulation re-sealed. Supply restored. | 30 CHURCH STREET, NHILL VIC 3418 | 33052036 | Working too close to underground cables | [6 empty] | LSA Rural Energy attended and found a Grampians Water crew had damaged LV 16x4mm Underground Cable conduit at the front of property 30 Church st Nhill Vic 3418, LSA . No Fire, No damage or shocks reported. | Cable | 2 | 2 | 2 |  | NHL016 | Excavations | No Go Zone (contact);Damage to network assets | 15/12/2017 16:20 |  |  | 9160 | Roadway |  | 20180131PWA_06 | Infrastructure (network-based) | -36.3372 | 141.6432 | 1 | Powercor | Report | 11091 | 0.021617 | Low voltage AC (<1kV) | Horsham Aerodrome | 3418 | Nhill | Dug up
he crew excavated the conduit (after area made safe) and confirmed that it was a spare conduit with no cable inside. Repairs were made to the damaged conduit. | UNIT 501 30 THERRY STREET, MELBOURNE VIC 3000 |  | Working too close to underground cables | [6 empty] | A contractor reported that they have bored into a conduit at the incident location. On arrival the fault crew found that a hydro-bore being used to complete works for the Metro tunnel project had drilled through a conduit at the incident location. There was no ground fire and no injury as a result of this incident. | Conduit;Other | 2 | 2 | 2 |  |  | Excavation works | No Go Zone (contact);Damage to network assets | 14/12/2017 13:10 |  |  | 9161 | Roadway |  | 20180131PWA_07 | Infrastructure (network-based) | -37.8072 | 144.9598 | 1 | CitiPower | Report | 11092 | 0.028892 | Not applicable | Essendon Airport | 3000 | Melbourne | Dug up
The crew referred the site for follow-up to re-install the stolen service. | 9 LANGSHAW STREET, ALTONA NORTH VIC 3025 |  | Copper theft | [6 empty] | Nicky, a developer for a residential site at 9 Langshaw St Altona North contacted Powercor at 14:55 hrs on 18/12/2017 to advise that personnel on the site had discovered that a newly installed LV service cable to an LV pit outside No. 9 had been stolen. The FOLCB above the cable head had not yet been connected to the bare overhead LV conductors because the customerâ€™s electrician had not yet installed the customer LV Mains into the LV pit. | Services cable | 2 | 2 | 2 |  |  | Copper theft | Damage to network assets | 18/12/2017 14:55 |  |  | 9171 | Roadway |  | 20180131PWA_11 | Infrastructure (network-based) | -37.8262 | 144.8477 | 1 | Powercor | Report | 11102 | 0.037693 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
Crew replaced cable terminations | 31-43 BRIDGE STREET, DRYSDALE VIC 3222 | 34021526 |  |  |  | Electrical breakdown;Electrical overload;Not built/maintained to design | Poor workmanship |  | 1 | Cable fault in zone substation resulted in prolonged supply outage to about 30,000 customers across Bellarine peninsula | Conductor (insulated) | 0 | 0 | 0 |  | DDL | Installation weather and location | Loss of supply;Significant disruption to the community | 28/01/2018 18:31 |  |  | 9174 | Other | Zone substation | 20180131PWA_14 | Infrastructure (network-based) | -38.1831 | 144.5636 | 1 | Powercor | Report | 11107 | 0.02689 | 22kV AC | Avalon Airport | 3222 | Drysdale | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Reticulation Neutral Bridge termination located at the Reticulation Pole, The attending Powercor Fault Crew re-terminated the existing O/H Reticulation Neutral Bridge at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 108 NOBLE STREET, ANGLESEA VIC 3230 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Larry Wilson was showering at the External Shower when he received an electric shock as he made simultaneous contact between one hand on the metallic Shower Tap and his bare feet while standing on the wet concrete pad. | Dropper/bridge | 2 | 2 | 2 |  |  | Loose connection | Minor shock | 43101.625 |  |  | 9202 | Residential |  | 20180205PWA_04 | Infrastructure (network-based) | -38.4149 | 144.1729 | 1 | Powercor | Report | 11136 | 0.0052743 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole, The attending Powercor Fault Crew replaced the Pole Type Connection Box and the existing O/H Neutral Screen Service Cable and with a Twisted ABC Service Cable which was connected directly to the distribution mains and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 10 REGINALD GROVE, WARRNAMBOOL VIC 3280 |  |  |  |  | Corrosion |  | Phase to earth |  | Mrs Mary Bagg was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare arm while leaning on the metallic Kitchen Sink. | Service conductor;Connection box | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 29/12/2017 0:00 |  |  | 9209 | Residential |  | 20180205PWA_11 | Infrastructure (network-based) | -38.3847 | 142.5228 | 1 | Powercor | Report | 11143 | 0.010554 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew removed service pending repairs by property owner. | 25 HOTHAM STREET, ROCHESTER VIC 3561 |  | Vehicle | [6 empty] | Customer reported that overhead service to property was low and could be reached from ground. On arrival the crew found that a unknown vehicle had struck a 2 core LV service cable crossing driveway to #25 Hotham Street, damage to customer POA and dog-bones damaged on both ends of the service. There were no reported injuries, no ground fire. | Service conductor | 2 | 2 | 2 |  |  | Unknown vehicle struck service | Damage to network assets | 13/01/2018 10:46 |  |  | 9214 |  |  | 20180205PWA_16 | Infrastructure (network-based) | -36.3584 | 144.6863 | 1 | Powercor | Report | 11148 | 0.030716 | Low voltage AC (<1kV) | Bendigo Airport | 3561 | Rochester | Vehicle
On arrival crew made site safe | 293 CAMBERWELL ROAD, CAMBERWELL VIC 3124 | 33110625 | Unauthorised work | [6 empty] | A contractor informed a wall knock down on to the substation at the incident location. Upon arrival, the Citipower crew found that the demolition site wall knock down on to ground type substation boundary wall. The sub wall, door and vents have been damaged. There were no injuries or fire. | Indoor | 2 | 2 | 2 |  | CL014 | Demolition works adjacent to substation | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43435.5139 |  |  | 9216 | Construction |  | 20180205PWA_18 | Infrastructure (network-based) | -37.8327 | 145.0586 | 1 | CitiPower | Report | 11150 | 0.01972 | 11kV AC | Moorabbin Airport | 3124 | Camberwell | Other
Supply was isolated and made safe at the pole in Tusanne Place and the LV fuses were replaced at "Daws-George" substation restoring supply to customers supplied on the south circuit. The 2 x three phase underground service cables were re-terminated and supply restored later that evening. | 3 DAWS ROAD, DONCASTER EAST VIC 3109 | 7063276 |  | Heat |  | Electrical overload;Overheated connection |  |  | 1 | Customers supplied from "Daws-George" substation advised of a loss of their electricity supply. During hot and windy conditions, a pole mounted FOLCB with underground cables connected at pole No. LIS 7063276 located in Tusanne Place caught on fire due to probable overload. This caused the LV 315 amp red and white LV fuses on the south circuit of "Daws-George" substation to operate. The cause was probable overload during the very hot conditions. | Connection box | 0 | 0 | 0 |  |  | The cause was probable overload during the very hot weather conditions. | Pole-top fire | 28/01/2018 19:05 | 1 | Negligible: no ground fire | 9221 | Residential |  | 20180205UTD_03 | Infrastructure (network-based) | -37.7827 | 145.1543 | 1 | United Energy Distribution | Report | 12989 | 0.019315 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Connection
On arrival crew isolated supply and carried out repairs | 98-100 COBURNS ROAD, MELTON SOUTH VIC 3338 | 30103225 | Vehicle | [6 empty] | A customer advised garbage truck hit service and no power at the incident location. Upon arrival the Powercor crew found that the live LV service cable had been pulled down over the dive way by the garbage truck. The POA was damaged and a circuit fuse blown. There were no injuries, fire or other damage. | Service conductor | 2 | 2 | 2 |  | MNL024 | Garbage truck struck service | Loss of supply;Damage to network assets | 22/01/2018 12:20 |  |  | 9247 | Roadway |  | 20180208PWA_10 | Infrastructure (network-based) | -37.6931 | 144.5668 | 1 | Powercor | Report | 11188 | 0.031273 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Vehicle
CEOT dispatched a fault crew to make safe, investigate and repair. Crew replaced the LV isolator. | 58 SHERWOOD DRIVE, THOMASTOWN VIC 3074 | 907631 |  |  |  | Overheated connection |  |  |  | IMS 232327. Fault crew attended substation fault and found a burnt out LV isolator - also sighted some burnt grass at base of pole. It is suspected a LV white phase Isolator failed with hot molten metal igniting an approx .2m x .2m small grass fire on the nature strip at the base of pole #907631. The local DAO could not see any private property damage resulting from the small fire except for some very minor burnt nature strip. | Disconnector/isolator | 0 | 0 | 0 |  | tt6 | Failed / burnt out LV isolator on pole. | Grassfire | 43283.8271 | 1 | Localised: less than 10 sq.m | 9244 | Residential |  | 20180208SPN_03 | Infrastructure (network-based) | -37.6832 | 144.9874 | 1 | AusNet Services Distribution | Report | 11185 | 0.01449 | Low voltage AC (<1kV) | Essendon Airport | 3074 | Thomastown | AF Other
On arrival crew isolated supply and carried out repairs. Defect notice issued to customer | 547 KATANDRA MAIN ROAD, KATANDRA WEST VIC 3634 | 31027814 | Working too close to underground cables | [6 empty] | Crew attended and found customer mains damaged, isolated supply and issued a defect on customers mains to have REC attend. Crew found Powercor LV Underground supply at the Pole # 5 Opie should signs of being overheated and made repairs and conduit was deteriorated. There was no fire or reported injuries | Services cable | 2 | 2 | 2 |  | SHN024 | Customer excavation | Loss of supply | 21/01/2018 9:47 |  |  | 9249 | Agricultural |  | 20180209PWA_02 | Infrastructure (network-based) | -36.2388 | 145.5519 | 1 | Powercor | Report | 11191 | 0.022704 | Low voltage AC (<1kV) | Shepparton Airport | 3634 | Katandra West | UG Cable
On arrival crew isolated supply and carried out repairs. | 13 KATHERINE DRIVE, RAVENHALL VIC 3023 | 30304013 |  |  |  | Overheated connection |  |  |  | Customer reported smoke coming from main fuse board at the incident location. A crew attended and found an overheated low voltage fuse holder on the customer board had melted There were no reported shocks or injuries. | Any other type | 2 | 2 | 2 |  | SU015 | Overheated connection | Melting or smoking only | 25/01/2018 7:45 |  |  | 9256 | Residential |  | 20180209PWA_09 | Infrastructure (customer connection) | -37.7644 | 144.7443 | 1 | Powercor | Report | 12093 | 0.016409 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Ravenhall | Connection
On arrival crew isolated supply and carried out repairs A defect notice was issues for the customer to have an REC make repairs to mains box and POA. | 91 GREY STREET, DARLEY VIC 3340 | 33075794 | Working too close to overhead lines | [6 empty] | Customer reported a truck unloading skip bin has pulled down a service wire at the incident location. The truck has left site. A crew attended and found the service to the premises had been broken and was laying on the ground. No protection operated. There were no reported shocks, injuries or fire start. | Service conductor | 2 | 2 | 2 |  | BMH004 | Unloading skip | No Go Zone (contact) | 25/01/2018 11:53 |  |  | 9258 | Residential |  | 20180209PWA_11 | Infrastructure (network-based) | -37.6576 | 144.4261 | 1 | Powercor | Report | 11200 | 0.0020914 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Darley | Vehicle
Jemena crew made property safe by disconnecting and removing the 16mm2 4 core underground service cable supply connection to the fused mains box on the cross arm and removed the service supplying the site (see attached photo). | 33 DEVON ROAD, PASCOE VALE VIC 3044 |  | Unauthorised work | [5 empty] | 2 | Builder began demolishing property before service to property was disconnected. Initial date booked for abolishment was 1st March 2018. When Jemena crew arrived on site they identified that the building was partly demolished and there was no existence of switchboard. The underground service supply pit to the property, could not be located due to excessive debris around the site (refer to photos). | Services cable;Connection to meter;Meter board (including fuses) | 0 | 0 | 0 |  | pv31 | Builder began demolition before electricity supply was abolished. Initial date booked for abolishment was 1st March 2018 (Jemena Reference no. #000072763). | No Go Zone (no contact) | 43436.5542 |  |  | 9278 | Residential |  | 20180212JEM_02 | Infrastructure (network-based) | -37.7216 | 144.9233 | 1 | Jemena | Report | 11223 | 0.040523 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
On arrival crew isolated supply and carried out repairs. Customer advised to contact REC to repair Point of attachment. | 124 DAVY STREET, TARADALE VIC 3447 | 30349337 |  | Fallen;Property owner/customer | [5 empty] | Vic fire reported wire down across roadway. On arrival crew found that during a storm a tree on private property have fallen across service wire. There was no fire or injuries reported. | Service conductor | 2 | 2 | 2 |  | CMN001 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43375.7812 |  |  | 9275 | Roadway |  | 20180212PWA_04 | Infrastructure (network-based) | -37.1358 | 144.341 | 1 | Powercor | Report | 11220 | 0.041205 | Low voltage AC (<1kV) | Bendigo Airport | 3447 | Taradale | Trees
CEOT dispatched a fault crew to isolate, make safe, investigate and carry out necessary repairs. It appears a tree was felled by unknown person/s. No one on site. No fire. Wire on the ground. Police contacted and attended the site. No official report or report number received from the Police. Richard Kelaart ( Select Solutions) went to site and carried out an investigation. ESV attended site on the 9th February. No findings or report number available. The tree caused the conductors to go out of sag and this was repaired on the day and power was restored. | 2029 PRINCES HIGHWAY, NOWA NOWA VIC 3887 | 1903116 | Vandalism | [5 empty] | 1 | IMS 232338. Feeder fault on NLA 32 feeder. Vic Fires called CEOT saying a report of tree over main wires on the corner Lake Tyers Beach Road and Princes Hwy, Toorloo Arm. NOTE: AusNet Services Investigated two separate tree felling events that impacted high voltage conductor spans, caused by an act of vandalism. The other incident occurred on 12 February at Blackfellows Road, Nowa Nowa. NOTE: Toorloo Arm is the location for both incidents but it appears the official address in Nowa Nowa. | Conductor (bare) | 0 | 0 | 0 |  | nla34 | Vegetation: Trees Incident | Wilful act of vandalism by unknown person/s.;Other | 43314.459 |  |  | 9264 | Residential |  | 20180212SPN_01 | Infrastructure (network-based) | -37.7341 | 148.087 | 1 | AusNet Services Distribution | Report | 11661 | 0.037926 | 22kV AC | Bairnsdale Airport | 3887 | Nowa Nowa | Trees
Fault crew arrived on-site and noticed LA had been broken off and spud (potato) irrigator was in area. The LA appears to have been struck by the sprinkler causing the LA to break and sit against the LV bushing on supply transformer.The line crew isolated the Ttansformer from the HV supply by using live line techniques to remove the HV droppers. The CEOT were able to close the Gas Switch remotely using the battery supply so it appears the control box is still functioning. Future operating means it will need to been done on-site manually as the batteries will be flat. No fire on-site. To complete the works the crew will need an outage on the 22KV and 66 KV to replace the supply transformer with a new single phase 16 KVA transformer. A NOTI to be created in SAP for transformer replacement. A local Network Service Representative to organise a meeting with the farmer to discuss No Go Zone requirements. | 2270 MCDONALDS TRACK, THORPDALE VIC 3835 | 2207019 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 231815. Incd-160855-r MO007 tripped off due to damage to MO029 control transformer bushings & LA's caused by a potato sprinkler machine. | Surge diverter;Transformer | 0 | 0 | 0 |  | moe31 | Broken LA clashed with LV bushing on supply TX MO029. | No Go Zone (contact) | 22/12/2017 19:02 |  |  | 9271 | Agricultural |  | 20180212SPN_04 | Infrastructure (network-based) | -38.3132 | 146.1631 | 1 | AusNet Services Distribution | Report | 11216 | 0.03633 | 22kV AC | Morwell (Latrobe Valley Airport) | 3835 | Thorpdale | Vehicle
n arrival crew isolated supply and carried out repairs | 6 RODERICK STREET, TARADALE VIC 3447 | 30035907 |  | Wind;Fallen | [5 empty] | During Wind storm there was a report of a wire hanging low over roadway at incident location. Upon arrival crew found that a tree had fallen across the LV ABC near the corner of Roderick and Lyell Sts â€“ Taradale. A number of houses sustained mechanical damage to their POA's . There was no fire, no reported injuries. | Conductor (ABC) | 2 | 2 | 2 |  | CMN001 | Wind storm | Loss of supply;Damage to network assets | 43375 |  |  | 9289 | Roadway |  | 20180214PWA_04 | Infrastructure (network-based) | -37.1381 | 144.3515 | 1 | Powercor | Report | 11678 | 0.01163 | Low voltage AC (<1kV) | Bendigo Airport | 3447 | Taradale | Trees
The crew isolated N/S service and replaced the service cable. | 31 GREEN GULLY ROAD, KEILOR VIC 3036 | 33074906 | Vehicle | [6 empty] | Customer reported a truck delivering timber has broken a wire at the incident location. The truck has left site. A crew attended and found the service to the incident location had been broken. There were no reported shocks, injuries or fire start. | Service conductor | 2 | 2 | 2 |  | SA002 | Truck struck service | Loss of supply;Damage to network assets | 25/01/2018 13:47 |  |  | 9304 | Roadway |  | 20180215PWA_02 | Infrastructure (network-based) | -37.7223 | 144.8268 | 1 | Powercor | Report | 11299 | 0.0095231 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Vehicle
Upon arrival the Powercor crew found a small flashover mark on LV line and the line fuse had blown There was no vehicle on site | 21 DEMPSTER AVENUE, BALWYN NORTH VIC 3104 | 30190725 | Working too close to overhead lines | [5 empty] | 1 | A customer advised a vehicle made contact with service and no power at the incident location. Upon arrival the Powercor crew found a small flashover mark on LV main line and the line fuse had blown. This was caused by a high vehicle that was unloading building materials to building construction site. The builder is Prestige Homes. There were no injuries, fire or other damage. | Conductor (bare) | 2 | 2 | 2 |  | WD013 | Truck unloading building materials | Loss of supply;Damage to network assets | 31/01/2018 11:53 |  |  | 9306 | Roadway |  | 20180215PWA_04 | Infrastructure (network-based) | -37.7945 | 145.092 | 1 | CitiPower | Report | 11301 | 0.031525 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Vehicle
CEOT dispatched a fault crew to isolate, make safe and carry out any necessary repairs. CEOT also advised the local DAO to investigate the incident. The fault crew attended and made safe. On arrival the crew observed the fire had already been extinguished and a burnt area of 500mm x 500mm at the base of pole Lis No 2614828 Pole 50 Bennetts Crk. The crew also observed a HV 3/12 steel conductor 1 phase down. The crew issued an EAP and completed the repair of the conductor and conduit cover on the earth conductor and restored supply. Root Cause is unknown. | 36 DUSTING ROAD, HAZELWOOD SOUTH VIC 3840 | 2614828 |  |  |  | Corrosion |  | Phase to earth | 1 | IMS 232416. A fault crew attended a report of a wire down and a report of a fire in the area. Electrical protection operated - a Boric Acid fuse was blown. | Conductor (bare) | 0 | 0 | 0 |  | mwts24 | Cause is possibly due to corrosion | Grassfire | 14/02/2018 10:03 | 1 | Localised: less than 10 sq.m | 9302 | Residential |  | 20180215SPN_01 | Infrastructure (network-based) | -38.3259 | 146.4606 | 1 | AusNet Services Distribution | Report | 11685 | 0.017765 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood South | Fuse
Removed service fuse at BTS pole and issued a defect notice. Fault truck was sent to disconnect supply. | 94 WEST STREET, HADFIELD VIC 3046 |  | Unauthorised access | [5 empty] | 2 | Unknown persons relocated an overhead service from residential dwelling to a BTS. | Aluminium twisted (XLPE) | 2 | 2 | 2 |  |  | Unknown persons relocated an overhead service from residential dwelling to a BTS. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/02/2018 14:15 |  |  | 9319 |  |  | 20180216JEM_02 | Infrastructure (network-based) | -37.7098 | 144.938 | 1 | Jemena | Report | 11315 | 0.036998 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
The crew made the site safe, and inspected the HV fuses for damage. | COBRAM EAST CARAVAN PARK, 3186 MURRAY VALLEY HIGHWAY, COBRAM VIC 3644 | 30143478 |  | Blown branch/vegetation | [5 empty] | The CFA reported a grass fire at the incident location. On arrival the crew found that a branch had blown onto the HV fuses at P1 Wyatt Spur in high winds, it subsequently came to ground and caused a ground fire at the incident location. The ground fire was approximately 20m X 40m. Damage was reported to the grassland only, no injury was reported. | Conductor (bare) | 2 | 2 | 2 |  | CME021 | Wind blown debris from outside clearance space | Grassfire | 15/02/2018 13:05 | 1 | Small: 10 - 1000 sq.m | 9314 | Roadway |  | 20180216PWA_03 | Infrastructure (network-based) | -35.9516 | 145.6824 | 1 | Powercor | Report | 11711 | 0.0094028 | 22kV AC | Shepparton Airport | 3186 | Cobram | Trees
Crew made site safe and repaired conductor. | 35 HERBERT STREET, AVONDALE HEIGHTS VIC 3034 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Council tree has brought down white phase LV conductor. | Conductor (bare) | 2 | 2 | 2 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/02/2018 19:42 |  |  | 9331 | Residential |  | 20180219JEM_02 | Infrastructure (network-based) | -37.7667 | 144.8574 | 1 | Jemena | Report | 11722 | 0.021299 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | Trees
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for any necessary repairs. Fault crew attended and replaced the HV fuse. | 33 LAKE BUNGA BEACH ROAD, LAKE BUNGA VIC 3909 | 1902792 |  | Lightning |  | Candled fuse |  |  | 2 | IMS 232467. Call from CFA advising of ground fire (2m x 3m) in vicinity of AusNet Services' assets. Suspect lightning strike caused LA to fail with subsequent mal-operation of an EDO fuse which candled, burnt in half with a section falling to ground. | EDO fuse | 0 | 0 | 0 |  | nla34 | Suspect lightning strike caused LA to fail with subsequent mal-operation of an EDO fuse which candled, burnt in half with a section falling to ground. | Grassfire | 18/02/2018 15:12 | 1 | Localised: less than 10 sq.m | 9324 | Residential |  | 20180219SPN_01 | Infrastructure (network-based) | -37.8607 | 148.033 | 1 | AusNet Services Distribution | Report | 11321 | 0.021391 | 22kV AC | Bairnsdale Airport | 3909 | Lake Bunga | Lightning
Crew attended, extinguished fire, removed branch and restored supply | 15 BENETOOK AVENUE, MILDURA VIC 3500 | 30099309 |  | Blown branch/vegetation |  |  |  |  | 1 | Customer reported dim lights and a load bang at the incident location. On arrival the crew found that tree branch from a nearby tree ( outside clearance space ) was blown onto single phase transformer, landing between the HV bushings and surge diverters. The branch began to burn due to electrical tracking, dropping burning material to the ground, a grass fire approximately 3M square resulted at the base of the pole. | Dropper/bridge | 0 | 0 | 0 |  | MDA024 | airborne debris | Grassfire | 18/02/2018 19:17 | 1 | Localised: less than 10 sq.m | 9334 | Roadway |  | 20180220PWA_03 | Infrastructure (network-based) | -34.1844 | 142.193 | 1 | Powercor | Report | 11335 | 0.01069 | 22kV AC | Mildura Airport | 3500 | Mildura | Trees
CEOT dispatched a fault crew to make safe, isolate, investigate and carry out/arrange for any necessary repairs. Tree clearers made site safe and contacted the CEOT. The faults crew attend and opened off the last fuse, isolated supply, earthed and issued permit to fix the fault and restored supply to the customer. ETS have stood down the service provider pending an investigation. | GALLERY, 201 NELSONS ROAD, NOWA NOWA VIC 3887 | 1903521 |  | Within clearances |  |  |  | Phase to phase | 1 | IMS 232503. Initial Report: Tree clearer called CEOT and advised he lost control of the head of a tree with the wind and that it broke through one bay of overhead conductor between lis#1903543 & lis# 1903436 2 x fuses blew at switch 805915. Tree clearer was OK. Final Report: A Delivery Partner were using a 19 metre EWP clearing trees from a 22kV conductor. Tree limbs had been removed on the conductor side of the tree, the EWP Operator raised the EWP and began scarfing the tree directly away from the conductor. The tree was â€œback cutâ€ and started to fall away from the conductor when a gust of wind caught the head of the tree pushing it back across the fly boom of the EWP and the 22kV conductor causing them to clash and arc back to the tree stump. One conductor broke as a result of the clash dropping to the ground with each end landing 5-10 metres in front of, and behind the EWP. The EWP Operator removed himself from the incident scene and no injuries were sustained. | Conductor (bare) | 0 | 0 | 0 |  | nla34 | Vegetation: Trees Incident | Loss of supply | 21/02/2018 12:00 |  |  | 9344 | Roadway |  | 20180222SPN_02 | Infrastructure (network-based) | -37.7487 | 148.1191 | 1 | AusNet Services Distribution | Report | 11664 | 0.024425 | 22kV AC | Bairnsdale Airport | 3887 | Nowa Nowa | Other
On arrival crew isolated supply. Pole and crossarm replaced. | 7894 NATIMUK-FRANCES ROAD, NEUARPURR VIC 3413 | 32091284 |  |  |  | Leakage |  |  |  | VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden pole and crossarm required replacement due to pole top fire damage. There was no ground fire, no injuries or third party party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | HSM004 | Excessive leakage current | Pole-top fire | 22/02/2018 21:47 | 1 | Negligible: no ground fire | 9352 | Agricultural |  | 20180223PWA_05 | Infrastructure (network-based) | -36.7657 | 141.1001 | 1 | Powercor | Report | 11361 | 0.0073356 | 22kV AC | Horsham Aerodrome | 3413 | Neuarpurr | Pole
On arrival crew isolated supply and carried out repairs. | 1976 WIMMERA HIGHWAY, MURTOA VIC 3390 | 30085231 |  |  |  | Leakage |  |  |  | VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden crossarm and pole top assembly required replacement due to fire damage. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | HSM001 | Excessive leakage current | Pole-top fire | 22/02/2018 22:03 | 1 | Negligible: no ground fire | 9354 | Roadway |  | 20180223PWA_06 | Infrastructure (network-based) | -36.6154 | 142.429 | 1 | Powercor | Report | 11363 | 0.040543 | 22kV AC | Horsham Aerodrome | 3390 | Murtoa | Crossarm
Operator isolated area to make safe and repaired conductors. | 43 KEON PARADE, RESERVOIR VIC 3073 |  | Vehicle | [5 empty] | 1 | Vehicle hit pole causing feeder to trip and live conductor on ground (refer to tbl# 160596). | Conductor (bare) | 2 | 2 | 2 |  |  | Vehicle impact to pole resulting in pole down and 1x Bay of LV conductor down. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/02/2018 9:31 |  |  | 9364 | Residential |  | 20180226JEM_02 | Infrastructure (network-based) | -37.6958 | 145.0178 | 1 | Jemena | Report | 11373 | 0.027796 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Vehicle
On arrival crew isolated supply and carried out repairs. | 22-24 WELLS PLACE, SOUTHBANK VIC 3006 | 30170397 | Vehicle | [6 empty] | A customer advised a service wire down and lying on the lane at the incident location. Upon arrival, the CitiPower crew found that an UG live service cable had been lying on the lane. The crew suspect a vehicle hit the cable. There were no injuries or fire. | Services cable | 2 | 2 | 2 |  | SO15 | Believe to be vehicle | Loss of supply;Damage to network assets | 43436.559 |  |  | 9367 | Public space |  | 20180226PWA_03 | Infrastructure (network-based) | -37.8296 | 144.97 | 1 | CitiPower | Report | 11377 | 0.023907 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole and the Customerâ€™s FOLCB. The Powercor Fault Crew re-terminated the existing O/H Service connections at the Reticulation Pole and the Customerâ€™s FOLCB and completed an NST test which confirmed a Pass result. The attending LEI also re-terminated the Neutral connections at the Meter and the Customerâ€™s Main Switchboard. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. The LEI also advised the Report Room further investigation was required by the Network Quality Assurance Group to help establish the source of the inherent network voltage. A Customer Installation Defect Notice was issued to the Customer with a 28 day follow up to ensure the existing Meter Panel was adequately secured. | 144 THE PARADE, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Luke Keys (Barwon Water Employee) was attempting to clean a blocked water pipe in the Nature Strip (Road Reserve) at 144 The Parade, Ocean Grove when he received an electric shock as he made simultaneous contact with his hand on a conductive tool which was in contact with the metallic water pipe and his arm on the ground whilst standing in a puddle of water within an excavated hole. | Service conductor | 2 | 2 | 2 |  |  | Corroded connections | Minor shock | 13/02/2018 11:30 |  |  | 9373 | Public space |  | 20180226PWA_05 | Infrastructure (network-based) | -38.2669 | 144.5314 | 1 | Powercor | Report | 11386 | 0.02084 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
On arrival crew found conduit only damaged. Crew carried out repairs | 34A COPPIN GROVE, HAWTHORN VIC 3122 | 30185933 | Working too close to underground cables | [6 empty] | A contractor reported that they have uncovered a cable at the incident location. On arrival the fault crew found that an asphalting vehicle had uncovered and damaged the underground service to 34A Coppin Grove. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | NR042 | Excavations near service cable | No Go Zone (contact) | 14/02/2018 13:39 |  |  | 9381 | Roadway |  | 20180226PWA_07 | Infrastructure (network-based) | -37.8245 | 145.0181 | 1 | CitiPower | Report | 11399 | 0.036892 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Dug up
Initial Report: CEOT dispatched a fault crew make safe, investigate and carry out/arrange for necessary repairs. CEOT also dispatched an AusNet Services' LEI to attend. Final Report: Fault crew tightened loose neutral connection on LIS pole 1307519. LV ABC to pole junction box. Customers at street numbers 3,5 & 8 said that some of their appliances are not working. LEI attended site after reported supply issues. LEI found premises to be on supply, they were reconnected after supply fault was repaired apparently. Customers described lights and equipment not operating correctly then called power company to attend. All premises passed NST tests. House no 3 test results: Volts 241.6 V, Loop impedance 0.39 Ohms, PSC 618.8 A. House no 5 test results: Volts 232 V, Loop 0.31Ohms, PSC 737.7 A. House no 8 test results: Volts 237 V, Loop 0.28ohms, PSC 838.9 A. LEI proceeded to document damaged appliances at the above properties. | 8 FULLER STREET, BELGRAVE VIC 3160 | 1307521 |  |  |  | Neutral fault |  |  |  | IMS 232513. Customers reported appliance damage. Attending fault crew ascertained a loose neutral connection at pole end being the LV ABC to a pole junction box connection. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  | bge11 | Loose neutral connection at pole end. High impedance connection. | HV injection | 22/02/2018 18:15 |  |  | 9365 | Residential |  | 20180226SPN_01 | Infrastructure (network-based) | -37.9187 | 145.354 | 1 | AusNet Services Distribution | Report | 11375 | 0.0060475 | Low voltage AC (<1kV) | Moorabbin Airport | 3160 | Belgrave | Connection
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. Crew hoppered over and replaced bridges. Final Report: Alleged Low Voltage bridge clamp was loose on an Low Voltage strain crossarm. Fault crew hoppered over bridge. Construction visited at a later date and replaced bridges with Ampac Clamp rather than old bolt up clamps. Local DAO attended site, made observations/photos and whilst on-site the customer adjacent pole (95 Cherlynne) came out and commented on the fire, and experiencing a flickering light since the Low Voltage crossarm had been replace two weeks before. The LV crossarm was previously replaced as it was deteriorated due to rot. | 95 CHERYLNNE CRESCENT, KILSYTH VIC 3137 | 1004182 |  |  |  | Overheated connection |  |  | 1 | IMS 232545. Initial Report: A small fire located at base of pole, less than 1 foot square. Burnt bridges on White and Blue phases on pole. Final Report: Customer report small fire at base of pole and sparks up pole. Fault crew dispatched to investigate and make safe, alleged customer use garden hose to put fire out (0.1 sq. metre in size). Fault crew hoppered over White & Blue Phase at pole 1004182 and replace Low Voltage transformer fuse. | Connector/termination;Dropper/bridge | 0 | 0 | 0 |  | cyn21 | Loose LV bridge clamp. | Grassfire | 23/02/2018 16:44 | 1 | Localised: less than 10 sq.m | 9368 | Residential |  | 20180226SPN_03 | Infrastructure (network-based) | -37.8131 | 145.3241 | 1 | AusNet Services Distribution | Report | 11380 | 0.023363 | Low voltage AC (<1kV) | Moorabbin Airport | 3137 | Kilsyth | Pole
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for nay necessary repairs. CEOT also advised the local DAO. A 10m x 20m ground fire was observed which was extinguished by the CFA. Final Report: JAMIESON TOWN SPUR ISOLATED VIA BS FUSES AT POLE 1A (3914990 - SW 821237) AND TREE REMOVED. HV CONDUCTOR HEIGHT MEASURED AFTER TREE REMOVED AT 7.3m. | 42 OLD EILDON ROAD, JAMIESON VIC 3723 | 3919353 |  | Fallen |  |  |  | Phase to phase | 1 | IMS 232548. Initial Report: Vicfire reported tree on power lines and ground fire in area. Final Report from the attending DAO: MSD001 ACR DEVICE MS034 TRIPPED AS A RESULT OF A TREE FALLING ONTO 22kV 3PH OVERHEAD CONDUCTORS OFF THE JAMIESON TOWN SPUR LINE BETWEEN POLES 25 A(3919354) AND POLE 26 (3919355). TREE SMOULDERED AND CAUSED EMBERS TO FALL FROM CANOPY ONTO GRASS UNDERNEATH RESULTING IN A SMALL GRASS FIRE APPROX 10m X 20m. CFA ATTENDED AND EXTINGUISHED THE FIRE BEFORE THE FAULT CREW ARRIVED. | Conductor (bare) | 0 | 0 | 0 |  | msd1 | Vegetation: Trees Incident | Grassfire | 25/02/2018 11:15 | 1 | Small: 10 - 1000 sq.m | 9377 | Agricultural |  | 20180226SPN_08 | Infrastructure (network-based) | -37.2771 | 146.132 | 1 | AusNet Services Distribution | Report | 11395 | 0.01691 | 22kV AC | Wangaratta Aero | 3723 | Jamieson | Trees
The retirement village where the incident occurred was located adjacent to high voltage transmission lines. After tests were completed it was determined that the voltages on the metal framework of the pergola and also the guttering which had originally 150 Volts to be cause from induction. A temporary bonding earth was installed for the purpose of the test and found the voltages to drop to 0 Volts. The problem was explained to the customer and a defect notice (NCID) was issued. Defect notice #28808. | ESTIA HEALTH SOUTH MORANG, 879 PLENTY ROAD, SOUTH MORANG VIC 3752 |  |  |  |  | Induction |  | Phase to earth | 2 | IMS 232121. A worker received an electric shock from metal pergola when installing an air conditioner unit caused by induction from nearby transmission line. | No failed asset;Customer installation | 0 | 0 | 0 |  | drn21 | Induction from nearby transmission line. | Minor shock | 23/01/2018 15:59 |  |  | 9386 | Other | Residential care | 20180226SPN_11 | Infrastructure (network-based) | -37.6474 | 145.0914 | 2 | AusNet Services Distribution | Report | 11405 | 0.0017616 | Low voltage AC (<1kV) | Essendon Airport | 3752 | South Morang | Other
The attending faults crew advised the resource co-ordinator that high priority tree cutting is required as there a danger of another fire occurring in high winds due to the large tree's proximity to the HV overhead conductors. Tree cutter attended after hours and cut the tree away from the 22kV overhead conductors and the council tree's were clear from the LVABC below. | 12 LYNDOCH STREET, BOX HILL SOUTH VIC 3128 | 7037421 |  | Blown branch/vegetation |  |  |  |  | 2 | Customer reported that a tree branch fell down in the wind on Monday night (19/02/2018) and it appears to be burnt. The tree is on the nature strip and other branches appear dead and burnt. During strong winds on 19/02/2018, a council tree was making intermittent contact with the HV overhead conductors and were burning. One branch had broken and fell to the ground also with burnt foliage. | Conductor (bare) | 0 | 0 | 0 |  | BH 21 | Vegetation: Trees Incident | Other vegetation | 21/02/2018 11:55 | 1 | Negligible: no ground fire | 9374 | Roadway |  | 20180226UTD_02 | Infrastructure (network-based) | -37.837 | 145.1181 | 1 | United Energy Distribution | Report | 13023 | 0.029196 | 22kV AC | Moorabbin Airport | 3128 | Box Hill South | Trees
On arrival crew isolated supply and carried out repairs. | 735 DUNCANS ROAD, WERRIBEE SOUTH VIC 3030 | 30112622 |  |  |  | Corrosion |  |  |  | MFB reported wire down at the above incident location. On arrival, the crew reported HV aluminium to copper clamp corroded away and cable did not hit the ground but was resting on LV spreader. There was no fire or ground fire and no shock or injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBE034 | Corroded connection | Loss of supply;Damage to network assets | 21/02/2018 7:15 |  |  | 9393 | Roadway |  | 20180227PWA_05 | Infrastructure (network-based) | -37.9397 | 144.7092 | 1 | Powercor | Report | 11414 | 0.029231 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Connection
CEOT dispatched a fault crew and duty officer to isolate, make safe and investigate. An AusNet fault crew attended, confirmed SWER line de-energised via ACR # BN045, made safe, and removed the HV conductor from the truck. The fault crew checked the HV conductor condition at point of contact with no damage found. The fault crew checked the HV conductor ground clearance height post incident and reported the following:- â€¢ Conductor ground clearance height at point of contact â€“ 8.7m; and â€¢ Conductor ground clearance height at mid-span point â€“ 6.8m (between poles 1 and 2 HARRING Spur line). These ground clearance heights meet the regulatory requirement to AusNet Servicesâ€™ ESMS standards/technical manuals. All clear given by WorkSafe and supply restored to HARRING SWER line via ACR device BN045. | 59 MOGLONEMBY HALL ROAD, MOGLONEMBY VIC 3666 | 3901466 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232571. Initial Report: CEOT received a call from the CFA that a truck had contacted an overhead line and the truck was on fire at 1334 hours. The truck driver is OK and clear of the truck. The section fuse tripped from the Miepole ISO section. 39 customers off supply. Final Report from attending investigation officer/DAO: A tip truck driver (Bradley Rix) was tipping a load of superphosphate from the large rear trailer. After tipping the load, the driver drove forward and made contact with the 12.7kV SWER conductor between poles 1 and 2 of HARRING Spur line with the front step ladder area of the rear trailer. Point of contact within paddock was 75.6 metres NW of pole 1 HARRING Spur line (3901466). The driver stopped when he heard a noise and saw smoke and flames at the rear trailer wheels. The driver stepped out of the truck cabin onto the fuel tank mounted step and felt a minor electric shock and he jumped clear of the truck. The driver was not injured but he did report a minor electric shock just before jumping off the truck. SWER ACR device BN045 operated and locked out. The fire caused significant damage to the truck and also burnt approximately 30m x 30m of paddock grass. One local CFA tanker attended and extinguished the fire. The CFA remained on site for mop up works and first aid observations of the driver. An ambulance attended and monitored the driver and treated him for a minor burn on his leg from fighting the fire. | Conductor (bare) | 0 | 0 | 0 |  | bn1 | Tip truck driver caused the rear trailer to make contact with a SWER line. | Loss of supply;Vehicle;No Go Zone (contact) | 26/02/2018 13:37 | 1 | Small: 10 - 1000 sq.m | 9387 | Agricultural |  | 20180227SPN_01 | Infrastructure (network-based) | -36.6414 | 145.5198 | 1 | AusNet Services Distribution | Report | 11409 | 0.021515 | 12.7kV AC (SWER) | Shepparton Airport | 3666 | Moglonemby | Vehicle
On arrival, Crew removed service line and arranged for LEI to attend the following morning when resident/s would be home. Hv cross-arm replaced. | 74 TIMBOON-TERANG ROAD, ECKLIN SOUTH VIC 3265 | 32057007 |  |  |  | Mechanical breakdown |  |  | 1 | Emergency services reported that there was a wire down on a car arcing and sparking. Customer also reported a fire. On arrival the attending crew found a HV cross-arm on pole 151 had broken and a HV conductor had fallen and contacted a Low voltage service line. Crew identified light globes in house had exploded consistent with high voltage injection. Crew found no evidence that line was down on car or any evidence of fire. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG003 | Crossarm failure | HV injection;Loss of supply | 28/02/2018 17:48 |  |  | 9403 | Residential |  | 20180301PWA_02 | Infrastructure (network-based) | -38.3852 | 142.9118 | 1 | Powercor | Report | 11433 | 0.0079514 | Low voltage AC (<1kV);22kV AC | Warrnambool Airport Ndb | 3265 | Ecklin South | Crossarm
On arrival crew isolated supply and carried out repairs. | 365 WALLINGTON ROAD, WALLINGTON VIC 3222 | 32072177 |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | Emergency services reported that there was a grass fire and trees on fire On arrival the attending crew found a gum tree on private property had broken and contacted HV. The tree had fallen clear of the conductors when the crew arrived. The conductors were hanging low but aloft. CFA crew on site advised they found no evidence of fire however did report sparking until the vegetation fell away from conductors. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | DDL023 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 28/02/2018 16:31 |  |  | 9406 | Agricultural |  | 20180301PWA_04 | Infrastructure (network-based) | -38.2392 | 144.5008 | 1 | Powercor | Report | 11439 | 0.030855 | 22kV AC | Avalon Airport | 3222 | Wallington | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 14 BREEZE STREET, BONBEACH VIC 3196 | 3302609 |  | Precipitation;Prone to salt deposition |  | HV injection;Leakage |  |  | 1 | At 0436hrs on 01/03/2018, 22kV feeder CRM 14 circuit breaker reclosed to lockout affecting 234 customers. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 3302609 located on the corner of Breeze and Patterson Streets, Bonbeach in close proximity to Port Phillip Bay. A HV conductor made brief contact with the LV conductors below when the cross arm broke and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the south circuit of "Patterson-Breeze" substation. The LEI confirmed a high voltage injection occurred (KEY 1801) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Crossarm (wood) | 0 | 0 | 0 |  | CRM 14 | Light rain following a long dry spell. | Pole-top fire;HV injection | 43103.1917 | 1 | Negligible: no ground fire | 9413 | Roadway |  | 20180302UTD_02 | Infrastructure (network-based) | -38.0681 | 145.1232 | 1 | United Energy Distribution | Report | 13029 | 0.023688 | 22kV AC | Moorabbin Airport | 3196 | Bonbeach | Crossarm
Jemena fault crew assessed the damage (as per the attached photo IMGXXXXXX545), made the site safe by removing the damage overhead service supply to the property and issued the customer with a defect notice due to the damage caused at the customerâ€™s Fused Overhead Line Connector Box FOLCB. The Jemena fault crew at the time, couldnâ€™t provide evidence nor see the tree cutting company or the customer on the site. The tree cutting company did not have any signs or identification on their vehicles. | 30 BROWN STREET, AVONDALE HEIGHTS VIC 3034 |  | Unauthorised access | Within clearances |  |  |  |  | 2 | Overhead single-phase service supply been brought down by tree cutting company (name unknown) engaged by property owner. The tree branch caused the service to be pulled away from the point of attachment. Neighbour advised that the property has been vacant and there are no personnel living at the property. Fallen overhead service was left wrapped around neighbours their fence. | Service conductor | 2 | 2 | 2 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43193.6146 |  |  | 9416 | Residential |  | 20180304JEM_01 | Infrastructure (network-based) | -37.7669 | 144.8552 | 1 | Jemena | Report | 11454 | 0.0038843 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | Other
On arrival crew made site safe and commenced repairs. | 1367 LEAKES ROAD, ROCKBANK VIC 3335 | 33071801 | Working too close to overhead lines | [5 empty] | 1 | Powercor was contacted by several customers indicating no supply in the vicinity of Leakes road, Rockbank. A report was received that an excavator had made contact with overhead conductors, On arrival the crew found that a worker from Winslow Constructions was operating an excavator and had hit the overhead HV conductors between poles LIS-107471 and LIS-107472 located in a paddock, approx. 500m east from Leakes road. 2 spans of HV conductors were affected. One bay of HV conductors snapped from the Termination pole LIS-107471 and were laying on the ground, the other bay of HV conductors, west side of pole LIS-107472 was hanging approx. 2m off the ground. There was no ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MLN021 | Operating excavator under line | No Go Zone (contact) | 43134.7562 |  |  | 9421 | Agricultural |  | 20180305PWA_03 | Infrastructure (network-based) | -37.7377 | 144.6585 | 1 | Powercor | Report | 11459 | 0.0042859 | 22kV AC | Laverton Raaf | 3335 | Rockbank | Vehicle
Section of HV line was de-energised. AusNet Services had already opened the ACR (BW2585) to isolate the line for the fire brigade. The fault crew opened a manual Gas Switch (BW1163) on School Rd, Bayles to reduce the affected area. The fault crew then fixed the fault once the fire brigade had finished their job. Both Switches then close to restore supply to affected customers. | 185 OBRIENS ROAD, BAYLES VIC 3981 | 513344 |  | Fallen | [5 empty] | IMS 232492. Report of a small grass fire in the vicinity of AusNet Services' asset (a fallen wire). Fault crew arrived and the fire brigade was already onsite. They had sprayed the pole and surrounding ground area with water before the fault crew arrived to site. The size of the fire was small according to the fault crew but the fire brigade had already put out the fire prior to the crew's arrival. A large tree branch falling on the a single overhead HV conductor cause the fault and fire to start. The branch had scorch marks on it. Report from AusNet Services' Vegetation section: Acacia melanoxylon has had a large branch failure at the branch union and had come to rest in the lower canopy of a neighbouring Blackwood, the branch length is 6m with the union located 7m from ground level on the trunk of the Blackwood, the total tree height is 13m and the trunk distance is 5m from the 22kv overhead conductors. 22kV conductors are 7m from ground level and the Blackwood DBH is 380mm, hazard tree report submitted to height reduce the Blackwood. The tree was a Shire tree with AusNet Services responsibility. The tree branch was not inside the clearance space. The weather conditions were mild wind with light to moderate rain. | Conductor (bare) | 0 | 0 | 0 |  | llg11 | Vegetation: Trees Incident | Grassfire | 14/02/2018 9:38 | 1 | Localised: less than 10 sq.m | 9431 | Agricultural |  | 20180307SPN_01 | Infrastructure (network-based) | -38.1972 | 145.5894 | 1 | AusNet Services Distribution | Report | 11686 | 0.016809 | 22kV AC | Moorabbin Airport | 3981 | Bayles | Trees
Site made safe. Section of HV overhead was isolated and earthed. Conductor has been repaired. The damaged conductor was quarantined for assessment and investigation. | 51 SMILEY ROAD, BROADMEADOWS VIC 3047 |  |  |  |  | Age | Poor workmanship |  | 1 | Centre phase of bare HV conductor (Aluminium Conductor Galvanised Steel Reinforced (ACSR) construction) failed at the point of connection with the McIntyre sleeve, which is a full tension type connector (used to join conductors under tension). The failure occurred at 5 metres south of pole A040633. Protection operated correctly therefore the HV conductor was dead when it fell to ground and did not pose a risk to the general public. Photo has been attached in "Notes & Findings" section | Conductor (bare);Aluminium | 0 | 0 | 0 |  | BMS12 | There were no splash marks on the McIntyre sleeve nor any evidence of clashing or contact with any object. The investigation found that the McIntyre sleeve did not fail. However, the conductor had narrowed and broken off at the point of connection with the McIntyre sleeve. Conductors are known to display a wear-out characteristic, with the onset of wear out at the end of the useful life. In this case, an Aluminium Conductor Galvanised Steel Reinforced (ACSR) conductor is expected to have a useful life of 50 years. Unfortunately the exact date of installation of the ACSR conductor at this location is unknown; however, we do know that ACSR conductors on the Jemena network were installed between 1960 and 1975. Therefore it is likely that the ACSR conductor at this location is approaching the end of its useful life, after which the frequency of failure increases with additional age. Given available information and evidence, and the fact that the ACSR conductor had failed at the connection with the McIntyre sleeve, it is likely that a combination of age-related degradation and possibly poor workmanship during installation were contributing factors in this incident. | Loss of supply | 43315.7847 |  |  | 9447 | Residential |  | 20180308JEM_01 | Infrastructure (network-based) | -37.6875 | 144.9329 | 1 | Jemena | Report | 11842 | 0.0025046 | 22kV AC | Essendon Airport | 3047 | Broadmeadows | Connection
The crew called CEOT and asked for the line to be isolated to allow for the spur fuses to be operated. CEOT isolated the line from the closest automatable gas switch. The crew then made the site safe and restored the line accordingly. Asset Management and Support have determined that although no setting changes are required for both TN18286 ACR and WGL21 feeder CB, but WL104F Fusesaver do need to be checked for operation adequacy. | 5 BINBEAL ROAD, DROUIN VIC 3818 | 2706424 |  | Blown branch/vegetation |  |  |  | Phase to earth | 2 | IMS 232619. During a recent storm event a work crew were dispatched to a no supply and HV conductor down and upon arrival the crew found the HV conductors (6/1/2.5 ACSR) that were down were alive and sparking. A tree branch broke two HV conductors clean off at the pole, leaving the 3rd HV conductor still up and alive. The fallen conductors were energised due to back feed from downstream transformer windings due to the high impedance fault. | Conductor (bare) | 0 | 0 | 0 |  | wgl21 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2018 8:57 |  |  | 9437 | Residential |  | 20180308SPN_01 | Infrastructure (network-based) | -38.1294 | 145.844 | 1 | AusNet Services Distribution | Report | 11480 | 0.0047986 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Drouin | Trees
CEOT dispatched a fault crew and an AusNet Servicis' LEI to attend, make safe and carry out any necessary repairs. The existing service cable was replaced with a new XPLE type service cable and tests were conducted with NST test passing and only 1V recorded on the neutral at completion. Lights not dimming under load any more. | 8 MERMAIDS WALK, CAPE PATERSON VIC 3995 | 2810958 |  |  |  | Age;Corrosion |  |  | 2 | IMS 232158. Customer reported tingles off meter box when opening it. Lights also dimmed under load. | Service conductor | 0 | 0 | 0 |  | wgi33 | Faulty overhead service cable. | Minor shock | 27/01/2018 13:05 |  |  | 9442 | Residential |  | 20180308SPN_06 | Infrastructure (network-based) | -38.6685 | 145.6169 | 1 | AusNet Services Distribution | Report | 11489 | 0.032706 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | Cape Paterson | OH Cable
CEOT dispatched a fault crew to make safe, investigate and carry out repairs. Crew arrived on site and removed hung-up HV fuse. Fuse unit replaced with a new 6A BA fuse unit. The pole has the incorrect fuse brackets fitted to the HV crossarm - follow on Notification in SAP to be raised by field crew. | 88 BENNETTS ROAD, LILLIPUT VIC 3682 | 5105092 |  |  |  | Candled fuse |  |  | 2 | IMS 232237. White Phase 6A Boric Acid fuse hung-up and burnt in half on substation pole "ARROWSMITH 6' 2151083600. | Boric acid | 0 | 0 | 0 |  | wn3 | Candled BA fuse. | Other electricity related | 31/01/2018 15:23 | 1 | Negligible: no ground fire | 9445 | Agricultural |  | 20180308SPN_08 | Infrastructure (network-based) | -36.1588 | 146.5133 | 1 | AusNet Services Distribution | Report | 11492 | 0.036039 | 22kV AC | Wangaratta Aero | 3682 | Lilliput | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 865 GLEN HUNTLY ROAD, CAULFIELD VIC 3162 | 2306516 |  |  |  | Electrical breakdown |  |  | 1 | At 0859hrs on 14/02/2018, 11kV feeder CFD 13 circuit breaker reclosed to lockout. Refer also to Incident Report 20180223UTD_03 that occurred the previous day. A HV helical termination failed at pole No. LIS 2306516 located in Glenhuntly Road that caused the feeder to reclose to lockout. The MFB reported that flames were evident at the time of the faults with scorch marks identified on the HV cross arm and discs. | Dropper/bridge | 0 | 0 | 0 |  | CFD 13 | Failed HV helical termination. | Pole-top fire | 14/02/2018 8:59 | 1 | Negligible: no ground fire | 9435 | Roadway |  | 20180308UTD_02 | Infrastructure (network-based) | -37.8871 | 145.0245 | 1 | United Energy Distribution | Report | 12992 | 0.013043 | 11kV AC | Moorabbin Airport | 3162 | Caulfield | AF Other
On arrival crew isolated supply and carried out repairs. | 97 FOUR TREE ROAD, LISMORE VIC 3324 | 30042226 |  |  |  | Leakage |  |  |  | CFA reported a pole fire at the incident location. On arrival crew found HV crossarm burnt off. THere was no ground fire, no reported injuries or third party property damage | Crossarm (wood) | 2 | 2 | 2 |  | CDN004 | Excessive leakage current | Pole-top fire | 20/01/2018 12:12 | 1 | Negligible: no ground fire | 9454 | Roadway |  | 20180309PWA_02 | Infrastructure (network-based) | -37.9842 | 143.3438 | 1 | Powercor | Report | 11504 | 0.040009 | 22kV AC | Ballarat Aerodrome | 3324 | Lismore | Crossarm
On arrival crew isolated supply and commenced repairs. | 370 DOUGAN ROAD, COOMBOONA VIC 3629 | 33088942 | Working too close to overhead lines | [6 empty] | Neighbour reported low wires lying in paddock at 370 Dougan Rd Coomboona 3629 and they had seen an excavator working in the vicinity of the overhead lines. On arrival crew found 1 conductor down, conductor tie was on the ground and insulator damaged at pole 1. Parts of the insulator were up to 15m away. There was evidence that the cross-arm had turned slightly, possibly due to impact. Crew also identified recent digging in drain near conductors. Landowners had said that no-one had been working in the vicinity that day. There was no excavation equipment on site, nearest operations were on a different property about 1km away. No fire, No injuries, No third party damage. | Conductor (bare) | 2 | 2 | 2 |  | MNA014 | Believed to be excavation operation, no equipment found on site | Loss of supply;No Go Zone (contact);Damage to network assets | 43346.6764 |  |  | 9473 | Agricultural |  | 20180313PWA_02 | Infrastructure (network-based) | -36.2875 | 145.2967 | 1 | Powercor | Report | 11532 | 0.014293 | 22kV AC | Shepparton Airport | 3629 | Coomboona | Vehicle
made safe and commenced repairs. | 179A CIVIC PARADE, ALTONA VIC 3018 | 32168871 |  | Lightning | [5 empty] | A customer reported that a wire has broken and caused damage to the roof of a house at the incident location. On arrival the fault crew found that the footpath side high voltage conductor has broken at the pole corner McIntyre Drive and Civic Parade,. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | AL012 | Conductor parted due to lightning activity in area | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/11/2017 11:45 |  |  | 6721 | Roadway |  | 20171117PWA_04 | Infrastructure (network-based) | -37.8635 | 144.8232 | 1 | Powercor | Report | 8456 | 0.031637 | 11kV AC | Laverton Raaf | 3018 | Altona | Lightning
On arrival crew carried out repairs | 59 WATTON STREET, PENSHURST VIC 3289 | 32127148 |  |  |  | Leakage |  |  | 1 | A Powercor fault crew were patrolling following a feeder outage and found a crossarm burnt off at the strap bolt at the incident location. There was no ground fire and no reported third party damage or any injuries. | Crossarm (wood) | 2 | 2 | 2 |  | HTN003 | Excessive leakage current | Pole-top fire | 43080.2812 | 1 | Negligible: no ground fire | 6722 | Public space |  | 20171117PWA_05 | Infrastructure (network-based) | -37.8768 | 142.2951 | 1 | Powercor | Report | 8457 | 0.013973 | 22kV AC | Hamilton Airport | 3289 | Penshurst | Crossarm
On arrival crew carried out repairs | 128 ALLENS ROAD, NUMURKAH VIC 3636 | 32185391 |  |  |  | Leakage |  |  | 1 | Vicfire advised of a x-arm fire AT P375 ON SHTS-NKA No.2 line. Upon arrival crew found that the 66kV x-arm had burnt off and the 66kV conductor had landed on the subsidiary 22kV line breaking a 22kV insulator. A ground fire ensued covering an area of approximately 70m x 5m. There were no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | SHTS-NKA2 | Excessive leakage current | Grassfire | 18/11/2017 11:36 | 1 | Small: 10 - 1000 sq.m | 6733 | Roadway |  | 20171121PWA_02 | Infrastructure (network-based) | -36.0739 | 145.4175 | 1 | Powercor | Report | 15128 | 0.022225 | 22kV AC;66kV AC | Shepparton Airport | 3636 | Numurkah | Conductor
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Line isolated and repairs completed safely by a construction crew. Supply restored. | 3155 BALLARTO ROAD, PAKENHAM SOUTH VIC 3810 | 516343 | Working too close to overhead lines |  |  |  |  | Phase to earth |  | IMS 231206. Feeder tripped due to overhead conductors down, broken from pole Lis 516343. Fault located and appears tip truck contacted HV overhead conductors. No vehicle details. | Conductor (bare) | 0 | 0 | 0 |  | phm12 | Tip truck made contact with overhead HV line. | No Go Zone (contact) | 14/11/2017 15:28 |  |  | 6735 | Agricultural |  | 20171121SPN_02 | Infrastructure (network-based) | -38.1559 | 145.5044 | 1 | AusNet Services Distribution | Report | 8474 | 0.024826 | 22kV AC | Moorabbin Airport | 3155 | Pakenham South | Vehicle
On arrival crew isolated supply and carried out repairs | 11 HIRTH LANE, DARTMOOR VIC 3304 | 30089387 | Crane, excavator or other construction/farming equipment | [6 empty] | An REC reported that the Mower on a tractor had hit the service cable at the incident location. On arrival the crew found that the property owner was operating a tractor with a mower and contacted a LV service cable causing damage to the cable and associated POA. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | PLD003 | Tractor contacted service | No Go Zone (contact);Damage to network assets | 17/10/2017 12:15 |  |  | 6746 | Agricultural |  | 20171122PWA_04 | Infrastructure (network-based) | -37.9325 | 141.2773 | 1 | Powercor | Report | 8486 | 0.012242 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3304 | Dartmoor | Vehicle
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 53 ORCHARD CRESCENT, MONT ALBERT NORTH VIC 3129 |  |  | Lightning |  |  |  |  | 2 | REC Brendan Gow (0418 998 589) advised there is no display on meter number 0534857 following yesterdays storm. There are also damaged appliances in units 1 and 2. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, customers who reside in Orchard Crescent had problems with their electricity supply after lightning struck at an unknown location and they proceeded to contact a REC to investigate. A faults truck attended and found two AMI meters were damaged and required replacement and they requested that a LEI attend as a HVI was suspected. The LEI confirmed a high voltage injection occurred (BWD 1703) affecting the two customers that sustained minor damage to appliances and equipment. | Smart meter | 0 | 0 | 0 |  | DC 05 | Lightning strike at an unknown location. | Damage to network assets | 18/11/2017 17:15 |  |  | 6739 | Residential |  | 20171122UTD_02 | Infrastructure (network-based) | -37.7962 | 145.1065 | 1 | United Energy Distribution | Report | 8479 | 0.014418 | 22kV AC | Moorabbin Airport | 3129 | Mont Albert North | Lightning
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. | 285 NEW STREET, BRIGHTON VIC 3186 |  |  | Lightning |  |  |  |  | 2 | Customers at 283 and 285 New Street advised that lightning has struck a pole outside their property. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, customers in New Street advised lightning struck the pole outside their property. An AMI meter was damaged at number 285 and required replacement. The faults crew isolated supply at the pole end and requested that a LEI attend as a HVI was suspected at the two properties. The LEI confirmed a high voltage injection occurred (BWD 1704) affecting the meter and an internal investigation revealed there was no minor damage to appliances and equipment. | Pole (wood) | 0 | 0 | 0 |  | NB 33 | Lightning struck a United Energy LV pole. | HV injection;Damage to network assets | 18/11/2017 17:15 |  |  | 6741 | Residential |  | 20171122UTD_03 | Infrastructure (network-based) | -37.9074 | 144.9924 | 1 | United Energy Distribution | Report | 8481 | 0.032698 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Lightning
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. The LEI isolated damaged circuits and appliances and supply was left on with a REC attending to complete the rectification work. | 78 HODDER STREET, BRIGHTON EAST VIC 3187 |  |  | Lightning |  |  |  |  | 2 | Caller reports that following the storm, a power point has exploded and the wires are now bare. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, a single customer that resides at 78 Hodder Street advised that lightning struck at an unknown location and has blown apart an external socket outlet on the north facing wall. A faults truck attended and requested that a LEI attend as a HVI was suspected. The LEI confirmed a high voltage injection occurred (CLA 1706) affecting the customer that sustained minor damage to appliances and equipment. | Customer installation | 0 | 0 | 0 |  | BT 10 | Lightning strike at an unknown location. | HV injection | 18/11/2017 17:15 |  |  | 6742 | Residential |  | 20171122UTD_04 | Infrastructure (network-based) | -37.9031 | 145.0235 | 1 | United Energy Distribution | Report | 8482 | 0.017027 | 11kV AC | Moorabbin Airport | 3187 | Brighton East | Lightning
A LEI investigated the amount of damage that occurred to customers appliances and equipment and issued damage cards to the occupiers of the two occupancies. | FLAT 1 16 ADRIAN STREET, BENTLEIGH EAST VIC 3165 | 1802183 |  | Lightning |  |  |  |  | 2 | Caller reports that lights are dimming and the neighbour has the same issue. Following a storm that struck Melbourne at approximately 5.15PM on 18/11/2017, residents from a unit development had problems with their electricity supply after lightning struck at an unknown location. A faults truck attended and found damaged appliances and they requested that a LEI attend as a HVI was suspected. The LEI confirmed a high voltage injection occurred (CLA 1707) affecting the two customers that sustained minor damage to appliances and equipment. | No failed asset | 0 | 0 | 0 |  | MR 15 | Lightning strike at an unknown location. | HV injection | 21/11/2017 9:30 |  |  | 6745 | Residential |  | 20171122UTD_06 | Infrastructure (network-based) | -37.9327 | 145.0599 | 1 | United Energy Distribution | Report | 8485 | 0.021367 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Lightning
CEOT dispatched a fault crew who attended and isolated the supply, made safe and investigated the incident. The incident is under further investigation by the APA Group. The AusNet Services' underground crew carried out the necessary repairs to the underground cable and supply was restored. ESV notified. | 175 BAIRNSDALE-DARGO ROAD, BAIRNSDALE VIC 3875 | 1612474 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 231127. Whilst in the process of underground directional boring from the main gas line for a new gas service line to a domestic premises, a subcontractor working for APA Group, made contact with a live underground HV cable (22kV). at Lis 5749606. Electrical protection operated - feeder BDL4, ACR BD107 tripped. No injuries were sustained by any persons. When the she strike alert activated on the boring machine the machine operator contacted his manager and then the incident was reported to AusNet Services. The subcontractor had Dial Before You Dig plans. Subcontractor details: Peter Reid, R&B Trenching, tel 0447 516285. APA Group contact person is: Ian Bowman, Project Manager South, APA Group, Vic Networks, Capital Delivery, Anderson Street, PO Box 369, Warragul, 3820. Telephone 56115307, 0418 511795. | Cable | 0 | 0 | 0 |  | bdl4 | Contractor drilled into UG HV cable. | Loss of supply;No Go Zone (contact) | 42958.5833 |  |  | 6752 | Residential |  | 20171123SPN_01 | Infrastructure (network-based) | -37.8381 | 147.5701 | 1 | AusNet Services Distribution | Report | 8497 | 0.01388 | 22kV AC | Bairnsdale Airport | 3875 | Bairnsdale | Dug up
On arrival crew carried out repairs | 34 HIGHFIELD ROAD, CANTERBURY VIC 3126 | 30177048 | Vehicle | [5 empty] | 2 | A customer advised a truck has brought down a wire at the incident location. Upon arrival the CitiPower crew found that the service had been damaged. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | RD006 | Vehicle struck service line | Loss of supply;Damage to network assets | 24/10/2017 7:35 |  |  | 6758 | Residential |  | 20171124PWA_02 | Infrastructure (network-based) | -37.8283 | 145.0863 | 1 | CitiPower | Report | 8505 | 0.02972 | Low voltage AC (<1kV) | Moorabbin Airport | 3126 | Canterbury | Vehicle
On arrival crew reported no damage to overhead conductors. | 578 WALTERS ROAD, MANANGATANG VIC 3546 | 30350763 | Working too close to overhead lines | [5 empty] | 1 | Customer reports a fire start after harvester contact SWER O/H conductor on property. Customer states on the 22nd Nov he was operating a harvester in the paddock when a ground fire start occurred, burning approx. 20 acres of stubble paddock. CFA attended and extinguished fire. Smart meter data shows a momentary outage for a SWER ACR reclose at the time of this event. The next day ( 23rd Nov ) the customer noticed a burn make on the harvesters GPS aerial and reported the incident to Powercor. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | BBD014 | Header GPS aerial contacted swer conductor | Grassfire | 22/11/2017 8:04 | 1 | Large: more than 10 ha | 6761 | Agricultural |  | 20171127PWA_01 | Infrastructure (network-based) | -35.0041 | 143.0409 | 1 | Powercor | Report | 8511 | 0.026825 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3546 | Manangatang | Vehicle
Made safe and earth cable replaced / repaired. | 2 OLYMPIA STREET, TOTTENHAM VIC 3012 | A052947 | Copper theft | [5 empty] | 2 | Unknown person(s) stole copper earthing from cable head pole in Olympia St on Olympia-Sunshine substation. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Unknown person(s) stole copper earthing cable | Damage to network assets | 26/11/2017 13:01 |  |  | 6777 | Industrial |  | 20171128JEM_02 | Infrastructure (network-based) | -37.8002 | 144.8577 | 2 | Jemena | Report | 8530 | 0.037405 | Earthing cable | Essendon Airport | 3012 | Tottenham | Other
As the thief left the cover guard and conduit neatly on the nature strip, the Forensics Unit of the Sunshine Police Dept decided to attend on site to determine if any fingerprints could be lifted. The fault crew returned later in the evening to remove the cover guard etc from site. The Powercor Urban Customer Services Group will need to follow up and have the cable re-installed to enable connection to occur when required by the customer at number 9. | 10 BUSCH STREET, SUNSHINE NORTH VIC 3020 | 32175621 | Copper theft | [6 empty] | Report received from resident at number 10 Busch St that suspicious activity was observed at LIS-21127 (LV inter pole outside number 12) during the afternoon of the 23/10/17. A single Caucasian male (wearing hi-vis vest and hard hat) claimed to the resident who reported the incident to be undertaking legitimate electrical works at the location in question. Upon arrival the fault crew found that the unknown male had removed the LV cover guard and pole conduit from the FOLCB to the flexible conduit at ground level, and had also removed/stolen the new, yet to be connected, 4/core 16mm underground service cable which runs from LIS-21127 to a pit on the front boundary of number 9 Busch St, located across the road. The thief used his vehicle, an unmarked white ute to remove the cable, by attaching the cable to the ute and driving away slowly, so as to pull through the entire length of cable (approx. 25m) which was installed in the conduit. CCTV footage of the thiefâ€™s â€˜daylight robberyâ€™ was captured by the resident at number 10. It was also noted that number 9 had an active camera, all of which was provided to Sunshine Police for their follow up. There was no fire or reported injuries | Earth/earthing | 2 | 2 | 2 |  | SSE012 | Cable theft | Loss of supply;Damage to network assets | 23/10/2017 15:51 |  |  | 6778 | Public space |  | 20171128PWA_02 | Infrastructure (network-based) | -37.7674 | 144.835 | 1 | Powercor | Report | 8531 | 0.039293 | Earthing cable | Essendon Airport | 3020 | Sunshine North | Other
On arrival crew carried out repairs | 792 ELIZABETH STREET, MELBOURNE VIC 3000 | 30205224 | Working too close to underground cables | [6 empty] | John Holland Construction were digging up the road when they hit and damaged a conduit. The HV cable was not damaged There was no fire or reported injuries | Cable | 2 | 2 | 2 |  | VM035 | Road excavations | Damage to network assets | 21/10/2017 6:10 |  |  | 6781 | Roadway |  | 20171128PWA_05 | Infrastructure (network-based) | -37.8001 | 144.9579 | 1 | CitiPower | Report | 8536 | 0.040828 | 11kV AC | Essendon Airport | 3000 | Melbourne | Dug up
Crew attended site and discovered 1 HV powder filled fuse candling fuse replaced .No evidence of fire on ground. no photo's available | 169 CHAPPLE STREET, WODONGA VIC 3690 | 5219216 |  |  |  | Candled fuse |  |  | 2 | IMS 230691 - 3ph Industrial customer called in part supply . Crew sent to investigate. | Powder filled | 0 | 0 | 0 |  | WOTS12 | Fuse candling | Pole-top fire | 43018.4444 | 1 | Negligible: no ground fire | 6785 | Commercial |  | 20171129SPN_02 | Infrastructure (network-based) | -36.137 | 146.903 | 1 | AusNet Services Distribution | Report | 15188 | 0.0080289 | 22kV AC | Wangaratta Aero | 3690 | Wodonga | Fuse
The substation was placed under parallel and isolated. Repairs were made. | 3 LEWIS STREET, KINGSVILLE VIC 3012 |  | Copper theft | [5 empty] | 2 | Unknown persons stole high voltage and low voltage earths from Albion-Geelong pole substation. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper earths were stolen by unknown persons. | Damage to network assets | 30/11/2017 22:02 |  |  | 6797 | Public space |  | 20171130JEM_01 | Infrastructure (network-based) | -37.8094 | 144.8738 | 1 | Jemena | Report | 8563 | 0.0033067 | Earthing cable | Essendon Airport | 3012 | Kingsville | Other
On arrival crew isolated supply and carried out repairs | 146 PULLAR ROAD, COBRAM VIC 3644 | 33083463 |  | Fallen;Property owner/customer | [5 empty] | Vic Fire rang to advise of wire down and small grass fire at the incident location. On arrival the crew found a tree limb had damaged service wire resulting in a grass fire of approx. 2m X 10m A Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries. | Service conductor | 2 | 2 | 2 |  | CME021 | Vegetation: Trees Incident | Grassfire | 26/11/2017 2:22 | 1 | Small: 10 - 1000 sq.m | 6802 | Residential |  | 20171201PWA_01 | Infrastructure (network-based) | -35.9405 | 145.6695 | 1 | Powercor | Report | 8569 | 0.032194 | Low voltage AC (<1kV) | Shepparton Airport | 3644 | Cobram | Trees
The crew replaced EDO fuse. Surge divertor disconnect tail had operated. On follow up surge divertor active lead had been cut clear. | 715 KILMORE-LANCEFIELD ROAD, FORBES VIC 3764 | 33024727 |  |  |  | Defective component |  |  | 1 | Customer advised of loud bang, no supply and small grass fire at the incident location. On arrival the crew found at an EDO fuse had operated resulting in a grass fire of approx. 300mm x 300mm but There were no reported shocks or injuries. | Surge diverter | 2 | 2 | 2 |  | WND013 | mal-operation of surge diverter disconnect tail | Loss of supply;Grassfire | 29/11/2017 21:06 | 1 | Localised: less than 10 sq.m | 6811 | Agricultural |  | 20171204PWA_03 | Infrastructure (network-based) | -37.2969 | 144.8763 | 1 | Powercor | Report | 11896 | 0.036017 | 22kV AC | Wallan (Kilmore Gap) | 3764 | Forbes | Fuse
The initial cause was a failed HV underground cable transition joint and a determination was going to be made on the method of repair that was required. Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions. When the supply was restored, it was identified that white phase 16amp HV powder filled fuses had operated at "Albion-Bedford" and "Sweetland-Barcelona" substations as customers reported dim lights. The fuses were replaced and supply was restored to the customers. | 434 ELGAR ROAD, BOX HILL VIC 3128 | 7024750 |  |  |  | Conductor clashing;Electrical breakdown |  |  | 1 | At 0248hrs on 23/11/2017, BH-NW No. 66kV feeder circuit breaker along with 22kV feeder BH 23 reclosed to lockout. A HV underground cable faulted at pole No. LIS 7024750 located on the corner of Elgar Road and Hopetoun that supplied "Prospect 810-Elgar" substation. Fault current caused the blue phase HV conductor to fall to the ground in Kent Street - pole No. LIS 7037195. In addition, it appears fault current from HV conductors clashing has caused a small ground fire after the white phase lightning arrestor located at the HV CHP at the BH23 exist pole was blown out at pole No. LIS 7024833 that caused also caused conductor damage. Police are in attendance and have barricaded the area off with incident tape. | Conductor (bare);Cable;Powder filled;Surge diverter | 0 | 0 | 0 |  | BH 23 | The initial cause was a failed HV underground cable transition joint that caused clashing of HV conductors. | Grassfire | 23/11/2017 2:48 | 1 | Localised: less than 10 sq.m | 6816 | Roadway |  | 20171204UTD_03 | Infrastructure (network-based) | -37.8187 | 145.1149 | 1 | United Energy Distribution | Report | 8586 | 0.00059144 | 22kV AC;66kV AC | Moorabbin Airport | 3128 | Box Hill | Conductor
Area made safe and conduct repairs | 104 STEPHEN STREET, YARRAVILLE VIC 3013 |  | Vehicle | [5 empty] | 1 | Truck hit pole resulting in high voltage conductor falling and coming to ground. No truck details available. | Conductor (bare) | 0 | 0 | 0 |  | FE09 | Truck hit pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42898.6361 |  |  | 6825 | Residential |  | 20171206JEM_03 | Infrastructure (network-based) | -37.8164 | 144.8943 | 1 | Jemena | Report | 9819 | 0.020213 | 22kV AC | Essendon Airport | 3013 | Yarraville | Vehicle
ESV have been notified via phone, reference number 8823730. Emergency services and Jemena Network Operator attended on site, supply isolated and site made safe. Jemena is cooperating with ESV and WorkSafe and is conducting a full and thorough investigation into the incident to understand its cause. Jemena's field teams at Tullamarine and Broadmeadows came together for briefings on the afternoon after incident occurred and the next morning, and are also being provided with the support they need. Jemena Works Practices have acknowledged the section 134 letter from ESV and has started collecting the data/information to meet the target date. Jemena are planning to have the review of incident completed in February 2018 subject to the availability of Jemena personnel. | 5-9 BLANCH STREET, PRESTON VIC 3072 | [5 empty] | Not followed |  | 2 | Two electrical persons were injured while working at Blanch-Isaacs indoor substation with ring-main unit (RMU). It is understood the incident took place during routine electrical connection work for a new apartment complex adjacent to the substation. The incident is being investigated and further details will be provided. Due to the medical treatment, the work crew are not available to be interviewed until late January 2018. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | CS03 | Persons working on underground cables made contact with live electrical assets. | Medical attention (first aid/doctor/hospital) | 42928.3854 |  |  | 6827 | Public space |  | 20171207JEM_02 | Infrastructure (network-based) | -37.7453 | 144.9995 | 1 | Jemena | Report | 10857 | 0.0030937 | 22kV AC | Essendon Airport | 3072 | Preston | Other
On arrival supply isolated. Repairs where to be co-ordinated with customer REC for the customer to resume supply | UNIT 17 133-145 CUBITT STREET, CREMORNE VIC 3121 | 30187885 |  |  |  | Unknown technical factor |  |  | 2 | MFB reported a garage fire at incident location. On arrival it was found that the fire affected customerâ€™s garage. The fire appears to have started at the meter board position. There was a small ground fire (3x2 m) There were no injuries reported. | Smart meter;Meter board (including fuses) | 2 | 2 | 2 |  | R031 | Cause could not be determined by CitiPower due the extent of the fire damage to the assets | Property;Meter board | 42989.1306 | 1 | Localised: less than 10 sq.m | 6830 | Residential |  | 20171207PWA_02 | Infrastructure (network-based) | -37.831 | 144.9923 | 1 | CitiPower | Report | 8613 | 0.037891 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Cremorne | AF Other
A LEI investigated the amount of damage that occurred to customers appliances and equipment. Procedures as indicated in the work instruction for HV injections has been followed with a claim form provided to the affected customer. | 72 MONASH DRIVE, MULGRAVE VIC 3170 |  |  |  |  | HV injection |  |  | 1 | Customer called to advise they have lost their electricity supply after the storm. Following storm activity, a single customer that resides at 72 Monash Dive advised that lightning struck an unknown location. A faults truck attended and requested that a LEI attend as a HVI was suspected after the service fuse at the POA had operated. The LEI confirmed a high voltage injection occurred (CLA 1708) affecting the customer who had electrical appliances and equipment damage. | No failed asset | 0 | 0 | 0 |  | MGE 14 | Lightning strike at a unknown location. | HV injection;Loss of supply | 25/11/2017 17:00 |  |  | 6834 | Residential |  | 20171207UTD_01 | Infrastructure (network-based) | -37.9175 | 145.1639 | 1 | United Energy Distribution | Report | 8612 | 0.020926 | Low voltage AC (<1kV) | Moorabbin Airport | 3170 | Mulgrave | Lightning
A Zinfra underground crew were on site and isolated the substation and will dismantle the substation to check for damage before supply is restored. Details of the workers were obtained for the associated recoverable work costs. It is not known if a No Go Zone permit had been requested at the time of the event. | 1447 NORTH ROAD, CLAYTON VIC 3168 |  | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Builder has contacted the United Energy faults and emergencies call centre advising the substation located adjacent to 1449 North Road in Clayton has been "bumped" by a counter weight of the boom. There appears to be no visible damage to the asset and check for safety. Kiosk substation named "North N1447 - Clayton" has shifted after being struck by a crane counter-weight when working in close vicinity. At the time, the substation was alive with the LV circuit isolated. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | SVW 54 | No Go Zone breach as crane made contact with kiosk substation. Additional information request was made to the Zinfra supervisor but not much added value from the original report. | No Go Zone (contact) | 27/11/2017 15:35 |  |  | 6835 | Roadway |  | 20171207UTD_02 | Infrastructure (network-based) | -37.9138 | 145.1201 | 1 | United Energy Distribution | Report | 9765 | 0.017492 | 22kV AC | Moorabbin Airport | 3168 | Clayton | Vehicle
Site was made safe as a matter of priority due to potential for public to contact livened concrete pole. Fault crew replaced service and pole box as soon as possible, then conducted all tests to ensure all was okay | 71 MCFADZEAN AVENUE, RESERVOIR VIC 3073 | Pole no. A010691 |  |  |  | Defective component |  |  | 1 | Dog bone clamp on pole no. A010691 failed, resulting in service rubbing against hook which livened this concrete pole. There were also reports that pole was "smoking at the base". | Service conductor;Aluminium;Pole (concrete) | 0 | 0 | 0 |  | TT08 | Failure of dog bone clamp | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Melting or smoking only | 42806.3764 |  |  | 6836 | Residential |  | 20171208JEM_01 | Infrastructure (network-based) | -37.705 | 144.9975 | 1 | Jemena | Report | 8615 | 0.0078553 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | AF Other
On arrival crew confirmed site safe and arranged for replacement of assets | 111 SUFFOLK ROAD, SUNSHINE NORTH VIC 3020 | 32174763 | Copper theft | [6 empty] | A resident called to report pole damage at the front of the property at the incident location. Upon arrival the fault crew found that the cover guard protecting the u/g service installed to a pit at the front boundary of 115 Suffolk Rd had been unscrewed and the pole conduit stolen along with the underground service installed in conduit 5 (approx. route length 28m). The installation was not in service and was awaiting the customer connection request. There was no fire, injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | SSE032 | Copper theft | Damage to network assets | 23/10/2017 19:51 |  |  | 7852 | Public space |  | 20171213PWA_01 | Infrastructure (network-based) | -37.7728 | 144.8421 | 1 | Powercor | Report | 9634 | 0.022837 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Other
On arrival crew isolated supply and carried out repairs | 23 RAINBOW ROAD, WARRACKNABEAL VIC 3393 | 33050983 |  |  |  | Overheated connection |  |  |  | CFA reported sparking on a pole at the incident location. On arrival the crew found that a connection had overheated on a LV isolator causing hot debris to fall to the ground resulting in a ground fire (Approx. 30m x 40m) on private property. There were no reported injuries or third party property damages. | Disconnector/isolator;Pole mounted | 2 | 2 | 2 |  | HSM003 | Overheated connection | Grassfire | 43081.85 | 1 | Small: 10 - 1000 sq.m | 7860 |  |  | 20171214PWA_01 | Infrastructure (network-based) | -36.2403 | 142.3975 | 1 | Powercor | Report | 9645 | 0.010066 | Low voltage AC (<1kV) | Horsham Aerodrome | 3393 | Warracknabeal | Connection
On arrival The crew found no damage to our assets. | EDWARDS ROAD, TALLYGAROOPNA VIC 3634 | 33090074 |  | Bird |  |  |  |  | 1 | The CFA reported a grass fire at the incident location. On arrival the crew found that a Hawk had flashed over on our HV assets, coming to ground and causing a ground fire. The ground fire was approximately 120m X 10m. Damage was reported to the grassland and fence line, no injury was reported. | Conductor (bare) | 2 | 2 | 2 |  | SHTS NKA 1 | Bird Incident | Grassfire | 13/12/2017 10:22 | 1 | Medium: 1000 sq.m - 10 ha | 7862 | Public space |  | 20171214PWA_02 | Infrastructure (network-based) | -36.2155 | 145.4651 | 1 | Powercor | Report | 9648 | 0.035845 | 66kV AC | Shepparton Airport | 3634 | Tallygaroopna | Animal
On arrival crew isolated supply | 175 WHITCOMBES ROAD, DRYSDALE VIC 3222 | 32077808 | Vehicle | [6 empty] | A customer reported a vehicle sitting on a customer pillar and power disconnection is required at the incident location. On arrival the fault crew found that the vehicle driven into a meter pole and the pit. There was no fire, the driver was transported to hospital. | Services pit;Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | DDL021 | Vehicle collided with pillar and metering structure | Loss of supply | 24/10/2017 15:11 |  |  | 7863 | Roadway |  | 20171214PWA_03 | Infrastructure (network-based) | -38.1607 | 144.5924 | 1 | Powercor | Report | 9649 | 0.028832 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Drysdale | Vehicle
The Asplundh crew immediately contacted the United Energy Network Control Centre of the incident and advised what had occurred and confirmed there were no injuries or damage sustained. Supply was restored to the 538 customers after a 5 minute outage. United Energy management were notified and an investigation commenced. | BONEO ROAD, BONEO VIC 3939 |  |  | Blown branch/vegetation |  |  |  |  | 1 | Asplundh were working for United Energy and were completing emergency tree clearing past ACR RB0391 located in Boneo Road near Browns Road with the auto reclose suppressed. Whilst tree cutting in Boneo Road maintaining a clearance of approximately 1.5m, a gust of wind blew a small branch onto the 22kV overhead conductors resulting in ACR RB0391 to open to lockout affecting 538 customers. | Conductor (bare) | 0 | 0 | 0 |  | RBD 21 | Vegetation: Trees Incident | Loss of supply | 14/12/2017 7:58 |  |  | 7861 | Roadway |  | 20171214UTD_01 | Infrastructure (network-based) | -38.3984 | 144.8878 | 1 | United Energy Distribution | Report | 10908 | 0.015105 | 22kV AC | Moorabbin Airport | 3939 | Boneo | Trees
Crew attended and replaced connections in pole box | 158 BALLAN ROAD, WERRIBEE VIC 3030 | 30105369 |  |  |  | Corrosion |  |  | 2 | Matthew reports receiving an electric shock in his right hand thumb when he touched the metallic flexible shower rose hose. | Service conductor | 0 | 0 | 0 |  | WBE023 | Connection malfunction | Minor shock | 15/10/2017 15:30 |  |  | 7884 | Residential |  | 20171215PWA_08 | Infrastructure (network-based) | -37.8934 | 144.6329 | 1 | Powercor | Report | 9679 | 0.026522 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
Crew attended and re terminated service connections | 141 THE TERRACE, OCEAN GROVE VIC 3226 | 30063493 |  |  |  | Corrosion |  |  | 2 | Ms Rani McElligott was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and her other hand in contact with the metallic Kitchen sink. | Service conductor;Neutral screen | 0 | 0 | 0 |  | DDL011 | Deteriorated Connection | Minor shock | 42896.625 |  |  | 7885 | Residential |  | 20171215PWA_09 | Infrastructure (customer connection) | -38.2676 | 144.5316 | 1 | Powercor | Report | 9680 | 0.033395 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
A LEI attended and had to wait for the damaged krone box to be replaced and supply being restored prior to testing the installation. Inspection of the switchboard revealed damage to the neutral conductors at the neutral bar. Tested polarity and IR of consumers mains and identified damage to switchboard and spa equipment and the details were forwarded to the United Energy Customer Relations team.. A defect notice was issued to the occupiers at 186 Nepean Highway for damaged underground consumers mains and supply to number 187 was reconnected following the completion of installation tests. 14/12/2017 - REC Drew Fletcher provided Prescribed CES No. 15647382 after the fault was rectified and the switchboard upgraded. The faults crew reconnected the underground consumers mains in the pit and the LEI re-tested the installation that confirmed the fault had been rectified. | 186 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | 3302395 |  |  |  | Neutral fault;Overheated connection;Fault on customer installation |  | Phase to earth | 2 | During very hot weather, a pole fire was reported to United Energy along with notification that a customer residing at 186 Nepean Highway received an electric shock. Following a pole fire caused when a krone box opposite the property caught fire, an occupier received an electric shock from the spa and a second person received a shock from a handrail who has gone to the local hospital for a check-up. It appears the red phase conductor made contact with the neutral in the krone box caused by overheating in extremely hot weather. The fault caused current to flow from the red phase through the service neutral conductor which caused damage to equipment at the two phase property as there was 415v across single phase appliances. | Services cable;Customer installation | 0 | 0 | 0 |  |  | It appears the red phase conductor made contact with the neutral in the krone box caused by overheating in extremely hot weather. The fault caused current to flow from the red phase through the service neutral conductor. | Minor shock | 13/12/2017 17:55 |  |  | 7895 | Residential |  | 20171218UTD_02 | Infrastructure (network-based) | -38.0312 | 145.1039 | 1 | United Energy Distribution | Report | 9691 | 0.0029792 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | Pole
CEOT dispatched a fault crew to investigate and patrol the SLE-LFD 66kV line after a Reclose. The crew patrolled from pole Lis 2503181 to Lis 1613365. The crew found an Eagle had earthed out 66 kV at pole structure Lis 1613390. | SOUTH GIPPSLAND HIGHWAY, SALE VIC 3850 | 1613390 |  | Bird |  |  |  | Phase to earth | 1 | IMS 231768. An Eagle caused a fault between phases on the SLE-LFD 66kV line and fell to the ground resulting in 200 sq. metre grass fire. The CFA were on site and extinguished the fire. No damage was caused to any AusNet Services' network assets. | Conductor (bare) | 0 | 0 | 0 |  | SLE-LFD 66kV Line | Bird Incident | Grassfire | 18/12/2017 16:19 | 1 | Small: 10 - 1000 sq.m | 7907 | Other | Nature Reserve adjacent to the Latrobe River. | 20171219SPN_02 | Infrastructure (network-based) | -38.1342 | 147.0935 | 1 | AusNet Services Distribution | Report | 9708 | 0.02866 | 66kV AC | Bairnsdale Airport | 3850 | Sale | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Upon investigation it was found that a loose LV fuse hinge and a small grass fire was in the vicinity. The crew repaired the LV fuse hinge. | HAUNTED HILLS ROAD, NEWBOROUGH VIC 3825 | 596942 |  |  |  | Defective component |  |  | 2 | IMS 231769. CEOT received an incident notification of a grass fire from the CFA . The cause was a loose LV fuse hinge on the pole which resulting in hot particles falling to the ground and a small grass fire of 5 sq. m in size in the vicinity. No damage to the pole or any other network assets. PHOTOS ARE NOT AVAILABLE. | Any other type | 0 | 0 | 0 |  | MOE13 | Loose LV fuse hinge at pole. | Grassfire | 18/12/2017 18:26 | 1 | Localised: less than 10 sq.m | 7908 | Residential |  | 20171219SPN_03 | Infrastructure (network-based) | -38.2002 | 146.3253 | 1 | AusNet Services Distribution | Report | 13559 | 0.0037731 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Newborough | Fuse
CEOT dispatched a fault crew to investigate, make safe and carry out any necessary repairs. CEOT also advised the local DAO. The HV fuse and fuse tube was replaced. ZA 90 day Notification is raised in SAP to replace both hung-up EDO's with BA fuse units as per policy 64-2009. | 20 MACSFIELD ROAD, WALLAN VIC 3756 | 912838 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 231358. All supply failure. The attending AusNet Services' fault crew advised that the 6 k EDO fuse tube had candled. No fire present. | EDO fuse | 0 | 0 | 0 |  | klo24 | Candled EDO fuse tube. | Other electricity related | 22/11/2017 7:03 | 1 | Negligible: no ground fire | 7927 | Agricultural |  | 20171220SPN_01 | Infrastructure (network-based) | -37.4369 | 144.978 | 1 | AusNet Services Distribution | Report | 12826 | 0.0068808 | 22kV AC | Wallan (Kilmore Gap) | 3756 | Wallan | Fuse
CEOT dispatched a fault crew to isolate and make safe. CEOT also notified the DAO to investigate. HV intermediate concrete pole struck by lightning damaging the base and bursting the gas main directly underneath the pole's base. Pole to be replaced in conjunction with gas main. Gas company was onsite to repair gas main, Fire brigade and police also on site. No LA's on pole. | 456-458 HULL ROAD, MOOROOLBARK VIC 3138 | 1014723 |  | Lightning | [5 empty] | IMS 231792. Lightning hit pole. Small fire (4 sq. metres) in vicinity of base of pole. | Pole (concrete) | 0 | 0 | 0 |  | ldl24 | Lightning strike to concrete HV pole | Grassfire | 19/12/2017 18:30 | 1 | Localised: less than 10 sq.m | 7936 | Commercial |  | 20171221SPN_02 | Infrastructure (network-based) | -37.781 | 145.3264 | 1 | AusNet Services Distribution | Report | 9751 | 0.02661 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | Lightning
Isolated supply and repaired SWER conductor to pole top | 691 MURRABIT WEST ROAD, MURRABIT WEST VIC 3579 | 33022802 |  | Blown branch/vegetation |  |  |  |  | 1 | Crew attended to find pole had been extinguished by CFA in paddock. Crew found tree across SWER between pole # 1 and pole # 2 Murrabit West Spur. No property damage, No injuries, No reported shocks. | Conductor (bare) | 2 | 2 | 2 |  | KGT003 | Severe wind storm | Grassfire | 20/12/2017 16:36 | 1 | Small: 10 - 1000 sq.m | 7941 | Agricultural |  | 20171222PWA_01 | Infrastructure (network-based) | -35.5116 | 143.8843 | 1 | Powercor | Report | 9759 | 0.0073368 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3579 | Murrabit West | Trees
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern with traffic control required. | 13 BAYVIEW ROAD, MCCRAE VIC 3938 | 8825718 |  |  |  | Overheated connection |  |  | 2 | CFA reports that a street light is on fire in Bayview Road near the Bunarong Track. A 150w HPS lantern on pole No. LIS 8825718 located in Bayview Road near the Hocking Stuart sign caught fire and was attended to by the CFA. | Public lighting | 0 | 0 | 0 |  |  | Probable loose overheated connection within the lantern. | Pole-top fire | 22/12/2017 4:21 | 1 | Negligible: no ground fire | 7942 | Roadway |  | 20171222UTD_01 | Infrastructure (network-based) | -38.3489 | 144.9434 | 1 | United Energy Distribution | Report | 12970 | 0.034461 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | AF Other
A faults crew attended and replaced the cover guard on the stay wire. | 18 WATTLE ROAD, MCCRAE VIC 3938 | 131608 |  |  |  | Mechanical breakdown |  |  | 2 | Caller (Damian 0412 198 896) was walking past a power pole and advised his wife hurt herself. A woman was injured when walking past a pole (LIS No. 131308) located outside 18 Wattle Road. McCrae. Strands from the stay wire were frayed and she suffered an injury when she brushed it. | Guy wire | 0 | 0 | 0 |  |  | Strands on a the stay wire for the HV/LV pole were frayed, exposed and were sharp in the narrow road way. | Public safety;Other | 22/12/2017 13:00 |  |  | 7952 | Roadway |  | 20171227UTD_01 | Infrastructure (network-based) | -38.3569 | 144.9225 | 1 | United Energy Distribution | Report | 9775 | 0.014978 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | AF Other
Crew attended and replaced fuse | 146 HEALY ROAD, COBRAM VIC 3644 | 33087379 |  |  |  | Defective component |  |  | 0 | Vicfire reported grassfire started by an EDO fuse falling to the ground at the intersection of Healy Rd and Cobram South Rd. Attending crew identified fault tamer fuse had mal-operated. | Any other type | 0 | 0 | 0 |  | CME015 | Fuse maloperation | Grassfire | 26/12/2017 13:43 | 1 | Small: 10 - 1000 sq.m | 7964 | Roadway |  | 20180102PWA_05 | Infrastructure (network-based) | -35.9699 | 145.6359 | 1 | Powercor | Report | 9795 | 0.0070498 | 22kV AC | Shepparton Airport | 3644 | Cobram | Fuse
Crew arrived onsite and observed transformer missing its lid and burning. No fire on the ground (lightning in the area). Crew extinguished the fire in the transformer and replaced the Transformer with another single phase 25KVA . | 71 AIRLY ROAD, STRATFORD VIC 3862 | 2511827 |  | Lightning |  |  |  |  | 2 | IMS 231828 - all supply failure. Crew sent to investigate and found TX had been hit by lightning and caused a fire within the TX. Transformer damaged - Lid blown off transformer resulting in a small fire in the transformer. The pole structure did not have surge diverters fitted - please see the comments in the Notes and Findings tab related to our policy on fitting surge diverters on pole substations. | Transformer | 0 | 1 | 0 |  | mfa21 | Lightning strike to substation transformer. | Loss of supply;Plant/equipment | 29/12/2017 21:13 | 1 | Negligible: no ground fire | 7960 | Agricultural |  | 20180102SPN_05 | Infrastructure (network-based) | -37.9873 | 147.0769 | 1 | AusNet Services Distribution | Report | 12849 | 0.040925 | 22kV AC | Bairnsdale Airport | 3862 | Stratford | Lightning
An underground crew attended on the Saturday morning and replaced the LV distribution cabinet with supply was restored with the exception of 82-84 Williams Road as the consumers mains were damaged. A defect notice was issued and left in the letterbox and the United Energy Customer Relations department notified as the occupier may need to be contacted as a REC is required to complete repairs before supply can be restored. | 78-80 WILLIAMS ROAD, DANDENONG SOUTH VIC 3175 | Closest Pole - Asset Number = 9575750 |  |  |  | Overheated connection |  |  | 2 | Passerby states there are flames and smoke coming from a pillar in front of this property and they can hear loud popping and banging sounds. A LV Distribution cabinet caught on fire outside 78 Williams Road, Dandenong due an undetermined cause but a loose overheated connection is the probable cause. A faults crew isolated supply at "Williams- L 28 Greens" kiosk substation that affected 5 factories in the vicinity. There was extensive damage to cabling inside the cabinet and the underground supervisor elected to commence repairs in daylight tomorrow morning. | LV Pillar | 0 | 0 | 0 |  |  | The actual cause was undetermined cause but a loose overheated connection is the probable cause. | Plant/equipment | 29/12/2017 20:18 | 1 | Negligible: no ground fire | 7957 | Roadway |  | 20180102UTD_01 | Infrastructure (network-based) | -38.0108 | 145.2214 | 1 | United Energy Distribution | Report | 12971 | 0.021132 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Connection
The crew made safe and carried out appropriate repairs | 58A OSBORNE STREET, SOUTH YARRA VIC 3141 | 30217304 |  |  |  | Overheated connection |  |  | 2 | The MFB notified the CitiPower report room of a pole box fire . Upon attendance the CitiPower faults crew found the FOLCB supplying customers at 58A, 58B, 51 and 53 Osborne St, South Yarra had been damaged | Any other type | 0 | 0 | 0 |  | BC024 | overloading | Pole-top fire | 28/12/2017 13:12 | 1 | Negligible: no ground fire | 7970 | Residential |  | 20180103PWA_02 | Infrastructure (network-based) | -37.8437 | 144.9908 | 1 | CitiPower | Report | 13696 | 0.011633 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Connection
Tree trimming initiated | 623 HARSTON ROAD, HARSTON VIC 3616 | 30126897 |  | Within clearances | [5 empty] | Emergency Services reported a grass fire that occurred two days ago at the incident location and possible cause was tree branches touching the power line. Upon arrival, the Powercor crew found that tree branches contacting the power line when there is a wind. | Conductor (bare) | 0 | 0 | 0 |  | SHP014 | vegetation encroachment | Grassfire | 43160.4826 | 1 | Small: 10 - 1000 sq.m | 7971 | Roadway |  | 20180103PWA_03 | Infrastructure (network-based) | -36.4698 | 145.0898 | 1 | Powercor | Report | 11444 | 0.035912 | 22kV AC | Shepparton Airport | 3616 | Harston | Trees
A faults crew promptly attended and proceeded to isolate the light in the pit. A new order was created for the replacement of the defective lantern and the crew will return on 04/01/2018 when the traffic has subsided. | 9 DOUGLAS STREET, NOBLE PARK VIC 3174 | 9821648 |  |  |  | Overheated connection |  |  | 2 | Per MFB - a street light was on fire outside Coles. A 250w HPS lantern on pole No. LIS 9821648 located outside Coles in Douglas Street, Noble Park caught fire and self-extinguished. The cause was unknown but most likely a loose connection that overheated may have been the cause. | Public lighting | 0 | 0 | 0 |  |  | The cause was undetermined but most likely a loose connection that overheated. | Pole-top fire | 43191.0104 | 1 | Negligible: no ground fire | 7972 | Commercial |  | 20180104UTD_01 | Infrastructure (network-based) | -37.9656 | 145.1736 | 1 | United Energy Distribution | Report | 12972 | 0.038723 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | AF Other
CFA had extinguished fire Crew attended and restored supply. | 170 DEWINGS BRIDGE ROAD, GERANGAMETE VIC 3249 | 32065469 |  | Bird |  |  |  |  | 1 | VicFire report a grass fire start at the above location. A crew attended and found a bird had caused a flash - over igniting approximately 30m/sq of grass burnt in a private paddock. No injuries or damage to Powercor assets. | Conductor (bare) | 0 | 0 | 0 |  | CLC007 | Bird Incident | Grassfire | 43191.4535 | 1 | Small: 10 - 1000 sq.m | 7973 | Agricultural |  | 20180105PWA_01 | Infrastructure (network-based) | -38.4383 | 143.7394 | 1 | Powercor | Report | 9817 | 0.023657 | 22kV AC | Avalon Airport | 3249 | Gerangamete | Animal
The Downer faults crew isolated the cap bank by opening the HV fuse units and the control box. The Network Control Centre was notified and a maintenance order was created for rectification work to be completed. | 44 CALLANDER ROAD, NOBLE PARK VIC 3174 | 633975 |  |  |  | Overheated connection |  |  | 2 | Pole fire - the top of the pole outside 44 Callander Road near the corner of Jason Court was flaming, arcing and sparking for about 10 minutes but has now stopped. The power supply appears to be okay with no outage. A pole top fire occurred at pole No. LIS 0633975 located near unit 1/44 Callander Road after a failed cap bank named "Callander-Jason" failed. The cause appeared to be the failure of the LLC at the top of the fuse and the fire had self-extinguished when the faults crew arrived. | Connector/termination | 0 | 1 | 0 |  | NP 16 | The cause appeared to be the failure of the Live Line Clamp (LLC) at the top of the powder filled fuse unit. | Pole-top fire | 20/12/2017 22:35 | 1 | Negligible: no ground fire | 7982 | Roadway |  | 20180108UTD_04 | Infrastructure (network-based) | -37.9591 | 145.1785 | 1 | United Energy Distribution | Report | 12969 | 0.012315 | 22kV AC | Moorabbin Airport | 3174 | Noble Park | Connection
Jemena Network Control dispatched Network Operator to investigate and patrol feeder. Operator located fallen conductor and made safe, contacted Network Control and requested assistance to complete repairs. | 2 ALICK ROAD, TOTTENHAM VIC 3012 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Excavator contacted high voltage overhead conductor on customer's property and causing it to fall onto a truck parked underneath at ground level. | Conductor (bare) | 0 | 0 | 0 |  | TH12 | Excavator operator was working under HV overhead conductors. Ground height had also been altered. | No Go Zone (contact) | 27/11/2017 16:09 |  |  | 8988 | Commercial |  | 20180109JEM_03 | Infrastructure (network-based) | -37.8077 | 144.8517 | 1 | Jemena | Report | 10839 | 0.033172 | 22kV AC | Essendon Airport | 3012 | Tottenham | Vehicle
ESV notified via phone, reference no. 9043485 Police was notified that someone may have been injsure, but were not interested and advised Jemena to contact the owner of warehouses Jemena removed on site earths and put up new 40amp powder filled fuse for all 3 phases Substation isolated, all LV circuits disconnected and repairs to be made to HV cable in order to restore electricity to Optus tower Further theft has occurred overnight at the location between the time crew finished (at midnight) and re-attendance on the morning of 10 January 2018. | 82-96 HAMPSTEAD ROAD, MAIDSTONE VIC 3012 |  | Copper theft | [5 empty] | 0 | Jemena crew attended factory site at 82 Hampstead Rd Maidstone after Optus report of power failure. Crew found HV fuse blown and evidence of copper theft at indoor substation inside property. The complex is made up of multiple abandoned warehouses which have been guttered by thieves. Vandals have separated live high voltage cable core (while alive) with timber blocks and attempted to cut and strip back cable while section was still energised. This caused an electrical flashover but there was no concrete evidence of anyone getting hurt as a result. Nobody was on site at the time Jemena crew attended site. Photos attached in Notes and Findings section. | Cable;Copper;Powder filled | 0 | 0 | 0 |  | BY14 | Copper theft | Loss of supply;Damage to network assets | 43344.4382 |  |  | 8990 | Roadway |  | 20180109JEM_04 | Infrastructure (network-based) | -37.7764 | 144.8793 | 1 | Jemena | Report | 10858 | 0.015256 | 22kV AC | Essendon Airport | 3012 | Maidstone | Other
The Jemena Network Operator assessed the situation and made the site safe and then contacted the Jemena Control Room to dispatch JEN fault crew to make repairs to the line. Jemena Works Practices also attended on site to find out more about the incident. As this work was neither for or by Jemena personnel or contractors â€“ no further formal investigation Jemena is possible. | 2B BEACHLEY STREET, BRAYBROOK VIC 3019 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Excavator contacted with HV overhead conductor in easement south of gas switch no. 19273, southern end of Beachley Street in Braybrook. On Wednesday 29th November at approximately 09.18am, JEN 22kv TH 22 Feeder, experienced successful lockout. On further investigation initiated by Jemena Control Room, a Network Operator was dispatched to patrol JEN 22kv TH 22 Feeder line to identify any cause that may have affected the line. While the network operator was patrolling the line, he identified a third party civil contractor carrying out civil works in the vicinity of JEN 22kv TH 22 Feeder, south of MGS 19273 Southern end of Beachley St, Tottenham. As the electrical operator entered the work site to examine the line, he was approached by a site worker who informed the electrical network operator that a machine operator had made contact with the line. Upon closer examination by the Network Operator, he identified burn splash marks on the top of the excavatorâ€™s boom (arm) which had made contact with JEN 22kv TH 22 Feeder conductor, and this had created burn damage on Blue Phase bare conductor from the boom contact on the line. The Network Operator subsequently approached the machine operator on site, who denied the incident. However, with the initial evidence was presented and the site supervisorâ€™s validation, the Machine Operator followed on to admit to the incident. The Machine Operator was shaken from the incident but there were no injuries incurred by the work party or the public. The name and contact details of the Machine Operator was not taken down. The site supervisor is Luke Curry of BMD Urban Pty Ltd and subcontractor involved in the incident is from CIVILINK Pty Ltd based in Braybrook (ATF CIVIL UNIT TRUST) ESV notified via phone, reference no. 8765080 For more information or any questions, please contact Nick Mateski of Jemena Works Practices on 0417339536 | Conductor (bare);Aluminium | 0 | 0 | 0 |  | TH22 | Factors identified by Work Practices on site: â€¢ The Developers site did have a current No Go Zone VESI Permit in place. â€¢ The Machine Operator had failed to comply with Safe Approach Distances (SAD) and also failed to request the assistance of a Spotter on site while migrating through the work zone. â€¢ The work party had identified all overhead electrical assets within their work zone and implemented the safety measures as per their No Go Zone permit (a copy has been attached in Notes & Findings section) | No Go Zone (contact) | 29/11/2017 9:18 |  |  | 8998 | Industrial |  | 20180110JEM_02 | Infrastructure (network-based) | -37.7946 | 144.8489 | 1 | Jemena | Report | 10855 | 0.0042812 | 22kV AC | Essendon Airport | 3019 | Braybrook | Vehicle
ESV notified via phone, reference no. 8411363. Jemena Control Room dispatched a Network Operator to attended the site, restore the customer supply, assess the situation and made safe. This was followed by Jemena Underground fault crew's actions to restore the damaged and extract the bore machineâ€™s head from the damaged HV cable. As this work was neither for or by Jemena personnel or contractors â€“ no further formal investigation is possible. | 17 ASCOT VALE ROAD, FLEMINGTON VIC 3031 |  | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | On Thursday, 12th October at approximately 12.06pm, a third party civil contractor carrying out works for TPG Telecommunications provider at 17 Ascot vale Rd, between Wisewould St and Duncan St, Flemington, made contact with JEN High Voltage underground cable while carrying direct underground bore adjacent to JEN Underground mains. GND Civil Group had been instructed to setup their worksite on footpath, west side of Ascot vale Rd between Wisewould St and Duncan St Flemington, to direct bore an tunnel for the installation of white 50mm2 telecommunication conduit adjacent to 22kv HV Feeder FT9 Underground Cable. Upon commencing the direct bore from north end of Ascot vale Rd to South side of Ascot vale Rd, the tunnelling feral head of the boring machine had made the bore approximately 30 meters under the ground adjacent to JEN HV underground cable before making contact with JEN HV cable. As a result, the FT9 feeder circuit tripped on JEN network system which impacted 288 customers on JEN. The boring machine operator (Cameron Perry) immediately seized work and shut down the boring machine and contacted JEN Control room. The machine operator was shaken from the incident but there has been no injuries to the work party or the general public. Photos are attached in Notes and Findings section. | Cable | 0 | 0 | 0 |  | FT09 | Third party civil contractor installing communication conduits made contact and damaged HV underground cable with directional borer. Contractor did not clearly locate and/or verify location of underground assets. Factors identified by work Practices interview and attendance on site: â€¢ The work party had had DBYD plans but they were out of date. â€¢ The work party did not have No Go Zone VESI Permit. â€¢ The work party had failed to comply with Safe Approach Distances (SAD) â€¢ The work party had failed to identify all underground electrical assets with in their work zone. | Loss of supply;No Go Zone (contact) | 43079.5042 |  |  | 9005 | Public space |  | 20180111JEM_01 | Infrastructure (network-based) | -37.7852 | 144.9216 | 1 | Jemena | Report | 10874 | 0.037197 | 11kV AC | Essendon Airport | 3031 | Flemington | Dug up
Initial report: CEOT dispatched a fault crew to isolate and make safe. CEOT also notified the local DAO to investigate the incident. Final report by local DAO: Attended on-site. Completed a fire report, took photos. Obtained the name of the person who was cutting the trees and referred the details back to Damage Recoveries. The property owner's details are listed in tab 6. Other Information Sources. Arranged ad hoc inspections of the poles either side of where the tree fell into the line to check that they are OK. No damage was sustained to the HV conductors. | LAURENVALE, 1935 OLD SYDNEY ROAD, WALLAN VIC 3756 | 4718426 |  | Within clearances |  |  |  | Phase to earth | 1 | IMS 231863. Initial report: A passer by reported that a tree was leaning on power lines at the corner of Old Sydney Road and Beauview Drive, Wallan. Also a report of a small fire in the vicinity. It appears the tree may have been cut down. There are no report of any injuries to any persons. Final report: Customer was clearing pine trees on a private property when a tree fell into the SMTS - KMS 66kV line at Wallan causing the conductors to clash. Feeder CB tripped. The tree was outside of the vegetation clearance space. | Conductor (bare) | 0 | 0 | 0 |  | SMTS - KMS 66kV line | Vegetation: Trees Incident | Grassfire | 43191.766 | 1 | Small: 10 - 1000 sq.m | 9001 | Agricultural |  | 20180111SPN_02 | Infrastructure (network-based) | -37.3787 | 144.9634 | 1 | AusNet Services Distribution | Report | 11445 | 0.028973 | 66kV AC | Wallan (Kilmore Gap) | 3756 | Wallan | Trees
CEOT dispatched a fault crew to isolate and make safe. CEOT also notified the local DAO to investigate the incident. The attending crew found a dead bird on the ground with a damaged shed insulator. LIS 2709198. Crew found a grass fire of approximately 10m x 2m in size that was extinguished by the CFA. | 260 COOK ROAD, LONGWARRY VIC 3816 | 2709198 |  | Bird |  |  |  | Phase to earth |  | IMS 231845. Emergency Authorities called AusNet Services to advise that there was a broken insulator and a grass fire at base of the pole. ACR tripped. A bird had flashed over the 5 shed insulator on a steel crossarm that did have disc type bird covers installed. | Insulators | 0 | 0 | 0 |  | WGL12 | Bird Incident | Grassfire | 43191.5618 | 1 | Small: 10 - 1000 sq.m | 9002 | Agricultural |  | 20180111SPN_03 | Infrastructure (network-based) | -38.1003 | 145.7423 | 1 | AusNet Services Distribution | Report | 12850 | 0.038515 | 22kV AC | Moorabbin Airport | 3816 | Longwarry | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. HV BA fuse was replaced. No other damage reported. | MIRANDA HIGH COUNTRY WINE, 1019 SNOW ROAD, OXLEY VIC 3678 | 5103451 |  |  |  | Corrosion;Electrical breakdown |  |  | 2 | IMS 231400. An AusNet Services' fault crew attending premises for a Supply Failure. The crew reported that a High Voltage BA fuse had hung-up and candled. | Boric acid | 0 | 0 | 0 |  | wn5 | Candled BA fuse tube. | Other electricity related | 25/11/2017 12:10 | 1 | Negligible: no ground fire | 9004 | Agricultural |  | 20180111SPN_04 | Infrastructure (network-based) | -36.4407 | 146.3685 | 1 | AusNet Services Distribution | Report | 10865 | 0.041557 | 22kV AC | Wangaratta Aero | 3678 | Oxley | Fuse
Crew made repairs and restored supply | 86 BICKFORDS ROAD, RAVENSWOOD VIC 3453 | 30333711 | Working too close to overhead lines | [5 empty] | 1 | A contractor reported a crane had struck and pulled down wires at the above location. A crew attended and found a Franna crane had struck and broken one 22kV conductor and brought two others to the ground. This resulted in clashing conductors and a ground fire start btn P240 and P241A Harcourt S/L. CFA attended and extinguished fire of approx. 4 Acres in area. Damage was sustained to a number of trees and fences on private property. The site is a temporary works yard for C.P.B contractors who are constructing a new roundabout for VicRoads. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | CMN003 | Crane contacted overhead conductors | Loss of supply;Grassfire;Damage to network assets | 43374.484 | 1 | Medium: 1000 sq.m - 10 ha | 9013 | Construction |  | 20180112PWA_01 | Infrastructure (network-based) | -36.8983 | 144.2143 | 1 | Powercor | Report | 11542 | 0.029067 | 22kV AC | Bendigo Airport | 3453 | Ravenswood | Vehicle
On arrival crew isolated supply and carried out repairs | 16 WRAY STREET, ANGLESEA VIC 3230 | 30073092 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a transformer on fire at the incident location. Upon arrival, the Powercor crew found that an UG service fuse box on a pole caught fire and melted debris fell on to ground causing a small ground fire. There were no injuries. CFA attended. | Connection box | 2 | 2 | 2 |  | WPD021 | Overheated connection | Grassfire | 43405.0479 | 1 | Localised: less than 10 sq.m | 9014 | Roadway |  | 20180112PWA_02 | Infrastructure (network-based) | -38.4028 | 144.1909 | 1 | Powercor | Report | 10886 | 0.0053507 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
CEOT dispatched a fault crew to investigate, isolate, make safe and arrange for repairs. The fault crew isolated supply, made safe and arranged for the transformer changeover. EDO fuses replaced with the new transformer. | 15 PORS ROAD, NERRENA VIC 3953 | 2008120 |  | Lightning |  |  |  |  | 2 | IMS 231499. An AusNet Services' fault crew found a EDO line fuse hung-up and candled at Madison pole 19 Substation. The cause was due to lightning. | EDO fuse | 0 | 0 | 0 |  | lga14 | EDO fuse candled. | Other electricity related | 42747.1521 | 1 | Negligible: no ground fire | 9030 | Agricultural |  | 20180115SPN_03 | Infrastructure (network-based) | -38.4781 | 146.0208 | 1 | AusNet Services Distribution | Report | 10924 | 0.035604 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Nerrena | Fuse
On arrival crew inspected assets no repairs required. Design check being initiated. | 16 CAMPBELL STREET, NEWSTEAD VIC 3462 | 30031722 |  | Animal |  |  |  |  | 1 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a HV circuit which transitions from vertical to horizontal construction, causing the possum to fall to the ground and ignite a small grass fire, approximately 20M x 40M square was burnt. CFA extinguished the fire and reported the freshly deceased possum in the fire area. There were no reported injuries, no 3rd party damage, CMN002 feeder successfully reclosed. | Conductor (bare) | 2 | 2 | 2 |  | CMN002 | Animal Incident | Grassfire | 14/01/2018 22:26 | 1 | Small: 10 - 1000 sq.m | 9035 | Roadway |  | 20180116PWA_02 | Infrastructure (network-based) | -37.1137 | 144.0577 | 1 | Powercor | Report | 10921 | 0.025503 | 22kV AC | Bendigo Airport | 3462 | Newstead | Animal
On arrival crew carried out repairs. | 40 DICKENS STREET, HAMILTON VIC 3300 | 30089969 |  |  |  | Leakage |  |  | 1 | A customer advised a loud bang and power outage at the incident location. On arrival the crew found that a HV cross arm caught fire and a part of arm fell on to ground. The fallen debris from the ignited arm caused very minor grass fire at the pole base. There was no injuries or third party property damage | Crossarm (wood) | 2 | 2 | 2 |  | HTN004 | Excessive leakage current | Grassfire | 15/01/2018 11:41 | 1 | Localised: less than 10 sq.m | 9036 |  |  | 20180116PWA_03 | Infrastructure (network-based) | -37.7342 | 142.0186 | 1 | Powercor | Report | 10922 | 0.0059954 | 22kV AC | Hamilton Airport | 3300 | Hamilton | Crossarm
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. CEOT also notified the local DAO. The crew arrived on site and observed a small burnt area at the base of pole Lis 5614362 of approximately 2m x 1m in size (on the road reserve). The crew also observed a loose fuse in the LV isolator Blue phase. The crew tightened the LV fuse in LV isolator Blue phase and checked all other LV connections. | HAUNTED HILLS ROAD, HERNES OAK VIC 3825 | 5614362 |  |  |  | Overheated connection |  |  | 2 | IMS 231688. An AusNet Services' worker reported burn marks to plant and equipment at pole lis 5614362 which was caused by a loose LV fuse in LV Isolator Blue phase. | Any other type | 0 | 0 | 0 |  | moe31 | Loose fuse in LV fuse isolator. | Grassfire | 13/12/2017 15:28 | 1 | Localised: less than 10 sq.m | 7858 | Agricultural |  | 20171214SPN_01 | Infrastructure (network-based) | -38.1966 | 146.3253 | 1 | AusNet Services Distribution | Report | 9640 | 0.040981 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Hernes Oak | Fuse
Crew attended and repaired insulated lead | 36 DEANS MARSH-LORNE ROAD, DEANS MARSH VIC 3235 | 33039995 |  |  |  | Electrical breakdown |  |  | 1 | Customer reported a grass fire near one of our poles. On arrival the crew found that the Insulated cable connected to the HV fuse unit had faulted. A fire of approximately 300 mm diameter was subsequently found at the base of the pole. | EDO fuse;Dropper/bridge | 0 | 0 | 0 |  | WIN011 | Damaged HV cable | Grassfire | 13/12/2017 13:24 | 1 | Localised: less than 10 sq.m | 7871 | Roadway |  | 20171215PWA_01 | Infrastructure (network-based) | -38.3997 | 143.8859 | 1 | Powercor | Report | 9663 | 0.020461 | 22kV AC | Avalon Airport | 3235 | Deans Marsh | OH Cable
Contractor set up exclusion zone until fault crew arrived. Fault crew isolated supply and arranged for repairs to take place. | 12 WILTSHIRE BOULEVARD, THORNHILL PARK VIC 3335 | 60354212 | Working too close to underground cables | [6 empty] | Report received from a landscaping contractor that while trying to install irrigation under the footpath, he had hit mains, Upon arrival the fault crew found that the landscaper (Brian) installing the irrigation was trying to bore directly under the footpath to run an irrigation pipe for sprinklers from the nature strip back into the front yard of the property (display home) at Lot 105, #12 Wiltshire Blvd, Thornhill Park (part of Thornhill Estate Stage 1). To complete this task he was using a crowbar which he was pushing/hammering forward with the bucket attachment of his mini loader. Being a new estate with a muddy worksite/footpath area, he didnâ€™t notice that there was an electrical pit directly in his path. Brianâ€™s crowbar broke through the side wall of the service pit and pierced both the Powercor service cable entering into the pit, and the consumer mains running out of the pit to Lot 105, #12 Wiltshire Blvd. This resulted in the pit lid blowing out and Brian realising what had occurred. Brian immediately stopped and reported the incident. There was no fire, no reported injuries. | Cable;Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | contractor excavating | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/10/2017 17:15 |  |  | 7888 | Roadway |  | 20171218PWA_02 | Infrastructure (network-based) | -37.7088 | 144.6213 | 1 | Powercor | Report | 9677 | 0.039024 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Dug up
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor between the Reticulation Pole Connection Box and the Service Pole Connection Box. The attending Powercor Fault Crew replaced the existing O/H Service Cable between the Reticulation Pole and Service Pole and completed an NST Test which confirmed a Pass result. An NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 15 BIRKDALE CLOSE, ANGLESEA VIC 3230 | 32007168 |  |  |  | Corrosion |  | Phase to earth |  | Guest was in the Bathroom showering when he or she made simultaneous contact between their hand on the metal tap and bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WPD021 | Corroded service conductor | Minor shock | 18/10/2017 0:00 |  |  | 7890 | Residential |  | 20171218PWA_04 | Infrastructure (network-based) | -38.4112 | 144.1701 | 1 | Powercor | Report | 9686 | 0.030382 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | OH Cable
On arrival crew carried out repairs. REC undertook some isolation within the installation | 4 KINGSTON COURT, SMYTHES CREEK VIC 3351 | 32007168 |  |  |  | Fuse failed to eject |  |  | 0 | Vic Fire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated. The barrel of the EDO fuse stayed in position without dropping down. The barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve and private property. There were no reported injuries . | EDO fuse | 2 | 2 | 2 |  | BAS021 | EDO fuse mal-operation | Property;Grassfire | 15/12/2017 18:00 | 1 | Small: 10 - 1000 sq.m | 7891 |  |  | 20171218PWA_05 | Infrastructure (network-based) | -37.5896 | 143.7574 | 1 | Powercor | Report | 9685 | 0.029705 | 22kV AC | Ballarat Aerodrome | 3351 | Smythes Creek | Fuse
On arrival crew carried out repairs | 4 OGRADY STREET, CLIFTON HILL VIC 3068 | 30173048 | Vehicle | [6 empty] | A passer-by (Phillip) reported that a garbage truck (Rhino Bin Hire) has struck a stay and has been flicked into the overhead lines at the incident location. On arrival the fault crew found that the stay wire had been broken no contact appears to have been made with the overhead lines at the incident location. No truck details obtained, truck had left the scene. There was no ground fire and no injury as a result of this incident. | Guy wire | 2 | 2 | 2 |  | F028 | Garbage truck entangled in stay wire | Damage to network assets | 30/10/2017 14:55 |  |  | 7903 | Roadway |  | 20171219PWA_01 | Infrastructure (network-based) | -37.7876 | 144.9976 | 1 | CitiPower | Report | 9699 | 0.030797 | Not applicable | Essendon Airport | 3068 | Clifton Hill | Vehicle
The crew made the site safe, and repaired the connection. | 174 FULHAM ROAD, TORRUMBARRY VIC 3562 | 33017122 |  |  |  | Corrosion |  |  |  | The CFA reported a grass fire at the incident location. On arrival the crew found that a â€œTâ€ Clamp had faulted at the incident location. The ground fire was approximately 100m X 250m. Damage was reported to the grassland only, no injury was reported. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | CHA005 | Corroded connection | Grassfire | 42959.4479 | 1 | Medium: 1000 sq.m - 10 ha | 7910 | Agricultural |  | 20171219PWA_03 | Infrastructure (network-based) | -36.0126 | 144.555 | 1 | Powercor | Report | 9714 | 0.003162 | 22kV AC | Bendigo Airport | 3562 | Torrumbarry | Connection
Crew have replaced/repaired the earth cables | 178-198 PAYNES ROAD, THORNHILL PARK VIC 3335 | 30238216 | Copper theft | [6 empty] | Rod, from ELECTRIX reported HV earth stolen from a pole substation. A crew attended and found that HV cable earths were cut and removed from pole LIS-996049. No shock, injuries or third party damage. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 42746.7736 |  |  | 7913 | Roadway |  | 20171219PWA_06 | Infrastructure (network-based) | -37.7184 | 144.6358 | 1 | Powercor | Report | 9719 | 0.033382 | Earthing cable | Laverton Raaf | 3335 | Thornhill Park | Other
CEOT dispatched a fault crew to make safe and investigate. The crew found a small 1 metre square fire at the LV pillar. Work crews isolated cct at substation PLENTY RIVER STH. LV pillar replaced. | 2 GOONYAH COURT, GREENSBOROUGH VIC 3088 | 5720887 |  |  |  | Electrical breakdown |  | Phase to phase |  | IMS 231770. CEOT received an incident report from the Fire Brigade of a fire at a transformer. The fire was actually found to be a small 1m square ground fire at a LV pillar. LV pillar blown and caught fire due to an internal short circuit fault. | LV Pillar | 0 | 0 | 0 |  | elm31 | Root cause not designated in IMS but appears to be a 3 phase short circuit. Request made to Engineering to investigate. | Other vegetation | 18/12/2017 22:38 | 1 | Localised: less than 10 sq.m | 7909 | Residential |  | 20171219SPN_04 | Infrastructure (network-based) | -37.6908 | 145.1041 | 1 | AusNet Services Distribution | Report | 9712 | 0.016321 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | AF Other
On arrival crew carried out repairs | 1514 MT CLAY ROAD, TYRENDARRA VIC 3285 | 30091494 |  |  |  | Candled fuse |  |  | 0 | A Fault crew attending following an outage found that an Boric Acid fuse had operated at the incident location, however the barrel of the Boric Acid fuse stayed in position without dropping down. The barrel then caught fire. There was no ground fire. There were no reported injuries or third party property damages. | Boric acid | 2 | 2 | 2 |  | PLD001 | Fuse barrel hung up | Pole-top fire;Loss of supply | 42777.5826 | 1 | Negligible: no ground fire | 7917 | Agricultural |  | 20171220PWA_01 | Infrastructure (network-based) | -38.2227 | 141.7552 | 1 | Powercor | Report | 9723 | 0.014079 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3285 | Tyrendarra | Fuse
The crew replaced the stolen earth. | 237-269 SINCLAIRS ROAD, DEANSIDE VIC 3336 | 31023184 | Copper theft | [6 empty] | Electrix contractors reported that the earth has been stolen form the substation at the incident location. On arrival the fault crew found that the high voltage earth (copper cable) had been removed from the substation between ground level and half way up the pole. There was no ground fire and no injury as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 42805.4806 |  |  | 7918 | Roadway |  | 20171220PWA_02 | Infrastructure (network-based) | -37.7363 | 144.7072 | 1 | Powercor | Report | 9724 | 0.023978 | Earthing cable | Laverton Raaf | 3336 | Deanside | Other
On arrival crew isolated line and carried out repairs. | 800 TOOLAMBA ROAD, TOOLAMBA VIC 3614 | 32189917 |  |  |  | Mechanical breakdown |  |  | 1 | The CFA reported a grass fire at the incident location. On arrival the crew found that a HV Splice had faulted at Tee Pole 118 and the conductor had come to ground between Tee pole 118 and pole 1 causing a ground fire. On further inspection it was found that a bird had flashed over at pole 1 Waugh spur. Damage was reported to grassland only, no injury was reported. | Conductor (bare) | 2 | 2 | 2 |  | MNA034 | Bird Incident | Grassfire | 19/12/2017 12:31 | 1 | Small: 10 - 1000 sq.m | 7926 | Agricultural |  | 20171220PWA_03 | Infrastructure (network-based) | -36.4576 | 145.3257 | 1 | Powercor | Report | 9736 | 0.0088484 | 22kV AC | Shepparton Airport | 3614 | Toolamba | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the reticulation Pole, The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 164 MURLONG STREET, SWAN HILL VIC 3585 | 31021817 |  |  |  | Corrosion |  | Phase to earth |  | Mr Neil Roberts was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hands on the metal Shower Taps and his bare feet while standing on the wet shower base. | Service conductor;Connector/termination | 2 | 2 | 2 |  | SHL007 | Corroded connection at pole end | Minor shock | 25/10/2017 9:00 |  |  | 7929 |  |  | 20171220PWA_04 | Infrastructure (network-based) | -35.3431 | 143.5438 | 1 | Powercor | Report | 9740 | 0.023786 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
CEOT dispatched a fault crew to make safe and repair. Fault crew attended and replaced the EDO fuse holder /tube and fuse link. A ZA 90 day Notification to be raised in SAP to replace hung-up/candled EDO's with BA fuse units as per policy 64-2009. | 4413 STRZELECKI HIGHWAY, BOOROOL VIC 3953 | 2002447 |  |  |  | Age;Corrosion;Electrical breakdown |  |  | 2 | IMS 231401. AusNet Services' fault crew attended a fault call and found a candled EDO fuse tube on CASTLEDOON Substation. No fire on ground or on pole. | EDO fuse | 0 | 0 | 0 |  | lga11 | Burnt EDO fuse tube. | Other electricity related | 26/11/2017 10:00 | 1 | Negligible: no ground fire | 7932 | Agricultural |  | 20171220SPN_04 | Infrastructure (network-based) | -38.4336 | 146.0371 | 1 | AusNet Services Distribution | Report | 9743 | 0.020578 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Boorool | Fuse
Incident was phoned into ESV, call reference number 8878564. The Jemena Network Operator assessed the situation and made the site safe, then contacted the Jemena Control Room to dispatch JEN fault crew to make repairs by re-sleeving the HV conductor which sustained minor damage. As this work was neither for or by Jemena personnel or contractors â€“ no further formal investigation is possible. If ESV requires more information, please contact Nick Mateski from Jemena Works Practices. | 27-29 TRANSPORT DRIVE, SOMERTON VIC 3062 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | On Thursday 14th December at approximately 08.40am, JEN 22kv ST13 Feeder, experienced reclose to lockout. On further investigation initiated by Jemena Control Room, a Network Operator was dispatched to patrol JEN 22kV ST13 feeder line to identify any cause that may have affected the line. While the Network Operator was patrolling the line, he identified a third party civil contractor working for Yarra Valley Waters, carrying out civil works direct underneath of JEN 22kV ST13 Feeder overhead conductors, between pole numbers A084000 and A006405 in Transport Drive, Somerton. As the electrical operator entered the work zone to examine the line, he was approached by a site foreman who informed the Network Operator that machine operator had made contact with the HV overhead line. Upon closer examination, the Network Operator identified burn splash marks on the top of the excavatorâ€™s boom (arm) which had made contact with JEN 22kV ST13 Feeder overhead conductor. The Network Operator concluded that the splash marks were the result of burn damage when the boom contacted red Phase of bare overhead conductor. The Machine Operator (John Maurici) was shaken from the incident but there were no injuries incurred by the work party or the public. | Conductor (bare) | 0 | 0 | 0 |  | ST13 | Factors identified by Work Practices on site: â€¢ The contractor on site, did have a current No Go Zone VESI Permit in place which covered all underground JEN assets, but failed to declare the excavation underneath our overhead line to the JEN No GO Zone Assessor. (see PDF of No Go Zone Inspection Report attached in "Notes and Findings" section) â€¢ The Machine Operator had failed to comply with Safe Approach Distances (SAD) and request the assistance of a Spotter on site while working close to JEN overhead bare conductors â€¢ The work party had identified the overhead electrical assets within their work zone and implemented the safety measures, but the safety measurers had been ignored by the machine operator â€¢ JEN overhead bare conductors have been measured on site by the Network Operator, which are compliant as per JEN standards and clearances. | No Go Zone (contact);Damage to network assets | 14/12/2017 8:40 |  |  | 7948 | Commercial |  | 20171222JEM_01 | Infrastructure (network-based) | -37.6379 | 144.9544 | 1 | Jemena | Report | 9771 | 0.017634 | 22kV AC | Essendon Airport | 3062 | Somerton | Vehicle
Tree removed and line repaired prior to restoration | 35 ZEERUST ROAD, CONGUPNA VIC 3633 | 33093453 |  | Alive;Fallen |  |  |  |  | 1 | Powercor crew locating fault found that a tree had fallen, bringing down conductor and resulting in a small grass fire | Conductor (bare) | 0 | 0 | 0 |  | SHN011 | Vegetation: Trees Incident | Grassfire | 26/12/2017 14:06 | 1 | Localised: less than 10 sq.m | 7965 | Roadway |  | 20180102PWA_06 | Infrastructure (network-based) | -36.2801 | 145.4284 | 1 | Powercor | Report | 9797 | 0.018701 | 22kV AC | Shepparton Airport | 3633 | Congupna | Trees
Crew attended and replaced fuse box on pole prior to restoration | 430 BALWYN ROAD, BALWYN NORTH VIC 3104 | 30186091 |  |  |  | Overheated connection |  |  |  | MFB reported a pole fire at the above incident location. On arrival, the crew found that the overhead line fuse box unit had overheated and caught on fire. | Any other type | 0 | 0 | 0 |  | WD021 | connection malfunction | Pole-top fire | 26/12/2017 20:43 | 1 | Negligible: no ground fire | 7966 | Residential |  | 20180102PWA_07 | Infrastructure (network-based) | -37.7855 | 145.0869 | 1 | CitiPower | Report | 9799 | 0.031672 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | Connection
Crew attended and removed service | 282 CRETE ROAD, ROBINVALE VIC 3549 | 33061544 |  | Within clearances | [5 empty] | Vic Fire reported grass fire and powerline down at intersection of Robinvale-Sea Lake Road and Crete Road Robinvale. Attending crew found service line to unoccupied house was on the ground and a small grass fire had occurred | Service conductor | 0 | 0 | 0 |  | RVL001 | Vegetation: Trees Incident | Grassfire | 29/12/2017 23:02 | 1 | Localised: less than 10 sq.m | 7967 | Residential |  | 20180102PWA_08 | Infrastructure (network-based) | -34.6173 | 142.7695 | 1 | Powercor | Report | 9801 | 0.0068843 | Low voltage AC (<1kV) | Mildura Airport | 3549 | Robinvale | Trees
Jemena installed cover around overhead service conductor and issued 5 day defect, but supply was left on. A faults crew is scheduled to disconnect overhead service and have underground supply installed in the morning of 10 January 2018. At the time of writing, a truck visit to customer has been scheduled for 17 January 2018. | 11 KENTWOOD ROAD, MACLEOD VIC 3085 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Jemena was informed by LEI Geoff Jackson at Techsafe of January 17 2018 that he noticed overhead service resting on the metal roof a a new structure at the front of the property he was passing in the vicinity of his own residence. The customer had erected a cubby house over the weekend (6 and 7 January 2018) in front of property, resulting in an overhead neutral screen service cable laying directly on top of the tin roof of the cubby house. Geoff Jackson immediately advised Jason Ford of Jemena Compliance to investigate and ensure that the site was made safe pending permanent arrangements to relocate the overhead service cable. Photos have been attached in the Notes & Findings section. | Service conductor;Neutral screen | 2 | 2 | 2 |  | NH02 | Customer erected a cubby house in front of property which came into contact with overhead service conductor | No Go Zone (no contact) | 43313.3549 |  |  | 7978 | Residential |  | 20180108JEM_02 | Infrastructure (network-based) | -37.7197 | 145.0917 | 1 | Jemena | Report | 9824 | 0.024278 | Low voltage AC (<1kV) | Essendon Airport | 3085 | Macleod | Other
CEOT dispatched a fault crew to the area as an outage had occurred in the area. The CEOT notified the local DAO to investigate the incident. The fault crew attended and made safe. The fault crew and a construction party isolated and repaired the catenary wire and HV ABC. Deteriorated HV ABC was previously identified for replacement. It has been surveyed and is programmed to be replaced shortly. | 2 KANGAROO GROUND-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113 | 1206325 |  |  |  | Electrical breakdown |  | Phase to earth | 1 | IMS 231899. Report of a grass fire outside opposite 2 Kangaroo-Warrandyte Rd, North Warrandyte. Burnt out HV ABC and catenary wire. CFA had attended. The DAO observed High Voltage Aerial Bundle Cable (HVABC) catenary wire burnt through between approximately 35 metre span of HVABC from lis 1206325 to lis 1206327 (RW 757 manual gas switch). Unable to see HVABC damage. No signs of grass fire, some minor burns to tree branched debris, damp mud area possibly as result from fire truck attending fire - mainly green grass observed. Feeder CB tripped. | Conductor (ABC) | 0 | 0 | 0 |  | RWN34 | The catenary wire shorted to HVABC conductor. | Other vegetation | 43252.3917 | 1 | Localised: less than 10 sq.m | 7981 | Residential |  | 20180108SPN_01 | Infrastructure (network-based) | -37.7355 | 145.2228 | 1 | AusNet Services Distribution | Report | 12851 | 0.039167 | 22kV AC | Moorabbin Airport | 3113 | North Warrandyte | OH Cable
A faults crew attended and replaced the damaged pole mounted FOLCB and supply was restored to the two units. The cause was attributed to a probable loose overheated connection with the location a short distance to Port Phillip Bay. | 2A-2B DUDLEY GROVE, EDITHVALE VIC 3196 | 3302798 |  |  |  | Overheated connection |  |  | 2 | Caller reports of a transformer fire on the corner of Denman Avenue and Dudley Grove, Edithvale. A two phase FOLCB that contained an underground service that supplied 2A and 2B Dudley Grove was burnt out and molten metal fell onto the dry grass below and started a small fire at the base of the pole that was quickly extinguished. | Cable;Connection box | 0 | 0 | 0 |  |  | The cause was attributed to a probable loose overheated connection with the location a short distance to Port Phillip Bay. | Grassfire | 43282.8542 | 1 | Localised: less than 10 sq.m | 7976 | Residential |  | 20180108UTD_03 | Infrastructure (network-based) | -38.0364 | 145.106 | 1 | United Energy Distribution | Report | 12974 | 0.016413 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Edithvale | Connection
An ACE Public Lighting crew promptly attended and replaced the fire damaged 150w HPS lantern, PE cell and re-terminated the burnt off 6mm cable ends. The light was tested and had been successfully repaired. | 452A HAMPTON STREET, HAMPTON VIC 3188 | 1818498 |  |  |  | Overheated connection |  |  | 2 | During public lighting fault rectification activities, a fire damaged lantern was identified. A 150w HPS lantern on pole No. LIS 1818498 located outside 454 Hampton Street had previously caught fire and self-extinguished. The cause was unknown but most likely a loose connection that overheated may have been the cause. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated may have been the cause. | Pole-top fire | 42898.5306 | 1 | Negligible: no ground fire | 8991 | Roadway |  | 20180109UTD_03 | Infrastructure (network-based) | -37.9369 | 145.0028 | 1 | United Energy Distribution | Report | 12962 | 0.023046 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton | Connection
An ACE Public Lighting crew promptly attended and replaced the fire damaged 250w HPS lantern, PE cell and re-terminated the burnt off 6mm cable ends. The light was tested and had been successfully repaired. | 594 SPRINGVALE ROAD, WHEELERS HILL VIC 3150 | 8805524 |  |  |  | Overheated connection |  |  | 2 | During public lighting fault rectification activities, a fire damaged lantern was identified. A 250w HPS lantern on pole No. LIS 8805524 located outside 594 Springvale Road had previously caught fire and self-extinguished. The cause was unknown but most likely a loose connection that overheated may have been the cause. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated may have been the cause. | Pole-top fire | 43051.384 | 1 | Negligible: no ground fire | 8992 | Roadway |  | 20180109UTD_04 | Infrastructure (network-based) | -37.9078 | 145.1611 | 1 | United Energy Distribution | Report | 12963 | 0.025559 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Wheelers Hill | Connection
A faults crew attended and assessed the tree was safe for now and an order was created for the tree to be trimmed later this week near pole No. LIS 2333019. | 325 EAST BOUNDARY ROAD, BENTLEIGH EAST VIC 3165 | 2333019 |  | Blown branch/vegetation |  |  |  |  | 2 | A caller reports that a tree branch had fallen onto the HV wires 2 days ago during the extreme weather and caught on fire as it fell to the ground. He has concerns as the tree remains in close proximity to the HV line. A customer notified the United Energy faults and emergencies call centre of a fallen tree branch that apparently caught fire as it dropped to the ground possibly on Saturday afternoon as the cool wind change occurred. The council tree is located underneath the NB-HTS 66kV feeder, 11kV OE 04 feeder and a LV street circuit with United Energy records showing there was no faults or outages in this area on Saturday. | Conductor (bare) | 0 | 0 | 0 |  | NB-HTS 66kV, OE 04 11kV and a LV street circuit. | Vegetation: Trees Incident | Other vegetation | 43313.509 | 1 | Negligible: no ground fire | 8993 | Roadway |  | 20180109UTD_05 | Infrastructure (network-based) | -37.9087 | 145.061 | 2 | United Energy Distribution | Report | 12975 | 0.040519 | 66kV AC | Moorabbin Airport | 3165 | Bentleigh East | Trees
On arrival crew isolated supply and carried out repairs | OLD PETERBOROUGH ROAD, PETERBOROUGH VIC 3270 | 30251713 |  | Bird |  |  |  |  | 1 | Customer called to report no supply, On arrival the Powercor crew found one strand of the steel conductor had unravelled and a fire of approximately 1 ac had occurred. On further inspection, the deteriorated carcass of a pelican was found near the conductor damage indicating that this may have previously initiated the conductor damage Fire had been extinguished by CFA, There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBL012 | Bird Incident | Grassfire | 43374.9097 | 1 | Medium: 1000 sq.m - 10 ha | 9003 | Agricultural |  | 20180111PWA_01 | Infrastructure (network-based) | -38.5662 | 142.8599 | 1 | Powercor | Report | 11495 | 0.016125 | 22kV AC | Warrnambool Airport Ndb | 3270 | Peterborough | Animal
The crew made safe, replacing both poles. | 2112 CHARLTON-THALIA ROAD, TEDDYWADDY WEST VIC 3527 | 32029041 |  | Animal |  |  |  |  | 1 | Vic Fire reported grass fire at the incident location but fire start was not initially thought to be connected to Powercor assets . On arrival the crew found two fire damaged poles. The following day it was identified ( CFA investigation) that the fire start was related to Goanna at LIS 602961, starting a grass fire of approx. 100HA, damaging shedding & fencing and destroying an unoccupied dwelling. There were no reported shocks or injuries. | Conductor (bare);Pole (wood);Crossarm (steel) | 2 | 2 | 2 |  | CTN003 | Animal Incident | Grassfire | 43344.8306 | 1 | Large: more than 10 ha | 9006 | Agricultural |  | 20180111PWA_02 | Infrastructure (network-based) | -36.1574 | 143.2727 | 1 | Powercor | Report | 10871 | 0.039541 | 22kV AC | Swan Hill Aerodrome | 3527 | Teddywaddy West | Animal
ESV notified via phone, reference no. 9080993 Oil spill to be cleaned up | 82-96 HAMPSTEAD ROAD, MAIDSTONE VIC 3012 |  | Copper theft | [5 empty] | 2 | Thieves have returned to steal transformer after previous copper theft in same location on 9 January 2018. Transformer hampstead 82-williamson has been completely removed from site. Photos have been attached in Notes & Findings section. | Cable;Copper;Powder filled | 0 | 1 | 0 |  | BY14 | Copper theft | Damage to network assets | 14/01/2018 12:06 |  |  | 9021 | Commercial |  | 20180114JEM_01 | Infrastructure (network-based) | -37.7764 | 144.8793 | 1 | Jemena | Report | 10904 | 0.013183 | 22kV AC | Essendon Airport | 3012 | Maidstone | Other
On arrival crew carried out repairs. LEI attended to incident to investigate potential HVI damage | 47 MCNEILL STREET, ARARAT VIC 3377 | 32109235 |  |  |  | Leakage |  |  | 1 | A customer advised loud bang at the incident location. On arrival the crew found, that HV conductor fell on to LV due to damaged cross arm. There was suspected HVI damage to around 10 houses. There was no ground fire or injuries reported. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | ART031 | Excessive leakage current | Pole-top fire;HV injection;Loss of supply | 43435.5389 | 1 | Negligible: no ground fire | 9022 | Roadway |  | 20180115PWA_01 | Infrastructure (network-based) | -37.2764 | 142.9335 | 1 | Powercor | Report | 10894 | 0.037481 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3377 | Ararat | Crossarm
On arrival crew carried out repairs | 257 HIGH STREET, NORTHCOTE VIC 3070 | 30190763 |  |  |  | Unknown technical factor |  |  |  | Street light fire outside 257 High st Northcote. There was no ground fire, no reported injuries and no third party property damage. There were no photos taken at time of incident. | Public lighting | 2 | 2 | 2 |  | NC005 | No cause located | Pole-top fire | 42806.9215 | 1 | Negligible: no ground fire | 9027 | Roadway |  | 20180115PWA_04 | Infrastructure (network-based) | -37.7727 | 144.9983 | 1 | CitiPower | Report | 10906 | 0.028833 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | AF Other
A LEI and faults truck attended and identified a severely corroded neutral at the consumers FMJB was the cause after 110v was measured on the installations earthing system. The REC who had remained on site, provided non-prescribes CES No. 231741802 after he replaced the consumers defective FMJB. The LEI re-tested the installation that confirmed the fault had been rectified and supply was left on. | 27 FORD STREET, RYE VIC 3941 | 1303079 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | REC is reporting that he received electric shocks from the metal fixtures at the property and the lights are dimming under load. REC believes the fault is from a bad neutral in the service wire as he has measured current on the earthing system. A REC contacted the United Energy faults and emergencies call centre after the occupier had contacted him following an electric shock and the lights had been dimming at the property. When questioned, the REC said that no electric shock had been received and he was in attendance for dim lights only. | Connection box;Customer installation | 0 | 0 | 0 |  |  | No electric shock was received. | Minor shock | 43405.5521 |  |  | 9034 | Residential |  | 20180116UTD_01 | Infrastructure (network-based) | -38.3656 | 144.7913 | 1 | United Energy Distribution | Report | 10919 | 0.019281 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Conductor
The crew isolated the line and repaired conductor. | 506 HANSEN ROAD, BAMAWM VIC 3561 | 33083603 | Working too close to overhead lines | [5 empty] | 1 | A customer called to advise a load had contacted a wire at the incident location. A crew found a load on a tractor had contacted a 22kV conductor, breaking 1 strand of conductor. Protection operated. There was no fire, no reported shocks, injuries or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | SHP012 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43405.5597 |  |  | 9039 | Roadway |  | 20180117PWA_01 | Infrastructure (network-based) | -36.2857 | 144.6393 | 1 | Powercor | Report | 10930 | 0.012505 | 22kV AC | Bendigo Airport | 3561 | Bamawm | Vehicle
On arrival crew carried out repairs | 561-569 ANDERSONS ROAD, DRYSDALE VIC 3222 | 32083675 |  |  |  | Candled fuse |  |  |  | A passer-by reported something dropped from pole and started a grass fire at the incident location. Upon arrival, the Powercor crew found that a grass fire (approx. 3 acres area) in the vicinity of the pole. There were no injuries. The grass fire on a private property and it caused minor fire damage to fence. No other damage identified by the crew. | Powder filled | 2 | 2 | 2 |  | DDL012 | candled Powder Filled Fuse | Grassfire | 18/01/2018 14:18 | 1 | Medium: 1000 sq.m - 10 ha | 9052 | Roadway |  | 20180119PWA_01 | Infrastructure (network-based) | -38.1927 | 144.6113 | 1 | Powercor | Report | 10947 | 0.0067928 | 22kV AC | Avalon Airport | 3222 | Drysdale | Fuse
The substation has been isolated by the attending crew. A group of LEIâ€™s to attend to assess damage to the local residents premises | 3 JAMES STREET, SUNSHINE WEST VIC 3020 | 32165615 |  |  |  | Unknown technical factor |  |  |  | A local resident reported losing power at 10:20, followed by other customers reporting a large bang and power loss at the incident location. On arrival the fault crew found that the neutral connection had burnt off at the James-Whitesides, 200kVA substation. About 176 customers may have been affected by voltage surges. There was no ground fire and no injury as a result of this incident. | Pole mounted;Connector/termination | 2 | 2 | 2 |  | SU035 | Neutral connection burnt off at substation | Loss of supply;Significant disruption to the community;Less than $50k damage;More than $50k damage | 19/01/2018 10:20 |  |  | 9054 | Residential |  | 20180119PWA_03 | Infrastructure (network-based) | -37.7847 | 144.8001 | 1 | Powercor | Report | 10951 | 0.011105 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Connection
On arrival the crew replaced carried out repairs and supply restored. | 159 ALEXANDRA AVENUE, TOORAK VIC 3142 | 30216322 |  |  |  | Corrosion |  |  |  | The MFB reported a pole fire at the incident location. On arrival the fault crew found that a FMJB had overheated burning material fell to the ground igniting a small grass fire at the base of the pole , fire self-extinguished. There was no injury as a result of this incident. | Connection box | 2 | 2 | 2 |  | TK001 | Overheated connection | Grassfire | 19/01/2018 2:00 | 1 | Localised: less than 10 sq.m | 9055 | Roadway |  | 20180119PWA_04 | Infrastructure (network-based) | -37.8322 | 145.0064 | 1 | CitiPower | Report | 10954 | 0.034112 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Connection
Jemena network operator isolated transformer (HV and LV) and made site safe A SILV is on issue to make customer LV switchboard safe | 27 INDWE STREET, WEST FOOTSCRAY VIC 3012 | INDWE 27-CALA | Copper theft | [5 empty] | 2 | Jemena crew found ground-type transformer stolen and customer switchboard vandalised. Site is being demolished. Nobody else was on site at the time and there was no evidence of anyone being injured as a result of incident. Photos have been attached in the "Notes and Findings" section | Transformer | 0 | 1 | 0 |  | FW09 | Copper theft | No Go Zone (contact) | 22/01/2018 7:00 |  |  | 9063 | Industrial |  | 20180122JEM_01 | Infrastructure (network-based) | -37.8041 | 144.8648 | 1 | Jemena | Report | 10970 | 0.035082 | Not applicable | Essendon Airport | 3012 | West Footscray | Other
LEI attended site and identified >40 volts (AC) on water meter, customers earthing system and all bonded metallic parts of the installation. Attending LEI identified a severely corroded neutral at the customers FOLCB, Jemena's service crew attended site and replaced neutral screen service and re-made connections. An NST test was carried out at the meter position and verified a PASS result. | 1 BRADFORD COURT, BRAYBROOK VIC 3019 |  |  |  |  | Corrosion |  |  | 2 | Western water contractor was digging the damp soil to repair a water leak at a meter where he made contact between the metal fence (colour bond fencing) and the meter simultaneously. | Neutral screen | 2 | 2 | 2 |  |  | Attending LEI identified a severely corroded neutral at the customers FOLCB, Jemena's service crew attended site and replaced neutral screen service and re-made connections. | Minor shock | 22/01/2018 13:41 |  |  | 9072 | Residential |  | 20180122JEM_02 | Infrastructure (network-based) | -37.7824 | 144.8627 | 1 | Jemena | Report | 10983 | 0.038664 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
On arrival crew carried out site inspection , no damage found. Region 22 CFA was contacted but no report of a call to attend this site in last 10 days. | MCCRACKEN ROAD, SHEPPARTON NORTH VIC 3630 | 33094747 |  | Bird | [5 empty] | A customer reported a burnt area of ground around a pole at the incident location. The customer requested a crew attended to inspect the Substation pole. A crew attended and found an area approx. 25m x 25m burnt around the base of P70 Boulevard S/L. A dead magpie was found at the base of the pole. Crew suspect the bird had flashed over and fallen to the ground causing the fire start. This fire had occurred sometime previous to today. No damage to pole or third party assets. There were no reported shocks or injuries. | Pole mounted | 2 | 2 | 2 |  | SHN021 | Bird Incident | Grassfire | 19/01/2018 11:32 | 1 | Small: 10 - 1000 sq.m | 9057 | Peri-urban |  | 20180122PWA_01 | Infrastructure (network-based) | -36.3107 | 145.3691 | 1 | Powercor | Report | 10959 | 0.016325 | 22kV AC | Shepparton Airport | 3630 | Shepparton North | Animal
On arrival crew carried out repairs | WESTERN HIGHWAY, NHILL VIC 3418 | 30077028 |  |  |  | Unknown technical factor |  |  | 1 | CFA reported a ground fire start near a Powercor pole at the incident location. CFA attended and extinguished fire. A crew attended and found an area of approx. 1acre burnt around the base of the pole. Protection operated. There were no reported shocks or injuries. | Surge diverter | 2 | 2 | 2 |  | NHL016 | Surge divertor tail had operated | Grassfire | 19/01/2018 10:51 | 1 | Medium: 1000 sq.m - 10 ha | 9061 | Public space |  | 20180122PWA_02 | Infrastructure (network-based) | -36.3505 | 141.634 | 1 | Powercor | Report | 10967 | 0.039787 | 22kV AC | Horsham Aerodrome | 3418 | Nhill | Fuse
Emergency LV switching was completed and an underground crew replaced the damaged LV pillar. 3 x 250amp fuses were replaced at "Kilburn-Palmerston " substation and the LV parallels removed to restore the system back to normal. | 13 PALMERSTON CRESCENT, WHEELERS HILL VIC 3150 | 8808475 (Closest) |  | Heat |  | Overheated connection |  |  | 1 | Customers supplied from "Kilburn-Palmerston " substation advised of a loss of their electricity supply. During warm humid conditions, a LV pillar located in the front yard of 14 Palmerston Street caught fire and damaged surrounding plants. The fault caused 3 x LV circuit fuses at "Kilburn-Palmerston " substation to operate and a underground crew were called to replace the damaged LV pillar. LV parallels were installed to restore supply to customers in the area. The probable cause was a loose connection that caused overheating to occur and the dry grass to catch on fire in the LV pillar. | LV Pillar | 0 | 0 | 0 |  |  | The probable cause was a loose connection that caused overheating to occur and the dry grass to catch on fire in the LV pillar. | Other vegetation | 22/01/2018 17:35 | 1 | Localised: less than 10 sq.m | 9081 | Residential |  | 20180123UTD_02 | Infrastructure (network-based) | -37.9093 | 145.1956 | 1 | United Energy Distribution | Report | 12983 | 0.00015394 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Wheelers Hill | Connection
The crew removed the service (made safe). | 491 BRUNSWICK ROAD, BRUNSWICK WEST VIC 3055 | 30157176 | Unauthorised work | [6 empty] | A customer reported that an excavator has pulled down a service and has left it wrapped around the pole at the incident location. On arrival the fault crew found that an excavating company had pulled down a service from a house to be demolished and the service was left wrapped around the pole, still â€œALIVEâ€ and in reach of passers-by. The service had been left in this position for at least one day. There was no ground fire and no injury as a result of this incident. | Service conductor | 2 | 2 | 2 |  |  | House demolition | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/11/2017 6:52 |  |  | 9084 | Residential |  | 20180124PWA_01 | Infrastructure (network-based) | -37.7747 | 144.9414 | 1 | CitiPower | Report | 11002 | 0.026499 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Other
On arrival crew inspected structure for damage | 599 DARLINGTON-CAMPERDOWN ROAD, BOOKAAR VIC 3260 | 33037204 |  | Bird |  |  |  |  | 1 | The CFA reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a 22kV pole and fallen to the ground starting a grassfire of approx. 2 Hectares of mostly road reserve, with some private land burnt and fence damage. There were no injuries or other damage reported. The protection operated. | Conductor (bare);Crossarm (steel) | 2 | 2 | 2 |  | CDN006 | Bird Incident | Grassfire | 23/01/2018 14:06 | 1 | Medium: 1000 sq.m - 10 ha | 9104 | Roadway |  | 20180125PWA_01 | Infrastructure (network-based) | -38.1532 | 143.107 | 1 | Powercor | Report | 11025 | 0.0016701 | 22kV AC | Warrnambool Airport Ndb | 3260 | Bookaar | Animal
CEOT dispatched a fault crew to isolate, make safe, investigate and repair. Crew isolated and made safe. Crew replaced the Red phase LV transformer lead. | 32 ELY STREET, ELTHAM VIC 3095 | 900437 |  |  |  | Overheated connection |  |  |  | IMS 232161. Initial Report: Fire at base of substation pole. Final Report: DAO attended site after receiving a call from the control room (CEOT). Arrived out on site and the fire had already been extinguished. Control room advised that the cause of the fire was a failed Red phase LV Transfomer lead which had caused sparks to occur and hit the ground. This had caused a fire to start at the base of the pole. Fault crews had already been out on site by the time DAO arrived. The issue was fixed and all customers were back on supply upon my arrival. Fire was approx. 4m in length and 0.3m in width. Fire did not impact private property, only the nature strip. | Transformer | 0 | 0 | 0 |  | elm34 | LV transformer lead burned through IPC which dripped hot metal which started a small fire. | Grassfire | 28/01/2018 5:18 | 1 | Localised: less than 10 sq.m | 9123 | Residential |  | 20180129SPN_02 | Infrastructure (network-based) | -37.7262 | 145.1401 | 1 | AusNet Services Distribution | Report | 11601 | 0.03825 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham | Conductor
CEOT dispatched a fault crew to isolate. make safe and investigate. The crew found remnants of fire which was already extinguished. The crew isolated and made safe. The crew repaired the faulty Red phase connection and lead from isolator at substation pole. | 3 DELATITE COURT, WARRANWOOD VIC 3134 | 1218137 |  |  |  | Overheated connection |  |  |  | IMS 232162. Initial Report: CEOT received a report of a small ground fire. Faulty Red phase connection and lead to isolator on substation pole. Final Report from attending DAO: Crew had completed the job and had left the site before my arrival. The fire was out upon my arrival. A new D-link had been replaced on the LV Red phase with new connections to the LV lead from the crossarm bus fused blade isolator. Found visible remnant of a small 0.5 sq. metre burnt grassed area below the LV D-Link (Red phase) connection on pole No. 1218137. Melted aluminium was found in the concrete guttering. Possible cause was a loose connection at D-Link connection. | Any other type;Connector/termination | 0 | 0 | 0 |  | rwn31 | Red phase conductor D burn through connection (loose connection) and lead from isolator at substation pole. | Grassfire | 28/01/2018 20:10 | 1 | Localised: less than 10 sq.m | 9124 | Residential |  | 20180129SPN_03 | Infrastructure (network-based) | -37.7748 | 145.2401 | 1 | AusNet Services Distribution | Report | 11588 | 0.0079838 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Warranwood | Connection
CEOT dispatched a fault crew to make safe and repair. The bat was removed with an operating stick. CEOT also notified the local DAO to investigate. Site investigation in daylight 6 hours after incident revealed an insulator and tie were damaged. A ZA notification in SAP was raised for insulator replacement. Fire area was measured at 1200 sq. metres. | 998 PLUNKETTS ROAD, BARNAWARTHA NORTH VIC 3691 | 5208299 |  | Bird |  |  |  | Phase to earth | 1 | IMS 232163. At pole LIS: 5208299 a bat came in contact between a x-arm and an O/H conductor. BWA22 successfully reclosed. A 1200 sq. metre fire in the vicinity brought was brought under control by CFA. Insulator: 310mm 5-shed tie-top were damaged. Bird cover burnt on end. Flashover caused by bat. Feeder CB tripped. | Conductor (bare);Crossarm (steel);Insulators | 0 | 0 | 0 |  | bwa22 | Bird Incident | Grassfire | 29/01/2018 2:18 | 1 | Medium: 1000 sq.m - 10 ha | 9126 | Agricultural |  | 20180129SPN_04 | Infrastructure (network-based) | -36.0867 | 146.7331 | 1 | AusNet Services Distribution | Report | 11625 | 0.019883 | 22kV AC | Wangaratta Aero | 3691 | Barnawartha North | Animal
Faults crew attended site and the section made safe by isolating the section of HV overhead. The cross arm was replaced by the faults crew. | 551 GEELONG ROAD, BROOKLYN VIC 3012 | Pole no. A101771 |  | Precipitation;Industrial or urban pollution |  | Leakage |  |  | 2 | Pole top fire on pole no. A101771 The intermediate HV wooden cross arm ignited due to tracking. The footpath side of the HV intermediate crossarm was burnt off but was held in the air from the remainder of the structure. No photo is available for this fire start incident. | Crossarm (wood) | 0 | 0 | 0 |  | FW05 | The cause of the crossarm fire was tracking across the insulators. The buildup of pollutants and wet conditions led to leakage current across the surface of the insulator, and this resulted in the ignition of a fire on the wooden crossarm. | Pole-top fire | 30/01/2018 10:02 | 1 | Negligible: no ground fire | 9152 | Commercial |  | 20180130JEM_02 | Infrastructure (network-based) | -37.817 | 144.8497 | 1 | Jemena | Report | 11543 | 0.0026076 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | Crossarm
On arrival crew isolated supply and carrie dout repairs | UNIT 1 73-75 DARE STREET, OCEAN GROVE VIC 3226 | 32071761 |  |  |  | Overheated connection |  |  |  | The CFA reported a ground fire had occurred at the incident location. A crew was dispatched to investigate. The crew attended and found an FSD had burnt out and fallen to the ground. This had caused scattered burns to the ground totalling approximately 1m x 1m. The CFA had left site before the crew arrived. There were no reported shocks or injuries. No further damage identified. | Disconnector/isolator | 2 | 2 | 2 |  | DDL023 | Insufficient remains to determine cause | Grassfire | 28/01/2018 19:45 | 1 | Localised: less than 10 sq.m | 9139 | Roadway |  | 20180130PWA_01 | Infrastructure (network-based) | -38.2684 | 144.522 | 1 | Powercor | Report | 11067 | 0.024954 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Fuse
The contact has caused significant damage to the customers POA and a R.E.C is required to make repairs before reconnection to the network can be completed. | 105 DOURO STREET, NORTH GEELONG VIC 3215 | 30298421 | Vehicle | [6 empty] | The MFB reported that an overhead service has been contacted by a truck and is lying on the road at the incident location. On arrival the fault crew found that a truck had contacted and torn down a three phase grey service between substation and POA to 105 Douro Street. The contact has caused significant damage to the customers POA and a R.E.C is required to make repairs before reconnection to the network can be completed. Krone box on substation destroyed, customerâ€™s POA and mains damaged. There was no ground fire and no injury as a result of this incident. | Service conductor;Customer installation | 2 | 2 | 2 |  | GB031 | Truck hitting service line | Loss of supply;Damage to network assets | 42959.3056 |  |  | 9142 | Roadway |  | 20180130PWA_02 | Infrastructure (network-based) | -38.1144 | 144.349 | 1 | Powercor | Report | 11072 | 0.037927 | Low voltage AC (<1kV) | Avalon Airport | 3215 | North Geelong | Vehicle
On arrival crew isolated supply and carried out repairs | 163 BROUGHAM STREET, KEW VIC 3101 | 30176832 | Working too close to overhead lines | [6 empty] | A gardener (Kon, 0408179132, 17 Willsmere Rd Kew) has advised he accidently cut the service wire while trimming branches at the incident location. Upon arrival, the CP crew found that service wire was clean cut. The crew carried out repairs. There were no reported injuries or other damage. | Service conductor | 2 | 2 | 2 |  | Q019 | Gardening works | Loss of supply;Damage to network assets | 16/12/2017 11:22 |  |  | 9164 | Residential |  | 20180131PWA_09 | Infrastructure (network-based) | -37.798 | 145.0316 | 1 | CitiPower | Report | 12091 | 0.037834 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Other
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a loose neutral connection at the FMJB located on the CitiPower pole. Fault truck remade neutral connection at FMJB at the pole end CTA re-tested property, all required VESI tests passed | 80 MATHOURA ROAD, TOORAK VIC 3142 | 30217353 |  |  |  | Corrosion |  | Phase to earth |  | Penny was showering at the time; she received an electric shock when she made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Connection box | 2 | 2 | 2 |  | TK015 | Loose connection | Minor shock | 15/12/2017 7:00 |  |  | 9175 | Residential |  | 20180131PWA_15 | Infrastructure (network-based) | -37.8424 | 145.0082 | 1 | CitiPower | Report | 17374 | 0.027399 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Connection
On arrival the crew found that the exposed service did not appear to be damaged, there was a slight mark on the insulation of the cable but no penetration. The crew re-tested the cable and ensured service was safe. | 20 CHESHUNT STREET, POINT LONSDALE VIC 3225 |  | Working too close to underground cables | [6 empty] | Dan from DirectBor, rang to advise that they had dug up and exposed an LV service cable in Cheshunt St, Point Lonsdale. Dan advised that Directbor was installing a pole to pit for a customer at 20 Cheshunt St, Point Lonsdale. The crew advised that Directbor had marked out where they believed the service was before digging. There was no third party damage, ground fire or injuries reported. | Services cable | 2 | 2 | 2 |  |  | Excavation work | Damage to network assets | 16/12/2017 12:30 |  |  | 9177 | Roadway |  | 20180201PWA_01 | Infrastructure (network-based) | -38.2835 | 144.6126 | 1 | Powercor | Report | 11109 | 0.028302 | Low voltage AC (<1kV) | Avalon Airport | 3225 | Point Lonsdale | Dug up
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral connection between the service cable and the customers FMJB Fault truck remade neutral connection at the customerâ€™s FMJB CTA re-tested property, all required VESI tests passed | 3 TATMAN DRIVE, ALTONA MEADOWS VIC 3028 |  |  |  |  | Corrosion |  | Phase to earth |  | Stef made contact with the garden tap at the time; she received an electric shock when she made simultaneous contact between the metallic tap with her hand and the general mass of earth with her foot. | Service conductor | 2 | 2 | 2 |  |  | Corroded neutral connection | Minor shock | 18/12/2017 19:30 |  |  | 9180 | Residential |  | 20180201PWA_03 | Infrastructure (customer connection) | -37.8854 | 144.7865 | 1 | Powercor | Report | 11113 | 0.0071759 | Extra low voltage AC (<50V) | Laverton Raaf | 3028 | Altona Meadows | Connection
After performing a walkthrough and investigation LEI confirmed in at approximately 6am that about 60 customers where off supply, 5 x 3 phase Meters will need to be changed and performed 4 disconnections at pole for no access. Only meter that had visible damage was 7 Acacia | 7 ACACIA STREET, CAMBERWELL VIC 3124 | 30173711 |  | Blown branch/vegetation | [5 empty] | A fault occurred on feeder RD009 due part of a water laden that tree fell onto the overhead lines, bridging the HV and LV conductors. This caused an HV injection resulting in customers off supply, blown fuses and damaged street lights. There were no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | RD009 | Vegetation: Trees Incident | HV injection;Loss of supply | 29/01/2018 11:41 |  |  | 9194 | Residential |  | 20180202PWA_01 | Infrastructure (network-based) | -37.8421 | 145.0847 | 1 | CitiPower | Report | 11127 | 0.019975 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3124 | Camberwell | Trees
The site was made safe and the cable was taken out of service to be repaired. | 53 TIVOLI ROAD, SOUTH YARRA VIC 3141 | 30216650 | Working too close to underground cables | [5 empty] | 1 | The company director (Shack Communications) reported one of their employees had made contact with an underground cable using a crow bar at the incident location. The crew attended and confirmed that a HV cable (TK009) had been damaged with a crow bar. It was confirmed that no injury or third party damage had occurred. The contractors employee said he did not receive a shock but was advised by Laurie (Citipower employee) to seek medical advice. | Cable | 2 | 2 | 2 |  | TK009 | Excavation work | No Go Zone (contact);Damage to network assets | 43102.4153 |  |  | 9196 | Roadway |  | 20180202PWA_02 | Infrastructure (network-based) | -37.8373 | 144.9984 | 1 | CitiPower | Report | 11129 | 0.041487 | 11kV AC | Essendon Airport | 3141 | South Yarra | Other
On arrival crew isolated supply and removed irrigator from contact and then repaired conductor damage. | 1034 BARKSTEAD ROAD, SPRINGBANK VIC 3352 | 31001383 | Working too close to overhead lines | [5 empty] | 1 | A field crew attending an outage found that a parked mobile irrigator had contacted a 22kV conductor mid span causing damage to the 22kV conductors. Protection operated. There were no reported injuries or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | BAN011 | Placement of irrigator near line | Loss of supply;No Go Zone (contact) | 43102.4979 |  |  | 9198 | Agricultural |  | 20180202PWA_03 | Infrastructure (network-based) | -37.4942 | 144.0504 | 1 | Powercor | Report | 11132 | 0.020112 | 22kV AC | Ballarat Aerodrome | 3352 | Springbank | Vehicle
On arrival crew carried out repairs | 41 FOREST STREET, WOODEND VIC 3442 | 31006290 | Vehicle | [6 empty] | A customer reported that a high load has struck a wire and the wire was on the ground at the incident location. On arrival the crew found that a high load had contacted an LV service cable causing the cable to break and fall to the ground. There were no reported injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | WND012 | Vehicle struck service line | Loss of supply;Damage to network assets | 43313.5479 |  |  | 9206 | Roadway |  | 20180205PWA_08 | Infrastructure (network-based) | -37.3544 | 144.527 | 1 | Powercor | Report | 11140 | 0.025416 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Vehicle
On arrival crew carrie dout repairs | 2A HIGH STREET, LAKE WENDOUREE VIC 3350 | 30012740 | Vehicle | [6 empty] | A customer reported that a garbage truck has struck a wire and the wire was laying on the road at the incident location. On arrival the crew found that a garbage truck ( Operated by: Ballarat City Council, Ph: 03 5320 5500 ) had contacted an LV service cable causing the cable to break and fall to the ground. There were no reported shocks, injuries or third party property damages. | Service conductor | 2 | 2 | 2 |  | BAN005 | Garbage truck struck service | Loss of supply;Damage to network assets | 43344.3514 |  |  | 9207 | Roadway |  | 20180205PWA_09 | Infrastructure (network-based) | -37.5515 | 143.8472 | 1 | Powercor | Report | 11141 | 0.029608 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Lake Wendouree | Vehicle
The crew isolated the line and repaired conductor | 100-106 SEVENTH STREET, MILDURA VIC 3500 | 32154363 |  |  |  | Mechanical breakdown |  |  |  | A customer called to advise of an outage and a wire on the ground. A crew attended and found a 22kV conductor had broken and was on the ground. There were no reported shocks, injuries or third party property damages. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | MDA032 | Connection failure | Loss of supply;Damage to network assets | 43405.35 |  |  | 9210 | Roadway |  | 20180205PWA_12 | Infrastructure (network-based) | -34.1849 | 142.1678 | 1 | Powercor | Report | 11496 | 0.0098403 | 22kV AC | Mildura Airport | 3500 | Mildura | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable with a new Twisted O/H Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 25 KANSAS AVENUE, BELL POST HILL VIC 3215 |  |  |  |  | Corrosion |  | Phase to earth |  | Miss Rachel Fox-Cully was operating the external tap when she received an electric shock as she made simultaneous contact with her hand on the metallic tap and her bare feet while standing on the wet ground. | Service conductor;Connection box | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 43374.4271 |  |  | 9212 | Residential |  | 20180205PWA_14 | Infrastructure (network-based) | -38.0958 | 144.3315 | 1 | Powercor | Report | 11146 | 0.020573 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded (Open Circuit) U/G Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Service Pole The attending Powercor Fault Crew re-terminated the Underground Service Neutral Conductor at the Pole Type Connection Box and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 725 GREAT OCEAN ROAD, EASTERN VIEW VIC 3231 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Karen Harper was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 43221 |  |  | 9213 | Residential |  | 20180205PWA_15 | Infrastructure (network-based) | -38.4719 | 144.0437 | 1 | Powercor | Report | 11147 | 0.025449 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Eastern View | Connection
On arrival crew isolated supply and replaced damaged pole. | SERVICETON NORTH-TELOPEA DOWNS ROAD, SERVICETON VIC 3420 | 32120511 |  |  |  | Leakage |  |  | 1 | System reports an outage of the Serviceton Nth P12 ACR. A crew patrolled line and found a pole fire had occurred at P56 Serviceton Nth line. The pole fire had self-extinguish. CFA did not attend. Top of pole burnt off and conductor still tied to insulator on ground. There was No ground fire start, no reported injuries or third party [property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 30/01/2018 5:27 | 1 | Negligible: no ground fire | 9226 | Agricultural |  | 20180207PWA_01 | Infrastructure (network-based) | -36.2294 | 140.9967 | 1 | Powercor | Report | 11161 | 0.0049873 | 22kV AC | Horsham Aerodrome | 3420 | Serviceton | Pole
Initial Report: CEOT immediately switched the line out from ACR WO022. An operator was already on his way to the incident and on arrival at switch 831886 he immediately made the line safe by isolation, tag and earth. The location of the incident was confirmed and the rest of the line was then switched on again. Final Report: 1st crew member to arrive on site approximately 6.20 pm noting CFA waiting to gain access to the fire but could not touch the wires or truck until an earth and short circuit was applied to the conductors. Two AusNet Services' line workers applied the E/S/C (Earth and Short Circuit) to the tee off conductors on pole 5200908 to make safe. | DUNDEE, 3162 KIEWA VALLEY HIGHWAY, KERGUNYAH VIC 3691 | 5200908 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232306. Initial Report: CEOT received reports from emergency services that a truck made contact and is hung up in the line ex Switch 831886. Final Report: 06/02/2018 - incident in a paddock where the raised trailer of a fertiliser truck has allegedly contacted overhead conductors approximately 8 metres above the ground resulting in the 2 outside conductors caught and pulled down by the trailer. The trailer caught fire resulting in a localised grass fire. AusNet Services received calls from some customers advising partial or no power to their properties with some seeing smoke in the area. | Conductor (bare) | 0 | 0 | 0 |  | wots11 | Raised trailer of a fertiliser truck has allegedly contacted overhead HV conductors. | Electrocution;Grassfire | 43253.75 | 1 | Localised: less than 10 sq.m | 9228 | Agricultural |  | 20180207SPN_01 | Infrastructure (network-based) | -36.3869 | 147.0408 | 1 | AusNet Services Distribution | Report | 12817 | 0.012316 | 22kV AC | Wangaratta Aero | 3162 | Kergunyah | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole The attending Powercor Fault Crew re-terminated the existing O/H Service Cable at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1 MORRIS STREET, PORT CAMPBELL VIC 3269 |  |  |  |  | Corrosion |  | Phase to earth |  | Ms Tanya White was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Taps and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | connection corroded | Minor shock | 15/12/2017 0:00 |  |  | 9235 | Residential |  | 20180208PWA_02 | Infrastructure (network-based) | -38.6214 | 142.998 | 1 | Powercor | Report | 11171 | 0.0010995 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Port Campbell | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a burnt (Open Circuit) Neutral Bridge Connection at the Crossarm on the LV Reticulation Pole following a Lightning Strike, The attending Powercor Fault Crew reterminated the burnt Neutral Bridge Connection at the Crossarm on the LV Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 33 MURLONG STREET, SWAN HILL VIC 3585 |  |  | Lightning |  | Overheated connection |  | Phase to earth |  | Ms Rachel Dickie was standing in front of the Meter Enclosure when she received an electric shock as she made simultaneous contact between her hand on the exposed metal of the Meter Enclosure and her bare feet while standing on the damp ground. | Dropper/bridge | 2 | 2 | 2 |  |  | Connection failure following lightning strike | Minor shock | 43313.75 |  |  | 9236 | Residential |  | 20180208PWA_03 | Infrastructure (network-based) | -35.3296 | 143.5459 | 1 | Powercor | Report | 11172 | 0.0058183 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Lightning
The crew completed the necessary repairs to re-instate the LV earth at the substation pole. | 40 LA COTE ROAD, GREENDALE VIC 3341 | 30105191 | Copper theft | [6 empty] | Report received of no power from customer. Upon arrival, the fault crew replaced a blown 100A service fuse supplying a property in La Cote Rd, and in completing this work, noticed that the LV earth (approx. 2m length) at LIS-100730 had also been stolen at some point prior | Earth/earthing | 2 | 2 | 2 |  | BMH003 | Copper theft | Damage to network assets | 13/01/2018 8:20 |  |  | 9237 | Roadway |  | 20180208PWA_04 | Infrastructure (network-based) | -37.5689 | 144.3161 | 1 | Powercor | Report | 11173 | 0.025354 | Earthing cable | Avalon Airport | 3341 | Greendale | Other
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. CEOT also dispatched a LEI to investigate. LEI confirmed a HVI occurred. Final Report: The LEI isolated all customers' installations and once the fault crew attended and re-instated power the LEI proceeded to test the properties. Metering was replaced on 14 properties. All available properties tested to VESI requirements and left on supply. The properties with appliance issues were checked and found items not working as they should - these items were written into the damage reports. Service crews repaired the lines as required and replaced meters where required. | 80 HENRY STREET, ELTHAM VIC 3095 | 921770 |  | Blown branch/vegetation |  |  |  | Phase to phase | 1 | IMS 232549. Initial rteport: Customer reported that a tree branch on power lines outside their address. Tree branch into HV and HV into LV at this address causing a HVI. Final Report: INCIDENT COMMENTS: Confirmed HVI HENRY LAMORNA substation - Fault crew called @ 1500. LEI required, street light at Lis# 921773 blown and report of an injection at 4 Lamarna Ct . East side sub bus fuses opened, located on lis# 921773 not 921772. An AusNet Services' LEI was called to attend the site to check for a possible HVI after a tree contacted overhead lines. A tree branch fell from a tree located in the property of no. 79 Henry St, Eltham. Twenty six properties were on this circuit. Switchboards and meters showed signs of an injection. Many customers stated appliances were having problems at the time of the tree falling down. | Conductor (bare) | 0 | 0 | 0 |  | elm13 | Vegetation: Trees Incident | HV injection | 25/02/2018 14:11 |  |  | 9379 | Residential |  | 20180226SPN_09 | Infrastructure (network-based) | -37.7179 | 145.1563 | 1 | AusNet Services Distribution | Report | 11397 | 0.030716 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3095 | Eltham | Trees
CEOT dispatched a fault crew to isolate, make safe and Paul Tanner and Peter Wilkinson ( Local DAO / Network Service Representative) to investigate and report. The measured height of HV conductor after spray was lifted away was 5.6m and there was no visible damage to the conductor. Distance from (E)Pole 2/12-12w BID 5102709 Skinns Spur Line was approx. 165m. The conductor was lifted while the final bracket and spray moved under the line, and when all clear, the HV line was energised. There is a line relocation project in place and the HV line in question is due to be retired within the next few weeks. | 118 GENTLE ANNIE LANE, WHITFIELD VIC 3733 | 5102714 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232569. Lost supply to WN210 Loader 2 ISO ACR at 1135 hours and then a report from Paul Tanner informing the CEOT that an Irrigator machine has contacted a SWER line Near Loader pole 3 substation in paddock. No one injured and 27 customers off supply. Greg Sheppard was moving assembled Rotary Irrigator from assembly position to anchor position by having his tractor connected to the pump base and pulling in a northerly direction. Contact was made with the wire support frame between (E)Pole 2/12-12w BID 5102709 Skinns Spur Line and (E)Pole 1/40â€™w BID 5102714 Cooper Spur Line. The sprinker end brackets and supports appear to be higher than the middle supports as it also kicks upward for the end sprinkler. | Conductor (bare) | 0 | 0 | 0 |  | wn5 | Irrigator sprinkler machine contacted a SWER line. | Loss of supply;No Go Zone (contact) | 26/02/2018 11:31 |  |  | 9384 | Agricultural |  | 20180226SPN_10 | Infrastructure (network-based) | -36.752 | 146.4239 | 1 | AusNet Services Distribution | Report | 11403 | 0.031987 | 12.7kV AC (SWER) | Wangaratta Aero | 3733 | Whitfield | Vehicle
A LEI and faults truck attended and completed a NST that failed. The LEI measured 22v between the water pipes and an independent earth with a load of 42amps applied. The neighbouring property was also tested with 22v also measured on the neutral bar and water pipes. Connections of the three phase service were checked and a deteriorated neutral conductor was identified between the overhead conductors and the pole mounted junction box installed on the tramways pole that supplied four shops. The conductor was replaced and a NST completed that passed confirming the fault had been rectified after 0.9v was measured on the water pipes and neutral bar. | 298 CARLISLE STREET, BALACLAVA VIC 3183 | Tramway pole No. 54 |  |  |  | Neutral fault |  | Phase to earth | 2 | Name of Business - Little Miss CafÃ©. REC on site has detected 22v on the water piping. A worker at the shop called the REC after a zap was received from the water pipe. The worker at the CafÃ© was opening the dishwasher and received a minor electric shock from the water pipe supplying the dishwasher. She called a REC to investigate the cause who measured 22v on the water pipes and contacted the United Energy faults and emergencies call centre. | Connector/termination | 0 | 0 | 0 |  |  | A deteriorated neutral conductor was identified between the overhead conductors and the pole mounted junction box. | Minor shock | 23/02/2018 16:30 |  |  | 9378 | Commercial |  | 20180226UTD_03 | Infrastructure (network-based) | -37.8686 | 144.9941 | 1 | United Energy Distribution | Report | 11394 | 0.0165 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | Balaclava | Connection
On arrival crew isolated supply and carried out repairs. | 125 BRIDGE STREET, BENDIGO VIC 3550 | 30025745 |  |  |  | Leakage |  |  |  | A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that the HV cross am and pole top slightly burnt through. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | EHK033 | Excessive leakage current | Pole-top fire | 19/02/2018 7:09 | 1 | Negligible: no ground fire | 9390 | Roadway |  | 20180227PWA_02 | Infrastructure (network-based) | -36.748 | 144.2881 | 1 | Powercor | Report | 11411 | 0.008353 | 22kV AC | Bendigo Airport | 3550 | Bendigo | Pole
On arrival crew carried out repairs | 850 AVIATION ROAD, WERRIBEE SOUTH VIC 3030 | 30108549 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer (Mary Camerlengo) called to say her husband had bought down the LV service to their house with his tractor. On arrival the crew found that a Low Voltage (LV) service had been bought to ground by a tractor. There were no reported injuries or other third party damage. | Service conductor | 2 | 2 | 2 |  | WBE034 | Tractor hit service | Loss of supply | 20/02/2018 8:42 |  |  | 9392 | Agricultural |  | 20180227PWA_04 | Infrastructure (network-based) | -37.9261 | 144.7208 | 1 | Powercor | Report | 11413 | 0.0079815 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Vehicle
CEOT dispatched a fault crew to make safe, isolate and carry out / arrange for necessary repairs. CEOT also notified the local DAO and ESV. The fault crew attended, isolated the HV line and sleeved the HV conductor together and sagged accordingly. | 200 BENA ROAD, KORUMBURRA VIC 3950 | 2006456 |  | Fallen |  |  |  | Phase to earth | 1 | IMS 232627. Initial Report: HV DOWN EX SW #828282 CAUSE TREE REPORTS FIRE NEAR ASSETS. Final Report; Under INCD-166778-r, reports of a fire around HV assets ex SW #828282. A tree fell over the HV conductors causing a conductor to fail and fall. The tall thin Gum tree well outside the clearance space and has two co-dominate leaders with included bark half way up trunk. Line side leader has failed and is resting in other vegetation under overhead 22kV power lines. Burnt grass in paddock evident under overhead 22kV power lines 40m from failed branch. The tree trunk was located 11-15 m from the HV line. The fire size was 20 sq. metres. The tree was a private tree. Red Phase HV fuse operated. | Conductor (bare) | 0 | 0 | 0 |  | LGA12 | Vegetation: Trees Incident | Loss of supply;Grassfire | 28/02/2018 17:15 | 1 | Small: 10 - 1000 sq.m | 9397 | Agricultural |  | 20180301SPN_01 | Infrastructure (network-based) | -38.4329 | 145.7928 | 1 | AusNet Services Distribution | Report | 12929 | 0.0076817 | 22kV AC | Morwell (Latrobe Valley Airport) | 3950 | Korumburra | Trees
The faults crew attended and found no persons on site but their tools remained in the ground type substation. HV switch FS0315 in Watts Parade was opened and the repairs were completed under Access Authority conditions. United Energy management was notified and the Police were in attendance and made a report detailing the attempted theft. Supply was restored upon completion. 29/01/2018 - A review of United Energy's records indicate the ground type substation had been broken into previously with the circuit for the hospital and LV isolators removed. There was no copper theft in this instance and a faults crew repaired the damaged substation door and lock. | PELICAN PLACE, MOUNT ELIZA VIC 3930 |  | Unauthorised access;Copper theft |  |  |  |  | Phase to phase | 1 | AMI meters in Pelican Place, Mount Eliza communicated there was an outage in the area and a faults truck was dispatched to investigate. 25/02/2018 - Ground type substation named "Geriatric Hosp - Watts" has been broken into in an attempted copper theft. The LV assets had flashed over that caused an outage to customers who reside in Pelican Court. It was unknown if any electric shock or flash burns were sustained. | Conductor (insulated);Copper;Outdoor | 0 | 1 | 0 |  | FSH 13 | Unknown persons broke into in a ground type substation in attempted copper theft. | Loss of supply;No Go Zone (contact);Damage to network assets | 25/02/2018 5:00 |  |  | 9399 | Commercial |  | 20180301UTD_01 | Infrastructure (network-based) | -38.169 | 145.087 | 1 | United Energy Distribution | Report | 11423 | 0.0159 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Other
On arrival crew isolated supply and carried out repairs | 13 MORRISON STREET, BIRCHIP VIC 3483 | 32018655 |  |  |  | Overheated connection |  |  |  | CFA advised pole fire outside 13 Morrison St â€“ Birchip. Upon arrival crew found that an LV bushing cover had melted and had fallen to the ground at incident location. The melted bushing had caused a 1mÂ² grassfire at the base of the pole. There was no shock, no injury, no damage to private property. | Pole mounted | 2 | 2 | 2 |  | CTN001 | LV bushing fault | Grassfire | 43134.9896 | 1 | Localised: less than 10 sq.m | 9420 | Roadway |  | 20180305PWA_02 | Infrastructure (network-based) | -35.9803 | 142.9128 | 1 | Powercor | Report | 11458 | 0.017198 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3483 | Birchip | Connection
Zinfra's substation subcontractor (Qmain) was called to secure the substation door. United Energy were advised and it was suggested the substation is isolated with the copper removed to avoid a re-occurrence. | PELICAN PLACE, MOUNT ELIZA VIC 3930 |  | Unauthorised access;Copper theft | [5 empty] | 1 | Customers supplied from "Geriatric Hosp-Watts" indoor substation advised of a loss of their electricity supply. Please also refer to Report No. 20180301UTD_01. An attempted copper theft occurred for the third time at "Geriatric Hosp - Watts" when unknown persons broke into the Indoor substation. The LV red phase 200amp fuse had operated and was replaced to restore supply customers that reside in Pelican Place. It appears no injuries occurred to the unknown persons. | Conductor (bare);Copper | 0 | 0 | 0 |  | FSH 13 | Unknown persons broke into the indoor substation in an attempted copper theft. | Loss of supply;No Go Zone (contact);Damage to network assets | 43103.5868 |  |  | 9422 | Residential |  | 20180305UTD_02 | Infrastructure (network-based) | -38.169 | 145.0871 | 1 | United Energy Distribution | Report | 11460 | 0.041628 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Other
The CEOT dispatched a fault crew to make safe, isolate, investigate and carry out / arrange for necessary repairs. The fault crew de-energised the LV line and made the area safe for the CFA to put out the fire. Construction crew reinstated the LV conductor. Supply restored. | 1 STRATTON COURT, BAYSWATER VIC 3153 | 1218733 |  |  |  | Rot |  | Phase to earth | 2 | IMS 232626 - Fault crew found an LV conductor on the ground still alive, which had caused a small grass fire. Final Report: LV conductor at pole lis 1218733 broken from LV crossarm. LV conductor on the ground which caused a small grass fire. The CFA extinguished the fire. The LV crossarm had rotted away at pole lis1218733. NO PHOTOS WERE TAKEN. | Conductor (bare) | 0 | 0 | 0 |  | bra11 | Broken LV crossarm. | Loss of supply;Grassfire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/02/2018 12:56 | 1 | Localised: less than 10 sq.m | 9424 | Residential |  | 20180306SPN_01 | Infrastructure (network-based) | -37.8513 | 145.2504 | 1 | AusNet Services Distribution | Report | 11765 | 0.015883 | Low voltage AC (<1kV) | Moorabbin Airport | 3153 | Bayswater | Crossarm
Site made safe. Switched out switchgear to test operation and condition, all okay. | 142 CRANWELL STREET, BRAYBROOK VIC 3019 |  | Copper theft | [5 empty] | 2 | Copper LV bonders and hooks stolen from Cranwell-Burke kiosk substation Vandals have cut locks of HV switches and tried to operate HV switches Damage done to shops McDonalds & BCF, customer defect issued | Pad mounted equipment/kiosk | 0 | 1 | 0 |  | BY11 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43284.3354 |  |  | 9430 | Public space |  | 20180307JEM_01 | Infrastructure (network-based) | -37.7774 | 144.85 | 1 | Jemena | Report | 11470 | 0.0015035 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
On arrival crew confirmed site safe and carried out repairs | 37 FIELD DAYS ROAD, LONGERENONG VIC 3401 | 32090480 | Unmanned balloon (advertising or drone) | [5 empty] | 1 | An REC reported a balloon has flown into the HV powerlines at the incident location. On arrival the crew found that a blimp used for advertising had broken free of its moorings, and its mooring lines then became entangled in the overhead HV conductors, and had caused the overhead HV conductors to clash. There were no injuries or fire, and no other damage reported. | Conductor (bare) | 2 | 2 | 2 |  | HSM003 | Blimp used for advertising had broken free of its moorings | Loss of supply;Damage to network assets | 43254.4069 |  |  | 9433 | Public space |  | 20180307PWA_01 | Infrastructure (network-based) | -36.6819 | 142.3031 | 1 | Powercor | Report | 11474 | 0.035719 | 22kV AC | Horsham Aerodrome | 3401 | Longerenong | Other
Initial report: CEOT dispatched a fault crew to make safe, investigate and repair. The fault crew found that LA's failed and caused ground fire approx. 15 - 20 sq metres. Final report: On arrival to site the fault crew observed a burnt grass area at the base of Gas Switch Pole 2201653. Burnt grassed area of 9m x 23m in size. The crew issued an EAP and checked over the pole and found a dead bird at top of pole stuck between the LA and the cross arm. The crew removed the bird and replaced the LAs on the pole. Cancelled EAP and restore supply | L1 WALSHES ROAD, WESTBURY VIC 3825 | 2201653 |  | Bird |  |  |  | Phase to earth |  | Initial report: IMS 232689. Received INCD from Vic Fire that a bird had started a ground fire after coming in contact with HV conductors at a HV pole. Final report: A bird caused a flashover between steel cross arm and Lightning Arrestor at pole top resulting in a small ground fire. | Crossarm (steel);Surge diverter | 0 | 0 | 0 |  | moe22 | Bird Incident | Grassfire | 43134.8354 | 1 | Small: 10 - 1000 sq.m | 9439 | Agricultural |  | 20180308SPN_03 | Infrastructure (network-based) | -38.1583 | 146.2357 | 1 | AusNet Services Distribution | Report | 11849 | 0.026703 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Westbury | Animal
A faults crew attended, made the site safe and restored supply after LV fuses were replaced at "Pasadena-Gareth" substation. Private and council trees were cut clear from the overhead conductors. | 9 GARETH AVENUE, BEAUMARIS VIC 3193 | 1811309 |  | Wind |  |  |  |  | 1 | Customers supplied from "Pasadena-Gareth" substation advised they have lost their electricity supply. Late in the afternoon, strong winds from the east caused many wind event faults within the United Energy area of supply. In Beaumaris at approximately 6.00PM, the MFB reported that a tree has come down over wires and clashing caused the tree to briefly catch on fire. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Other vegetation | 19/02/2018 18:01 | 1 | Negligible: no ground fire | 9434 | Residential |  | 20180308UTD_01 | Infrastructure (network-based) | -37.9845 | 145.0319 | 1 | United Energy Distribution | Report | 12997 | 0.014731 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Beaumaris | Trees
The Inspector attended and completed installation tests that all passed and signed the Prescribed CES. Supply was left on after the faults crew re-sagged the overhead service cable and left supply on. They also took photos and provided copies to their supervisor as they were concerned in the manner the REC had completed the work activities. | 15 MCALISTER STREET, FRANKSTON VIC 3199 | 3309413 | Caused by REC/contractor | [5 empty] | 2 | A smart meter for a life support customer communicated that an outage has occurred. As part of United Energy procedures, a customer relations staff member contacts the customer to ensure they have their contingency plan in place. The life support customer was unable to be contacted and a faults crew was sent to the site after the meter communicated that supply was restored at 9.51AM. The faults crew attended and found an unsigned Prescribed CES No. 15608956 in the meter enclosure with no Inspectors details. The faults crew concluded the REC had removed the fuse cartridge at the POA, completed installation work and restored supply with no contact with United Energy. The faults crew contacted the REC for further details and isolated supply until the Inspectors details were obtained. This was completed and the faults crew contacted the Inspector who knew nothing about the job and was going to the site to investigate. | Customer installation | 0 | 0 | 0 |  |  | Isolating supply and not following the correct procedures. | Loss of supply | 43162.3125 |  |  | 9456 | Residential |  | 20180309UTD_04 | Infrastructure (network-based) | -38.142 | 145.135 | 1 | United Energy Distribution | Report | 11506 | 0.026954 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Other
On arrival crew arranged for insulator replacement. | 105 LEMNOS NORTH ROAD, LEMNOS VIC 3631 | 33096892 |  | Bird | [5 empty] | Vic Fire reported grass fire at 105 Lemnos North Rd Lemnos. On arrival the crew found evidence of a flashover from a bat on a HV 5 shed insulator. Area of approx. 15m x 30m of burnt grass in the road reserve. There was no reported shock or injuries. | Conductor (bare) | 2 | 2 | 2 |  | SHN024 | Bird Incident | Grassfire | 43376.109 | 1 | Small: 10 - 1000 sq.m | 9468 | Roadway |  | 20180313PWA_01 | Infrastructure (network-based) | -36.3564 | 145.4619 | 1 | Powercor | Report | 11527 | 0.023148 | 22kV AC | Shepparton Airport | 3631 | Lemnos | Animal
CEOT dispatched a fault crew to investigate, make safe and carry out/arrange for any necessary repairs. CFA on site and put the fire out. CEOT advised the local DAO. Fuses replaced. | 7 GRIFFIN AVENUE, MANSFIELD VIC 3722 | 3917722 |  | Bird |  |  |  | Phase to earth | 1 | IMS 232770. A Magpie caused 2 x HV fuses to blow on transformer. One fuse hung-up and burnt fuse tube. A small <1 sq. metre fire at the base of pole. | EDO fuse;Pole mounted | 0 | 0 | 0 |  | msd4 | Bird Incident | Grassfire | 43284.8438 | 1 | Localised: less than 10 sq.m | 9464 | Residential |  | 20180313SPN_02 | Infrastructure (network-based) | -37.0632 | 146.0844 | 1 | AusNet Services Distribution | Report | 11521 | 0.031134 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Animal
CEOT dispatched a Fault crew to isolate, make safe and restore supply. Fault crew replaced the burnt fuse tube and fuse and restored supply. | 1 SAND PIT ROAD, YARRAGON VIC 3823 | 2203792 |  |  |  | Age;Corrosion;Electrical breakdown;Candled fuse |  |  | 2 | IMS 232238. Customer called with no power. Fault crew found a Candling 6k EDO Fuse on substation Dempster 3. No fire on pole or ground. | EDO fuse | 0 | 0 | 0 |  | moe22 | Candled EDO fuse tube. | Other electricity related | 31/01/2018 21:02 | 1 | Negligible: no ground fire | 9466 |  |  | 20180313SPN_04 | Infrastructure (network-based) | -38.2242 | 146.0612 | 1 | AusNet Services Distribution | Report | 11524 | 0.0071736 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon | Fuse
Site made safe Replaced HV crossarm | 275 GEELONG ROAD, KINGSVILLE VIC 3012 | Pole no. A052011 |  |  |  | Leakage |  |  | 1 | Pole and crossarm fire on pole no. A052011 No ground fire Photo is attached in the "Notes and Findings" section | Crossarm (wood) | 0 | 0 | 0 |  | FW08 | Tracking/electrical leakage | Pole-top fire | 43103.6708 | 1 | Negligible: no ground fire | 9481 | Residential |  | 20180314JEM_02 | Infrastructure (network-based) | -37.8057 | 144.8805 | 1 | Jemena | Report | 11545 | 0.024354 | 22kV AC | Essendon Airport | 3012 | Kingsville | Crossarm
Site made safe, isolated HV and LV to conduct repairs Pole-mounted subtation to be replaced | 310 BALLARAT ROAD, BRAYBROOK VIC 3019 | Pole no. A073308 |  |  |  | Electrical overload |  |  | 1 | Small grass fire < 1 sq. m. due to faulty LV ABC switch on pole-mounted substation The transformer had failed at the LV bushing gasket, however there was no fire associated with transformer Photos attached in the "Notes and Findings" section | Any other type;Pole mounted | 0 | 1 | 0 |  | BY11 | Melted, or hot hardware fell from the pole-mounted substation LV ABC switch and caused a small grassfire | Grassfire | 43283.4743 | 1 | Localised: less than 10 sq.m | 9491 | Public space |  | 20180315JEM_02 | Infrastructure (network-based) | -37.7793 | 144.852 | 1 | Jemena | Report | 13019 | 0.016539 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | AF Other
On arrival crew isolated supply and carried out repairs. | ORANA, 412 MORTLAKE-ARARAT ROAD, MORTLAKE VIC 3272 | 32061375 |  |  |  | Leakage |  |  |  | Report from Vic fire of pole fire at incident location. On arrival crew found crossarm burnt off. There was no ground fire , no reported injuries and no third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | TRG002 | Excessive leakage current | Pole-top fire | 29/01/2018 21:27 | 1 | Negligible: no ground fire | 9485 | Roadway |  | 20180315PWA_01 | Infrastructure (network-based) | -38.0416 | 142.8195 | 1 | Powercor | Report | 11549 | 0.012196 | 22kV AC | Warrnambool Airport Ndb | 3272 | Mortlake | Crossarm
On arrival crew isolated supply and carried out repairs | 127 FRENCH STREET, HAMILTON VIC 3300 | 32126397 |  |  |  | Leakage |  |  |  | Emergency services reported a pole on fire. On arrival the attending crew found the wooden HV cross-arm on pole 47 had ignited at the king bolt and burnt the pole top and cross-arm. There was no ground fire. There were no reported shocks or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | HTN005 | Excessive leakage current | Pole-top fire | 23/02/2018 4:35 | 1 | Negligible: no ground fire | 9498 | Roadway |  | 20180315PWA_06 | Infrastructure (network-based) | -37.7435 | 142.0282 | 1 | Powercor | Report | 11563 | 0.0065556 | 22kV AC | Hamilton Airport | 3300 | Hamilton | Crossarm
Site made safe Jemena dispatched Faults crew who identified and rectified rupture to white phase circuit fuse and damage to white and blue phase conductors | 63 TYLER STREET, PRESTON VIC 3072 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  | Conductor clashing |  |  | 2 | Mobile Franna crane made contact with overhead Optus communications cable causing low voltage aluminium conductors to clash. No Go Zone clearances not maintained. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | NH16 | Mobile Franna crane operator did not check overhead clearance to Optus communication cable | No Go Zone (contact) | 16/03/2018 13:00 |  |  | 9505 | Residential |  | 20180316JEM_02 | Infrastructure (network-based) | -37.7333 | 145.0329 | 1 | Jemena | Report | 11573 | 0.0034977 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Vehicle
On arrival the crew isolated supply and carried out repairs. | 380 PEMBERTONS ROAD, VITE VITE VIC 3325 | 32061488 |  |  |  | Leakage |  |  |  | A customer reported an insulator on a cross arm had broken causing conductor to hang very low. The attending crew found evidence of a HV crossarm fire. The live HV conductor was hanging at a waste height. There was no evidence of ground fire. There were no reported shocks or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | CDN006 | Excessive leakage current | Pole-top fire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43407.5174 | 1 | Negligible: no ground fire | 9503 | Agricultural |  | 20180316PWA_04 | Infrastructure (network-based) | -37.8009 | 143.1105 | 1 | Powercor | Report | 11571 | 0.0039005 | 22kV AC | Ballarat Aerodrome | 3325 | Vite Vite | Crossarm
Site made safe. Fire extinguished by MMFB. Bridge repaired. | 46 CRISSANE ROAD, BUNDOORA VIC 3083 | Pole no. A031466 |  | Bird |  | Mechanical breakdown |  |  | 1 | 8 sq. m. of grass fire burnt at base of pole and put out by MMFB Burnt off bridge (PG clamps) found at base of pole No photo is available | Dropper/bridge | 0 | 0 | 0 |  | NH16 | Bridge was burnt off due to fault caused by bat strike on concrete pole no. A142981 with substation Chaleyer-Ashton | Grassfire | 17/03/2018 12:16 | 1 | Localised: less than 10 sq.m | 9508 | Commercial |  | 20180317JEM_02 | Infrastructure (network-based) | -37.728 | 145.0458 | 1 | Jemena | Report | 11577 | 0.040942 | 22kV AC | Essendon Airport | 3083 | Bundoora | Animal
On arrival crew isolated supply and commenced repairs | 90 FRYS ROAD, GELLIBRAND VIC 3239 | 33039091 |  | Wind;Fallen |  |  |  |  | 1 | Customer reported power lines down and had caused a fire. On arrival the crew found a tree had fallen and brought down a HV conductor between BLANC pole 5 and 6. There was a ground fire (30x10m) in the road reserve. Crew advised a large tree had fallen in high winds bring 1 conductor to ground and starting a fire. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | Extreme winds | Grassfire | 17/03/2018 10:46 | 1 | Small: 10 - 1000 sq.m | 9515 | Public space |  | 20180319PWA_01 | Infrastructure (network-based) | -38.511 | 143.5529 | 1 | Powercor | Report | 11596 | 0.023128 | 22kV AC | Ballarat Aerodrome | 3239 | Gellibrand | Trees
On arrival crew made safe and carried out repairs. | 3 HERTFORD STREET, SEBASTOPOL VIC 3356 | 33103334 |  | Blown branch/vegetation | [5 empty] | Customers and emergency services reported a flashover and wires down at the incident location. On arrival the crew found that it appears that bark blown by wind caused a flashover on pole 37 Hertford St. A HV injection caused a LV service to street lights to fail and caused the suspension style street lights to drop onto the road. There was also damage to a watchman light control box on the concrete pole. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | BAS034 | Wind blown debris | HV injection;Damage to network assets | 18/03/2018 9:21 |  |  | 9525 | Roadway |  | 20180319PWA_03 | Infrastructure (network-based) | -37.5854 | 143.8397 | 1 | Powercor | Report | 11827 | 0.0050822 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3356 | Sebastopol | Other
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe, investigate and arrange for necessary repairs. Downer has attended site on behalf of AusNet Services and isolated the supply from pole 909935 by pulling the LV fuses at the fused mains box. An AusNet Services' LEI has been to site and accessed the damaged and the safety of this site and deemed it to be safe. The LEI has tested the underground service cable and found there to be low IR value present and the pole to pit underground cable will need to be replaced. | 15 CHAPMAN AVENUE, THOMASTOWN VIC 3074 | 909935 | Working too close to underground cables | [6 empty] | IMS 232485. A plumber, Scott Ward, tel. 0431 530 848, was using a hands-free underground boring machine to install a new gas or water pipe. Whist in the process of using this machine it has come into contact with the AusNet Services' underground LV service cable running from pole 909935 to the shared service pit at 15 Chapman Ave, Thomastown. The contractor was not in contact with the machine at the time of the incident and has not suffered any electrical shock. The cable was a 700mm depth and in HD conduit with warning tape installed. | Services cable | 0 | 0 | 0 |  | tt5 | Boring machine contacted a live underground LV service cable. | No Go Zone (contact) | 20/02/2018 9:45 |  |  | 9524 | Residential |  | 20180319SPN_07 | Infrastructure (network-based) | -37.6825 | 145.035 | 1 | AusNet Services Distribution | Report | 11603 | 3.9352e-05 | Low voltage AC (<1kV) | Essendon Airport | 3074 | Thomastown | Dug up
A LEI and faults truck attended and measured 15v between the neutral and an independent earth with load applied. The cause of the shock was found to be a high resistance neutral connection at the pole end. The high resistance within the neutral connection allowed the installations earthing system, via the MEN connection to take on a parallel path of return current via the water piping system and many other extraneous parallel earthing paths. As a result of the usual high resistance in the underground water pipe system and other extraneous paths; a voltage rise was impressed on the earthing system allowing a voltage rise on the shower taps. The faults crew cleaned, greased and re-terminated the neutral connection and the LEI re-tested the installation confirming the fault had been rectified with supply left on. | UNIT 6 144-146 WARREN ROAD, MORDIALLOC VIC 3195 | 1808678 |  | Prone to salt deposition |  | Electrical breakdown |  | Phase to earth | 2 | A smart meter communicated a neutral fault at a unit development and a faults crew was dispatched to investigate the cause. Coincidently, a REC was also on site investigating a call from the occupier of unit 6 that electric shocks had been occurring from the shower taps. | Connector/termination | 0 | 0 | 0 |  |  | Loose neutral connection at the pole end. | Minor shock | 16/03/2018 11:30 |  |  | 9526 | Residential |  | 20180319UTD_03 | Infrastructure (network-based) | -37.9874 | 145.095 | 1 | United Energy Distribution | Report | 11605 | 0.0059201 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Mordialloc | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 29 THE CORSO, PARKDALE VIC 3195 | 1808896 |  | Precipitation;Wind |  | Electrical breakdown |  |  | 2 | ACR CH7952 in Warrigal Road, reported the feeder was dim lighting. During very windy conditions following light rain after a lengthy dry spell, 11kV feeder M 35 was patrolled to determine the cause of dim lights and the white phase aluminium to copper ampact connection on the north side of switch number CH7952 was found to be burnt off at pole number LIS 1806675. The feeder patrol continued and a HV intermediate cross arm was found broken due to a pole fire with the HV cross arm hanging in close proximity to the LV conductors at pole number LIS 1808896 in Antibes Street north of The Corso. | Crossarm (wood) | 0 | 0 | 0 |  | M 35 | Insulator tracking to cross arm following light rain. | Pole-top fire | 18/03/2018 12:48 | 1 | Negligible: no ground fire | 9530 | Roadway |  | 20180319UTD_05 | Infrastructure (network-based) | -37.9925 | 145.0724 | 1 | United Energy Distribution | Report | 13042 | 0.001309 | 11kV AC | Moorabbin Airport | 3195 | Parkdale | Crossarm
On arrival crew carried out repairs | MAILORS FLAT-KOROIT ROAD, MAILORS FLAT VIC 3275 | 31017376 |  |  |  | Leakage |  |  | 1 | It could not be determined who reported this incident. On arrival the crew found that a pole fire had occurred on a 22kV & 66kV pole. The pole fire resulted in a grass fire of approx. 5m x 100m = 500m2 of mostly road reserve. There was minor damage to fences and a small area of private property burnt. There were no injuries, and no other damage reported. | Crossarm (wood) | 2 | 2 | 2 |  | KRT PLD 2 | Excessive leakage current | Grassfire | 17/03/2018 21:40 | 1 | Small: 10 - 1000 sq.m | 9552 | Roadway |  | 20180322PWA_01 | Infrastructure (network-based) | -38.299 | 142.4332 | 1 | Powercor | Report | 11645 | 0.039128 | 22kV AC;66kV AC | Warrnambool Airport Ndb | 3275 | Mailors Flat | Pole
On arrival crew carried out repairs | 7165 WESTERN HIGHWAY, NHILL VIC 3418 | 32112322 |  |  |  | Leakage |  |  |  | VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden crossarm required replacement due to the pole fire. There was a small ground fire in private property of approximately 10x3m in the vicinity of the base of the pole. There were no injuries. | Crossarm (wood) | 2 | 2 | 2 |  | NHL015 | Excessive leakage current | Pole-top fire;Grassfire | 19/03/2018 23:19 | 1 | Small: 10 - 1000 sq.m | 9561 | Agricultural |  | 20180322PWA_05 | Infrastructure (network-based) | -36.3368 | 141.7 | 1 | Powercor | Report | 15133 | 0.025716 | 22kV AC | Horsham Aerodrome | 3418 | Nhill | Pole
crew attended and replaced pole | 880 TIMBOON-COLAC ROAD, SIMPSON VIC 3266 | 30044211 |  | Wind;Fallen | [5 empty] | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Simpson area. A farmer reported the pole was severely damaged. The attending crew replaced a pole and subsequently identified a large tree had contacted with the SWER kV line between poles 2 and 3 of the SMIT spur. There was a ground fire of some 400 by 500 m that was extinguished by the CFA. | Conductor (bare) | 0 | 0 | 0 |  | COB011 | Vegetation contacted line | Grassfire | 17/03/2018 21:38 | 1 | Large: more than 10 ha | 9563 | Roadway |  | 20180322PWA_06 | Infrastructure (network-based) | -38.4494 | 143.1409 | 1 | Powercor | Report | 11855 | 0.009463 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3266 | Simpson | Trees
The crew made safe and repaired the broken HV conductor. | NORTHERN HIGHWAY, BALLENDELLA VIC 3561 | 30123456 | Working too close to overhead lines | [5 empty] | 1 | Following an ACR operation., the crew found at Northern Highway Ballendella between LIS 23026 and LIS 27851 a contract Header had made contact with the HV, damaging one of the conductors. There was no reported ground fire, shocks, injuries or property damage. | Conductor (bare) | 2 | 2 | 2 |  | SHP012 | Header struck conductors | Loss of supply;No Go Zone (contact) | 21/03/2018 16:52 |  |  | 9569 | Agricultural |  | 20180323PWA_05 | Infrastructure (network-based) | -36.3018 | 144.6837 | 1 | Powercor | Report | 11680 | 0.041086 | 22kV AC | Bendigo Airport | 3561 | Ballendella | Other
On arrival crew made safe/trimmed trees. | 2A GREENHILL AVENUE, CASTLEMAINE VIC 3450 | 32049313 |  | Within clearances | [5 empty] | Report of damaged powerline and grass fire, at the incident location. On arrival the crew found at Greenhill Ave, Castlemaine, between LIS 508022 & LIS 508023 trees making contact with LV, causing conductors to clash with a broken conductor making contact with the ground, causing a small 20m x 1.5m grass fire There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | CMN003 | Wind storm and vegetation | Grassfire | 18/03/2018 2:53 | 1 | Small: 10 - 1000 sq.m | 9572 | Roadway |  | 20180326PWA_01 | Infrastructure (network-based) | -37.069 | 144.2168 | 1 | Powercor | Report | 11692 | 0.016468 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Trees
On arrival crew made safe and LEI attended to check for possible HVI, no issues identified. | 21 TANTALLA STREET, WEDDERBURN VIC 3518 | 30018807 |  | Blown branch/vegetation | [5 empty] | Customers reported damaged powerline and sparking, at the incident location. On arrival the crew found at 21 Tantalla Street Wedderburn, between LIS 852793 & LIS 610343 a tree had made contact with HV, broken conductors making contact with the ground, causing a small 1m x 1m grass fire. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | CTN002 | Wind storm | Grassfire | 20/03/2018 3:20 | 1 | Localised: less than 10 sq.m | 9578 | Public space |  | 20180326PWA_03 | Infrastructure (network-based) | -36.4124 | 143.6126 | 1 | Powercor | Report | 11707 | 0.0064201 | 22kV AC | Bendigo Airport | 3518 | Wedderburn | Trees
CEOT immediately opened the LGA23 Feeder CB de-energising the line. Dispatched a fault crew to make safe, isolate, investigate and carry out arrange for necessary repairs. Feeder isolated and T-off dropper replaced using bridging insulator to prevent contact. | 6870 BASS HIGHWAY, POUND CREEK VIC 3996 | 5725063 |  |  |  | Conductor clashing |  | Phase to earth | 1 | INS 232938. Initial report: CEOT received a report of transformer leads arcing at lis 5725063. A ground fire was also reported in the vicinity. Final report from attending DAO: LGA23 Bass Hwy, Inverloch area, report of fire beneath our 22kV and WGI-LSSS 1. David Brann (DAO) attended, INCD 57592-x. Weather condition: 20 degrees C, 40-60km/h wind, 45% humidity, fire area, Very high fire rating. Observed burnt fences, scrub on roadside and paddocks, trees in paddocks and about 200m x 500m grass paddock burnt. Flexible T-off dropper at pole 5725063 was blowing in strong wind and contacting the base of insulator on steel x-arm and concrete pole. While flapping in the wind, observed a massive 5m+ arc which burnt spiral dampers on t-off conductors and possibly sent burning material into the paddock. Arc was stopped by reclose at zone substation CB as ACR was by-passed. The arc had happened at least 3 times as per witness and I observed this happen once. T-off dropper replaced using bridging insulator to prevent contact. Dropper is burnt and frayed from contact resulting in arc. Base of insulator has arc marks and dampers are charred black from being burnt by the Arc. Observed about 10 fire trucks on-site, tractors pulling water spray tankers, tanker trucks, tractors with plough and front buckets making fire breaks. Concrete pole 66kV/22kV vertical intermediate, 1phase t-off, steel x-arms. | Dropper/bridge | 0 | 0 | 0 |  | lga23 | Flexible HV T-off dropper at 5725063 was blowing in strong wind and contacting base of insulator on steel x-arm & concrete pole causing arcing and burnt spiral dampers on conductors. | Grassfire | 21/03/2018 17:27 | 1 | Large: more than 10 ha | 9574 | Agricultural |  | 20180326SPN_02 | Infrastructure (network-based) | -38.5916 | 145.7978 | 1 | AusNet Services Distribution | Report | 12630 | 0.032539 | 22kV AC | Morwell (Latrobe Valley Airport) | 3996 | Pound Creek | AF Other
Initial report: CEOT dispatched a fault crew to make safe and investigate. Final report: CEOT dispatched a fault crew to make safe and investigate. All attending carried out a risk assessment and a course of action, was discussed. All non authorised people were instructed not to approach the area. Temporary barricades were used. A Modiewark test was carried out and it was found that the ground earth around the pole was â€œaliveâ€ with potential, and the cows were also â€œaliveâ€ with potential. It was decided to Isolate the HV back further afield, with the control rooms, agreement. Once the HV was isolated another Modiewark test was carried out and the potential was OK and non existent. The local HV fuses at the LGA12POOWONGNth2 at pole 2009546 were, then removed along with the LV pole fuses. All were clear of the area, then the remote, HV fuses, were re- inserted. A further Modiewark test was carried out, and again the potential was non-existent. EAP112385 was issued to carry out further tests on the transformer as a precaution. Tests carried out were:- HV P1-Earth 470 MOhms. HV P2-Earth 470 MOhms. HV P1-P2 low as expected. HVP1-LVP1 400 MOhms. HV-LVP2 400 MOhms. LVP1 & P2 to tank 3.8 MOhms. HV Earth test 4 Ohms. LV Earth test 6 Ohms. As the readings appeared to be in limits, focus was then placed on the LV side. A visual inspection of the overhead cable between, the pole 2009546 and the house, revealed, damage which had worn through the insulation from its metal tie that secures the conductor â€œwrap around., rubbed through, the insulation, of the overhead cable phase, which in turn tracked through the metal tie, then through the hook on the concrete pole, tracked through the poles earth system, down to ground, causing a step potential. The metal tie strain â€œwrap aroundâ€ that was on the private service cable (POEL) was not designed to be used on this type of conductor, rubbed through, the insulation, of the private overhead cable phase, which in turn tracked through the hook on the concrete pole, tracked through the poles earth system, down to ground, causing a step potential. The damaged LV overhead cable was removed from pole 2009546 by disconnecting it from the junction box. EAP 112385 was then cancelled, and with the Modiewark tester in place, HV was restored at Sub LGA12POOWONGNth2. No step potential was detected or present. Defect 11652 was issued to the customer with a verbal explanation of the problem with the LV overhead cable between the pole 2009546 and house mains box. | 385 OMEARAS ROAD S, POOWONG NORTH VIC 3988 | 2009546 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 233016. Initial report: 3 Dead cows found at base of substation pole 2009546. Final report: Luke went out to herd the cows for milking and discovered 3 Jersey milking cows near the sub transformer pole laying on their sides showng no movement, he attended to them wearing his rubber boots, to see if he could help them, actually touching one with his boot. He reports hearing a zapping /arcing noise from the pole, realising his situation slowly moved away and yelled at his partner Melanie, and Children, to stay away from the pole. Luke then instructed his wife Melanie to call AusNet Services and â€œheardedâ€ the rest of the cows away to another area for milking. Melanie called the AusNet Services' faults line. The private service (POEL) cable was attached with a steel make-off onto the steel framework of the pole that rubbed into the active conductor creating a circuit straight to ground. The private cable was a 3 Wire black ribbon type cable with copper conductors. | Pole (concrete);Customer installation | 0 | 0 | 0 |  | lga12 | Overhead POEL cable between the pole and the house was damaged with insulation worn through the a metal tie that secured the cable wrap-on (around) termination, which in turn tracked through the metal tie, and the hook on the concrete pole, tracked through the pole's earth system, down to ground, causing a step potential. | Fatality of livestock, pet or companion animal | 26/03/2018 7:17 |  |  | 9584 | Agricultural |  | 20180326SPN_07 | Infrastructure (network-based) | -38.3025 | 145.8003 | 1 | AusNet Services Distribution | Report | 11717 | 0.031471 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3988 | Poowong North | OH Cable
The single phase service was replaced with a XLPE type and the tree was cut clear. Installation tests were completed and supply was left on. | 20 WAKOOL AVENUE, ROSEBUD VIC 3939 | 1311483 |  | Wind;Alive |  |  |  |  | 2 | Caller reports wire has come down and caused a small grass fire. During strong winds, a single phase overhead service was rubbing on a tree on the customers property that caused molten metal to fall into the dry grass below and a small fire estimated to be 0.5sqm to start that was quickly extinguished by the CFA who were on site. | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Grassfire | 22/03/2018 20:15 | 1 | Localised: less than 10 sq.m | 9586 | Residential |  | 20180326UTD_02 | Infrastructure (network-based) | -38.3829 | 144.9229 | 1 | United Energy Distribution | Report | 13052 | 0.005338 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Trees
NAO AH Ardeer has instructed all works to cease immediately on site, and contact PCA NGZ and PTW for further information | 56 CANONBURY CIRCLE, SEABROOK VIC 3028 | 60084103 | Working too close to underground cables | [6 empty] | Whilst excavating for a pool installation an excavator had hit and damaged (prior to Friday 23/03/2018 @ 11:36) 1 x 125mm spare conduit at the South Western corner of the property of 56 Canonbury Circle, Seabrook, 3028 and in an attempt to establish what and if the second 125mm conduit was spare/empty the customers excavator Bower Excavations, has attempted to put a hack saw and cut through the second conduit. This second conduit is not spare and has a LIVE in service 185mm.3/c.22.a.x.hc.h HV UG Cable. In an attempt to stop further damage to PCA Assets and possible injury or death to the excavator driver, a verbal argument, abuse and threats have occurred between Mrs Babic of 56 Canonbury Circle, Seabrook, 3028 and the excavator driver. Due to the argument, abuse and threats directed towards Mrs Babic she has threatened to call the Police and out of fear she has had to lock herself inside her house. At this point the excavator driver, stopped work packed up and has left site. There was no fire, no reported injuries and no third party property damage. | Cable | 2 | 2 | 2 |  | LV006 | Excavation work | No Go Zone (contact) | 24/03/2018 11:36 |  |  | 9587 | Residential |  | 20180327PWA_01 | Infrastructure (network-based) | -37.8823 | 144.7612 | 1 | Powercor | Report | 11723 | 0.0060683 | 22kV AC | Laverton Raaf | 3028 | Seabrook | Vehicle
The house was vacant with no evidence of any residents. The crew made the site safe and issued a defect notice. | 9 FITZGERALD STREET, BALWYN VIC 3103 | 30176449 |  | Blown branch/vegetation | [5 empty] | Vicfire reported a small grass fire in the front yard of 9 Fitzgerald Street, Balwyn. On Arrival the CitiPower crew found a private tree within the yard of 9 Fitzgerald St, Balwyn had bought down the overhead service to the property. The crew found the insulation of the service wire had been damage by the tree and a 150mm2 charring mark was found on the grass. There was no reported injuries, no third party damage, no shocks. | Service conductor | 2 | 2 | 2 |  | WD032 | Vegetation: Trees Incident | Grassfire | 24/03/2018 11:12 | 1 | Localised: less than 10 sq.m | 9589 | Residential |  | 20180327PWA_03 | Infrastructure (network-based) | -37.8096 | 145.0993 | 1 | CitiPower | Report | 11727 | 0.0055833 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Trees
On arrival crew isolated supply and carried out repairs. | 16 EDWARDS DRIVE, ALTONA MEADOWS VIC 3028 | 30116842 |  |  |  | Leakage |  |  | 1 | A customer reported that there is a pole on fire at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. There was no ground fire and no injury as a result of this incident. | Crossarm (wood) | 2 | 2 | 2 |  | LVN022 | Excessive leakage current. | Pole-top fire | 43103.2986 | 1 | Negligible: no ground fire | 9594 | Roadway |  | 20180327PWA_06 | Infrastructure (network-based) | -37.8835 | 144.7788 | 1 | Powercor | Report | 11732 | 0.031924 | 22kV AC | Laverton Raaf | 3028 | Altona Meadows | Crossarm
The tree cutter from "The Tree Works" advised the First Responder that he was happy for it to be reported to ESV to stop this from happening in the future. | 1 FOREST ROAD, BLACKBURN VIC 3130 |  | Working too close to overhead lines | [5 empty] | 2 | A Zinfra First Responder was completing planned HV switching and found tree cutter in close proximity to the over head conductors at 1 Forest Road, Blackburn. The Zinfra First Responder advised them to stop work immediately and come down from the tree which they did. The First Responder advised the crew they were in breach of No Go Zone Rules and a tree cutter replied by stating itâ€™s a "grey area". | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/03/2018 8:30 |  |  | 9596 | Roadway |  | 20180327UTD_03 | Infrastructure (network-based) | -37.8306 | 145.166 | 1 | United Energy Distribution | Report | 11734 | 0.0013218 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Other
United Energy's zone substation maintenance contractor was contacted and sent to the site to repair the door lock and bolt moved to the inside of the access gate (Telstra has no access to enter their tower with out contacting UE for access). Finally the gate was bent back to normal and the chain fence re-wired. A review of the break-in was completed with the following actions created. - Access to the communications tower is now only available through NP zone substation until the upgrading of the door lock is completed to an acceptable security standard. This is the third break-in through this door in as many years. - Review the lease for the Telco at NP zone substation to identify the level of security required by the telecommunications company. - Upgrading the internal fence with the new standard high security palisade or weld mesh fencing. This site is a store for cable and kiosk transformers and a target for theft and vandalism. United Energy to review the housing of materials at the zone substation under the NSA single service provider arrangement. | CORRIGAN ROAD, NOBLE PARK VIC 3174 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Passerby states the gate is wide open at NP Zone Substation. The Noble Park zone substation telecommunications door was reported to be open and a Zinfra First Responder was dispatched to investigate. He identified the door lock was broken with the chain fence cut. In addition, the main gate was bent and cables were cut from cable drums. The Victoria Police were advised and attended a short time later. The First Responder took photos and advised his supervisor. | Conductor (insulated);Zone substation | 0 | 0 | 0 |  | NP zone substation | Unknown copper thief's broke into NP zone substation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 24/03/2018 12:15 |  |  | 9598 | Other | Zone Substation | 20180327UTD_05 | Infrastructure (network-based) | -37.9791 | 145.166 | 1 | United Energy Distribution | Report | 11736 | 0.0049977 | 66kV AC | Moorabbin Airport | 3174 | Noble Park | Other
Jemena faults were notified at approximately 2.30pm to disconnect supply. Jemena faults crew attended the premises at approximately 5.00pm, disconnected supply and issued a level 1 defect. Due to the nature and seriousness of the customers installation, ESV were notified and their on call compliance officer attended. The ESV officer was able to observe the situation on site and obtain photos and investigate the situation. | 10 MERINO STREET, RESERVOIR VIC 3073 |  | Unauthorised work;Unauthorised access | [5 empty] | 2 | Jemena/Zinfra compliance officer received a call from a Techsafe LEI who was working next door to advise that Jemena network assets had been disturbed and were in an unsafe manner. Jemena/Zinfra compliance officer was in the area and attended site to find 3 electricians on site working. He found the customer POA and FOLCB had been removed from the house facia and the FOLCB cover missing, with exposed live parts and the overhead service hanging across the house roof and the metal guttering. He also found the customer meter board and fuse board inside the house had also been moved and relocated. The fuse board was completely open and exposed with live parts. The house was in a complete mess with people working and renovating in the house. There were also people living in the house along with a number of dogs, one of which kept jumping up to the meter box fuse board. Shortly after the compliance officer's arrival and observation of the unsafe installation, the electricians on site began to pack up and then left site. The customer's electrical installation was left in a seriously unsafe situation. The home owner was extremely hostile and aggressive and made numerous violent threats toward the compliance officer, the ESV officer (David Bibby) and the Jemena Faults crew who attended the premises to disconnect supply. Photos have been attached in the "Notes & Findings" section Details of Registered Electrical Contractor (REC) have been included in the "Other information sources" section | Service conductor;Switchboard;Meter board (including fuses) | 0 | 0 | 0 |  | TT03 | Unauthorised work and unauthorised access to electrical assets | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/03/2018 12:29 |  |  | 9599 | Residential |  | 20180328JEM_01 | Infrastructure (network-based) | -37.7079 | 145.0329 | 1 | Jemena | Report | 11773 | 0.034524 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
On arrival crew isolated supply and carried out repairs. | 2415 PORTARLINGTON ROAD, BELLARINE VIC 3223 | 30076493 |  |  |  | Leakage |  |  |  | A passer-by reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | GLE031 | Excessive leakage current | Pole-top fire | 43103.5819 | 1 | Negligible: no ground fire | 9602 | Roadway |  | 20180328PWA_03 | Infrastructure (network-based) | -38.1652 | 144.4169 | 1 | Powercor | Report | 11740 | 0.0060336 | 22kV AC | Avalon Airport | 3223 | Bellarine | Crossarm
On arrival crew isolated supply and carried out repairs. | 8 WATTLEPARK AVENUE, MOOLAP VIC 3224 | 31011967 |  |  |  | Leakage |  |  | 1 | A customer reported to Powercor a pole fire at the incident location. On arrival the crew found that a wooden pole with HV wood cross arm had sustained significant damage due to a pole fire. The top of the pole structure had collapsed onto itself resulting in the HV Assets resting in close proximity to the LV conductors. Initially is was suspected that a HVI may of also occurred however no evidence of a HVI has been found. There was no ground fire, no reported injuries, no 3rd party damage , protection operated as expected. | Crossarm (wood) | 2 | 2 | 2 |  | GLE031 | Excessive leakage current | Pole-top fire | 24/03/2018 13:45 | 1 | Negligible: no ground fire | 9615 | Roadway |  | 20180329PWA_05 | Infrastructure (network-based) | -38.1646 | 144.4092 | 1 | Powercor | Report | 11756 | 0.006213 | 22kV AC | Avalon Airport | 3224 | Moolap | Pole
On arrival crew isolated supply and carried out repairs. | 772 HENTY HIGHWAY, WARRACKNABEAL VIC 3393 | 32107264 |  |  |  | Leakage |  |  |  | A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm burnt through. The crew made the place safe and the repairs have been completed. There were no injuries, HVI or ground fire | Crossarm (wood) | 2 | 2 | 2 |  | HSM003 | Excessive leakage current | Pole-top fire | 26/03/2018 9:20 | 1 | Negligible: no ground fire | 9616 | Agricultural |  | 20180329PWA_06 | Infrastructure (network-based) | -36.1848 | 142.3986 | 1 | Powercor | Report | 11757 | 0.015181 | 22kV AC | Horsham Aerodrome | 3393 | Warracknabeal | Crossarm
On arrival crew isolated supply and carried out repairs. | 1422 CHARLTON-ST ARNAUD ROAD, YEUNGROON VIC 3525 | 32027217 |  |  |  | Leakage |  |  |  | Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden support ( for ISO single phase side HV fuse units ) cross-arm was fire damaged but supply remained on. There was no ground fire, no reported injuries, no 3rd party damage. | Crossarm (wood) | 2 | 2 | 2 |  | CTN006 | Excessive leakage current | Pole-top fire | 25/03/2018 22:42 | 1 | Negligible: no ground fire | 9618 | Roadway |  | 20180329PWA_08 | Infrastructure (network-based) | -36.384 | 143.293 | 1 | Powercor | Report | 11760 | 0.0022546 | 22kV AC | Swan Hill Aerodrome | 3525 | Yeungroon | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 2 CRESTVIEW COURT, RYE VIC 3941 | 1317970 |  | Precipitation;Prone to salt deposition |  | Conductor clashing;Electrical breakdown;Leakage |  |  | 1 | At 1336hrs on 26/03/2018, ACR RB7183 reclosed to lock out with FLISR disabled at the time. Emergency services advised a smoking transformer at the intersection of Crestview Court and Sunshine Grove, Rye. Following light drizzle, tracking occurred at a HV/LV tee-off pole causing a pole fire to occur at the LV cross arm kingbolt and the pole to break. The HV conductors were hanging loosely in the air and clashed at pole number LIS 1317970. The pole was severely damaged and requires replacement. The faults crew requested that a LEI attend to investigate as a HVI was suspected to customers supplied from "Crestview-Sunshine" substation. The LEI attended and checked properties in the vicinity and confirmed that a high voltage injection did not occur. | Pole (wood) | 0 | 0 | 0 |  | STO 23 | Tracking due to probable salt borne contaminants as the pole is in close proximity to Port Phillip Bay. | Pole-top fire | 26/03/2018 13:36 | 1 | Negligible: no ground fire | 9614 | Residential |  | 20180329UTD_02 | Infrastructure (network-based) | -38.3824 | 144.8321 | 1 | United Energy Distribution | Report | 13056 | 0.010714 | 22kV AC | Moorabbin Airport | 3941 | Rye | Pole
Crew completed repairs and restored supply. | 25 ROWSLEY STATION ROAD, MADDINGLEY VIC 3340 | 32176821 | Working too close to overhead lines | [5 empty] | 1 | Customers HV operator reports tipper has contacted and broken a HV conductor on site. A crew attended and found a HV conductor had been broken and laying on ground btn P1 and P2 C.S.R S/L. The truck was not on site when crew arrived There were no reported shocks, injuries or fire starts. | Conductor (bare) | 2 | 2 | 2 |  | BMH005 | Truck contacted conductors | No Go Zone (contact);Damage to network assets | 29/03/2018 12:06 |  |  | 9621 | Industrial |  | 20180403PWA_02 | Infrastructure (network-based) | -37.7098 | 144.4074 | 1 | Powercor | Report | 11776 | 0.02935 | 22kV AC | Avalon Airport | 3340 | Maddingley | Vehicle
On arrival crew isolated supply and carried out repairs. | 759 GUNAMALARY ROAD, MURRAYVILLE VIC 3512 | 32153230 |  |  |  | Leakage |  |  | 1 | Following customer calls, a patrol found pole fire at incident location (Gunmalary 15 ) There was no ground fire or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 25/03/2018 22:03 | 1 | Negligible: no ground fire | 9628 | Agricultural |  | 20180403PWA_09 | Infrastructure (network-based) | -35.3303 | 141.2487 | 1 | Powercor | Report | 11783 | 0.0034491 | 22kV AC | Mildura Airport | 3512 | Murrayville | Pole
CEOT dispatched a LEI to the customer's installation with a reported electric shock and dimming lights. Tested on site found 5.5 volts on the earth bar. LEI isolated supply until the service truck attended. Service truck removed supply, checked connections at POA and at distribution pole. Service passed NST test and loop impedance test. Service crew proceeded to check customer's connection and found a loose neutral at the FOLCB. LEI continued to test at the main switchboard and supply passed all VESI tests. Tests all passed. NST â€“ pass. Loop impedance - 0.42 Ohm PSC - 587 Amps. Independent Earth to N bar - 0 .5V. 242 Volts. | 63 BROWNS ROAD, MONTROSE VIC 3765 | 1001418 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 232662. An AusNet Services' LEI was called to a customer's electrical installation with reported electric shock and dimming lights. Customer called to inform AusNet Services' her son received an electric shock. Supply neutral broke away in neutral screen cable at the FOLCB at POA. | Service conductor | 0 | 0 | 0 |  | cyn33 | Supply neutral broke away in neutral screen cable at the FOLCB at POA. | Minor shock | 43103.9417 |  |  | 9639 | Residential |  | 20180405SPN_01 | Infrastructure (customer connection) | -37.8103 | 145.3644 | 1 | AusNet Services Distribution | Report | 11798 | 0.017009 | Low voltage AC (<1kV) | Moorabbin Airport | 3765 | Montrose | Connection
Fault crew sent to investigate and found burnt out fuse box on pole 1409569. Plastic fell to ground and caused a ground fire at base of pole. Fire approx. 30cm around base of pole. | 717 MAROONDAH HIGHWAY, COLDSTREAM VIC 3770 | 1409569 |  |  |  | Overheated connection |  |  |  | IMS 233147. Received call from Fire Brigade for pole fire. Possibly at POA. DAO Attended 6/4/18 at 630pm. Photos taken and attached. Small fire at base of pole approx. 30cm around pole. No structural damage to pole or customers property. Customer advised minimal load connected at time as early AM. | Any other type | 0 | 0 | 0 |  | ldl23 | LV fuse box. | Grassfire | 43255.2729 | 1 | Localised: less than 10 sq.m | 9644 | Agricultural |  | 20180406SPN_02 | Infrastructure (network-based) | -37.6897 | 145.422 | 1 | AusNet Services Distribution | Report | 11809 | 0.019741 | Low voltage AC (<1kV) | Moorabbin Airport | 3770 | Coldstream | Fuse
On arrival crew isolated supply and carried out repairs | 3312 MELBOURNE-LANCEFIELD ROAD, LANCEFIELD VIC 3435 | 30036827 | Working too close to underground cables | [6 empty] | A contractor (David) reported he had hit an underground LV cable while doing civil works for VicRoads at the incident location. On arrival the crew found that a Low Voltage (LV) UG service had been dug up by the contractor. There were no reported injuries or other third party damage. | Services cable | 2 | 2 | 2 |  | WND013 | Excavation work | Loss of supply;Damage to network assets | 22/02/2018 12:45 |  |  | 9648 | Roadway |  | 20180409PWA_02 | Infrastructure (network-based) | -37.3042 | 144.7369 | 1 | Powercor | Report | 11815 | 0.022571 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3312 | Lancefield | Dug up
Crew attended and repaired conductors | 645 COBDEN-PORT CAMPBELL ROAD, GLENFYNE VIC 3266 | 33036052 |  | Fallen |  |  |  |  | 1 | Emergency services reported a tree pulled wires down, started grass fire in Cobden-port Campbell rd. Cobden On arrival the crew found a large gum tree had fallen bringing down conductors on the opposite side of the road. There was a grass fire initiated which then burnt an area of around 300m by 5 m, largely along road reserve. Some farm fencing was damaged. There were no reported injuries. | Conductor (bare) | 0 | 0 | 0 |  | COB011 | Vegetation: Trees Incident | Grassfire | 43316.5979 | 1 | Medium: 1000 sq.m - 10 ha | 9650 | Roadway |  | 20180409PWA_04 | Infrastructure (network-based) | -38.3877 | 143.0697 | 1 | Powercor | Report | 11820 | 0.012017 | 22kV AC | Warrnambool Airport Ndb | 3266 | Glenfyne | Trees
On arrival crew isolated supply and carried out repairs. | 6-9 QUEENS ROAD, MELBOURNE VIC 3004 | 30213082 |  |  |  | Mechanical breakdown |  |  |  | Emergency Services reported a fire at above incident location. On arrival the crew found a HV cable head termination/connection failure at the insulators, overheated and caught on fire, then caused High Voltage injection due to flash over onto the low voltage overhead line. There were no reported injuries nor fire on the ground. There were potential third party property damages to some public lightings and VicRoad traffic light gantries on Queens Road. | Dropper/bridge | 2 | 2 | 2 |  | AP017 | mechanical failure of helical terminations | HV injection;Damage to network assets | 43376.7431 |  |  | 9475 | Roadway |  | 20180313PWA_03 | Infrastructure (network-based) | -37.8378 | 144.9738 | 1 | CitiPower | Report | 11536 | 0.023 | 11kV AC | Essendon Airport | 3004 | Melbourne | Connection
Controller opened upstream ACR when made aware. CEOT dispatched a fault crew and operator to make safe and repair broken conductors. CEOT notified the local DAO. Fault crew repaired the conductor. | 582 CANAVANS ROAD, MOUNT ECCLES VIC 3953 | 2000744 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232769. Excavator (Allens 0417550568) drove into bare O/H HV conductors. Conductor broke @ LIS: 2000744. 2 x HV Fuses blew @ sw: 568172. No injuries occurred and no other damage. Upon arrival the local DAO measured the repaired conductors at 7.23 metres. There were track marks visible on the day where the conductor was repaired however the excavator operator said he never went in that area and had no need to. The excavator was parked nowhere near the line by the time the DAO had attended the site. | Conductor (bare) | 0 | 0 | 0 |  | lga11 | Excavator made contact with overhead HV conductors. | No Go Zone (contact) | 43315.7076 |  |  | 9463 |  |  | 20180313SPN_01 | Infrastructure (network-based) | -38.3937 | 145.9926 | 1 | AusNet Services Distribution | Report | 11516 | 0.02437 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Mount Eccles | Vehicle
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. Final report: Dispatched fault crew to investigate. Found small fire in vicinity of AusNet Services' pole. The old service LV leads / cable and the LV fuses were removed and replaced by the fault crew. The local DAO attended site after the fault had been rectified and took photos of the burnt area on the ground around the base of the pole. The fire area was contained to approximately 3m x 3m. There was no damage to the pole or other AusNet Services' assets at this location. | 1315 MEENIYAN-MIRBOO NORTH ROAD, DUMBALK VIC 3956 | 2002195 |  |  |  | Electrical breakdown;Overheated connection |  |  | 1 | IMS 232793. Initial report: CFA reported pole fire. AusNet Services' fault crew found a 3m x 3m ground fire in the vicinity. Damaged LV transformer leads. Final report: Failed LV supply cable (LV leads) from the substation transformer fuse box to the customer's fuse box (FOLCB) protecting an underground supply. Fault crew attended site and found that the service cable between AusNet Services' transformer LV fuses and the customer's private fuses at FOLCB had failed. LV fuses on Transformer side had blown. | Pole mounted | 0 | 0 | 0 |  | lga13 | Damaged LV transformer leads cable. | Grassfire | 43376.3986 | 1 | Localised: less than 10 sq.m | 9465 | Agricultural |  | 20180313SPN_03 | Infrastructure (network-based) | -38.5048 | 146.1174 | 1 | AusNet Services Distribution | Report | 12017 | 0.037007 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3956 | Dumbalk | OH Cable
As indicated in the previous report, it was suggested the indoor substation is isolated with the copper removed to avoid a re-occurrence. This has now been urgently programmed to avoid the potential of a copper thief being electrocuted as the HV remains alive to the substation with concerns for safety around unauthorised and unlawful entry to this substation. Below is the basic scope of works required for decommissioning the high risk "Geriatric Hosp-Watts" indoor substation. 1. Install approximately 50m of LV underground cable from new fused krone box at pole 3315632 to the â€˜Eâ€™ LV underground cable outside number 1 Pelican Court (south circuit of "Geriatric Hosp-Watts" indoor sub). 2. Upgrade LV north-west circuit (LV1) fuses from the 315kVA "Williams-Watts" substation at pole 3315629. 3. Decommission the "Geriatric Hosp-Watts" indoor substation by removing all HV/LV equipment and cables in and connecting the substation including any HV pole mounted switchgear. 4. Cut and cap HV UGC at CHP feeding "Geriatric Hosp-Watts" indoor substation. 5. Cut and terminate LV cable in NEW pit at the north end of Pelican Court. 6. Update all plan drawings, GIS systems and SAP as required including closing of any outstanding notifications assigned to "Geriatric Hosp-Watts" indoor substation. United Energy have requested the work is completed by 16/03/2018 or earlier if possible. The Police have ceased entering the site due to the asbestos issues and the owner of the property has arranged for a security guard to remain on site. | PELICAN PLACE, MOUNT ELIZA VIC 3930 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Caller reports the substation has been broken into again. Refer also to Incident Reports 20180301UTD_01 and 20180305UTD_02. An attempted copper theft occurred for the fourth time at "Geriatric Hosp - Watts" when unknown persons broke into the Indoor substation. It appears nothing was stolen in this instance. The police have been in attendance and advised of a safety issue as disturbed asbestos has been identified throughout the vandalised and derelict site. | Copper;Indoor | 0 | 0 | 0 |  | FSH 13 | Unknown persons broke into the indoor substation in an attempted copper theft. | No Go Zone (contact);Damage to network assets | 43254.4167 |  |  | 9462 | Construction |  | 20180313UTD_01 | Infrastructure (network-based) | -38.1691 | 145.0871 | 1 | United Energy Distribution | Report | 11513 | 0.010815 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Other
A faults crew attended and the underground supply was disconnected at the pole end (pole No. LIS 1804478) and the site made safe. The pole to pit supervisor was arranging the installation of a new pit base for the new development. | 5 SHASTA AVENUE, BRIGHTON EAST VIC 3187 | 1804478 | Vandalism | [5 empty] | 2 | The Zinfra pole to pit supervisor attended the vacant land following an email that was received by the United Energy New Connections Department from violettaw1@hotmail.com that mentioned. To whom it may concern, I've spoken to Jocelyn today from United Energy and informed her of the issue with my underground electrical pit at 5 Shasta Avenue, Brighton East VIC 3187. The underground electrical pit which was installed in 2017 was installed too close to the front fence and when the front brick fence was pulled down by the Demolition company the footings of the fence pulled the pit up. The pit only had asphalt to cover the hole around, and therefore it was very mobile and not fully concreted in. The pit is now broken and needs to be replaced early next week. I have attached the photos. The first photo is of the current broken pit and the second photo is of the pit when it was installed. Should you have any questions or queries, please feel free to contact me anytime. Kind Regards Violetta 0402 065 325 The Zinfra pole to pit supervisor attended the site and found the pit base had been removed with live cables left in a dangerous manner where members of the general public could easily touch the bare cable terminations. The pit lid remained at the site. (Photos attached) | Services pit | 0 | 0 | 0 |  |  | Demolition workers removed the base of the pit and left live cables dangerously exposed. | No Go Zone (contact);Damage to network assets | 43284.625 |  |  | 9471 | Residential |  | 20180313UTD_03 | Infrastructure (network-based) | -37.9165 | 145.0076 | 1 | United Energy Distribution | Report | 11530 | 0.019316 | Low voltage AC (<1kV) | Moorabbin Airport | 3187 | Brighton East | Dug up
Site made safe Replaced HV crossarm | 23-27 VICTORY ROAD, AIRPORT WEST VIC 3042 | Pole no. A087267 |  |  |  | Leakage |  |  | 2 | HV crossarm fire on pole no. A087267 The crossarm significantly charred but did not fail No ground fire Photos are attached in the "Notes & Findings" section | Crossarm (wood) | 0 | 0 | 0 |  | AW05 | Tracking/electrical leakage | Pole-top fire | 28/02/2018 23:09 | 1 | Negligible: no ground fire | 9480 | Commercial |  | 20180314JEM_01 | Infrastructure (network-based) | -37.7187 | 144.8898 | 1 | Jemena | Report | 12948 | 0.0025428 | 22kV AC | Essendon Airport | 3042 | Airport West | Crossarm
Site made safe Replaced HV/LV pole Electrical inspector attended site to investigate possible high voltage injection, but did not find any damage or evidence of high voltage injection (Techsafe report attached in Notes and Findings section) | 8-10 SCAMMEL STREET, CAMPBELLFIELD VIC 3061 | Pole no. A100460 |  | Precipitation |  | Leakage |  |  | 2 | Light rain caused crossarm fire on pole No ground fire No photo is available | Pole (wood) | 0 | 0 | 0 |  | ST12 | Tracking/leakage due to conducive climatic conditions (light rain) | Pole-top fire | 43103.3139 | 1 | Negligible: no ground fire | 9483 | Commercial |  | 20180314JEM_03 | Infrastructure (network-based) | -37.6474 | 144.9443 | 1 | Jemena | Report | 13018 | 0.0172 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Crossarm
The surge diverter was programmed to be replaced and there was no identified cause. | 11 FOAM STREET, ELWOOD VIC 3184 | 2308135 |  |  |  | Defective component |  |  | 1 | At 1831hrs on 08/03/2018, 11kV feeder EW 14 circuit breaker successfully reclosed and held. The occupier of a unit at 23 Foam Street, Elwood advised of a load bang from the pole that was on fire. Leaves from a nearby tree also caught on fire and they now have extinguished with emergency services arriving on site. It appeared a surge diverter at pole number LIS 2308135 failed but the cause was unknown. | Surge diverter | 0 | 0 | 0 |  | EW 14 | Failed surge diverter. | Pole-top fire | 43315.7715 | 1 | Negligible: no ground fire | 9490 | Roadway |  | 20180315UTD_02 | Infrastructure (network-based) | -37.8843 | 144.9911 | 1 | United Energy Distribution | Report | 13036 | 0.017316 | 11kV AC | Moorabbin Airport | 3184 | Elwood | AF Other
On arrival crew isolated supply and carried out repairs | 970 COGHILLS CREEK ROAD, COGHILLS CREEK VIC 3364 | 30006858 |  |  |  | Leakage |  |  | 1 | An employee reported a burnt cross arm on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | BAN006 | Excessive leakage current | Pole-top fire | 15/03/2018 9:45 | 1 | Negligible: no ground fire | 9499 | Roadway |  | 20180316PWA_01 | Infrastructure (network-based) | -37.3736 | 143.7488 | 1 | Powercor | Report | 11565 | 0.038569 | 22kV AC | Ballarat Aerodrome | 3364 | Coghills Creek | Crossarm
On arrival crew isolated supply and carried out repairs. | 18 MALINDA CRESCENT, BELL PARK VIC 3215 | 34013007 | Vehicle | [6 empty] | A customer reported that the pillar outside his property had caught on fire at the incident location. On arrival the crew found that a 415V LV UG pillar had been damaged by an unknown vehicle at some time in the past. The Customer reported that he tried to straighten the Pillar by pushing on the lid, at which time the cables inside the pillar began arcing, resulting in a small grass fire of less than 0.5m2 around the base of the pillar. The Customer did not receive a shock, and was not injured. There were no injuries, and no other damage reported. | LV Pillar | 2 | 2 | 2 |  | CRO022 | Customer straitening pillar lid | Grassfire | 15/03/2018 17:32 | 1 | Localised: less than 10 sq.m | 9502 | Public space |  | 20180316PWA_03 | Infrastructure (network-based) | -38.0954 | 144.3392 | 1 | Powercor | Report | 11812 | 0.0036597 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Park | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 4 ESTA STREET, BLACKBURN NORTH VIC 3130 | 7028663 | Vehicle |  |  | HV injection |  |  | 1 | At 1426hrs on 15/03/2018, 22kV feeder DC 08 circuit breaker reclosed to lockout affecting 3017 customers. An unknown vehicle struck a council tree outside 4 Esta Street and flicked the broken branch into the HV and LV conductors near pole number LIS 7028663. Secondary damage occurred in Eram Road, 1 pole east of "Eram-Docking" substation where the white phase HV bridge was found burnt off at pole number LIS 7035527 due to probable fault current. Customers in the area advised the faults crew of a loud bang followed by a burning smell from inside their homes. The faults crew requested that a LEI attend to investigate as a HVI was suspected to customers supplied from "Chapman-Mdlboro" substation. The LEI confirmed a high voltage injection occurred (BWD 1804) affecting customers who reside in the vicinity that sustained minor damage to metering equipment and appliances. | Conductor (bare);Smart meter | 0 | 0 | 0 |  | DC 08 | Vegetation: Trees Incident | HV injection;Loss of supply | 15/03/2018 14:26 |  |  | 9500 | Residential |  | 20180316UTD_01 | Infrastructure (network-based) | -37.8027 | 145.1425 | 1 | United Energy Distribution | Report | 11566 | 0.016855 | 22kV AC | Moorabbin Airport | 3130 | Blackburn North | Vehicle
The attending LEI removed the internal service fuse and disconnected the light and requested a service crew. Crew made site safe and Jemena service crew replaced the burnt out din rail connection terminal and re terminated the neutral and earthing conductors. They performed an NST test which passed. The LEI conducted voltage tests and recorded zero volts between an independent earth and the light pole. The light remained on supply. | 35A YELLOWBOX DRIVE, CRAIGIEBURN VIC 3064 |  |  |  |  | Neutral fault |  |  | 2 | Customer (Robert) received electric shock when his right hand was holding one section of fencing while his left hand made contact with another section. | Public lighting | 0 | 0 | 0 |  |  | Voltage tests revealed that a metallic street light had an open circuit neutral resulting in a voltage rise measured at 205v on the pole which was in contact with the metallic fence. | Minor shock | 17/03/2018 12:00 |  |  | 9509 |  |  | 20180317JEM_03 | Infrastructure (network-based) | -37.6185 | 144.9424 | 1 | Jemena | Report | 11578 | 0.0078426 | Low voltage AC (<1kV) | Essendon Airport | 3064 | Craigieburn | Connection
On arrival crew isolated supply and carried out repairs. | WESTERN HIGHWAY, LILLIMUR VIC 3420 | 32122137 |  |  |  | Leakage |  |  |  | An customer reported a low conductor at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. No protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 18/03/2018 11:37 | 1 | Negligible: no ground fire | 9527 | Agricultural |  | 20180319PWA_04 | Infrastructure (network-based) | -36.3654 | 141.1588 | 1 | Powercor | Report | 11606 | 0.027476 | 22kV AC | Horsham Aerodrome | 3420 | Lillimur | Crossarm
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for necessary repairs. The fault crew made safe the substation was placed under parallel. The crew returned on Sunday to repair the damage to the LV bushing connection. | 15 VIEW STREET, HEALESVILLE VIC 3777 | 1403271 |  |  |  | Overheated connection |  |  | 1 | IMS 232876. Initial report: Fire brigade reported a fire in vicinity of an AusNet Services' pole. Red phase LV bushing was burnt off at substation. 30 sq. metre fire. Final report: Report from the attending DAO: Attended site on the 20/03/2018 to a report of a fire and discovered that the LV bushing of the pole type substation transformer was burnt out. The lead running to the LV bushing was also burnt. The fire had occurred the night before and was out on my arrival. The substation had been placed under parallel and had not been fixed on my arrival. The cause of the incident was a loose LV connection. The loose connection caused sparks to arise and these sparks hit the ground and caused a moderate fire around the base of the pole. No damage to any property or residences. Only a small grass fire of 5 sq. metres in size occurred. LV fuses operated. | Connector/termination;Transformer | 0 | 0 | 0 |  | wyk24 | Burnt off LV bushing on transformer - faulty connection. | Grassfire | 17/03/2018 18:39 | 1 | Localised: less than 10 sq.m | 9510 | Residential |  | 20180319SPN_01 | Infrastructure (network-based) | -37.6565 | 145.5171 | 1 | AusNet Services Distribution | Report | 13556 | 0.02091 | Low voltage AC (<1kV) | Moorabbin Airport | 3777 | Healesville | Connection
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out /arrange for repairs. CEOT also advised the local DAO. CFA attended and extinguished the fire. Site made safe, photos taken. Final report by DAO: AusNet Services crews had isolated the spur line by breaking bridges on pole 2510933 and installed an on-site earth at pole 2510934. I visited multiple poles with the lines crew to take photos and gather data for the investigation. Crew have repaired the damaged conductor and replaced the damaged pole LIS 2510936 and repaired the crossarm 2501936 after extreme wind and thunders storm activity in the area on the 18th of March 18. | LICOLA ROAD, GLENMAGGIE VIC 3858 | 2510936 |  | Lightning | [5 empty] | IMS 232878. Initial report: CEOT received a report of wires down and a grass fire in vicinity. HV conductor was down between Poles 2510935 & 2510937. Final report by local DAO: Upon arriving on site I viewed a paddock which had been burnt. The fire size was approx. 100mx50m. Location of burnt area was under the MFA22 22kV feeder. Only grass burnt, no fencing or buildings. Conductor was down between Pole 2510935 & 2510937. Pole 2510936 was split in half with the cross arm on the ground beside the pole. Lighting strike on pole. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | mfa22 | Lightning strike on HV wood pole. | Grassfire | 18/03/2018 10:30 | 1 | Medium: 1000 sq.m - 10 ha | 9514 | Agricultural |  | 20180319SPN_03 | Infrastructure (network-based) | -37.8391 | 146.6391 | 1 | AusNet Services Distribution | Report | 11587 | 0.035781 | 22kV AC | Morwell (Latrobe Valley Airport) | 3858 | Glenmaggie | Lightning
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for necessary repairs. A grass fire of approximate size 800 metres x 800 metres. HV Line isolated at pole 140224 due to fire. Line repaired and supply restored. | 437 LARRITTS LANE, GLENBURN VIC 3717 | 1401222 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 232883. Initial report: CEOT received call for broken conductors and a grass fire in vicinity. Final report from attending DAO: Received a call as DAO regarding a fire out in Larritts lane Glenburn. The cause of the fire was a large tree branch that had come down between Pole#1401222 and Pole#1401223. The tree branch had caused the overhead high voltage line to snap in half and make contact with the ground. The fault current from when the overhead line hit the ground caused sparks to arise and a fire to start. Due to the extremely dry terrain and lake of recent rain fall the fire started quite easily. The fire spread over a large distance, firstly engulfing a nearby creek. The fire then proceed to jump over the Larrits Lane and spread near Pole#1401221. The high winds carried the fire in north easterly direction and caused severe damage to the customerâ€™s property. No damage to any of the customerâ€™s buildings or sheds occurred. In total 3 separate paddocks were damaged by a fire. The CFA had controlled and put the fire out by the time I had arrived. The fault current caused the ACR at the SWER isolating transformer to trip. This occurred on Pole#14-1156. CFA was on site at arrival. No damage occurred to any of our existing assets as the tree broke the line mid-span. ACR tripped and HV fuse operated. | Conductor (bare) | 0 | 0 | 0 |  | klk1 | Vegetation: Trees Incident | Grassfire | 18/03/2018 11:01 | 1 | Large: more than 10 ha | 9522 | Agricultural |  | 20180319SPN_06 | Infrastructure (network-based) | -37.379 | 145.4362 | 1 | AusNet Services Distribution | Report | 11599 | 0.00015625 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3717 | Glenburn | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 125 COCHRANES ROAD, MOORABBIN VIC 3189 | 1815975 |  | Precipitation |  | Electrical breakdown |  |  | 2 | At 1058hrs on 18/03/2018, the MFB advised of a pole on fire in Cochranes Road on the corner of Warrigal Road. Following light rain after a lengthy dry spell, a HV strain cross arm fire occurred at the HV/LV tee-off pole (LIS 1815975) located on the corner of Cochranes and Warrigal Roads. The blue phase HV insulator on the top of the strain cross arm was tracking to the cross arm. | Crossarm (wood) | 0 | 0 | 0 |  | HT 03 | Light rain following a long dry spell. | Pole-top fire | 18/03/2018 10:58 | 1 | Negligible: no ground fire | 9528 | Roadway |  | 20180319UTD_04 | Infrastructure (network-based) | -37.9441 | 145.0777 | 1 | United Energy Distribution | Report | 13041 | 0.023316 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Crossarm
Upon isolation crew carried out repairs and made site safe. | 105-121 DOHERTYS ROAD, LAVERTON NORTH VIC 3026 | 32176040 |  |  |  | Leakage |  |  |  | Powercor/Citipower Controller reported there is a fire burning at the top of the pole Pole 95 LIS-30506 (BLTS-SCI & BLTS-LVN DBL CCT 66kV) & (LVN032 22KV feeder). There was no reported HVI, injury, shocks or ground fire as a result of this incident. | Pole (wood) | 2 | 2 | 2 |  | LVN032 | Excessive leakage current | Pole-top fire | 18/03/2018 11:36 | 1 | Negligible: no ground fire | 9531 | Roadway |  | 20180320PWA_01 | Infrastructure (network-based) | -37.8285 | 144.7892 | 1 | Powercor | Report | 11611 | 0.028628 | 22kV AC;66kV AC | Laverton Raaf | 3026 | Laverton North | Pole
On arrival the crew made site safe and carried out repairs. | 100 BOOROOK ROAD, COORIEMUNGLE VIC 3268 | 30149644 |  | Wind;Fallen |  |  |  |  | 2 | A customer reported a Cyprus tree fell on to powerlines at the incident location. Upon arrival, the Powercor crew found a large tree fell on to the HV line, conductor had been damaged and approx. 2Sqm grass burnt . There were no injuries. | Conductor (bare) | 0 | 0 | 0 |  | COB011 | Wind storm | Grassfire | 17/03/2018 21:38 | 1 | Localised: less than 10 sq.m | 9533 | Agricultural |  | 20180320PWA_03 | Infrastructure (network-based) | -38.5471 | 143.0919 | 1 | Powercor | Report | 15132 | 0.013142 | 22kV AC | Warrnambool Airport Ndb | 3268 | Cooriemungle | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 54 ELLIOTT ROAD, DANDENONG SOUTH VIC 3175 | 211919 |  | Precipitation;Wind;Industrial or urban pollution |  |  |  |  | 0 | At 1306hrs on 18/03/2018, 22kV feeder circuit breaker DSH 14 failed to operate for a fault and the No. 1 22kV bus tripped at DSH zone substation as a result. The cause of the incorrect protection operation will be investigated by United Energy engineers. During very windy conditions following light rain after a lengthy dry spell, a pole fire occurred at pole number LIS 0635717 located in Elliott Street, 2 poles east of Hammond Road. The pole fire originated at the king bolt that attached the HV tee-off cross arm. The pole broke at this point leaving the top part of the pole with 66kV and 22kV conductors holding it up. | Pole (wood) | 0 | 0 | 0 |  | DSH 14 and TRANS No. 1 CB at DSH | Pole fire following light rain. | Pole-top fire | 18/03/2018 13:06 | 1 | Negligible: no ground fire | 9539 | Industrial |  | 20180320UTD_04 | Infrastructure (network-based) | -38.0228 | 145.205 | 1 | United Energy Distribution | Report | 13044 | 0.023946 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 12 DROVERS LANE, SOMERVILLE VIC 3912 | 1109045 |  | Blown branch/vegetation |  |  |  |  | 1 | At 1417hrs on 18/03/2018, 22kV feeder circuit breaker HGS 33 went directly to lockout as the auto reclose was suppressed due to previous fault switching activities. During extreme wind conditions, a branch from a privately owned tree has come down over the HV SWER 3/12 steel overhead conductors near pole No. LIS 1109045 that caused two HV fuses to operate at RB0573. As a result, one HV conductor was felled to the ground that caused a grass fire to start in road side bracken that was quickly extinguished. | Conductor (bare) | 0 | 0 | 0 |  | HGS 33 | Vegetation: Trees Incident | Grassfire | 18/03/2018 14:17 | 1 | Localised: less than 10 sq.m | 9543 | Roadway |  | 20180321UTD_02 | Infrastructure (network-based) | -38.2275 | 145.1914 | 1 | United Energy Distribution | Report | 13046 | 0.0013947 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Trees
Crew attended, removed tree and restored supply | 2450 COBDEN-WARRNAMBOOL ROAD, LAANG VIC 3265 | 32056486 |  | Wind;Fallen |  |  |  |  | 1 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Laang Area (Warrnambool â€“ Cobden Road) area. The information from fire investigators is that this fire originated where a large tree may have contacted a high voltage line. A Powercor crew attended removed the tree and undertook repairs.. This fire is known as the Warrnambool- Cobden fire. | Conductor (bare) | 0 | 0 | 0 |  | TRG005 | Line contacted by Vegetation | Grassfire | 17/03/2018 21:16 | 1 | Large: more than 10 ha | 9564 | Agricultural |  | 20180322PWA_07 | Infrastructure (network-based) | -38.3874 | 142.8434 | 1 | Powercor | Report | 11853 | 0.041537 | 22kV AC | Warrnambool Airport Ndb | 3265 | Laang | Trees
Crew attended and at LIS 1032892 found ground fire approximately1 sq. metre in size. DAO notified. The existing grey twisted overhead service cable was replaced with a new XLPE type overhead service cable. | 28 ALBERT STREET, UPPER FERNTREE GULLY VIC 3156 | 1032892 |  | Bird |  |  |  | Phase to neutral | 2 | IMS 232937. Emergency Authorities called AusNet Services to report service on fire. It is suspected a 2x25mm ABC grey type overhead service cable was damaged by Cockatoos pecking and penetrating the outer cable insulation causing the service cable to short circuit and fail with fault current causing holt molten plastic and aluminium to fall to the ground scorching approximately 1 sq. metre of grass near the base of pole #1032892. | Service conductor | 0 | 0 | 0 |  | fgy33 | Service cable damaged by cockatoos chewing insulation causing a short circuit. | Grassfire | 21/03/2018 20:09 | 1 | Localised: less than 10 sq.m | 9556 | Residential |  | 20180322SPN_01 | Infrastructure (network-based) | -37.8997 | 145.3141 | 1 | AusNet Services Distribution | Report | 11652 | 0.0029086 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Upper Ferntree Gully | Animal
CEOT dispatched a fault crew to make safe, isolate, investigate and repair. The crew made the section safe and arranged for a construction crew to replace the pole substation and repair the HV conductors. Supply restored. | 2225 TRARALGON CREEK ROAD, KOORNALLA VIC 3844 | 2605374 |  | Wind;Fallen |  |  |  | Phase to phase | 1 | IMS 232942. Initial report: Reports of small fire near assets. HV conductor down. Final report from attending DAO: On attending the site, a new pole had been stood in place of where a pole had broken at the base. Crews had attended to replace pole, crossarm, transformer and HV conductors the previous night. Upon investigation a 30 metre tree has been uprooted and was on the ground under the conductors. There were burn marks on some branches and a small 1m x 1m burnt area with only burnt grass in the area. The tree would have stood approximately 20 metres from the HV line. Report from Vegetation section: Semi-mature Eucalyptus regnans, 20m H, DBH 400mm, has faulted at the root base due to extreme winds & fallen onto HV conductors, snapping the pole 1.5m from ground level. A small fire has started at the site. Signs of decay in sheared roots, below ground level. No signs of decay in upper limbs. | Conductor (bare) | 0 | 0 | 0 |  | tgn23 | Vegetation: Trees Incident | Grassfire | 21/03/2018 17:36 | 1 | Localised: less than 10 sq.m | 9559 | Residential |  | 20180322SPN_03 | Infrastructure (network-based) | -38.3797 | 146.5318 | 1 | AusNet Services Distribution | Report | 11658 | 0.014506 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Koornalla | Trees
The attending LEI conducted voltage tests between an independent earth and all exposed metallic water system parts within the unit and identified 10 volts under no load and 120V under load. Further voltage tests at the customer earth/neutral bar and FOLCB recorded the same results. An NST was conducted at the customers switchboard and the FOLCB with a fail high impedance fault identified. A neutral impedance test was conducted with a result of 1.26 ohms between the active and neutral conductors indicating a high impedance neutral. The LEI contacted Jemena. A Jemena crew replaced the overhead neutral screen service to the property. After the service was replaced, an NST was conducted at the FOLCB and customers switchboard with a pass result identified. Voltage tests between an independent earth and all exposed metallic water system parts identified a maximum voltage of <1 volt AC. The customer was left on supply. | 68 MITCHELL STREET, MAIDSTONE VIC 3012 |  |  |  |  | Neutral fault |  |  |  | Customer received electric shock from shower while touching the tap with her hand and simultaneously standing on the wet shower base. | Service conductor | 2 | 2 | 0 |  |  | Faulty overhead neutral screen service to the property. | Minor shock | 23/03/2018 17:50 |  |  | 9571 |  |  | 20180323JEM_01 | Infrastructure (network-based) | -37.7826 | 144.8821 | 1 | Jemena | Report | 11682 | 0.011008 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | OH Cable
On arrival crew made safe and carried out repairs | 4350 COBDEN-WARRNAMBOOL ROAD, ALLANSFORD VIC 3277 | 30134052 |  | Blown branch/vegetation |  |  |  |  | 1 | Multiple customers called to report no supply in the area. On arrival the crew found that a large tree branch had contacted the HV conductors at the incident location. The subsequent clashing of the 22kV conductors resulted in a grass fire of approx. 4000m2 of road reserve and private property. There was damage to fences pasture and a tree plantation. There were no injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBL002 | Wind storm | Grassfire | 18/03/2018 0:25 | 1 | Medium: 1000 sq.m - 10 ha | 9566 | Public space |  | 20180323PWA_02 | Infrastructure (network-based) | -38.3904 | 142.6409 | 1 | Powercor | Report | 11671 | 0.041144 | 22kV AC | Warrnambool Airport Ndb | 3277 | Allansford | Trees
CEOT dispatched a fault crew to make safe, isolate and carry out/arrange for necessary repairs. CEOT also advised the local DAO to investigate. The HV line was repaired and power restored. | 2470 SOUTH GIPPSLAND HIGHWAY, DEVON MEADOWS VIC 3977 | 517096 |  | Fallen |  |  |  | Phase to earth | 1 | IMS 232936. Initial report; Grass fire in area of AusNet Services' assets. A gum tree branch broke and fell into HV conductor causing the conductor to break and causing a grass fire. Final report from attending DAO: It is suspected 14 metre tall gum tree branch that appeared to have part termite infested damage where it broke approximately 2 metres up the main trunk of the gum tree, located approximately 18 metres north of pole #517096 and 7 metres away from an outer phase 22kV, 1-3/12 steel overhead conductor to fall on to the conductor in strong winds causing the conductor to break. The resultant fault current caused an approximate 35m x15m grass fire approximately 10 metres west of pole #517095 and a protection sectionaliser trip on Switch BW1508. The weight of the tree branch also caused conductor ties to fail on cross arms on poles #517095 & #517287. Report from Vegetation section: Large Eucalyptus has had a significant limb failure at the branch union from internal decay; the large limb of 14m in length has come to rest under the 22kV HV conductors. The failed limb has evidence of burning on it and also evidence of burning on the tree trunk. Hazard tree report sent. The tree branch was outside the vegetation clearance space. The tree is classed as a private tree. | Conductor (bare) | 0 | 0 | 0 |  | cre33 | Vegetation: Trees Incident | Grassfire | 21/03/2018 12:42 | 1 | Small: 10 - 1000 sq.m | 9573 | Agricultural |  | 20180326SPN_01 | Infrastructure (network-based) | -38.1919 | 145.3491 | 1 | AusNet Services Distribution | Report | 11694 | 0.024877 | 22kV AC | Moorabbin Airport | 3977 | Devon Meadows | Trees
On arrival crew carried out repairs. | 831 YANAC-NETHERBY ROAD, YANAC VIC 3418 | 32113215 |  |  |  | Leakage |  |  | 1 | Customers reported a power outage and dim lights at the incident location. On arrival the Powercor fault crew found that the HV cross arm and pole top burnt through. Protection operated. There was no ground fire, no injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 26/03/2018 6:52 | 1 | Negligible: no ground fire | 9592 | Agricultural |  | 20180327PWA_04 | Infrastructure (network-based) | -36.113 | 141.5206 | 1 | Powercor | Report | 11730 | 0.0018056 | 22kV AC | Horsham Aerodrome | 3418 | Yanac | Crossarm
The faults crew attended and replaced 3 x 65amp Boric Acid HV fuses that had all operated. | DEIDRE STREET, DANDENONG NORTH VIC 3175 | 208557 | Working too close to overhead lines;Unauthorised work | Within clearances |  |  |  |  | 1 | At 1419hrs on 23/03/2018, 22kV spur fusing at DN7439 located in Simpson Drive operated interrupting supply to 261 customers. A private tree contractor with no signage on their vehicle, felled a gum tree branch over the three phase 22kV overhead conductors. No damage was sustained or injuries were received at the site on the corner of Deidre, Miller and Dobson Streets near pole number LIS 0627255. The tree cutters were very un-cooperative and ESV were advised of the breach. | Conductor (bare) | 0 | 0 | 0 |  | LD 04 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/03/2018 14:19 |  |  | 9597 | Roadway |  | 20180327UTD_04 | Infrastructure (network-based) | -37.9692 | 145.2223 | 1 | United Energy Distribution | Report | 11735 | 0.02245 | 22kV AC | Moorabbin Airport | 3175 | Dandenong North | Trees
On arrival crew isolated supply and carried out repairs. | 12 TARELLA DRIVE, KEILOR DOWNS VIC 3038 | 30111815 |  |  |  | Leakage |  |  |  | A Customer reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported. | Crossarm (wood) | 2 | 2 | 2 |  | SA006 | Excessive leakage current | Pole-top fire | 43103.3562 | 1 | Negligible: no ground fire | 9601 | Roadway |  | 20180328PWA_02 | Infrastructure (network-based) | -37.7261 | 144.8157 | 1 | Powercor | Report | 11739 | 0.033889 | 22kV AC | Melbourne Airport | 3038 | Keilor Downs | Crossarm
On arrival crew isolated supply and carried out repairs. | 823 MADEIRA PACKET ROAD, PORTLAND VIC 3305 | 32135488 |  |  |  | Leakage |  |  |  | An employee reported a pole fire had occurred at the incident location. The attending crew found that Pole 13 (LIS-905457) had caught fire at the HV tee off insulator position. There were no reported shocks or injuries. No evidence of ground fire. | Pole (wood) | 2 | 2 | 2 |  | PLD006 | Excessive leakage current | Pole-top fire | 43407.7604 | 1 | Negligible: no ground fire | 9603 |  |  | 20180328PWA_04 | Infrastructure (network-based) | -38.3642 | 141.6253 | 1 | Powercor | Report | 11741 | 0.029635 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Pole
Works on the new buildings roof have been stopped and mechanical protection has been applied to the service supply effected Jemena Works Practices emailed the responsible third party (a copy of which is attached in "Notes and Findings" section) who were on site | 60 RUBY STREET, PRESTON VIC 3072 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | New housing development has breached No Go Zone by erecting roof scaffold close to the next door property's overhead electrical service supply. Details of the builder have been included in "Other information sources" section Photo is attached in the "Notes and Findings" section. For more information, please contact Nick Mateski of Jemena Works Practices on 0417339536 | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | EPN35 | Builder on site has missed the scaffold process that will affect the Safe Approach Distances and did not apply for No Go Zone permit | No Go Zone (no contact) | 27/03/2018 10:43 |  |  | 9613 | Residential |  | 20180329JEM_01 | Infrastructure (network-based) | -37.7424 | 145.0167 | 1 | Jemena | Report | 11800 | 0.0040799 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
On arrival crew isolated supply and carried out repairs | 19 HANNON STREET, SEA LAKE VIC 3533 | 32157793 |  |  |  | Leakage |  |  |  | Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden angle-strain cross-arm failed due to fire damage but conductors remained suspended by cross-arm braces. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 25/03/2018 23:37 | 1 | Negligible: no ground fire | 9617 | Agricultural |  | 20180329PWA_07 | Infrastructure (network-based) | -35.5043 | 142.8404 | 1 | Powercor | Report | 11759 | 0.028314 | 22kV AC | Swan Hill Aerodrome | 3533 | Sea Lake | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 18 GRANDVIEW ROAD, CHADSTONE VIC 3148 |  |  | Blown branch/vegetation |  | HV injection |  |  | 0 | AMI meters communicated a loss of a neutral and customers supplied from "Grandview-Huntingdale" substation are experiencing 340v and above. During strong winds, a branch from a council tree fell over the LV reticulation and broke the neutral conductor at the corner of Grandview Road and Maude Street. Subsequently, the neutral conductor contacted the LV red phase conductor and a LV injection was suspected to customers supplied from "Grandview-Huntingdale" substation. A LEI confirmed a low voltage injection occurred (KEY 1802) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. The Optus communication cable was also damaged and they were contacted and requested to also attend the site. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | HV injection | 26/03/2018 12:48 |  |  | 9609 | Roadway |  | 20180329UTD_01 | Infrastructure (network-based) | -37.875 | 145.1074 | 1 | United Energy Distribution | Report | 11747 | 0.016764 | Low voltage AC (<1kV) | Moorabbin Airport | 3148 | Chadstone | Trees
Area isolated and repairs conducted | 1 ELSTONE COURT, NIDDRIE VIC 3042 | Pole no. A056862 |  | Animal |  |  |  |  | 1 | Possum across HV fuse units at Elstone-Keilor pole mounted substation causing HV conductor (centre phase) to come to ground Protection systems operated correctly to isolate the fault and Jemena network operator confirmed that HV conductor was dead when it fell to ground Photos have been attached in "Notes and Findings" section | Conductor (bare);Boric acid;Pole mounted | 0 | 0 | 0 |  | AW06 | Animal Incident | Loss of supply | 43163.8264 |  |  | 9632 | Residential |  | 20180403JEM_01 | Infrastructure (network-based) | -37.7348 | 144.8878 | 1 | Jemena | Report | 11788 | 0.014174 | 22kV AC | Essendon Airport | 3042 | Niddrie | Animal
On arrival crew isolated supply and made site safe. Repairs arranged | 316 QUEEN STREET, MELBOURNE VIC 3000 | 33111763 | Copper theft | [6 empty] | While investigating an outage, CP faults noticed unauthorised people in a distribution substation at 316 Queen St Melbourne. The substation is located in an empty building. The crew called the Police and the Police arrested all three people in the substation trying to steal copper. There was also oil on the ground from the damaged LV OCB however the oil was contained within the substation. One of the arrested individual had received an electrical shock to his hand from the LV bus. There was no fire or third party property damage. | Indoor | 2 | 1 | 0 |  | JA033 | Copper theft attempt | Minor shock;Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43104.9465 |  |  | 9620 | Commercial |  | 20180403PWA_01 | Infrastructure (network-based) | -37.8113 | 144.9594 | 1 | CitiPower | Report | 11775 | 0.014775 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3000 | Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 867 SUNSET ROAD, COWANGIE VIC 3506 | 32145320 |  |  |  | Leakage |  |  | 1 | Following customer calls, a patrol found pole fire at incident location (Tyalla P43) There was no ground fire or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 26/03/2018 0:57 | 1 | Negligible: no ground fire | 9627 |  |  | 20180403PWA_08 | Infrastructure (network-based) | -35.1496 | 141.42 | 1 | Powercor | Report | 11782 | 0.034888 | 22kV AC | Mildura Airport | 3506 | Cowangie | Pole
0n arrival crew isolated supply and carried out repairs | 535 OCONNORS ROAD, WERRIBEE SOUTH VIC 3030 | 30110190 |  |  |  | Leakage |  |  |  | Report of a pole fire at the incident location. On arrival the field crew has advised that there was a burnt out HV Inter X-arm. There was no reported Ground fire, HVI, injury, shock or third party damage as a result of this incident. | Crossarm (wood) | 2 | 2 | 2 |  | WBE034 | Excessive leakage current | Pole-top fire | 26/03/2018 15:59 | 1 | Negligible: no ground fire | 9629 | Roadway |  | 20180403PWA_10 | Infrastructure (network-based) | -37.9633 | 144.6954 | 1 | Powercor | Report | 11784 | 0.016669 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Crossarm
Ownership of assets at this site clarified with REC developer and council. | HAWKE AND ADDERLEY STREET PARK, 92-108 HAWKE STREET, WEST MELBOURNE VIC 3003 | 30182386 | Unauthorised work | [5 empty] | 2 | REC working for developer abolished supply to 2 Citipower street lights in parkland. | Public lighting;Pole (steel) | 0 | 0 | 0 |  | VM026 | Interference - mistakenly thought this lighting was under council ownership | No Go Zone (no contact) | 29/11/2017 9:43 |  |  | 9633 | Public space |  | 20180404PWA_01 | Infrastructure (network-based) | -37.8086 | 144.945 | 1 | CitiPower | Report | 11789 | 0.0069595 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 10024 NATIMUK-HAMILTON ROAD, CAVENDISH VIC 3314 | 32125402 |  |  |  | Leakage |  |  | 1 | Vicfire reported a pole fire at the incident location. On arrival the crew found that a Strain cross-arm had burnt off at one end, allowing the conductor and insulators to fall onto a service cable below. There was no ground fire, and further tests showed that there was no apparent HVI. There was no reported third party damage or any injuries. | Crossarm (wood) | 2 | 2 | 2 |  | HTN004 | Excessive leakage current | Pole-top fire | 18/03/2018 7:51 | 1 | Negligible: no ground fire | 9638 | Roadway |  | 20180405PWA_03 | Infrastructure (network-based) | -37.5206 | 142.0404 | 1 | Powercor | Report | 11796 | 0.010889 | 22kV AC | Hamilton Airport | 3314 | Cavendish | Crossarm
On arrival crew isolated supply and carried out repairs | 931 TOWER HILL ROAD, ILLOWA VIC 3282 | 32195786 |  |  |  | Leakage |  |  |  | Vicfire reported a pole smoking at the incident location. On arrival the crew found the pole had burnt around the bolts of an LA bracket, There were no reported injuries, ground fire or third party damage. | Pole (wood) | 2 | 2 | 2 |  | KRT013 | Excessive leakage current | Pole-top fire | 30/03/2018 11:33 | 1 | Negligible: no ground fire | 9642 | Roadway |  | 20180406PWA_02 | Infrastructure (network-based) | -38.3154 | 142.4054 | 1 | Powercor | Report | 11804 | 0.032419 | 22kV AC | Warrnambool Airport Ndb | 3282 | Illowa | Pole
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for repairs. On arrival the crew observed 1 phase (1 bay of single phase HV conductor) down between poles Lis No 2617732 and 2617733 of Chishill spur. On further inspection found at Termination Substation Pole, lis no 2617733, Chishill spur, found that the Boric Acid fuse unit on the phase down had come away from the bracket plus the bushing and the LA were broken off the transformer. There was no-one at the site (suspect the line was possibly struck by the farmer's machinery). The crew were unable to contact the farmer. The crew then arranged on call crew and additional construction resources to carry out repairs. Crew to repair arrived on site - contacted CEOT issued EAP. Measured the one phase of the single phase conductor that was still in the air between Lis No's 2617732 and 261773 and it was at 4.6 metres above the ground which is traversable by vehicle. The crew replaced the transformer and the Boric Acid fuse unit, re strung and sagged the conductor (3/12 steel), re-measured the height between Lis No's 2617732 and 261773 to record above ground at 6.5 metres. | 1125 HAZELWOOD ROAD, HAZELWOOD NORTH VIC 3840 | 2617733 | Working too close to overhead lines |  |  |  |  | Phase to earth |  | IMS 233152. AT LIS 2617733 HV OVERHEAD HAS BEEN BROUGHT DOWN. OPERATOR SUSPECTS CONTACT WITH FARMING EQUIPMENT WAS CAUSE | Conductor (bare) | 0 | 0 | 0 |  | tgn23 | Farm machine contacted overhead HV line. | No Go Zone (contact) | 43255.5417 |  |  | 9645 | Agricultural |  | 20180406SPN_03 | Infrastructure (network-based) | -38.2834 | 146.4595 | 1 | AusNet Services Distribution | Report | 11811 | 0.028984 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | Vehicle
Voltage tests were conducted between an independent earth and various points of the electrical installation, including the distribution assets, revealed a defective neutral conductor at the service pole. 38V was measured on the water piping system. Upon visual inspection of the service pole connections, the neutral conductor could be seen completely disconnected from the pole mounted FOLCB. The attending service crew replaced the Multi phase Aluminium service cable. And re-terminated and tested all connections. The installation was tested by the attending L.E.I and zero volts were recorded on the installation neutral bar at the main switchboard and the water piping system, and between the points where the victim received the shock. An NST test carried out by the LEI Result - passed Installation left on supply. | 39 WARANGA CRESCENT, BROADMEADOWS VIC 3047 |  |  |  |  | Neutral fault |  |  | 2 | Customer received electric shock when she was standing bare foot on the wet concrete and turning on the rear external (outdoor) tap when she made simultaneous contact between the tap and the wet ground. | Neutral screen | 0 | 0 | 0 |  |  | Neutral conductor disconnected from the pole mounted FOLCB. | Minor shock | 43285.5868 |  |  | 9646 | Residential |  | 20180407JEM_01 | Infrastructure (customer connection) | -37.6817 | 144.9312 | 1 | Jemena | Report | 11813 | 0.02494 | Extra low voltage AC (<50V) | Essendon Airport | 3047 | Broadmeadows | Connection
Crew attended and found evidence of flash over, replacement of cable terminations initiated. | 16 L GRAYLANDS ROAD, COBDEN VIC 3266 | 30149427 |  | Animal |  |  |  |  | 1 | Vicfire reported â€œgrass fire, powerline and pole sparking may be the possible cause.â€ On arrival the crew found a grass fire near the base of the cable head pole which burnt an area of around 20m by 3 m. The crew identified some evidence of flashover on the cable terminations. There were no reported injuries. | Cable | 0 | 0 | 0 |  | COB012 | Animal Incident | Grassfire | 43285.9882 | 1 | Small: 10 - 1000 sq.m | 9651 | Roadway |  | 20180409PWA_05 | Infrastructure (network-based) | -38.3354 | 143.0559 | 1 | Powercor | Report | 11822 | 0.01683 | 22kV AC | Warrnambool Airport Ndb | 3266 | Cobden | Animal
On arrival crew isolated supply and commenced repairs | 61 CASTRO WAY, DERRIMUT VIC 3030 | 30244805 |  | Bird |  | Overheated connection |  |  | 1 | Report received of a loud bang and loss of supply. Bird contact at cable head pole caused primary fault Secondary faults occurred during re-energisation and resulted in separate ground and kiosk substation fires. This report relates to ground fire only | Disconnector/isolator;Dropper/bridge | 2 | 1 | 2 |  | SU013 | Bird Incident | Grassfire;Plant/equipment | 43316.7049 | 1 | Localised: less than 10 sq.m | 9656 | Roadway |  | 20180410PWA_02 | Infrastructure (network-based) | -37.7917 | 144.7788 | 1 | Powercor | Report | 12465 | 0.00090394 | 22kV AC | Laverton Raaf | 3030 | Derrimut | Animal
The site has been secured by a security company that is hired by the contractor. This incident was reported to the Police and also to the security company by the contractor. The repairing works have been arranged by the CitiPower fault crew. | 141-147 CAPEL STREET, NORTH MELBOURNE VIC 3051 | 30181192 | Copper theft | [6 empty] | A contractor (Lendlease) reported a copper theft at the incident location. Upon arrival, the Citipower fault crew found that the 63mm earthing cables about 50m on the 66kV UG joint/cable maintenance site had been cut away. The cables run along 66kV lines. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | VMTS-VM1 | cable theft | Damage to network assets | 43223.4194 |  |  | 9671 | Public space |  | 20180412PWA_02 | Infrastructure (network-based) | -37.804 | 144.9554 | 1 | CitiPower | Report | 11847 | 0.017657 | Earthing cable | Essendon Airport | 3051 | North Melbourne | Other
Crew arrived on site & isolated supply and repaired conductors. | 24 JANSON STREET, MAIDSTONE VIC 3012 |  |  | Council |  | Conductor clashing |  |  | 2 | Council trees not cut to code caused low voltage conductor clashing resulting in conductors on the ground. | Conductor (bare) | 2 | 2 | 2 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/04/2018 12:42 |  |  | 9685 | Residential |  | 20180414JEM_02 | Infrastructure (network-based) | -37.7847 | 144.8686 | 1 | Jemena | Report | 11867 | 0.027953 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | Trees
On arrival crew isolated supply and carried out repairs. | 3584 OLD MAIL ROAD, CULLULLERAINE VIC 3496 | 32147375 |  |  |  | Leakage |  |  | 1 | SCADA alarm for Lake Cullulleraine P264 ACR lockout initiated a fault crew investigating the outage cause, subsequently a customer with specific location details called reporting a pole fire at the incident location. On arrival the crew found that a wooden termination cross-arm failed due to fire damage at a EDO fuse unit mounting location, resulting in the conductor falling onto the ground below. There was no ground fire, no reported injuries, no 3rd party damage. | Crossarm (wood) | 2 | 2 | 2 |  | MBN031 | Excessive leakage current | Pole-top fire | 14/04/2018 16:40 | 1 | Negligible: no ground fire | 9697 | Agricultural |  | 20180416PWA_06 | Infrastructure (network-based) | -34.1898 | 141.6219 | 1 | Powercor | Report | 11880 | 0.027929 | 22kV AC | Mildura Airport | 3584 | Cullulleraine | Fuse
On arrival crew found damage to an LV underground cable, re[pairs arranged. | 1243 CALDER HIGHWAY, DRUMMOND NORTH VIC 3446 | 30033573 |  | Animal | [5 empty] | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a single phase substation structure, the exact location of the flashover has not been confirmed, causing the possum to fall to the ground and ignite a small grass fire, approximately 10M x 20M square was burnt. CFA extinguished the fire, and doused the pole also at its base. There were no reported injuries, no 3rd party damage, | Pole mounted | 2 | 2 | 2 |  | CMN001 | Animal Incident | Grassfire | 43438.8528 | 1 | Small: 10 - 1000 sq.m | 9699 | Roadway |  | 20180416PWA_08 | Infrastructure (network-based) | -37.1801 | 144.3618 | 1 | Powercor | Report | 11882 | 0.010045 | 22kV AC | Bendigo Airport | 3446 | Drummond North | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for any necessary repairs. CEOT also advised the DAO. IMS done. | MEKKENVILLE, 4301 PRINCES HIGHWAY, WAYGARA VIC 3888 | 1905903 |  | Blown branch/vegetation |  |  |  | Phase to phase | 1 | IMS 233218. Branch found at pole 19005903. Burnt, no damage. 8mx8m fire. Fire out when crew arrived. Feeder trip. Grass fire 8m x 8m. below ausnet asset. | Conductor (bare) | 0 | 0 | 0 |  | NLA34 | Vegetation: Trees Incident | Grassfire | 14/04/2018 17:00 | 1 | Small: 10 - 1000 sq.m | 9689 | Agricultural |  | 20180416SPN_01 | Infrastructure (network-based) | -37.7535 | 148.3242 | 1 | AusNet Services Distribution | Report | 11872 | 0.032119 | 22kV AC | Bairnsdale Airport | 3888 | Waygara | Trees
On arrival crew isolated supply and carried out repairs. | 585B TOL TOL ROAD, TOL TOL VIC 3549 | 30097375 |  |  |  | Leakage |  |  |  | Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the cross-arm strap, conductor remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | RVL008 | Excessive leakage current | Pole-top fire | 14/04/2018 16:40 | 1 | Negligible: no ground fire | 9702 | Agricultural |  | 20180417PWA_01 | Infrastructure (network-based) | -34.6463 | 142.8534 | 1 | Powercor | Report | 11885 | 0.004765 | 22kV AC | Mildura Airport | 3549 | Tol Tol | Crossarm
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a loose/corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Service Pole. The attending Powercor Fault Crew tightened the O/H Service Neutral Conductor terminations at the Reticulation Service Pole Type Connection Box and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 181 GREAT OCEAN ROAD, APOLLO BAY VIC 3233 | 30052121 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Francis O'Brien and her extended family have been receiving electric shocks from the laundry faucet for an extended period of time as they made simultaneous contact with their hands on the metal faucet whilst standing on the conductive floor. | Connection box | 2 | 2 | 2 |  | CLC007 | Corroded connection | Minor shock | 43103.4375 |  |  | 9704 | Residential |  | 20180417PWA_03 | Infrastructure (network-based) | -38.752 | 143.6693 | 1 | Powercor | Report | 11887 | 0.020186 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Connection
CEOT dispatched a fault crew to make safe, investigate and repair. Crew restored supply after risk assessment. Transformer was tested - no Volts. Crew isolated the substation to change the faulted transformer. | 950 GLEN ALVIE ROAD, GLEN ALVIE VIC 3979 | 2008155 |  |  |  | Candled fuse |  |  | 1 | IMS 232874. Initial report of two Candled fuse units on a single phase substation. No ground fire. The attending fault crew advised CEOT that only one EDO fuse hung-up and candled and the other HV fuse operated as designed. A faulty substation transformer was the cause of the incident. NO PHOTOS WERE TAKEN. | EDO fuse | 0 | 0 | 0 |  | lga23 | Faulty substation transformer resulted in EDO fuse operation with one EDO fuse hung-up and candled. | Other electricity related | 17/03/2018 13:40 | 1 | Negligible: no ground fire | 9705 | Agricultural |  | 20180417SPN_01 | Infrastructure (network-based) | -38.4618 | 145.6439 | 1 | AusNet Services Distribution | Report | 13540 | 0.020758 | 22kV AC | Moorabbin Airport | 3979 | Glen Alvie | Fuse
CTA/LEI performed NST at installation main switchboard with a fail result recorded. Fault Crew discovered the loose connection of the 2 wire ABC service neutral conductor to the reticulation neutral conductor pole end. Crew re-terminated the neutral conductor and performed NST at the POA with a pass result recorded. CTA/LEI performed NST at the installation main switchboard with a pass result recorded. Installation left ON supply. | 5 RICHARD AVENUE, OCEAN GROVE VIC 3226 | 32088973 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Leonie was standing at the back yard tap, when she felt a slight shock to her right hand adjusting the tap, with her left wet hand in the water flow from the hose and standing on wet pavers. | Service conductor | 2 | 2 | 2 |  | DDL011 | Loose connection | Minor shock | 43407.625 |  |  | 9709 | Residential |  | 20180418PWA_01 | Infrastructure (network-based) | -38.2556 | 144.5049 | 1 | Powercor | Report | 11892 | 0.01458 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole The attending Powercor Fault Crew replaced the existing N/S O/H Service Cable from the Pole Top Connection Box to the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 12 BUFFALO AVENUE, CORIO VIC 3214 | 32084678 |  |  |  | Corrosion |  | Phase to earth |  | Ms Tanya Barraclougci was in the rear yard watering her 3m Crocodile at the External Garden Tap when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the wet ground. | Service conductor | 2 | 2 | 2 |  | FNS021 | Corroded connection | Minor shock | 43254.4792 |  |  | 9711 | Residential |  | 20180418PWA_03 | Infrastructure (network-based) | -38.0736 | 144.3683 | 1 | Powercor | Report | 11895 | 0.033291 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
On arrival crew isolated supply Both premises were defected, with the premises at 312 Albion St requiring a raiser bracket. Supply restored after completion of repairs. | 312 ALBION STREET, BRUNSWICK VIC 3056 | 30160193 | Vehicle | [6 empty] | A CitiPower crew were called to a report of multiple cables down at the incident location. On arrival the crew found that a truck (Rego- FATARG) had struck several comms cables, and two service cables. There was no reported fire, other third party damage or any injuries. | Service conductor | 2 | 2 | 2 |  | WB002 | Vehicle struck services | Loss of supply;Damage to network assets | 27/03/2018 12:56 |  |  | 9717 | Commercial |  | 20180418PWA_08 | Infrastructure (network-based) | -37.7598 | 144.954 | 1 | CitiPower | Report | 12050 | 0.0080914 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Vehicle
On arrival crew isolated supply and carried out repairs | 5125 DIMBOOLA-RAINBOW ROAD, RAINBOW VIC 3424 | 32121639 |  |  |  | Leakage |  |  | 1 | Following a feeder outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | NHL015 | Excessive leakage current | Pole-top fire | 18/04/2018 8:13 | 1 | Negligible: no ground fire | 9720 |  |  | 20180419PWA_01 | Infrastructure (network-based) | -36.0331 | 142.0367 | 1 | Powercor | Report | 11908 | 0.036663 | 22kV AC | Horsham Aerodrome | 3424 | Rainbow | Crossarm
CEOT dispatched a fault crew to isolate supply, make safe, investigate and carry out necessary repairs. Line was isolated and the pole was replaced by a work crew. Supply subsequently restored. | 465 SILCOCKS HILL ROAD, TOORA NORTH VIC 3962 | 2014437 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | IMS 231603. SACR FT122 tripped to lock out. Work crew dispatched to investigate and found top of SWER pole burnt off @ LIS 2014437. There was no visible signs that the intermediate insulator or the glass disc had failed. But the stay wire had been cut for some time and we suspect this has touched the SWER line and caused the fire to start. As there was rain in the area previously, the stay could have been resting against the pole and the SWER line causing the fire. The pole stay may have been cut by the farmer's slasher when cutting grass or it could have broken due to rust. There were no outstanding work orders in SAP. | Pole (wood) | 0 | 0 | 0 |  | ftr12 | Broken pole stay wire. | Pole-top fire | 42959.3812 | 1 | Negligible: no ground fire | 9043 | Agricultural |  | 20180117SPN_02 | Infrastructure (network-based) | -38.6341 | 146.3554 | 1 | AusNet Services Distribution | Report | 10935 | 0.027164 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3962 | Toora North | Pole
Electrical inspector onsite, tested, found neutral sound. Jemena field crew Arranged to replace the 2-wire neutral screen service All tests carried out - PASS result obtained - supply left on. | 604 MURRAY ROAD, PRESTON VIC 3072 |  |  |  |  | Age |  | Phase to earth | 2 | A tradesman received an electric shock during the course of painting the facia around the equipment associated with the overhead point of attachment For further details, refer to TechSafe report attached in "Notes & Findings" section | Service conductor;Neutral screen | 2 | 2 | 2 |  | CN08 | No fault found by electrical inspector. However, the most likely causal factor was the old service cable which was subsequently replaced. | Minor shock | 17/01/2018 14:58 |  |  | 9049 | Residential |  | 20180118JEM_01 | Infrastructure (network-based) | -37.736 | 144.9874 | 1 | Jemena | Report | 11518 | 0.020361 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | OH Cable
A LEI and faults truck attended after confirming with the REC that access is available to complete installation tests. The faults crew cleaned, greased and re-terminated the neutral connection for the underground cable at pole end but the fault remained. They were unable to locate the pit at the property boundary and a cable tester was dispatched to find the pit. The pit was located and the consumers mains were meggered and found to be okay. When the cable was reconnected at the pit, tests confirmed the voltage remained on the neutral. The faults crew proceeded to check connections at the intermediate pole south of "Central-Melbourne" pole type substation and all connections were tightened but 7v was measured on the neutral at this pole to an independent earth. They continued to check and tighten al connections at the substation pole and replaced the ampact connection on the neutral conductor. The LEI re-tested at the installation and 4v was measured on the neutral under load and a NST passed. Supply was left on after the LEI measured 0.1ohm neutral impedance between the substation and the meter. Refer also to Incident Report 20180112UTD_02 where a similar electric shock was received on 10/01/2018 at 35 Central Avenue. Further investigation is required and was referred to Voltek to determine why volts remained on the neutral conductor. 17/01/2018 - Voltek representatives commenced an investigation to determine the cause of customers (14 and 35 Central Avenue, Blairgowrie) supplied from the 315kVA transformer at "Central-Melbourne" pole type substation receiving slight electric shocks. Voltek identified the fault at the copper to aluminium ampact connection at the neutral bridge north of the pole type substation near the corner of Central Avenue and Melbourne Road where the connections were corroded due to the salt air borne contaminates. They completed temporary repairs with permanent repairs to be completed by a construction crew. Voltek also re-attended 14 and 35 Central Avenue with zero volts measured on the neutral at both locations. | 14 CENTRAL AVENUE, BLAIRGOWRIE VIC 3942 |  |  | Prone to salt deposition |  | Corrosion |  | Phase to earth | 2 | REC has advised the customer has been getting tingles off the outside and inside taps at the holiday house. The occupier received an electric shock to her hand from the water taps as she stood bare footed on the wet ground and contacted a REC to investigate the cause. | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  |  | The fault was identified at the neutral copper to aluminium ampact connection where the connection was corroded as a result of the salt air borne contaminates due to the poles location near Bass Straight and Port Phillip Bay. | Minor shock | 15/01/2018 10:00 |  |  | 9047 | Residential |  | 20180118UTD_01 | Infrastructure (network-based) | -38.3641 | 144.7612 | 1 | United Energy Distribution | Report | 10940 | 0.0013345 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Connection
The LV connection was repaired at pole number LIS 19054 and supply restored to customers in the vicinity. | 74 CHANDLER ROAD, NOBLE PARK VIC 3174 | 619054 |  | Heat |  | Electrical overload |  |  | 2 | Caller contacted United Energy with an all supply failure. A meter ping failed and a faults truck was dispatched to investigate the reason for the outage. During hot weather conditions, the red phase LV connection to the transformer isolator at "Leman-Chandler" pole type substation failed due to probable overload. Molten metal fall onto the nature strip and a small 1sqm started that was promptly extinguished. | Connector/termination | 0 | 0 | 0 |  | NP 36 | Probable overload during warm weather. | Grassfire | 18/01/2018 17:35 | 1 | Localised: less than 10 sq.m | 9064 | Roadway |  | 20180122UTD_01 | Infrastructure (network-based) | -37.9694 | 145.1864 | 1 | United Energy Distribution | Report | 12978 | 0.0050359 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Connection
The LV connection was repaired at pole number LIS 1100188 and supply restored to customers in the vicinity. | 253 DUNNS ROAD, MORNINGTON VIC 3931 | 1100188 |  | Heat |  | Electrical breakdown |  |  | 2 | Caller contacted United Energy with an all supply failure. A meter ping failed and a faults truck was dispatched to investigate the reason for the outage. During hot weather conditions, the blue phase LV connection to the fused isolator at the south circuit of "Ikara-Dunns" pole type substation failed due to probable overload. Molten metal fall onto the nature strip and a small 4 x 2 sqm started that was promptly extinguished. | Connector/termination | 0 | 0 | 0 |  | MTN 31 | The cause was probable overload during warm weather. | Grassfire | 18/01/2018 18:24 | 1 | Localised: less than 10 sq.m | 9067 | Roadway |  | 20180122UTD_03 | Infrastructure (network-based) | -38.2417 | 145.0475 | 1 | United Energy Distribution | Report | 12980 | 0.04092 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Connection
On arrival the crew replaced the damaged isolator and restored supply | 901 SKIPTON STREET, REDAN VIC 3350 | 30012689 |  |  |  | Overheated connection |  |  |  | A Powercor crew attended a report of an All Supply Failure at the above location. On arrival the crew found that the white phase LV Isolator on the North Circuit of â€œSkipton-Cookeâ€ substation had failed and molten metal had fallen to the group starting a small fire (4 x 2 metres) which self-extinguished. There was no injury, shock or third party damage. | Disconnector/isolator | 2 | 2 | 2 |  | BAS034 | Loose connection | Grassfire | 21/01/2018 15:44 | 1 | Localised: less than 10 sq.m | 9073 | Roadway |  | 20180123PWA_01 | Infrastructure (network-based) | -37.5809 | 143.8415 | 1 | Powercor | Report | 10987 | 0.032171 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Redan | Fuse
On arrival crew isolated supply and carried out repairs | 2 HARPIN PLACE, EAST BENDIGO VIC 3550 | 33032935 |  |  |  | Overheated connection |  |  |  | Numerous Customers called reporting no supply. Crew attended to LV Fused Disconnecting Box on Substation Pole # 6 Lloyd Solomon in Lloyd Street Bendigo East. LV Fuse had overheated and melted the box and fell to the ground resulting is causing a small grass fire at base of the pole. No property damage, shock reports or injuries reported. | Connection box | 2 | 2 | 2 |  | BGO022 | connection failure | Grassfire | 20/01/2018 17:10 | 1 | Localised: less than 10 sq.m | 9075 | Roadway |  | 20180123PWA_02 | Infrastructure (network-based) | -36.7545 | 144.304 | 1 | Powercor | Report | 10988 | 0.019402 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | East Bendigo | Fuse
The site was made safe and the LV service was re-attached | 17 FRANCIS STREET, BELMONT VIC 3216 | 30318286 | Vehicle | [6 empty] | customer reported a moving van pulled the service off the hook at the incident address. On arrival the crew found that a Low Voltage (LV) service had been hit by a truck and pulled off the hook. There were no reported injuries or other third part damage. | Service conductor | 2 | 2 | 2 |  | GCY023 | Truck hit service | Damage to network assets | 31/10/2017 16:55 |  |  | 9077 | Residential |  | 20180123PWA_03 | Infrastructure (network-based) | -38.1734 | 144.3495 | 1 | Powercor | Report | 10996 | 0.0027627 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Vehicle
On arrival crew isolated supply and replaced pole | WILLOWBANK, 534 EDMONSTON ROAD, WEATHERBOARD VIC 3352 | 30004509 | Vehicle | [5 empty] | 1 | Vic Fire reported a car had hit a pole at 534 Edmonston rd Weatherboard, Ballarat at 18-00 on the 12/11/2017 On arrival the crew found that the pole LIS-3581 had snapped at the base with the car on site, registration number AMM-782, There was no fire reported | Pole (wood) | 2 | 2 | 2 |  | BAN006 | vehicle struck pole | Loss of supply;Damage to network assets | 43080.7847 |  |  | 9078 | Roadway |  | 20180123PWA_04 | Infrastructure (network-based) | -37.4209 | 143.6707 | 1 | Powercor | Report | 10997 | 0.014162 | 22kV AC | Ballarat Aerodrome | 3352 | Weatherboard | Vehicle
1. Work party made contact with TOC & Powercor control rooms. Investigate trip targets and agree to restore No.3 66kV Bus as it was not a genuine protection operation. 2. Contact made with Broadspectrum / AusNet Project Manager. 3. Decision made to restore the LV1 X Protection without the relay relocation. Work to take place at a later date. | 12-14 MARIA STREET, LAVERTON NORTH VIC 3026 | ATS No.3 66kV Bus |  |  |  |  | Poor or no communication |  | 1 | IMS232051. During the removal of wiring on existing LV1 66kV X Protection relay, the No.3 X bus protection tripped due to the secondary wiring inadvertently making contact. Loss of No3 66KV BUS @ ATS, testers working on LV1 protection relay, failed to Isolate prot cct's resulting in loss of BUS during testing, Loss of 7.2 MW to ALQ. Trip @ 07.48 Bus restored @ 07.54,ALQ restored @08.03 | Terminal substation | 0 | 0 | 0 |  | ATS | No.3 66kV Bus tripped as a result of trip signal initiation from existing LV 1 X Protection wiring. During the removal of wiring on existing LV1 66kV X Protection relay, the No.3 X bus protection tripped due to the secondary wiring inadvertently making contact. Investigation report attached | Loss of supply | 16/01/2018 7:48 |  |  | 9076 |  |  | 20180123SPN_02 | Infrastructure (network-based) | -37.8382 | 144.786 | 1 | AusNet Services Transmission | Report | 10990 | 0.016898 | 66kV AC | Laverton Raaf | 3026 | Laverton North | Other
The crew replaced the 27 meters stolen underground mains cable (35mm2 copper). | 202 MILLERS ROAD, ALTONA NORTH VIC 3025 | 30103670 | Copper theft | [6 empty] | A REC reported that Powercor consumer mains has been stolen between the pit and pole at the incident location. On arrival the fault crew found that consumer mains has been stolen between the pit and pole at the incident location. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | BLT021 | copper theft | Damage to network assets | 17/11/2017 11:20 |  |  | 9089 | Residential |  | 20180124PWA_06 | Infrastructure (network-based) | -37.8346 | 144.8473 | 1 | Powercor | Report | 11007 | 0.012088 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
On arrival crew arranged for repairs to be carried out | 2 BEAUREPAIRE DRIVE, LORNE VIC 3232 | 34026042 | Working too close to underground cables | [6 empty] | A customer reported he has dug up a cable at the incident location and it seems a HV cable. Upon arrival, the Powercor fault crew found that a minor damage done to the conduit but no damage has been done to the cable. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | CLC005 | Excavation near underground cable | No Go Zone (no contact);Damage to network assets | 15/11/2017 13:36 |  |  | 9090 | Roadway |  | 20180124PWA_07 | Infrastructure (network-based) | -38.5411 | 143.9664 | 1 | Powercor | Report | 11008 | 0.017572 | 22kV AC | Avalon Airport | 3232 | Lorne | Dug up
On arrival crew isolated supply and carried out repairs | 40 GLERUMS ROAD, TIMBOON VIC 3268 | 33036292 | Working too close to underground cables | [6 empty] | Powercor received a report from a customerâ€™s electrician advising the UG cable between a pole and pit had been dug up and damaged by a plumbing contractor. On arrival the crew found that a Low Voltage service cable had been struck by an excavator while digging a trench for a tank overflow pipe installation. The 63mm conduit was damaged and the LV cable pulled up and the outer sheath slightly damaged. Supply remained on as no fuses operated. There was no other reported third party damage, shock or any injuries. | Services cable | 2 | 2 | 2 |  | TRG003 | excavating near underground cable | No Go Zone (contact);Damage to network assets | 16/11/2017 18:55 |  |  | 9091 | Agricultural |  | 20180124PWA_08 | Infrastructure (network-based) | -38.4968 | 142.9925 | 1 | Powercor | Report | 11009 | 0.012507 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Timboon | Dug up
On arrival crew made site safe and arrange for replacement pillar | 60 QUEEN STREET, MELBOURNE VIC 3000 | 30210914 | Vehicle | [6 empty] | A Citipower employee reported a damaged pillar at the incident location. On arrival the fault crew found that the LV pillar had been hit by a bus. No injuries or fire has been reported. | LV Pillar | 2 | 2 | 2 |  | LQ034 | Bus hit pillar | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/11/2017 8:14 |  |  | 9092 | Roadway |  | 20180124PWA_09 | Infrastructure (network-based) | -37.817 | 144.9618 | 1 | CitiPower | Report | 11010 | 0.027463 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination located at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 63 RACE STREET, FLORA HILL VIC 3550 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Jacob Shanahan was in the Bathroom having a shower when he received an electric shock as he made simultaneous contact between his hands on the metallic Shower Tap and his bare feet while standing on the wet shower base. Mr Shanahan also noticed dimming lights when appliances were operating. | Service conductor | 2 | 2 | 2 |  |  | corroded neutral connection | Minor shock | 20/11/2017 0:00 |  |  | 9093 | Residential |  | 20180124PWA_10 | Infrastructure (network-based) | -36.7811 | 144.2966 | 1 | Powercor | Report | 11011 | 0.027166 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Flora Hill | Connection
Tests were carried out on various parts of the electrical installation including the points of contact using an independent earth and 12V was observed momentarily on the rear garden tap. Investigations found that the connection between the open wire reticulation and the ABC service feeding the property was full of corrosion. Fault crew replaced connection for neutral on open wire mid-span service. Tests were carried out and supply was left on to the property. | 7 DUKE STREET, WERRIBEE VIC 3030 |  |  |  |  | Corrosion |  | Phase to earth |  | Jenelle reports her boyfriend Anthony received an electric shock in his right hand whilst using the rear garden tap. | Service conductor | 2 | 2 | 2 |  |  | connection | Minor shock | 23/11/2017 15:00 |  |  | 9111 | Residential |  | 20180125PWA_06 | Infrastructure (customer connection) | -37.8981 | 144.6455 | 1 | Powercor | Report | 11032 | 0.02923 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
The crew isolated the damaged underground supply cable at the supplying pole. Repair works pending. | 368 HOGANS ROAD, HOPPERS CROSSING VIC 3029 | 32165533 | Working too close to underground cables | [6 empty] | A contractor widening Hoganâ€™s Road reported digging up an underground cable at the incident location. On arrival the fault crew found that an excavator used to widen the road had inadvertently dug up and severed the street light supply at the incident location. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | WBE032 | Road excavations | No Go Zone (contact) | 27/11/2017 12:00 |  |  | 9113 | Roadway |  | 20180125PWA_07 | Infrastructure (network-based) | -37.8607 | 144.6671 | 1 | Powercor | Report | 11034 | 0.036381 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Dug up
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination located at the Customerâ€™s FOLCB at the POA, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew re-terminated the existing O/H Aluminium Twisted Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 454 BOOMERANG AVENUE, CARDROSS VIC 3496 |  |  |  |  | Corrosion |  | Phase to earth |  | Mrs Muruvvet Yilmaz was in the Bathroom having a shower when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Taps and her bare feet while standing on the wet shower base. Mrs Muruvvet also received an electric shock while she was standing bare footed on the concrete veranda turning on the external rear Tap when she made simultaneous contact between the metal tap and the concrete veranda. | Service conductor | 2 | 2 | 2 |  |  | Corroded neutral conductor at FOLCB | Minor shock | 19/11/2017 8:00 |  |  | 9114 | Residential |  | 20180125PWA_08 | Infrastructure (customer connection) | -34.2967 | 142.1271 | 1 | Powercor | Report | 11035 | 0.0269 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Cardross | Connection
A voltage test between the taps and the grassed area resulted with 210 Volts rise between various points of the installation with reference to an independent earth. The rise was due to a damaged neutral conductor at the pole box on the Powercor pole. Powercor linesman repaired the service neutral & CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 7 NORTH AVENUE, ALTONA MEADOWS VIC 3028 | 32166676 |  |  |  | Corrosion |  | Phase to earth |  | Mark received an electric shock when he simultaneously contacted the metallic tap with one hand and the grassed area with his feet | Connection box | 2 | 2 | 2 |  | LV003 | Corroded connection in PTJB | Minor shock | 30/11/2017 17:30 |  |  | 9118 | Residential |  | 20180125PWA_12 | Infrastructure (network-based) | -37.8656 | 144.7777 | 1 | Powercor | Report | 17379 | 0.010455 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Connection
Initial Report: CEOT dispatched a fault crew to isolate and make safe. CEOT also called an AusNet Services' LEI Ben Pickering to investigate. Final Report by LEI: AusNet Services' replaced the faulty meter. An NST test was performed on the installation- passed. Damage report handed to the homeowner for appliance damage. Customers A/C and garage roller doors damaged due to power surge. Unable to find evidence of HVI at customer's property, however there was severe weather conditions in the area that night. Possible lightning. | 116 LEE ROAD, WINTON VIC 3673 | 5681746 |  | Lightning |  |  |  |  | 2 | IMS 232138. Initial Report: Customer called with no display on meter, no hot water and some appliance damage. Roller doors not working since fault on the 22nd January, INCD 162885-r, damaged LA at Line Fuse 834992. Fault crew called for an AusNet Services' LEI to attend as premises appears to have subjected to HV injection damage. Final Report by attending LEI: Attended site after report of a faulty meter. Ausnet Services had an electrical incident on 22.1.18. Blown LA at line fuse on pole # 5681746. Lend Lease LEI did not attend the original fault. | Surge diverter;Customer installation | 0 | 0 | 0 |  | wn6 | HVI due to suspected severe weather conditions - lightning. | HV injection | 24/01/2018 19:25 |  |  | 9103 | Agricultural |  | 20180125SPN_02 | Infrastructure (network-based) | -36.4852 | 146.128 | 1 | AusNet Services Distribution | Report | 11024 | 0.038001 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3673 | Winton | Lightning
On arrival crew isolated supply and carried out repairs | 1789 BRIDGEWATER-SERPENTINE ROAD, SERPENTINE VIC 3517 | 30027013 | Crane, excavator or other construction/farming equipment | [6 empty] | CFA reported a car hit a pole and a ground fire start at the incident location. A crew attended and found a high load had contacted and broken a low voltage conductor across a road, resulting in the conductor falling to the ground, starting a grass fire of 600sq/m on the road reserve. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | EHK024 | Unidentified high load struck conductors | Grassfire | 25/01/2018 11:23 | 1 | Small: 10 - 1000 sq.m | 9127 | Roadway |  | 20180129PWA_02 | Infrastructure (network-based) | -36.4411 | 143.9678 | 1 | Powercor | Report | 11052 | 0.029486 | Low voltage AC (<1kV) | Bendigo Airport | 3517 | Serpentine | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an Open Circuit U/G Supply Neutral Conductor in the Underground Reticulation Service Pit. The attending Powercor Fault Crew reterminated the Powercor U/G Service Neutral Conductor in the Service Pit and completed an NST which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1 LINDEN CLOSE, MILDURA VIC 3500 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr Andrew Kilroy was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet while standing on the wet shower base. | Services cable | 2 | 2 | 2 |  |  | loose connection | Minor shock | 26/11/2017 17:00 |  |  | 9128 | Residential |  | 20180129PWA_03 | Infrastructure (network-based) | -34.2125 | 142.1657 | 1 | Powercor | Report | 11054 | 0.03 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Connection
isolated supply and carried out repairs | 4 SHAW STREET, CAMPERDOWN VIC 3260 | 32059660 |  |  |  | Overheated connection |  |  |  | The CFA reported a grass fire at the incident location. A crew was dispatched to investigate. The crew attended and confirmed a 5m x 7m ground fire had occurred outside 3 Shaw St around the base of LV pole . It was identified that the neutral screen service to # 4 Shaw St had failed, leaving the customer with no power. There were no reported shocks or injuries. No further damage identified. | Service conductor | 2 | 2 | 2 |  | CDN003 | Loose connection at pole end | Grassfire | 28/01/2018 14:26 | 1 | Small: 10 - 1000 sq.m | 9132 |  |  | 20180129PWA_04 | Infrastructure (network-based) | -38.2387 | 143.1414 | 1 | Powercor | Report | 11058 | 0.03634 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3260 | Camperdown | Connection
Emergency switching was completed and the substation placed under LV parallel to maintain supply to customers in the vicinity. The faulty transformer was replaced, LV parallels removed and supply restored to normal. The oil spill was immediately contained and cleaned up in accordance with United Energy requirements. | 13 DALGETY STREET, DANDENONG VIC 3175 | 8813035 |  | Heat |  | Electrical breakdown |  |  | 2 | Pole fire reported at the corner of Canberra Avenue and Dalgety Street. During warm conditions, the 22kV 200kVA transformer at "Canberra-Dalgety" pole type substation was leaking hot oil from a bushing that fell to ground and a small grass fire occurring. The transformer subsequently failed and required replacement. | Pole mounted | 0 | 1 | 0 |  | KBH 32 | The 200kVA transformer at "Canberra-Dalgety" pole type substation was leaking hot oil from a bushing that fell to ground and a small grass fire started. | Grassfire | 25/01/2018 18:00 | 1 | Localised: less than 10 sq.m | 9130 | Roadway |  | 20180129UTD_01 | Infrastructure (network-based) | -37.9944 | 145.2078 | 1 | United Energy Distribution | Report | 12985 | 0.010431 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the damaged lightning arrestors were cut away using live line techniques. A further trouble order was created to replace the lightning arrestors and to inspect the CHP termination as it may require further maintenance. | 221 EASTBOURNE ROAD, ROSEBUD VIC 3939 | 1309970 |  | Bird |  |  |  |  | 1 | At 1608hrs on 27/01/2018, 22kV feeder RBD 24 circuit breaker successfully reclosed and held. A crow at the RBD 24 feeder exit cable head pole (RBD0184) at the corner of Eastbourne Road and Ashenden Square caused molten metal to fall to the dry grass below and small grass fires to occur that were extinguished by the CFA. All three lightning arrestors had flashed over with the road and centre phases badly blacked. | Surge diverter | 0 | 0 | 0 |  | RBD 24 | Bird Incident | Grassfire | 27/01/2018 16:08 | 1 | Localised: less than 10 sq.m | 9134 | Roadway |  | 20180129UTD_03 | Infrastructure (network-based) | -38.3677 | 144.8931 | 1 | United Energy Distribution | Report | 12987 | 0.012595 | 22kV AC | Moorabbin Airport | 3939 | Rosebud | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the LV Reticulation Neutral Conductor The attending Powercor Fault Crew reterminated the existing O/H Service Neutral connection located at the at the LV Reticulation and the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. The following additional tests were also completed: â€¢ A clip on amp meter tong test on the O/H Service Cable indicated Zero amps or equal current flow. â€¢ A clip on amp meter tong test on the main earth indicated Zero amps flowing in the earth. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1 MADELEY STREET, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Mrs Alice Claringbold was outside when she received an electric shock as she made simultaneous contact between her hand on the external metal Garden Tap and her bare feet while standing on the wet grass. | Service conductor | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 42837 |  |  | 9151 | Residential |  | 20180130PWA_10 | Infrastructure (network-based) | -38.2622 | 144.5276 | 1 | Powercor | Report | 11081 | 0.014096 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
On arrival crew isolated supply and carried out repairs | 23-29 GHAZEEPORE ROAD, WAURN PONDS VIC 3216 | 32084727 |  |  |  | Corrosion |  |  |  | The CFA reported a ground fire had occurred at the incident location. The report from the CFA was that the fire had started from a blown fuse. A crew was dispatched to investigate. The crew attended and found evidence of a ground fire totalling approximately 1m x 3m. They advised the cause was likely falling debris from an overheated LV copper-aluminium clamp There were no reported shocks or injuries. No further damage identified. | Connector/termination | 2 | 2 | 2 |  | WPD031 | Overheated connection | Grassfire | 28/01/2018 19:45 | 1 | Localised: less than 10 sq.m | 9154 | Roadway |  | 20180131PWA_01 | Infrastructure (network-based) | -38.2074 | 144.3027 | 1 | Powercor | Report | 11084 | 0.019705 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Waurn Ponds | Connection
A LEI and faults truck attended and completed installation tests and measured 15v on the earthing system to an independent earth. The faults crew checked connections and identified a corroded bullet connection at the neutral conductor where the service line connects onto the overhead reticulation conductors. Due to the high resistance in the bullet connection, 15v was impressed into the earthing system via the MEN connection, resulting in livening up the installation water pipes via the equipotential bond. The defective connection was replaced by the faults crew and the LEI re-tested the installation with supply left on after installation tests confirmed the fault had been rectified. | FLAT 8 373 NEERIM ROAD, CARNEGIE VIC 3163 | 2327325 |  | Heat |  | Neutral fault |  | Phase to earth | 2 | Estate Agent advised that slight shocks have been received from the shower taps. A REC has attended and cannot find the location of the fault. The occupier at the property received slight electric shocks from the shower taps and contacted the Real Estate Agent. A REC was sent to investigate the cause and contacted the United Energy faults and emergencies call centre when the fault could not be identified within the property. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  |  | Defection neutral connection at the pole end. | Minor shock | 30/01/2018 14:00 |  |  | 9170 | Residential |  | 20180131UTD_03 | Infrastructure (network-based) | -37.8901 | 145.0631 | 1 | United Energy Distribution | Report | 11101 | 0.039003 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | Connection
On arrival crew isolated supply and carried out repairs | 309-375 BREAMLEA ROAD, BREAMLEA VIC 3227 | 32070583 |  | Bird |  |  |  |  | 1 | A customer reported a conductor broken from one end and was lying over a bike path and entrance of home at the incident location. On arrival the crew found that a pelican had hit the line and broke the center phase. The break in conductor and bike path was between BREAMLEA SPUR 9 & 10. Backfed via downstream transformers. There was no reported fire, third party damage or any injuries. | Conductor (bare) | 2 | 2 | 2 |  | WPD024 | Bird Incident | Loss of supply | 26/12/2017 6:23 |  |  | 9184 | Roadway |  | 20180201PWA_06 | Infrastructure (network-based) | -38.2854 | 144.4007 | 1 | Powercor | Report | 11117 | 0.032301 | 22kV AC | Avalon Airport | 3227 | Breamlea | Animal
On arrival crew carried out repairs | 2 HOLMES STREET, ARDEER VIC 3022 |  | Copper theft | [6 empty] | While Powercor Crew where working in the area operations asked crew to check substation. Upon investigating the crew found that the earth cable appears to have been stolen. LIS 19559, Holmes -Suspension Substation. Sub located in Holmes Street near intersection of Suspension Street, Ardeer. | Earth/earthing | 2 | 2 | 2 |  |  | copper theft | Damage to network assets | 28/12/2017 17:36 |  |  | 9187 | Roadway |  | 20180201PWA_07 | Infrastructure (network-based) | -37.7823 | 144.7992 | 1 | Powercor | Report | 11120 | 0.011365 | Earthing cable | Laverton Raaf | 3022 | Ardeer | Other
On arrival crew carried out repairs | 9 COLE AVENUE, KEW EAST VIC 3102 |  | Copper theft | [6 empty] | The CitiPower report room was notified on 30/12/17 at 3.05pm by a customer, Ian, that a copper theft had occurred of the underground service to No. 9 Cole Ave, Kew. The customer advised the property was currently under construction and service cable had been stolen and the cable guard was now hanging over the footpath low enough to be touch by pedestrians. | Services cable | 2 | 2 | 2 |  |  | copper theft | Damage to network assets | 30/12/2017 15:05 |  |  | 9189 | Roadway |  | 20180201PWA_09 | Infrastructure (network-based) | -37.7948 | 145.0428 | 1 | CitiPower | Report | 11122 | 0.028103 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a loose O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Customers first POEL Pole, The attending Powercor Fault Crew reterminated the O/H Service Neutral Conductor in the existing Pole Top Connection Box on the Customerâ€™s first POEL Pole and checked the connections in the Pole Mounted Circuit Breaker and completed an NST Test which confirmed a Pass result. The attending LEI tightened all Neutral and Active connections within the Customerâ€™s Main Switchboard. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | MELBA PARADE, ANGLESEA VIC 3230 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Wes Smith advised several unknown persons had received an electric shock in the Changeroom Shower over the course of the past few years when they made simultaneous contact with their hand on the metallic Shower Head and their bare feet while standing on the wet floor. | Service conductor | 2 | 2 | 2 |  |  | Loose connection | Minor shock | 13/12/2017 16:15 |  |  | 9199 | Commercial |  | 20180205PWA_01 | Infrastructure (customer connection) | -38.426 | 144.1788 | 1 | Powercor | Report | 11133 | 0.032308 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
On arrival crew inspected conductor , no damage observed | 3556B HATTAH-ROBINVALE ROAD, WEMEN VIC 3549 | 30317284 | Working too close to overhead lines | [5 empty] | 1 | Customer reported loss of supply and machinery making contact with bare LV conductor. On arrival the crew found that a wheeled loader had struck LV bare overhead conductor between LIS 823267 and LIS 28170, no damage to conductor or pole attachments transpired. Machinery was no longer on site when crew arrived, work being undertaken to clear tree debris from previous weekâ€™s storm for land owner Rhonda Cattanach. There were no reported injuries, no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | WMN013 | Loader struck LV | Loss of supply | 13/01/2018 15:05 |  |  | 9215 | Agricultural |  | 20180205PWA_17 | Infrastructure (network-based) | -34.7871 | 142.634 | 1 | Powercor | Report | 11149 | 0.010135 | Low voltage AC (<1kV) | Mildura Airport | 3556 | Wemen | Vehicle
The capacitor bank was isolated to enable supply to be restored to the HV feeder. | 71 WILLIAMSONS ROAD, DONCASTER VIC 3108 | 7055546 |  | Heat |  | Electrical breakdown |  |  | 1 | At 1252hrs on 25/01/2018, 11kV feeder WD 23 circuit breaker reclosed to lockout affecting 616 customers. Caller reports that a power pole outside the property is on fire and sparking. During warm conditions, 11kV pole mounted capacitor bank "Williamsons-Bordeaux" flashed over that caused the feeder to reclose to lockout. Following the flash over that caused a minor pole fire that self extinguished, an oil spill occurred as a result of the capacitor banks failure that was immediately contained and cleaned up in accordance with United Energy requirements. | Pole top | 0 | 0 | 0 |  | WD 23 | The cause was unknown but conditions were warm at the time of the event. | Plant/equipment | 25/01/2018 12:43 | 1 | Negligible: no ground fire | 9217 | Residential |  | 20180205UTD_01 | Infrastructure (network-based) | -37.7806 | 145.1232 | 1 | United Energy Distribution | Report | 12984 | 0.02385 | 11kV AC | Moorabbin Airport | 3108 | Doncaster | AF Other
The burnt out krone box was replaced by a faults crew and supply restored. | 39A BRUARONG CRESCENT, FRANKSTON SOUTH VIC 3199 | 3315978 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | Customers supplied from "Bruarong-Grange" substation advised of a loss of their electricity supply. During hot and windy conditions, a krone box attached to pole No. LIS 3315978 caught on fire due to probable overload. The red phase LV connection in the krone box failed and there was no ground fire. The krone box supplied the north circuit of "Bruarong-Grange" pole type substation. | Connection box | 0 | 0 | 0 |  | FSH 13 | The cause was probable overload. | Pole-top fire | 28/01/2018 10:37 | 1 | Negligible: no ground fire | 9219 | Residential |  | 20180205UTD_02 | Infrastructure (network-based) | -38.1593 | 145.1094 | 1 | United Energy Distribution | Report | 12988 | 0.0029653 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston South | Connection
On arrival crew carried out reapirs | 7 SMITH STREET, ST ARNAUD VIC 3478 | 32017467 | Vehicle | [6 empty] | The occupier of #8 Smith St â€“ St Arnaud reported that a truck had hit wires out the front of school and that wires were down and sparking. Upon arrival crew found that the owner of a new truck (Hayden McKenzie) as reported by linesmen had brought down 2C/25mmÂ² twisted LV service at the supply pole end. There was no shock, no injury, no damage to third party assets or property | Service conductor | 2 | 2 | 2 |  | CTN006 | Truck struck service | Loss of supply;Damage to network assets | 43192.5097 |  |  | 9227 | Roadway |  | 20180207PWA_02 | Infrastructure (network-based) | -36.6102 | 143.2514 | 1 | Powercor | Report | 11162 | 0.016269 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3478 | St Arnaud | Vehicle
A fault crew attended, the damaged conductors were sleeved and supply restored. | 1 DAVLIN DRIVE, MILDURA VIC 3500 | 30325814 | Working too close to overhead lines | [5 empty] | 1 | A local resident reported that a truck had contacted the powerlines and power is out at the incident location. On arrival the fault crew found that a concrete pumping truck had been positioned near powerlines at the incident location. The operator raised the truckâ€™s boom, he did not see the overhead conductors due to low light (06:30am) and contacted same resulting in arcing and blown section fuses. There was no ground fire and no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | MBN012 | Concrete pumper struck line | Loss of supply;No Go Zone (contact);Damage to network assets | 43283.3264 |  |  | 9231 | Roadway |  | 20180207PWA_03 | Infrastructure (network-based) | -34.2017 | 142.1129 | 1 | Powercor | Report | 11167 | 0.0028634 | 22kV AC | Mildura Airport | 3500 | Mildura | Vehicle
On arrival crew isolated supply and carried out repairs. | 93 PARK STREET, HAMILTON VIC 3300 | 30094546 |  |  |  | Corrosion |  |  |  | Vicfire reported a wire down and sparking at the incident location. On arrival the crew found that a neutral screen service had failed near the POA and fallen to the ground starting a grassfire of approx. 2 square metres of the customerâ€™s front lawn. There were no injuries or other damage reported. | Service conductor | 2 | 2 | 2 |  | HTN004 | Overheated | Loss of supply;Grassfire | 43253.6618 | 1 | Localised: less than 10 sq.m | 9232 | Residential |  | 20180207PWA_04 | Infrastructure (network-based) | -37.7264 | 142.0239 | 1 | Powercor | Report | 11168 | 0.011348 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | OH Cable
On arrival crew carried out repairs | 50 PARK WEST DRIVE, DERRIMUT VIC 3030 | 34018189 | Working too close to underground cables | [6 empty] | A customer advised a contractor has dug up UG cable at the incident location. Upon arrival, the Powercor crew found that the Kiosk sub earthing cable had been dug up and a minor damage was done to the cable. There was no fir or reported injuries. | Earth/earthing | 2 | 2 | 2 |  | SU034 | contractor excavating | Damage to network assets | 18/01/2018 9:02 |  |  | 9251 | Public space |  | 20180209PWA_04 | Infrastructure (network-based) | -37.8083 | 144.8039 | 1 | Powercor | Report | 11193 | 0.021056 | Earthing cable | Laverton Raaf | 3030 | Derrimut | Other
On arrival crew isolated supply and Carried out repairs | 2 BIGGS STREET, ST ALBANS VIC 3021 | 32175211 |  |  |  | Overheated connection |  |  |  | VicFire reported a Fire outside 2 Biggs St, St Albans Upon arrival the crew had found that the POA/FOLCB at incident location, had failed and caused the POA/FOLCB to melt and burn away, approximately 6-7 inches of the customers mains had also been damaged and burnt as a result of this incident. The resultant hot melted plastic from the POA/FOLCB above had fallen onto the grassed front yard/lawn below causing a very-minor grass fire within the front yard of approximately 0.5mÂ² total area. The MFB attended site and the grass fire was extinguished. There was no reported injury or shocks as a result of this incident. | Connection box | 2 | 2 | 2 |  | SA005 | Insignificant remains to accurately determine cause | Loss of supply;Grassfire | 43314.6806 | 1 | Localised: less than 10 sq.m | 9261 | Residential |  | 20180212PWA_01 | Infrastructure (network-based) | -37.7392 | 144.8222 | 1 | Powercor | Report | 11203 | 0.035848 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Fuse
CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. Crew removed tree. Spur isolated and repairs carried out. Tree appears to have been felled deliberately towards HV conductors. Richard Kelaart (Select Solutions) has inspected the site and produced a report. Spur isolated and repairs carried out. He feels that the same person carried out both incidents (please refer to other incident on 8 February 2018 ESV number 20180212SPN_01). | BLACKFELLOWS ROAD, TOORLOO ARM VIC 3909 | 1903154 | Vandalism | Within clearances |  |  |  |  | 1 | IMS 232380. Feeder tripped on NLA32. An AusNet Sevices' crew patrolled the line and found a tree on the overhead HV conductors, lis 1903154, the Corner of Princess Highway and Blackfellows Rd in Nowa Nowa. Please note CEOT reported the location as Nowa Nowa but the pole location shows it is in Toorloo Arm, close to Nowa Nowa. There is no street address provided in this locality. CEOT advice tree on HV conductor, public tree on easement, cut down. | Conductor (bare) | 0 | 0 | 0 |  | NLA34 | Vegetation: Trees Incident | Unknown person cut tree down;Other | 43375.2972 |  |  | 9266 | Other | Easement | 20180212SPN_02 | Infrastructure (network-based) | -37.8221 | 148.0289 | 1 | AusNet Services Distribution | Report | 11677 | 0.025678 | 22kV AC | Bairnsdale Airport | 3909 | Toorloo Arm | Trees
CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. CEOT also notified the local DAO to investigate. HV conductor sleeved with 3/12 splices and supply restored. | 85 BLACKSANDS ROAD, THREE BRIDGES VIC 3797 | 1411451 |  | Fallen |  |  |  |  | 2 | IMS 232381. Initial report: HV conductor down - a small fire observed on the ground. Fire now out. Final report: It is suspected a 22 metre tall grown sapling tree located approximately 60 metres north of pole #1411451 and approximately 20 metres away from an outer phase 22kV, 1-1/2.275 steel overhead conductor fell on to the conductor causing the conductor to break and fault current causing a small grass fire of approximate size 1m x1m. | Conductor (bare) | 0 | 0 | 0 |  | wyk23 | Vegetation: Trees Incident | Grassfire | 43375.8326 | 1 | Localised: less than 10 sq.m | 9270 | Agricultural |  | 20180212SPN_03 | Infrastructure (network-based) | -37.8304 | 145.6787 | 1 | AusNet Services Distribution | Report | 11215 | 0.033743 | 22kV AC | Moorabbin Airport | 3797 | Three Bridges | Trees
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe and investigate and carry out any necessary repairs. The Lines crew attended and identified a broken neutral at the pole end at lis 2021691. The existing grey twisted service cable was replaced with a new XPLE type service cable and left off supply for the LEI to attend, test and restore supply. The LEI attended and confirmed the issue had been rectified and left the property on supply. The LEI carried out an IR test of the cables and earth integrity - OK. Carried out a NST test - passed. Checked for stray voltages and only found <0.5 Volt. Carried out tests to point of contact (shed handle) - negligible volts. Polarity checks OK. | 10 SUNSHINE RISE, SANDY POINT VIC 3959 | 2021691 |  |  |  | Neutral fault |  | Phase to earth | 2 | IMS 231817. Customer reported electric an shock. Steve (the property owner) and Riley were opening the shed door when a minor electric shock was felt from the door handle. Steve turned the garage circuit off and cautioned other occupants to stay away. Steve called AusNet Services' Faults number. The cause was a broken service neutral at pole end. | SWER conductor | 0 | 0 | 0 |  | phi11 | Fault at service neutral at pole end. High impedance fault. | Minor shock | 23/12/2017 12:42 |  |  | 9272 | Residential |  | 20180212SPN_05 | Infrastructure (network-based) | -38.8284 | 146.1244 | 1 | AusNet Services Distribution | Report | 11217 | 0.0014722 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3959 | Sandy Point | Connection
CEOT dispatched a fault crew to make safe, investigate and carry out any necessary repairs. The crew found that a possum had fallen from the 10kVA transformer and started a ground fire. The transformer was not damaged in any way. The local DOA also attended site during daylight hours and found no damage to assets and a small grass fire around the base of the pole. Inspection of assets from ground level showed no visible damage to pole, transformer or conductors. Fire contained in the road reserve and no damage to customer property. | 5 JACKSONS ROAD, FOSTER VIC 3960 | 2024724 |  | Animal |  |  |  | Phase to earth |  | IMS 232394. CEOT received INCD from Vic Fire saying that a transformer had blown up and caused a ground fire. VicFire called back to say that a possum had fallen from the transformer and started a ground fire. | Pole mounted | 0 | 0 | 0 |  | ftr21 | Animal Incident | Grassfire | 43436.9153 | 1 | Localised: less than 10 sq.m | 9280 | Agricultural |  | 20180213SPN_01 | Infrastructure (network-based) | -38.6489 | 146.2193 | 1 | AusNet Services Distribution | Report | 11233 | 0.015881 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Foster | Animal
Fault truck checked all connections and re-terminated neutral connection at the pole end CTA re-tested property, all required VESI tests passed | 1 YENDA COURT, HOPPERS CROSSING VIC 3029 |  |  |  |  | Corrosion |  |  |  | Colleen was showering at the time; she received an electric shock when she made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Service conductor | 2 | 2 | 2 |  |  | Loose connections | Minor shock | 43019.375 |  |  | 9292 | Residential |  | 20180214PWA_07 | Infrastructure (network-based) | -37.8855 | 144.6837 | 1 | Powercor | Report | 11282 | 0.023186 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe, investigate and carry out any required necessary repairs. The LEI conducted a NST test on no. 3 Pine Ave which failed so the LEI isolated supply and requested the fault truck to attend. Conducted a neutral check on 5 Pine Ave which also failed so isolated supply. Carried out a neutral check on 9 Pine Ave - passed. No. 3 and 5 Pine Avenue are fed from a common service pit supplied from a common FOLCB at the pole end. The fault crew attended and disconnected the old FOLCB at the pole. Consumer's mains underground cable IR tested - OK. The fault was discovered to be a corrosion in the pole FOLCB (pole 2809418). The FOLCB was replaced by the crew. Neutral checks still failed on no. 3 and 5 Pine Ave. It was then found that the neutral supply cable from the FOLCB to the overhead street mains neutral was faulty. This neutral cable was replaced and neutral checks passed. LEI re-checked voltage between points of contact after repairs and both points were <1 V to an independent earth. Supply restored | 3 PINE AVENUE, SURF BEACH VIC 3922 | 2809418 |  |  |  | Corrosion |  | Phase to earth | 2 | IMS 231824. The customer received an electric shock from the shower tap and the garden tap. The cause of the shock was a corroded neutral at the FOLCB on the pole plus a faulty neutral supply cable from the FOLCB to the overhead mains neutral. | Connection box | 0 | 0 | 0 |  | wgi31 | High impedance connections in pole mounted FOLCB. | Minor shock | 28/12/2017 14:56 |  |  | 9284 | Residential |  | 20180214SPN_01 | Infrastructure (network-based) | -38.5127 | 145.2981 | 1 | AusNet Services Distribution | Report | 11269 | 0.016501 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Surf Beach | Connection
CEOT dispatched a fault crew to make safe, isolate, investigate and carry out or arrange for necessary repairs. The crew replace the LV pillar with a new pillar. | 20 MARIEMONT AVENUE, WANTIRNA VIC 3152 | 5804164 |  |  |  | Age;Electrical breakdown |  | Phase to phase | 2 | IMS 231962. An incident was initially reported to CEOT as a meter box fire and an area outage. The fault crew attended and found that a LV pillar was burnt outside 20 Mariemont Ave, Wantirna. It was not a meter box. Old HRC fuse holders inside the pillar had broken down over time which then cause a fault to the frame which started a fire in the pillar. The fire was contained to the LV fuse units within the LV pillar. NO PHOTOS ARE AVAILABLE. | LV Pillar | 0 | 0 | 0 |  | BRA32 | Electrical breakdown of old HRC fuse fittings inside LV pillar. | Plant/equipment | 31/12/2017 11:21 | 1 | Negligible: no ground fire | 9287 | Residential |  | 20180214SPN_02 | Infrastructure (network-based) | -37.8567 | 145.2375 | 1 | AusNet Services Distribution | Report | 12928 | 0.0072245 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | Fuse
CEOT dispatched a fault crew to isolate, make safe and investigate. The crew isolated supply, made safe and replaced the burnt out BA fuse. CEOT also issued the incident to the local Duty Officer to do a fire report and investigate. The local Electrical Network Representative visited the site but was unable to gain access due to the locked paddock. No photo was taken by the initial fault truck visit. | 215 NUMBER SEVEN DRAIN ROAD, CORA LYNN VIC 3814 | 512759 |  |  |  | Candled fuse |  |  | 2 | IMS 231839. Customer called with part supply failure to pump and the transformer in the paddock has a fuse damaged. The attending fault crew alleged the transformer was hit by lightning last week and a 6 Amp Boric Acid fuse and the fuse tube had candled and burnt in half. No fire on ground or pole. | Boric acid | 0 | 0 | 0 |  | phm33 | Burnt BA fuse tube / candled. | Other electricity related | 43191.7326 | 1 | Negligible: no ground fire | 9297 | Agricultural |  | 20180214SPN_04 | Infrastructure (network-based) | -38.1645 | 145.6151 | 1 | AusNet Services Distribution | Report | 11288 | 0.024918 | 22kV AC | Moorabbin Airport | 3814 | Cora Lynn | Lightning
On arrival crew isolated supply repairs arranged. | 96 MUNRO AVENUE, SUNSHINE NORTH VIC 3020 | 30245830 |  |  |  | Electrical breakdown |  |  |  | A PCA Customer/Member of the Public:- advised at Corner of Munro Avenue & Davis avenue - wire broken at pole, was sparking (started fire which is now out). Customer advised wire broken but not down on ground. Upon arrival the crew had found that the 185mm 3/C HVABC at HV Pole LIS-727309 had failed, resulting in a flashover, the resultant sparks from the Failed HVABC have fallen onto the nature strip grassed area below causing a grass fire of approximately 6m x 2m. The crew has advised that upon arrival the grass-fire had self-extinguished. There was no reported HVI, injury or shocks as a result of this incident. | Conductor (ABC) | 2 | 2 | 2 |  | SSE012 | probable micro arcing and partial discharge | Grassfire | 13/02/2018 17:43 | 1 | Small: 10 - 1000 sq.m | 9301 | Roadway |  | 20180215PWA_01 | Infrastructure (network-based) | -37.7575 | 144.8356 | 1 | Powercor | Report | 11294 | 0.019811 | 22kV AC | Essendon Airport | 3020 | Sunshine North | OH Cable
The crew isolated the cable and repairs where completed. | 471 DOHERTYS ROAD, TRUGANINA VIC 3029 | 30119532 | Working too close to underground cables | [6 empty] | A contractor reported that the backhoe on their site has hit the service cable at the incident location. On arrival the crew found that a contractor (AAA Above Plumbing Group â€“ 03 0438 293 702) was operating a backhoe and contacted an LV underground service causing damage and breaking the cable. There were no reported injuries or third party property damages. | Cable | 2 | 2 | 2 |  | TNA023 | Excavation works | Loss of supply;No Go Zone (contact) | 43133.525 |  |  | 9317 | Roadway |  | 20180216PWA_06 | Infrastructure (network-based) | -37.8248 | 144.7457 | 1 | Powercor | Report | 11313 | 0.03109 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Vehicle
Crew replaced service to premises. | 11 GOLF LINKS ROAD, ARARAT VIC 3377 | 30081982 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer reported he has contacted the service wire with his vehicle and the wire has detached from the house end at the incident location. On arrival the crew found that the LV service cable was broken and laying on ground. There were no reported shocks or injuries. | Service conductor | 2 | 2 | 2 |  | ART034 | High load contacted service | Loss of supply;Damage to network assets | 43222.8264 |  |  | 9321 | Residential |  | 20180216PWA_07 | Infrastructure (network-based) | -37.2717 | 142.9203 | 1 | Powercor | Report | 11317 | 0.01744 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Vehicle
Jemena crew were called out to fix a broken pit and discovered cable had been stolen. Jemena crew made site safe, replaced cable and repaired pit. No injury to public and no loss of supply as cable had not been connected as yet because location was a vacant block. | 324 GEELONG ROAD, WEST FOOTSCRAY VIC 3012 |  | Copper theft | [5 empty] | 2 | A pole to pit underground copper cable was stolen about 20 meters. | Cable | 2 | 2 | 2 |  |  | Unknown person stole copper. | Damage to network assets | 18/02/2018 13:21 |  |  | 9323 | Residential |  | 20180218JEM_01 | Infrastructure (network-based) | -37.8067 | 144.8768 | 1 | Jemena | Report | 11319 | 0.00043287 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Other
The faults crew attended and isolated the faulted section, then the LV conductors were crimped at the point of failure. | 1 POWER STREET, PASCOE VALE SOUTH VIC 3044 | equipment no. 10571754 (conductor span) |  | Wind |  | Conductor clashing |  |  | 2 | Strong windy conditions caused conductor clashing on the low voltage span between pole numbers A093974 and A093982 As a result, the blue and white phase conductors fell to the the ground live. | Conductor (bare) | 0 | 0 | 0 |  | CS02 | Strong winds on day of incident caused LV conductors to clash between the two phases. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/02/2018 18:22 |  |  | 9330 | Residential |  | 20180219JEM_01 | Infrastructure (network-based) | -37.7361 | 144.9337 | 1 | Jemena | Report | 11328 | 0.016706 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale South | Conductor
Fault isolated and cross-arm replaced | 847 YENDON-EGERTON ROAD, MILLBROOK VIC 3352 | 32007989 |  |  |  | Leakage |  |  | 1 | A call was received from the customer at 847 Yendon-Egerton Rd, Millbrook that an explosion had occurred on the pole out the front of the above property. On arrival the crew found that a X-arm Fire had occurred on Millbrook Pole 82. The X-arm had burnt through where the EDO fuse unit mounts to the X-arm. Protection operated as expected | Crossarm (wood);EDO fuse | 0 | 0 | 0 |  | BAN011 | Excessive electrical leakage | Pole-top fire | 16/02/2018 3:40 | 1 | Negligible: no ground fire | 9328 | Roadway |  | 20180219PWA_01 | Infrastructure (network-based) | -37.6302 | 144.0679 | 1 | Powercor | Report | 11326 | 0.0084769 | 22kV AC | Ballarat Aerodrome | 3352 | Millbrook | Crossarm
A daylight inspection of the assets was completed and no damage was identified. | 3 SWILK STREET, TEMPLESTOWE VIC 3106 | 7057869 |  | Animal |  |  |  |  | 1 | At 0328hrs on 12/02/2018, 11kV feeder BU 14circuit breaker reclosed to lockout affecting 1749 customers. Per MFB - Caller reports there was a loud bang on the pole outside 12 Swilk Street near Foot Street. A possum flashed over on a HV/LV tee-off pole No. LIS 7057869 that caused no damage although a small grass fire started near the base of the pole after the possum dropped into the dry grass below. | Conductor (bare) | 0 | 0 | 0 |  | BU 14 | Animal Incident | Grassfire | 43436.1444 | 1 | Localised: less than 10 sq.m | 9326 | Roadway |  | 20180219UTD_01 | Infrastructure (network-based) | -37.7563 | 145.124 | 1 | United Energy Distribution | Report | 12991 | 0.015258 | 11kV AC | Essendon Airport | 3106 | Templestowe | Animal
A faults crew promptly attended and proceeded to isolate the damaged light at the base of the pole and removed the fire damaged 250w HPS lantern. A new order was created for the replacement of the defective lantern. | 6 DOUGLAS STREET, NOBLE PARK VIC 3174 | 9821649 |  |  |  | Overheated connection |  |  | 2 | Caller reports pole fire outside the Coles store in Douglas Street, Noble Park. A 250w HPS lantern on pole No. LIS 9821649 located in Douglas Street caught on fire. | Public lighting | 0 | 0 | 0 |  |  | The cause was a probable loose connection that overheated. | Pole-top fire | 16/02/2018 23:02 | 1 | Negligible: no ground fire | 9327 | Roadway |  | 20180219UTD_02 | Infrastructure (network-based) | -37.9655 | 145.1734 | 1 | United Energy Distribution | Report | 12996 | 0.0303 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | AF Other
The damaged HV intermediate cross arm was replaced under glove and barrier techniques. | 39 NEPEAN HIGHWAY, SEAFORD VIC 3198 | 3318176 |  | Prone to salt deposition |  | Leakage |  |  | 2 | Caller reports there is a fire on the cross arm outside 39 Nepean Highway, Seaford. During misty early morning conditions, a cross arm fire occurred on pole No. LIS 3318167. The pole is located directly opposite Port Phillip Bay and air blown salt contaminants contributed to the HV insulators tracking. There were additional reports of insulators tracking in the area at the same time. | Crossarm (wood) | 0 | 0 | 0 |  | FTN 21 | The pole is located directly opposite Port Phillip Bay and air blown salt contaminants contributed to the HV insulators tracking. | Pole-top fire | 16/02/2018 4:02 | 1 | Negligible: no ground fire | 9329 | Roadway |  | 20180219UTD_03 | Infrastructure (network-based) | -38.0904 | 145.1255 | 1 | United Energy Distribution | Report | 12995 | 0.024034 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Crossarm
Removed the damaged bottom half of the fuse tube on the centre phase EDO unit and installed a new EDO Fuse Tube to restore supply. The other 2 fuse tubes were not replaced. | 457 MOUNT BUFFALO ROAD, POREPUNKAH VIC 3740 | 4505257 |  |  |  | Candled fuse |  |  |  | IMS 232052 Found the centre phase EDO fuse tube burnt in half. The bottom half was stuck in the fuse unit and the top half was sitting on a concrete driveway near the base of the pole. There was no fire at the base of the pole. | EDO fuse | 0 | 0 | 0 |  | BRT22 | Burnt EDO Fuse Tube | Other electricity related | 16/01/2018 20:34 | 1 | Negligible: no ground fire | 9336 |  |  | 20180220SPN_01 | Infrastructure (network-based) | -36.6928 | 146.8638 | 1 | AusNet Services Distribution | Report | 12939 | 0.0087083 | 22kV AC | Wangaratta Aero | 3740 | Porepunkah | Fuse
Feeders in the easement de-enegised. AusNet Services and 2 Jemena feeders were de-energised at the request of MFB. Access Coordinator on site and local DAO notified. ESV notified. Gas Switch HV lead was replaced. | 19 HIGH STREET, THOMASTOWN VIC 3074 | 907481 |  |  |  | Overheated connection |  |  |  | IMS 232493. Report of a grass fire in the vicinity of AusNet Services' assets in easement to the north of TT ZSS. Burnt out HV lead/conductor on Gas Switch GB2491. The fire size was 375 sq. metres. The actual cause is unknown, most likely a poor connection at the Gas Switch. | Disconnector/isolator | 0 | 0 | 1 | 2 Jemena feeders de-energised. | tt7 | Burnt HV lead on pole mounted Gas Switch. | Grassfire | 14/02/2018 7:20 | 1 | Small: 10 - 1000 sq.m | 9343 | Other | In easement behind Thomastown Zone Substation | 20180222SPN_01 | Infrastructure (network-based) | -37.6912 | 145.0118 | 1 | AusNet Services Distribution | Report | 12829 | 0.038245 | 22kV AC | Essendon Airport | 3074 | Thomastown | Connection
Isolated LV at substation and carried out repairs. | 69 BUNTING ROAD, BROOKLYN VIC 3012 |  | Vehicle | [5 empty] | 1 | Blue phase LV conductor was brought down by vehicle (refer to tbl# 160906). | Conductor (bare) | 0 | 0 | 0 |  |  | Vehicle impacted pole pulling blue phase LV conductor out of shackle to ground. No details of vehicle recorded. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/02/2018 7:49 |  |  | 9349 |  |  | 20180223JEM_01 | Infrastructure (network-based) | -37.8119 | 144.8472 | 1 | Jemena | Report | 11358 | 0.034753 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Vehicle
Attending fault crew remover tree and replaced service. | 17 WIDFORD STREET, HAWTHORN EAST VIC 3123 | 30199632 |  | Fallen;MEC | [5 empty] | CitiPower Report Room was notified by the SES and customers on 19/02/18 at 19:08pm of a supply interruption and a pop sound from their internal switchboards. A High Voltage injection is believed to has occurred. A CitiPower LEI attended Widford St in Hawthorn and arranged defect notices and repairs on a number of customers switchboards. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | K011 | Vegetation contacts | HV injection;Loss of supply | 19/02/2018 19:08 |  |  | 9348 | Residential |  | 20180223PWA_02 | Infrastructure (network-based) | -37.8404 | 145.0505 | 1 | CitiPower | Report | 11801 | 0.0006331 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3123 | Hawthorn East | Trees
On arrival crew made safe and carried out repairs | 54 THORBURN STREET, BELL PARK VIC 3215 | 32083397 | Working too close to underground cables | [6 empty] | A council employee reported that the backhoe on their site has hit the service cable at the incident location. On arrival the crew found that a council employee (City of Greater Geelong â€“ 03 53725272) was operating a backhoe and contacted a LV service causing damage to the conduit but not the cable. There were no reported injuries or third party property damages. | Services cable | 2 | 2 | 2 |  | GL015 | Excavation works | Damage to network assets | 43133.3653 |  |  | 9350 | Roadway |  | 20180223PWA_03 | Infrastructure (network-based) | -38.1118 | 144.3366 | 1 | Powercor | Report | 11359 | 0.0039653 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Park | Vehicle
On arrival crew isolated supply and carried out repairs. | 132 SAILORS GULLY ROAD, SAILORS GULLY VIC 3556 | 30030467 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang by the bridge. There was no sign of the HV conductor making contact with the LV circuit below. CFA extinguished the cross-arm fire, a controlled interruption was required. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. | Crossarm (wood) | 2 | 2 | 2 |  | EHK024 | excessive leakage current | Pole-top fire | 18/02/2018 5:47 | 1 | Negligible: no ground fire | 9357 | Roadway |  | 20180223PWA_08 | Infrastructure (network-based) | -36.7082 | 144.2428 | 1 | Powercor | Report | 11366 | 0.028889 | 22kV AC | Bendigo Airport | 3556 | Sailors Gully | Crossarm
On arrival crew isolated supply and carried out repairs. | 34 MONTGOMERY STREET, SKIPTON VIC 3361 | 33106473 | Vehicle | [6 empty] | A customer reported that a truck has struck a wire and the wire was on the ground and started a ground fire at the incident location. On arrival the crew found that a truck had contacted the LV mains conductors crossing Glenelg Hwy and causing a conductor to break and fall to the ground. There was a resulting ground fire start of approx. 1m/sq on road reserve. CFA attended There were no reported injuries or third party property damages. | Conductor (bare) | 2 | 2 | 2 |  | BAS021 | Truck struck conductors | Loss of supply;Grassfire;Damage to network assets | 19/01/2018 10:51 | 1 | Localised: less than 10 sq.m | 9238 | Roadway |  | 20180208PWA_05 | Infrastructure (network-based) | -37.6855 | 143.365 | 1 | Powercor | Report | 11175 | 0.019262 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3361 | Skipton | Vehicle
CEOT dispatched a fault crew to isolate, make safe and carry out necessary repairs. CEOT also notified the local DAO to investigate. The LV ABC IPC Connector was replaced and cleaned connections. | 18 KIAMA DRIVE, LALOR VIC 3075 | 911324 |  |  |  | Overheated connection |  |  |  | IMS 232325. Vic Fire reported a grass fire encroaching an AusNet Services' pole and possible wires down. Report from attending local DAO: It is suspected a LV ABC IPC Connector on a white phase s/s cct failed with hot molten plastic from the IPC Connector igniting an approximate 0.3m x 0.3m small grass fire on the nature strip at the base of pole #911324. I could not see any private property damage resulting from the small fire except for some burnt nature strip. I also notified CEOT for repair of an exposed LV earth and broken conductor strand at base of s/s pole. | Connector/termination | 0 | 0 | 0 |  | epg31 | LV ABC connector failed. | Grassfire | 43283.7667 | 1 | Localised: less than 10 sq.m | 9242 | Residential |  | 20180208SPN_01 | Infrastructure (network-based) | -37.6625 | 145.0156 | 1 | AusNet Services Distribution | Report | 11180 | 0.021962 | Low voltage AC (<1kV) | Essendon Airport | 3075 | Lalor | Connection
A Zinfra faults crew attended, removed the tree branch from the LV conductors and ensured the site was safe before replacing the 315amp white phase din type fuse for the north circuit at "Station-Morton" substation. | STATION STREET, BURWOOD VIC 3125 | 7038579 |  | Within clearances |  | Conductor clashing |  |  | 1 | Customers supplied from the north circuit of "Station-Morton" substation advised of a loss of their electricity supply. City Wide Service Solutions were cutting council trees on behalf of the council and clashed the LV white and blue phases together that caused the white phase LV fuse to operate at "Station-Morton" substation. No injuries or damage was sustained between pole numbers 7038579 and 7038680. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43283.5833 |  |  | 9262 | Residential |  | 20180212UTD_01 | Infrastructure (network-based) | -37.8396 | 145.1215 | 1 | United Energy Distribution | Report | 11204 | 0.029595 | Low voltage AC (<1kV) | Moorabbin Airport | 3125 | Burwood | Vehicle
A LEI and faults truck attended the property and replaced the single phase meter panel fuse. Upon completion, the installation was tested and supply left on. | UNIT 5 2 HARWOOD ROAD, CAPE SCHANCK VIC 3939 |  |  | Heat |  | Overheated connection |  | Phase to earth | 2 | An onsite tradesman received a tingle from the meter box enclosure and advised the fuse holder has melted. A single phase meter panel fuse assembly had overheated due to a probable loose connection that caused subsequent overheating and requires replacement. The live metal fuse carrier terminals were slightly exposed and the tradesman working at the site touched the melted housing or terminal and received a strong electric shock to his hand. When he opened the door, AMI meter paperwork and booklet began to fall from inside the box. While the tradesman attempted to prevent the papers from falling, the rear of his left hand inadvertently made contact with the live exposed contact of the service fuse that had it plastic cover melted off from the cartridge while he was hanging onto the meter panel door with his right hand. | Meter board (including fuses) | 0 | 0 | 0 |  |  | The tradesman's left hand inadvertently made contact with the live exposed contact of the service fuse. | Minor shock | 43102.3542 |  |  | 9263 | Residential |  | 20180212UTD_02 | Infrastructure (network-based) | -38.4642 | 144.8996 | 1 | United Energy Distribution | Report | 11205 | 0.0091875 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Cape Schanck | Fuse
Feeder circuit breaker opened. Jemena staff isolated the faulted section. Asset was cut clear under access authority to make safe. The light bracket has now been secured appropriately using coach screws thus ensuring that this will not occur again. | ROSANNA ROAD, HEIDELBERG VIC 3084 |  |  | Wind |  |  | Poor workmanship | Phase to earth | 1 | Loose street light bracket made contact with the road phase HV conductor at Tee pole (A139688) Rosanna Rd opposite Banyule Rd causing the conductor to fall to ground. | Conductor (bare) | 0 | 0 | 0 |  | HB 32 | The light bracket was not attached securely to the wood pole, it therefore slipped (or shifted) in the wind. The investigation into the weakening of the street light bracket connection over time did not find conclusive causal factors: there is no evidence of vehicle impact. In this context, a likely contributing factor - although not proven - is poor workmanship during installation. The HV conductor clashed with the light bracket stay wire resulting in wire down. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2018 14:21 |  |  | 9296 | Roadway |  | 20180214JEM_02 | Infrastructure (network-based) | -37.7429 | 145.0725 | 1 | Jemena | Report | 11641 | 0.016149 | 11kV AC | Essendon Airport | 3084 | Heidelberg | AF Other
Site was isolated to make safe. LV conductors were repaired and supply restored. | 3 THE RIDGEWAY, KENSINGTON VIC 3031 |  |  | Wind;Fallen |  |  |  |  | 2 | Low voltage conductor on ground at Epsom Rd south of The Ridgeway due to council owned tree failing on the low voltage conductors. (Internal Jemena reference: TBL 160510). | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2018 9:03 |  |  | 9298 |  |  | 20180214JEM_03 | Infrastructure (network-based) | -37.7935 | 144.9271 | 1 | Jemena | Report | 11710 | 0.032065 | Low voltage AC (<1kV) | Essendon Airport | 3031 | Kensington | Trees
Section isolated to make safe. Conductor repaired and supply restored. | 21 EPSOM ROAD, ASCOT VALE VIC 3032 |  |  | Wind;Fallen |  |  |  |  | 2 | Two LV conductors on ground between poles A010840 and A133976. LV conductors were brought down by tree. Refer to TBL 160493. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2018 10:14 |  |  | 9299 |  |  | 20180214JEM_04 | Infrastructure (network-based) | -37.7855 | 144.9194 | 1 | Jemena | Report | 11709 | 0.041287 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Trees
Site was isolated and made safe. Crew replaced conductors and installed LV spreaders, then restored supply. | 17 SHERBOURNE STREET, ESSENDON VIC 3040 |  |  | Blown branch/vegetation | [5 empty] | Tree branch fell across 1 bay of low voltage overhead conductors resulting in the white and blue phase conductors to the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/02/2018 10:23 |  |  | 9300 |  |  | 20180214JEM_05 | Infrastructure (network-based) | -37.7597 | 144.916 | 1 | Jemena | Report | 11708 | 0.032485 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Trees
On arrival crew isolated supply and carried out repairs | 8 POVEYS ROAD, BLACKWOOD VIC 3458 | 31007271 |  | Wind;Fallen | [5 empty] | Wires down across road at incident location. Upon arrival crew found that during a storm in the area a tree had fallen across a mains LV ABC. There was no fire, no reported injuries or third party property damage. | Conductor (ABC) | 2 | 2 | 2 |  | WND024 | Wind storm | Loss of supply;Damage to network assets | 43406.7882 |  |  | 9285 | Roadway |  | 20180214PWA_01 | Infrastructure (network-based) | -37.472 | 144.2911 | 1 | Powercor | Report | 11679 | 0.0014954 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3458 | Blackwood | Trees
On arrival crew inspected assets for damage , non found | 1724 BIRREGURRA-FORREST ROAD, BARWON DOWNS VIC 3243 | 33039489 |  | Animal |  |  |  |  | 1 | Powercor received a call from VicFire reporting a grass fire caused by a pole fire at 1724 Forrest Rd, Barwon Downs. When crews arrived at the incident site, they found a deceased possum on the ground at the base of the pole., located on the road reserve. A small ground fire (35m x 15m) near the base of the pole had been extinguished by the CFA. No conductors fell to ground. No electrical asset damage was found. No other third party property damage was reported. No injuries were reported. | Conductor (bare);Crossarm (steel) | 2 | 2 | 2 |  | CLC007 | Animal Incident | Grassfire | 43406.9917 | 1 | Small: 10 - 1000 sq.m | 9286 | Public space |  | 20180214PWA_02 | Infrastructure (network-based) | -38.4764 | 143.7505 | 1 | Powercor | Report | 11272 | 0.031697 | 22kV AC | Avalon Airport | 3243 | Barwon Downs | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for any necessary repairs. A scout crew was initially sent to investigate and a subsequent fault crew was sent to rectify the fault. The HV line was isolated at the closest remote switch until the construction crew could attend. | 1729 LARDNERS TRACK, LARDNER VIC 3821 | 2705277 |  | Fallen | [5 empty] | IMS 232421. A tree came down during severe weather conditions. A fire of approximate size 20m x 6m occurred in the area which was extinguished by the CFA. The tree branch landed on the 3/12 steel HV conductor however it did not break and the HV line protection did not operate due to the high impedance fault. | Conductor (bare) | 0 | 0 | 0 |  | WGL23 | Vegetation: Trees Incident | Grassfire | 14/02/2018 20:15 | 1 | Small: 10 - 1000 sq.m | 9303 | Agricultural |  | 20180215SPN_02 | Infrastructure (network-based) | -38.2451 | 145.8757 | 1 | AusNet Services Distribution | Report | 12855 | 0.03789 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Lardner | Trees
EAP issued to investigate bus fault. Bus was restored and new cable pothead installed. All tests conducted - OK. A detailed investigation is currently in progress. | 412 COMMERCIAL ROAD, MORWELL VIC 3840 |  |  |  |  | Defective component |  |  | 1 | IMS 231900 - Rupture of the No.1 11 kV bus behind No.1 11/66kV CB and a cable pothead fault at No.1 11kV 11/22kV Transformer 11kV stub bus at MPS. No ground fire. No one injured. | Equipment;Connector/termination;Surge diverter | 1 | 0 | 0 |  |  | shortly after planned switching to open the 1-2 11kV Bus Tie CB at MPS, three separate protection operations and CBs tripping were recorded. There was no supply interruption to any customers for this incident. The cause was a defective/failed Red phase 11kV surge arrester on No1 11/6.6kV Transformer directly connected to the 11kV Feeder MWE1. The No1 11kV Bus fault was located on Blue phase bus in the vicinity of the No1 11/66kV Transformer 11kV CB position.The MPS No1 11/22kV Transformer trip was due to cable termination failure on the Red phase at the No1 11/22kV Transformer 11kV Stub Bus location. The cause of each of the three separate faults are attributed to suspected higher than usual voltages, transients or switching surges on the No1 11kV Bus network following the opening of the 1-2 11kV Bus Tie CB. The switching of the bus tie CB also changed the bus neutral earthing arrangement from the installed NEC to a star connected earthing transformer associated with the diesel generator installation. The combined contribution of these factors is believed to have caused failures of plant and equipment insulation. There is no high speed voltage recording devices to measure actual voltage levels or waveforms at the time of the faults. The increased voltage to earth stress is as a result of the Switching transients when the 11kV Bus Tie CB was opened; Pre-existing PD at the 11kV Bus on the White phase isolating contact bus-side spout on the No1 11/66kV Transformer 11kV CB; The dynamic changes to phase-earth voltages associated with the No1 11kV Bus delta network due to the installation of 11kV star connected and unloaded earthing transformer by the project to connect 100MW of diesel generators to the MPS. The 11kV bus section was repaired and the HV cable termination was replaced. | Plant/equipment | 43221.7083 | 1 | Negligible: no ground fire | 9307 | Industrial |  | 20180215SPN_03 | Infrastructure (network-based) | -38.2541 | 146.4146 | 1 | AusNet Services Distribution | Report | 11447 | 0.034919 | 11kV AC | Morwell (Latrobe Valley Airport) | 3840 | Morwell | AF Other
CEOT dispatched a fault crew to make safe, investigate and repair. EDO fuse tube replaced on single phase 10kVA substation. CFA on-site, no fire, just damage to the EDO fuse tube - slightly melted and ward on further inspection. Note: fuse had a blown 6K fuse element and tube hadn't dropped out of EDO unit. A ZA 90 day Notification to be raised in SAP to replace hung-up EDO's with BA fuse units as per policy 64-2009. Conclusion from investigation: EDO fuse holder was hung up and smoking. EDO fuse blew and failed to open causing fuse tube to heat up. No fire. therefore not F factor reportable. | 205 OLD CALLIGNEE ROAD, CALLIGNEE VIC 3844 | 2605600 |  |  |  | Age;Corrosion;Electrical breakdown;Candled fuse |  |  | 0 | IMS 231903. EDO fuse holder was hung up and smoking. EDO fuse blew and failed to open causing fuse tube to heat up. No fire. Burnt fuse tube. | EDO fuse | 0 | 0 | 0 |  | tgn23 | EDO fuse tube burnt. | Melting or smoking only | 43252.9493 |  |  | 9309 | Agricultural |  | 20180215SPN_04 | Infrastructure (network-based) | -38.3228 | 146.5833 | 1 | AusNet Services Distribution | Report | 13388 | 0.011884 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Callignee | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 49 GARDEN ROAD, DONVALE VIC 3111 | 7067244 |  | Heat |  | Fatigue |  |  | 1 | At 1907hrs on 14/02/2018, 22kV feeder NW 13 circuit breaker reclosed to lockout affecting 2126 customers. The MFB advise wires are down across the road. During warm conditions, HVABC failed in Garden Road between pole numbers LIS 7067244 and 7067243 near Flora Road and fell to the ground. A small grass fire occurred 3sqm that was quickly extinguished. The cause of the HVABC was under investigation. | Conductor (ABC) | 0 | 0 | 0 |  | NW 13 | The cause of the HVABC failure is under investigation. | Grassfire | 14/02/2018 19:07 | 1 | Localised: less than 10 sq.m | 9318 | Roadway |  | 20180216UTD_01 | Infrastructure (network-based) | -37.7888 | 145.1904 | 1 | United Energy Distribution | Report | 12993 | 0.011222 | 22kV AC | Moorabbin Airport | 3111 | Donvale | OH Cable
Crew attended and isolated supply CFA in attendance | 570 WHITES ROAD, RAINBOW VIC 3424 | 320898781 | Crane, excavator or other construction/farming equipment | [6 empty] | Vic Fire reported that a tractor towing a grain auger had contacted the SWER line as 570 Whites Rd, Rainbow. On arrival the crew found that farmer towing a grain auger had contacted the SWER line between Poles 32 and 33 Nandemarriman Spur line. The contact resulted in a fire that burnt approx. 0.1 hectares of stubble paddock and also destroyed the tractor. Minor damage was sustained to the conductor. At the point of contact the conductor height was measured at 7.4 metres. The crew isolated supply and carried out repairs. The driver of the tractor reported receiving a minor shock when he jumped off the tractor. The crew advised him to seek a medical assessment. The driver Patrick White attended the local hospital later in the day for checks. | Conductor (bare) | 0 | 0 | 0 |  | NHL015 | Interference, plant contacted line | Minor shock;Grassfire;Vehicle | 18/02/2018 11:47 | 1 | Small: 10 - 1000 sq.m | 9332 | Roadway |  | 20180220PWA_01 | Infrastructure (network-based) | -35.8181 | 142.1322 | 1 | Powercor | Report | 11331 | 0.029632 | 12.7kV AC (SWER) | Horsham Aerodrome | 3424 | Rainbow | Vehicle
On arrival crew isolated supply and replaced crossarm | ECHUCA-NANNEELLA ROAD, NANNEELLA VIC 3564 | 30122451 |  |  |  | Leakage |  |  |  | Customer reported a low conductor at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the kingbolt through to the insulator pin on one side causing the conductor to come adrift and hang approximately 5.0M above the ground, the other phase was still attached to the pole via the cross-arm strap. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | KYM001 | Excessive leakage current | Pole-top fire | 19/02/2018 14:44 | 1 | Negligible: no ground fire | 9339 | Agricultural |  | 20180221PWA_01 | Infrastructure (network-based) | -36.2788 | 144.7741 | 1 | Powercor | Report | 11749 | 0.031222 | 22kV AC | Shepparton Airport | 3564 | Nanneella | Crossarm
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out repairs. CEOT also dispatched the local DAO to investigate. The crew found a small grass fire in the area of 10 m square metres in size. Final Report: Fault crew replaced the service with a new XLPE type service cable. | 18 SPEAR STREET, CAPE PATERSON VIC 3995 | 2810983 |  | Wind;Property owner/customer | [5 empty] | IMS 232491. Initial Report: Report of service cable down by customer. Final Report: The fault crew found a 25 sq. metre grass fire on the customer's front lawn. A 2-Wire 25 sq.mm grey twisted aluminium service cable had burnt through and there were burn marks on the branch of a wattle tree on the customer's property at a distance from house where service cable was burnt through. Both the tree and burnt through service cable were located on the customer's property. | Service conductor | 0 | 0 | 0 |  | wgi33 | Vegetation: Trees Incident | Grassfire | 20/02/2018 16:39 | 1 | Small: 10 - 1000 sq.m | 9338 | Residential |  | 20180221SPN_02 | Infrastructure (network-based) | -38.6691 | 145.6162 | 1 | AusNet Services Distribution | Report | 11342 | 0.029037 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | Cape Paterson | Trees
Emergency high voltage switching was completed and the Zinfra fault crew identified some splash marks on the 66kV conductors that was documented and reported for future maintenance works (photos by fault crew provided to Zinfra Management). Once all authorities had completed their investigations, supply was restored. | 12B KOMBI ROAD, CLAYTON SOUTH VIC 3169 | 24885 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | At 1302hrs on 19/02/2018, 66kV feeder "CDA-SVTS" went to lockout but no customers were affected. Per MFB - person has hit the overhead conductors with a concrete truck. A mobile concrete pumping vehicle that was laying a concrete slab at the domestic building site made contact with the live "SVTS-CDA" 66kV overhead conductors outside 12 Kombi Road, Clayton South (15 First Avenue) that resulted in the loss of the feeder. The plant struck the overhead aluminium conductors between pole numbers LIS 24885 and 24886. The concrete pump operator received a severe electric shock while hosing down his tools and was admitted to the Alfred Hospital. The Zinfra fault crew had isolated the HV and LV overhead conductors and the LEI was informed by Greg Sieburn from ESV that Rachael Baker from WorkSafe Victoria would be leading the investigation. United Energy had contacted the ESV faults and emergencies call centre and was advised the MFB had previously notified ESV of the electrical event. There had been no contact with the United Energy No Go Zone team for an assessment or Permit to Work prior to the commencement of the construction work activities. | Conductor (bare) | 0 | 0 | 0 |  | CDA-SVTS | The mobile concrete pumping vehicle made contact with the live 66kV overhead conductors. | Minor shock;No Go Zone (contact) | 19/02/2018 13:02 |  |  | 9341 | Roadway |  | 20180221UTD_01 | Infrastructure (network-based) | -37.9314 | 145.1353 | 1 | United Energy Distribution | Report | 11345 | 0.039559 | 66kV AC | Moorabbin Airport | 3169 | Clayton South | Vehicle
Procedures as indicated in the work instruction for HV injections has been followed and a letter and claim form was provided to the single customer. | 80 VALLEY ROAD, LANGWARRIN VIC 3910 |  |  | Wind;Property owner/customer |  | HV injection |  |  | 1 | At 2053hrs on 19/02/2018, 22kV feeder LWN 21 circuit breaker successfully reclosed and held. A short time later at 2141hrs, ACR FS1069 locked out that was carrying LWN 21 at the time of the event. During extreme windy conditions, a large private tree branch fell over "Potts2-Valley" pole type substation and broke the HV/LV crossarms and damaged a transformer bushing. The operation of the ACR, delayed restoration of the feeder and the substation was placed under LV parallel to restore supply to customers. The construction work was completed early the following morning and the construction crew who had removed the tree and completed rectification work, requested that a LEI attend as a high voltage injection was suspected. The LEI tested installations in the vicinity and confirmed that a HVI didn't occur. 20/02/2018 - A customer who resides at 80 Valley Road, Skye contacted United Energy and advised they have had problems with electrical equipment following the previous outage and a LEI was dispatched to investigate. The LEI confirmed a high voltage injection occurred (MOR 1801) affecting the single customer that sustained minor damage to the main switch board, blown surge arrestors, burnt out RCBO and a blown compact fluorescent globe. The LEI issued a damage report to the occupier and was advised to contract a REC to rectify the damage to the main switch board. | Conductor (bare);Pole mounted | 0 | 0 | 0 |  | LWN 21 | Vegetation: Trees Incident | HV injection;Loss of supply | 20/02/2018 21:41 |  |  | 9342 | Roadway |  | 20180221UTD_02 | Infrastructure (network-based) | -38.1253 | 145.1985 | 1 | United Energy Distribution | Report | 11347 | 0.028331 | 22kV AC | Moorabbin Airport | 3910 | Langwarrin | Trees
CFA attended and extinguished the fire. On arrival crew inspected assets and carried out repairs | 90 HORFIELD SCHOOL ROAD, HORFIELD VIC 3567 | 33022765 |  | Bird |  |  |  |  | 1 | CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew indicated that a bird had flashed over on the bypass switch on load side of an ACR pole, causing the bird to fall to the ground and ignite a small area of grass commencing at the base of the pole and running along a roadside drain, approximately 10M x 60M square was burnt. There were no reported injuries, no 3rd party damage. | Disconnector/isolator | 2 | 2 | 2 |  | CHA005 | Bird Incident | Grassfire | 21/02/2018 19:57 | 1 | Small: 10 - 1000 sq.m | 9347 | Roadway |  | 20180223PWA_01 | Infrastructure (network-based) | -35.8853 | 144.2316 | 1 | Powercor | Report | 11355 | 0.03273 | 22kV AC | Swan Hill Aerodrome | 3567 | Horfield | Animal
On arrival crew isolated supply and replaced pole | 790 KEWELL EAST ROAD, KEWELL VIC 3390 | 30226897 |  |  |  | Leakage |  |  | 1 | Customers called to advise of an outage and a pole fire that had occurred at the above location. A crew attended and found there had been a pole fire at P34A Kellalac east S/L. Protection operated. CFA did not attend. Customer extinguished fire. Ground fire start of approx.2sq/m on private property. There were no reported shocks or injuries. | Pole (wood) | 2 | 2 | 2 |  | HSM005 | Excessive leakage current | Pole-top fire;Grassfire | 23/02/2018 9:39 | 1 | Localised: less than 10 sq.m | 9360 | Agricultural |  | 20180223PWA_10 | Infrastructure (network-based) | -36.4112 | 142.4841 | 1 | Powercor | Report | 11369 | 0.0046944 | 12.7kV AC (SWER) | Horsham Aerodrome | 3390 | Kewell | Pole
There was no damage to the HV overhead conductors as the tree dropped clear and supply was restored. | 231 NEPEAN HIGHWAY, DROMANA VIC 3936 | 1103402 |  | Wind;Fallen |  |  |  |  | 1 | At 0951hrs on 14/02/2018, 22kV feeder circuit breaker reclosed to lockout. Caller reports that a tree has brought down power lines and there is arcing and sparking. During hot and windy conditions, a tree fell onto the HV conductors near pole No. LIS 1103402 in Nepean Highway west of Old Moorooduc Road and a small grass fire started from molten metal falling into the dry grass. There were no wires down as indicated in the initial call. | Conductor (bare) | 0 | 0 | 0 |  | DMA 24 | Vegetation: Trees Incident | Grassfire | 14/02/2018 9:51 | 1 | Localised: less than 10 sq.m | 9372 | Roadway |  | 20180226UTD_01 | Infrastructure (network-based) | -38.308 | 145.0296 | 1 | United Energy Distribution | Report | 12994 | 0.0049919 | 22kV AC | Moorabbin Airport | 3936 | Dromana | Trees
On arrival crew carried out repairs | 135 KINGSTON ROAD, KINGSTON VIC 3364 | 32001388 |  | Blown branch/vegetation | [5 empty] | Customer reported a small ground fire at the incident location. On arrival the crew found that an elm tree branch had come down in windy conditions and contacted a 3 phase open wire low voltage line. There was a small ground fire of approximately 3mÂ². There were no injuries. | Conductor (bare) | 2 | 2 | 2 |  | BAN009 | Vegetation: Trees Incident | Grassfire | 25/02/2018 14:23 | 1 | Localised: less than 10 sq.m | 9388 | Public space |  | 20180227PWA_01 | Infrastructure (network-based) | -37.3984 | 143.9465 | 1 | Powercor | Report | 11410 | 0.032551 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3364 | Kingston | Trees
On arrival crew confirmed isolation and initiated cleanup. | VENS RIVER PROPRIETARY LIMITED ABATIOR, 43 HICKS ROAD, YARRAWONGA VIC 3730 | 33080126 | Copper theft | [6 empty] | Customer reported copper theft and damage to electrical equipment at incident location. On arrival the crew found that the ground type enclosure had been breached by thieves, a ground type transformer has been tipped on its side, the lid opened and an attempt to remove the copper core had taken place, the entire oil contents of the transformer were released into the bunded area, the HV cables supplying the transformer were also cut and stolen from pole to transformer bushings. Customer side assets were also stripped ( copper bus in CT metering cabinet ), the fence was also extensively damaged to the ground type enclosure. There were no reported injuries, no ground fire Note: This installation was already isolated from supply (unused asset) | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | CME016 | Vandalism - Copper theft | Damage to network assets | 19/02/2018 16:52 |  |  | 9391 | Commercial |  | 20180227PWA_03 | Infrastructure (network-based) | -36.0539 | 146.0005 | 1 | Powercor | Report | 11412 | 0.021241 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3730 | Yarrawonga | Other
Initial Report: CEOT dispatched a fault crew to make safe, isolate and carry out / arrange for necessary repairs. CEOT notified the local DAO to investigate. ESV advised. Final Report: The fault crew issued a EAP, removed the tree off the HV conductor, repaired the conductor and cancelled the EAP. Supply was restored. | 200 PURVIS ROAD, TANJIL SOUTH VIC 3825 | 2210545 |  | Wind;Fallen |  |  |  | Phase to earth | 1 | IMS 232631. Initial Report: Customer reported no supply. tree on HV. wire down and localised ground fire reported. Fault crew arrived on-site and observed a HV conductor was down resting on a Gum tree. A broken HV conductor resulting in a small burnt grassed area of size 500mm x 500mm. Nil injuries or property damage. CFA were on-site. Semi mature Eucalyptus viminalis, H 18m, DBH 350mm has had line side leader fault and fall onto HV conductors. No signs of decay or previous faults at site of fault. Trunk was located 6-10m from the HV line. Final Report: Under INCD-166784-r, reports of a fire around LIS #2210545. | Conductor (bare) | 0 | 0 | 0 |  | MOE14 | Vegetation: Trees Incident | Loss of supply;Grassfire | 28/02/2018 17:54 | 1 | Localised: less than 10 sq.m | 9398 | Residential |  | 20180301SPN_02 | Infrastructure (network-based) | -38.1384 | 146.2948 | 1 | AusNet Services Distribution | Report | 12831 | 0.015814 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Tanjil South | Trees
CEOT dispatched a fault crew to make safe, isolate and carry out / arrange for necessary repairs. CFA attended the incident. The crew repaired the HV conductors and restored supply. There was a 52m x 5m fire along the fence line in the area. The tree was outside the minimum clearance space. | 604 NAMBROK HALL ROAD, NAMBROK VIC 3847 | 2509549 |  | Wind;Fallen |  |  |  | Phase to earth |  | IMS 232632 - Conductor down - caused by tree - grass fire in area 30m x 2.5m. Tree come down onto 22kV conductors. There was a 52m x 5m fire along the fence line in the area. Wind event caused two Cypress trees that formed a line of trees of a farm shelter belt to heave and impact the lines. Fire started. A site inspection identified a tree adjacent to a failed tree required urgent works. Crew activated to be reduced to below line height immediately. The tree trunk was located 5m from the HV line. The tree was a private tree. | Conductor (bare) | 0 | 0 | 0 |  | MFA22 | Vegetation: Trees Incident | Grassfire | 28/02/2018 19:51 | 1 | Small: 10 - 1000 sq.m | 9400 | Agricultural |  | 20180301SPN_03 | Infrastructure (network-based) | -38.0773 | 146.9015 | 1 | AusNet Services Distribution | Report | 12823 | 0.020747 | 22kV AC | Morwell (Latrobe Valley Airport) | 3847 | Nambrok | Trees
CFA attended. made safe and DAO notified to investigate. CEOT dispatched a fault crew to make safe, isolate and carry out necessary repairs. The local DAO and ESV were notified. The fault crew isolated the HV line, disconnected the HV bridges from the tee-off pole to substation pole. The crew replaced a section of damaged HV steel conductor. | 54 MAXWELLS ROAD, LARDNER VIC 3821 | 2705329 |  | Blown branch/vegetation |  |  |  |  | 1 | IMS 232633. Reported tree on HV and fire in the vicinity. Under INCD-166774-r, reports of a fire around LIS #2718525. A gum tree branch broke off in high winds and landed on the HV conductor (3/12 steel) single phase. The branch broke off and landed on the conductors breaking one and trapping one. The fire size was 12,000 sq. metres in size. The main tree trunk is 15 metres away from the HV conductor. The tree is classed as a private tree. The tree branch in length was about 22 metres long and the tree height is about 30 to 40 metres in height from ground level. | Conductor (bare) | 0 | 0 | 0 |  | WGL23 | Vegetation: Trees Incident | Grassfire | 28/02/2018 16:56 | 1 | Medium: 1000 sq.m - 10 ha | 9401 | Agricultural |  | 20180301SPN_04 | Infrastructure (network-based) | -38.2371 | 145.884 | 1 | AusNet Services Distribution | Report | 11429 | 0.026529 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Lardner | Trees
On arrival crew crew removed saplings. | MUNDY STREET, BENDIGO VIC 3550 | 33017852 |  | Within clearances |  |  |  |  | 1 | 66Kv Feeder CB for BGO EHK 66Kv Went to Lockout during wind storm. Line patrol found tree in contact with 66Kv at Pole # 22 LIS # 413178 in gusty wind in VLine Reserve near the corner of Mundy and McLaren Streets BENDIGO. There was a ground fire 15 Metres X 8 Metres. There were no reported shocks, No third party damage. | Conductor (bare) | 2 | 2 | 2 |  | BGOEHK | Wind storm | Loss of supply;Grassfire | 28/02/2018 15:29 | 1 | Small: 10 - 1000 sq.m | 9412 |  |  | 20180302PWA_01 | Infrastructure (network-based) | -36.7612 | 144.288 | 1 | Powercor | Report | 15131 | 0.0016771 | 66kV AC | Bendigo Airport | 3550 | Bendigo | Trees
On arrival crew isolated supply and carried out repairs | 735 BACCHUS MARSH ROAD, MERRIMU VIC 3340 | 30116368 |  |  |  | Leakage |  |  |  | Employee reports a broken HV Xarm at P84 Melton line. Xarm burnt though at king bolt and hanging from pole by bridges. No ground fire start. There were no reported shocks or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | BMH006 | Excessive leakage current | Pole-top fire | 43134.5972 | 1 | Negligible: no ground fire | 9418 | Roadway |  | 20180305PWA_01 | Infrastructure (network-based) | -37.6832 | 144.4885 | 1 | Powercor | Report | 11456 | 0.0061968 | 22kV AC | Laverton Raaf | 3340 | Merrimu | Crossarm
LEI conducted subsequent tests at the customers main switch to identify 22 volts on the incoming neutral. The attending Fault Crew replaced the defective single phase O/H neutral screened aluminium service cable. The attending LEI, conducted consumers mains verification testing at the switchboard prior to energisation. Then completed testing of the premises when supply was provided to the FOLCB. Voltage tests between an independent earth and various points of the electrical installation, including the M.E.N. and metallic water pipe system, the point of contact being the metal garage and the metal fence and the distribution assets, identified a constant voltage of 0 Volts. An NST test carried out by LEI indicated a Pass result. The Installation was left ON supply. | 16 WONGANELLA DRIVE, KEILOR EAST VIC 3033 |  |  |  |  | Neutral fault |  |  | 2 | Resident reported receiving an electric shock from her color-bond boundary fence. After identifying the area where the shock was received (boundary color-bond fence), LEI conducted a voltage test and found that the fence and a metal garage in contact with the fence had a reading of 240v to earth. | Neutral screen | 2 | 2 | 2 |  |  | Defective single phase O/H neutral screened aluminium service cable. | Minor shock | 43254.4632 |  |  | 9427 | Residential |  | 20180306JEM_01 | Infrastructure (network-based) | -37.7345 | 144.8639 | 1 | Jemena | Report | 11467 | 0.020382 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | OH Cable
Isolated supply for repairs to be carried out Beattys Rd P6 pole-mounted substation to be replaced | 167 BEATTYS ROAD, FRASER RISE VIC 3336 |  | Copper theft | [5 empty] | 1 | HV earth cut away by vandals who attempted to pull away underground service cable, and damaged neutral bushing in doing so. | Services cable;Pole mounted;Earth/earthing | 2 | 2 | 2 |  | SHM14 | Copper theft | Loss of supply;Damage to network assets | 43254.7417 |  |  | 9429 | Residential |  | 20180306JEM_02 | Infrastructure (network-based) | -37.6962 | 144.7199 | 1 | Jemena | Report | 11469 | 0.036785 | Not applicable | Melbourne Airport | 3336 | Fraser Rise | Other
An investigation commenced by Zinfra and United Energy with the 3 Universal lineworkers immediately stood down from the United Energy network. The 3 Universal lineworkers were interviewed on 05/03/2018 with written statements taken with individual observations of the events that led to the transposed conductors in the pole box. The investigation revealed that a Zinfra subcontractor (Universal) was preparing and installing a new 3 phase underground supply on a service pole in Wickham Road, Hampton East. The work involved the replacement of the existing single phase overhead service supplying the service pole with a new 3 phase XLPE overhead service. This type of work is a commonly performed task and well within the normal range of duties for a lineworker. During the works, an error occurred that resulted in a voltage of ~400V being injected into the customerâ€™s premises. The effect of this was significant damage occurring to appliances within the premises. The two main contributing factors that caused this incident are: â€¢ An error when connecting the new 3 phase overhead service to a pole box; and â€¢ A failure to test the installation in accordance with established industry standards. (The VESI Installation Supply Connection Tests & Procedures). Each if these factors are explored in more detail in the United Energy Electrical Incident Report that will be finalised on 16/03/2018. | 39 WICKHAM ROAD, HAMPTON EAST VIC 3188 | 1819314 |  |  |  | HV injection;Reverse polarity | Not followed |  | 2 | 3.25PM - Zinfra advised United Energy that a "Reverse Polarity" occurred following work by a subcontractor (Universal). The crew have remained on-site. 3.35PM - United Energy advised ESV who will be attending and requested the site be quarantined. (Reference No. 9442876). The property is located at 39 Wickham Road, Hampton East and the initial investigation revealed. â€¢ 3 Universal lineworkers directly involved in incident were completing a supply upgrade for a new pole to pit underground supply for number 41Wickham Road â€¢ Connections found to be transposed in the pole mounted junction box on the service pole. Active to active and the neutral connected to an active conductor in the pole junction box â€¢ LV fuse cartridge had been left in at the point of attachment and the crew failed to correctly prepare the installation as a requirement of the VESI Installation Supply Connection Tests & Procedures â€¢ Licenced Electrical Inspector Frank Zahra (EIV) attended and completed an internal examination of the customers electrical equipment and identified that a Low Voltage injection occurred that damaged the customers air conditioning unit and stove. United Energy Customer Resolution team worked with the REC to rectify the damage in a timely manner. An onsite investigation took place and supply was restored following rectification of the transposed conductors. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | The cause was transposed conductors in the pole mounted junction box and the failure to test in accordance with the VESI Installation Supply Connection Tests & Procedures. | HV injection;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43134.5417 |  |  | 9425 | Residential |  | 20180306UTD_01 | Infrastructure (network-based) | -37.9433 | 145.0285 | 1 | United Energy Distribution | Report | 11772 | 0.015567 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton East | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 113 ELDER STREET S, CLARINDA VIC 3169 | 2330256 |  | Precipitation |  | Leakage |  |  | 1 | At 0454hrs on 01/03/2018, 22kV feeder CDA 22 circuit breaker successfully reclosed and held. At 0542hrs on 01/03/2018, 22kV feeder CDA 22 circuit breaker reclosed to lockout affecting 360 customers. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 2330256 located outside 113 Elder Street. The HV strain cross arm had HV isolators (OA3477) attached and the creaser fire occurred at the cross arm brace. A HV conductor fell with the isolator attached and made brief contact with the LV conductors below and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Rosella-Burke" and "Elder-Tina" substations. The LEI tested properties in the vicinity and confirmed that a high voltage injection did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | CDA 22 | The cross arm fire started following light rain after a lengthy dry spell. | Pole-top fire;Loss of supply | 43103.2375 | 1 | Negligible: no ground fire | 9428 | Residential |  | 20180306UTD_02 | Infrastructure (network-based) | -37.9423 | 145.102 | 1 | United Energy Distribution | Report | 13031 | 0.031383 | 22kV AC | Moorabbin Airport | 3169 | Clarinda | Crossarm
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. Fault crew notified CEOT and Manual Gas Switch was opened. Fault crew Lifted and stowed Live Line Clamps on tee-off conductors. Fault crew then drove back to the Manual Gas Switch to re-energise Bostock Spur line and re-energise customers - this left just one customer of supply. The crew tested and attached E/S/C, tagged pole and issued EAP to Crew. Crew using EPV cut the head of the Gum tree clear of the HV conductors, packed up EPV and proceed back to the isolation point ready to re-energise supply at pole 17A Bostock Spur line. The LV and HV fuses on pole 17AE Bostock Spur LIS 3918933 were open and pole tagged, ready for energisation. The EAP was cancelled, E/S/C was removed, CEOT was contacted and Live Line Clamps were reinstated at pole 17A Bostock Spur line Mansfield, re-energising supply to pole 17AE Bostock Spur line Mansfield, Fault crew then closed HV and LV fuses on pole 17AE Bostock Spur line and completed all relevant tests. Crew notified supervisor, Manager and DAO. The crew also took photos before the tree was removed from the HV conductors. | 185 BANUMUM ROAD, MANSFIELD VIC 3722 | 3918933 |  | Wind;Fallen |  |  |  | Phase to phase |  | IMS 232621. Initial Report: Fire brigade reported grass fire at 185 Banumum Rd, Mansfield. Fault Crew attended. Tree contacted an overhead HV conductor. Final Report: Fire brigade reported a grass fire at 185 Banumum Rd, Mansfield. Fault crew attended site and found head of a gum tree resting on HV conductors between pole 17A Bostock Spur line LIS 3918933 and pole 17AE Bostock Spur line LIS 3918934. The tree appeared to spilt at the base of the tree trunk. It was an extremely windy day. | Conductor (bare) | 0 | 0 | 0 |  | msd2 | Vegetation: Trees Incident | Grassfire | 28/02/2018 12:11 | 1 | Small: 10 - 1000 sq.m | 9432 | Agricultural |  | 20180307SPN_02 | Infrastructure (network-based) | -37.1009 | 145.9743 | 1 | AusNet Services Distribution | Report | 11475 | 0.014966 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Trees
Crew sent to investigate and found that tip truck had contacted OH conductors causing fault. The tip truck owner/operator had left site and could not be identified at the time. THE ONSITE OFFICE MANAGER (DENE WARREN) WAS CONTACTED AFTER THE INCIDENT AND ASKED ABOUT THE ACTIVITIES WHICH CAUSED THE INCIDENT; THE INFORMATION PROVIDED HAS BEEN USED TO COMPILE THIS REPORT. DENE ADVISED THE COMPANIES DIRECTOR AMOS, HAD INTIATED IMMEDIATE ACTION FOLLOWING THE LAST INCIDENT AND ERECTED A STAR PICKET & PLAIN WIRE FENCE WITH WARNING SIGNAGE BELOW THE OVERHEAD LINE IMMEDIATELY ADJACENT TO THE SPANS OF CONDUCTOR STRUCK BY THE TIP TRUCK/S PREVIOUSLY. | 10 BUCKLER ROAD, NORTH WANGARATTA VIC 3678 | 5652722 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232622. Received INCD for part supply failures and also that a truck had contacted OH conductors. THE HYBRIG AG INSTALLATION AT 52 BUCKLER RD WANGARATTA NORTH PRODUCES THE ADBLUE CHEMICAL FROM ORGANIC MATTER AT THIS SITE. THE FACTORY ACCEPTS LARGE VOLUMES OF ORGANIC MATERIAL DELIVERED TO THEIR SITE AND PROCESSES THIS MATERIAL ONSITE. IT WOULD APPEAR THAT TIM PETTY FROM SOIL & TOIL WAS DELIVERING SOME BULK MATERIALS IN A TANDEM TIPPER AND HAS RAISED HIS TIP[PER UNDER OUR 22,00VOLT SINGLE PHASED DOM REST SPUR BETWEEN POLE 5 (565722) AND POLE 6 (5652723) AND CONTACTED ONE OR BOTH PHASES WHICH HAS RESULTED IN THE 22,000 VOLT SPUR FUSE AT POLE 513094 <826218>. AUNSET FAULTS PERSONNEL ATTENDED THE BLOWN LINE FUSE AND PATROLLED THE LINE BEFORE REPLACING THE FUSE AND RESTORING SUPPLY. WHILST NO CAUSE COULD BE LOCATED AT THE TIME, THEY WERE ADVISE THAT A TIP TRUCK HAD CONTACTED THE OVERHEAD CONDUCTORS AT THE HYBRID AG INSTALLATION IN BUCKLER RD. NOTE: THIS HAS BEEN THE SECOND OCCURENCE OF A TIPPER CONTACTING THE OVERHEAD LINE IN 12MONTHS AND WHILST IT IS NOT KNOWN WHETHER THE SAME VEHICLE/DRIVER/COMPANY WERE RESPONSIBLE FOR THE PREVIOUS INCIDENT, IT IS BELIEVED IT OCCURRED WITHIN THE SAME SPAN OF OVERHEAD CONDUCTOR. | Conductor (bare) | 0 | 0 | 0 |  | wn3 | Tipper truck contacted overhead HV line. | No Go Zone (contact) | 28/02/2018 11:31 |  |  | 9438 | Industrial |  | 20180308SPN_02 | Infrastructure (network-based) | -36.3314 | 146.368 | 1 | AusNet Services Distribution | Report | 11482 | 0.0098611 | 22kV AC | Wangaratta Aero | 3678 | North Wangaratta | Vehicle
CEOT dispatched a fault crew on 2 March 2018 to investigate and found evidence of a previous ground fire of 150 sq. metres in size. Construction crew re-sagged the single phase HV conductor line and lowered the aerial stay on the pole. | 480 COOPER STREET, EPPING VIC 3076 | 928777 |  |  |  | Not built/maintained to design |  | Phase to earth |  | IMS 232692. Initial Report: On 2 March 2018 CEOT received INCD for a grass fire at this address. Caller stated that it was caused by AusNet Services and that it was on 23rd February 2018. Advice from Bruce Phillips (Investigation Officer): There was no supply interruption on 23 February. Arcing at pole LIS 28777 caused by incorrect clearance between HV conductor and the aerial stay wire and a small grass fire of 50m x 30m in size resulted. The HV line was a slack bay and required re-sagging. Also, we do not know the time the grass fire started. Final Report: Arcing at pole LIS 28777 caused by in correct clearance between HV conductor and aerial stay wire resulted in a small grass fire of approximate size 50 m x 30 m. There is no investigation report available. All details are included in this OSIRIS incident record. Additional inclusion of the Plan of Information to the Notes and Findings tab. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | epg35 | Investigation has shown that the HV line has not been constructed as per any of the plans stored in our system. The pole stay was not lowered as per the work instruction when the HV line was extended. | Grassfire | 24/02/2018 6:59 | 1 | Small: 10 - 1000 sq.m | 9440 | Industrial |  | 20180308SPN_04 | Infrastructure (network-based) | -37.6467 | 144.9792 | 1 | AusNet Services Distribution | Report | 12843 | 0.018912 | 22kV AC | Essendon Airport | 3076 | Epping | Conductor
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. The local DAO was advised. Final report: CFA attended and extinguished fire. Line crew attended and took photos. DAO completed Investigation. Field crew to remove any remaining remnants of bird nest during planned ACR works on 09/02/18. | 25 MORRISON ROAD, BOWSER VIC 3678 | 5103947 |  | Bird |  |  |  | Phase to earth |  | Initial report: IMS 232756. Successful reclose on WN068. Report of fire in area. Final Report: CFA attended call to grass fire on the 07.03.18, ~9:17am and extinguished grass fire in vicinity of pole 5103947. Approximate area 50-100 sq. metres. Fault Crew attended site and witnessed remains of birds nest in ACR (WN068). No other damage. | Pole (concrete) | 0 | 0 | 0 |  | wn3 | Bird Incident | Grassfire | 43284.4431 | 1 | Small: 10 - 1000 sq.m | 9441 | Agricultural |  | 20180308SPN_05 | Infrastructure (network-based) | -36.316 | 146.3698 | 1 | AusNet Services Distribution | Report | 11488 | 0.0053715 | 22kV AC | Wangaratta Aero | 3678 | Bowser | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 2 ASQUITH STREET, BOX HILL SOUTH VIC 3128 | 7037441 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 1 | At 0607hrs on 01/03/2018, 22kV feeder BH 21 circuit breaker reclosed to lockout affecting 1075 customers. Following light rain after a lengthy dry spell, a HV intermediate cross arm fire occurred at pole No. LIS 7037441 located outside 2 Asquith Street. A HV conductor fell and made brief contact with the LV conductors and street light below and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Douglas-Station" substation. The LEI tested properties in the vicinity and confirmed that a high voltage injection did not occur. | Crossarm (wood) | 0 | 0 | 0 |  | BH 21 | Following light rain after a lengthy dry spell, a HV intermediate cross arm fire occurred. | Pole-top fire | 43103.2549 | 1 | Negligible: no ground fire | 9436 | Residential |  | 20180308UTD_03 | Infrastructure (network-based) | -37.8359 | 145.1212 | 1 | United Energy Distribution | Report | 11769 | 0.035958 | 22kV AC | Moorabbin Airport | 3128 | Box Hill South | Crossarm
The damaged krone box was replaced by a faults crew and supply restored to normal upon completion. | 4 GLEN EBOR AVENUE, BLACKBURN VIC 3130 | 7033760 |  | Animal |  |  |  |  | 2 | MFB reports that a box on the pole is on fire. A krone box attached to pole No. LIS 7033760 caught on fire due to a possum that was on the top of the LV krone box with tracking occurring. The possum was removed and "Morton Park- Glen Ebor" substation was placed under LV parallel and will be replaced in daylight tomorrow. | Connection box | 0 | 0 | 0 |  |  | Animal Incident | Pole-top fire | 43375.0035 | 1 | Negligible: no ground fire | 9444 | Roadway |  | 20180308UTD_04 | Infrastructure (network-based) | -37.8217 | 145.1575 | 1 | United Energy Distribution | Report | 12990 | 0.0074757 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. The HV powder filled fuse units were replaced with boric acid fuses. | 32 BARKLY STREET, MORDIALLOC VIC 3195 | 1807136 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | At 0521hrs on 01/03/2018, a HV termination cross arm failed and requires replacement. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 1807136 located in Barkly Street opposite Edith Street. The HV fuse units at "Barkly-Edith" pole type substation were tracking and caused the termination cross arm to burn through and fall down with the fuse unit still attached. No high voltage injection was suspected and an inspector wasn't required to investigate. | Crossarm (wood) | 0 | 0 | 0 |  | MC 02 | HV fuse units tracking to the cross arm during light rain after a long dry spell. | Pole-top fire | 43103.2229 | 1 | Negligible: no ground fire | 9446 | Roadway |  | 20180308UTD_05 | Infrastructure (network-based) | -38.0018 | 145.0873 | 1 | United Energy Distribution | Report | 13030 | 0.040993 | 22kV AC | Moorabbin Airport | 3195 | Mordialloc | Crossarm
Site made safe, section isolated by operator. HV crossarm replaced. | 83-85 MICKLEHAM ROAD, TULLAMARINE VIC 3043 | Pole no. A031140 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to tracking/electrical leakage Photos attached in "Notes and Findings" section | Crossarm (wood) | 0 | 0 | 0 |  | AW09 | Tracking/electrical leakage | Pole-top fire;Grassfire | 43103.3604 | 1 | Localised: less than 10 sq.m | 9450 | Roadway |  | 20180309JEM_01 | Infrastructure (network-based) | -37.6973 | 144.8805 | 1 | Jemena | Report | 13017 | 0.00091667 | 22kV AC | Essendon Airport | 3043 | Tullamarine | Crossarm
Site made safe. Line manually de-energised. Sub-transmission pole replaced. | 172-184 DYNON ROAD, WEST MELBOURNE VIC 3003 | Pole no. A010091 |  |  |  | Leakage |  |  | 2 | Sub-transmission pole and crossarm fire reported by MFB and Citipower No ground fire No photo is available | Pole (wood) | 0 | 0 | 0 |  | WMTS-FE2 | Tracking/electrical leakage | Pole-top fire | 43103.3021 | 1 | Negligible: no ground fire | 9451 | Roadway |  | 20180309JEM_02 | Infrastructure (network-based) | -37.8028 | 144.9291 | 1 | Jemena | Report | 11501 | 0.028642 | 66kV AC | Essendon Airport | 3003 | West Melbourne | Crossarm
It was established that the new overhead service to 27A will not meet the minimum boundary crossing requirements The crew did not complete the new connection to the dwelling because of the non-compliance and NGZ breach. A member of the Work Practices team member attended site to further investigate the NGZ breach. | 27A CHALLIS STREET, NEWPORT VIC 3015 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Jemenaâ€™s new connection contractor Zinfra, had attended 27A Challis St, Newport for connection of new overhead customer service supply. On arrival at the site, the crew had identified a No Go Zone breach by the builder with the construction of the new property to the neighbouring property service supply as per the attached photos (in the Notes and Findings section) The crew had advised their team leader of the NGZ breach, with only 600mm clearance from the new balcony and can be easily reached and touched by the future occupier of the new dwelling. For more information, please contact Nick Mateski from Jemena Works Practices on 0417339536 | Service conductor | 0 | 0 | 0 |  | NT03 | Factors identified by Work Practices attendance on site: â€¢ The work party did not have No Go Zone VESI Permit â€¢ The work party had failed to comply with Safe Approach Distances (SAD) â€¢ The building is developed by customer/owner builder which is his first time taking on this type of project â€¢ REC did not inform the customer/owner builder of the correct compliance for the correct outcome â€¢ The customer/owner builder was handed an Alteration/Relocation of Jemena Assets form to rectify the NGZ breach â€¢ Customer had acknowledged the cost of rectifying the NGZ breach at his own expense | No Go Zone (no contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43315.5 |  |  | 9457 | Residential |  | 20180309JEM_03 | Infrastructure (network-based) | -37.8465 | 144.8724 | 1 | Jemena | Report | 11507 | 0.008309 | Low voltage AC (<1kV) | Laverton Raaf | 3015 | Newport | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 678 MITCHAM ROAD, VERMONT VIC 3133 | 639555 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | At 0707hrs on 01/03/2018, the MFB advised of a pole on fire in Mitcham Road near the corner of Canterbury Road. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 0639555 located on the corner of Mitcham and Canterbury Roads. The HV insulator on the strain cross arm has burnt off and was on fire. | Crossarm (wood) | 0 | 0 | 0 |  | RWT 24 | A HV cross arm occurred following light rain after a lengthy dry spell. | Pole-top fire | 43103.2965 | 1 | Negligible: no ground fire | 9449 | Roadway |  | 20180309UTD_01 | Infrastructure (network-based) | -37.835 | 145.195 | 1 | United Energy Distribution | Report | 13032 | 0.028731 | 22kV AC | Moorabbin Airport | 3133 | Vermont | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 47 GOLF VIEW ROAD, HEATHERTON VIC 3202 | 1814372 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | At 0707hrs on 01/03/2018, the MFB advised of a pole on fire in Golf View Road on the corner of Henry Street. Following light rain after a lengthy dry spell, a cross arm fire occurred at the HV/LV tee-off pole (LIS 1814372) located on the corner of Golf View Road and Henry Street. | Crossarm (wood) | 0 | 0 | 0 |  | HT 10 | A pole fire occurred after light rain that followed a lengthy dry spell. | Pole-top fire | 43103.2965 | 1 | Negligible: no ground fire | 9452 | Roadway |  | 20180309UTD_02 | Infrastructure (network-based) | -37.9507 | 145.087 | 1 | United Energy Distribution | Report | 13033 | 0.0043345 | 22kV AC | Moorabbin Airport | 3202 | Heatherton | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 1 WENDY STREET, FOREST HILL VIC 3131 | 7033459 |  | Precipitation |  | Electrical breakdown;Leakage |  |  | 2 | At 0739hrs on 01/03/2018, a driver contacted the United Energy faults and emergency call centre advising that a strut on a pole located in Mount Pleasant Road approximately 300m from the Canterbury Road intersection is on fire. The pole is outside 1 Wendy St. Following light rain after a lengthy dry spell, a cross arm fire occurred at the HV/LV tee-off pole (LIS 7033439) located on the corner of Mount Pleasant Road and Fisher Street. The HV tee-off supplied "Wendy-Mount Pleasant" substation that was placed under LV parallel to maintain supply to customers whilst the HV cross arm was replaced. | Crossarm (wood) | 0 | 0 | 0 |  | NW 33 | A pole fire occurred after light rain that followed a lengthy dry spell. | Pole-top fire | 43103.3187 | 1 | Negligible: no ground fire | 9453 | Roadway |  | 20180309UTD_03 | Infrastructure (network-based) | -37.8324 | 145.1802 | 1 | United Energy Distribution | Report | 13034 | 0.019119 | 22kV AC | Moorabbin Airport | 3131 | Forest Hill | Crossarm
On arrival crew examine conductor, no visual damage found. | 170 GOLDSBURY ROAD, COPE COPE VIC 3480 | 32020115 | Working too close to overhead lines | [5 empty] | 1 | A Powercor fault crew attending an outage found that a vehicle contacted HV Swer conductor at the incident location. Protection operated. There were no injuries, fire or third-party damage. | Conductor (bare) | 2 | 2 | 2 |  | CTN006 | Tip truck struck conductors | Loss of supply;No Go Zone (contact) | 43347.4653 |  |  | 9655 | Agricultural |  | 20180410PWA_01 | Infrastructure (network-based) | -36.4831 | 143.0897 | 1 | Powercor | Report | 11826 | 0.014391 | 12.7kV AC (SWER) | Horsham Aerodrome | 3480 | Cope Cope | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor at the Reticulation Service Pole, The attending Powercor Fault Crew reterminated the existing O/Head Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 6 FISHER STREET, WARRNAMBOOL VIC 3280 | 32198131 |  |  |  | Corrosion |  | Phase to earth |  | Ms Sarah Drylie was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WBL004 | corroded connection | Minor shock | 15/02/2018 19:00 |  |  | 9657 | Residential |  | 20180410PWA_03 | Infrastructure (network-based) | -38.396 | 142.47 | 1 | Powercor | Report | 11831 | 0.025804 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Voltage tests were conducted between an independent earth and various points of the electrical installation, including the distribution assets, revealed a defective service neutral conductor termination at the FOLCB. Attending service crew removed the old service cable then fitted a new service cable and replaced the neutral terminal screw clamps on the FOLCB. An NST test carried out by LEI Result passed and installation was left on supply. | 95 STEPHEN STREET, YARRAVILLE VIC 3013 |  |  |  |  | Neutral fault |  |  |  | Customer received minor electric shock from shower taps whilst showering. | Connection box | 0 | 2 | 0 |  |  | Corroded neutral termination at FOLCB. | Minor shock | 43408.6847 |  |  | 9669 | Residential |  | 20180411JEM_01 | Infrastructure (customer connection) | -37.8158 | 144.8947 | 1 | Jemena | Report | 11845 | 0.024028 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Connection
The site was made safe and the cable was isolated until repairs could be made. | HACKETTS ROAD, POINT COOK VIC 3030 | 33073497 | Working too close to underground cables | [6 empty] | A civil contractor reported that they had contacted an underground cable with an excavator at the incident location, there were no sparks but some they saw smoke coming from the cable. On arrival the crew found that a worker from Symon Brothers Constructions (ph. 0394602888) was operating an excavator and contacted a LV underground service cable causing damage to the cable. There were no civil workers on site when the crew arrived and found the damaged cable live and exposed in the trench. There was no ground fire and no injury as a result of this incident. | Cable | 2 | 2 | 2 |  | WBE013 | Excavation work | No Go Zone (contact);Damage to network assets | 43103.7222 |  |  | 9664 | Public space |  | 20180411PWA_04 | Infrastructure (network-based) | -37.8795 | 144.719 | 1 | Powercor | Report | 11838 | 0.028943 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
CEOT dispatched a fault crew to make safe and investigate. The crew found a burnt LV fuse isolator was the cause. Construction crew requested to replace LV fuse isolator. | 106 DUFFYS ROAD, NARRE WARREN EAST VIC 3804 | 523041 |  |  |  | Overheated connection |  |  |  | IMS 232690. CEOT received INCD call for a Pole Fire. LV fuse isolator on a substation pole had a poor connection. NO PHOTOS WERE TAKEN. | Any other type | 0 | 0 | 0 |  | bge12 | Poor LV (high impedance) connection at LV fuse isolator. | Other electricity related | 43134.7174 | 1 | Negligible: no ground fire | 9668 | Other | MMBW station | 20180411SPN_01 | Infrastructure (network-based) | -37.9707 | 145.3872 | 1 | AusNet Services Distribution | Report | 11850 | 0.01687 | Low voltage AC (<1kV) | Moorabbin Airport | 3804 | Narre Warren East | Connection
The crew made the site safe, and restored supply. | 55 DOOKIE STREET, DOOKIE VIC 3646 | 33090594 |  |  |  | Unknown technical factor |  |  |  | A customer, Suzanne Hall advised a wire had come down and resulted in fire on the nature strip. On arrival the crew found that a catenary and service cable had faulted and come to ground. This caused a ground fire of approximately 10m X 5m. There was no injury or third party damage reported. | Service conductor | 2 | 2 | 2 |  | STN024 | service cable faulted, reason not found | Grassfire | 43438.3764 | 1 | Small: 10 - 1000 sq.m | 9677 | Public space |  | 20180412PWA_07 | Infrastructure (network-based) | -36.3313 | 145.6867 | 1 | Powercor | Report | 12300 | 0.024709 | Low voltage AC (<1kV) | Shepparton Airport | 3646 | Dookie | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral connection in the Pole Type Connection Box located at the Reticulation Service Pole The attending Powercor Fault Crew replaced the existing Pole Type Connection Box located at the Reticulation Service Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 5 MACS STREET, PETERBOROUGH VIC 3270 | 30045978 |  |  |  | Corrosion |  | Phase to earth |  | Ms Sally Towell was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet whilst standing on the wet shower base. | Connection box | 2 | 2 | 2 |  | TRG005 | Corroded neutral connection | Minor shock | 43193 |  |  | 9683 | Residential |  | 20180413PWA_05 | Infrastructure (network-based) | -38.6072 | 142.8784 | 1 | Powercor | Report | 11865 | 0.021668 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3270 | Peterborough | Connection
Supply isolated on arrival and repaired conductors. | 12 LYNCH ROAD, BROOKLYN VIC 3012 |  |  | Blown branch/vegetation |  | Conductor clashing |  |  | 2 | Strong winds caused tree branch to fall into the low voltage conductors causing then to fall to the ground. | Conductor (bare) | 2 | 2 | 2 |  |  | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/04/2018 14:29 |  |  | 9686 | Roadway |  | 20180414JEM_03 | Infrastructure (network-based) | -37.8239 | 144.8398 | 1 | Jemena | Report | 11868 | 0.024046 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Trees
Site made safe (exposed cable ends were made safe). Seven sections of underground cable replaced between pole to pit. | 2 OLD RIDDELL ROAD, SUNBURY VIC 3429 | A136725, A136726, A136727, A136728, A136729, A136730, A136731, A136732 | Copper theft | [5 empty] | 2 | Underground public lighting cable stolen between eight (8) public street light poles. | Services cable | 0 | 0 | 0 |  |  | Vandals stole underground cable from eight (8) public street light poles. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/04/2018 16:37 |  |  | 9687 | Roadway |  | 20180415JEM_01 | Infrastructure (network-based) | -37.5555 | 144.7012 | 1 | Jemena | Report | 11869 | 0.023282 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Jemena attended and assessed the situation, and organised for repairs to be made | 30 CRAIG STREET, SPOTSWOOD VIC 3015 |  | Working too close to overhead lines |  |  |  | Followed but inappropriate;Ineffective planning/procedures/processes |  | 2 | No Go Zone infringement outside 30 Craig St in Spotswood. Excavator contacted aerial earth wire, which snapped and fell to the ground. Photos attached in "Notes & Findings" section | Conductor (bare) | 0 | 0 | 0 |  | NT10 | Third-party excavator infringed limits of approach | No Go Zone (no contact) | 16/04/2018 11:27 |  |  | 9696 | Industrial |  | 20180416JEM_01 | Infrastructure (network-based) | -37.832 | 144.8905 | 1 | Jemena | Report | 11879 | 0.034637 | Earthing cable | Essendon Airport | 3015 | Spotswood | Vehicle
On arrival crew isolated supply and carried out repairs. | 444 COWANNA AVENUE, MERBEIN VIC 3505 | 32145013 |  |  |  | Leakage |  |  |  | Customer called reporting a pole fire at the incident location. On arrival the crew found that a wooden termination cross-arm failed due to fire damage at the bridging insulator / disc string hardware mounting points, the overhead conductor remained suspended held up by the bridge. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | MBN031 | Excessive leakage current | Pole-top fire | 14/04/2018 19:31 | 1 | Negligible: no ground fire | 9695 |  |  | 20180416PWA_05 | Infrastructure (network-based) | -34.1758 | 142.0314 | 1 | Powercor | Report | 11878 | 0.016238 | 22kV AC | Mildura Airport | 3505 | Merbein | Crossarm
On arrival crew isolated supply and carried out repairs. | 132 STRADBROKE AVENUE, SWAN HILL VIC 3585 | 30101023 |  |  |  | Leakage |  |  | 1 | SCADA alarm for SHL008 feeder lockout initiated a fault crew investigating the outage cause, discovering a pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a cross-arm strap resulting in the conductor falling onto the LV circuit below, contacting the red phase. There was no ground fire, no reported injuries, no 3rd party damage, no evidence of HV injection was found by LEI. | Crossarm (wood) | 2 | 2 | 2 |  | SHL008 | Excessive leakage current | Pole-top fire | 14/04/2018 15:30 | 1 | Negligible: no ground fire | 9698 |  |  | 20180416PWA_07 | Infrastructure (network-based) | -35.3395 | 143.551 | 1 | Powercor | Report | 11881 | 0.037884 | 22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Pole
CEOT dispatched a fault crew to make safe, investigate and repair. The crew replaced the damaged LV cross arm and all pin insulators. Checked all other assets on the pole. | 1 MAIN STREET, PAKENHAM VIC 3810 | 500606 |  | Precipitation |  | Leakage |  |  |  | IMS 232880. POLE FIRE ON INTERMEDIATE POLE LIS 50606 DUE TO TRACKING ON LV XARM. Fault crew were called to a pole fire which was caused by tracking on LV cross arm due to faulty pin insulator and build up of dust. Drizzle weather conditions prevailed. NO PHOTOS WERE TAKEN. | Crossarm (wood) | 0 | 0 | 0 |  | phm32 | Burnt LV cross arm due to voltage / current tracking from polluted LV insulator | Pole-top fire | 18/03/2018 11:59 | 1 | Negligible: no ground fire | 9706 | Residential |  | 20180417SPN_02 | Infrastructure (network-based) | -38.0723 | 145.4759 | 1 | AusNet Services Distribution | Report | 12832 | 0.035963 | Low voltage AC (<1kV) | Moorabbin Airport | 3810 | Pakenham | Crossarm
On arrival crew isolated supply and carried out repairs. | 161 AUSTRALIS DRIVE, DERRIMUT VIC 3030 | 30266247 |  | Precipitation |  | Moisture ingress |  |  |  | Customer called to advise Rain went into pit and caught on fire. It is still on fire. No supply. There was no reported ground fire, injury or shocks as a result of this incident. | Services pit | 2 | 2 | 2 |  | TNA024 | Moisture ingress | Other electricity related | 24/03/2018 10:21 | 1 | Negligible: no ground fire | 9714 | Public space |  | 20180418PWA_06 | Infrastructure (network-based) | -37.8046 | 144.7637 | 1 | Powercor | Report | 11899 | 0.010653 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Derrimut | UG Cable
On arrival crew carried out repairs to earthing system. | 12 STRATHTULLOH CIRCUIT, STRATHTULLOH VIC 3338 | 33104473 | Copper theft | [6 empty] | Whilst Powercor Fault-Crew where working in the area after a storm and a number of faults, it was discovered that the earth cable appears to have been stolen @ Strathtulloh P18,. There were no reported shockâ€™s, injuries, fire or third party damage as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 24/03/2018 18:31 |  |  | 9718 | Roadway |  | 20180418PWA_09 | Infrastructure (network-based) | -37.7452 | 144.597 | 1 | Powercor | Report | 11905 | 0.033031 | Earthing cable | Laverton Raaf | 3338 | Strathtulloh | Other
On arrivae crew isolated supply and carried out repairs | 145 FORD ROAD, GRAHAMVALE VIC 3631 | 33088530 |  | Bird |  |  |  |  | 1 | Customer rang to advise he heard a loud bang and reports ground fire at the incident location. There was a reclose of the SHTS-STN 66kV line at that time. A crew attended and found a 3mx3m grass fire had start at the base of S/S P13 Ford Tie S/L, Fire had self-extinguished when crew arrived. Crew advise a pair of birds had flashed over on the 66kV pole SHTS-STN P9 on the cnr of Verney Rd and Ford Rd, resulting in a HVI into a street lighting CCT that was fed from the Ford Rd P13 S/S. This flash over caused damage to a 66kV insulator on P9, 9 damaged street lights and a melted fuse box on P13, that started the ground fire An LEI attended. No damage to customer installation identified. The crew replaced the fuse box and left the street lighting CCT off supply awaiting repairs. Damaged 66kV insulator listed for replacement. There were no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | SHTS-STN | Bird Incident | Grassfire | 19/04/2018 14:23 | 1 | Localised: less than 10 sq.m | 9725 | Roadway |  | 20180420PWA_01 | Infrastructure (network-based) | -36.3475 | 145.4174 | 1 | Powercor | Report | 12097 | 0.040471 | Low voltage AC (<1kV);66kV AC | Shepparton Airport | 3631 | Grahamvale | Animal
Supply isolated to make safe. Repairs were made to HV conductor as soon as practicable. Failed assets were quarantined for investigation. | 252 PASCOE VALE ROAD, ESSENDON VIC 3040 | Pole no. A110870 |  |  |  | Age;Earth fault | Followed but inappropriate;Poor or no communication |  | 1 | HV conductor fell down to ground due to parallel groove (PG) clamp connector failure at a weak point, which was triggered by a fault current passing through it. The fault current was triggered by a switching error (refer to the "Cause" section for details). Protection operated correctly according to design in response to the primary and secondary faults, therefore the HV conductor was de-energised when it fell to ground and did not pose a safety risk to the public. Photos attached in "Notes & Findings" section | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | NS07 | A fault current triggered a failure at a weak point in parallel groove (PG) clamps connector, which subsequently led to the secondary consequence of HV conductor falling to ground. Note that all assets installed on the network according to design and construction standard (applicable at the time) are designed to be able to withstand continuous load current (normal rating) and short duration fault current (short circuit rating). PG clamps are recognised by Jemena asset class strategy as unreliable non-tension connectors and Jemena has not installed any new PG clamps on the HV system since Ampact fired wedge connectors were rolled out. The failed PG clamp is believed to be over 20 years old. As per Jemena's asset class strategy, bulk replacement of PG clamps on the HV system with Ampact connectors shall be undertaken where fault mapping and cost benefit analysis shows this to be economically viable. This program proactively replaces non-tension connectors in the backbone of HV feeders and at the start of feeders based on fault history and fault level considerations. The investigation concluded that the deteriorated PG clamp was unlikely to have been picked up by routine asset inspection. It also determined that there was no outstanding thermal survey notification associated with the failed PG clamp. The last survey was conducted in December 2015 and the next one is due in November 2018. The fault current was caused by a switching error in Carlyle Street, Essendon where the work crew were unable to remove an Earth & Short Circuit (E&SC) and needed to reposition the MEWP to remove it. The electrical network operator did not confirm all earths had been removed prior to restoration of supply. Refer to the HSE Alert attached in "Notes & Findings" section. | Loss of supply | 22/04/2018 15:37 |  |  | 9729 | Roadway |  | 20180422JEM_01 | Infrastructure (network-based) | -37.7511 | 144.9255 | 1 | Jemena | Report | 11968 | 0.018464 | 11kV AC | Essendon Airport | 3040 | Essendon | Connection
The Attending LEI tested all metalic and earthed components of the property including the metalic pipes originating from the customers premises and recorded a voltage of 2 volts AC under normal load conditions. The same voltage tests were conducted under loaded conditions, which revealed a rising voltage of >13 Volts AC. An NST test was conducted which returned a FAIL result. Jemena lines crew replaced the existing overhead service, checked all connections and performed all mandatory tests. Following rectification works, the attending LEI performed all subsequent voltage tests including at the point of contact which returned a pass result. An NST was performed, a PASS result was obtained. Supply was left ON. | 21 WINGATE AVENUE, ASCOT VALE VIC 3032 |  |  |  |  | Neutral fault |  |  | 2 | Melbourne Water plumbers were working on water pipes located in the nature strip. The plumber working on the metallic pipes received an electric shock when he made contact with the metallic pipe and direct contact with the general mass of earth. The plumber who had received the electric shock was not on-site at the time of investigation and was not contactable. | Service conductor;Neutral screen | 2 | 2 | 2 |  |  | Faulty service. | Minor shock | 23/04/2018 13:43 |  |  | 9733 |  |  | 20180423JEM_01 | Infrastructure (network-based) | -37.7794 | 144.9177 | 1 | Jemena | Report | 11924 | 0.039397 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | UG Cable
A voltage test between the tap and the conductive metallic shower screen resulted with 24 Volts and various points of the installation with reference to an independent earth including the distribution assets revealed the service neutral conductor was damaged. Powercor linesman replaced the service & CTA carried out N.S.T & Voltage tests following the replacement and normal results were obtained. | 5 LYNCH STREET, SUNSHINE VIC 3020 | 30110818 |  |  |  | Corrosion |  | Phase to earth |  | Naseem received an electric shock when she simultaneously contacted the metallic tap with one hand and the metallic shower base trap with her foot. | Service conductor | 2 | 2 | 2 |  | SSE032 | Corroded connection at poa | Minor shock | 23/03/2018 13:30 |  |  | 9731 | Residential |  | 20180423PWA_02 | Infrastructure (customer connection) | -37.7806 | 144.8344 | 1 | Powercor | Report | 11921 | 0.041098 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Connection
CEOT dispatched a fault crew sent to make safe, investigate and carry out/arrange for any necessary repairs. | 4 FORGE CREEK ROAD, EAGLE POINT VIC 3878 | 1610710 |  | Bird |  |  |  | Phase to earth |  | IMS 233328. Initial Report: CEOT received a call from Fire Brigade for fire at base of a pole. A magpie caused a flashover on a BA fuse unit. Final Report from attending DAO: A dead Magpie was found at the base of a pole and there were burn marks at the top of BA fuse and the pole. Magpie dead on the ground. HV fuses did not blow, no loss of supply. There was also a small grass fire in the vicinity of the base of the pole. | Pole top;Boric acid | 0 | 0 | 0 |  | BDL42 | Bird Incident | Grassfire | 24/04/2018 11:03 | 1 | Localised: less than 10 sq.m | 9738 | Residential |  | 20180426SPN_01 | Infrastructure (network-based) | -37.8919 | 147.6758 | 1 | AusNet Services Distribution | Report | 12857 | 0.012719 | 22kV AC | Bairnsdale Airport | 3878 | Eagle Point | Animal
A LEI and faults truck attended and completed a NST that passed. With a load of 20amps applied, 0.6v was measured on the neutral and also between the shower taps to an independent earth. The faults crew cleaned and greased all connections at the POA and 0.4v was measured to the neutral and to the shower taps. The cause was attributed to a slightly corroded neutral connection at the POA. The customer was advised of findings. | 17 TAMMANY DRIVE, CLARINDA VIC 3169 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Caller reports that an electric shock was received from a tap in the bathroom and the lights are flickering. The occupier received a slight electric shock from a shower tap and has noticed the recent constant flickering lights and contacted the United Energy faults and emergencies call centre. She also advised that a noise could be heard at the front of the house. | Customer installation | 0 | 0 | 0 |  |  | The cause was attributed to a slightly corroded neutral connection at the POA. | Minor shock | 30/03/2018 12:10 |  |  | 9740 | Residential |  | 20180426UTD_01 | Infrastructure (customer connection) | -37.944 | 145.0998 | 1 | United Energy Distribution | Report | 11934 | 0.00964 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clarinda | Connection
A faults crew attended, made the site safe and completed repairs. Upon completion, supply was restored to customers supplied from "Balcombe-Safeway Co" Indoor substation. At 9.15AM, a phone call was received from Rosemary Burrell (wife of cyclist â€“Malcolm) who reported that her husband was injured earlier in the morning when his bicycle hit the broken red phase LV conductor that got caught up in his handle bars and he fell of his bicycle resulting in broken bones. She mentioned that her injured husband was transported to hospital by ambulance. The United Energy Customer Relations Manager made contact with the injured cyclists wife and they exchanged contact details. It was mentioned during this conversation that the cyclist had a broken leg and collar bone and will be remaining in hospital for treatment. There was no formal investigation to the cause of the fallen conductor. Photos are attached that demonstrates the overhang of the LV red phase conductor over the road way outside the Woolworths store. | 105-111 BALCOMBE ROAD, MENTONE VIC 3194 | 1820428 & 3444804 |  |  |  | Mechanical breakdown |  |  | 1 | The MFB reports there are wires down outside this address and a trouble order was previously created for a unplanned low voltage outage to customers supplied from "Balcombe-Safeway Co" Indoor substation. A LV midspan joint failed between pole numbers LIS 1820428 and 3444804 located outside 105 Balcombe Road, Mentone that resulted in the red phase LV conductor to fall de-energised to the ground. | Conductor (bare);Copper | 0 | 0 | 0 |  |  | A LV midspan connection failed between pole numbers LIS 1820428 and 3444804 located outside 105 Balcombe Road, Mentone. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43224.2708 |  |  | 9745 | Roadway |  | 20180426UTD_04 | Infrastructure (network-based) | -37.9812 | 145.0625 | 1 | United Energy Distribution | Report | 11961 | 0.0081262 | Low voltage AC (<1kV) | Moorabbin Airport | 3194 | Mentone | Connection
On arrival crew isolated supply and rep[laced transformers | 1360 BLACKGATE ROAD, FRESHWATER CREEK VIC 3217 | 30067860 |  | Lightning | [5 empty] | A customer called regarding a supply interruption. The crew attended and found failed transformers in the area. Harrison Fâ€™Water Ck transformer had been hit by lightning and this resulted in a ground fire. The fire was approximately 1 X 2 meters. No injury or third party damage had occurred. | Pole mounted;Transformer | 2 | 1 | 2 |  | WPD014 | Lightning strike | Grassfire | 24/04/2018 15:39 | 1 | Localised: less than 10 sq.m | 9753 | Roadway |  | 20180427PWA_02 | Infrastructure (network-based) | -38.2764 | 144.2428 | 1 | Powercor | Report | 11950 | 0.015144 | 22kV AC | Avalon Airport | 3217 | Freshwater Creek | Lightning
A LEI attended and commenced to test the installation and only 191v was measured on the incoming supply. The LEI went to the neighbouring property and 191v was also measured. A faults crew was re-directed from faults as there was high fault activity at the time and a HV fuse had operated at the HV spur fusing at DN7439 located in Simpsons Drive. The white phase HV boric acid fuse was replaced and affected occupancy was re-tested that confirmed the fault had been rectified. | 44 JARVIS CRESCENT, DANDENONG NORTH VIC 3175 |  |  | Blown branch/vegetation |  |  |  | Phase to earth | 1 | The occupier noticed the recent dimming of lights and an electric shock was received from the kitchen kettle. There was high winds and rain at the time of the fault. | Boric acid | 0 | 0 | 0 |  | LD 04 | A HV fuse had operated that caused a fluctuating voltage. | Minor shock | 14/04/2018 9:40 |  |  | 9757 | Residential |  | 20180427UTD_07 | Infrastructure (network-based) | -37.9678 | 145.2216 | 2 | United Energy Distribution | Report | 11954 | 0.031002 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong North | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was temporarily replaced under Access Authority conditions. The pole requires urgent replacement and it was recommended the GFB switch is replaced with a manual gas switch that was completed later this day. | 1300 NEPEAN HIGHWAY, CHELTENHAM VIC 3192 | 1822160 |  | Precipitation |  | Leakage |  |  | 2 | Caller reports the high voltage pole top is burning. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 1822160 located outside 1300 Nepean Highway, Cheltenham. The HV glass disc insulators for the centre and road side phases had been tracking on the wet pole and burnt out a large hole under the GFB switch (CH8926). | Pole (wood) | 0 | 0 | 0 |  | M 23 | A pole fire occurred during light rain after a lengthy dry spell, | Pole-top fire | 14/04/2018 13:07 | 1 | Negligible: no ground fire | 9763 | Roadway |  | 20180430UTD_03 | Infrastructure (network-based) | -37.972 | 145.0623 | 1 | United Energy Distribution | Report | 13061 | 0.04113 | 11kV AC | Moorabbin Airport | 3192 | Cheltenham | Crossarm
The faults crew proceeded to replace the single phase overhead service and a damaged FOLCB at the service pole before supply was restored. | 1 NASHS LANE, RED HILL VIC 3937 |  |  | Wind;Alive;Council |  |  |  |  | 2 | Caller reports they have lost their electricity supply. During strong winds, a council tree has brought down the single phase overhead service outside 1 Nashs Lane, Red Hill. The service fell down alive and when the faults crew arrived on site, unknown persons had removed the live service from the road way. No shocks or injuries were reported. | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/04/2018 13:15 |  |  | 9765 | Roadway |  | 20180430UTD_05 | Infrastructure (network-based) | -38.3731 | 145.0207 | 1 | United Energy Distribution | Report | 11966 | 0.032843 | Low voltage AC (<1kV) | Moorabbin Airport | 3937 | Red Hill | Trees
A LEI and faults truck attended and met the Woods Group REC who received the shock. Supply was isolated immediately to the cabinet due to the neutral service conductor coming away from the LV reticulation at pole number LIS 2329559. The faults crew cleaned, greased and re-terminated the neutral connection at the pole end and a NST was completed that passed with 0v recorded between and independent earth to cabinet frame and the customers earthing system. The customer was left on supply - Unmetered supply. | 161 HUNTINGDALE ROAD, OAKLEIGH EAST VIC 3166 | 2329559 |  |  |  | Neutral fault |  | Phase to earth | 2 | Harry from the Wood Group called to report that he received an electric shock from the distribution board at the Yarra Valley Water flow cabinet. Woods Group were completing maintenance work on the Yarra Valley Water flow water cabinet located in the nature strip outside 161 Huntingdale Road and the REC received an electric shock to his hand from the cabinet enclosure. | Service conductor | 0 | 0 | 0 |  |  | The cause was due to the neutral service conductor coming away from the LV reticulation. | Minor shock | 23/04/2018 11:00 |  |  | 9770 | Roadway |  | 20180501UTD_01 | Infrastructure (network-based) | -37.8984 | 145.1056 | 1 | United Energy Distribution | Report | 11972 | 0.014833 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh East | Connection
A faults truck attended and replaced the damaged single phase service. Installation tests were completed and supply was left on. | 5 YORK AVENUE, BALNARRING VIC 3926 | 1106688 |  | Precipitation;Wind;Alive |  |  |  |  | 2 | Customer advised that a branch come into contact with the electricity cable for the house and there was fire evident on the wire and not on the branch. The customer has turned off the main switch. During strong winds and rain, a private tree branch was rubbing on the single phase overhead service that caused the tree voltage to catch fire. | Service conductor | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Other vegetation | 43346.341 | 1 | Negligible: no ground fire | 9773 | Residential |  | 20180501UTD_03 | Infrastructure (network-based) | -38.3819 | 145.1243 | 1 | United Energy Distribution | Report | 13037 | 0.0077824 | Low voltage AC (<1kV) | Moorabbin Airport | 3926 | Balnarring | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | AUSTIN RESERVE, 217R AUSTIN ROAD, SEAFORD VIC 3198 | 3307951 |  | Blown branch/vegetation |  |  |  |  | 1 | The MFB reports that a transformer is on fire in Henry Crescent on the corner of Austin Road. During strong winds and rain, a tree branch from Austin Reserve was blown onto the transformer at "Austin-Henry" pole type station that caused a HV 16amp powder filled fuse to operate. In addition, the HV bushing cover was melted and a HV fuse unit was damaged that caused a flashover. | Dropper/bridge | 0 | 0 | 0 |  | FTN 12 | Vegetation: Trees Incident | Pole-top fire | 24/03/2018 11:10 | 1 | Negligible: no ground fire | 9781 | Roadway |  | 20180502UTD_02 | Infrastructure (network-based) | -38.1072 | 145.1525 | 1 | United Energy Distribution | Report | 13054 | 0.030351 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Trees
Crew attended and made safe Underground cable isolated, for follow up repairs Cross-arm on struck pole replaced | 144 FITZGERALD ROAD, LAVERTON NORTH VIC 3026 | 30112356 | Vehicle |  |  | Overheated connection |  |  | 1 | Truck contacted pole and ground fire some distance away was attributed to fault current damage. A ground fire was reported at the address in this report and crews found a HV cable termination requires repair. A separate report of a truck contacting a pole, twisting cross-arm and dislodging conductor was also received . This pole is on the same feeder and downstream of the ground fire location by some 2.1 Km. | Conductor (bare);Cable | 0 | 0 | 0 |  | LVN034 | Vehicle contacted pole and resultant fault current damaged line. | Loss of supply;Grassfire | 43136.1458 | 1 | Small: 10 - 1000 sq.m | 9785 | Roadway |  | 20180503PWA_01 | Infrastructure (network-based) | -37.8215 | 144.7868 | 1 | Powercor | Report | 11991 | 0.017497 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
A faults truck attended and contacted United Energy after a unsafe situation was found as the home had been demolished and the POA and meter was laying on the ground with the live single phase XLPE overhead service resting on a timber pole. A United Energy representative attended the site and when questioned, a young builder who was on site cutting up hard wood mentioned it was his builder uncle who did the house demolition and he completes all of the abolishment work himself. A review of United Energy systems shows that no abolishment request had been received. Photos were taken that demonstrated the serious risk to public safety that had been created. | 2 INGRAM AVENUE, GLEN WAVERLEY VIC 3150 |  | Working too close to overhead lines;Unauthorised work | [5 empty] | 2 | Caller reported the service connecting to the property has detached from the POA and isn't sure how it has happened. The house is being demolished and access is okay. Michael called the United Energy faults and emergencies call centre of a wire down after the home has been demolished. He wasn't sure how it happened but must have occurred last night. No shocks or injuries have been received. | Service conductor;Aluminium | 0 | 0 | 0 |  |  | Incorrect abolishment of the home that created an unsafe situation. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43164.3333 |  |  | 9789 | Residential |  | 20180503UTD_02 | Infrastructure (network-based) | -37.8837 | 145.1659 | 1 | United Energy Distribution | Report | 11996 | 0.039979 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Glen Waverley | Other
On arrival crew isolated supply and carried out repairs | 205 HADDON SCHOOL ROAD, HADDON VIC 3351 | 32013728 |  |  |  | Overheated connection |  |  |  | A report was received from a customer of sparks coming from our pole at the above location. On arrival the crew found that the 100A FOLCB had overheated and caught fire. Molten plastic and metal had dropped to the ground and caused a small grass fire which burnt an area 5 x 1 metres. The CFA were onsite and had extinguished the fire. There was no injury, shock or third party damage. | Connection box | 2 | 2 | 2 |  | BAS011 | Connection failure | Grassfire | 43256.7431 | 1 | Localised: less than 10 sq.m | 9796 | Agricultural |  | 20180507PWA_01 | Infrastructure (network-based) | -37.5982 | 143.694 | 1 | Powercor | Report | 12008 | 0.015366 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Haddon | Connection
CEOT dispatch a fault crew to make safe, isolate supply, investigate and arrange for UG crew to repair. Incd 172628-r cable to be repaired tomorrow Tuesday 1st May emailed Graeme Vernon and Damage Recovery. | 113 OBAN ROAD, RINGWOOD NORTH VIC 3134 |  | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | IMS 233463. Initial Report: Contact with UG HV cable ex RWN32 o/s 113 Oban Rd, Tina Carindi, HESQ contact for Multinet Gas (0400 917254). (CEOT created a late incident record in IMS on 4 May). Final report: A Backhoe hit an UG HV cable o/s 113 Oban Rd, HV cable damage, notification send to UG crew for repair. Tina Carindi HSEQ for Multinet Gas (Comdain Infrstructure), tel 0400917254. AusNet Services CEOT Incident No. 172628-r. HV cable to be repaired tomorrow Tuesday 1st May. Damage Recovery advised. TC 6305298787 - Caller reports that during gas works they have dug 2 holes near this premises. After returning to the first hole they found arcing. Also reports that areas of streetlights went out as arcing happened. Protection operation followed by isolation of faulted section. | Cable | 0 | 0 | 0 |  | rwn32 | UG HV cable contacted by a gas pipe contractor. | No Go Zone (contact) | 30/04/2018 14:28 |  |  | 9792 | Residential |  | 20180507SPN_01 | Infrastructure (network-based) | -37.7942 | 145.2372 | 1 | AusNet Services Distribution | Report | 12004 | 0.0069282 | 22kV AC | Moorabbin Airport | 3134 | Ringwood North | Dug up
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | RUTHERFORD ROAD, SEAFORD VIC 3198 | 3307585 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 0711hrs on 04/05/2018, 22kV feeder CRM 13 circuit breaker reclosed to lockout affecting 130 customers. A truck contacted a stay wire at pole No. LIS 3307590 on the corner of Rutherford Road and Oliphant Street that caused the feeder protection to lockout when the conductors clashed. Following a patrol, the feeder was re-energised and a HV connection failed at pole No. LIS 3307585 located in Rutherford Road on the corner of Keppler Circuit causing a HV conductor to fall to the ground. The HV conductor made brief contact with a LV conductor below and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the west circuit of "Rutherford-Stephenson" substation. The LEI confirmed a high voltage injection occurred (BWD 1809) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Guy wire | 0 | 0 | 0 |  | CRM 13 | A truck contacted a stay wire on the corner of Rutherford Road and Oliphant Circuit that caused conductors to clash. | HV injection;Loss of supply | 43195.2993 |  |  | 9795 | Roadway |  | 20180507UTD_02 | Infrastructure (network-based) | -38.0989 | 145.1508 | 1 | United Energy Distribution | Report | 12007 | 0.016118 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Vehicle
A LEI and faults truck attended and tested between an independent earth to the bathroom sink and nearby plumbing with a voltage of 20.7v measured. A NST was completed that failed. The faults crew checked connections at the POA and found the neutral conductor has broken away inside the consumers MJB. The neutral connection was cleaned, greased and re-terminated and the LEI and faults crew completed further installation tests that confirmed the fault had been rectified. Supply was left on. | 7 LEO STREET, BENTLEIGH EAST VIC 3165 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Caller reports of intermittent supply as the appliances have been surging and going on and off. He advised that an electric shock was also received when cleaning his teeth this morning. The occupier noticed the electricity supply was intermittent with appliances not working correctly and an electric shock was received from the bathroom tap. | Customer installation | 0 | 0 | 0 |  |  | Corroded neutral connection at thePOA. | Minor shock | 43256.4167 |  |  | 9799 | Residential |  | 20180507UTD_04 | Infrastructure (customer connection) | -37.9261 | 145.0621 | 1 | United Energy Distribution | Report | 12011 | 0.03224 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Connection
On arrival crew isolated supply and carried out repairs. | 2126 LODDON RIVER ROAD, APPIN SOUTH VIC 3579 | 32037296 |  |  |  | Leakage |  |  | 1 | All supply failure reported, crew attended at incident location. They walked an inaccessible area and found SWER Intermediate Pole 6 Appin South had burnt off. An area of 100m Square was reported as burnt. There was no reported shocks, no injuries reported. No CFA in attendance. | Pole (wood) | 2 | 2 | 2 |  | KGT004 | Excessive leakage current | Grassfire | 43195.4222 | 1 | Small: 10 - 1000 sq.m | 9803 | Agricultural |  | 20180508PWA_01 | Infrastructure (network-based) | -35.9399 | 143.8584 | 1 | Powercor | Report | 12019 | 0.038392 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3579 | Appin South | Conductor
CEOT DISPATCHED A FAULT CREW TO MAKE SAFE AND INVESTIGATE. CREW MADE SAFE AND REPLACED EDO FUSE WITH A 10 AMP FUSE. | 1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984 | 519170 |  |  |  | Candled fuse |  |  |  | IMS 233053. CANDLED EDO FUSE AT SWITCH BW1236. | EDO fuse | 0 | 0 | 0 |  | LLG11 | Burnt EDO fuse tube. | Other electricity related | 28/03/2018 8:44 | 1 | Negligible: no ground fire | 9806 | Agricultural |  | 20180508SPN_03 | Infrastructure (network-based) | -38.2517 | 145.6579 | 1 | AusNet Services Distribution | Report | 12930 | 0.036462 | 22kV AC | Moorabbin Airport | 3984 | Lang Lang East | Fuse
The crew made the site safe and the pole was replaced | 350 POGUE ROAD, TOOLAMBA VIC 3614 | 32188653 |  |  |  | Leakage |  |  | 1 | A Powercor fault crew attending a feeder outage on MNA034 found that a pole top burnt through at Pogue P3E. There were shocks, no injuries or ground fire start. | Pole (wood) | 2 | 2 | 2 |  | MNA034 | Excessive leakage current | Pole-top fire | 43195.3556 | 1 | Negligible: no ground fire | 9807 | Agricultural |  | 20180509PWA_01 | Infrastructure (network-based) | -36.4732 | 145.3274 | 1 | Powercor | Report | 12025 | 0.010067 | 22kV AC | Shepparton Airport | 3614 | Toolamba | Pole
The attending crew disconnected the service neutral at the F.O.L.C.B and performed a NST test was resulted in a FAIL. A reading of 1.7 Ohms was obtained. The attending crew checked connections at the pole and identified a corroded neutral connection. The crew rectified the fault. All subsequent tests performed with a pass result obtained (0.2 Ohm). Customer left Safe-On supply. | 15 STATION STREET, OFFICER VIC 3809 | 509406 |  |  |  | Corrosion;Neutral fault |  | Phase to earth |  | IMS 233108. Customer received an electric shock to his hands whilst attempting to repair a damaged copper water pipe in this front yard. AusNet Services' LEI tested voltage with an independent earth to taps and area around damaged pipe which at the time was full of water. The attending LEI performed subsequent votage tests to Independent Earth, a reading of 0 Volts (AC) was obtained at the alleged point of contact and all metallic parts of the installation, including at the installation switchboard under loaded condition. Supply voltage at the installation switchboard was measured at 252 volts (AC). An NST test was performed at the customer's switchboard, a PASS result was obtained. | Connector/termination | 0 | 0 | 0 |  | ofr21 | Corroded neutral connection at pole end. | Minor shock | 31/03/2018 11:50 |  |  | 9810 | Residential |  | 20180509SPN_01 | Infrastructure (network-based) | -38.0619 | 145.41 | 1 | AusNet Services Distribution | Report | 12032 | 0.01591 | Low voltage AC (<1kV) | Moorabbin Airport | 3809 | Officer | Connection
On arrival crew isolated supply and arranged repairs. | 380 ST KILDA ROAD, ST KILDA VIC 3182 | 30311738 | Working too close to underground cables | [6 empty] | Nathan (0403 770 587) from Cross Yarra Partnership reported an excavator made contact with an LV UG cable at 380-398 St Kilda Road, Melbourne. Field crew dispatched to investigate. On arrival it was found that a service pit and underground service cable where damaged by an excavator. This damaged cable supplied public lights it was found that between 15 and 20 public lights where without supply as a result of the incident. There was no injuries or third party damage reported | Cable | 2 | 2 | 2 |  | SO005 | Excavation work | Damage to network assets | 43316.0521 |  |  | 9816 | Public space |  | 20180510PWA_03 | Infrastructure (network-based) | -37.8323 | 144.972 | 1 | CitiPower | Report | 12042 | 0.022309 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Dug up
On arrival crew isolated supply and carried out repairs. | 83 BROOMFIELD ROAD, CRESWICK VIC 3363 | 30013362 |  |  |  | Leakage |  |  |  | Report of a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | BAN009 | Excessive leakage current | Pole-top fire | 16/03/2018 7:39 | 1 | Negligible: no ground fire | 9833 | Roadway |  | 20180514PWA_05 | Infrastructure (network-based) | -37.4048 | 143.8922 | 1 | Powercor | Report | 12062 | 4.3981e-05 | 22kV AC | Ballarat Aerodrome | 3363 | Creswick | Pole
The pole was badly damaged as a result of the pole fire and required replacement. Emergency high voltage switching was completed to minimise the number of customers affected and the pole type substation was replaced under Access Authority conditions. | ROBIN PARK CARAVAN PARK, 90 MARINE DRIVE, SAFETY BEACH VIC 3936 | 8825005 |  | Prone to salt deposition |  | Leakage |  |  | 2 | CFA report there is a pole on fire opposite the caravan park. Following light rain, a timber substation pole located opposite the caravan park on the foreshore of Port Phillip Bay was smoking internally as the centre phase HV dressing down insulator was tracking badly due to the substations location. The faults crew isolated "Marine-Prescott" pole type substation and the CFA hosed the pole down until the smoking ceased. | Pole (wood) | 0 | 0 | 0 |  | DMA 14 | Tracking due to salt borne contaminants as the substation pole is located directly on the foreshore of Port Phillip Bay. | Pole-top fire | 43317.3368 | 1 | Negligible: no ground fire | 9834 | Roadway |  | 20180514UTD_01 | Infrastructure (network-based) | -38.3192 | 144.989 | 1 | United Energy Distribution | Report | 13063 | 0.031235 | 22kV AC | Moorabbin Airport | 3936 | Safety Beach | Pole
On arrival crew isolated supply and commenced repairs. | 3117 BORUNG HIGHWAY, WARRACKNABEAL VIC 3393 | 32111009 |  |  |  | Leakage |  |  | 1 | Customer reported a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | HSM003 | Excessive leakage current | Pole-top fire | 24/03/2018 21:53 | 1 | Negligible: no ground fire | 9837 | Agricultural |  | 20180515PWA_03 | Infrastructure (network-based) | -36.2467 | 142.5165 | 1 | Powercor | Report | 12100 | 0.032811 | 22kV AC | Horsham Aerodrome | 3117 | Warracknabeal | Pole
On arrival crew isolated supply and carried out repairs. | KEL-HEATH PARK, 431 NGALLO ROAD, MURRAYVILLE VIC 3512 | 32153983 |  |  |  | Leakage |  |  |  | Customer reported a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 26/03/2018 9:59 | 1 | Negligible: no ground fire | 9846 | Agricultural |  | 20180515PWA_05 | Infrastructure (network-based) | -35.2865 | 141.1434 | 1 | Powercor | Report | 12113 | 0.0010139 | 22kV AC | Mildura Airport | 3512 | Murrayville | Pole
On arrival crew isolated supply and carried out repairs. | 4780 PATCHEWOLLOCK-SEA LAKE ROAD, NYARRIN VIC 3533 | 33069395 |  |  |  | Leakage |  |  |  | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 26/03/2018 17:50 | 1 | Negligible: no ground fire | 9849 | Public space |  | 20180515PWA_07 | Infrastructure (network-based) | -35.3907 | 142.6945 | 1 | Powercor | Report | 12116 | 0.0070104 | 22kV AC | Swan Hill Aerodrome | 3533 | Nyarrin | Pole
CEOT dispatched a fault crew to make safe and investigate. Crew check assets for damage. | 45 RUTHVEN WAY, RINGWOOD EAST VIC 3135 |  | Working too close to overhead lines | [5 empty] | 1 | IMS 233123. A COAXIAL CABLE HAS COME INTO CONTACT WITH HV AT LIS 1209775. NBN CREW WORKING ON SITE BUT LEFT AS AUSNET SERVICES' FAULT CREW ARRIVED. BURNT CABLE FOUND AT BASE OF POLE (INITIALLY BELIEVED TO BE CAUSED BY A BRANCH RE: @ LIS 1209775. BRANCH FALLEN THROUGH HV. NO DAMAGE TO HV OR LV. NO SIGN OF FIRE OR HVI. TC 6305555898 - Customer saw street wire sparking before losing power. An NBN worker caused a NBN Coaxial cable to make contact with overhead 22 kV conductor causing a flashover and the communications cable to burn. BWR23 FDR 22KV CB operated. | Conductor (bare) | 0 | 0 | 1 | NBN Coaxial cable |  | NBN worker caused a NBN Coaxial cable to contact overhead 22kV conductor. | No Go Zone (contact) | 43194.5417 |  |  | 9841 | Residential |  | 20180515SPN_03 | Infrastructure (network-based) | -37.8071 | 145.2628 | 1 | AusNet Services Distribution | Report | 12104 | 0.0019861 | 22kV AC | Moorabbin Airport | 3135 | Ringwood East | Other
Fault crew dispatched and isolated and earthed the HV LV temporarily repaired to get customers back on supply. HV repaired following Weekend. | 56 NIGHTINGALE AVENUE, WEST WODONGA VIC 3690 |  | Vehicle | [6 empty] | IMS 233210 - Member of public drove car into LV end of kiosk 'NIGHTINGALE -WREN' and damaged LV and HV Cables and LV switchgear. | Pad mounted equipment/kiosk | 0 | 1 | 0 |  |  | Vehicle drove into kiosk | Damage to network assets | 13/04/2018 9:10 |  |  | 9845 | Public space |  | 20180515SPN_06 | Infrastructure (network-based) | -36.1275 | 146.8552 | 1 | AusNet Services Distribution | Report | 12112 | 0.033152 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3690 | West Wodonga | Vehicle
On arrival crew isolated supply and carried out repairs. | 156 HOCKING ROAD, HAPPY VALLEY VIC 3549 | 32147929 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location. There was no ground fire, no reported injuries and no third part property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WMN014 | Excessive leakage current | Pole-top fire | 23/04/2018 13:28 | 1 | Negligible: no ground fire | 9858 | Agricultural |  | 20180517PWA_02 | Infrastructure (network-based) | -34.6652 | 142.7106 | 1 | Powercor | Report | 12127 | 0.018259 | 22kV AC | Mildura Airport | 3549 | Happy Valley | Pole
Supply was isolated by the faults crew and the FOLCB was replaced. The supply to the pavilion was restored upon completion. | 41-45 WIDDOP CRESCENT, HAMPTON EAST VIC 3188 | 1821596 |  |  |  | Overheated connection |  |  | 2 | Moorabbin Kangaroos Football Club - Caller advised the MFB have attended and put a fire out but exposed cables have exploded. No fire now as the fire has been put out. A fire occurred at a three phase FOLCB at a service pole located within the property in the car park. The FOLCB was supplied by an overhead cable that supplied an underground service cable to the sporting club. The probable cause was an overheated connection due to overload or a loose connection. | Connection box | 0 | 0 | 0 |  |  | The probable cause was an overheated connection due to overload or a loose connection. | Pole-top fire | 43317.75 | 1 | Negligible: no ground fire | 9853 | Commercial |  | 20180517UTD_01 | Infrastructure (network-based) | -37.9402 | 145.0291 | 1 | United Energy Distribution | Report | 12122 | 0.0022488 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton East | Connection
Crew attended and repaired cable sheath | 44 FESTIVAL DRIVE, POINT COOK VIC 3030 | 30272602 | Working too close to underground cables | [5 empty] | 2 | Civil worker reports receiving a slight electrical shock whilst using a steel shovel to excavate around live Powercor underground cable. It was apparent the underground cable had been dug up and damaged by an excavator although the excavator wasnâ€™t near the hole on arrival. Thorough visual inspection of the damaged cable by Powercor underground crews were unable to find any sign of primary insulation failure that may have explained how the worker received the shock. Cable outer jacket was repaired and left in service. | Cable | 0 | 0 | 0 |  | WBE013 | Interference | Damage to network assets | 16/05/2018 10:00 |  |  | 9870 | Roadway |  | 20180521PWA_06 | Infrastructure (network-based) | -37.9081 | 144.7438 | 1 | Powercor | Report | 12142 | 0.028435 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
Crew attended and tightened Loose connection in pole junction box | 38 MATTHEWS STREET, SUNSHINE VIC 3020 | 30323471 |  |  |  | Mechanical breakdown |  |  | 2 | customer reported receiving an electric shock when she touched the flexible shower hose of her shower. The service truck attended prior to the CTA and carried out testing at the POA. The service truck reports an NST fail | Connector/termination | 0 | 0 | 0 |  | SSE034 | Loose Connection | Minor shock | 13/05/2018 8:00 |  |  | 9879 | Residential |  | 20180522PWA_09 | Infrastructure (network-based) | -37.7933 | 144.84 | 1 | Powercor | Report | 12152 | 0.020227 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Connection
The attending Powercor Fault Crew re-terminated the Neutral Service Conductor at the FOLCB on the Reticulation Pole and completed an NST test | 17 BYNAN STREET, ECHUCA VIC 3564 | 32182907 |  |  |  | Corrosion |  |  | 2 | Customer was standing beside the Spa when she received an electric shock as she made simultaneous contact with one hand in the water and her bare feet while standing on the wet paved area adjacent the Spa. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Service Neutral Conductor termination at the Network FOLCB located on the Reticulation Pole forming part of the U/G Service supplying the property. (Twisted Service Dress Down Cable between the Reticulation Conductors and the FOLCB), causing a higher than normal impedance within the neutral service conductor. | Dropper/bridge | 0 | 0 | 0 |  | ECA003 | Corroded Connection | Minor shock | 20/04/2018 9:00 |  |  | 9885 | Residential |  | 20180522PWA_14 | Infrastructure (network-based) | -36.1282 | 144.7709 | 1 | Powercor | Report | 12158 | 0.017735 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | Connection
The attending Powercor Fault Crew re-terminated the neutral conductor in the fuse mains box and completed an NST test | 7 MCGRATH CLOSE, KEALBA VIC 3021 | 34915534 |  |  |  | Corrosion |  |  | 2 | Customer received an electric shock as he made simultaneous contact between his hands on the outside taps and his feet while standing on the wet ground. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded conductor in fused mains box | Aluminium twisted (grey) | 0 | 0 | 0 |  | SA002 | corroded connection | Minor shock | 43136.4167 |  |  | 9891 | Residential |  | 20180523PWA_04 | Infrastructure (customer connection) | -37.7365 | 144.8243 | 1 | Powercor | Report | 12164 | 0.012417 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kealba | Connection
A LEI attended and identified that a voltage of 130v was induced from the 66kV overhead conductors even when it was set up 8m away from he conductors. The weather at this time was damp with light rain and drizzle. The LEI earthed the crane and no voltage was measured to an independent earth. The LEI instructed the site manager to correctly bond the crane to earth as the cranes earth crane didn't appear to be adequate. The following morning, United Energy passed the information to our No Go Zone assessors as a further assessment could be required. | RAILWAY PARADE, MURRUMBEENA VIC 3163 |  |  | Precipitation |  | Induction |  | Phase to earth | 2 | Contractor on site advised that his crews are receiving electric shocks from the on-site crane near the corner of Poath Road and Railway Parade opposite the Hughesdale Railway station. Mentions that no power lines have been hit and the crane is 8m from the power lines. The crews have ceased work for the evening but he will remain on-site. The Poath Road, Hughesdale level crossing is being removed as part of the Caulfield to Dandenong Level Crossing Removal Project that will see a new station at Hughesdale constructed. A crane was located 8m from the 66kV overhead conductors and workers advised their supervisor that slight electric shocks are being received from the crane stabilizer arms and he contacted the United Energy faults and emergencies call centre. | Conductor (bare) | 0 | 0 | 0 |  | MTS-OR | Induction between the 66kV conductors and the crane that was outside of the No Go Zone Framework. | Minor shock | 17/05/2018 23:00 |  |  | 9914 | Construction |  | 20180525UTD_02 | Infrastructure (network-based) | -37.8947 | 145.0767 | 2 | United Energy Distribution | Report | 12187 | 0.013895 | 66kV AC | Moorabbin Airport | 3163 | Murrumbeena | Other
The faults crew disconnected supply in a pillar in the URD area, took photos and forwarded to the Resource Coordinator and their supervisor. An investigation revealed the meter had stopped communicating on 29/04/2018 and its present location is unknown. | 155 HAVERBRACK DRIVE, MULGRAVE VIC 3170 |  | Unauthorised work;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Caller states the meter has been abolished today and live wires have been left exposed with sparks coming from them. The site has been evacuated and please contact Shanthini on 0401 660 940 if required. The faults crew arrived on site and found the home in the URD had been half demolished. When questioned, the 16 tonne excavator operator said the meter was gone and assumed the electricity supply had been safely removed to allow the demolition work to commence. No electric shocks or injuries were received. There had been no abolishment request received and the abolishment process was ignored, although there are contact notes in United Energy records following four enquiries earlier in the day, including the final call about the exposed, sparking wires. There was also no request for a de-energisation from the previous occupier. | Services cable | 0 | 0 | 0 |  |  | Failing to follow the abolishment process. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/05/2018 13:00 |  |  | 9919 | Residential |  | 20180525UTD_04 | Infrastructure (network-based) | -37.9366 | 145.1998 | 1 | United Energy Distribution | Report | 12192 | 0.0056296 | Low voltage AC (<1kV) | Moorabbin Airport | 3170 | Mulgrave | Other
On arrival crew confirmed site safe. Some disturbance to ties, ties replaced once site cleared. | 607 CHAPEL ROAD, KATAMATITE VIC 3649 | 33085508 | Vehicle | [6 empty] | Emergency services report a car into a pole. Crew attended and found a car had struck a pole follow at accident with a truck. Driver of car died at the scene. Police, Ambulance and CFA in attendance. No protection operated. Minor damage to Powercor assets. No shocks or ground fire start. | Conductor (bare);Insulator tie wires/connections;Pole (concrete) | 2 | 2 | 2 |  | NKACME | Vehicle struck pole. | Not involving electrocution;Damage to network assets | 25/05/2018 13:56 |  |  | 9923 | Roadway |  | 20180528PWA_01 | Infrastructure (network-based) | -36.0116 | 145.6956 | 1 | Powercor | Report | 12201 | 0.0077419 | 22kV AC;66kV AC | Shepparton Airport | 3649 | Katamatite | Vehicle
On arrival crew isolated supply and carried out repairs. | 6065 MIDLAND HIGHWAY, TATURA VIC 3616 | 30138758 |  |  |  | Corrosion |  |  |  | CFA reported transformer explosion and grass fire at incident location. On arrival crew found a FOLCB had failed, There was a 15x10 metre grass fire. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | SHTS-SHP 66KV | Overheated connection | Loss of supply;Grassfire | 23/05/2018 23:45 | 1 | Small: 10 - 1000 sq.m | 9927 | Roadway |  | 20180528PWA_03 | Infrastructure (network-based) | -36.4105 | 145.2495 | 1 | Powercor | Report | 17368 | 0.0089861 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Tatura | Connection
Fault crew disconnected the supply. | 125 GRANGE ROAD, FAIRFIELD VIC 3078 |  | Unauthorised access | [5 empty] | 2 | A Jemena contractor discovered a BTS pole that has a neutral screen OH service attached to the pole (ie. relocation of service and meter). Unauthorised access to the Jemena network. Refer to the attached photos. | Service conductor;Neutral screen | 2 | 2 | 2 |  |  | Unauthorised access to service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/05/2018 12:32 |  |  | 9941 |  |  | 20180529JEM_02 | Infrastructure (network-based) | -37.7728 | 145.026 | 1 | Jemena | Report | 12219 | 0.013931 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Fairfield | Other
The immediate temporary repairs on fence have been arranged | 15 GLADMAN STREET, WINCHELSEA VIC 3241 | 30295909 | Copper theft | [6 empty] | Torquay Police reported cut fence at the incident location (WIN ZSS) and requested call 000 if there was a theft occurred. Upon arrival, a Powercor crew found that a large hole on the boundary fence. They also believe conductor/LV cable drums were taken from the ZSS. The Police were informed again but there were unable to attend to scene at the time. There was no fire, no reported injuries or third party property damage. | Zone substation | 2 | 2 | 2 |  | GTSWIN | Copper theft | Damage to network assets | 16/04/2018 9:07 |  |  | 9943 | Commercial |  | 20180529PWA_05 | Infrastructure (network-based) | -38.2356 | 144.0033 | 1 | Powercor | Report | 12221 | 0.029149 | Not applicable | Avalon Airport | 3241 | Winchelsea | Other
CEOT dispatched a fault crew to make safe, investigate and arrange for repair. The fault crew found that the light head had caught fire. Crew requested public lighting crew to replace the street lantern. Our delivery partner has removed the failed head and replaced it with a new head. | 38 ROSEHILL ROAD, LOWER PLENTY VIC 3093 | 905963 |  |  |  | Electrical breakdown |  |  |  | IMS 233155. Received INCD from Fire Brigade saying that there was a fire at a street light. This is an older public light fitting where the igniter or starter has failed causing a light head fire. Please note the reporting delay is due to a delay caused by the investigation officer. | Public lighting | 0 | 0 | 0 |  | ELM34 | Street light head caught fire. Exact cause uncertain but it is common for such older street lights to fail due to either faulty ignitors with repetitive striking or failed plastic clad capacitors. | Other electricity related | 43347.0188 | 1 | Negligible: no ground fire | 9939 | Residential |  | 20180529SPN_01 | Infrastructure (network-based) | -37.737 | 145.128 | 1 | AusNet Services Distribution | Report | 12293 | 0.025398 | Low voltage AC (<1kV) | Essendon Airport | 3093 | Lower Plenty | AF Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 30 Volts no load to 120 Volts maximum load. Fault Crew found a loose neutral terminal in the take-off on the service pole that supplies an O/H ABC 2 wire service to 30-32 Talbot St. The neutral conductor of the LV reticulation across the road had come adrift of the neutral terminal in the take-off box on the service pole. Crew re-terminated the neutral conductor into the neutral terminal of the take-off box and ensured terminal screws were tight. Crew performed NST at the POA with a pass result recorded. Installation left ON supply. | 30-32 TALBOT STREET, COLAC VIC 3250 | 30056064 |  |  |  | Corrosion |  | Phase to earth |  | Tim was standing at the laundry basin, when he felt a slight shock to his right hand when adjusting the tap, with his left hand in the water flow. | Connection box | 2 | 2 | 2 |  | CLC001 | Loose connection | Minor shock | 28/02/2018 15:00 |  |  | 9722 | Residential |  | 20180419PWA_03 | Infrastructure (network-based) | -38.3474 | 143.5966 | 1 | Powercor | Report | 11910 | 0.028769 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | Connection
Crew attended Tree cleared and line restored. | 1209 HARRIS ROAD, MINJAH VIC 3276 | 33102095 |  | Fallen |  |  |  |  | 1 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Minjah Hawkesdale area. The attending crew found damaged conductor near the intersection of Harris Road Fire damage response and repair activities were undertaken as part of response to a number of fires in the area. | Conductor (bare) | 0 | 0 | 0 |  | KRT012 | Vegetation: Trees Incident | Grassfire | 17/03/2018 21:00 | 1 | Small: 10 - 1000 sq.m | 9732 | Agricultural |  | 20180423PWA_03 | Infrastructure (network-based) | -38.0717 | 142.4398 | 1 | Powercor | Report | 12024 | 0.017575 | 22kV AC | Warrnambool Airport Ndb | 3276 | Minjah | Trees
A defect notice has been issued and fuse removed, Dispatch notified with the request for a fault crew to attend to remove the service until defects rectified and new COES received. | 107 WEST STREET, HADFIELD VIC 3046 |  | Unauthorised work | [5 empty] | 2 | Compliance officer attended 107 West street Hadfield for a compliance check of the new connection. While onsite it was observed the BTS appears to have been relocated, The pole was installed with excessive movement, one stay not attached, The overhead service has excessive sag and did not maintain the minimum heights over the road or driveway. | Aluminium twisted (XLPE) | 2 | 2 | 2 |  |  | Un-authorised unknown person relocated service including BTS pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/04/2018 16:47 |  |  | 9755 | Residential |  | 20180427JEM_03 | Infrastructure (network-based) | -37.7062 | 144.9383 | 1 | Jemena | Report | 11952 | 0.038171 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 457 STEPHENSONS ROAD, MOUNT WAVERLEY VIC 3149 | 602822 |  | Alive |  | Conductor clashing |  |  | 1 | At 0840hrs on 09/04/2018, 22kV feeder ACR DN 3360 located in Waverley Road successfully reclosed and held. An unknown vehicle struck a council tree located outside 757 Stephensons Road, Mount Waverley and flicked the broken branch into the HV and LV conductors near pole number LIS 0602822. It appeared the blue phase LV conductor clashed briefly with a HV conductor and the 250amp HRC fuse operated at "Birdee-Fairway" pole type substation The faults crew requested that a LEI attend to investigate as a HVI was suspected to customers supplied from the west circuit of "Birdee-Fairway" substation. The LEI confirmed a high voltage injection occurred (BWD 1806) affecting customers who reside in the vicinity that sustained minor damage to metering equipment and appliances. | Conductor (bare) | 0 | 0 | 0 |  | GW 03 | Vegetation: Trees Incident | HV injection | 43347.3611 |  |  | 9748 | Roadway |  | 20180427UTD_02 | Infrastructure (network-based) | -37.8901 | 145.1261 | 1 | United Energy Distribution | Report | 11945 | 0.008184 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Vehicle
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for any necessary repairs. Communication between the control and the DAO confirmed that the Downer crew that attended the site the night before could not find the cause. There was no damage to our assets and all were ok to operate as per normal | 20 ARGOON ROAD, HEALESVILLE VIC 3777 | 1402987 |  |  |  | Conductor clashing |  |  |  | IMS 233378. INCD for grass fire in vicinity of AusNet Services' assets received from CFA. Initial report from the attending fault crew indicated no signs of conductors clashing nor any sign of tree branches involved. DAO attended call out located down Heritage lane Healesville. Arrived on site next morning to find a burnt out area between Pole#1402987 and Pole#1402988. Investigated the area, only to find no real evidence of the cause. There were no tree branches located at the scene and the line was far enough away from the line to not impact it and there were no foreign objects around the site. Suspected conductor clashing Action item assigned for further investigation. | Conductor (bare) | 0 | 0 | 0 |  | LDL23 | The incident is currently under investigation. | Grassfire | 27/04/2018 17:48 | 1 | Small: 10 - 1000 sq.m | 9759 | Agricultural |  | 20180430SPN_01 | Infrastructure (network-based) | -37.6695 | 145.5086 | 1 | AusNet Services Distribution | Report | 12837 | 0.035899 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3777 | Healesville | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 229 BALCOMBE ROAD, BEAUMARIS VIC 3193 |  |  |  |  | HV injection;Electrical breakdown |  |  | 1 | At 0200hrs on 20/04/2018, 11kV feeder BR 15 circuit breaker reclosed to lockout affecting 487 customers. A possum flashed over the GFB switch (CH9484) located outside 229 Balcombe Road, Beaumaris that caused a HV connection to fail and a HV conductor to fall to the ground. The HV conductor made brief contact with the LV blue phase conductor below and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "the south circuit of "Church-Balcombe" substation. The LEI confirmed a high voltage injection occurred (KEY 1803) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. Secondary damage was sustained due to probable fault current with a connection failure at CH8068 located in Balcombe Road on the corner of Charman Road that was repaired by a glove and barrier crew. | Conductor (bare);Disconnector/isolator | 0 | 0 | 0 |  | BR 15 | Animal Incident | HV injection;Loss of supply | 21/04/2018 2:00 |  |  | 9764 | Roadway |  | 20180430UTD_04 | Infrastructure (network-based) | -37.9793 | 145.0469 | 1 | United Energy Distribution | Report | 11965 | 0.033852 | 11kV AC | Moorabbin Airport | 3193 | Beaumaris | Animal
Emergency high voltage switching was completed to minimise the number of customers affected. The faulted surge arrestor is planned for replacement on 23/04/2018. Photos attached. | BOGONG AVENUE, GLEN WAVERLEY VIC 3150 |  |  |  |  | Electrical breakdown |  |  | 1 | 12.08PM - 22kV feeder, GW03 circuit breaker reclosed to lockout. At the same time, 66kV feeder GW-NO successfully reclosed and held. 22kV feeder GW03 was sectionalised and restored via NO04 but the first part of GW03 tripped again on sectionalising. All sections were inspected during a patrol with no faults identified and GW03 was restored. A short time later following the fault earlier in the day, a catastrophic (explosive) failure of a network asset occurred when a surge arrester on the GW03 rack within the GW zone substation ruptured with GW03 and GW12 circuit breakers reclosing to lockout. No persons were in the vicinity and there was no other major damage. ESV was advised with reference number 9763042 provided. | Switchyard;Zone substation;Surge diverter | 1 | 0 | 0 |  | GW 03 | The cause of the surge arrestor failure was under investigation and was presently undetermined. | Loss of supply | 21/04/2018 12:08 |  |  | 9766 | Other | Zone substation | 20180430UTD_06 | Infrastructure (network-based) | -37.8878 | 145.1553 | 1 | United Energy Distribution | Report | 12323 | 0.037101 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | AF Other
Investigations by the fault crew revealed illegal wiring at the meter box; with wiring connected to bypass the meters. Police on site found a hydroponics set up inside the installation, and later TV reports showed vision of Police removing in the order of 200 leafy green plants from this property. Police advised the fault crew not to restore supply to this installation. The fault crew cut the U/G service tails to isolate the installation at the Service Pit. | 13 GOLF LINKS ROAD, ARARAT VIC 3377 | 30081982 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the crew found that the 3 phase LV Fused Junction Box had melted and dropped from its mounting position, and wiring in the Underground Service Pit at the base of this pole were running hot.. There was no pole fire, no ground fire or any other damage caused by this incident. | Connection box | 2 | 2 | 2 |  | ART034 | Illegal wiring causing overloading | Pole-top fire | 31/03/2018 22:53 | 1 | Negligible: no ground fire | 9767 | Roadway |  | 20180501PWA_01 | Infrastructure (network-based) | -37.2717 | 142.9203 | 1 | Powercor | Report | 11969 | 0.022591 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Fuse
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole, The attending Powercor Fault Crew re-terminated the O/H Aluminum Twisted Service Cable at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 7 SUNSET STRIP, JAN JUC VIC 3228 | 30074127 |  |  |  | Corrosion |  | Phase to earth |  | Masters Josh & Ky DeVries received an electric shock from an external Tap at the side of the property whilst using the Tap to play in the sprinkler when their hands made simultaneous contact with the metal Tap and their bare feet whilst standing on the wet ground. | Service conductor | 2 | 2 | 2 |  | WPD032 | Corroded connections | Minor shock | 22/03/2018 13:00 |  |  | 9771 | Residential |  | 20180501PWA_04 | Infrastructure (network-based) | -38.3456 | 144.3031 | 1 | Powercor | Report | 11973 | 0.027172 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
Site was made safe by isolating supply and then repairs were carried out. | 50 BUCKLAND WAY, SUNBURY VIC 3429 |  | Copper theft | [6 empty] | Unknown persons attempted to steal copper (low voltage underground cable) at pole substation Buckland Way-P8 | Services cable | 0 | 0 | 0 |  |  | Unknown person attempted to steal copper. | Damage to network assets | 43136.3424 |  |  | 9783 | Agricultural |  | 20180502JEM_01 | Infrastructure (network-based) | -37.6071 | 144.724 | 1 | Jemena | Report | 11988 | 0.0037326 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. CEOT also notified the DAO. Crew attended site and made safe. A fire on the ground in the vicinity was put out. The crew under EAP replaced the HV dropper lead and restored supply. | 36 OCEAN VIEW PARADE, LAKES ENTRANCE VIC 3909 | 5622581 |  |  |  | Electrical breakdown |  | Phase to earth | 1 | IMS 233413. Initial report: HV dropper burnt off bushing - fire observed on ground. Final report: An insulated HV dropper termination lead connection at the transformer bushing White Phase failed causing a flashover at the water sheds. The HV dropper lead shorted out to the transformer tank melting the water sheds of the dropper lead. HV fuse operated. | Pole mounted;Connector/termination | 0 | 0 | 0 |  | BDL41 | HV dropper lead termination burnt off transformer bushing. | Grassfire | 43105.5965 | 1 | Localised: less than 10 sq.m | 9780 | Residential |  | 20180502SPN_02 | Infrastructure (network-based) | -37.8682 | 148.0211 | 1 | AusNet Services Distribution | Report | 12858 | 0.0037639 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | Connection
An underground faults crew promptly attended and re-terminated the LV cable with supply restored upon completion after the LV fuses were replaced. | 42 JACKSONS ROAD, CHELSEA VIC 3196 | 3304380 |  | Precipitation |  | Moisture ingress |  |  | 1 | Caller reports of a fire with small flames on the pole located outside 42-44 Jacksons Road. Following light rain, a LV underground cable crutch has blown up at pole number LIS 3304380 that caused the LV white and blue phase HRC fuses to operate at "Jacksons-Kingston" substation. | Cable | 0 | 0 | 0 |  |  | The cause of the LV underground cable was probable water ingress. | Other electricity related | 24/03/2018 15:35 | 1 | Negligible: no ground fire | 9782 | Roadway |  | 20180502UTD_03 | Infrastructure (network-based) | -38.0431 | 145.1259 | 1 | United Energy Distribution | Report | 12036 | 0.020753 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | UG Cable
Crew made safe and repairs undertaken | 96 BAMBRA ROAD, AIREYS INLET VIC 3231 | 33045917 |  |  |  | Overheated connection |  |  | 2 | CFA reported a pole fire at Bambra Rd, Aireys Inlet. A crew was dispatched to investigate. Upon arrival, the crew found evidence of a LV crossarm fire and a burnt LV service fuse mount. The crew made safe and made necessary repairs. There was evidence of a small ground fire at the base of pole. There were no reported shocks or injuries. | Crossarm (wood);Any other type | 0 | 0 | 0 |  | WPD014 | Connection malfunction | Loss of supply;Grassfire | 28/04/2018 23:51 | 1 | Localised: less than 10 sq.m | 9786 | Roadway |  | 20180503PWA_02 | Infrastructure (network-based) | -38.4499 | 144.0979 | 1 | Powercor | Report | 11993 | 0.019667 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Aireys Inlet | Connection
23/04/2018 - on the weekend prior, a NGZ appointment was booked for the weekend and the attending crew arrived and noticed the tree had already been cut and the limbs lying on the ground. The builder had been instructed many times the tree cutting activities were within a No Go Zone but he continued to arrange for the breach of clearances. The United Energyâ€™s ex-Vegetation Liaison Officer suggested that ESV are advised as the builder understood he was in breach of the No Go Zone Framework but continued to proceed placing person subcontracted by him in a dangerous situation. | 8 ST AUBINS AVENUE, CAULFIELD NORTH VIC 3161 |  | Working too close to overhead lines | [5 empty] | 2 | A new unit development was being constructed at 6 St Aubins Avenue with a new pole type substation installed to supply the site. Part of the electricity supply offer was a HV extension from existing HV infrastructure to the pole type substation. Private trees were required to be cut to ensure clearances are maintained to the new HV conductors and the builder was instructed the tree cutting activities are within a No Go Zone and do not proceed and arrange for a site assessment. United Energyâ€™s Vegetation Liaison Officer inspected this site and provided the following information to the builderâ€¦ "I have inspected the site and can provide the below advice. The overhang in the below picture will need to be removed prior to the new HV being constructed and energised. As per the approved design drawing, there is an offset type construction which indicated the inner HV phase will be in line with the centre of the poles. The customer will need to arrange for a NGZ Live Line quote or Shutdown in order for their arborist to safely remove this overhang whilst eliminating damage or an outage to our network. The crew will prune back to a clearance of 3m which is more than ample as the required clearance for HV in a Low Bush Fire Risk Area is 2m plus re-growth pending on the length of the span. Overhang is permitted within a Low Bushfire Risk Area but the minimum 2m clearance plus re-growth is still required. Just to clarify I believe this requires a NGZ raised as access to the tree will be breached as there is a 3m minimum required clearance for any persons not working directly for UE (Unauthorised Persons) under the VESI No Go Zone requirements. No Go Zone can be contacted at 132 099". Also on 22/03/2018, the UE Vegetation Liaison Officer spoke with the builder and re-iterated the No Go Zone requirements. | Conductor (bare) | 0 | 0 | 0 |  |  | Breach of No Go Zone framework clearances. | No Go Zone (no contact) | 21/04/2018 9:00 |  |  | 9788 | Roadway |  | 20180503UTD_01 | Infrastructure (network-based) | -37.8738 | 145.0098 | 2 | United Energy Distribution | Report | 11995 | 0.01965 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Other
The contractor was working under a No Go Zone Permit (34047) issued via Extec under the No Go Zone process and has provided photographs to demonstrate they were meeting the No Go Zone permit conditions. Matter has been investigated with inputs from Extec who have been out a number of times to site. Action created to AusNet Services' Access Coordinator who oversees Extec works. When Downer attended the site they discovered that the soil had been reinstated already by the civil works contractor Winslow. We have altered our processes from learning's in this case and will now implement the following to assist in the prevention of this type of incident that could expose ourselves and AusNet Service. . We are going to give customers a copy of Excavation next to poles diagram. . As we now have to put so much information on our PTWâ€™s we are going to have the conditions pre-typed up and attach to permit so it is clearer (we have Darren Linkins approval for this). . We are going to have contractors/customers sign they are not permanently altering ground level. . We are going to specify as an additional condition that all soil is backfilled nightly around poles. | 100 PATTERSONS ROAD, CLYDE VIC 3978 | 508600 | Working too close to overhead lines | [5 empty] | 2 | IMS 232759. Turnkey project developer's contractor has removed the soil from around distribution poles reducing pole footings to 1m. Tony (Extec Services) issued a permit to Adam Rawsthown (tel. 0408 168944) 8/2/2018 to 8/3/2018 as attached. At Tony's site visits Winslow were requesting to work adjacent to poles and under lines to install pipes, conduits, etc. and at no time did they indicate they would be permanently removing soil for retaining walls and changing heights of ground level. We would expect they backfill after excavation and pipe install. If and when customers/contractors advise they are changing ground levels or removing significant soil around poles we would refer them back to AusNet Services. The PTW outlined clearances to overhead lines, conditions with excavating adjacent to cables and the excavation depths next to poles. In this instance Tony gave them a PTW that requested they not excavate greater than 300mm within 600mm, not greater than 900mm within 600mm to 1500mm and not greater than 1800mm within 1500mm to 1800mm. This is exactly as per NGZ guidelines for Network Operator's chart. For your information this chart is a guideline only and in some cases we alter what we allow based on pole type, forces on pole, soil type, earths, etc. I believe they have not followed their permit to work and have not indicated to us they are changing soil levels and discussions were around excavating and re-instating. | Pole (wood) | 0 | 0 | 0 |  | cln22 | Turnkey project developer's contractor has removed the soil from around distribution poles reducing pole footings to 1m. | No Go Zone (no contact) | 43284.6667 |  |  | 9793 | Construction |  | 20180507SPN_02 | Infrastructure (network-based) | -38.1234 | 145.3407 | 1 | AusNet Services Distribution | Report | 12005 | 0.024593 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3978 | Clyde | Other
Site made safe for repairs. Jemena crew replaced cable. | 25 OLD RIDDELL ROAD, SUNBURY VIC 3429 |  | Vandalism | [5 empty] | 2 | Unknown member of the public removed underground cable between poles A136724 and A136726 - both poles are street light poles. The Jemena crew found the removed cable in bushes close to the location of the incident. | Cable | 0 | 0 | 0 |  |  | Unknown person removed underground cable and left the cable near the incident. | Damage to network assets | 43317.4563 |  |  | 9802 | Residential |  | 20180508JEM_01 | Infrastructure (network-based) | -37.5552 | 144.6984 | 1 | Jemena | Report | 12018 | 0.0041273 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
CEOT dispatched fault crew to isolate, make safe and investigate. Crew investigated and restored supply. No fire occurred. Boric Acid fuse candling and broke in half. | 80 WATERHOLES ROAD, GRANITE ROCK VIC 3875 | 1600885 |  |  |  | Candled fuse |  |  |  | IMS 233044. Customer call with no power. Attending fault crew found a Boric Acid fuse had burnt through. No fire on the ground and no fire on the pole. | Boric acid | 0 | 0 | 0 |  | bdl8 | Burnt Boric Acid fuse tube. | Other electricity related | 27/03/2018 12:00 | 1 | Negligible: no ground fire | 9805 | Agricultural |  | 20180508SPN_02 | Infrastructure (network-based) | -37.7472 | 147.677 | 1 | AusNet Services Distribution | Report | 12023 | 0.023218 | 22kV AC | Bairnsdale Airport | 3875 | Granite Rock | Fuse
The electrical inspector performed all VESI tests including, NST tests at both of the properties switchboards - a FAIL result was obtained. All relevant voltage tests were carried on the installations earthing system, voltages of 12 - 24V (ac) was measured under normal and loaded conditions. The electrical inspector requested a fault truck to replace severely corroded service cable. Following the installation of the new service cable, all related tests were carried out. A PASS result was obtained following an NST test, all subsequent voltage tests carried out on the customers earthing system, taps and metallic surfaces to an independent earth resulted in an acceptable result of <1 volt AC. | 14 EASTGATE STREET, PASCOE VALE SOUTH VIC 3044 |  |  |  |  | Age;Corrosion |  |  | 2 | The customer received electric shocks whilst showering. The electrical inspector attend the site to investigate. The inspector measured voltages on the shower and bathroom taps of between 12 and 24 volts (AC) relevant to the installation load. | Service conductor;Neutral screen | 0 | 2 | 0 |  |  | Corroded neutral service | Minor shock | 43348.6535 |  |  | 9813 | Residential |  | 20180509JEM_01 | Infrastructure (network-based) | -37.7361 | 144.9429 | 1 | Jemena | Report | 12037 | 0.00061806 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale South | OH Cable
Site made safe and repair undertaken | 60 BUCKLAND WAY, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Person unknown has stolen copper | Copper | 2 | 2 | 2 |  |  | Person stole customer underground mains to get copper | Loss of supply | 43378.6312 |  |  | 9823 |  |  | 20180510JEM_02 | Infrastructure (network-based) | -37.6063 | 144.7239 | 1 | Jemena | Report | 12052 | 0.038167 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 29 WHITE AVENUE, WENDOUREE VIC 3355 | 32011803 |  |  |  | Corrosion |  | Phase to earth |  | Mr Stephen Matthews was in the Bathroom showering when he received an electric shock as he made simultaneously contact with his hand on the metallic Shower Tap and his bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | BAN002 | Corroded connection | Minor shock | 27/03/2018 8:30 |  |  | 9817 | Residential |  | 20180510PWA_04 | Infrastructure (network-based) | -37.5393 | 143.8468 | 1 | Powercor | Report | 12043 | 0.033103 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | Connection
first respond dispatched to make safe. CFA on site to extinguish the fire. earthing (for repair) was delayed due to extreme weather condition. Vegetation assessor on site the next morning to investigate. conductor repaired and supply restored 13:00 hours next day. | 582 FIRMINS LANE, HAZELWOOD NORTH VIC 3840 | 2577249 |  | Wind;Fallen |  |  |  | Phase to earth | 1 | IMS 233532 - fire on the corner of Firmins Ln & Hazelwood Rd in Hazelwood North | Conductor (bare) | 0 | 0 | 0 |  | TGN23 | Vegetation: Trees Incident | Loss of supply;Grassfire | 14/02/2018 12:58 | 1 | Medium: 1000 sq.m - 10 ha | 9825 | Roadway |  | 20180511SPN_02 | Infrastructure (network-based) | -38.2557 | 146.4898 | 1 | AusNet Services Distribution | Report | 12054 | 0.018152 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | Trees
On arrival crew isolated supply and carried out repairs. | 1463 HOPETOUN-SEA LAKE ROAD, HOPETOUN VIC 3396 | 32159080 |  |  |  | Leakage |  |  | 1 | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 26/03/2018 3:21 | 1 | Negligible: no ground fire | 9840 | Agricultural |  | 20180515PWA_04 | Infrastructure (network-based) | -35.6922 | 142.581 | 1 | Powercor | Report | 12103 | 0.035461 | 22kV AC | Swan Hill Aerodrome | 3396 | Hopetoun | Pole
On arrival crew isolated supply and carried out repairs. | 4723 PATCHEWOLLOCK-SEA LAKE ROAD, NYARRIN VIC 3533 | 32158659 |  |  |  | Leakage |  |  |  | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 26/03/2018 16:00 | 1 | Negligible: no ground fire | 9848 |  |  | 20180515PWA_06 | Infrastructure (network-based) | -35.3901 | 142.6632 | 1 | Powercor | Report | 12115 | 0.03081 | 22kV AC | Swan Hill Aerodrome | 3533 | Nyarrin | Pole
CEOT dispatched fault crew to make safe and repair | 50 CARMODYS ROAD, LEONGATHA SOUTH VIC 3953 | 2001147 |  |  |  | Corrosion |  |  | 1 | IMS 233540 - HV conductor on ground between poles LIS 2023156 and LIS 2001147. fuse operated. small grass fire - 30 cm x 30 cm | Conductor (bare) | 0 | 0 | 0 |  | LGA14 | Corroded steel conductor broke at existing sleeve on conductor which fell to ground & burnt small area of grass on nature strip | Grassfire | 14/05/2018 7:45 | 1 | Localised: less than 10 sq.m | 9843 |  |  | 20180515SPN_05 | Infrastructure (network-based) | -38.5017 | 145.9547 | 1 | AusNet Services Distribution | Report | 12838 | 0.014138 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Leongatha South | Conductor
On arrival crew isolated supply and carried out repairs. | 1764 MURRAY VALLEY HIGHWAY, BEVERFORD VIC 3590 | 30546795 |  |  |  | Leakage |  |  |  | Pole fire reported at incident location. There was no ground fire, no reported injuries and no third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 14/04/2018 21:56 | 1 | Negligible: no ground fire | 9854 | Roadway |  | 20180517PWA_01 | Infrastructure (network-based) | -35.2206 | 143.4463 | 1 | Powercor | Report | 12123 | 0.025523 | 22kV AC | Swan Hill Aerodrome | 3590 | Beverford | Pole
On arrival crew found lantern had been on fire. supply isolated repairs made | 70 CITY ROAD, SOUTHBANK VIC 3006 | 30160563 |  |  |  | Unknown technical factor |  |  |  | MFB reported pole fire at incident location. There was no ground fire, no reported injuries or third property damages. | Public lighting | 2 | 2 | 2 |  | SO022 | Unable to determine from evidence | Pole-top fire | 17/04/2018 0:03 | 1 | Negligible: no ground fire | 9861 | Roadway |  | 20180517PWA_03 | Infrastructure (network-based) | -37.8218 | 144.9657 | 1 | CitiPower | Report | 12130 | 0.041541 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | Pole
CEOT dispatched a fault crew to make safe, investigate and repair. The crew isolated the Krone box (FSD). The burnt out side was on the load side and the crew replaced pole and asociated equipment. | 763 HIGH STREET, EPPING VIC 3076 | 915175 |  |  |  | Overheated connection |  |  |  | IMS 233230. MFB report of a pole fire. Lis 915175 Krone box (FSD) has burnt out at the pole. Needs to be replaced. No photos available. | Any other type | 0 | 0 | 0 |  | EPG32 | Burnt out LV Fuse Switch Disconnector on the load side. | Other electricity related | 17/04/2018 12:56 | 1 | Negligible: no ground fire | 9859 | Commercial |  | 20180517SPN_01 | Infrastructure (network-based) | -37.6491 | 145.0252 | 1 | AusNet Services Distribution | Report | 12931 | 0.0056053 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | Fuse
Crew isolated supply and replaced HV Xarm and centre phase insulator. Pole to be replaced. | 6134 MURRAY VALLEY HIGHWAY, COHUNA VIC 3568 | 32033895 |  |  |  | Leakage |  |  |  | Vicfire reports pole fire at the incident location. A crew attended and found a pole top fire had occurred, damaging top of pole and Xarm. CFA attended. There were shocks, no injuries or ground fire start. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | CHA003 | Excessive leakage current | Pole-top fire | 18/05/2018 8:13 | 1 | Negligible: no ground fire | 9863 | Agricultural |  | 20180518PWA_02 | Infrastructure (network-based) | -35.8322 | 144.2473 | 1 | Powercor | Report | 12133 | 0.038502 | 22kV AC | Swan Hill Aerodrome | 3568 | Cohuna | Pole
Crew attended and re-terminated service connections | 10 DE BURGH ROAD, DRYSDALE VIC 3222 | 31033876 |  |  |  | Corrosion |  |  | 2 | Mr Sam Dalton was in the rear garden operating an external garden Tap when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet while standing on the wet ground. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole, which was identified as the cause of the high impedance within the service neutral conductor. | Aluminium twisted (grey) | 0 | 0 | 0 |  | DDL021 | connection malfunction | Minor shock | 15/05/2018 9:00 |  |  | 9869 | Residential |  | 20180521PWA_05 | Infrastructure (network-based) | -38.1794 | 144.5647 | 1 | Powercor | Report | 12141 | 0.01577 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Drysdale | Connection
On arrival crew isolated supply and carrie out repairs. LEI investigated HVI damage | 11 WILLIAM STREET, STAWELL VIC 3380 | 33051913 |  | Lightning |  |  |  |  | 1 | A customer advised loud bang at the incident location. On arrival the crew found that the HV conductor on cross arm and also live LV conductors on the ground. Crew believed lightning hit the line and also they called LEI to investigate possible HVI. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | STL005 | crew believed lightning strike | HV injection;Loss of supply;Damage to network assets | 21/05/2018 13:05 |  |  | 9875 | Roadway |  | 20180522PWA_05 | Infrastructure (network-based) | -37.0633 | 142.7922 | 1 | Powercor | Report | 12147 | 0.0070127 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3380 | Stawell | Lightning
On arrival crew isolated supply and carried out repairs | 2 MAPLEWOOD CLOSE, BROOKFIELD VIC 3338 | 31024012 |  |  |  | Overheated connection |  |  |  | Customer called in to advise - - Pole is on fire directly outside. Weather is raining customer is calling the Fire Brigade. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out on Transformer Pole. The resultant heat has also caused the insulation to melt off the LV UG Street cct mains cable. There was no reported ground fire, third party damage, injury or shocks as a result of this incident | Disconnector/isolator | 2 | 2 | 2 |  | MLN013 | connection failure | Pole-top fire | 43348.9938 | 1 | Negligible: no ground fire | 9878 | Roadway |  | 20180522PWA_08 | Infrastructure (network-based) | -37.7051 | 144.5527 | 1 | Powercor | Report | 12151 | 0.02233 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Connection
Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. | 10 LEURA COURT, CORIO VIC 3214 | 32084726 |  |  |  | Moisture ingress;Corrosion |  |  | 2 | Customer received numerous electric shocks (over a two week period) in the Kitchen while she was washing dishes at the Kitchen sink when she made simultaneous contact with one hand on the metallic Tap and the other hand on the metal sink. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor Mid Span of an O/H Aluminium Neutral Screened Service Cable which was identified as the cause of the high impedance within the neutral service conductor. The corrosion of the O/H Service Cable was the result of water entering the outer sheath via a small perforation, the cause of which was unable to be determined. | Aluminium;Neutral screen | 0 | 0 | 0 |  | FNS021 | Corroded Neutral Screen Conductor | Minor shock | 43225.4167 |  |  | 9884 | Residential |  | 20180522PWA_13 | Infrastructure (network-based) | -38.0744 | 144.3674 | 1 | Powercor | Report | 12493 | 0.0085324 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 109 ELDER STREET S, CLARINDA VIC 3169 | 2330255 |  | Precipitation |  | Leakage |  |  | 2 | Pole fire reported at the corner of Elders Street and Carbine Avenue, Clayton. Following light drizzly rain after a dry spell, a HV cross arm fire occurred on a staked HV/LV strain pole (LIS No. 2330255) located outside 109 Elder Street, Clarinda on the corner of Carbine Avenue. | Crossarm (wood) | 0 | 0 | 0 |  | CDA 22 | Probable insulator tracking during light rain. | Pole-top fire | 17/05/2018 18:49 | 1 | Negligible: no ground fire | 9881 | Roadway |  | 20180522UTD_01 | Infrastructure (network-based) | -37.9419 | 145.1021 | 1 | United Energy Distribution | Report | 13066 | 0.026771 | 22kV AC | Moorabbin Airport | 3169 | Clarinda | Crossarm
The attending Fault Crew re-terminated the O/H Service Neutral Conductor at the Reticulation Pole and completed an NST test | 22 CAMBRIDGE STREET, CAULFIELD NORTH VIC 3161 | 30219897 |  |  |  | Corrosion |  |  | 2 | Plumber was work at property when his received an electric shock as he made simultaneous contact between his hand on the water pipe and while standing on the wet ground Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole. | Connector/termination | 0 | 0 | 0 |  | AR010 | connection failure | Minor shock | 27/04/2018 16:00 |  |  | 9890 | Residential |  | 20180523PWA_03 | Infrastructure (network-based) | -37.8622 | 145.0121 | 1 | CitiPower | Report | 12163 | 0.0033056 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Connection
The attending Powercor Fault Crew replaced the existing O/H Service Cable between the Reticulation Pole and Service Pole and the Customers FOLCB located at the POA | 205 ANAKIE ROAD, BELL POST HILL VIC 3215 | 32080754 |  |  |  | Corrosion |  |  | 2 | Tennant was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor between the Reticulation Service Pole Connection Box and the Customerâ€™s FOLCB | Aluminium twisted (grey) | 0 | 0 | 0 |  | CRO022 | Corroded service neutral conductor | Minor shock | 30/04/2018 6:00 |  |  | 9892 | Residential |  | 20180523PWA_05 | Infrastructure (network-based) | -38.098 | 144.3339 | 1 | Powercor | Report | 12165 | 0.023312 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | OH Cable
On arrival crew isolated supply and carried out repairs. | 1 WATERS EDGE CLOSE, BATHUMI VIC 3730 | 60154247 | Working too close to underground cables | [6 empty] | An excavator operator reported that he had hit an UG low voltage cable at the incident location. On arrival the crew found that the excavator had damaged a low voltage underground service cable. There was no ground fire, no reported third party damage or any injuries. | Services cable | 2 | 2 | 2 |  | CME016 | Excavation operations | Damage to network assets | 43377.566 |  |  | 9893 | Public space |  | 20180523PWA_06 | Infrastructure (network-based) | -36.027 | 146.0727 | 1 | Powercor | Report | 12166 | 0.034378 | Low voltage AC (<1kV) | Wangaratta Aero | 3730 | Bathumi | Dug up
REC conducted voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a severely corroded neutral screen on the O/H service cable. The corrosion of the service cable was the result of exposure and deterioration over time. | 455 KEILOR ROAD, NIDDRIE VIC 3042 |  |  |  |  | Neutral fault |  |  |  | A carpenter was removing roofing sheets when he experienced an electric shock when he made contacted the roof sheets | Neutral screen | 0 | 0 | 0 |  |  | Severely corroded neutral screen on the O/H service cable. | Minor shock | 24/05/2018 7:52 |  |  | 9906 |  |  | 20180524JEM_01 | Infrastructure (network-based) | -37.7367 | 144.8902 | 1 | Jemena | Report | 12179 | 0.035903 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | OH Cable
On arrival crew isolated supply and carried out repairs. | 1203 GOORNONG-MAYREEF ROAD, AVONMORE VIC 3559 | 32030650 | Working too close to overhead lines | [5 empty] | 1 | At 11:19 am the Avonmore P7 ACR tripped to lockout. The customer at the incident address reported that a truck had contacted a wire . On arrival the crew confirmed the trailer of a tip truck had contacted a HV SWER between P14 and P15 of the Childs line. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | KYM001 | Tip truck | No Go Zone (contact) | 22/05/2018 11:42 |  |  | 9911 | Commercial |  | 20180525PWA_01 | Infrastructure (network-based) | -36.5086 | 144.5014 | 1 | Powercor | Report | 12184 | 0.023061 | 12.7kV AC (SWER) | Bendigo Airport | 3559 | Avonmore | Vehicle
A LEI attended and identified the damaged lighting bollard had no head on it with the 240v baton holder exposed. The LEI removed the holder from the bollard and proceeded to make it safe by capping the tails and water proof with duct tape. The LEI issued a defect notice advising onsite staff that a REC is required to attend to complete repairs at the Caltex Service Station. | 147 KOORNANG ROAD, CARNEGIE VIC 3163 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Caller advised that her son received an electric shock from the light pole on Sunday night. The cover is missing on the pole and the wires are exposed at the Caltex Service Station in Neerim Road on the corner of Koornang Road near the city side exit. A passerby's son received a strong electric shock to his hand from a private light bollard within the Caltex Service Station. The two year old boy screamed and fell backwards. | Customer installation | 0 | 0 | 0 |  |  | Damaged lighting bollard had no head on it with the 240v baton holder exposed. | Minor shock | 20/05/2018 18:00 |  |  | 9915 | Commercial |  | 20180525UTD_03 | Infrastructure (network-based) | -37.8894 | 145.0568 | 1 | United Energy Distribution | Report | 12188 | 0.030198 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | AF Other
A LEI attended and identified that a voltage of 180v was induced from the "MTS-OR" 66kV overhead conductors near pole No. LIS 3436628. The United Energy Network Control de-energised the 66kV feeder to demonstrate the induction was created from the conductors. The voltage was measured at 0v and returned to 180v when the 66kV feeder was energised. It was concluded with the on-site staff that the crane earthing was insufficient. Once again the following morning, United Energy forwarded the information to our No Go Zone assessors as further assessment could be required. | RAILWAY PARADE, MURRUMBEENA VIC 3163 | 3436628 |  |  |  | Induction |  | Phase to earth | 2 | Matt Green reports the level crossing removal construction team are receiving electric shocks from the on-site crane that is more than 6m from the power lines. The crews have ceased work and cleared the area. Refer also to Report 20180525UTD_02 that occurred on 17/05/2018. The Poath Road, Hughesdale level crossing is being removed as part of the Caulfield to Dandenong Level Crossing Removal Project that will see a new station at Hughesdale constructed. Workers advised their supervisor that slight electric shocks are still being received from the crane stabilizer arms when in the stationary position and the United Energy faults and emergencies call centre was contacted. | Conductor (bare) | 0 | 0 | 0 |  | MTS-OR | Induction to the crane from the 66KV overhead conductors. | Minor shock | 24/05/2018 19:30 |  |  | 9920 | Construction |  | 20180525UTD_05 | Infrastructure (network-based) | -37.8946 | 145.0766 | 1 | United Energy Distribution | Report | 12194 | 0.026931 | 66kV AC | Moorabbin Airport | 3163 | Murrumbeena | Other
On arrival crew isolated supply and carried out repairs | 96 BLYTH STREET, ALTONA VIC 3018 | 30259764 | Working too close to overhead lines | [5 empty] | 1 | Customer reported sparks from junction box on pole at Corner of Blyth and Upton st Altona. There was also reports of nearby properties not having power. There would appear to be vegetation maintenance occurring nearby. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | AL012 | Vegetation clearing | Loss of supply;No Go Zone (contact);Damage to network assets | 23/05/2018 15:12 |  |  | 9930 | Roadway |  | 20180528PWA_04 | Infrastructure (network-based) | -37.8676 | 144.8233 | 1 | Powercor | Report | 12207 | 0.011721 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Trees
CEOT dispatched a fault crew to make safe, investigate and repair. DAO also notified. A three phase overhead connector box was replaced. | 68 WALDARA DRIVE, WALDARA VIC 3678 | 5106454 |  |  |  | Overheated connection |  | Phase to phase |  | IMS 233388. CEOT received a report of a pole fire at the Wangaratta Golf Club. CFA attended. An AusNet Services' fault crew attended and reported that they replaced a completely burnt out 3 phase overhead connector box that had melted at pole LIS 5106454 supplying the Wangaratta Golf Club. The connection box was burnt to the extent there was only blobs of metal representing each phase. It was impossible to ascertain what brand of box it had been and if the failure was caused by overload or a loose connection, or a combination of these. No photos taken. No damage to pole | Connection box | 0 | 0 | 0 |  | wn2 | Melted and burnt out three phase LV connection box. | Other electricity related | 30/04/2018 10:00 | 1 | Negligible: no ground fire | 9929 | Commercial |  | 20180528SPN_03 | Infrastructure (network-based) | -36.3253 | 146.2966 | 1 | AusNet Services Distribution | Report | 12206 | 0.012991 | Low voltage AC (<1kV) | Wangaratta Aero | 3678 | Waldara | Connection
Site made safe Once the Jemena and Powercor crews repaired the damaged assets, Jemena re-energized the LV circuit Techsafe LEI's conducted all required checks and tests as per HVI procedure. inspected premises for safety | 176 MASON STREET, NEWPORT VIC 3015 |  | Vehicle |  |  | HV injection |  |  | 1 | A truck traveling along Mason street in Newport had its boom partially extended and clipped a Powercor owned overhead HV line. The Powercor HV cable came into contact with the Jemena owned LV blue phase line below. The HV injection caused the the blue phase fuse in the local transformer to operate. As a result all the properties on the blue phase on Mason St from Blenheim St to Maddox Rd lost power. TechSafe report attached in "Notes & Findings" section. | Conductor (bare) | 0 | 0 | 0 |  | NT03 | A truck traveling along Mason street in Newport had its boom partially extended and clipped a Powercor owned overhead HV line. The Powercor HV cable came into contact with the Jemena owned LV blue phase line below. | HV injection;Loss of supply | 27/05/2018 14:11 |  |  | 9937 | Residential |  | 20180529JEM_01 | Infrastructure (network-based) | -37.8406 | 144.8673 | 1 | Jemena | Report | 12228 | 0.0025243 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3015 | Newport | Vehicle
Crew sent to site to disconnect. | 16 CLUNES STREET, KINGSBURY VIC 3083 |  | Unauthorised access | [5 empty] | 2 | Jemena contractor come across another unauthorised and illegal BTS pole connection at 16 Clunes St, Kingsbury. Crews attended this evening with an abolishment service order for meter 38990 and SL (service line). When the crews arrived they found the SL was connected into an old small SEC junction box and the meter read showing 24499.0 KWH. It is alleged that the SL and meter has again been relocated to the pole by non Jemena personal from an existing house that has since been demolished Refer to photos. | Service conductor;Aluminium twisted (XLPE);Smart meter | 2 | 2 | 2 |  |  | Unauthorised access by unknown persons to the netwrok. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/05/2018 18:02 |  |  | 9944 | Residential |  | 20180530JEM_01 | Infrastructure (network-based) | -37.7165 | 145.0406 | 1 | Jemena | Report | 12222 | 0.040265 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Kingsbury | Other
Faults crew isolated supply to the public lighting. Public lighting crew identified junction box on pole had been crushed, apparently by excavator. Stray voltage subsequently found on pole due to damaged underground supply cable ( leakage) The pole was subsequently tested to an independent earth and a recording of zero vaults was detected. | THE MELBURNIAN, 236-254 ST KILDA ROAD, SOUTHBANK VIC 3006 | 30194161 | Working too close to underground cables |  |  | Electrical breakdown |  | Phase to earth |  | Chris reports receiving a severe electric shock in his right hand when he leant against steel tramways pole, he was standing on a section of grass at the time. Testing using an independent earth found 210V on the steel pole. | Pole (steel) | 2 | 2 | 2 |  | MP036 | 1. Junction box on steel pole crushed by excavator 2. Underground supply cable damaged causing secondary leakage voltage | Minor shock | 43408.9375 |  |  | 9954 | Roadway |  | 20180531PWA_02 | Infrastructure (network-based) | -37.8261 | 144.9714 | 1 | CitiPower | Report | 12294 | 0.0054097 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | AF Other
On arrival the attending LEI confirmed the circumstances leading to the electric shock with Mr Brown and conducted a visual inspection and voltage testing to an Independent Earth and recorded the following results. The attending Powercor Fault Crew conducted additional testing aloft and recorded a significantly higher voltage at the Transformer. The voltage between the LV Neutral at the Tx and the Tx casing was 242 Volts. The Fault Crew also inspected all Pole Top Junction Boxes and FOLCB, which were all confirmed to be in a serviceable condition. The Transformer was de-energised to allow the Fault Crew to check the LV Earthing system and measure the ground resistance which was confirmed to be within acceptable limits. A limited inspection was conducted on the Transformer, which did not identify any obvious faults contributing to the rising ground voltage. The Transformer was left de-energised pending installation of a replacement transformer which was completed the following day 26 March 2018. The replacement Transformer was commissioned and placed into service by the Powercor Construction Crew and Report Room advised accordingly. TechSafe received a request from the Report Room to revisit the site on 5 April 2018, wherein LEI Wayne Rooke attended site and undertook subsequent voltage tests which confirmed Zero Volts from an Independent Earth to various locations at and around the base of the Transformer Pole and the metallic Pole Guard attached to the Concrete Pole. | 2604 PRINCES HIGHWAY, PORT FAIRY VIC 3284 | 33102476 |  |  |  | Electrical breakdown |  | Phase to earth |  | Mr Paul Brown was taking his Domestic Rubbish Bin to the front of the property at the Road Reserve when he experienced an electric shock to his bare feet as he stepped towards the Powercor Reticulation Transformer Pole. Mr Brown was approximately 1 metre from the base of the Reticulation Transformer Pole when he experienced the electric shock. | Pole mounted | 2 | 2 | 2 |  | KRT022 | not currently identified | Minor shock | 25/03/2018 19:30 |  |  | 9960 | Roadway |  | 20180531PWA_03 | Infrastructure (network-based) | -38.3863 | 142.2068 | 1 | Powercor | Report | 12240 | 0.021377 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 35 ROBERNA STREET, MOORABBIN VIC 3189 | 1816408 |  | Precipitation |  | Leakage |  |  | 2 | ESV reported a sparking pole outside 46 Roberna Street, Moorabbin. Following light rain, a HV tee-off cross arm fire occurred at pole No. LIS 1816408 located outside 35 Roberna Street, Moorabbin. The faults crew identified burn marks on the cross arm and the pole and there was discussion with the Duty Officer as to whether the pole required replacement. | Crossarm (wood) | 0 | 0 | 0 |  | HT 13 | Tracking insulators following light rain. | Pole-top fire | 14/05/2018 21:00 | 1 | Negligible: no ground fire | 9956 | Roadway |  | 20180531UTD_02 | Infrastructure (network-based) | -37.9441 | 145.0678 | 1 | United Energy Distribution | Report | 13065 | 0.0029757 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Crossarm
Fault crew replaced faulty service and supply was left on after re-testing | UNIT 2 177 BROUGHAM STREET, KEW VIC 3101 | 30176828 |  |  |  | Corrosion |  | Phase to earth |  | Chi reports receiving an electric shock when he touched the taps of his bath and shower. | Service conductor | 2 | 2 | 2 |  | Q019 | Corroded service | Minor shock | 43408.0833 |  |  | 9971 | Residential |  | 20180604PWA_01 | Infrastructure (network-based) | -37.7972 | 145.0318 | 1 | CitiPower | Report | 12252 | 0.018811 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | OH Cable
On arrival crew observed pole down and four dead foxes nearby. Crew organised line isolation and replaced the pole. The customer was advised to call an ambulance. The ambulance attended and advised the patient had normal blood pressure but a fluctuating heart beat and a sore hip, he has been taken to Mildura hospital for observation. | HANNIG ROAD, WALPEUP VIC 3507 | 32147282 |  | Lightning |  |  |  | Phase to earth | 1 | A customer reported a pole on ground and conductors low across farming land. The conductor remained just clear of the ground in a live state supported by the post insulator. It would appear that a recent lightning strike had shattered the pole. During later discussion we became aware that an elderly man had attempted to remove the conductors with a shovel from his ute when they had become entangled in them and he was at home after receiving an apparent shock. There was no fire and no reported third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | OYN001 | Lightning strike destroyed pole | Minor shock;Medical attention (first aid/doctor/hospital);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Fatality of livestock, pet or companion animal | 43226.7021 |  |  | 9981 | Agricultural |  | 20180606PWA_02 | Infrastructure (network-based) | -35.0742 | 142.0366 | 1 | Powercor | Report | 12263 | 0.025969 | 12.7kV AC (SWER) | Mildura Airport | 3507 | Walpeup | Lightning
Crew ceased works, first aid administered. investigation initiated | 272 LYGON STREET, CARLTON VIC 3053 | 12769187 |  |  |  | Corrosion | Ineffective planning/procedures/processes |  | 2 | A Cable Jointer was working on an LV mains Tee joint (Paper Lead Cable) as part of a new LV service connection. While cutting the steel outer sheathing from the LV cable with a hacksaw, the Cable Jointer cut through the lead sheathing protecting the LV cores and made contact with one of the LV phases. This resulted in an electrical flash-over between the live conductor and the earthed sheathing. | Cable | 0 | 0 | 0 |  | BQ053 | Inadvertently cut through lead sheath beneath steel cable armouring | Medical attention (first aid/doctor/hospital) | 17/04/2018 10:40 |  |  | 9985 | Roadway |  | 20180607PWA_01 | Infrastructure (network-based) | -37.8004 | 144.9673 | 1 | CitiPower | Report | 12307 | 0.0092373 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Other
A faults crew attended and isolated "Nepean-Station" pole type substation after placing the transformer under LV parallels to maintain supply to occupancies in the area as the transformer LV leads at the krone switch had melted together. The damaged leads and LV krone switch at pole No. LIS 3302246 were replaced under Access Authority conditions and supply restored to normal at the completion of the work. | 28 NEPEAN HIGHWAY, ASPENDALE VIC 3195 | 3302246 |  |  |  | Overheated connection |  |  | 2 | CFA on the way to a pole fire. The CFA contacted United Energy advising there was a reported pole fire in Coleman Road near the corner of Nepean Highway, Aspendale. | Dropper/bridge | 0 | 0 | 0 |  | MC 01 | The probable cause was a loose connection that overheated. | Pole-top fire | 29/05/2018 20:46 | 1 | Negligible: no ground fire | 9986 | Roadway |  | 20180608UTD_01 | Infrastructure (network-based) | -38.0137 | 145.0908 | 1 | United Energy Distribution | Report | 13069 | 0.00386 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | Connection
A private tree branch was removed from the overhead conductors outside 230 Myers Road that supposedly had burn marks near pole No. LIS 3440979. | 230 MYERS ROAD, BALNARRING VIC 3926 | 3440979 |  | Blown branch/vegetation |  |  |  |  | 2 | Customer is reporting the tree is on fire directly in front of the property. No lines are down and the branch is still on the power lines. During strong gusty winds, a caller reports that a tree branch is on fire outside 230 Myers Road, Bittern. | Conductor (bare) | 0 | 0 | 0 |  | HGS 23 | Vegetation: Trees Incident | Other vegetation | 14/04/2018 10:56 | 1 | Negligible: no ground fire | 9988 | Roadway |  | 20180608UTD_03 | Infrastructure (network-based) | -38.3387 | 145.1222 | 1 | United Energy Distribution | Report | 13062 | 0.038356 | 22kV AC | Moorabbin Airport | 3926 | Balnarring | Trees
A faults crew attended and repaired and re-sagged the LV ABC tee-off conductors to Anita Court. In addition, the crew replaced four x two core services to homes supplied from pole No. LIS 1806909 located outside 59 Scarlett Street. Supply was restored to homes upon completion. | SCARLET STREET, MORDIALLOC VIC 3195 | 1806909 | Manned aircraft | [5 empty] | 2 | A pilot has been killed in a small plane crash in a residential street near Moorabbin Airport in Melbourne's south-east. Police said the single-engine Cessna was coming in to land at the airport when it crashed into nearby Scarlet Street, Mordialloc, just after 5:00PM. The light plane clipped the roof of a house and damaged a fence when it came down about 200 metres from the end of the runway at Moorabbin Airport. The sole pilot had been on an hour-long joy flight and the cause of the crash is not yet known. The plane had torn down power lines as it came down and caught fire, with the flames rising higher than seven metres before they were put out by firefighters. No-one else was injured. | Service conductor | 0 | 0 | 0 |  | MC 06 | The cause of the plane crash is not yet known but not related to network assets. | Loss of supply;Damage to network assets | 43318.7153 |  |  | 9992 | Roadway |  | 20180611UTD_01 | Infrastructure (network-based) | -37.9893 | 145.0962 | 1 | United Energy Distribution | Report | 12276 | 0.015356 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Mordialloc | Other
A voltage test between the tap and the conductive metallic shower screen and shower base, as well as various points of the installation, found readings of up to 43 Volts with reference to an independent earth. Investigations revealed the service neutral conductor was damaged at the connection of the neutral service conductor at the Powercor pole. Powercor linesman repaired the service Neutral & CTA carried out N.S.T & Voltage tests following the repairs and normal results were obtained. | 45 CAYLEYS ROAD, WERRIBEE SOUTH VIC 3030 | 30110685 |  |  |  | Corrosion |  | Phase to earth |  | Don received an electric shock when he simultaneously contacted the metallic tap with one hand and the metallic shower base trap with his foot. | Service conductor | 2 | 2 | 2 |  | WBE034 | service neutral connection | Minor shock | 24/04/2018 16:30 |  |  | 10000 | Residential |  | 20180612PWA_05 | Infrastructure (network-based) | -37.9514 | 144.6825 | 1 | Powercor | Report | 12288 | 0.011238 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Connection
On arrival crew isolated supply and carried out repairs. | 46 FIFTH STREET, NICHOLS POINT VIC 3501 | 32140950 | Vehicle | [6 empty] | A customer called to advise that garbage truck had hit a power line. The crew attended and found a service wire had been hit and bought to ground. The crew also reported that the garbage truck had had left site and they were unable to supply further details There was no fire, no reported injuries or third party property damage | Service conductor | 2 | 2 | 2 |  | RCT011 | Garbage truck struck service | Loss of supply;Damage to network assets | 20/04/2018 13:13 |  |  | 10007 | Roadway |  | 20180613PWA_05 | Infrastructure (network-based) | -34.2024 | 142.1932 | 1 | Powercor | Report | 12297 | 0.020119 | Low voltage AC (<1kV) | Mildura Airport | 3501 | Nichols Point | Vehicle
The site was made safe and the HV earth was replaced. | 38 GREGORY STREET W, WENDOUREE VIC 3355 | 30256703 | Copper theft | [6 empty] | A Powercor contractor reported that the HV earth was stolen from the incident location. On arrival the crew found that a High Voltage earth had been stolen. There were no reported injuries or other third party damage. | Earth/earthing | 2 | 2 | 2 |  | BAN002 | Copper theft | Damage to network assets | 26/04/2018 10:28 |  |  | 10009 | Roadway |  | 20180614PWA_02 | Infrastructure (network-based) | -37.5411 | 143.8107 | 1 | Powercor | Report | 12299 | 0.032193 | Earthing cable | Ballarat Aerodrome | 3355 | Wendouree | Other
The site was made safe and repairs will be conducted at a future date. | 12 MIAMI STREET, HAWTHORN EAST VIC 3123 | 30201638 | Copper theft | [6 empty] | A customer (Carole Daves Ph 0417 386 456) reported damage to Powercor assets. On arrival the crew found that a Low Voltage (LV) service cable (Pole to pit) had been stolen from the pole where it had been installed and awaiting final connection to the customer. The damage to the installation was consistent with the cable being ties to a vehicle and reefed from the conduit. There were no reported injuries or other third party damage. | Services cable | 2 | 2 | 2 |  | CL022 | Vandalism, copper theft | Damage to network assets | 23/05/2018 9:35 |  |  | 10031 | Roadway |  | 20180618PWA_05 | Infrastructure (network-based) | -37.8345 | 145.0444 | 1 | CitiPower | Report | 12366 | 0.033326 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Other
Fault crew attended to find a tree branch had fallen through a neutral screen service. Service sparked when it hit the ground but no fire was observed. Crew made safe, replaced the service and restored supply. | 17 BEN CRUACHAN PARADE, COONGULLA VIC 3860 | 2510741 |  | Fallen |  |  |  | Phase to earth |  | IMS 234003 - customer called saying service to house had come down and started small ground fire in the vicinity of the service. Fault crew arrived to find a tree branch had fallen onto and brought down the overhead service which sparked when it hit the ground. No fire was present. Crew made safe, replaced the service and restored supply. | Service conductor | 0 | 0 | 0 |  | MFA22 | Vegetation: Trees Incident | Loss of supply | 16/06/2018 13:43 |  |  | 10032 | Residential |  | 20180618SPN_01 | Infrastructure (network-based) | -37.8949 | 146.7881 | 1 | AusNet Services Distribution | Report | 12926 | 0.035108 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3860 | Coongulla | Trees
On arrival crew isolated supply and carried out repairs. | 32 BANNERMAN STREET, BENDIGO VIC 3550 | 32040059 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross am and pole top had slightly burnt through. There were no injuries, HVI or ground fire | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BET002 | Excessive leakage current | Pole-top fire | 19/02/2018 6:59 | 1 | Negligible: no ground fire | 9359 | Roadway |  | 20180223PWA_09 | Infrastructure (network-based) | -36.7481 | 144.2692 | 1 | Powercor | Report | 11368 | 0.013891 | 22kV AC | Bendigo Airport | 3550 | Bendigo | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 37 MASTERS STREET, CAULFIELD VIC 3162 | 2301975 |  |  |  | Leakage |  |  | 1 | At 1737hrs on 13/02/2018, 11kV feeder CFD13 circuit breaker successfully reclosed and held. The MFB advised of an explosion at the power pole opposite this premise and the pole is on fire. A bird on pole No. LIS 2306514 located in Glenhuntly Road opposite Jasmine Street caused the feeder to reclose and hold. The feeder was patrolled and a severely burnt HV cross arm was identified at OA8806 where the centre phase isolator had been tracking and requires urgent replacement at pole No. LIS 2301975. | Crossarm (wood) | 0 | 0 | 0 |  | CFD 13 | Bird Incident | Pole-top fire | 13/02/2018 17:37 | 1 | Negligible: no ground fire | 9358 | Roadway |  | 20180223UTD_03 | Infrastructure (network-based) | -37.8854 | 145.0254 | 1 | United Energy Distribution | Report | 11367 | 0.038994 | 11kV AC | Moorabbin Airport | 3162 | Caulfield | Animal
On arrival crew isolated supply and commenced repairs | 19 GRANT STREET, BACCHUS MARSH VIC 3340 | 33075351 |  |  |  | Fault on customer installation |  |  |  | MFB reported an overhead service cable on fire at the incident location. On arrival the crew found that the fuse main junction box connected to the overhead service had been on fire. Mains Box had melted and parts had fallen to the ground. There was no ground fire or any other damage caused by this incident. | Customer installation | 2 | 2 | 2 |  | BMH004 | Unable to determine direct cause due to damage. | Melting or smoking only | 17/02/2018 9:15 |  |  | 9385 | Residential |  | 20180226PWA_09 | Infrastructure (network-based) | -37.6769 | 144.4349 | 1 | Powercor | Report | 11404 | 0.012157 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Bacchus Marsh | Fuse
CEOT dispatched a fault crew to investigate. The service line was still normally attached at both ends at the time of arrival attending crew. Metropolitan Fire Brigade on site requested AusNet Services' crew isolate connection. Crews isolated at the pole disconnecting the service tails which were tied back. | 193 HIGH STREET, THOMASTOWN VIC 3074 | 908465 | Unknown external/community factor | [6 empty] | IMS 232512. Police called AusNet Services to advise of a fatality when a person stood on roof of shop and cut a service line with bolt cutters. Electrocution of an individual who came into contact with an AusNet Services' electrical overhead service attached to a shop front above a shared cantilevered veranda. | Service conductor | 0 | 0 | 0 |  | tt9 | The person allegedly cut the service line with bolt cutters. | Electrocution | 23/02/2018 3:15 |  |  | 9369 | Commercial |  | 20180226SPN_04 | Infrastructure (network-based) | -37.6807 | 145.0136 | 1 | AusNet Services Distribution | Report | 11383 | 0.033692 | Low voltage AC (<1kV) | Essendon Airport | 3074 | Thomastown | Other
CEOT dispatched a fault crew to make safe, switch, investigate and repair fault. CEOT also advised the local DAO. Crew isolated supply and repaired the fault. Supply restored. | BURRAGAH, 138 JOINERS ROAD, NEWMERELLA VIC 3886 | 1905975 |  | Lightning |  | Conductor clashing |  |  | 1 | IMS 232554. Report of lightning striking a 22/66kV pole and a fire started in the vicinity. The attending fault crew also discovered a burnt HV bridge at the pole. It was found that the bridging pin broke (see photo image 629). No visible evidence as to why it broke but residence said there was some lightning at the time of the fault. The broken HV insulator caused the bridge to come into contact with another HV phase and thus tripped the HV line out. Feeder CB tripped to lockout. The other photos show that a fire was in the vicinity of the base of the pole and spread to another paddock. Approximate fire size was 300 sq. metres of burnt grass. | Insulators;Dropper/bridge | 0 | 0 | 0 |  | nla34 | 22kV insulator holding a bridge to Drop Out Fuse broke and the bridge became free and clashed with another phase of the 22kV network. | Grassfire | 24/02/2018 17:37 | 1 | Small: 10 - 1000 sq.m | 9371 | Agricultural |  | 20180226SPN_05 | Infrastructure (network-based) | -37.7435 | 148.4049 | 1 | AusNet Services Distribution | Report | 11764 | 0.024251 | 22kV AC | Bairnsdale Airport | 3886 | Newmerella | Lightning
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for any necessary repairs. Myrtleford Fault crew dispatched to site. The fault crew found no damage or evidence of an incident. The paragliders had already left the site. No reclose or fuse operation was recorded. The local DAO made contact with the Paragliding company (Wally) and discussed the incident. The company has dedicated paddocks for landing but in this incident the glider made an error and landed in the wrong paddock. The DAO provided a map of the local AusNetâ€™s Services' network for their reference. | FERGUSON LANE, BOWMANS FOREST VIC 3735 | 4500351 | Manned aircraft | [6 empty] | IMS 232550. Initial Report: CEOT received a call that a paraglider had crashed into a conductor. Person ok, but chute stuck in the conductor. CEOT received a further call to say the chute had fallen through the conductor to the ground. The conductor is a SWER line. Final Report: At 4:47PM Sunday 25th February, fault call was received that a paraglider had crashed into a SWER 3/12 conductor near pole 4500351 by the Paraglider company owner (Wally - tel. 0481 283 489). Person OK (Mick Kennish +64221504700 NZ), but the chute was stuck in the overhead HV conductor. Received further call to say that the chute had fallen through the HV conductor to the ground. Please note that the location of the fault does not have a property address. The paddock resides in Ferguson Lane, Lot 3 approximately 500m to the North of Sinclair Lane on West. See attached maps. | Conductor (bare) | 0 | 0 | 0 |  | myt7 | A paraglider made contact with a SWER conductor. | No Go Zone (contact) | 25/02/2018 16:45 |  |  | 9375 | Agricultural |  | 20180226SPN_06 | Infrastructure (network-based) | -36.4366 | 146.624 | 1 | AusNet Services Distribution | Report | 11390 | 0.034699 | 12.7kV AC (SWER) | Wangaratta Aero | 3735 | Bowmans Forest | Other
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. Fault crew made safe. Construction crew dispatched to rectify fault. Vegetation Section performed on-site assessment and provided report - NO GRASS FIRE, NOT ABLE DETECT ANY BURNT GRASS. | 2 CLEGG ROAD, MOUNT EVELYN VIC 3796 | 1014208 |  | Blown branch/vegetation |  |  |  | Phase to phase | 1 | IMS 232555. TREE HAS FALLEN THROUGH HV AND LV RESULTING IN BURN DAMAGE ON HV AND LV CONDUCTORS AND A SMALL 1 METRE SQUARE GROUND FIRE. HV Sectionaliser operated until 40 A Boric Acid HV Fuse operated LD346. Vegetation section report: Small branch out of a eucalypt has sailed in strong winds (10mm diameter approx. 500mm long) and contacted HV and burnt on line. Unable to determine which tree. No evidence of a ground fire. | Conductor (bare) | 0 | 0 | 0 |  | ldl13 | Vegetation: Trees Incident | Hung-up fuse only;Melting or smoking only | 25/02/2018 8:43 |  |  | 9376 | Residential |  | 20180226SPN_07 | Infrastructure (network-based) | -37.7901 | 145.3887 | 1 | AusNet Services Distribution | Report | 13386 | 0.004265 | 22kV AC | Moorabbin Airport | 3796 | Mount Evelyn | Trees
Emergency switching was completed and the substation placed under LV parallel to maintain supply to customers in the vicinity. The faulty transformer was replaced, LV parallels removed and supply restored to normal. The oil spill was immediately contained and cleaned up in accordance with United Energy requirements. | 55 LYPPARDS ROAD, LANGWARRIN VIC 3910 | 3312536 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | Per CFA - Fire at transformer. Following a spell of hot weather, a LV bushing at "Lyppards-Cranbourne" pole type substation melted and leaking oil fell to the dry grass below and a small 2sqm fire started. The 100kVA transformer was isolated at pole No. LIS 3312536 and requires replacement. | Pole mounted | 0 | 1 | 0 |  | LWN 21 | Probable loose, overheated connection to the transformer. | Grassfire | 22/02/2018 19:55 | 1 | Localised: less than 10 sq.m | 9389 | Roadway |  | 20180227UTD_01 | Infrastructure (network-based) | -38.1308 | 145.2222 | 1 | United Energy Distribution | Report | 13024 | 0.021823 | Low voltage AC (<1kV) | Moorabbin Airport | 3910 | Langwarrin | AF Other
On arrival crew isolated supply and commenced repairs | 839 COLLINS STREET, DOCKLANDS VIC 3008 | 30312941 | Working too close to underground cables | [5 empty] | 1 | A CitiPower fault crew attending an outage found that an UG HV cable had been contacted by a borer head at the incident location. Protection operated. No fire or injuries reported. | Cable | 2 | 2 | 2 |  | WG038 | Interference by Directional borer | No Go Zone (contact);Damage to network assets | 26/02/2018 11:22 |  |  | 9395 | Roadway |  | 20180228PWA_01 | Infrastructure (network-based) | -37.8217 | 144.9443 | 1 | CitiPower | Report | 11417 | 0.0029225 | 11kV AC | Essendon Airport | 3008 | Docklands | Dug up
ESV has been advised via phone, reference no. 9432651 Trees trimmed and spreaders installed on LV Electrical inspectors assessed damages at all reported properties and issued damage notices. All properties left on supply | 46 GRANGE ROAD, AIRPORT WEST VIC 3042 |  |  | Council |  | Conductor clashing |  |  |  | Suspected injection into LV neutral conductor Electrical inspector attended site, but could not confirm whether it was a high voltage injection as the circuit was energised prior to arrival Techsafe report has been attached in "Notes & Findings" section | Conductor (bare);Customer installation | 0 | 0 | 0 |  | AW07 | Vegetation: Trees Incident | HV injection | 28/02/2018 11:30 |  |  | 9408 | Residential |  | 20180301JEM_01 | Infrastructure (network-based) | -37.7304 | 144.8839 | 1 | Jemena | Report | 11449 | 0.037009 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Airport West | Conductor
On arrival crew isolated supply and carried out repairs. | BOUNDARY ROAD, TIMBOON WEST VIC 3268 | 30255711 |  | Blown branch/vegetation |  |  |  |  | 1 | Emergency services reported power lines down and had possibly caused a fire. On arrival the attending crew found a tree had broken brought down 3 HV conductors between poles 35 and 36 of the Peterborough line. There was a fire of some 200 by 20 m on private property. Crew advise large gum tree broke approximately 1 metre above the ground during high winds. There were no reported shocks or injuries | Conductor (bare) | 2 | 2 | 2 |  | TRG005 | Vegetation: Trees Incident | Loss of supply;Grassfire | 28/02/2018 14:41 | 1 | Medium: 1000 sq.m - 10 ha | 9396 | Agricultural |  | 20180301PWA_01 | Infrastructure (network-based) | -38.507 | 142.9341 | 1 | Powercor | Report | 11431 | 0.034396 | 22kV AC | Warrnambool Airport Ndb | 3268 | Timboon West | Trees
On arrival crew isolated supply and carried out repairs. | TIVERTON, 1316 DARLINGTON-NERRIN ROAD, DUNDONNELL VIC 3271 | 30047629 |  |  |  | Moisture ingress |  |  |  | Customer reported information about a potential cause of an outage and that â€œa transformer had arced out caused a fire but has now been put outâ€. On arrival the attending crew found a HV fuse had mal-operated . Parts of the fuse barrel had fallen to the ground and there was a fire of some 150 by 6 m on the road reserve. There were no reported shocks or injuries. | EDO fuse | 2 | 2 | 2 |  | CDN006 | EDO fuse Barrel hung up | Grassfire | 28/02/2018 18:39 | 1 | Small: 10 - 1000 sq.m | 9405 | Roadway |  | 20180301PWA_03 | Infrastructure (network-based) | -37.8815 | 142.9734 | 1 | Powercor | Report | 11436 | 0.00065625 | 22kV AC | Warrnambool Airport Ndb | 3271 | Dundonnell | Fuse
Emergency high voltage switching was completed and repairs were completed to the electrical infrastructure under electrical access permit conditions. Supply was restored upon completion. | 74 HYSLOPS ROAD, BONEO VIC 3939 | 1308857 |  | Prone to salt deposition |  | Electrical breakdown;Leakage |  |  | 2 | Pole fire was reported at pole number 1308857. A pole fire occurred at the high voltage on pole No. LIS 1308857 located outside 64 Hyslops Road, Boneo. The fire was contained to the pole that started near the king bolt. | Pole (wood) | 0 | 0 | 0 |  | RBD 12 | The pole is located in the vicinity of the Ocean and Bay and tracking may have been the most likely cause. | Pole-top fire | 26/02/2018 14:06 | 1 | Negligible: no ground fire | 9404 | Agricultural |  | 20180301UTD_02 | Infrastructure (network-based) | -38.4041 | 144.9363 | 1 | United Energy Distribution | Report | 13025 | 0.020037 | 22kV AC | Moorabbin Airport | 3939 | Boneo | Crossarm
The LV connection was repaired at pole number LIS 1805141 and supply restored to customers in the vicinity. | 19 YUILLE STREET, BRIGHTON VIC 3186 | 1805141 |  | Heat |  | Overheated connection |  |  | 2 | Caller reports one of the phases on the pole is burning and there are flames that has set the grass alight. During warm weather conditions, the white phase LV connection to the transformer isolator at "Yuille-Roslyn" pole type substation failed due to probable overload. Molten metal fall onto the nature strip and a small 0.5sqm grass fire that was out when the crew arrived. | Dropper/bridge | 0 | 0 | 0 |  | MR 32 | A loose connection was created due to probable overload. | Grassfire | 27/02/2018 16:53 | 1 | Localised: less than 10 sq.m | 9407 | Roadway |  | 20180301UTD_03 | Infrastructure (network-based) | -37.9272 | 145.0008 | 1 | United Energy Distribution | Report | 13026 | 0.026586 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Connection
Emergency HV switching was completed and the substation was isolated with Live Line Clamps lifted at the tee-off and an Access Authority was issued to cut and remove the branch. The branch was removed and supply restored upon completion. | 184 HIGH STREET, HASTINGS VIC 3915 | 1110404 |  | Blown branch/vegetation |  |  |  |  | 2 | The CFA on site as the wires are arcing and sparking. During strong winds, a council tree branch fell on the HV overhead conductors in the tee-off to "High-Tavern" substation near pole No. 1110404. A small 2sqm grass fire started in the dry grass below the conductors that was extinguished by the CFA. | Conductor (bare) | 0 | 0 | 0 |  | HGS 21 | Vegetation: Trees Incident | Grassfire | 28/02/2018 11:11 | 1 | Localised: less than 10 sq.m | 9409 | Roadway |  | 20180301UTD_04 | Infrastructure (network-based) | -38.3074 | 145.1794 | 1 | United Energy Distribution | Report | 13027 | 0.0032894 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Trees
The area was made safe and the single phase overhead service removed with a defect notice issued to the home owner as the POA was damaged and required repairs before supply can be restored. | 464 WAVERLEY ROAD, MOUNT WAVERLEY VIC 3149 | 602741 |  | Wind;Fallen;Property owner/customer |  |  |  |  | 2 | The MFB advised of a pole fire after a tree fell over a powerline and the customer has lost their electricity supply. During strong winds, a customers gum tree in their front yard broke and fell over the single phase overhead service bringing it down. A tree branch caught of fire and subsequently caused a small fire to start on the nature strip. | Service conductor | 0 | 0 | 0 |  | GW03 | Vegetation: Trees Incident | Grassfire | 28/02/2018 16:45 | 1 | Localised: less than 10 sq.m | 9410 | Residential |  | 20180301UTD_05 | Infrastructure (network-based) | -37.886 | 145.1375 | 1 | United Energy Distribution | Report | 13028 | 0.029344 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Trees
ESV notified via phone, reference no. 9444183 Site made safe, feeder patrolled, bird found at the base of concrete pole no. A056421. Damage to conductor found and repaired. CFA attended and extinguished grass fire. | 285 LOEMANS ROAD, BULLA VIC 3428 | Pole no. A056421 |  | Bird |  |  |  |  | 2 | Bird contact caused Jemena conductor to fall to ground and cause a grass fire in HBRA There were no injuries or property damage as a result of the incident Photos attached in the "Notes and Findings" section | Pole (concrete) | 0 | 0 | 0 |  | KTS-SBY | Bird Incident | Grassfire | 43134.5229 | 1 | Medium: 1000 sq.m - 10 ha | 9415 | Peri-urban |  | 20180302JEM_02 | Infrastructure (network-based) | -37.6702 | 144.7964 | 1 | Jemena | Report | 13016 | 0.025051 | 66kV AC | Melbourne Airport | 3428 | Bulla | Animal
Defect notice issued on the new connections | 29-33 HAWKER STREET, AIRPORT WEST VIC 3042 |  | Building too close or within the No Go Zone | [5 empty] | 2 | No go zone breach occurred during new connection to property (no. 29-33 Hawker Street, Airport West). Builder/REC placed pole in the next door property (no. 35 Hawker Street, Airport West). The overhead service at no. 35 has been pulled to the side and cable tied to the pole. | Aluminium twisted (grey) | 0 | 0 | 0 |  | AW05 | Builder/REC did not comply to the clearances mandated by regulations and No Go Zone Rules | No Go Zone (contact) | 23/02/2018 11:30 |  |  | 9417 | Commercial |  | 20180305JEM_01 | Infrastructure (network-based) | -37.7226 | 144.8883 | 2 | Jemena | Report | 11455 | 0.014419 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Airport West | Other
The crews replaced the Blue and White phase Flexâ€™s and inspected the Red phase which was in good order. | 7507 MORTLAKE-ARARAT ROAD, MAROONA VIC 3377 | 33054332 |  |  |  | Corrosion |  |  | 1 | Emergency Services reported a grass and scrub fire at the incident location. On arrival the attending crew found a HV Flex on the white phase had failed causing it to flash over on the blue phase. The result has caused two grass fires, one 20 mtrs x 75 mtrs and the second 5 mtrs x 5 mtrs both in the road reserve and customers property which had been extinguished by the CFA prior to Powercor attendance . There were no reported shocks or injuries | Dropper/bridge | 2 | 2 | 2 |  | ART033 | Overheated connection | Grassfire | 43162.5854 | 1 | Medium: 1000 sq.m - 10 ha | 9423 | Agricultural |  | 20180306PWA_01 | Infrastructure (network-based) | -37.4225 | 142.8569 | 1 | Powercor | Report | 11461 | 0.024352 | 22kV AC | Hamilton Airport | 3377 | Maroona | Connection
The LEI, Damian Harris, tested all customer connections and confirmed no HVI and no damage to customer property. The site was made safe and appropriate repairs were made. | 44 TALBOT STREET, ALTONA MEADOWS VIC 3028 | 32177509 |  |  |  | Leakage |  |  |  | Report was received of a HV conductor down at pole LIS 213813 Cnr of Talbot st and Alma Ave. Possible HVI, LEI required. On arrival the crew found, that a HV conductor fell on to LV due to a burnt off HV crossarm cross arm. This resulted in the outer phase HV conductor falling on top of the LV conductors. There was no ground fire, no third party damage or injuries reported. | Crossarm (wood) | 2 | 2 | 2 |  | LVN022 | Excessive leakage current | Pole-top fire | 43193.4 | 1 | Negligible: no ground fire | 9426 | Roadway |  | 20180306PWA_02 | Infrastructure (network-based) | -37.8699 | 144.7856 | 1 | Powercor | Report | 11466 | 0.018579 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3028 | Altona Meadows | Crossarm
On arrival crew isolated supply and commenced repairs. | UNIT 1 29 MURRAY STREET, APOLLO BAY VIC 3233 | 30052457 |  |  |  | Unknown technical factor |  |  |  | Crew reported FSD burnt out and had caught fire. Customers underground service burnt off. There was no ground fire, no reported injuries | Connection box | 2 | 2 | 2 |  | CLC007 | Unable to determine | Pole-top fire | 18/01/2018 0:54 | 1 | Negligible: no ground fire | 9448 | Roadway |  | 20180309PWA_01 | Infrastructure (network-based) | -38.751 | 143.6633 | 1 | Powercor | Report | 11498 | 0.010566 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Fuse
On arrival crew isolated supply and carried out repairs | 980 TWO TREE ROAD, CARAG CARAG VIC 3623 | 30255469 |  | Bird |  |  |  |  | 1 | Vic Fire reported grass fire and fuses down near intersection of Two Trees Rd and Geodetic Rd Carag Carag. On arrival the crew found evidence of a flashover on the Boric Acid fuse unit. Flash over marks on fuse unit bracket. An Area of approx. 80m x 20m of burnt grass in road reserve. Also a small amount of damage was noticed on the fence adjacent to the road reserve. There was no reported injuries . | Boric acid | 2 | 2 | 2 |  | SHP021 | Bird Incident | Grassfire | 43315.6215 | 1 | Medium: 1000 sq.m - 10 ha | 9455 | Roadway |  | 20180309PWA_03 | Infrastructure (network-based) | -36.4988 | 144.9308 | 1 | Powercor | Report | 11505 | 0.039119 | 22kV AC | Mangalore Airport | 3623 | Carag Carag | Animal
A LEI and faults truck attended and commenced an investigation to the cause. Initial testing at the customer premises had the NST passing with a minor voltage of 0.1v measured on the shower taps and customer earthing system with tests at the grouped meter panel indicating the same result. The faults crew checked all overhead service connections at pole number LIS 2306830 with no faults identified. They proceeded to check connections at the POA and a faulty neutral connection was identified that was cleaned, greased and re-terminated. Installation tests confirmed there were no further issues and the occupier was advised of the rectification work with supply left on. | UNIT 2 113 ADDISON STREET, ELWOOD VIC 3184 | 2306830 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | REC advised the tenant has experienced shocks in the shower during the past week. The occupier advised the Metropol Estate Agent that electric shocks had been received from the shower taps and a REC was called who proceeded to contact the United Energy faults and emergencies call centre as he suspected the problem is with the reticulations neutral. | Customer installation | 0 | 0 | 0 |  |  | Deteriorated neutral connection in the consumers FMJB. | Minor shock | 43223.7083 |  |  | 9458 | Residential |  | 20180312UTD_01 | Infrastructure (customer connection) | -37.8811 | 144.9801 | 1 | United Energy Distribution | Report | 11509 | 0.020958 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | Connection
The glove and barrier crew cut the tree and the site was made safe. | 19 SPENSER STREET, ST KILDA VIC 3182 | 2306019 |  | Alive;Property owner/customer |  |  |  |  | 2 | Warren from Citipower passed on a report from the MFB of a palm tree on fire. A private palm tree located at 19 Spenser Street was touching the 11kV overhead conductors and burning. As the conditions were benign at the time, it was decided to utilise a glove and barrier crew the following morning in daylight to safely cut the palm tree to code away from the HV conductors near pole number LIS 2306019. | Conductor (bare) | 0 | 0 | 0 |  | EW 12 | Vegetation: Trees Incident | Other vegetation | 43284.9431 | 1 | Negligible: no ground fire | 9472 | Residential |  | 20180313UTD_04 | Infrastructure (network-based) | -37.8697 | 144.9774 | 1 | United Energy Distribution | Report | 13035 | 0.033297 | 11kV AC | Essendon Airport | 3182 | St Kilda | Trees
A faults crew promptly attended, isolated supply and replaced the pole mounted FOLCB and re-terminated the underground service cable. | 945 MOOROODUC HIGHWAY, MOOROODUC VIC 3933 | 1104826 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | CFA report of a pole fire at pole number 11004826 at a property named "Shedbarmah Park". A pole fire occurred at pole number LIS 1104826 located outside 945 Moorooduc Road. The pole box supplied an underground cable and its suspected the cause was a loose and overheated connection to the property on the warm day. Molten metal fell into the dry grass below that was quickly extinguished. | Connection box | 0 | 0 | 0 |  | MTN 24 | The most likely cause was a loose and overheated connection in the pole mounted FOLCB on the warm day. | Grassfire | 43376.7861 | 1 | Localised: less than 10 sq.m | 9476 | Roadway |  | 20180313UTD_06 | Infrastructure (network-based) | -38.2496 | 145.0822 | 1 | United Energy Distribution | Report | 13038 | 0.012368 | Low voltage AC (<1kV) | Moorabbin Airport | 3933 | Moorooduc | Connection
Site made safe HV crossarm replaced | 26 BROWN STREET, AVONDALE HEIGHTS VIC 3034 | pole no. A047650 |  |  |  | Leakage |  |  | 1 | HV crossarm fire HV crossarm burnt and broken and sitting between red and neutral conductors No ground fire No photo is available | Crossarm (wood) | 0 | 0 | 0 |  | BY11 | Tracking/electrical leakage | Pole-top fire | 43103.3313 | 1 | Negligible: no ground fire | 9484 | Residential |  | 20180314JEM_04 | Infrastructure (network-based) | -37.7672 | 144.8551 | 1 | Jemena | Report | 11548 | 0.020926 | 22kV AC | Essendon Airport | 3034 | Avondale Heights | Crossarm
On arrival crew isolated supply and arranged for lighting replacement. | 146 EUREKA STREET, BALLARAT EAST VIC 3350 | 30262779 |  |  |  | Overheated connection |  |  |  | VicFire reported a pole fire at the incident location. On arrival the crew found that the wiring in the 80w Mercury Vapour Street Light attached to this pole had shorted and had melted / burned the wiring in the Street Light. There was no ground fire. There were no injuries. | Public lighting | 2 | 2 | 2 |  | BAN015 | unable to determine due to damage | Pole-top fire | 43407.0722 | 1 | Negligible: no ground fire | 9487 | Roadway |  | 20180315PWA_02 | Infrastructure (network-based) | -37.5658 | 143.8732 | 1 | Powercor | Report | 11551 | 0.016605 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat East | AF Other
On arrival crew isolated supply and carried out repairs. | 171-205 TROUPS ROAD S, TRUGANINA VIC 3029 | 30108240 |  |  |  | Leakage |  |  |  | CFA reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm had slightly burnt through. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MLN021 | Excessive leakage current | Pole-top fire | 13/03/2018 6:40 | 1 | Negligible: no ground fire | 9488 | Roadway |  | 20180315PWA_03 | Infrastructure (network-based) | -37.748 | 144.6674 | 1 | Powercor | Report | 11552 | 0.015331 | 22kV AC | Laverton Raaf | 3029 | Truganina | Crossarm
Crew corrected connections in lantern | 101 GRATTAN STREET, CARLTON VIC 3053 | 30203653 |  |  |  |  | Faulty tools/plant/equipment |  | 2 | A public lighting crew attended a public lighting fault report at the incident location. On arrival the crew found that the pole had 240 Volts from the pole to an independent earth when the cascade system was energised. The crew found that the active tail was connected to earth terminal inside the lantern. The crews corrected the connections and tested the pole and there was zero volts. There were no reported shockâ€™s, injuries, fire or damaged to third party as a result of this incident. | Public lighting;Pole (steel) | 0 | 0 | 0 |  | BQ015 | transposed connection | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/12/2017 22:00 |  |  | 9494 | Roadway |  | 20180315PWA_04 | Infrastructure (network-based) | -37.8007 | 144.966 | 1 | CitiPower | Report | 11559 | 0.031152 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Connection
CEOT dispatched a fault crew to make safe, and carry out/arrange for any necessary repairs. CEOT also informed the local DAO. Crew attended and found a bat on HV transformer and 40 sq. metre grass fire in vicinity. Secondary cause found to be faulty HV earth. Damaged section of LV earth repaired. HV earth replaced. Due to concern with customer's installation, the AusNet Services' LEI arranged to check the installation to ensure integrity of customer's installation and that there are no dangers to the customer from the fault. | 1522 MURRAY VALLEY HIGHWAY, HUON VIC 3695 | 5214098 |  | Bird |  |  |  | Phase to earth | 1 | IMS 232843. Report of all supply failure and alleged grass fire in vicinity. The attending fault crew found a bat on the HV transformer and a 40m sq. metre grass fire in the vicinity. Bat was between EDO fuse unit and earth system (on EDO unit between flag bolt and EDO bracket). Feeder CB tripped. Electrical protection operation details: 15/3/18 01:22:55, WOTS13 tripped & reclosed on Red ph TOC1, SEF & Negative Sequence. Last Trip Amps R=525A, W=75A, B=58A, N=504A. WO106 Phase 1 - L1 & EARTH FAULT - L1 & L2, SEF. | Transformer | 0 | 0 | 0 |  | wots13 | Bird Incident | Grassfire | 15/03/2018 1:34 | 1 | Small: 10 - 1000 sq.m | 9493 | Agricultural |  | 20180315SPN_01 | Infrastructure (network-based) | -36.2403 | 147.0957 | 1 | AusNet Services Distribution | Report | 11558 | 0.034468 | 22kV AC | Wangaratta Aero | 3695 | Huon | Animal
A LEI and faults truck attended and completed an IR test on the underground service cable and the consumer mains entering the property. They observed the service pit to be located higher than the service pole conduit behind the steel protective covers. The water would drain into the pit and then into the conduit crossing the road to the service pole. All tests passed and the LEI instructed the fault crew to re-terminate the consumers mains in the pit with IPC connectors. A NST at the meter position passed and the LEI recommended that an underground crew to check the pit and surrounding drainage. At the time of testing, there hasn't been rain for 41 days and no water was bubbling out of the conduit. | 390 BALDRYS ROAD, MAIN RIDGE VIC 3928 | 1308687 |  |  |  | Moisture ingress |  | Phase to earth | 2 | A meter technician was working in the vicinity and a customer advised that an electric shock had been received from a pole when heavy rain occurs. Mentions that bubbling water comes out of the white conduit at pole number 1308687 and at least one person has received an electric shock. A customer advised a United Energy meter technician that an electric shock had been received from pole number LIS 1308687 located outside 390 Baldrys Road. This pole is a substation pole named "Baldrys-Raymond" substation. Please note, the same customer reported of receiving electric shocks from the water on 09/08/2017 and no cause was found. Incident Report 20170811UTD_01. | Services pit | 0 | 0 | 0 |  |  | The cause could be attributed to the service pit to be located higher than the service pole conduit. | Minor shock | 13/03/2018 18:25 |  |  | 9492 | Roadway |  | 20180315UTD_03 | Infrastructure (network-based) | -38.4061 | 144.9548 | 2 | United Energy Distribution | Report | 11556 | 0.0056088 | Low voltage AC (<1kV) | Moorabbin Airport | 3928 | Main Ridge | AF Other
On arrival crew carried out isolation of supply and completed repairs. | 30 WILSONS ROAD, PORTLAND VIC 3305 | 32134173 |  |  |  | Leakage |  |  |  | Vicfire reported a pole on fire at the incident location. On arrival the crew found that a 22kV angle pole was on fire just below the steel cross arm. The crew attempted to isolate supply, however the pole burnt off before the isolation was completed, resulting in the crossarm and conductors falling to the ground causing a small grass fire on the road reserve of around 20m2 in size. There were no injuries, and no other damage reported. | Pole (wood) | 2 | 2 | 2 |  | PLD002 | Excessive leakage current | Pole-top fire;Grassfire | 15/03/2018 15:12 | 1 | Small: 10 - 1000 sq.m | 9501 | Public space |  | 20180316PWA_02 | Infrastructure (network-based) | -38.3306 | 141.5872 | 1 | Powercor | Report | 11568 | 0.015531 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Pole
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for any necessary repairs. CFA on site. Fire under control. HV BA fuses replaced. Restored supply to customers. | FEN FARM, 7890 SOUTH GIPPSLAND HIGHWAY, ALBERTON VIC 3971 | 2608311 |  | Bird |  |  |  |  | 1 | IMS 232875. Initial report: Bird found dead @ LIS: 2608311. Both 22kV SWER ISO fuses blown @ YM049. 25 square meter ground fire in the vicinity. Final report: Switch YM049 old Welshpool Rd SWER ISO ftr023. A Starling bird caused both 12k BA fuses at ISO to blow. A dead bird was found on the ground at base of pole and fire started in this area in mown grass area of customer driveway. Fire has burnt in long grass back into the direction of wind since mown area offering little fuel and was on down wind side. Fire size 9mx7m. Temperature 30 degrees C, wind 19 km/h, humidity 29%, Fire Rating Very High at Alberton. HV fuses operated. | Conductor (bare) | 0 | 0 | 0 |  | ftr23 | Bird Incident | Grassfire | 17/03/2018 16:00 | 1 | Small: 10 - 1000 sq.m | 9512 | Agricultural |  | 20180319SPN_02 | Infrastructure (network-based) | -38.6251 | 146.6351 | 1 | AusNet Services Distribution | Report | 11584 | 0.027682 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3971 | Alberton | Animal
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out /arrange for necessary repairs. CFA called and controlled the fire. An AusNet Services' Operator made safe. Repairs to be done during the day (19-03-2018). Final report: The construction crew upon attendance only noticed a small singe to the tree and no ground fire. The tree clearers arrived and had to be shown where the tree had come into contact and where the tree had singe marks on it. Tree clearers have removed the head of the tree after construction had completed to remove the issue. No DAO attendance and no photos taken. | 906 BONA VISTA ROAD, GAINSBOROUGH VIC 3822 | 2705515 |  | Blown branch/vegetation |  |  |  | Phase to earth | 2 | IMS 232881. Initial report: Tree on line caused conductors to break @ LIS: 2705515. 1 square metre grass fire in vicinity. Final report: A Cypress tree was blown into the HV conductor due to the extremely strong winds. NO PHOTOS WERE TAKEN. | Conductor (bare) | 0 | 0 | 0 |  | wgl23 | Vegetation: Trees Incident | Grassfire | 18/03/2018 17:40 | 1 | Localised: less than 10 sq.m | 9516 | Agricultural |  | 20180319SPN_04 | Infrastructure (network-based) | -38.2207 | 145.9836 | 1 | AusNet Services Distribution | Report | 12028 | 0.0046111 | 22kV AC | Morwell (Latrobe Valley Airport) | 3822 | Gainsborough | Trees
Initial Report: CEOT DISPATCHED TO FAULT CREW TO MAKE SAFE, ISOLATE INVESTIGATE AND CARRY OUT / ARRANGE FOR NECESSARY REPAIRS. CREW ISOLATED & MADE SAFE. CEOT NOTIFIED THE LOCAL DAO. Final Report: Benalla fault truck arrived on site, made safe and contacted the DAO for a second truck to assist. HV conductor repaired and line returned to service. Replaced 2 x blown HV fuses at Switch 814478. The tree was pushed over with earth moving equipment and grubbed out. | ALMARU, 2365 BENALLA-TOCUMWAL ROAD, YUNDOOL VIC 3727 | 3911226 |  | Wind;Fallen |  |  |  |  | 1 | IMS 232877. Initial Report: UNDER INCD-167962-r @ LIS #3911225 - #3911226 TREE BROUGHT DOWN HV. LARGE GRASS FIRE REPORTED IN AREA. ON ARRIVAL @ SW #814478 FOUND 2X BLOWN FUSES. Final Report: A large limb on mature Sugar Gum positioned 28m from the closest HV conductor failed in extreme weather conditions. The limb contacted the closest conductor creating a break resulting in the conductor falling to ground. A fire ignited in the dry grass and burnt an area 100m wide x 2,000m long in an easterly direction fanned by extreme, gusty, westerly winds. The fire jumped the Benalla â€“ Tocumwal Rd. and raced through a cereal stubble paddock and then out onto sparsely grassed pasture land where it became more accessible and controllable and was extinguished. The fire area covered multiple properties. Started in 2365 Benalla-Tocumwal Rd, Yundool. Other properties were 2535 Benalla-Tocumwal Rd, Yundool and Crown Allotments (owner Anker Farms Pty Ltd). The tree was a private tree and was outside the vegetation clearance space. | Conductor (bare) | 0 | 0 | 0 |  | bn2 | Vegetation: Trees Incident | Grassfire | 18/03/2018 12:47 | 1 | Large: more than 10 ha | 9519 | Agricultural |  | 20180319SPN_05 | Infrastructure (network-based) | -36.2817 | 145.8194 | 1 | AusNet Services Distribution | Report | 11595 | 0.018903 | 22kV AC | Shepparton Airport | 3727 | Yundool | Trees
On arrival crew made site safe and commenced repairs | 2 MILL ROAD, LARA VIC 3212 | 30064782 | Vehicle | [6 empty] | Vicfire reported that a car had hit a pole at the incident location. On arrival the crew found that a Vehicle had struck a HV/LV Intermediate pole, resulting in a fatality to one of the occupants of the vehicle. No other details were available. There was no fire. | Pole (wood) | 2 | 2 | 2 |  | FNS012 | Vehicle struck pole | Not involving electrocution;Damage to network assets | 17/03/2018 5:17 |  |  | 9532 | Roadway |  | 20180320PWA_02 | Infrastructure (network-based) | -38.0196 | 144.4151 | 1 | Powercor | Report | 11612 | 0.00053356 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3212 | Lara | Vehicle
The large private eucalyptus tree that had split in half was cut away and supply restored to customers in the vicinity. | 35 STANLEYS ROAD, MERRICKS VIC 3916 | 1108223 |  | Wind;Fallen |  |  |  |  | 1 | At 0809hrs on 17/03/2018, 22kV feeder ACR MT7621 reclosed to lockout affecting 312 customers. During strong gusty winds, a large private eucalyptus tree located between the first and second poles of the spur line has broken and fallen over one wire of the spur line ex MT0227. This occurred mid-span in the long bay of HV conductors and one conductor was pulled down to the ground without breaking or damaging assets with the exception of the ACR locking out. A 1sqm of blackened grass was identified where the conductor had hit the ground in the paddock near pole number LIS 1108223. | Conductor (bare) | 0 | 0 | 0 |  | MTN 32 | Vegetation: Trees Incident | Grassfire | 17/03/2018 8:09 | 1 | Localised: less than 10 sq.m | 9536 | Agricultural |  | 20180320UTD_02 | Infrastructure (network-based) | -38.3742 | 145.0903 | 1 | United Energy Distribution | Report | 13040 | 0.016522 | 22kV AC | Moorabbin Airport | 3916 | Merricks | Trees
The MFB extinguished the grass and scrub fire and supply to the feeders was restored after they were patrolled. | 85 WETHERBY ROAD, DONCASTER VIC 3108 | 7061588 |  | Blown branch/vegetation |  |  |  |  | 0 | At 1249hrs on 18/03/2018, 22kV feeder circuit breakers DC03 and DC 10 opened auto to lockout that caused the DC zone substation BTOS to operate and open the 1-2 and the 2-3 22kV bus tie circuit breakers. During extreme windy conditions, a tree branch from a tree in the park adjacent to Wetherby Road near the Eastern Freeway, contacted the DC03 and DC10 22kV overhead conductors where they run as the upper and lower circuits on pole number LIS 7061588. The MFB were in attendance following a 100sqm grass fire that was started from sparking and there was no damage to assets. | Conductor (bare) | 0 | 0 | 0 |  | DC 03 | Vegetation: Trees Incident | Bushfire | 18/03/2018 12:58 | 1 | Small: 10 - 1000 sq.m | 9537 | Public space |  | 20180320UTD_03 | Infrastructure (network-based) | -37.7968 | 145.1417 | 1 | United Energy Distribution | Report | 13043 | 0.0090255 | 22kV AC | Moorabbin Airport | 3108 | Doncaster | Trees
CEOT dispatched a fault crew to make safe, investigate and carry out necessary repairs. The crew tested the meter box and it had 230 Volts on it. The crew went back to the pole and the pole mount fuse box (FOLCB) neutral termination was completely cooked and had melted some of the active termination. The crew replaced both connections on the overhead LV line, the pole mounted fuse box (FOLCB) and the connections in the service pit (pole to pit supply arrangement). The crew re-tested for voltage on the meter box and it was all OK. | 38 GLEN PARK ROAD, ELTHAM NORTH VIC 3095 |  |  |  |  | Neutral fault;Overheated connection |  | Phase to earth |  | IMS 232362. CEOT received a report of an All Supply Failure. The fault crew attended and the customer had no supply on arrival. When the lady opened her meter box in front of the fault crew she received an electric shock. It appears the FOLCB had come off the pole and was upside down allowing water to enter the fuse box. The victim's details were not provided. and informed CEOT that lady at the premises received an electric shock off the meter box panel. | Any other type | 0 | 0 | 0 |  |  | Faulty pole mounted FOLCB. High impedance neutral. | Minor shock | 43314.6465 |  |  | 9541 | Residential |  | 20180321SPN_01 | Infrastructure (network-based) | -37.6982 | 145.1445 | 1 | AusNet Services Distribution | Report | 11624 | 0.034586 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham North | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 12 BRACKEN RIDGE, DROMANA VIC 3936 | 1306759 |  | Wind;Alive |  |  |  |  | 0 | CFA advise there is multiple wires down and a live line is whipping around on the ground causing grass spot fires. During extreme wind conditions, a privately owned tree has come down over the HV spur overhead conductors that caused two HV fuses to operate at RB0573. The fallen conductors near pole number LIS 1306759 were inadvertently back fed through the transformer at "Towerhill-Garner" substation as one of the HV fuses didn't operate. This caused a small grass fire of 10sqm to start that was extinguished by a local resident. | Conductor (bare) | 0 | 0 | 0 |  | DMA 13 | Vegetation: Trees Incident | Grassfire | 18/03/2018 13:26 | 1 | Localised: less than 10 sq.m | 9542 | Residential |  | 20180321UTD_01 | Infrastructure (network-based) | -38.3466 | 144.9555 | 1 | United Energy Distribution | Report | 13047 | 0.015179 | 22kV AC | Moorabbin Airport | 3936 | Dromana | Trees
CEOT dispatched a fault crew to make safe, investigate, isolate and repair. The feeder was switched out by the CEOT Controller. The HV conductors were sleeved and supply restored. | 105 KORUMBURRA-INVERLOCH ROAD, KONGWAK VIC 3951 | 2804133 |  | Fallen |  |  |  |  | 1 | IMS 232941. Initial Report: Reports of small grass fire near assets. HV conductor on ground. Feeder protection tripped. Final Report: Final report: Two HV conductors down at pole 2804133. There was a very small patch of grass burnt near fallen conductors and burn marks and sparking was apparent on sealed pavement area of the road. The tree had fallen on the HV line and was still partly covering the road. 3 phase overhead with 2 phases broken. Conductor size 3-7/3.0 AAC. Conditions: 19 degrees C, 43km/h wind, 47% humidity, fire area - very high fire rating. | Conductor (bare) | 0 | 0 | 0 |  | wgi22 | Vegetation: Trees Incident | Grassfire | 21/03/2018 15:57 | 1 | Localised: less than 10 sq.m | 9558 | Agricultural |  | 20180322SPN_02 | Infrastructure (network-based) | -38.5191 | 145.7218 | 1 | AusNet Services Distribution | Report | 11906 | 0.014029 | 22kV AC | Morwell (Latrobe Valley Airport) | 3951 | Kongwak | Trees
Dispatched Fault to fault crew and Duty Availability Officer to isolate, make safe and investigate. Repairs made by crew and supply reinstated. | 696 RIVERSDALE ROAD, RIVERSLEA VIC 3860 | 2511542 | Working too close to overhead lines | [5 empty] | 2 | IMS 232960. Initial report: CFA reports wire down hit by tractor and fire on ground. Final report from the attending DAO: Upon arriving on site, LV conductors were on the ground over 2 spans from source pole 2511529 to 2511542 (200m). LV conductors were disconnected from source pole 2511549. At pole 2511542 a stay that had previously gone over a track used by farm machinery was broken at the base. Close to pole 2511529 where the LV conductors were on the ground there was a small burnt area of grass, weeds and old tyres (5x2). | Conductor (bare) | 0 | 0 | 0 |  | mfa34 | Tractor contacted overhead LV line / pole stay. | Grassfire | 22/03/2018 12:26 | 1 | Small: 10 - 1000 sq.m | 9560 | Agricultural |  | 20180322SPN_04 | Infrastructure (network-based) | -38.0202 | 146.9645 | 1 | AusNet Services Distribution | Report | 12035 | 0.013251 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3860 | Riverslea | Vehicle
On arrival crew inspected assets no repairs required | 171 HENDERSON ROAD, TONGALA VIC 3621 | 33107920 |  | Bird | [5 empty] | Report of grass fire at incident location. On arrival the crew found at 171 Henderson Road Tongala, LIS 953084, two dead birds were found at base of pole and a 10m x 10m burnt area of grass. There was no reported shocks, injuries or property damage. | Conductor (bare) | 2 | 2 | 2 |  | KYM006 | Bird Incident | Grassfire | 21/03/2018 20:51 | 1 | Small: 10 - 1000 sq.m | 9581 | Public space |  | 20180326PWA_04 | Infrastructure (network-based) | -36.2044 | 144.9481 | 1 | Powercor | Report | 11828 | 0.019157 | 22kV AC | Shepparton Airport | 3621 | Tongala | Animal
Initial report: CEOT dispatched a fault crew to make safe, investigate and carry out /arrange for any necessary repairs. CEOT also advised the local DAO. The attending crew reported that no network assets were damaged. Final report: HV fuse replaced and supply restored. | 1580 MAIN DRAIN ROAD S, CORA LYNN VIC 3814 | 512569 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 232997. Initial report: Customer called CEOT stating that a tipper truck had made contact with overhead mains on a property. No Injuries to any persons. Reclose event recorded at 1719. Final report from attending DAO: It is suspected a tipping truck while in operational mode made contact with 3-3/2.75 Steel 22kV Conductors between poles #512581 & #512569 with fault current causing a number of the tyres on the truck to blow out and a HV fuse to operate at BW3354. There were no personal injuries or damage to the overhead line that was measured with a conductor height on 7.8 metres in the immediate vicinity of the contact point. The vehicle registration number is TEQ 611 and the driverâ€™s name was Steve Armstrong, mobile 042 243 319. | Conductor (bare) | 0 | 0 | 0 |  | phm33 | Tipper tuck contacted overhead 22kV HV conductor. | No Go Zone (contact) | 23/03/2018 17:40 |  |  | 9576 | Agricultural |  | 20180326SPN_03 | Infrastructure (network-based) | -38.1393 | 145.6363 | 1 | AusNet Services Distribution | Report | 11699 | 0.039137 | 22kV AC | Moorabbin Airport | 3814 | Cora Lynn | Vehicle
Initial Report: CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for necessary repairs. The local DAO was advised. The crew found a 1 sq. metre grass fire at the site but the fire was out when the crew attended the 2nd call. Final report: Repairs undertaken and supply restored. | 351 LYSTERFIELD ROAD, LYSTERFIELD VIC 3156 | 1302523 |  |  |  | Electrical breakdown;Mechanical breakdown |  |  |  | IMS 233000. Initial report: CEOT received reports of a sparking pole but nothing was found from the first fault crew visit. A 2nd call was for a grass fire at the base of the pole and the fault crew were dispatched again with a more accurate location and pole number. Final report: It is suspected service cable leads from overhead mains to a pole mounted fuse junction box on pole had worn through and short circuited phase to phase with fault current causing holt fallen plastic and metal particles to ground and starting a small 1 metre x1 metre grass fire around base of the pole. | Service conductor | 0 | 0 | 0 |  | fgy21 | A 4 core LV service mains to a FOLCB on pole for a customer's UG service was worn through and faulted phase to phase. | Grassfire | 24/03/2018 18:00 | 1 | Localised: less than 10 sq.m | 9577 | Agricultural |  | 20180326SPN_04 | Infrastructure (network-based) | -37.9158 | 145.2999 | 1 | AusNet Services Distribution | Report | 12048 | 0.010192 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Lysterfield | OH Cable
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for any necessary repairs. CEOT also notified the local DAO. Checked if the excavator driver was OK. Checked conductors for any damage and restored supply to customers. Replaced 1x 10 Amp HV fuse, single phase, Red phase, with power being restored. There was no damage to the overhead HV line as a result of this incident. | 355 VEARINGS ROAD, WOLLERT VIC 3750 | 913659 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS 233002. An excavator hit an overhead HV line which blew HV fuses at the tee-off pole. Excavator driver OK, no injuries. Report from attending DAO: On 26/3 Sash Boumovac (mobile 0413 355 731) advised an excavator operator, Branco Boumovac of Rokan Constructions, (mobile contact 0421 893 496 and postal address 74 Malcolm Creek Pde, Craigieburn, Vic, 3064), raised his excavator by the machineâ€™s own bucket and boom to carry out maintenance work under the machine. Branco not realizing how close he actually was to overhead lines with strong winds then pushing the overhead conductor and making contact to the top part of the machineâ€™s boom. He was warned by another worker on site. I advised Sash for No Go Zone Rules requiring a job safety assessment plan prior to any type any type of work, maintenance or activity occurring with 0 to 3 metres from 22kV overhead conductors being a No Go Zone, 3 to 6.4 metres a Safety Observer being posted on site with excavator works and a Dial Before You Dig for latest underground plans prior to any excavation taking place. | Conductor (bare) | 0 | 0 | 0 |  | epg13 | Excavator contacted an overhead HV conductor. | Loss of supply;No Go Zone (contact) | 25/03/2018 15:50 |  |  | 9579 | Construction |  | 20180326SPN_05 | Infrastructure (network-based) | -37.6021 | 144.9907 | 1 | AusNet Services Distribution | Report | 12046 | 0.034843 | 22kV AC | Essendon Airport | 3750 | Wollert | Vehicle
On arrival crew carried out repairs. | 229 BRIDPORT STREET W, ALBERT PARK VIC 3206 | 30173056 |  |  |  | Overheated connection |  |  |  | A customer reported that there is a grass fire adjacent the incident location. On arrival the fault crew found that fault current had caused overheating of a high voltage connection which ejected hot debris onto the ground igniting a small grass fire approximately 3m by 2m in area. The fire self-extinguished. There was no injury as a result of this incident. | Conductor (bare) | 2 | 2 | 2 |  | AP003 | debris ejected due to fault current | Grassfire | 19/03/2018 16:45 | 1 | Localised: less than 10 sq.m | 9604 | Public space |  | 20180328PWA_05 | Infrastructure (network-based) | -37.8424 | 144.9501 | 1 | CitiPower | Report | 11742 | 0.0048218 | 11kV AC | Essendon Airport | 3206 | Albert Park | Connection
On arrival crew inspected asset and carried out repairs. | 348 BLACKSHAWS ROAD, ALTONA NORTH VIC 3025 | 30117064 |  |  |  | Leakage |  |  |  | Pole Fire on the 22kV subsidiary cross-arm on Pole 34 of BLTS-SCI line inBlackshaws Rd corner Mahon Ave, Altona North. There was no reported HVI, injury, shocks or ground fire as a result of this incident. | Pole (wood) | 2 | 2 | 2 |  | BLTS-SCI | Excessive leakage current | Pole-top fire | 18/03/2018 11:55 | 1 | Negligible: no ground fire | 9608 | Roadway |  | 20180329PWA_01 | Infrastructure (network-based) | -37.8314 | 144.8507 | 1 | Powercor | Report | 15135 | 0.022573 | 22kV AC | Laverton Raaf | 3025 | Altona North | Pole
On arrival crew isolated supply and carried out repairs. LEI to inspect installation | 48 NEW STREET, SOUTH KINGSVILLE VIC 3015 | 33072189 | Recreation - Helium (party) balloons | [6 empty] | Jemena Dispatch advised, MFB had reported that balloons went through powerlines near LIS 28296 and the sub on the pole blown at the incident location. On arrival the crew found HV has tracked through insulator and fuse unit through to conductive pole and LV earth which is now also damaged. The crew suspects possible HVI. The fallen debris caused very minor grass fire (2m x 1m) at the pole base. | Pole mounted | 2 | 2 | 2 |  | BLT022 | Party balloons entangled | HV injection;Grassfire | 43194.7389 | 1 | Localised: less than 10 sq.m | 9636 |  |  | 20180405PWA_01 | Infrastructure (network-based) | -37.8272 | 144.8671 | 1 | Powercor | Report | 11793 | 0.032991 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3015 | South Kingsville | Other
On arrival crew isolated supply and carried out repairs Powercor crew later also found a bin that had been set alight, putting it out using extinguisher on their truck. | 5 CORIO STREET, BELMONT VIC 3216 | 30066627 | Vandalism | [6 empty] | Vicfire reported a grass fire possibly caused by Powercor assets. On arrival the crew & NAO found a tree had been on fire and caused a 2x25mm2 LVABC service to break after sparking. NAO contacted the brigade via phone after a finding suspicious item in the tree, the brigade confirmed the fire had started at the bottom of the tree and the call was made to Powercor when the service started sparking. There were no reported injuries. Ground fire and damage due to arson. | Service conductor | 2 | 2 | 2 |  | GCY023 | Vandalism | Grassfire;Other vegetation;Damage to network assets | 30/03/2018 18:40 | 0 | Small: 10 - 1000 sq.m | 9641 | Public space |  | 20180406PWA_01 | Infrastructure (network-based) | -38.1767 | 144.3438 | 1 | Powercor | Report | 11803 | 0.016307 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Trees
On arrival crew carried out repairs | 66 HIGH STREET, MELTON VIC 3337 | 30112318 |  |  |  | Leakage |  |  |  | During feeder patrol crew located pole fire outside 66 high st Melton A hv termination crossarm had broken as a result of a pole fire. There was no ground fire, no reporteed injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MLN021 | Excessive leakage current | Pole-top fire | 16/02/2018 14:01 | 1 | Negligible: no ground fire | 9647 | Roadway |  | 20180409PWA_01 | Infrastructure (network-based) | -37.6894 | 144.603 | 1 | Powercor | Report | 11814 | 0.016953 | 22kV AC | Laverton Raaf | 3337 | Melton | Pole
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Connection Box located on the Reticulation Service Pole. The attending Powercor Fault Crew reterminated the existing O/Head Twisted Service Cable at the Reticulation Service Pole with IPCâ€™s and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 75 MORTLAKE ROAD, WARRNAMBOOL VIC 3280 | 30136031 |  |  |  | Corrosion |  | Phase to earth |  | Mr Troy Wilson was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metal shower tap and his bare feet while standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | WBL002 | Corroded connection | Minor shock | 15/02/2018 9:00 |  |  | 9661 |  |  | 20180411PWA_01 | Infrastructure (network-based) | -38.3678 | 142.4932 | 1 | Powercor | Report | 11835 | 0.041252 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB The attending REC replaced the corroded FOLCB at the Customerâ€™s POA following disconnection of the O/H Service Cable by the Powercor Fault Crew. The Powercor Fault Crew subsequently re-terminated the existing O/H Twisted Service Cable at the new FOLCB and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 8 BYRNES STREET, SWAN HILL VIC 3585 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Paul Hatcher was in the Bathroom having a shower when he received an electric shock as he made simultaneous contact with his hand on the metal shower tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded service connection | Minor shock | 13/02/2018 9:00 |  |  | 9662 | Residential |  | 20180411PWA_02 | Infrastructure (customer connection) | -35.3299 | 143.548 | 1 | Powercor | Report | 11839 | 0.008456 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
On arrival crew isolated supply and replaced meter board | 35 CULLINAN ROAD, BATESFORD VIC 3213 | 33043550 |  |  |  | Overheated connection |  |  |  | A customer reported that their lights are flickering and a smell is coming from the supply box at the incident location. On arrival the fault crew found that a loose connection had caused heating of the fuse connection resulting in charring of the meter panel. There was no ground fire and no injury as a result of this incident. | Meter board (including fuses) | 2 | 2 | 2 |  | GL015 | Overheated connection in fuse base | Meter board | 28/02/2018 13:30 | 1 | Negligible: no ground fire | 9663 | Residential |  | 20180411PWA_03 | Infrastructure (customer connection) | -38.0903 | 144.2645 | 1 | Powercor | Report | 15136 | 0.005603 | Low voltage AC (<1kV) | Avalon Airport | 3213 | Batesford | Connection
The crew repaired the damaged underground cable and supply was restored. | HALLOWELLS ROAD, CUDGEE VIC 3265 | 30136187 | Working too close to underground cables | [5 empty] | 1 | A REC working for Metricon Homes reported that he has struck a low voltage underground cable with his excavator and believes it may be damaged at the incident location. On arrival the fault crew found that an excavator had dug up and damaged a low voltage underground cable running between the pole LIS 5008 and the low voltage pit on the boundary of the incident location. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | WBL002 | excavation work | No Go Zone (contact);Damage to network assets | 43284.4931 |  |  | 9672 | Agricultural |  | 20180412PWA_03 | Infrastructure (network-based) | -38.3454 | 142.6426 | 1 | Powercor | Report | 11848 | 0.0041123 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Cudgee | Dug up
On arrival crew carried out repairs. | 128 STRADBROKE AVENUE, SWAN HILL VIC 3585 | 31022051 | Working too close to underground cables | [6 empty] | Swan Hill City Council reported that contractors were removing kerb and channel at this address and exposed an earth wire. On arrival, crew found exposed HV earth for HV switch at pole 310963. Crew identified that there was some minor damage to the earth There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | SHL008 | Excavation work | Damage to network assets | 43346.7007 |  |  | 9679 |  |  | 20180413PWA_01 | Infrastructure (network-based) | -35.3391 | 143.551 | 1 | Powercor | Report | 11861 | 0.041384 | Earthing cable | Swan Hill Aerodrome | 3585 | Swan Hill | Dug up
On arrival crew isolated supply and carried out repairs. | KERANG-MURRABIT ROAD, CAPELS CROSSING VIC 3579 | 32030396 |  |  |  | Leakage |  |  |  | Customer reported a low conductor at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a grey fog pin insulator, conductor was adrift but remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. | Crossarm (wood) | 2 | 2 | 2 |  | KGT003 | Excessive leakage current | Pole-top fire | 14/04/2018 23:59 | 1 | Negligible: no ground fire | 9703 | Agricultural |  | 20180417PWA_02 | Infrastructure (network-based) | -35.5799 | 143.9311 | 1 | Powercor | Report | 11886 | 0.016255 | 22kV AC | Swan Hill Aerodrome | 3579 | Capels Crossing | Crossarm
Attending LEI conducted a voltage test between an independent earth and unit 1 and 2 earth/neutral bars under no load, recording a result of 8V. Unit 2 under load and conducted relevant tests recording a voltage of 57V(Ac). Subsequent tests were also completed to the conductive piping of unit two under load including the outdoor tap where the shock was received recording 61V. An NST was carried out at unit 1 and 2 switchboards, both which failed. Attending LEI conducted an NST at the FOLCB on the line neutral which also failed. Jemena crew was called to investigate issue further. Truck crew identified a severely corroded neutral at the FOLCB on the pole. Jemena crew replaced the FOLCB and service cable. Following rectification works, an NST test was carried out at the installations FOLCB and all residents switchboards, all recording a PASS result. A further test was also carried out from an independent earth to residents earth neutral bars, recording 0-1V. A volt test to metallic piping under load and no load resulted in 0 volts. Supply was left on. | UNIT 2 34 BARTON STREET, RESERVOIR VIC 3073 |  |  |  |  | Neutral fault |  |  | 2 | Several of the residents of units 1-5 of 34 Barton Street reported flicker/dimming lights and shocks from taps. Customer from unit 2 reported receiving a shock from the outdoor tap while making simultaneous contact with the tap and the wet ground (customer was bare foot at the time). | Copper;Neutral screen | 0 | 0 | 0 |  |  | Severely corroded neutral at the FOLCB on the pole. | Minor shock | 18/04/2018 13:55 |  |  | 9719 | Residential |  | 20180418JEM_01 | Infrastructure (network-based) | -37.7113 | 145.0034 | 1 | Jemena | Report | 11907 | 0.00018519 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Connection
On arrival crew isolated supply and carried out repairs | 369 EAGLEHAWK ROAD, CALIFORNIA GULLY VIC 3556 | 30026311 |  | Bird |  | Overheated connection |  |  | 1 | Customer reported powerline down at 69 Victoria St Eaglehawk. When crew arrived they reported that they suspected a bat had flown into HV conductors causing a phase to phase fault, resulting in HV conductor contacting LV. Crew attended secondary site and found that centre phase HV conductor had come down and a ground fire had been extinguished at base of the pole 116 adjacent to 369 Eaglehawk rd There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | EHK031 | Bird Incident | HV injection;Grassfire | 43346.8569 | 1 | Small: 10 - 1000 sq.m | 9477 | Public space |  | 20180314PWA_01 | Infrastructure (network-based) | -36.7257 | 144.2583 | 1 | Powercor | Report | 11538 | 0.029105 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3556 | California Gully | Animal
On arrival crew isolated supply and commenced repairs. | 23 RAILWAY STREET N, ALTONA VIC 3018 | 30107794 |  | Bird | [5 empty] | Fire Brigade reported an LV pole leaning with the possibility of the pole falling onto an adjacent house. On arrival the crew observed that the LV pole had fractured at ground level The pole was supported by Cables and did not fall to ground. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | AL014 | insect damage | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/03/2018 18:40 |  |  | 9479 | Roadway |  | 20180314PWA_02 | Infrastructure (network-based) | -37.8677 | 144.836 | 1 | Powercor | Report | 17365 | 0.0052847 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Animal
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe and investigate. The fault crew determined the customer's underground mains had been damaged and isolated supply at the mains box on the pole that supplied the service pit (2:20 pm). An AusNet Services' LEI attended at 3:15pm and the customer's REC was in attendance to repair the damaged underground consumer's mains. | 93 BAILEY ROAD, MOUNT EVELYN VIC 3796 | 1009907 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 232389. A fencing contractor reported receiving an electric shock whilst digging. The victim was excavating soil with a metal handled shovel to install a new fence post when the shovel damaged the customer's underground wiring enclosure (orange conduit) and single phase SDI cables enclosed within the conduit. Customer underground mains supplied from a pole to pit. | Customer installation | 0 | 0 | 0 |  | ldl13 | Whilst digging a fencing contractor caused damage to the customer's underground consumer's mains. | Minor shock | 43436.5542 |  |  | 9478 | Residential |  | 20180314SPN_01 | Infrastructure (network-based) | -37.7827 | 145.3918 | 1 | AusNet Services Distribution | Report | 11539 | 0.0079873 | Low voltage AC (<1kV) | Moorabbin Airport | 3796 | Mount Evelyn | Dug up
On arrival crew arranged isolation and pole was replaced. | PRINCES FREEWAY, LAVERTON NORTH VIC 3026 | 31024388 |  |  |  | Leakage |  |  |  | A Powercor Line Worker advised of a grass fire in the road reserve of the Princes Freeway, Laverton North near the base of DBL CCT 66kV Pole 108. The pole appears to have burnt through and snapped at this point, just below the bottom 66kV x-arm. The resultant sparks from this have fallen to the ground below and caused a grass fire of approximately 8m x 5m near the base of Pole 108 LIS-3172. There was no reported HVI, injury or shocks as a result of this incident. | Pole (wood) | 2 | 2 | 2 |  | ATS-TYA | Excessive leakage current | Pole-top fire;Grassfire | 18/03/2018 15:06 | 1 | Small: 10 - 1000 sq.m | 9523 | Roadway |  | 20180319PWA_02 | Infrastructure (network-based) | -37.8371 | 144.8002 | 1 | Powercor | Report | 11817 | 0.028191 | 22kV AC;66kV AC | Laverton Raaf | 3026 | Laverton North | Pole
Initial report: DAO advised. Site made safe. Final report; The conductor was repaired and the line was returned to service on the 19th March 2018 at approximately 21:25hrs. | MCDONALDS TRACK, HERNES OAK VIC 3825 | 7700545 |  | Fallen |  |  |  |  | 1 | IMS 232898. Initial report: MWTS-YPS No1 66kV line tripped. Line patrolled no cause found. Line returned to service. After 6min MWTS-YPS no1 66kV line tripped. Report of fire near Princes FWY near Haunted Hills Rd. Final report: On the 18th of March 2018 at approximately 13:29hrs AEST, the Morwell Terminal Station to Yallourn Power Station (MWTS-YPS) No 1 66kV Line tripped from its line protection. There was a white phase - blue phase fault on the line. At MWTS end, both X (SEL311L) and Y (Siemens 7SD610) protection current differential protection operated. Fault current was 8.8kA peak and CB opened in 89ms. At YPS end, both X (SEL311L) and Y (Siemens 7SD610) protection current differential protection operated. Fault current was 2.1kA peak and CB opened in 98ms. Auto reclose functions are not provided for circuit breakers of this line. The Line remained out of service from the time of the tripping until the following day. On the 19th of March 2018, a patrol of the line was undertaken and due to site access difficulties approximately 90% of the line was completed with no cause found. The line was restored to service on the 19th of March 2018 at approximately 12:15hrs. The line tripped approximately six minutes later at 12:21hrs from its line protection. There was a red phase -earth fault on the line. According to oscillograph downloaded from relays at both ends, the fault was only fed from YPS end with a peak value of 610A. There was negligible fault current from MWTS end until the last 3 cycles of the event where fault current has risen to 160A. In this event, Y protection (Siemens 7SD610) at both ends operated. X protection (SEL311L) at both ends did not operate. This is due to the different algorithms used in the two protection schemes, which have different sensitivities under different fault scenarios. The line crew observed the CFA was in attendance, a broken 66kV conductor and a tree on the ground south-side of the line. A burnt area of ground approximately 15m x 9m near pole (LIS 7700545). PLEASE NOTE - discussed with Phil Brant and Hawaii Ho - Our CEOT advised there is no known address for this incident location so we have included the correct road address and town/area being Hernes Oak and the coordinates for pole 7700545. | Conductor (bare) | 0 | 0 | 0 |  | MWTS-YPS No1 66kV line | Vegetation: Trees Incident | Grassfire | 19/03/2018 12:21 | 1 | Small: 10 - 1000 sq.m | 9529 | Forest - plantation |  | 20180319SPN_08 | Infrastructure (network-based) | -38.2099 | 146.3251 | 1 | AusNet Services Distribution | Report | 12504 | 0.0304 | 66kV AC | Morwell (Latrobe Valley Airport) | 3825 | Hernes Oak | Trees
Initial Report: CEOT dispatched a fault crew to make safe, investigate and arrange for repairs. CEOT also advised the local DAO. The fault crew made the site safe. Final Report: SWER conductor repaired and the HV line was returned to service. | 859 HEDLEY RANGE ROAD, BINGINWARRI VIC 3966 | 2611459 |  | Wind;Fallen |  |  |  | Phase to earth | 1 | IMS 232913. Initial Report: Successful Reclose on YM066. Reports of all supply failure past YM073. Crew found wire down at pole 2611459 to 2611462. HV BA Fuse at YM073 blown. Reports of fire in area. Final Report: SWER conductor was broken and on the ground and a dead burnt tree was in the vicinity. Wire down between poles 2611459 & 2611462. The fire started in the grass easement and burnt into the forest area in high wind. Fire brigade attended and extinguished the fire. Fire area was approximately 2,000 sq. metres in size. | Conductor (bare) | 0 | 0 | 0 |  | ftr12 | Vegetation: Trees Incident | Grassfire | 19/03/2018 12:11 | 1 | Medium: 1000 sq.m - 10 ha | 9534 | Agricultural |  | 20180320SPN_01 | Infrastructure (network-based) | -38.6066 | 146.4843 | 1 | AusNet Services Distribution | Report | 11616 | 0.014214 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3966 | Binginwarri | Trees
Transformer and aerial service line replaced Line patrolled prior to restoration | CROSS FOREST ROAD, NAROGHID VIC 3266 | 33037538 |  | Wind;Fallen |  |  |  |  | 2 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Gnotuk area. Preliminary investigations by the Arson squad have identified that this fire originated near the intersection of Cross Forrest Road and Saddlers roads in Gnotuk ( Naroghid) The police information attributes this fire to a tree branch that had contacted power lines.Tree contacted service crossing road and resulted in damage to wiring on pole mounted substation. | Conductor (bare) | 0 | 0 | 0 |  | CDN006 | Vegetation: Trees Incident | Grassfire | 17/03/2018 21:00 | 1 | Large: more than 10 ha | 9544 | Roadway |  | 20180321PWA_01 | Infrastructure (network-based) | -38.2329 | 143.0798 | 1 | Powercor | Report | 12094 | 0.034809 | 22kV AC | Warrnambool Airport Ndb | 3266 | Naroghid | Trees
Crew attended Tree cleared and line restored after site observed by victoria Police as part of investigation into cluster of fires. | BANEMORE, 992 TWOMEYS BRIDGE ROAD, YATCHAW VIC 3301 | 33058409 |  | Fallen |  |  |  |  | 1 | Customer reported wires down had started a fire in paddock at the incident location. On arrival the crew found that a tree (Blue gum) had fallen on the line and brought down a HV conductor between ELLBURGER P1 & P2. The fire was at the northern edge of a large bushfire. Victoria police requested to attend | Conductor (bare) | 0 | 0 | 0 |  | HTN003 | Vegetation: Trees Incident | Grassfire | 17/03/2018 20:42 | 1 | Large: more than 10 ha | 9545 | Forest - plantation |  | 20180321PWA_02 | Infrastructure (network-based) | -37.8758 | 142.1508 | 1 | Powercor | Report | 11632 | 0.0093785 | 22kV AC | Hamilton Airport | 3301 | Yatchaw | Trees
site isolated pending investigation subsequent repairs undertaken to the conductor and pole. | 6695 PRINCES HIGHWAY, TERANG VIC 3264 | 32194776 |  | Wind |  | Conductor clashing |  | Phase to phase | 1 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Terang area. The attending crew found evidence of conductor clashing under strong winds the site was left undisturbed and referred to Victoria Police prior to any restoration works. Fire damage and response activities undertaken as part of response to 4 fires in the area. | Conductor (bare) | 0 | 0 | 0 |  | TRG004 | Conductor clashing | Grassfire | 17/03/2018 20:45 | 1 | Large: more than 10 ha | 9546 | Roadway |  | 20180321PWA_03 | Infrastructure (network-based) | -38.2374 | 142.9289 | 1 | Powercor | Report | 12082 | 0.039329 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Conductor
site isolated, inspected by Vicpol prior to restoration. Pole subsequently replaced | OCCUPATION LANE, THE SISTERS VIC 3265 | 32055108 |  | Wind |  |  |  | Phase to earth | 1 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Garvoc area. The attending crew found evidence of broken pole. The site was left undisturbed and referred to Victoria Police prior to any restoration works. Fire damage and response activities undertaken as part of response to 4 fires in the area. Address approximate | Pole (wood) | 0 | 0 | 0 |  | TRG002 | strong wind storm | Grassfire | 17/03/2018 20:49 | 1 | Large: more than 10 ha | 9547 | Agricultural |  | 20180321PWA_04 | Infrastructure (network-based) | -38.2184 | 142.7741 | 1 | Powercor | Report | 12081 | 0.011123 | 22kV AC | Warrnambool Airport Ndb | 3265 | The Sisters | Pole
On arrival crew carried out repairs | 85 JAMIESON STREET, WARRNAMBOOL VIC 3280 | 30137710 |  |  |  | Overheated connection |  |  |  | It could not be determined who reported this incident. On arrival the crew found that a 22kV HV Isolator top connection had failed, causing hot debris to fall to the ground, resulting in a grass fire of approx. 8m x 8m = 64m2. There were no injuries, and no other damage reported. | Connector/termination | 0 | 0 | 0 |  | WBL008 | connection failed | Grassfire | 17/03/2018 15:04 | 1 | Small: 10 - 1000 sq.m | 9554 | Roadway |  | 20180322PWA_02 | Infrastructure (network-based) | -38.374 | 142.4913 | 1 | Powercor | Report | 11649 | 0.038083 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Crew attended and removed branch and repaired line | 20 SPRING DAM ROAD, TERANG VIC 3264 | 32055460 |  | Blown branch/vegetation |  |  |  |  | 1 | Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Terang (Spring Dam road) area. An off duty Powercor worker was part of the CFA crew attending. He subsequently reported that there was a large gum tree in contact with the 22kV line between poles 2 and 3 of the spring dam spur. There was a ground fire of some 300 by 500 m that was extinguished by the CFA prior to them mobilising to the nearby Terang fire. Fire damage and response activities undertaken as part of response to other fires in the area and may have initially been considered as advance spotting of another fire | Conductor (bare) | 0 | 0 | 0 |  | TRG001 | Vegetation fell and contacted line | Grassfire | 17/03/2018 20:50 | 1 | Medium: 1000 sq.m - 10 ha | 9555 | Roadway |  | 20180322PWA_03 | Infrastructure (network-based) | -38.2308 | 142.9501 | 1 | Powercor | Report | 11648 | 0.022924 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Trees
On arrival crew carried out repairs. | DIGGER JIMS ROAD, TOOLONDO VIC 3401 | 30082900 |  |  |  | Leakage |  |  |  | Customers reported a supply outage in the Charam area and there was a loss of supply to the Charam Zone Substation at 1551 hours on 19/03/18. There was also a subsequent report of a ground fire at the incident location. On arrival the crew found that a pole fire on a wooden 66 kV pole had resulted in the pole top structure including a steel x arm falling to the ground. There was a ground fire of approximately 150mÂ². There were no injuries. | Pole (wood) | 2 | 2 | 2 |  | HOTS CHM | Excessive leakage current | Grassfire | 19/03/2018 15:55 | 1 | Small: 10 - 1000 sq.m | 9557 | Agricultural |  | 20180322PWA_04 | Infrastructure (network-based) | -37.0002 | 141.8089 | 1 | Powercor | Report | 11651 | 0.010882 | 66kV AC | Horsham Aerodrome | 3401 | Toolondo | Pole
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 3670 FRANKSTON-FLINDERS ROAD, MERRICKS VIC 3916 | 9648679 |  | Wind;Alive |  |  |  |  | 1 | At 1720hrs on 18/03/2018, 22kV feeder ACR RB7257 located in Tucks Road reclosed to lockout affecting 90 customers. HV conductors were found on the ground after a large tree fell over HV conductors. During extremely windy conditions on a TFB day, a large tree has fallen over the HV overhead conductors between poles LIS 1109045 and 9648679 located outside 3670 Frankston-Flinders Road. ACR RB7257 locked out as a result but molten metal from clashing conductors caused a 100sqm grass fire. | Conductor (bare);Steel | 0 | 0 | 0 |  | DMA 15 | Vegetation: Trees Incident | Grassfire | 18/03/2018 17:20 | 1 | Small: 10 - 1000 sq.m | 9548 | Roadway |  | 20180322UTD_01 | Infrastructure (network-based) | -38.403 | 145.0716 | 1 | United Energy Distribution | Report | 13048 | 0.037494 | 22kV AC | Moorabbin Airport | 3670 | Merricks | Trees
The HV/LV pole was made safe and liaison with the PTC would determine the time and date of the pole replacement. | 48 RAILWAY PARADE, SEAFORD VIC 3198 | 3306355 |  | Precipitation;Prone to salt deposition |  | Electrical breakdown |  |  | 2 | Per CFA - HV cross arm and pole on fire in Railway Parade on the corner of McKenzie. Following light drizzly rain after a long dry spell, the top of a HV/LV two way tee-off pole on the corner of Railway Parade and McKenzie Street, Seaford. The pole fire occurred at the 22kV offset cross arm that tracked through the king bolt near the number 5 stay. Emergency switching took place to de-energise the 22kV conductors to allow the CFA to extinguish the pole fire. The pole was damaged to an extent that it has to be replaced. The 22kV overhead conductors head west over the Frankston railway line (1500v DC) and the railway conductors are required to be shut down for the duration of the work estimated to be approximately 6-8 hours to enable the pole replacement to be completed safely. The PTC were advised that a shutdown is required and they asked if the work could be done tomorrow night as they can arrange buses to replace the trains. | Pole (wood) | 0 | 0 | 0 |  | CRM 33 | The pole fire occurred following light rain. Also contributing was the location of the pole is in close proximity to Port Phillip Bay. | Pole-top fire | 19/03/2018 21:30 | 1 | Negligible: no ground fire | 9551 | Roadway |  | 20180322UTD_04 | Infrastructure (network-based) | -38.1033 | 145.1286 | 1 | United Energy Distribution | Report | 13049 | 0.014249 | 22kV AC | Moorabbin Airport | 3198 | Seaford | Pole
A LEI attended and tested the installation after the HV fuse was replaced. No voltages were recorded in the area of the staff room where the staff member received the shock. A NST passed with 0.1ohms measured for the neutral impedance. Voltages on all phases were normal and supply was left on after the LEI advised the school staff of the investigation findings. | 16 HINTON STREET, ROSEBUD VIC 3939 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Name - Our Lady of Fatima Primary School. Caller reports they have dim lights at the property and some parts don't have any power. One of their staff also received a buzz from the switches but she's okay. Due to strong winds, a HV fuse had operated that dim lighted the circuit. At Our Lady of Fatima Primary School a staff member operated the light switch in the staff room she felt a slight buzzing tingle feeling from the light switch. | Customer installation | 0 | 0 | 0 |  |  | No cause was identified at the time of the investigation. | Minor shock | 21/03/2018 12:30 |  |  | 9562 | Commercial |  | 20180322UTD_06 | Infrastructure (network-based) | -38.3704 | 144.8977 | 2 | United Energy Distribution | Report | 11660 | 0.0016343 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Fuse
On arrival crew made site safe and carried out repairs | GARDEN GULLY VINEYARD, 1477 WESTERN HIGHWAY, GREAT WESTERN VIC 3374 | 31014142 |  |  |  | Leakage |  |  |  | VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden 66/22 kV pole was slightly damaged between the steel crossarms on the centre and bottom circuits. There was no ground fire. There were no injuries. | Pole (wood) | 2 | 2 | 2 |  | ART STL 66 | Excessive leakage current | Pole-top fire | 20/03/2018 0:38 | 1 | Negligible: no ground fire | 9570 | Public space |  | 20180323PWA_06 | Infrastructure (network-based) | -37.1663 | 142.8674 | 1 | Powercor | Report | 11681 | 0.022244 | 22kV AC;66kV AC | Horsham Aerodrome | 3374 | Great Western | Pole
On arrival crew extinguished fire and carried out repairs. | 1328 BACCHUS MARSH ROAD, BULLENGAROOK VIC 3437 | 33075101 |  |  |  | Candled fuse |  |  |  | A PCA fault crew attended a fault at the incident location. On arrival they noticed a grass fire had started (10 x 5 mtrs) They found a burnt EDO fuse tube in the burnt area. There were no reported injuries, there was minor damage to the customers fence and service pit. | EDO fuse | 2 | 2 | 2 |  | BMH006 | Fuse holder burnt | Loss of supply;Grassfire | 19/03/2018 0:25 | 1 | Small: 10 - 1000 sq.m | 9575 | Roadway |  | 20180326PWA_02 | Infrastructure (network-based) | -37.5274 | 144.4769 | 1 | Powercor | Report | 11701 | 0.0004838 | 22kV AC | Melbourne Airport | 3437 | Bullengarook | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 21 GREENFIELD WAY, MOUNT MARTHA VIC 3934 | 1102825 |  | Wind |  |  |  |  | 1 | At 1306hrs on 21/03/2018, customers supplied from Greenfield and Balcombe Roads reported of a loss of their electricity supply and the MFB reports of wires down near the Balcombe Pre-School. During strong winds, a branch from a private gum tree has fallen over the 22kV conductors bringing one phase down near pole No. LIS 1102825. HV fuses operated at the HV spur fusing (MT0042) as a result. Molten metal fall to the ground and a small grass started that was quickly extinguished. | Conductor (bare) | 0 | 0 | 0 |  | DMA 24 | Vegetation: Trees Incident | Grassfire | 21/03/2018 13:06 | 1 | Localised: less than 10 sq.m | 9585 | Residential |  | 20180326UTD_01 | Infrastructure (network-based) | -38.2744 | 145.0291 | 1 | United Energy Distribution | Report | 13051 | 0.01531 | 22kV AC | Moorabbin Airport | 3934 | Mount Martha | Trees
On arrival crew carried out repairs. Arrangements made for pole replacement. | 1845 PRAIRIE-ROCHESTER ROAD, LOCKINGTON VIC 3563 | 30122637 |  |  |  | Leakage |  |  |  | Vicfire reported a pole fire at the incident location. On arrival the crew found that a single phase intermediate pole had caught on fire about 1.5M below the cross-arm, the embers which fell commenced a ground fire of approximately 6M x 40M in area, grass on the road side burnt, minor damage to a nearby fence occurred. CFA in attendance to extinguish ground fire & pole fire. There was no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | SHP012 | Excessive leakage current | Pole-top fire;Grassfire | 24/03/2018 14:19 | 1 | Small: 10 - 1000 sq.m | 9588 | Roadway |  | 20180327PWA_02 | Infrastructure (network-based) | -36.301 | 144.4798 | 1 | Powercor | Report | 11725 | 0.033269 | 22kV AC | Bendigo Airport | 3563 | Lockington | Pole
On arrival the crew isolated supply and carried out repairs. | 1243-1257 EXFORD ROAD, EXFORD VIC 3338 | 30142925 |  |  |  | Leakage |  |  |  | Report received from a motorist driving along Exford Rd towards Eynesbury of a line that had come down; not disconnected but hanging low in the paddock. Upon arrival the fault crew found that at LIS-936380 the outer section of the 3-phase HV wood crossarm had burnt through. The outer phase HV conductor falling to within 1.5m-2.0m of the ground. Supply remained alive and no protection operated as a result of the incident, and apart from the burnt crossarm, there was no further damage sustained to the pole or the HV conductor. There was no asset fire/ground fire, shock or third party damage to report. | Crossarm (wood) | 2 | 2 | 2 |  | MLN011 | Excessive leakage current | Pole-top fire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 26/02/2018 18:50 | 1 | Negligible: no ground fire | 9593 | Agricultural |  | 20180327PWA_05 | Infrastructure (network-based) | -37.7472 | 144.5715 | 1 | Powercor | Report | 11731 | 0.021181 | 22kV AC | Laverton Raaf | 3338 | Exford | Crossarm
On arrival crew isolated supply and carried out repairs. | 46 EDWARDS DRIVE, ALTONA MEADOWS VIC 3028 | 30116799 |  |  |  | Leakage |  |  | 1 | A customer reported that there is a pole on fire at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. There was no ground fire and no injury as a result of this incident. | Crossarm (wood) | 2 | 2 | 2 |  | LVN022 | Excessive leakage current. | Pole-top fire | 43103.2986 | 1 | Negligible: no ground fire | 9595 | Roadway |  | 20180327PWA_07 | Infrastructure (network-based) | -37.8861 | 144.7777 | 1 | Powercor | Report | 11733 | 0.040061 | 22kV AC | Laverton Raaf | 3028 | Altona Meadows | Crossarm
On arrival crew carried out repairs. | 36 ROMAWI STREET, ALTONA VIC 3018 | 30107670 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the crew found that a pole and HV crossarm had caught fire. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | AL012 | Excessive leakage current | Pole-top fire | 43103.2576 | 1 | Negligible: no ground fire | 9600 | Roadway |  | 20180328PWA_01 | Infrastructure (network-based) | -37.8668 | 144.8251 | 1 | Powercor | Report | 11738 | 0.013771 | 11kV AC | Laverton Raaf | 3018 | Altona | Pole
CEOT dispatched a fault crew to make safe, investigate and repair. The fault truck replaced the EDO fuse tube and restored supply. No fire present. | 288 HAGANS ROAD, AIRLY VIC 3851 | 2503668 |  |  |  | Age;Corrosion;Electrical breakdown;Candled fuse |  |  | 2 | IMS 232630. Customer reported no supply. The attending fault crew found a hung-up and candling 6 Amp EDO fuse tube. | EDO fuse | 0 | 0 | 0 |  | sle32 | Burnt EDO fuse tube. | Other electricity related | 28/02/2018 18:30 | 1 | Negligible: no ground fire | 9606 | Agricultural |  | 20180328SPN_01 | Infrastructure (network-based) | -38.0435 | 147.0889 | 1 | AusNet Services Distribution | Report | 11744 | 0.040685 | 22kV AC | Bairnsdale Airport | 3851 | Airly | Fuse
CEOT dispatched an AusNet Services' LEI to investigate. Independent earth to point of contact measured 25 Volts. Area taped off, ready for replacement of Insulators on the pole for the next day. The service crew to preform all tests as per VESI. The pole top insulators were subsequently replaced - SAP Noti 102779064. | 3425 WHITTLESEA-YEA ROAD, FLOWERDALE VIC 3717 | 4703972 |  |  |  | Insulator |  | Phase to earth | 2 | IMS 232634. Customer reported getting an electric shock from the fence. Mr Hargrave received an electric shock while making contact with the farm fence. The cause of the electric shock was defective pole top insulators on the pole. Voltage was detected on the pole and around the vicinity of pole 4703971 (SWER system). Mr Hargrave made contact with the ground wire on the farm fence, which in turn made a electrical circuit and he received an electrical shock. | Insulators | 0 | 0 | 0 |  | smr5 | Faulty pole top insulators. | Minor shock | 28/02/2018 12:50 |  |  | 9607 | Agricultural |  | 20180328SPN_02 | Infrastructure (network-based) | -37.3188 | 145.2969 | 1 | AusNet Services Distribution | Report | 11745 | 0.024034 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3425 | Flowerdale | AF Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 19 PEACEDALE GROVE, NUNAWADING VIC 3131 | 7029117 |  | Lightning |  | HV injection |  |  | 1 | Customers supplied ex of HV spur fuses BH7342 advise they have lost their electricity supply after lightning was seen in the area. The MFB are also in attendance inspecting houses that may have had a power surge. Lightning struck a HV a cross arm at pole No. LIS 7029117 located outside 19 Pearcedale Grove, Nunawading that caused 3 x HV 65amp boric acid fuses to operate at BH7342 located in Jubilee Grove. This caused damage to the HV cross arm and it appears a HV conductor made brief contact with the LV conductors below when the cross arm broke. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Pearcedale- Whorse" substation. The LEI confirmed a high voltage injection occurred (BWD 1805) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Crossarm (wood) | 0 | 0 | 0 |  | NW 21 | Lightning struck a HV conductor / cross arm that broke and contacted the LV conductors. | Pole-top fire;HV injection | 24/03/2018 14:35 | 1 | Negligible: no ground fire | 9605 | Residential |  | 20180328UTD_01 | Infrastructure (network-based) | -37.816 | 145.1668 | 1 | United Energy Distribution | Report | 13055 | 0.037174 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Lightning
On arrival crew isolated supply and carried out repairs. | BIRCHIP-WYCHEPROOF ROAD, NARRAPORT VIC 3483 | 30023395 |  |  |  | Leakage |  |  | 1 | SCADA alarm advised that Birchip P29 ACR had tripped to lockout, shortly after customer reported a conductor down at the incident location. On arrival the crew found that a wooden angle-strain cross-arm had burnt through at the roadside disc / bridging insulator, causing the conductor to fall to ground. There was no ground fire, no reported injuries, no 3rd party damage, protection operated. | Crossarm (wood) | 2 | 2 | 2 |  | CTN001 | Excessive leakage current | Pole-top fire | 24/03/2018 11:42 | 1 | Negligible: no ground fire | 9610 | Agricultural |  | 20180329PWA_02 | Infrastructure (network-based) | -36.0538 | 143.1022 | 1 | Powercor | Report | 11748 | 0.00080208 | 22kV AC | Swan Hill Aerodrome | 3483 | Narraport | Crossarm
On arrival crew isolated supply and carried out repairs. | 94 MCKENZIE ROAD, TYNTYNDER SOUTH VIC 3586 | 32155814 |  |  |  | Leakage |  |  | 1 | Customer reported a pole had exploded and it was smoking / smouldering at the incident location. On arrival the crew found that a wooden termination cross-arm had burnt through at the disc insulator string, causing the conductor to fall to ground. There was no ground fire, no reported injuries, no 3rd party damage, protection operated. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 24/03/2018 16:54 | 1 | Negligible: no ground fire | 9611 | Agricultural |  | 20180329PWA_03 | Infrastructure (network-based) | -35.2626 | 143.5024 | 1 | Powercor | Report | 11750 | 0.0109 | 22kV AC | Swan Hill Aerodrome | 3586 | Tyntynder South | Crossarm
On arrival crew isolated supply and carried out repairs. | 24 PIONEER ROAD, GROVEDALE VIC 3216 | 32084603 |  |  |  | Leakage |  |  |  | Vic Fire report to Powercor advising of a pole smoking at the incident location. On arrival the crew found that a wooden pole with HV steel cross arms appeared to be burning internally, at approx. Â¾ distance up the pole. The pole was still intact and supply remained on with no wires falling to ground. A controlled interruption was undertaken in the area to allow fire brigade crews safe access to extinguish the fire. The pole was found to be extensively damaged and required replacement. There was no ground fire, no reported injuries, no 3rd party damage | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | WPD012 | Excessive leakage current | Pole-top fire | 24/03/2018 10:12 | 1 | Negligible: no ground fire | 9612 | Roadway |  | 20180329PWA_04 | Infrastructure (network-based) | -38.2028 | 144.3379 | 1 | Powercor | Report | 11751 | 0.031919 | 22kV AC | Avalon Airport | 3216 | Grovedale | Pole
On arrival crew inspected assets for damage and carried out repairs. | PRINCES HIGHWAY, WERRIBEE VIC 3030 | 30150264 | Working too close to overhead lines | [5 empty] | 1 | A shop owner at the incident location called to say the crane of a truck hit the High Voltage conductors while unloading porter loos. The crew attended and confirmed what the shop owner had said. No injury or third party damage had occurred. The porter loo employee said he did not receive a shock. There was no fire. | Conductor (bare) | 2 | 2 | 2 |  | WBE023 | Truck crane contacted conductor | No Go Zone (contact) | 29/03/2018 9:26 |  |  | 9619 | Commercial |  | 20180329PWA_09 | Infrastructure (network-based) | -37.9273 | 144.6314 | 1 | Powercor | Report | 11763 | 0.015581 | 22kV AC | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival crew isolated supply and carried out repairs. | 7332 MALLEE HIGHWAY, PANITYA VIC 3512 | 32153749 |  |  |  | Leakage |  |  | 1 | Following customer calls , a patrol found pole fire at Murrayville 988. There was no ground fire or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 26/03/2018 4:08 | 1 | Negligible: no ground fire | 9622 | Agricultural |  | 20180403PWA_03 | Infrastructure (network-based) | -35.2402 | 141.0413 | 1 | Powercor | Report | 11777 | 0.012444 | 22kV AC | Mildura Airport | 3512 | Panitya | Pole
On arrival crew isolated supply and carried out repairs. | 1198 MURRAYVILLE NORTH ROAD, MURRAYVILLE VIC 3512 | 32147691 |  |  |  | Leakage |  |  | 1 | Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 25/03/2018 23:45 | 1 | Negligible: no ground fire | 9623 | Agricultural |  | 20180403PWA_04 | Infrastructure (network-based) | -35.1557 | 141.1905 | 1 | Powercor | Report | 11778 | 0.0038299 | 22kV AC | Mildura Airport | 3512 | Murrayville | Pole
On arrival crew isolated supply and carried out repairs. | 867 SUNSET ROAD, COWANGIE VIC 3506 | 32145257 |  |  |  | Leakage |  |  | 1 | Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 26/03/2018 0:57 | 1 | Negligible: no ground fire | 9624 | Agricultural |  | 20180403PWA_05 | Infrastructure (network-based) | -35.1603 | 141.4257 | 1 | Powercor | Report | 11779 | 0.013639 | 22kV AC | Mildura Airport | 3506 | Cowangie | Pole
On arrival crew isolated supply and carried out repairs. | 867 SUNSET ROAD, COWANGIE VIC 3506 | 32145306 |  |  |  | Leakage |  |  | 1 | Following customer calls, a patrol found pole fire at incident location (Tyalla P42) There was no ground fire or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 26/03/2018 0:57 | 1 | Negligible: no ground fire | 9625 |  |  | 20180403PWA_06 | Infrastructure (network-based) | -35.1519 | 141.4193 | 1 | Powercor | Report | 11780 | 0.02506 | 22kV AC | Mildura Airport | 3506 | Cowangie | Pole
Report from the attending AusNet Services' LEI: At 4:00 pm on the 01/03/2018 I was contacted regarding a fault at 256 York Street, Sale, On arrival I spoke to Leanne, the owner, who had received the tingle off the shower taps regarding the severity of the shock and was informed it was only a mild sensation. I tested for voltage via an independent earth and the taps in the installation which measured 2-3 volts. The customer then informed me that the flickering lights were only present on days and nights of bad weather. The next test was the NST test at the meter position with a pass result. At this time the on call truck crew arrived and we preformed an inspection on the fuse mains box. This is when we found the neutral connection to be in very poor condition. This poor connection was the cause of the issues with the windy conditions acting on the overhead conductor making it flex in the neutral terminal connection within the FMB. The customer was informed of the findings and was disconnected from supply for approximately 20 minutes while rectification works were preformed. The installation was tested again and found to be compliant. | 254-256 YORK STREET, SALE VIC 3850 | 2502198 |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | IMS 232658. Over a period of several weeks on stormy / windy days the customer had noticed the lights dimming and flickering. On the 01/03/2018 the customer was having a shower and noticed a slight tingle when she touched the hot water tap. Also her son felt a similar thing in the second shower within the house. Customer contacted an REC and was instructed to contact AusNet Services' faults. | Connection box | 0 | 0 | 0 |  | sle14 | Corroded neutral in FOLCB at the POA. | Minor shock | 43103.659 |  |  | 9640 | Residential |  | 20180405SPN_02 | Infrastructure (customer connection) | -38.1037 | 147.0683 | 1 | AusNet Services Distribution | Report | 11799 | 0.039027 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | Connection
Crew attended and replaced missing cable. | 1211 LEAKES ROAD, ROCKBANK VIC 3335 | 33071799 | Copper theft | [6 empty] | Inspector reports 4m of HV copper earth missing from substation at incident location. There were no reported fires, shocks or injuries. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | copper theft | Damage to network assets | 23/02/2018 9:11 |  |  | 9649 |  |  | 20180409PWA_03 | Infrastructure (network-based) | -37.7359 | 144.66 | 1 | Powercor | Report | 11816 | 0.0024375 | Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew carried out repairs | 951-971 MOUNT COTTRELL ROAD, THORNHILL PARK VIC 3335 | 30341004 | Copper theft | [6 empty] | An employee reported that an LV earth was stolen from the incident location. On arrival the crew found that a Low Voltage (LV) earth at Mt Cottrell P226 S/Stn had been stolen. There were no reported injuries or other third party damage | Earth/earthing | 2 | 2 | 2 |  | DPTS MLN 1 | Copper theft | Damage to network assets | 22/02/2018 10:40 |  |  | 9652 | Roadway |  | 20180409PWA_06 | Infrastructure (network-based) | -37.7177 | 144.6185 | 1 | Powercor | Report | 11823 | 0.015859 | Earthing cable | Laverton Raaf | 3335 | Thornhill Park | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded (detached) O/H Service Neutral Conductor at the Pole Type Connection Box located at the Reticulation Pole. The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 622 PEEL STREET N, BLACK HILL VIC 3350 | 32009431 |  |  |  | Corrosion |  | Phase to earth |  | Ms Kristen Grant was watering the garden when she received an electric shock as she made simultaneous contact with her hand on the metal tap and her bare feet while standing on the concrete footpath. | Connection box | 2 | 2 | 2 |  | BAN007 | Corroded connection | Minor shock | 13/02/2018 18:00 |  |  | 9653 | Residential |  | 20180409PWA_07 | Infrastructure (network-based) | -37.5476 | 143.8668 | 1 | Powercor | Report | 11824 | 0.028219 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Black Hill | Connection
LEI tested voltages at water pipes, metallic kitchen sink, earth electrode, metallic meter box, pillar and recorded voltages of 3-4volts to independent earth. NST and impedance tests at switchboard, meter box and pillar recorded a pass result and impedance readings of under 0.30. Continuity test at water pipes, kitchen sink, earth stake, meter box and pillar recorded results of less than 0.5 ohms. Connections at FOLCB OK. Jemena service crew checked connections junction box. Loose connections identified and repaired at junction box at cross arm. NST conducted at installation switchboard - pass result obtained. | 60 FAIRMOUNT STREET, HADFIELD VIC 3046 |  |  |  |  | Loose connections at junction box at cross arm;Other |  |  | 2 | Customer reported an alleged electric shock from the metallic kitchen sink. Customer also reports instances of lights dimming over a few months. | No failed asset | 0 | 0 | 0 |  |  | Loose connections identified at junction box at cross arm. | Minor shock | 43377.5007 |  |  | 9660 |  |  | 20180410JEM_02 | Infrastructure (network-based) | -37.7113 | 144.9526 | 1 | Jemena | Report | 11834 | 0.032433 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Service Pole The attending Powercor Fault Crew reterminated the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 99 SHARPS ROAD, PORT CAMPBELL VIC 3269 | 33034684 |  |  |  | Corrosion |  | Phase to earth |  | Mr Bradley Little was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his arm on the metal Shower Tap and his bare feet while standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | TRG003 | Corroded connection | Minor shock | 17/02/2018 14:00 |  |  | 9658 |  |  | 20180410PWA_04 | Infrastructure (network-based) | -38.6071 | 142.9539 | 1 | Powercor | Report | 11832 | 0.0091771 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Port Campbell | Connection
The site was made safe and both cables were repaired. | 11 KRIS COURT, MELTON WEST VIC 3337 | 34006059 | Working too close to underground cables | [6 empty] | Control Room Ausnet Services (ph 0392295962) reported that crew was working on a gas leak issue at a customerâ€™s house on 11 Kris court Melton West and they had determined that the ground around the leak area was live. He requested Powercorâ€™s attendance urgently. On arrival the crew found that a P/L service cable near a service pit had been hit with a shovel and the insulation of the cable was broken and at the same time a 16mm 4C service cable next to it was damaged as well. There was no ground fire, no shock or injuries as a result of this incident. | Services cable | 2 | 2 | 2 |  | MLN022 | Gas repair works | No Go Zone (contact) | 43193.434 |  |  | 9665 | Roadway |  | 20180411PWA_05 | Infrastructure (network-based) | -37.6832 | 144.5564 | 1 | Powercor | Report | 11840 | 0.026969 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Dug up
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 119 HASTINGS ROAD, GREENDALE VIC 3341 | 30105118 |  |  |  | Corrosion |  | Phase to earth |  | Mr Stanley was in the Bathroom showering when he made simultaneous contact between his hand on the metal tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | BMH003 | corroded connection | Minor shock | 23/02/2018 8:00 |  |  | 9666 | Residential |  | 20180411PWA_06 | Infrastructure (network-based) | -37.5681 | 144.3258 | 1 | Powercor | Report | 11841 | 0.035293 | Low voltage AC (<1kV) | Avalon Airport | 3341 | Greendale | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screened Conductor of an O/H Neutral Screened Service Cable at the Wrap-onâ€™s located at the Reticulation Pole and the Service Pole. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable between the Reticulation pole and the Service Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. | UNIT 2 4 MARRINERS LOOKOUT ROAD, APOLLO BAY VIC 3233 | 60316141 |  |  |  | Corrosion |  | Phase to earth |  | Ms Gray was in the rear garden operating the external Water Tap when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the damp ground. | Service conductor | 2 | 2 | 2 |  | CLC007 | corroded neutral | Minor shock | 43436.3542 |  |  | 9667 | Residential |  | 20180411PWA_07 | Infrastructure (network-based) | -38.7426 | 143.6735 | 1 | Powercor | Report | 11843 | 0.0073137 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Connection
The damage was repaired, the cable reinstated and supply restored. | 850 FORD ROAD, MERRIGUM VIC 3618 | 32191192 | Working too close to underground cables | [5 empty] | 1 | customer reported that he has lost power at the incident location. On arrival the fault crew found that an excavator working in an easement had damaged / severed a low voltage underground cable at the incident location. The crew found a damaged / severed cable and exposed conductors. There was no ground fire and no injury as a result of this incident. | Services cable | 2 | 2 | 2 |  | SHP014 | Excavation works | No Go Zone (contact);Damage to network assets | 43284.4931 |  |  | 9674 | Roadway |  | 20180412PWA_04 | Infrastructure (network-based) | -36.4016 | 145.1433 | 1 | Powercor | Report | 11852 | 0.019605 | Low voltage AC (<1kV) | Shepparton Airport | 3618 | Merrigum | Dug up
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral connection at the POA. Fault truck repaired neutral connection at the POA CTA re-tested property, all required VESI tests passed | 57 REED STREET, ALBERT PARK VIC 3206 | 30172550 |  |  |  | Corrosion |  | Phase to earth |  | Lucy opened the dishwasher at the time; she received an electric shock when she made simultaneous contact between the metallic dishwasher with her hand and the concrete floor with her foot. | Connection box | 2 | 2 | 2 |  | AP008 | Corroded Neutral connection at POA | Minor shock | 27/02/2018 17:30 |  |  | 9675 | Residential |  | 20180412PWA_05 | Infrastructure (customer connection) | -37.8457 | 144.9471 | 1 | CitiPower | Report | 17373 | 0.00042593 | Low voltage AC (<1kV) | Essendon Airport | 3206 | Albert Park | Connection
Crew to remove the KSS casing and once customer has secured the site, a new KSS will be install. Police have been notified | 72-80 BUCKLEY GROVE, MOOLAP VIC 3224 | 30065968 | Copper theft | [6 empty] | An employee reports vandalism and copper theft at the Buckley â€“ Alreco KSS site. The site was not energised as the customer is still negotiating supply to site. Crew identified unknown persons had cut the HV U/G on the pole but had not removed it ( Non copper conductor! ). They also found the KSS had been opened and copper TX windings and cabling had been removed. This resulted in a loss of an unknown amount of oil to the surrounding area. There were no reported shocks or injuries. | Pad mounted equipment/kiosk | 2 | 1 | 2 |  | GLE031 | Copper theft | Less than $50k damage;Damage to network assets | 43346.3812 |  |  | 9676 | Industrial |  | 20180412PWA_06 | Infrastructure (network-based) | -38.1638 | 144.4303 | 1 | Powercor | Report | 11857 | 0.017872 | Not applicable | Avalon Airport | 3224 | Moolap | Other
CEOT dispatched a fault crew to make safe, investigate and repair. Line patrolled. No cause found. | 1060 WESTERNPORT ROAD, LANG LANG EAST VIC 3984 | 519170 |  |  |  | Age;Corrosion;Electrical breakdown;Candled fuse |  |  |  | IMS 232664. Blown EDO fuse @ LIS 519170. Line patrolled NCF. Fuse candled. No photos are available. | EDO fuse | 0 | 0 | 0 |  | llg11 | Candled EDO fuse tube. | Other electricity related | 43134.1229 | 1 | Negligible: no ground fire | 9673 | Agricultural |  | 20180412SPN_01 | Infrastructure (network-based) | -38.2517 | 145.6579 | 1 | AusNet Services Distribution | Report | 11854 | 0.021712 | 22kV AC | Moorabbin Airport | 3984 | Lang Lang East | Fuse
On arrival crew isolated supply at services pit. | 110 TUSCAN COURT, HEATHCOTE VIC 3523 | 30144379 | Working too close to underground cables | [5 empty] | 1 | Customer reported that fencing contractor had dug up underground cables at his property and no one was hurt. On arrival, crew found that consumer mains cable had been hit by a post digger. No shock, injuries or third party damage. | Services cable | 2 | 2 | 2 |  | BGO023 | Post hole digging | Loss of supply;No Go Zone (contact) | 13/03/2018 16:13 |  |  | 9680 | Residential |  | 20180413PWA_02 | Infrastructure (network-based) | -36.8643 | 144.6854 | 1 | Powercor | Report | 11862 | 0.012954 | Low voltage AC (<1kV) | Bendigo Airport | 3523 | Heathcote | Dug up
LEI attended and checked properties but found no evidence of property damage from a HVI. Crew repaired conductor. | 230 TANNERY LANE, MANDURANG VIC 3551 | 30041863 |  |  |  | Corrosion |  |  | 1 | A member of the community reported arcing from a pole top. Attending Crew identified a loose connection at the live line clamp dee loop. During tightening, the steel conductor parted and fell. There was No injuries, ground fire, or third party damage identified. | Conductor (bare) | 2 | 2 | 2 |  | BET007 | corrosion | Loss of supply;Damage to network assets | 14/03/2018 21:56 |  |  | 9681 | Public space |  | 20180413PWA_03 | Infrastructure (network-based) | -36.8146 | 144.3168 | 1 | Powercor | Report | 11863 | 0.014896 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3551 | Mandurang | Connection
LV OVERHEAD CONDUCTOR WAS ISOLATED AND MADE SAFE. CREW REPLACED LV OERHEAD CONDUCTORS. | 209 ARTHUR STREET, FAIRFIELD VIC 3078 |  |  | Wind |  | Conductor clashing |  |  |  | Strong winds caused low voltage conductors to clash resulting on blue phase and neutral conductors on the ground. Ref tbl# 162873 | Conductor (bare) | 0 | 0 | 0 |  |  | Low voltage conductor clashing due to strong winds. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/04/2018 10:15 |  |  | 9684 | Residential |  | 20180414JEM_01 | Infrastructure (network-based) | -37.7725 | 145.0206 | 1 | Jemena | Report | 12318 | 0.031308 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Fairfield | Conductor
CFA called by NAO to extinguish pole fire which continued to burn. On arrival crew isolated supply and carried out repairs. | MODBURY, 863 WELLS ROAD, AVON PLAINS VIC 3477 | 32021671 |  |  |  | Leakage |  |  | 1 | SCADA alarm from Swanwater ACR initiated fault crew response who discovered a pole fire at the incident location. On arrival the crew found that a three phase intermediate pole had burnt off at the pole top. The embers which fell commenced a ground fire of approximately 6M x 5M in area, grass on the road side burnt, fire self extinguished. There was no reported injuries, no 3rd party property damage. | Pole (wood) | 2 | 2 | 2 |  | CTN006 | Excessive leakage current | Grassfire | 14/04/2018 15:36 | 1 | Small: 10 - 1000 sq.m | 9688 | Roadway |  | 20180416PWA_01 | Infrastructure (network-based) | -36.5045 | 142.9237 | 1 | Powercor | Report | 11870 | 0.038054 | 22kV AC | Horsham Aerodrome | 3477 | Avon Plains | Pole
On arrival crew isolated supply and carried out repairs | 54B DAMASCUS ROAD, ROBINVALE VIC 3549 | 32141555 |  |  |  | Leakage |  |  |  | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, conductors remained suspended above the ground. There was no ground fire, no reported injuries, no 3rd party damage | Crossarm (wood) | 2 | 2 | 2 |  | RVL001 | Excessive leakage current | Pole-top fire | 14/04/2018 16:40 | 1 | Negligible: no ground fire | 9690 | Roadway |  | 20180416PWA_02 | Infrastructure (network-based) | -34.6225 | 142.7866 | 1 | Powercor | Report | 11873 | 0.034903 | 22kV AC | Mildura Airport | 3549 | Robinvale | Pole
On arrival crew isolated supply and carried out repairs. | 636 BARINGHUP ROAD, CARISBROOK VIC 3464 | 30017729 |  |  |  | Leakage |  |  |  | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, resulting in the conductors being suspended approximately 2M above the ground. There was no ground fire, no reported injuries, no 3rd party damage, | Crossarm (wood) | 2 | 2 | 2 |  | MRO007 | Excessive leakage current | Pole-top fire | 14/04/2018 16:40 | 1 | Negligible: no ground fire | 9691 | Roadway |  | 20180416PWA_03 | Infrastructure (network-based) | -37.028 | 143.8709 | 1 | Powercor | Report | 11874 | 0.016961 | 22kV AC | Ballarat Aerodrome | 3464 | Carisbrook | Pole
CEOT dispatched a fault crew to make safe, investigate and repair. CEOT also advised the DAO. Linesmen attended the site and found the property side fuse of the single phase substation arcing at the top of the fuse tube. The fuse tube was opened stopping the arcing. The fuse tube was removed and it fell into two pieces at ground level. The fuse tube was replaced and supply restored. No cause was found at the site as to why the fuse operated, but it appears from explored data that the fuse may have started arcing inside the tube at least 5 days before. An investigation of the fuse tube found the fuse link was stuck in the tube and it blocked the tube from hinging down. The tube burnt off at the very top of the fuse tube. The EDO tube looked to be a Morlynn Power type, did not have an age on the tube but is believed to have been manufactured from 1984-1986. The fuse tube on the other phase is a different type of tube and was not replaced. Ronan Spur pole 1 is concrete and the existing EDO units are the incorrect type for a concrete pole. A follow in SAP on Noti 102958456 has been raised to replace the EDO units with BA fuse units and animal proof the substation. | 1077 OMEO HIGHWAY, TALLANGATTA SOUTH VIC 3701 | 5211317 |  |  |  | Candled fuse |  |  |  | IMS 232791. CFA reported a fire/ arcing at the top of pole 1 Ronan Spur (BID #5211317) located in Hibbersons Rd, Fernvale. The attending fault crew found an arcing and burnt EDO fuse tube. There was no fire at ground level. | EDO fuse | 0 | 0 | 0 |  | wots24 | Arcing and burnt EDO fuse tube. | Other electricity related | 43346.9479 | 1 | Negligible: no ground fire | 9694 | Agricultural |  | 20180416SPN_03 | Infrastructure (network-based) | -36.301 | 147.2316 | 1 | AusNet Services Distribution | Report | 11877 | 0.018684 | 22kV AC | Wangaratta Aero | 3701 | Tallangatta South | Fuse
CEOT dispatched a fault crew to make safe, investigate and repair. The BA fuse barrel was replaced and supply restored. There was no evidence as to what caused the incident, and it is expected that water could have gotten in to the barrel if it was left in the open position for a long period. | 1 LISHEEN ROAD, COCKATOO VIC 3781 | 408391 |  |  |  | Candled fuse |  |  |  | IMS 232869. A person passing by the pole heard a buzzing noise and called AusNet Services and the fault crew attained. CANDLING FUSE AT SWITCH BG0488.The lower section of the BA fuse barrel broken through, and the top section remained in with situ. The base of the assembly was still attached to the barrel, and rotated as it would do when a fuse has blown. As a result of the rotation of the base section, it made contact with the remaining fuse element of the BA fuse, resulting in no outage. There was no fire at the site. The crew that attended replaced the failed BA fuse. | Boric acid | 0 | 0 | 0 |  | ofr23 | Candled BA fuse tube. | Other electricity related | 16/03/2018 11:03 | 1 | Negligible: no ground fire | 9700 | Residential |  | 20180416SPN_04 | Infrastructure (network-based) | -37.9535 | 145.5043 | 1 | AusNet Services Distribution | Report | 12856 | 0.0083067 | 22kV AC | Moorabbin Airport | 3781 | Cockatoo | Fuse
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 50 Volts no load to 80 Volts maximum load. Performed voltage test from an independent earth spike to all conductive plumbing fittings resulting in a reading of 50 Volts no load to 80 Volts maximum load. CTA/LEI performed NST at installation main switchboard with a fail result recorded. Fault Crew discovered the loose connection of the 3 wire grey twisted service neutral conductor into the neutral terminal of the customers FOLCB at the POA. Crew performed NST with pass result recorded. Crew re-terminated the neutral conductor into the FOLCB neutral terminal. Installation left ON supply. | 14 WILLOWFIELD COURT, HIGHTON VIC 3216 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Gillian was standing at the back yard tap, when she felt a slight shock to her right hand whilst adjusting the tap, with her left wet hand holding a metal bowl under the water flow and standing on wet pavers. | Service conductor | 2 | 2 | 2 |  |  | loose connection in FOLCB | Minor shock | 18/03/2018 15:00 |  |  | 9708 | Residential |  | 20180417PWA_05 | Infrastructure (customer connection) | -38.1509 | 144.313 | 1 | Powercor | Report | 11891 | 0.029655 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded/burnt Crows Foot Clamp on an O/H Service Neutral Conductor termination to the Reticulation Neutral Conductor The attending Powercor Fault Crew replaced the Crows Foot Clamp at the O/H Service Neutral Conductor termination to the Neutral Reticulation Conductor and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 55 INGLEWOOD STREET, GOLDEN SQUARE VIC 3555 | 30331113 |  |  |  | Corrosion |  | Phase to earth |  | Ms Vanhappen was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metal tap and her bare feet while standing on the wet conductive shower base. | Service conductor | 2 | 2 | 2 |  | BET001 | Corroded connection pole end | Minor shock | 43315.7083 |  |  | 9712 | Residential |  | 20180418PWA_04 | Infrastructure (network-based) | -36.7638 | 144.2452 | 1 | Powercor | Report | 11897 | 0.00047685 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Golden Square | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Conductor termination at the Reticulation Sub-station Pole The attending Powercor Fault Crew reterminated the Neutral Conductor at the Reticulation Sub-station Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 27 DAVIES STREET, CHARLTON VIC 3525 | 30022016 |  |  |  | Corrosion |  | Phase to earth |  | Mr Andrew McGurk was opening a metallic gate when he received an electric shock as he made simultaneous contact between his hand on the metal gate and his arm which was in contact with the adjacent metallic fence that had a reference to the installation earthing system. | Conductor (bare) | 2 | 2 | 2 |  | CTN003 | Corroded connection | Minor shock | 43346.375 |  |  | 9713 | Residential |  | 20180418PWA_05 | Infrastructure (network-based) | -36.2703 | 143.3576 | 1 | Powercor | Report | 11898 | 0.037105 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3525 | Charlton | Connection
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 6 Volts no load to 30 Volts maximum load. Fault Crew discovered the loose and corroded termination of the 2 wire grey twisted service neutral conductor into the neutral terminal of the customers FOLCB at the POA. Crew also found that the service neutral was loose in the take-off box on PAL pole. Crew abolished the existing grey service to allow the customers REC to replace the faulty customer FOLCB Crew installed new 2 wire ABC service and performed NST with pass result recorded. CTA/LEI performed NST at the installation main switchboard with a pass result recorded. | 32A GREY STREET, TERANG VIC 3264 | 30043708 |  |  |  | Corrosion |  | Phase to earth |  | Coleman was standing in the shower, having a shower, when he felt a slight tingle to his right hand adjusting the tap with his left hand holding the flexible shower hose whilst standing bare foot on the wet shower base. | Service conductor | 2 | 2 | 2 |  | TRG004 | corroded connections | Minor shock | 27/03/2018 8:00 |  |  | 9723 | Residential |  | 20180419PWA_04 | Infrastructure (customer connection) | -38.2381 | 142.9129 | 1 | Powercor | Report | 11911 | 0.018258 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3264 | Terang | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded and damaged O/H Service Neutral Conductor, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 49 BUCKLEYS ROAD, POINT LONSDALE VIC 3225 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Christopher Heinz was operating an external Tap at the side of the property whilst rinsing his wet suit when he received an electric shock as he made simultaneous contact with his hand on the metal tap and his bare feet whilst standing on the wet ground. | Service conductor | 2 | 2 | 2 |  |  | Corroded neutral connection | Minor shock | 43376.7917 |  |  | 9724 | Residential |  | 20180419PWA_05 | Infrastructure (customer connection) | -38.2872 | 144.6091 | 1 | Powercor | Report | 11912 | 0.027987 | Low voltage AC (<1kV) | Avalon Airport | 3225 | Point Lonsdale | Connection
On arrival crew isolated supply and replace crossarm | 1541 AXEDALE-GOORNONG ROAD, BARNADOWN VIC 3557 | 32038909 |  |  |  | Leakage |  |  | 1 | A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | EHK023 | Excessive leakage current | Pole-top fire | 14/04/2018 14:00 | 1 | Negligible: no ground fire | 9730 | Agricultural |  | 20180423PWA_01 | Infrastructure (network-based) | -36.6568 | 144.5213 | 1 | Powercor | Report | 11919 | 0.0077569 | 22kV AC | Bendigo Airport | 3557 | Barnadown | Crossarm
On arrival crew isolated supply and carried out repairs. | AXEDALE-GOORNONG ROAD, GOORNONG VIC 3557 | 33021748 |  |  |  | Mechanical breakdown | Inappropriate tools/plant/equipment |  | 1 | Vic Fire reported wires down and grass fire at incident location. On arrival, crew found a HV conductor had fallen, starting a 120mÂ² grass fire. There was no reported shocks or injuries. | Conductor (bare) | 2 | 2 | 2 |  | EHK023 | Fallen conductor. Conductor pulled out of splice used some time in the past to join dissimilar conductor of same diameter. | Grassfire | 22/04/2018 21:41 | 1 | Small: 10 - 1000 sq.m | 9737 | Agricultural |  | 20180426PWA_01 | Infrastructure (network-based) | -36.6378 | 144.5248 | 1 | Powercor | Report | 13752 | 0.0058414 | 22kV AC | Bendigo Airport | 3557 | Goornong | Conductor
On arrival crew inspected asset and restored supply | 7840 MURRAY VALLEY HIGHWAY, KOYUGA VIC 3622 | 30125482 |  | Bird |  |  |  |  | 1 | Police reported wires sparking and explosion at incident location. On arrival the crew found Magpies had caused a HV fault, starting a 15m x 60m grass fire. There was no reported shocks, injuries or property damage. | Pole mounted | 2 | 2 | 2 |  | ECA005 | Bird Incident | Grassfire | 25/04/2018 7:42 | 1 | Small: 10 - 1000 sq.m | 9742 | Roadway |  | 20180426PWA_02 | Infrastructure (network-based) | -36.195 | 144.9121 | 1 | Powercor | Report | 15137 | 0.0056065 | 22kV AC | Shepparton Airport | 3622 | Koyuga | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole. The attending Powercor Fault Crew reterminated the O/H Neutral Service Conductor and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1090 KULKYNE WAY, RED CLIFFS VIC 3496 | 32152056 |  |  |  | Corrosion |  | Phase to earth |  | A female person unknown was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metallic Shower Tap and her bare feet while standing on the wet concrete shower base. | Service conductor | 2 | 2 | 2 |  | RCT014 | Corroded connection | Minor shock | 43346.5417 |  |  | 9946 | Commercial |  | 20180530PWA_02 | Infrastructure (network-based) | -34.3701 | 142.269 | 1 | Powercor | Report | 12224 | 0.027522 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination in the Pole Type Junction Box located on the Reticulation Pole. The attending Powercor Fault Crew reterminated the O/H Neutral Service Conductor at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 688 HILDEBRAND ROAD, LEITCHVILLE VIC 3567 | 32040246 |  |  |  | Corrosion |  | Phase to earth |  | Mr Sean Millar was in the Bathroom showering when he received an electric shock as he made simultaneous contact with one hand on the metallic Shower Tap and his bare feet while standing on the wet concrete shower base. | Service conductor | 2 | 2 | 2 |  | CHA005 | Corroded connection | Minor shock | 43224 |  |  | 9961 | Residential |  | 20180531PWA_04 | Infrastructure (network-based) | -35.9096 | 144.2802 | 1 | Powercor | Report | 12241 | 0.0027315 | Low voltage AC (<1kV) | Bendigo Airport | 3567 | Leitchville | Connection
CEOT dispatched a fault crew to make safe and investigate the incident. CEOT also notified the local DAO. On attendance it was found the truck had hit the concrete pole at the base and damaged the pole to the point it had to be replaced immediately requiring a full lines crew to complete the task. | 101 PRINCES WAY, DROUIN VIC 3818 | 2706260 | Vehicle | [6 empty] | IMS 233478. CEOT received reports of a truck impacting a dual circuit 22kV HV pole. The truck had been detoured by a roads resurfacing crew and the truck's trailer hit the pole when it was turning around the roundabout. As of 23 May 2018 the Police have not talked to the driver due to him being an interstate driver therefore no advice or details as of yet. Advice from CEOT: A truck driver took a short cut and subsequently collided with a concrete pole. The truck continued on and then stopped and then drove off. The concrete pole broke near the base of the pole and was supported by the overhead HV conductors. There were no live overhead conductors on the ground nor were they very low. The incidents resulted in customers being off supply. CEOT called the Police to report the incident. | Pole (concrete) | 0 | 0 | 0 |  | wgl14 | Truck contacted HV concrete pole. | Damage to network assets | 43317.1806 |  |  | 9955 | Commercial |  | 20180531SPN_04 | Infrastructure (network-based) | -38.1352 | 145.8557 | 1 | AusNet Services Distribution | Report | 12234 | 0.039219 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Drouin | Vehicle
Pre-rectification test results: Faults crew and an AusNet Services' LEI dispatched (LEI arrived after rectification, installation left on supply until tested by the LEI). Initial NST test performed which failed. What was rectification? Fault crew checked connections at FOLCB and then at pole 2604558 where they found a faulty neutral connection at pole junction box and repaired the connection. Birds nest also found inside box. After-rectification test results: Final NST test performed which passed by fault crew. Left off supply for LEI to complete testing. Z (Line) â€“ impedance 0.32O - Pass. Voltage from independent earth to point of contact tap and shower hose was measured at 0.8 Volt. With Fluke Stray Voltage Eliminator (2kO resistor) - Pass. IR of eg consumerâ€™s mains was measured above 550 MOhm - Pass. Continuity test on consumer's mains passed. Any other test results? Earth electrode loop impedance test recorded at 11.5O â€“ Pass. Voltage dip with 7.2 Amp hair dryer recorded at 2 Volts. The LEI requested the property owner to contact her REC to apply earthing equipotential bond onto water pipes in bathroom to help eliminate any potential difference if was to happen and RW & AR Inglis Electrical, contacted the LEI shortly after for guidance on where to place earth bond. Mr Everett said he did not require any Medical Attention. | 6 JOSEPHINE COURT, TRARALGON VIC 3844 | 2604558 |  | Bird |  | Neutral fault |  | Phase to earth |  | IMS 233448. Mr Everett had been complaining of dim lights and the microwave not working correctly for a few days. While showering when he received what he described as a serious belt across his back from the flexible metallic shower hose which threw him back onto the shower screen. The cause was found to be faulty neutral connection in the pole junction box on pole Lis 2604558. | Connection box | 0 | 0 | 0 |  | tgn11 | Faulty connections in pole junction box. High impedance neutral fault. | Minor shock | 43164.6083 |  |  | 9958 | Residential |  | 20180531SPN_05 | Infrastructure (network-based) | -38.1845 | 146.518 | 1 | AusNet Services Distribution | Report | 12238 | 0.024182 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
A faults truck attended and replaced the defective and burnt out 150w HPS lantern. | 99A LIGHTWOOD ROAD, NOBLE PARK VIC 3174 | 620877 |  | Precipitation |  | Overheated connection |  |  | 2 | MFB reported they have extinguished a pole fire on the corner of Heatherton Road and Douglas Street at pole number 0620877. During light drizzle, a 150w high pressure sodium (HPS) lantern caught fire on pole No. LIS 0620877 located on the corner of Heatherton Road and Douglas Street, Noble Park. The MFB had been in attendance and extinguished the pole fire. | Public lighting | 0 | 0 | 0 |  |  | A probable loose connection that overheated. | Pole-top fire | 26/05/2018 21:06 | 1 | Negligible: no ground fire | 9957 | Roadway |  | 20180531UTD_03 | Infrastructure (network-based) | -37.9633 | 145.1715 | 1 | United Energy Distribution | Report | 13067 | 0.015281 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Connection
On arrival crew isolated supply and carried out repairs | 2310 PRINCETOWN ROAD, PRINCETOWN VIC 3269 | 33037378 |  |  |  | Overheated connection |  |  |  | A customer reported pole on fire in the middle below transformer. On arrival the crew found a fuse box had been on fire and extinguished from the rain. No ground fire, injuries, 3rd party property damage was reported. | Connection box | 2 | 2 | 2 |  | COB011 | Insufficient remains to determine cause | Pole-top fire | 20/05/2018 14:26 | 1 | Negligible: no ground fire | 9966 | Roadway |  | 20180601PWA_02 | Infrastructure (network-based) | -38.6408 | 143.1336 | 1 | Powercor | Report | 12246 | 0.022655 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Princetown | Fuse
Voltage tests between an independent earth at the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral conductor at the FMJB. PCA fault truck removed and refitted the service neutral, cleaned the neutral connection block then replaced the service neutral to the property. CTA completed required VESI tests. | 11 COOK ROAD, MELTON SOUTH VIC 3338 |  |  |  |  | Corrosion |  | Phase to earth |  | Peter received an electric shock when he made simultaneous contact between the metallic tap with his hands and the wet concrete covered ground with his feet. | Service conductor | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 16/04/2018 13:00 |  |  | 9980 | Residential |  | 20180606PWA_01 | Infrastructure (customer connection) | -37.7137 | 144.5691 | 1 | Powercor | Report | 12261 | 0.00017824 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 551-557 DONCASTER ROAD, DONCASTER VIC 3108 | 7055915 |  |  |  | Electrical breakdown |  |  | 2 | At 2344hrs on 26/05/2018, 22kV feeder WD 23 circuit breaker successfully reclosed and held. The MFB advised of a pole on fire in Doncaster Road near the corner of Bailey Grove. A HV switch connection failed at HV manual gas switch DT 0077 located in Bailey Grove, 1 pole south of "Bailey-Doncaster" substation. The centre phase conductor was blown out from the switch insulator and was resting in close proximity to the switch casing. | Dropper/bridge | 0 | 0 | 0 |  | WD 23 | Failed connection at the manual gas switch. | Pole-top fire | 26/05/2018 23:50 | 1 | Negligible: no ground fire | 9989 | Roadway |  | 20180608UTD_04 | Infrastructure (network-based) | -37.788 | 145.1197 | 1 | United Energy Distribution | Report | 13068 | 0.021523 | 22kV AC | Moorabbin Airport | 3108 | Doncaster | Connection
The electrical inspector conducted the required tests and fault crew replaced the faulty service. | 4 ALVIE COURT, WESTMEADOWS VIC 3049 |  |  |  |  | Corrosion |  |  | 2 | Yarra Valley Water contractor received an electric shock during the course of repairing the burst water main within the nature strip. He felt the shock after he had disconnected the water main to number 3 Alvie and made hand contact with the street water main of which was still connected to number 4. The shock was caused due to the neutral conductor in the aluminum NS service supplying number 4 was completely corroded and open circuited mid span. The high resistance in the neutral impressed a voltage rise of 10 VAC on the street water main due to the high resistance parallel path that the MEN system allows into the water pipe system as the metallic water pipes are equipotential bonded to each installations earthing system. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Aluminum neutral screen service had corroded and open circuited mid span. | Minor shock | 43349.9208 |  |  | 9991 | Residential |  | 20180611JEM_01 | Infrastructure (network-based) | -37.6701 | 144.9066 | 1 | Jemena | Report | 12275 | 0.00018287 | Low voltage AC (<1kV) | Essendon Airport | 3049 | Westmeadows | OH Cable
Electrical inspector attended the site and completed the required tests. The inspector found a faulty neutral screen service. The fault crew attended and replaced the service. | 3 PHILLIP ROAD, KEILOR EAST VIC 3033 |  |  |  |  | Corrosion |  |  | 2 | Customer received a shock when he made hand contact with the shower taps. | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | The aluminum neutral screen service had been completely corroded and open circuit mid span. | Minor shock | 43410.7958 |  |  | 9993 | Residential |  | 20180612JEM_01 | Infrastructure (network-based) | -37.7512 | 144.8687 | 1 | Jemena | Report | 12277 | 0.034014 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | OH Cable
On arrival crew isolated supply and carried out repairs | 231 LEAKES ROAD, TRUGANINA VIC 3029 | 30233147 |  |  |  | Mechanical overload |  |  | 1 | Customer calls and report of a pole fire at pole 67 of the ATS-WBE 66kv line. ON arrival it appears the centre phase post type insulator had separated from its mounting allowing conductor to rest on the steel crossarm. The current flow through the pole appears to have caused the pole to ignite. There was no ground fire, no reported injuries or third party property damage. | mounting hardware (stud);Conductor (bare);Insulators;Other | 2 | 2 | 2 |  | ATS-WBE | Insulator stud fractured | Pole-top fire | 43287.1667 | 1 | Negligible: no ground fire | 9995 | Roadway |  | 20180612PWA_02 | Infrastructure (network-based) | -37.8392 | 144.7458 | 1 | Powercor | Report | 12554 | 0.035081 | 66kV AC | Laverton Raaf | 3029 | Truganina | AF Other
On arrival crew isolated supply and carried out repairs. | 540 PURRUMBETE ESTATE ROAD, KOALLAH VIC 3260 | 32059366 |  |  |  | Overheated connection |  |  |  | Vicfire reported a transformer fire at the incident location. On arrival the crew found that a 480V LV fuse box had burnt out at one end. There was no ground fire. There was no reported third party damage or any injuries. | Connection box | 2 | 2 | 2 |  | CDN002 | overheated connnection | Melting or smoking only | 43349.7937 |  |  | 9999 |  |  | 20180612PWA_04 | Infrastructure (network-based) | -38.2941 | 143.2207 | 1 | Powercor | Report | 12287 | 0.018338 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3260 | Koallah | Connection
Fence repaired, Police notified | 25 HAMS ROAD, WAURN PONDS VIC 3216 | 30254101 | Copper theft | [5 empty] | 2 | Unknown persons broke into zone substation and departed with drum of copper conductor ( material not connected to network) | Conductor (bare);Copper | 0 | 0 | 0 |  | WPD021 | suspect criminal activity | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43379.375 |  |  | 10008 | Other | Network Enclosure (Zone substation) | 20180614PWA_01 | Infrastructure (network-based) | -38.2152 | 144.3005 | 1 | Powercor | Report | 12298 | 0.0024826 | Not applicable | Avalon Airport | 3216 | Waurn Ponds | Other
CitiPower substation fitters have secured the door and a fault follow up will need to be actioned to retro fit the stolen copper to allow approx. 10 customers supplies to be re-instated. | 542 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | Cp0002698 | Copper theft | [6 empty] | After a customer outage a CitiPower HV operator identified a Break-in and subsequent copper theft at substation FRUIT MARKET â€˜Aâ€™ at 542 Footscray Road, West Melbourne. Victoria Police were called and were in attendance. Police report no. 21778747 has been initiated. The CitiPower operator found significant loss of copper to both the substation and the customers main switch room. The majority of the LV from the load side of the transformers including bus bar, neutral/earth bar were also missing. Additionally, the earth to the RMUâ€™s were also stolen. Access appears to be gained via the mains switch room and possibly through the substation double doors. Personal belongings were found in the substation, including a winch, which were removed and confiscated by police. There was no fire, no reported injuries. | Indoor | 2 | 2 | 2 |  | DA030 | Copper theft | Loss of supply;Damage to network assets | 43195.0465 |  |  | 10010 | Commercial |  | 20180614PWA_03 | Infrastructure (network-based) | -37.8079 | 144.9232 | 1 | CitiPower | Report | 12301 | 0.023796 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
On arrival crew isolated supply. Defect issued for POA repairs | 148 WHITEHORSE ROAD, DEEPDENE VIC 3103 | 30164624 | Working too close to overhead lines | [6 empty] | A customer informed a service pulled down at the incident location. Upon arrival the crew found that the service cable lying on the ground and the POA had been damaged. The crew found that the cable was hit by an excavator that belongs to a contractor who was working at the next door (146 Whitehorse Rd Balwyn). There was no fire, no injuries. | Service conductor | 2 | 2 | 2 |  | L010 | Excavator (Demolition) work | Loss of supply;Damage to network assets | 43286.4597 |  |  | 10015 |  |  | 20180614PWA_08 | Infrastructure (network-based) | -37.8117 | 145.071 | 1 | CitiPower | Report | 12306 | 0.010626 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Vehicle
On arrival crew isolated supply and carried out repairs. | ARGYLE HUT, 2 ARGYLE PLACE S, CARLTON VIC 3053 | 33111593 | Working too close to underground cables | [6 empty] | UG cable damage was reported adjacent to Argyle Place substation. Upon arrival, the CitiPower fault crew found that the UG LV cables had been dug up by a contractor while they removing a retaining wall. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | WA023 | Excavation work | Loss of supply;Damage to network assets | 16/04/2018 15:00 |  |  | 10017 |  |  | 20180615PWA_01 | Infrastructure (network-based) | -37.8035 | 144.9672 | 1 | CitiPower | Report | 12310 | 0.013828 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Dug up
On arrival crew isolated supply and carried out repairs. | 9 MARY COURT, YARRAWONGA VIC 3730 | 30323890 | Working too close to underground cables | [6 empty] | A contractor advised he has dug up an UG cable at the incident location. The contractor was digging with a shovel Upon arrival, the Powercor crew found that a street light cable had been damaged just away from the UG pit. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | CME014 | Hand excavation | No Go Zone (contact);Damage to network assets | 43286.4611 |  |  | 10018 | Roadway |  | 20180615PWA_02 | Infrastructure (network-based) | -36.0066 | 146.0195 | 1 | Powercor | Report | 12311 | 0.030691 | Low voltage AC (<1kV) | Wangaratta Aero | 3730 | Yarrawonga | Dug up
Electrical inspector made the required tests and fault crew replaced the overhead service | 59 MARIBYRNONG ROAD, ASCOT VALE VIC 3032 |  |  |  |  | Age |  |  | 2 | Customer received tingles as he was showering as he made simultaneously contact with the shower taps and the wet shower base. | Service conductor;Aluminium twisted (grey) | 2 | 2 | 2 |  |  | Defective neutral service at the pole end. | Minor shock | 18/06/2018 8:13 |  |  | 10026 | Residential |  | 20180618JEM_01 | Infrastructure (network-based) | -37.7723 | 144.9202 | 1 | Jemena | Report | 12331 | 0.030343 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Conductor
Arrangements were being made to secure the site. Police attended the scene and apprehended a suspect. | 542 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 |  | Copper theft | [6 empty] | A High Voltage Operator (Ashleigh Talbot) reported additional cable had been stolen from Fruit Market A substation. This is the third break-in at this substation so I am not sure what was taken on this occasion as opposed to the other occasions. From the photoâ€™s Ashleigh has supplied I can make a reasonable assumption and estimate of vandalism caused on this occasion. The other two break-ins occurred on the 4/05/2018 and the 14/05/2018. | Indoor | 2 | 2 | 2 |  | DA026 | vandalism, copper theft | Damage to network assets | 22/05/2018 9:18 |  |  | 10030 | Commercial |  | 20180618PWA_04 | Infrastructure (network-based) | -37.8079 | 144.9232 | 1 | CitiPower | Report | 12365 | 0.020529 | 11kV AC | Essendon Airport | 3003 | West Melbourne | Other
A LEI and faults truck attended and observed the property is supplied by a single phase overhead service with a switchboard in good condition. The LEI tested the installation and measured 4.8v between the shower taps and an independent earth with no load and 90v was identified with load applied. A NST was completed at the main switchboard that failed. The faults crew proceeded to check connections at pole number LIS 18272 and identified a deteriorated neutral connection at the line tap attached to the overhead reticulation. The neutral conductor was cleaned, greased and was re-terminated and installation tests completed after the fault was rectified that passed and supply was left on. | 3 ORSINO STREET, SPRINGVALE VIC 3171 | 18272 |  |  |  | Fatigue |  | Phase to earth | 2 | Caller reports that slight electric shocks have been received from the shower taps. The occupier had received electric shocks from the shower taps and proceeded to contact the United Energy faults and emergencies call centre. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | Faulty neutral connection at the pole end. | Minor shock | 16/06/2018 10:30 |  |  | 10029 | Residential |  | 20180618UTD_03 | Infrastructure (network-based) | -37.9407 | 145.157 | 1 | United Energy Distribution | Report | 12346 | 0.034911 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB located at the POA. The attending Powercor Fault Crew re-terminated the existing O/H Service Cable at the Customerâ€™s FOLCB and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 60 LINDSAY STREET, HEYWOOD VIC 3304 | 30087782 |  |  |  | Corrosion |  | Phase to earth |  | Ms Marley Bryant was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Tap and her bare feet while standing on the wet conductive shower base | Service conductor | 2 | 2 | 2 |  | PLD001 | Corroded service connection | Minor shock | 24/05/2018 7:00 |  |  | 10043 | Residential |  | 20180619PWA_04 | Infrastructure (customer connection) | -38.1326 | 141.6229 | 1 | Powercor | Report | 12474 | 0.027925 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3304 | Heywood | Connection
Crew attended. Crane removed no damage to conductor found | 610 WILSON STREET, CANADIAN VIC 3350 | 32002857 | Working too close to overhead lines | [5 empty] | 1 | A Powercor fault crew attending a 66kV line outage found that a crane contacted the line conductor. The driver was taken to hospital but no more information received. | Conductor (bare) | 0 | 0 | 0 |  | BATS BAS#2 | Interference crane operation close to OH Line | Medical attention (first aid/doctor/hospital);No Go Zone (contact) | 20/06/2018 10:54 |  |  | 10045 | Construction |  | 20180620PWA_01 | Infrastructure (network-based) | -37.5732 | 143.8857 | 1 | Powercor | Report | 12663 | 0.040512 | 66kV AC | Ballarat Aerodrome | 3350 | Canadian | Vehicle
On arrival crew isolated supply and carried out repairs. | 2-4 PLUMMER ROAD, LAVERTON NORTH VIC 3026 | 31036924 | Working too close to overhead lines | [5 empty] | 1 | A Powercor fault crew attending a 22kV line (SU034) outage found that a fork lift hit HV conductors and damaged strands on 2 conductors between LIS 213176 and LIS 975121 at 2-4 Plummer Rd Laverton North. Protection operated (22kV CB opened). There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | SU034 | Forklift struck conductors. | Loss of supply;No Go Zone (contact);Damage to network assets | 23/06/2018 11:37 |  |  | 10052 | Industrial |  | 20180625PWA_01 | Infrastructure (network-based) | -37.8161 | 144.8102 | 1 | Powercor | Report | 12488 | 0.01327 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
Fault crew attended to isolate, make safe and carry out repairs | 8 BELGRAVE AVENUE, COCKATOO VIC 3781 | LIS420504 |  | Property owner/customer |  |  |  | Phase to earth |  | IMS 233908 Medium sized Eucalypt was uprooted in strong winds at number 8 Belgrave Ave Cockatoo behind pole LIS 420504. crew found tree hard on LV & HV at pole LIS 420504 top of tree was smouldering. There was no sign of any ground fire in the vicinity of the fault | Conductor (bare) | 0 | 0 | 0 |  | BGE22 | Medium sized Eucalypt on customer property was uprooted in strong winds and fell into conductors near pole LIS 420504. investigations by both vegetation and asset teams found a phase-phase fault but â€œno sign of any ground fire in the vicinity of the faultâ€ | Singeing or local charring/blackening only | 43318.0764 |  |  | 10059 | Residential |  | 20180626SPN_02 | Infrastructure (network-based) | -37.928 | 145.4965 | 1 | AusNet Services Distribution | Report | 13387 | 0.028652 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3781 | Cockatoo | Trees
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern with traffic control required. | 1A LAGOONA COURT, BLACKBURN VIC 3130 | 7026473 |  |  |  | Overheated connection |  |  | 2 | As per Vic Roads - Street light is on fire. A 150w HPS lantern on pole No. LIS 7026473 located in Lagoona Court caught fire and was found to be burnt out and requiring replacement. | Public lighting | 0 | 0 | 0 |  |  | The cause was attributed to a loose connection that overheated. | Pole-top fire | 15/06/2018 9:35 | 1 | Negligible: no ground fire | 10056 | Roadway |  | 20180626UTD_02 | Infrastructure (network-based) | -37.833 | 145.1594 | 1 | United Energy Distribution | Report | 13074 | 0.015398 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | Connection
The Zo Go Zone supervisor contacted the United Energy control room and explained the situation. It was important to note, the work was being completed at the front of a primary school and subsequently it was decided the LV should be isolate to enable the work to be completed safely. Supply was interrupted for about 20 minutes while the scaffold was safely dismantled Andrew Rippon (Work Safe) inspector arrived at about 0915 and began his investigation. When asked about the clearances, the scaffold supervisor knew the scaffold could not be installed within 4600mm of the live power lines. | 31 ARANGA CRESCENT, DONVALE VIC 3111 |  | Working too close to overhead lines | [5 empty] | 2 | A Zinfra No Go Zone Supervisor attended a building site at 31 Aranga Crescent, Donvale where scaffold was being installed 2500mm from live low voltage conductors. A trouble order was issued to Gary Harding from Zinfra who contacted Cameron Afrasiabi 0431 630 779 of Vector Constructions on 19/6/2018 and made an appointment to meet on-site on 20/06/2018 at 0730. The No Go Zone Assessor discovered the scaffold was being installed approximately 2500mm from the Low Voltage overhead conductors. The site supervisor was informed this is a serious breech and all workers should remove them selves from the scaffold. Gary was told the scaffold was not safe in this state by the builder and they should complete the scaffold to ensure it can be tied and secured to the building. Gary proceeded to contact Work Safe and his supervisor to attend the and there may need to be an emergency shutdown to allow the scaffolding company to dismantle the scaffold. They commenced to dismantle the scaffold but the supervisor directed the workers to immediately stop as they were handling 4000mm lengths of scaffolding close proximity to the live low voltage overhead conductors. No injuries or damage was sustained. | Conductor (bare) | 0 | 0 | 0 |  |  | Breach of No Go Zone clearances between scaffold and LV overhead conductors. | No Go Zone (no contact) | 20/06/2018 8:30 |  |  | 10063 | Other | Primary School | 20180626UTD_04 | Infrastructure (network-based) | -37.8011 | 145.1735 | 1 | United Energy Distribution | Report | 12503 | 0.022765 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | Other
LEI attended site and found 294 volts at service fuse active and 47 volts on earthing system (water pipe and frame of meter panel) supply at meter panel was isolated but voltage still existed. Fault crew arrived and found active from TX rubbing against TX frame causing voltage on frame and neutral. Faulty cable has been replaced and TX put back in service. NST at service pit and all other tests at meter panel passed. Customer back on supply. | 90 HILDEBRAND ROAD, COTTLES BRIDGE VIC 3099 | LIS 920559 |  |  |  | Mechanical breakdown |  | Phase to earth | 2 | IMS 233782 Customer reported electric shock when walking outside property/house and taps tingling | Aluminium | 0 | 0 | 0 |  | DRN23 | LV cable from TX has been rubbing against TX frame resulting in damaged cable and voltage on earth and neutral causing water pipe at 90 Hilderbrand to become live. | Minor shock | 30/05/2018 15:00 |  |  | 10067 |  |  | 20180627SPN_03 | Infrastructure (network-based) | -37.5984 | 145.2272 | 1 | AusNet Services Distribution | Report | 12510 | 0.039057 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3099 | Cottles Bridge | OH Cable
Failed light removed and replaced with new. Failed light identified as an older style unit where the igniter/starter has failed. | 538 MONBULK ROAD, MONBULK VIC 3793 | 1321115 |  |  |  | Age;Defective component |  |  | 2 | IMS 233644 Pole fire reported on pole LIS 1321115 | Public lighting | 0 | 0 | 0 |  | LDL13 | Failed light identified as an older style unit where the igniter/starter has failed resulting in fire. | Other electricity related | 19/05/2018 23:47 | 1 | Negligible: no ground fire | 10072 | Residential |  | 20180628SPN_01 | Infrastructure (network-based) | -37.8728 | 145.4063 | 1 | AusNet Services Distribution | Report | 12932 | 0.012684 | Low voltage AC (<1kV) | Moorabbin Airport | 3793 | Monbulk | AF Other
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a loose neutral connection at the FMJB. Fault truck removed the existing service cable and replaced with a new service cable. CTA re-tested property, all required VESI tests passed | UNIT 7 51 KINKORA ROAD, HAWTHORN VIC 3122 |  |  |  |  | Corrosion |  | Phase to earth |  | Ishtar was showering at the time; she received an electric shock when she made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Service conductor | 2 | 2 | 2 |  |  | corroded connection | Minor shock | 43106.6458 |  |  | 10079 | Residential |  | 20180629PWA_06 | Infrastructure (customer connection) | -37.8169 | 145.035 | 1 | CitiPower | Report | 12526 | 0.010685 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Connection
The attending Fault Crew replaced the defective single phase overhead neutral screened aluminum service cable. | 42 LAHINCH STREET, BROADMEADOWS VIC 3047 |  |  |  |  | Corrosion |  |  | 2 | The customer was attempting to tighten the incoming cold water supply hose on his instantaneous hot water service when he received an electric shock as he touched the metallic casing with his left hand while he was holding a metallic shifter in his right hand which was in contact with the hose. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a severely corroded neutral screen. | Service conductor | 2 | 2 | 2 |  |  | Severely corroded neutral screen of an aluminum overhead neutral screened service cable. | Minor shock | 43107.7451 |  |  | 10082 | Residential |  | 20180701JEM_02 | Infrastructure (network-based) | -37.6909 | 144.9236 | 1 | Jemena | Report | 12529 | 0.013123 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | OH Cable
On arrival crew isolated supply and carried out repairs | 3 ELEANOR DRIVE, CAMPBELLS CREEK VIC 3451 | 30255740 |  |  |  | Electrical breakdown |  |  | 1 | Customer reported transformer was on fire but still sparking and another neighbour had heard a loud bang. Crew attended and found that two of the HV insulated leads between HV fuse and HV bushings on transformer had crossed over on two of the phases and melted. There were no injuries, no ground fire, no third party property . | Dropper/bridge | 2 | 2 | 2 |  | CMN001 | Mechanical clearance | Pole-top fire | 29/05/2018 20:52 | 1 | Negligible: no ground fire | 10089 | Roadway |  | 20180705PWA_02 | Infrastructure (network-based) | -37.1018 | 144.2055 | 1 | Powercor | Report | 12541 | 0.00058218 | 22kV AC | Bendigo Airport | 3451 | Campbells Creek | OH Cable
Fault crew and LEI dispatched to investigate, make safe and carry out repairs The attending service crew isolated the supply due to the bare conductors on the ground and contacted LEI to investigate suspected HVI. LEI inspected all affected properties and found evidence of HV injection, affected customers isolated at LV POA. Repairs carried out and supply restored following testing and re connection process | 1 STATION STREET, BELGRAVE VIC 3160 | LIS 1307923 |  | Fallen | [5 empty] | IMS 234227 - Tree fell and made contact with overhead conductors resulting in HV Injection | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | HV injection | 43197.6653 |  |  | 10088 |  |  | 20180705SPN_01 | Infrastructure (network-based) | -37.9127 | 145.3448 | 1 | AusNet Services Distribution | Report | 12540 | 0.008162 | 22kV AC | Moorabbin Airport | 3160 | Belgrave | Trees
Crew attended and replaced missing earth cable | HACKETTS ROAD, POINT COOK VIC 3030 | 33073497 | Copper theft | [5 empty] | 2 | Employee report earth cable stolen from Hackett Dunning Nth pole 04S. There were no shocks, injuries or ground fire start. | Earth/earthing | 2 | 2 | 2 |  | WBE013 | Copper theft | Damage to network assets | 43106.4861 |  |  | 10103 | Roadway |  | 20180709PWA_04 | Infrastructure (network-based) | -37.8795 | 144.719 | 1 | Powercor | Report | 12560 | 0.036579 | Earthing cable | Laverton Raaf | 3030 | Point Cook | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. In addition, an illegal connection was identified at the POA at 1274 Toorak Road and supply was isolated at the pole end and a defect notice issued. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1256 TOORAK ROAD, CAMBERWELL VIC 3124 | 2309719 | Vehicle |  |  | HV injection |  |  | 1 | At 0332hrs on 25/06/2018, 11kV feeder RD 10 circuit breaker reclosed to lockout affecting 1009 customers. An out of control vehicle struck a HV/LV intermediate pole number LIS 2309719 outside 1256 Toorak Road that caused significant damage. A HV conductor made brief contact with the LV conductors below when the pole and cross arm broke and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Yeovil-Toorak" substation. The LEI confirmed a high voltage injection occurred (BWD 1810) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | RD 10 | A vehicle struck a HV/LV intermediate pole. | HV injection | 25/06/2018 3:32 |  |  | 10099 | Residential |  | 20180709UTD_02 | Infrastructure (network-based) | -37.8492 | 145.0837 | 1 | United Energy Distribution | Report | 12555 | 0.037853 | 11kV AC | Moorabbin Airport | 3124 | Camberwell | Vehicle
The crew removed the OH service and meter from site and issued a level 1 defect. | 4 IDA STREET, NIDDRIE VIC 3042 |  | Unauthorised access | [5 empty] | 2 | Jemena Network Connections (NCâ€™s) contacted compliance with an enquiry where the customer contacted NCâ€™s trying to arrange an abolishment of an OH BTS. NCâ€™s had no record of a BTS on site with the meter on site registered as a residential tariff and not a BTS. A crew attended to make an assessment. Please see attached photos of the OH service. It was confirmed the meter on site was not registered to a BTS and NCâ€™s confirmed it is a residential meter and not a BTS. The high meter read also confirms this is not an authorised BTS connection and there is no record of a BTS at this address. The crew removed the OH service and meter from site and issued a level 1 defect. | Service conductor;Smart meter | 0 | 2 | 0 |  |  | Unauthorised relocation of Jemena Assets by unknown persons | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43350.5111 |  |  | 10105 | Residential |  | 20180710JEM_01 | Infrastructure (network-based) | -37.7459 | 144.8906 | 1 | Jemena | Report | 12564 | 0.026821 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | Other
Line was isolated, cross-arm was replaced. Customer service was replaced & installation tested for signs of possible HVI | 3794B HATTAH-ROBINVALE ROAD, WEMEN VIC 3549 | 30099965 |  |  |  | Leakage |  |  |  | Customer reported a low conductor at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a EDO fuse unit mounting position. conductor was adrift but remained suspended 4.0M above the ground. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WN013 | Excessive leakage current | Pole-top fire | 43319.9132 | 1 | Negligible: no ground fire | 10106 |  |  | 20180710PWA_01 | Infrastructure (network-based) | -34.7784 | 142.6515 | 1 | Powercor | Report | 12565 | 0.032571 | 22kV AC | Mildura Airport | 3794 | Wemen | Crossarm
Crew repaired damaged earth cable. | 289 PRINCES STREET, PORT MELBOURNE VIC 3207 | 30239340 | Working too close to underground cables | [6 empty] | Contractor reports damaging U/G cable OPP 289 Princes St, Port Melbourne. Crew attended and found contractor using trencher had hit and damaged HV earth cable at S/S Stokes Farrell P01N. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MG014 | Excavation works | Damage to network assets | 43226.3785 |  |  | 10108 | Roadway |  | 20180710PWA_03 | Infrastructure (network-based) | -37.8362 | 144.9411 | 1 | CitiPower | Report | 12567 | 0.038291 | Earthing cable | Essendon Airport | 3207 | Port Melbourne | Dug up
The crew isolated supply to the private service cable and advised the customer to engage an REC to replace the private service cable with an underground service. | 271 SOLLY ROAD, RAINBOW VIC 3424 | 30148900 |  |  |  | Fault on customer installation |  |  |  | A report was received from the customer at the above address that the service cable from our pole to an un-occupied house on the property had been hit and broken by an excavator. On arrival the crew found that an excavator had hit and broken the private service from Rainbow West Pole 31 to an un-occupied house on the customers property. There was no fire or reported injuries. | Private overhead electric line (POEL) | 2 | 2 | 2 |  | NHL015 | Excavator contacted POEL | Loss of supply;No Go Zone (contact) | 43410.541 |  |  | 10112 | Agricultural |  | 20180710PWA_06 | Infrastructure (network-based) | -35.9024 | 141.9433 | 1 | Powercor | Report | 12571 | 0.03102 | Low voltage AC (<1kV) | Horsham Aerodrome | 3424 | Rainbow | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole The attending Powercor Fault Crew reterminated the existing O/H Service Cable to the Red Phase at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 22 LAIDLAW AVENUE, EDENHOPE VIC 3318 | 33050278 |  |  |  | Corrosion |  | Phase to earth |  | Ms Amy Stokes was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | CHM011 | Corroded connection | Minor shock | 31/05/2018 0:00 |  |  | 10115 | Residential |  | 20180710PWA_08 | Infrastructure (network-based) | -37.0335 | 141.2833 | 1 | Powercor | Report | 12574 | 0.0079965 | Low voltage AC (<1kV) | Horsham Aerodrome | 3318 | Edenhope | Connection
Supply was isolated and the site made safe. The melted FOLCB and damaged services were repaired and/or replaced and supply restored upon completion. | 10 CLEMATIS COURT, RYE VIC 3941 | 1318371 |  |  |  | Electrical overload;Overheated connection |  |  | 2 | Pole fire per fire authority. A pole mounted FOLCB with underground cables connected at pole No. LIS 1318371 located in Clematis Court caught on fire due to probable overload or loose connections. | Connection box | 0 | 0 | 0 |  |  | The cause was attributed to either probable overload or loose connections. | Pole-top fire | 30/06/2018 20:05 | 1 | Negligible: no ground fire | 10116 | Roadway |  | 20180710UTD_02 | Infrastructure (network-based) | -38.3838 | 144.7931 | 1 | United Energy Distribution | Report | 13079 | 0.02572 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Connection
On arrival crew isolated supply and carried out repairs. | 33-35 BANOOL ROAD, BALWYN VIC 3103 | 30176489 |  |  |  | Overheated connection |  |  |  | Police and MFB reported a pole fire at the above incident location. On arrival, the crew found that a Fuse Switch Disconnect (FSD) unit overheated and caught on fire. Melted pieces fell onto the grass nature strip. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | WD031 | Insufficient remains to determine cause. | Pole-top fire | 43319.7674 | 1 | Negligible: no ground fire | 10118 | Roadway |  | 20180711PWA_01 | Infrastructure (network-based) | -37.8128 | 145.093 | 1 | CitiPower | Report | 12793 | 0.026714 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Fuse
Site was made safe Jemena Works Practices contacted REC to advise him that he should have contacted Jemena Compliance who would have arranged an Authorised Contractor to install a "Pole to Pit" for the customer | 50 CARROLL LANE, GREENVALE VIC 3059 | Pole no. pole A054621 | Building too close or within the No Go Zone;Unauthorised access | [5 empty] | 2 | Jemena crew attended a overhead BTS (buider's temporary supply) connection appointment on Tuesday 3 July 2018 at the incident location, and discovered that the REC (registered electrical contractor) had run underground mains directly out to Jemena's pole in the street and mounted a new one phase mains box directly behind the low voltage terminals of the transformer. Incident was reported by Compliance Officer who completed an inspection of the installation and is considered a No Go Zone breach because the REC accessed Jemena's pole to install underground cable. REC details is shown on the Certificate of Electricity Safety, which is attached in the "Notes and Findings" section. | Pole (wood);Cable;Pole mounted | 0 | 2 | 2 |  | COO21 | REC did not contact Jemena Compliance who would have arranged an Authorised Contractor to install a "Pole to Pit" for the customer | No Go Zone (contact) | 43166.4903 |  |  | 10131 | Residential |  | 20180712JEM_01 | Infrastructure (network-based) | -37.646 | 144.8747 | 1 | Jemena | Report | 12601 | 0.0029051 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
On arrival crew isolated supply and carried out repairs. | 23 KATHERINE DRIVE, RAVENHALL VIC 3023 | 30304015 | Vandalism | [6 empty] | The Lendlease contractor informed vandalized cable pit at the incident location. Upon arrival, the Powercor crew found that the UG pit had been taken off from the ground and vandalized. They found the UG pit at 21 Katherine Dr also vandalized There was no fire, no reported injuries or third party property damage. | Services pit | 2 | 2 | 2 |  | SU015 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43411.5889 |  |  | 10124 | Public space |  | 20180712PWA_01 | Infrastructure (network-based) | -37.7656 | 144.7442 | 1 | Powercor | Report | 12594 | 0.0039282 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Ravenhall | Other
On arrival crew isolated supply and carried out repairs. | PORTLAND N, 632 HENTY HIGHWAY, PORTLAND NORTH VIC 3305 | 33056439 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a pole fire at the incident location. Upon arrival, the Powercor crew found that the street light caught fire at the incident location There was no ground fire, no reported injuries or third party property damage | Public lighting | 2 | 2 | 2 |  | PLD004 | Overheated connection | Pole-top fire | 43350.3667 | 1 | Negligible: no ground fire | 10126 | Roadway |  | 20180712PWA_03 | Infrastructure (network-based) | -38.3201 | 141.5965 | 1 | Powercor | Report | 12596 | 0.017656 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland North | Connection
Fault crew attended to de-endergise, make safe and carry out repairs | 4 MARDAN-DUMBALK ROAD, DUMBALK VIC 3956 | LIS 2008452 |  |  |  | Age;Corrosion;Defective component |  | Phase to earth |  | IMS 234434 - Live HV conductor on the ground. 3/12 Steel conductor broken at the Ampac connector at pole LIS 2008452. | Conductor (bare) | 0 | 0 | 0 |  | LGA13 | 3/12 Steel conductor broken at the Ampac connector at pole LIS 2008452 | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/07/2018 0:42 |  |  | 10148 |  |  | 20180716SPN_03 | Infrastructure (network-based) | -38.522 | 146.0827 | 1 | AusNet Services Distribution | Report | 12623 | 0.016785 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Dumbalk | Connection
LEI attended to investigate and make safe 4.5 v measured from water pipe to independent earth. Voltage ranged from 1V â€“ 6V with customers main switch in the off position. Fault crew replaced poor neutral bridge at pole on the corner of Parkview Dr & Merricks Close | 5 MERRICKS CLOSE, FERNTREE GULLY VIC 3156 |  |  |  |  | Neutral fault |  | Phase to earth |  | IMS 234300 - Tradesperson was repairing central heating ducting under house & received electrical shock from water pipe | Service conductor | 0 | 0 | 0 |  |  | Damaged neutral bridge at pole | Minor shock | 43350.5257 |  |  | 10154 | Residential |  | 20180716SPN_05 | Infrastructure (network-based) | -37.8902 | 145.2869 | 1 | AusNet Services Distribution | Report | 12634 | 0.029639 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Ferntree Gully | Connection
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern located in the north bound lane and traffic control will be required to complete the replacement after hours. | SPRINGVALE ROAD, NUNAWADING VIC 3131 | 9751815 |  | Precipitation |  | Electrical overload;Overheated connection |  |  | 2 | MFB advised that a street light is on fire. During light drizzle, a 150w high pressure sodium (HPS) lantern caught fire on pole No. LIS 9751815 located on the corner of Springvale Road 1 pole north of Whitehorse Road opposite the ambulance depot. | Public lighting | 0 | 0 | 0 |  |  | Probable loose and overheated connection. | Pole-top fire | 43350.0382 | 1 | Negligible: no ground fire | 10153 | Roadway |  | 20180716UTD_04 | Infrastructure (network-based) | -37.8179 | 145.176 | 1 | United Energy Distribution | Report | 12631 | 0.010941 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Nunawading | Connection
On arrival, the crew found that the residents blue was indeed out of service. Further investigation determined that earlier on in the day, a truck (semi-trailer) lost control and hit a few HV poles along Toorak Road on United Energy (UE) Network which caused HV injection. Repairs organised | 1263 TOORAK ROAD, CAMBERWELL VIC 3124 | 30176684 | Vehicle | [6 empty] | CitiPower residents reported their LV Blue Phase is out of service at the above incident locations after their Registered Electrical Contractor checked their supply. There were no reported shockâ€™s, injuries or fire as a result of this incident. | Conductor (bare) | 2 | 2 | 1 | United Energy network | RD010 | Vehicle incident | HV injection | 25/06/2018 18:34 |  |  | 10161 | Residential |  | 20180717PWA_05 | Infrastructure (network-based) | -37.8489 | 145.0844 | 1 | CitiPower | Report | 12640 | 0.024023 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Vehicle
On arrival crew isolated supply and carried out repairs | 3399 WOORNDOO-STREATHAM ROAD, STREATHAM VIC 3351 | 30356380 |  |  |  | Corrosion;Fatigue |  |  |  | A passer-by advised a ground fire at the incident location. On arrival the Powercor crew found that a HV conductor lying on the ground. There was a ground fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | ART033 | Fallen conductor | Grassfire | 17/07/2018 12:50 | 1 | Small: 10 - 1000 sq.m | 10169 | Roadway |  | 20180718PWA_01 | Infrastructure (network-based) | -37.6998 | 143.0749 | 1 | Powercor | Report | 13111 | 0.020487 | 22kV AC | Ballarat Aerodrome | 3399 | Streatham | Conductor
On arrival isolated supply and carried out repairs | 32 HEDDERWICK STREET, BALWYN NORTH VIC 3104 | 30189247 | Working too close to underground cables | [6 empty] | Powercor contractor dug up and damaged LV U/G cable. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WD032 | Excavation work | No Go Zone (contact) | 17/07/2018 15:34 |  |  | 10171 | Roadway |  | 20180718PWA_03 | Infrastructure (network-based) | -37.7992 | 145.0993 | 1 | CitiPower | Report | 12862 | 0.0085833 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Dug up
On arrival crew isolated supply and carried out repairs | RIVERVIEW, 185 UPTONS ROAD, STRATHDOWNIE VIC 3312 | 32134589 |  |  |  | Leakage |  |  |  | Customer reported Pole Fire at Myaring P43, HTN002. Crew attended and confirmed incident . There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | HTN002 | Excessive leakage current | Pole-top fire | 43441.3694 | 1 | Negligible: no ground fire | 10175 | Agricultural |  | 20180718PWA_06 | Infrastructure (network-based) | -37.736 | 141.2397 | 1 | Powercor | Report | 12657 | 0.013177 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3312 | Strathdownie | Pole
On arrival crew isolated supply and replaced pole. | WOROOA, 710 BOINKA SOUTH ROAD, BOINKA VIC 3490 | 32140466 |  |  |  | Leakage |  |  | 1 | Customer reports outage and pole in paddock on ground. crew attended and found P35 Boinka Sth S/L on ground, burnt off at butt. There was no reports of injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire;Grassfire | 20/07/2018 7:35 | 1 | Localised: less than 10 sq.m | 10196 | Agricultural |  | 20180723PWA_02 | Infrastructure (network-based) | -35.2551 | 141.5878 | 1 | Powercor | Report | 12688 | 0.0097789 | 12.7kV AC (SWER) | Mildura Airport | 3490 | Boinka | Pole
On arrival crew isolated supply and carried out repairs | 14 BUCCLEUGH STREET, DRYSDALE VIC 3222 | 30065961 |  |  |  | Leakage |  |  |  | A customer reported a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | DDL013 | Excessive leakage current. | Pole-top fire | 22/07/2018 12:32 | 1 | Negligible: no ground fire | 10198 | Roadway |  | 20180723PWA_04 | Infrastructure (network-based) | -38.1812 | 144.5706 | 1 | Powercor | Report | 12690 | 0.0025093 | 22kV AC | Avalon Airport | 3222 | Drysdale | Pole
Tree was cut clear and removed from HV & LV Conductors. Crew also repaired R and B HV conductors and B and N LV conductors LEI attended and managed HVI damage | 25 CHEDGEY DRIVE, ST ALBANS VIC 3021 | 32169488 |  | Blown branch/vegetation |  |  |  |  | 1 | Nearby customer advised that branches from a tree in the adjacent school property dislodged and landed across the overhead high voltage. It appears the weight of the vegetation brought the HV into contact with the LV circuit underneath There was HV injection damage confirmed to some 14 premises and there have been several Licenced Electrical Inspectors were on site this morning evaluating damage. Contact was reportedly between pole LIS 14968 and LIS 14969 Most supplies in the area have now been restored. | Conductor (bare) | 0 | 0 | 0 |  | SA001 | vegetation broken during storm | HV injection;Loss of supply | 23/07/2018 17:32 |  |  | 10206 | Roadway |  | 20180724PWA_05 | Infrastructure (network-based) | -37.756 | 144.81 | 1 | Powercor | Report | 12699 | 0.01175 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3021 | St Albans | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a damaged and corroded O/H Service Neutral Conductor at the POA and the Reticulation Pole, he insulation of the Active and Neutral Conductors of the O/H Service Cable were also damaged by the â€œDog Boneâ€ where the sharp end of the inner metallic rod was exposed and made contact with the Active and Neutral Conductors at the Customerâ€™s POA. The attending Powercor Fault Crew replaced the damaged O/H Twisted Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 18 OBERON DRIVE, BELMONT VIC 3216 | 30076664 |  |  |  | Corrosion;Mechanical breakdown |  | Phase to earth |  | Mrs Daniela Lowden was in the Bathroom Showering when she received an electric shock as she made simultaneous contact with her hand on the metal Shower Tap and her bare feet whilst standing on the wet shower base. | Service conductor;Connector/termination | 2 | 2 | 2 |  | GLE012 | Damaged and corroded O/H Service Neutral Conductor | Minor shock | 20/07/2018 12:15 |  |  | 10220 |  |  | 20180726PWA_02 | Infrastructure (network-based) | -38.1886 | 144.3414 | 1 | Powercor | Report | 12715 | 0.026862 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customer's POA. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 4 MONTGOMERY AVENUE, HAMLYN HEIGHTS VIC 3215 | 30057960 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Megan Hickey was in the Bathroom showering when she received an electric shock as she made simultaneous contact with her hand on the metal Shower Rose and her bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GL015 | Corroded O/H Service Neutral Conductor termination at the Customer's POA. | Minor shock | 22/06/2018 20:00 |  |  | 10222 | Residential |  | 20180726PWA_04 | Infrastructure (customer connection) | -38.1219 | 144.3338 | 1 | Powercor | Report | 12717 | 0.0066412 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | Connection
On arrival crew isolated supply, and commenced repairs. Individual was transported to hospital for observation (prior to crew arriving) and released next morning. | 127 BURROWS STREET, MILDURA VIC 3500 | 32145875 | Misadventure | [6 empty] | A 21 YO male fell from Tree landing on service line. and subsequently fell to ground. The service broke on impact also damaging POA on adjacent premises. The service was found to be alive resting on a metal fence. There was no fire. or reported electrical shocks. | Service conductor | 2 | 2 | 2 |  | MDA032 | Misadventure | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/07/2018 12:15 |  |  | 10225 | Roadway |  | 20180727PWA_01 | Infrastructure (network-based) | -34.1979 | 142.1499 | 1 | Powercor | Report | 12720 | 0.037639 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Other
The attending Luma glove and barrier crew contacted United Energy and proceeded to replace the copper earth conductor at the pole type substation and made the site safe. | 295 OLD DANDENONG ROAD, DINGLEY VILLAGE VIC 3172 | 637029 | Copper theft | [5 empty] | 2 | A Luma Energy Glove & Barrier crew identified the LV earth conductor had been removed from pole number LIS 0637029. When in attendance for planned work, the glove and barrier crew identified the copper earth conductor at "Old Dnong-Boundary" pole type substation had been removed from the pole by unknown persons. | Earth/earthing | 0 | 0 | 0 |  | ss 24 | Copper theft from a pole in the road reserve. | Damage to network assets | 26/07/2018 13:00 |  |  | 10229 | Roadway |  | 20180727UTD_04 | Infrastructure (network-based) | -37.9677 | 145.1137 | 1 | United Energy Distribution | Report | 12724 | 0.029942 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Other
Made Safe | 115 PROVIDENCE ROAD, GREENVALE VIC 3059 |  | Copper theft | [5 empty] | 2 | Copper theft from pole and pillar | Cable;LV Pillar | 0 | 0 | 0 |  |  | Copper Theft: UG LV cable going down side of pole to pillar | Damage to network assets | 30/07/2018 17:40 |  |  | 10238 | Roadway |  | 20180730JEM_02 | Infrastructure (network-based) | -37.6477 | 144.8692 | 1 | Jemena | Report | 12734 | 0.027053 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
Fault truck dispatched to make safe and carry out repairs | 75 MT EIRENE ROAD, NAR NAR GOON NORTH VIC 3812 | LIS 503977 |  | Fallen |  |  |  | Phase to earth |  | IMS 234510 - LV conductors on ground due to tree | Conductor (bare) | 0 | 0 | 0 |  | OFR23 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/07/2018 7:21 |  |  | 10234 | Forest - native (not park) |  | 20180730SPN_01 | Infrastructure (network-based) | -38.0021 | 145.5549 | 1 | AusNet Services Distribution | Report | 12730 | 0.038427 | Low voltage AC (<1kV) | Moorabbin Airport | 3812 | Nar Nar Goon North | Trees
Crews removed extension cord and made site safe. No impact to customers installation | 62 BLANDFORD STREET, WEST FOOTSCRAY VIC 3012 |  | Building too close or within the No Go Zone | [5 empty] | 2 | Jemena crew in transit the guys last came across illegal wiring and a No Go Zone Breach. Supply went across the road from owners house to another premise in which he owns and is building. Tech Safe Scott Beesly attended. | No failed asset | 2 | 2 | 2 |  |  | It appears owner ran an extension cord across the road to his/her another property. | No Go Zone (no contact) | 29/07/2018 14:26 |  |  | 10244 | Residential |  | 20180731JEM_03 | Infrastructure (network-based) | -37.7967 | 144.8768 | 1 | Jemena | Report | 12740 | 0.025479 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Other
Tests using an independent earth to various points of the installation including the reported points of contact, 5V was found on the customers earthing system and distribution neutral. It was traced back to a possible fault in the CitipPwer Bristol-Middlesex pole mounted substation. Up to 10V was measured at the transformer star point and LV neutral at the substation The crew put LV parallels in and the substation was switched out of service. This resulted in the neutral voltage dropping to around 1V. A follow up request was lodged to get the substation tested. | 100 MIDDLESEX ROAD, SURREY HILLS VIC 3127 | 33109644 |  |  |  | Neutral fault |  | Phase to earth |  | Chris reports receiving a slight shock in her right hand fingers when she touched the shower taps. | Transformer | 2 | 2 | 2 |  | RD006 | Suspected Transformer fault | Minor shock | 22/07/2018 7:30 |  |  | 10239 | Residential |  | 20180731PWA_01 | Infrastructure (network-based) | -37.8331 | 145.0886 | 1 | CitiPower | Report | 12735 | 0.026741 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | AF Other
Crew isolated supply to pit and replaced broken conduit. Re installed pit. | 37 TORQUAY BOULEVARD, JAN JUC VIC 3228 | 32081564 | Working too close to underground cables | [5 empty] | 2 | Customer rang to advise builder has ripped up pit of property boundary. Crew attended and found concreter install new driveway had pulled up pit and conduit/cable on property boundary. Supply still on. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WPD032 | Excavation work | No Go Zone (contact);Damage to network assets | 43139.3472 |  |  | 10252 | Roadway |  | 20180802PWA_05 | Infrastructure (network-based) | -38.3421 | 144.3015 | 1 | Powercor | Report | 12751 | 0.037292 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Dug up
Crew replaced stolen copper cable. | 55 CUMMINGS ROAD, MADDINGLEY VIC 3340 | 30308301 | Copper theft | [6 empty] | Electrix inspector reports copper earth cables missing from SW P1 Balliang S/L. No shocks, 3rd party damage or ground fire starts. | Earth/earthing | 2 | 2 | 2 |  | BMH006 | Copper theft | Damage to network assets | 27/07/2018 8:48 |  |  | 10257 | Roadway |  | 20180803PWA_02 | Infrastructure (network-based) | -37.7003 | 144.4496 | 1 | Powercor | Report | 12756 | 0.040354 | Earthing cable | Avalon Airport | 3340 | Maddingley | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customerâ€™s POA, The attending Powercor Fault Crew reterminated the existing O/H Service Cable at the FOLCB located at the Customerâ€™s POA and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 97-101 VERDON STREET, WARRNAMBOOL VIC 3280 | 33101335 |  |  |  | Corrosion |  | Phase to earth |  | Mr Philip Lawrence was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metal tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WBL012 | corroded connection | Minor shock | 17/07/2018 0:00 |  |  | 10260 | Residential |  | 20180803PWA_04 | Infrastructure (customer connection) | -38.3866 | 142.5052 | 1 | Powercor | Report | 12759 | 0.023431 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew confirmed site safe | 20 MIAMI STREET, HAWTHORN EAST VIC 3123 | 30201531 | Vandalism;Copper theft | [6 empty] | arly in the morning about :5:00pm a truck pulled up near this address and attached the 16mm2 4core service to its rear then drove off pulling the service from the pole. The service was ready to be installed by new connections. Thirty meters of service stolen. Damage to fixtures and fittings on the pole. No injuries or fire reported. | Services cable | 2 | 2 | 2 |  | CL011 | Vandalism, Copper theft | Damage to network assets | 43259.2083 |  |  | 10269 | Roadway |  | 20180807PWA_03 | Infrastructure (network-based) | -37.8347 | 145.0452 | 1 | CitiPower | Report | 12772 | 0.017177 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Other
Crew made area safe and the underground service has been made secure. | 10 THEA AVENUE, BALWYN NORTH VIC 3104 | 30191228 | Copper theft | [6 empty] | The underground service to demolished building was left rolled up on pole LIS 7408. The underground service had been tampered with insulation stripped away and copper removed. Date when this happened is unknown. There was no injury or fire associated with this incident. | Services cable | 2 | 2 | 2 |  | WD032 | Copper theft | Damage to network assets | 43259.5729 |  |  | 10270 | Roadway |  | 20180808PWA_01 | Infrastructure (network-based) | -37.7977 | 145.0994 | 1 | CitiPower | Report | 12773 | 0.019826 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
Fault crew dispatched to make safe | 130 COOPER STREET, EPPING VIC 3076 | LIS 5658165 |  |  |  | Defective component |  |  |  | IMS 234761 - MFB reported street light fire | Public lighting | 0 | 0 | 0 |  | EPG23 | DAO arrived on site to find evidence of a burnt out 150w Street light. The street light was burnt from the top of the structure indicating faulty wiring rather than a blown globe. The light structure itself extends over the road so there was no ground fire to report. The fire was contained to the top of the pole. Fault crew had already attended site the night before but light had not been repaired/replaced as crew did not have spare 150W available at the time. | Pole-top fire | 43198.7875 | 1 | Negligible: no ground fire | 10273 |  |  | 20180808SPN_02 | Infrastructure (network-based) | -37.651 | 145.0166 | 1 | AusNet Services Distribution | Report | 12778 | 0.012565 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | Pole
Inspector conducted test to find the cause. Corroded service was replaced. Test was repeated to confirm safety. | 29A GLADSTONE STREET, COBURG VIC 3058 |  |  |  |  | Corrosion |  |  | 2 | Customer received a minor shock from the shower taps due to corroded neutral. Additional information can be found in TechSafe report attached in '7.Notes & Findings' | Neutral screen | 2 | 2 | 2 |  |  | Corroded neutral termination at the junction box on pole causing higher than normal impedance within neutral service conductor. | Minor shock | 43351.6986 |  |  | 10285 |  |  | 20180809JEM_01 | Infrastructure (network-based) | -37.7449 | 144.9761 | 1 | Jemena | Report | 12796 | 0.021759 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets,identified a corroded O/H Service Neutral Conductor termination external to the FOLCB located at the Customer's POA. The attending Powercor Fault Crew replaced the FOLCB at the Customer's POA and re-terminated the existing O/H Service Cable and completed an NST test which confirmed a PASS result. final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 6395 HAMILTON HIGHWAY, CRESSY VIC 3322 | 32066626 |  |  |  | Corrosion |  | Phase to earth |  | Mr John Nelson was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metallic Shower Tap and his bare feet while standing on the wet conductive shower base. | Service conductor | 2 | 2 | 2 |  | CLC003 | Corroded O/H Service Neutral Conductor termination | Minor shock | 25/05/2018 21:30 |  |  | 10040 | Residential |  | 20180619PWA_03 | Infrastructure (customer connection) | -38.0322 | 143.6679 | 1 | Powercor | Report | 12469 | 0.037897 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3322 | Cressy | Connection
The faults crew installed LV parallels to restore supply to the street circuit and the indoor substation was secured with the stolen copper cables replaced. Supply was restored to normal upon completion. The indoor substation cannot be isolated as it presently supplies a LV circuit that supplies the surrounding shopping strip with another LV circuit providing a dedicated supply to the Grand Hotel. | PLAYNE STREET, FRANKSTON VIC 3199 |  | Copper theft | [5 empty] | 2 | Customers supplied from "Playne N16 Nepean" substation advised of an all supply failure and a faults truck was dispatched to investigate. A live United Energy Indoor type substation named "Playne N16 Nepean" has been broken into by unknown persons and electricity (copper) cabling stolen. The multi-storey building has been abandoned and unauthorised entry was made through the steel door that had hinges fitted with bolts that been grinded off to gain access. A live street circuit supplying the local shopping strip appeared to have been isolated by opening fuses at the weber strip and short lengths of copper cables removed for two circuits cut between the live LV bus and the bottom of the weber strip. In addition, a length of copper cable that supplied the abandoned building where the indoor substation is located had been cut and removed. It was unknown if any electric shocks or flash burns were sustained in the brazen theft. Apparently young kids frequently break into the abandoned building along with homeless people residing inside. The police were called by the faults crew as people remained in the building and they wanted to ensure they were safe during the rectification work to secure the site. | Cable;Copper;Indoor | 0 | 0 | 0 |  | FSH 31 | Unauthorised entry into a United Energy indoor substation and copper cables stolen. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/06/2018 8:00 |  |  | 10044 | Commercial |  | 20180620UTD_01 | Infrastructure (network-based) | -38.1447 | 145.1212 | 1 | United Energy Distribution | Report | 12475 | 0.039323 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Other
A LEI attended and tested the guttering and fascia with a voltage on 0.4v identified at the point of contact. When load was applied to the electrical installation, there was no change in the voltage recording. NST was completed and passed at the main switchboard and metering equipment. The LEI discussed the circumstances with the plumber when the shock was received and it was determend that water ingress prior to works comencing was the likley cause as water was seen in and around the consumers FMJB. | 5 RICHARD STREET, DONCASTER EAST VIC 3109 |  |  |  |  | Moisture ingress |  | Phase to earth | 2 | REC Luke rang the United Energy faults and emergencies call centre to report that plumbers from Wizz and Works are receiving tingles from the guttering. A plumber recieved a slight electric shock to his hand whilst replacing the guttering and fascia near the point of attachment. | Customer installation | 0 | 0 | 0 |  |  | Water ingress at POA that had earlier tracked to the guttering and facia board. | Minor shock | 19/06/2018 15:30 |  |  | 10049 | Residential |  | 20180624UTD_01 | Infrastructure (customer connection) | -37.795 | 145.1671 | 2 | United Energy Distribution | Report | 12484 | 0.032692 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Connection
Fault crew attended to isolate and make safe. Fuse units replaced | 13 CHAFFEY STREET, THOMASTOWN VIC 3074 | 907501 |  |  |  | Candled fuse |  |  | 0 | IMS 233830 Bird contact with Overhead line resulting in candling fuse | Powder filled | 0 | 0 | 0 |  | TT7 | Bird Incident | Hung-up fuse only;Other electricity related | 43196.2215 | 1 | Negligible: no ground fire | 10061 | Commercial |  | 20180626SPN_03 | Infrastructure (network-based) | -37.6895 | 145.0052 | 1 | AusNet Services Distribution | Report | 12818 | 0.0050521 | 22kV AC | Essendon Airport | 3074 | Thomastown | Animal
A faults crew promptly attended and proceeded to isolate and remove the two fire damaged three phase FOLCB's. There was evidence also of blackening on the pole from heat and fire where the FOLCB's were located. The two fire damaged three phase FOLCB's were replaced and supply restored following the completion of installation tests. | 1 KEATING AVENUE, SORRENTO VIC 3943 | 1306410 |  | Prone to salt deposition |  | Corrosion |  |  | 2 | Pole fire reported by the CFA. Two x three phase FOLCB on pole No. LIS 1306410 located opposite 8 Keating Avenue caught fire and was found to be burnt out and requiring replacement. The pole is located in close proximity to Port Phillip Bay and a possible cause was attributable to salt corrosion. | Connection box | 0 | 0 | 0 |  |  | The pole is located in close proximity to Port Phillip Bay and a possible cause was attributable to salt corrosion. | Pole-top fire | 19/06/2018 4:30 | 1 | Negligible: no ground fire | 10057 | Roadway |  | 20180626UTD_03 | Infrastructure (network-based) | -38.3569 | 144.7509 | 1 | United Energy Distribution | Report | 13076 | 0.012826 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Pole
A LEI and faults crew attended and completed installation tests and identified fluctuating voltages on the water pipes with the highest reading of 4.4v measured. The faults crew proceeded to check all of the overhead service connections found that a pole mounted junction box at pole No. LIS 0610296 had a damaged neutral connection. A new XLPE overhead service was installed and the LEI tested the installation upon completion and measured 0.6v to an independent earth. A NST was completed that passed and supply was left on. | 15 PAULINE AVENUE, DINGLEY VILLAGE VIC 3172 | 610296 |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 2 | The caller advised he was having a shower and received minor tingles which he described was enough for him to let go of the taps. His partner Carmen was having a shower the evening before at approximately 6.00PM and also experienced the same sensation. He advised the lights in the house were flickering on both of these occasions. The occupier had received electric shocks from the shower taps and proceeded to contact the United Energy faults and emergencies call centre. Explained the lights were also constantly flickering. | Connection box | 0 | 0 | 0 |  |  | Deteriorated neutral connection in the pole mounted junction box. | Minor shock | 23/06/2018 8:00 |  |  | 10064 | Residential |  | 20180626UTD_05 | Infrastructure (network-based) | -37.9846 | 145.1315 | 1 | United Energy Distribution | Report | 12507 | 0.028535 | Low voltage AC (<1kV) | Moorabbin Airport | 3172 | Dingley Village | Connection
LEI attended to make safe and investigate Installation repaired and copper crimps installed, subsequent NST and voltage tests pasts. Supply restored | 65 RECREATION ROAD, YAN YEAN VIC 3755 | LIS 918108 |  |  |  | Not built/maintained to design |  | Phase to earth | 2 | IMS 233786 The customer reported received electric shock from their shower tap. Crew attended site and found the POA neutral sparking. The aluminium service was installed directly into the POA causing sparking | Aluminium | 0 | 0 | 0 |  | DRN22 | Aluminium service installed directly into POA without suitable lugs/crimps | Minor shock | 30/05/2018 16:20 |  |  | 10066 | Residential |  | 20180627SPN_02 | Infrastructure (customer connection) | -37.5652 | 145.1218 | 1 | AusNet Services Distribution | Report | 12509 | 0.018979 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3755 | Yan Yean | Connection
LEI attended to make safe and investigate Inspected all connections and everything tested ok, no voltage was measured and NST passed | 30 WEBSTER AVENUE, VENUS BAY VIC 3956 |  |  | Precipitation |  | Corrosion |  | Phase to earth |  | IMS 233707 Plumber reported electric shock off roof | Connection box | 0 | 0 | 0 |  | WGI14 | Light rain had been falling and POA had dust/cobwebs which may have caused tracking Corroded Neutral connection in pole junction box | Minor shock | 23/05/2018 9:37 |  |  | 10069 | Residential |  | 20180627SPN_04 | Infrastructure (customer connection) | -38.6752 | 145.7888 | 1 | AusNet Services Distribution | Report | 12512 | 0.0053924 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3956 | Venus Bay | Connection
Fault crew dispatched to investigate | 250 MAIN STREET, LILYDALE VIC 3140 | 1006146 |  |  |  | Defective component |  |  |  | IMS 234128 - Report of fire from MFB. Fault crew arrived to find bad IP connection on LV ABC mains but no evidence of ground fire | Conductor (ABC) | 0 | 0 | 0 |  | LDL12 | Fault crew attended to find faulty/failed IPC connection on LV ABC mains | Other electricity related | 26/06/2018 13:00 | 1 | Negligible: no ground fire | 10073 | Commercial |  | 20180628SPN_02 | Infrastructure (network-based) | -37.758 | 145.3519 | 2 | AusNet Services Distribution | Report | 12933 | 0.023921 | Low voltage AC (<1kV) | Moorabbin Airport | 3140 | Lilydale | Connection
Crew to repair damaged cable and restore supply | 55 TANNERY HEIGHTS DRIVE, MANDURANG VIC 3551 | 33031856 | Working too close to underground cables | [5 empty] | 1 | Customer rang to report cable dug up with auger on excavator. Crew attended and found the LV U/G cable running to customer property from S/S to a pit on the property boundary had been struck and damaged There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BET007 | Excavation work | Loss of supply;No Go Zone (contact) | 43106.3688 |  |  | 10078 |  |  | 20180629PWA_05 | Infrastructure (network-based) | -36.8095 | 144.3199 | 1 | Powercor | Report | 12523 | 0.029678 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Mandurang | Dug up
Crew isolated supply and issued an access permit to complete repairs. | 40 BARRINGTON LANE, SUNBURY VIC 3429 |  | Vehicle | [5 empty] | 1 | A car hit distribution substation pole causing it to snap at the base resulting in the high voltage conductors falling to the ground. Jemena ref tbl# 166000 | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  |  | Vehicle impact to pole | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43107.0819 |  |  | 10081 | Residential |  | 20180701JEM_01 | Infrastructure (network-based) | -37.5872 | 144.6938 | 1 | Jemena | Report | 12528 | 0.015211 | 22kV AC | Melbourne Airport | 3429 | Sunbury | Vehicle
Powercor crew attended and repaired conductor crossing Mason street and repaired ruptured bridge in New street South Kingsville | 181 MASON STREET, NEWPORT VIC 3015 | 30112075 | Vehicle | [5 empty] | 1 | Powercor received reports of dim lights in the Newport area. The attending crew found that a bridging connection had ruptured due to a high load contacting a Jemena service resulting in the service contacting the Powercor HV line above it. There was no HVI damage to powercor customers however it is believed some HVI damage may have occurred to customers on the Jemena LV network | Conductor (bare) | 0 | 0 | 0 |  | BLT022 | High vehicle or load contacted overhead line/s | Loss of supply;Damage to network assets | 28/05/2018 13:59 |  |  | 10083 | Roadway |  | 20180703PWA_01 | Infrastructure (network-based) | -37.841 | 144.8675 | 1 | Powercor | Report | 12533 | 0.023171 | 22kV AC | Laverton Raaf | 3015 | Newport | Vehicle
On arrival crew isolated supply and replaced crossarm | 64 COBURNS ROAD, MELTON SOUTH VIC 3338 | 30103173 |  |  |  | Leakage |  |  |  | Pole fire found at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MLN013 | Excessive leakage current | Pole-top fire | 20/06/2018 16:44 | 1 | Negligible: no ground fire | 10084 | Roadway |  | 20180704PWA_01 | Infrastructure (network-based) | -37.6964 | 144.5661 | 1 | Powercor | Report | 12535 | 0.041132 | 22kV AC | Laverton Raaf | 3338 | Melton South | Pole
Crew made safe and completed repairs | 124 BROUGHAM ROAD, MOUNT MACEDON VIC 3441 | 32043129 |  | Blown branch/vegetation |  | Rot |  |  | 1 | Customer reported wire down and grass fire at incident location and CFA attended to control 10m x 5m grass fire. Attending crew found a HV conductor had been brought down by a tree branch starting the fire. No injuries or property damage. | Conductor (bare) | 2 | 2 | 2 |  | GSB014 | Fallen vegetation | Grassfire | 43197.1611 | 1 | Small: 10 - 1000 sq.m | 10087 | Roadway |  | 20180705PWA_01 | Infrastructure (network-based) | -37.4114 | 144.5923 | 1 | Powercor | Report | 13110 | 7.5231e-05 | 22kV AC | Melbourne Airport | 3441 | Mount Macedon | Trees
On arrival crew isolated supply and carried out repairs. | 18 ISABELLA STREET, SHEPPARTON VIC 3630 | 30128742 | Misadventure | [6 empty] | Report of football damaging powerline at incident location. On arrival crew found a damaged service neutral caused by children kicking a football,. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | STN022 | Football striking service line | Loss of supply;Damage to network assets | 21/05/2018 17:48 |  |  | 10090 | Roadway |  | 20180705PWA_03 | Infrastructure (network-based) | -36.3897 | 145.4018 | 1 | Powercor | Report | 12543 | 0.022846 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 28 TYRRELL STREET, LAKE BOGA VIC 3584 | 31022577 |  |  |  | Corrosion |  | Phase to earth |  | Ms Chloe Whelan was standing in front of the Meter Enclosure when she received an electric shock as she made simultaneously contact with her hand on the metallic metal Meter Box and her feet in wet Boots whilst standing on the wet ground. | Service conductor | 2 | 2 | 2 |  | KGT004 | Corroded connection | Minor shock | 26/05/2018 18:00 |  |  | 10093 | Residential |  | 20180706PWA_03 | Infrastructure (network-based) | -35.462 | 143.6269 | 1 | Powercor | Report | 12548 | 0.0082905 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3584 | Lake Boga | Connection
On arrival crew isolated supply and commenced repairs. | 63 WOLLAHRA RISE, WYNDHAM VALE VIC 3024 | 32162926 | Working too close to overhead lines | [5 empty] | 1 | Excavator struck and broke HV conductors. Force of contact caused pole failure. There was no fire, no reported injuries or thirdparty property damage. | Conductor (bare);Pole (wood) | 2 | 1 | 2 |  | WBE014 | Excavator struck line. | No Go Zone (contact);Damage to network assets | 43258.6104 |  |  | 10096 | Roadway |  | 20180709PWA_01 | Infrastructure (network-based) | -37.8732 | 144.6224 | 1 | Powercor | Report | 12551 | 0.041355 | 22kV AC | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
On arrival crew carried out repairs. | HACKETTS ROAD, POINT COOK VIC 3030 | 30109201 | Copper theft | [6 empty] | Employee reported earth cable stolen from Hackett Dunning Nth pole 03S, There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | WBE013 | Copper theft | Damage to network assets | 43106.4861 |  |  | 10102 |  |  | 20180709PWA_03 | Infrastructure (network-based) | -37.879 | 144.719 | 1 | Powercor | Report | 12559 | 0.017149 | Earthing cable | Laverton Raaf | 3030 | Point Cook | Other
The crew were advised to take photos for the new BSP connection and provide them to their supervisor. Photos and CES are attached. The Citipower/Powercor meter was removed and an investigation revealed that it was last connected at 28 Helston Street, Balwyn North and ceased communicating on 17/05/2018. | 49 SHADY GROVE, NUNAWADING VIC 3131 |  | Unauthorised work | [5 empty] | 2 | Crew had the task of connecting a new Builders Supply Pole (BSP) at 49 Shady Grove, Nunawading. Whilst completing their work Job Safety Assessment they identified a Citipower/Powercor single phase meter was still in place within the meter enclosure and contacted their supervisor. They had concerns that a CES was issued for the BSP with the meter remaining in place. | Smart meter | 0 | 0 | 0 |  |  | Relocation of a BSP with another Distributors meter remaining installed in the meter enclosure. A CES had been provided. | Damage to network assets | 25/06/2018 9:30 |  |  | 10097 | Construction |  | 20180709UTD_01 | Infrastructure (network-based) | -37.8297 | 145.1771 | 1 | United Energy Distribution | Report | 12552 | 0.02085 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Nunawading | Other
The attending crew made the site safe. No other customers were affected. | 19 STATION STREET, MADDINGLEY VIC 3340 | 30112887 | Copper theft | [6 empty] | A Powercor crew attended the site and found: - the pit appeared to have been forcibly removed from the ground, - the Powercor 4c x16mm LV copper underground service cable was no longer present, - the customerâ€™s newly installed LV mains had been ripped out of the pit and ground causing some damage to them. - Powercor LV conduit and FOLCB at the service cable head at pole LIS 105835 was still present. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | BMH004 | Vandalism | Damage to network assets | 43288.3646 |  |  | 10120 | Roadway |  | 20180711PWA_02 | Infrastructure (network-based) | -37.6876 | 144.4411 | 1 | Powercor | Report | 12581 | 0.027208 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 4 Volts no load to 40 Volts maximum load. The incident was caused by a combination of a loose and corroded termination of the 2 wire grey twisted service neutral conductor at the neutral terminal of the customers FOLCB at the POA, and a loose termination of the service neutral at the take-off box on the PAL pole. | 1 TAROONGA COURT, NORLANE VIC 3214 | 30062857 |  |  |  | Corrosion |  | Phase to earth |  | Luigi was standing at the kitchen sink washing dishes, when he felt a slight tingle to his right hand adjusting the tap, with his left hand in the water. | Service conductor | 2 | 2 | 2 |  | CRO022 | Corroded connections | Minor shock | 43257.7917 |  |  | 10122 | Residential |  | 20180711PWA_04 | Infrastructure (customer connection) | -38.097 | 144.3483 | 1 | Powercor | Report | 12588 | 0.029249 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Connection
On arrival crew isolated supply and carried put repairs. | 303 FLEMINGTON ROAD, NORTH MELBOURNE VIC 3051 | 30199870 |  |  |  | Overheated connection |  |  |  | MFB reported Street lighting on fire at the incident location. On arrival the crew found that a public lighting circuit board faulted and may have caused some sparking. There was no fire, no reported injuries or third party property damage | Public lighting | 2 | 2 | 2 |  | LS025 | Overheated connections | Melting or smoking only | 43227.3243 |  |  | 10125 | Roadway |  | 20180712PWA_02 | Infrastructure (network-based) | -37.7915 | 144.9449 | 1 | CitiPower | Report | 12595 | 0.037711 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Connection
The site was made safe and the HV earth was replaced. | BULBAN ROAD, WERRIBEE VIC 3030 | 32177125 | Copper theft | [6 empty] | A Powercor contractor reported the HV earth was stolen from the incident location. On arrival the crew found that approx. 1m of High Voltage earth at â€œBulban Rd 19â€ S/Stn had been stolen. There were no reported injuries or other third party damage. | Earth/earthing | 2 | 2 | 2 |  | WBE023 | Copper theft | Damage to network assets | 14/06/2018 13:42 |  |  | 10138 | Roadway |  | 20180713PWA_05 | Infrastructure (network-based) | -37.9186 | 144.6102 | 1 | Powercor | Report | 12610 | 0.026064 | Earthing cable | Laverton Raaf | 3030 | Werribee | Other
On arrival crew isolated supply and carried out repairs | 22 MIAMI STREET, HAWTHORN EAST VIC 3123 | 30201531 | Vandalism | [6 empty] | Resident at 22 Miami St Hawthorn East, Miss Mun Kwan (0410 943 788) reported a cracked pole outside her property. She was concerned it may fall. On arrival it was found the pole was still in good condition however the underground service cable was removed from the pole and a couple of metres away from the pole. There was no fire, no injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | CL011 | Vandalism | Damage to network assets | 19/06/2018 2:59 |  |  | 10151 | Roadway |  | 20180716PWA_07 | Infrastructure (network-based) | -37.8347 | 145.0453 | 1 | CitiPower | Report | 12627 | 0.034985 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Other
LEI attended to make safe and investigate Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, and the point of contact revealed poorly insulated connections within the PIT causing a tracking voltage along the wet supply cables, recording a voltage of 137 Volts. Fault crew organised to re-terminate connections in pit and LEI to re-test following the rectification works to verify the shock risk has been removed. | 7 FLEMING COURT, RESEARCH VIC 3095 | LIS 5809569 |  |  |  | Leakage;Not built/maintained to design |  | Phase to earth | 2 | IMS 234432 - REC reported tingle from pit | Services pit | 0 | 0 | 0 |  | ELM33 | REC received electric shock while kneeling on the ground beside the Electrical Supply PIT while simultaneously making contact with his hand to the damp / wet insulation of a supply cable within the PIT. There are a number of connections in the pit that have heat shrink covering the connections, the inside of the pit is very wet. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, and the point of contact revealed poorly insulated connections within the PIT causing a tracking voltage along the wet supply cables, recording a voltage of 137 Volts. It appears that voltages are originating at the heat shrunk joints of the cables and tracking throughout the service pit due to the water and dampness within the pit, causing current to flow from the cable connection, along the wet heat shrunk joint, to the outside of the damp supply cables Fault crew organised to re-terminate connections in pit and LEI to re-test following the rectification works to verify the shock risk has been removed. | Minor shock | 14/07/2018 12:36 |  |  | 10149 | Residential |  | 20180716SPN_04 | Infrastructure (network-based) | -37.7076 | 145.1878 | 1 | AusNet Services Distribution | Report | 12860 | 0.030759 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Research | Connection
A LEI and faults truck was dispatched and commenced an investigation. The installation is supplied by an underground service to a sole use pit from pole LIS No. 3302321 and observed the main switch had been turned of by the occupants prior to their arrival and initial testing had the NST failing (neutral impedance). The installation was isolated at the meter panel fuses and the fault crew checked connections and found a number of faulty connections in the neutral and active conductors to the LV reticulation including the pole mounted fused mains junction boxes. All connections were re-terminated and supply was restored after a NST, Network Analyses and voltage testing confirmed the fault had been rectified. Socket outlets inside the customer premises were also tested and showed to be operating correctly. The customer had a number of appliances that were not working as a result of the fault including the floor heating that was disconnected by the LEI. A defect notice was issued to the customer to engage a REC to rectify any faults. | 5 HEARLE AVENUE, ASPENDALE VIC 3195 | 33002321 |  | Prone to salt deposition |  | Corrosion;Electrical breakdown |  | Phase to earth | 2 | AMI meter communicated sustained voltages over 270v reported on meter number 01355749 with a maximum of 419.39 measured. A trouble order was auto-created that advised..."Please check all neutral connections between the meter and upstream pole/pillar/pit for any bad connections or corrosion". The United Energy Network Intelligence Manager advised the fault was detected and issued within 10 minutes of the fault occurring in the field and the customer received an electric shock 15 minutes later. One of the occupants noticed smoke coming from some of the charging appliances that were plugged in to the various socket outlets. Both the people involved felt a minor tingle from the meter panel enclosure when they went to isolate the installation at the main switch. | Services cable;Connection box | 0 | 0 | 0 |  |  | The pole is located approximately 50m from Port Phillip Bay and salt borne contaminants would have contributed to the connections severely corroding. | Minor shock | 43380.6042 |  |  | 10156 | Residential |  | 20180716UTD_05 | Infrastructure (network-based) | -38.0148 | 145.0914 | 1 | United Energy Distribution | Report | 12635 | 0.024904 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Aspendale | Connection
On arrival crew isolated supply and carried out repairs. | 13 STEVENSTON STREET, DEER PARK VIC 3023 | 30108310 | Vehicle | [5 empty] | 1 | Customer reported loss of power. On arrival, the crew found that a large vehicle had contacted our service assets and 3rd party assets and left the scene, This caused LV Xarm to snap off the king bolt and cause the neutral and white conductors to make contact with the Xarm straps. There were no reported shock, injuries and fire as a result of this incident. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | SU021 | Unknown vehicle stuck services | Loss of supply;Damage to network assets | 27/06/2018 6:00 |  |  | 10166 |  |  | 20180717PWA_08 | Infrastructure (network-based) | -37.7603 | 144.7665 | 1 | Powercor | Report | 12645 | 0.039523 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | ELGAR ROAD, BOX HILL NORTH VIC 3129 | 7028514 | Vehicle |  |  | HV injection |  |  | 1 | At 0347hrs on 15/07/2018, 22kV feeder DC 05 circuit breaker reclosed to lockout affecting 2838 customers. A vehicle struck a HV/LV tee-off pole (LIS number 7028514) located on the corner of Elgar Road and Peter Street that caused significant damage. A HV conductor made brief contact with the LV conductors below when the pole and cross arm broke and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Peter-Elgar" substation. The LEI confirmed a high voltage injection occurred (BWD 1811) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | DC 05 | Car contacted pole that caused a high voltage injection. | HV injection;Loss of supply | 15/07/2018 3:47 |  |  | 10167 | Roadway |  | 20180717UTD_03 | Infrastructure (network-based) | -37.7993 | 145.1183 | 1 | United Energy Distribution | Report | 12646 | 0.0057292 | Low voltage AC (<1kV) | Moorabbin Airport | 3129 | Box Hill North | Vehicle
On arrival crew confirmed isolation. Arrangements made to remove transformer. | 258 BALLARAT-DAYLESFORD ROAD, GONG GONG VIC 3352 | 41067476 | Vandalism;Copper theft | [6 empty] | Report received from Powercor contractor of vandalism and oil spill at the incident location. On inspection it was found all the HV and LV mains plus all customer mains had been cut and removed. The TX lid had been removed and oil spread over a 10m/sq. area. The site is vacant but was an old saw mill. Supply was disconnected on 2.10.2017 for non-payment. Gas SW at CHP 40 Gong S/L is open. There was no fire or reported injuries. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | BAN015 | Vandalism, copper theft | Damage to network assets | 29/06/2018 11:19 |  |  | 10181 | Industrial |  | 20180719PWA_04 | Infrastructure (network-based) | -37.5526 | 143.9306 | 1 | Powercor | Report | 12670 | 0.010373 | Not applicable | Ballarat Aerodrome | 3352 | Gong Gong | Other
Supply was isolated by the faults crew and the FOLCB was replaced. | 72 DANDENONG ROAD W, FRANKSTON VIC 3199 | 8818998 |  |  |  | Overheated connection |  |  | 2 | Caller reports the power pole is on fire half way up the pole. A fire occurred at a three phase FOLCB at concrete pole No. LIS 8818998 and no ground fire started. | Connection box | 0 | 0 | 0 |  |  | The cause was a probable loose connection that subsequently overheated. | Pole-top fire | 25/06/2018 13:09 | 1 | Negligible: no ground fire | 10189 | Residential |  | 20180720UTD_02 | Infrastructure (network-based) | -38.136 | 145.1285 | 1 | United Energy Distribution | Report | 13077 | 0.015264 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Section of HV line isolated and conductors reinstated. | 117-123 BANKSIA STREET, EAGLEMONT VIC 3084 |  |  | Blown branch/vegetation |  |  |  |  | 1 | Large tree knocked over by wind brought down 2 Bays (Lines) of HV conductors | Conductor (bare) | 0 | 0 | 0 |  | HB22 | Vegetation: Trees Incident | Loss of supply | 23/07/2018 19:37 |  |  | 10200 |  |  | 20180723JEM_01 | Infrastructure (network-based) | -37.7584 | 145.0555 | 1 | Jemena | Report | 12870 | 0.034315 | 11kV AC | Essendon Airport | 3084 | Eaglemont | Trees
On arrival crew isolated supply and carried out repairs | 115 MOORA ROAD, RUSHWORTH VIC 3612 | 30127332 |  |  |  | Fuse failed to eject |  |  |  | Crew attended a reported supply outage. They found the HV EDO tube had candled and fallen to the ground. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | SP014 | Corrossion | Pole-top fire | 20/07/2018 10:13 | 1 | Negligible: no ground fire | 10195 | Roadway |  | 20180723PWA_01 | Infrastructure (network-based) | -36.5812 | 145.0033 | 1 | Powercor | Report | 12687 | 0.033847 | 22kV AC | Mangalore Airport | 3612 | Rushworth | Fuse
On arrival crew isolated various supplies. Pole straightened There was no reported HVI, this was confirmed by the LEI, Miles Tobias, who attended later in the evening. Repairs completed | 129 KINGS ROAD, KINGS PARK VIC 3021 | 32172304 | Vehicle | [5 empty] | 1 | Passerby Peter advised unknown truck with excavator has brought down wires at the incident location. MFB has also reported truck has brought down power lines. Upon arrival, the Powercor Operator advised that an unknown truck/vehicle , possibly a large truck, had hit the Optus Cable running across Kings Rd into Grevillea Road., this has resulted in the Optus Catenary Flicking into the HV & LV Conductors. There was no fire, damage to various property POA's, LV pole leaning. There was suspected HVI - This was confirmed not to be the case. | Conductor (bare) | 2 | 2 | 2 |  | SA009 | Unknown vehicle | Loss of supply;Damage to network assets | 21/07/2018 12:02 |  |  | 10197 | Roadway |  | 20180723PWA_03 | Infrastructure (network-based) | -37.73 | 144.7818 | 1 | Powercor | Report | 12689 | 0.028941 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3021 | Kings Park | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the POA The attending Powercor Fault Crew re-terminated the existing O/H Service Neutral Conductor at the Pole Type Connection Box located at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. A Customer Installation Defect Notice was issued to the Department of Housing Services to replace the deteriorating Point of Attachment. | UNIT 3 25 MARGARETS LANE, WARRNAMBOOL VIC 3280 | 30236249 |  |  |  | Corrosion |  | Phase to earth |  | Client was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metallic Shower Tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | WBL008 | Corroded connection | Minor shock | 18/06/2018 0:00 |  |  | 10212 | Residential |  | 20180725PWA_06 | Infrastructure (customer connection) | -38.3894 | 142.4894 | 1 | Powercor | Report | 12705 | 0.0081921 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a high impedance neutral conductor within the existing service cable to property. Fault truck removed and replaced service cable CTA re-tested property, all required VESI tests passed | 8 PARKHILL ROAD, KEW VIC 3101 | 30180631 |  |  |  | Corrosion |  | Phase to earth |  | Adisak was washing dishes when he received an electric shock. Adisak made simultaneous contact between the metallic tap with one hand and the metallic kitchen bench with his other hand. | Service conductor | 2 | 2 | 2 |  | Q006 | Corroded service | Minor shock | 43319.75 |  |  | 10221 | Residential |  | 20180726PWA_03 | Infrastructure (network-based) | -37.8038 | 145.0392 | 1 | CitiPower | Report | 12716 | 0.011647 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | OH Cable
Transformer and HV fuses removed, site made safe. | UNIT 2 2A BEACHLEY STREET, BRAYBROOK VIC 3019 | 10197844 | Copper theft | [5 empty] | 2 | Copper theft of isolated (HV/LV) pole type substation. (Location is closest street address, see latitude and longitude for actual pole location) | Outdoor | 0 | 1 | 0 |  |  | Copper theft to isolated pole type substation. | Damage to network assets | 30/07/2018 14:36 |  |  | 10237 | Public space |  | 20180730JEM_01 | Infrastructure (network-based) | -37.7952 | 144.8487 | 1 | Jemena | Report | 12733 | 0.00018866 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
Supply was isolated by HV operator and a work party conducted repairs and replacement. | 20 RAILWAY PLACE, WILLIAMSTOWN VIC 3016 |  |  | Animal |  |  |  |  | 2 | Bare conductor on ground due to possum coming into contact with conductors near HV switch. | Conductor (bare) | 0 | 0 | 0 |  |  | Animal Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/07/2018 6:08 |  |  | 10242 | Residential |  | 20180731JEM_02 | Infrastructure (network-based) | -37.8662 | 144.9014 | 1 | Jemena | Report | 12769 | 0.027546 | 22kV AC | Essendon Airport | 3016 | Williamstown | Animal
On arrival crew isolated supply and carried out repairs | 338-340 MANSFIELD STREET, THORNBURY VIC 3071 | 30194669 | Working too close to underground cables | [5 empty] | 1 | Underground faults crew attended a fault and determined that the fault location lay beneath recently excavated soil at the incident location. On excavating the faulted cable it became clear that a third party was responsible for the damage. A new water main had been installed in the months before before by Yarra Valley Water and their contractor DKM Plumbing are alleged to have caused the damage. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | FF097 | Destructive digging methods. | Loss of supply;No Go Zone (contact);Damage to network assets | 24/07/2018 11:20 |  |  | 10246 | Roadway |  | 20180801PWA_01 | Infrastructure (network-based) | -37.7593 | 145.0278 | 1 | CitiPower | Report | 12742 | 0.027646 | 11kV AC | Essendon Airport | 3071 | Thornbury | Dug up
On arrival crew inspected assets and arranged repairs. LEI arranged to inspect pumping site for HVI | 76A FORD ROAD, SHEPPARTON VIC 3630 | 33095226 |  | Bird |  |  |  |  | 1 | Following a reclose on SHTS-SHN No1 66kv line its was found that bird flashover had occurred on Pole 19. The resultant flashover is suspected to have caused a HVI to Pumping site fed from this substation pole. There was no fire, no reported injuries. | Conductor (bare);Connection box;Pole (concrete) | 2 | 2 | 2 |  | SHTS-SHN # 1 | Bird Incident | HV injection;Damage to network assets | 43139.6507 |  |  | 10253 | Roadway |  | 20180803PWA_01 | Infrastructure (network-based) | -36.3478 | 145.4109 | 1 | Powercor | Report | 12752 | 0.0053935 | Low voltage AC (<1kV);66kV AC | Shepparton Airport | 3630 | Shepparton | Animal
Crew replaced stolen copper cable. | 55 CUMMINGS ROAD, MADDINGLEY VIC 3340 | 33071241 | Copper theft | [6 empty] | Electrix inspector reports copper earth cables missing from ACR P1A Balliang S/L. No shocks, 3rd party damage or ground fire starts. | Earth/earthing | 2 | 2 | 2 |  | BMH006 | Copper theft | Damage to network assets | 27/07/2018 11:40 |  |  | 10258 | Roadway |  | 20180803PWA_03 | Infrastructure (network-based) | -37.7006 | 144.4496 | 1 | Powercor | Report | 12757 | 0.0045949 | Earthing cable | Avalon Airport | 3340 | Maddingley | Other
On arrival site secured, repairs arranged | 62 BUCKHURST STREET, SOUTH MELBOURNE VIC 3205 | 30167753 | Copper theft | [5 empty] | 2 | A company employee reported a vandalized indoor substation at the incident location.Â On arrival, CitiPower fault crew found that the substation had been vandalized and copper cable cut away. The door was also damaged. | Conductor (insulated);Copper;Indoor | 0 | 0 | 0 |  | MG019 | interference - copper theft | Loss of supply;Damage to network assets | 43138.1583 |  |  | 10263 | Commercial |  | 20180806PWA_02 | Infrastructure (network-based) | -37.8302 | 144.9512 | 1 | CitiPower | Report | 12765 | 0.026051 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Other
Fault crew sent to investigate and rectify The attending Fault crew were in the process of repairing damaged LV earth from the possum which caused a short circuit from conductor to steel X-arm on a concrete Substation pole when LEI arrived at site. Attending LEI inspected 3 affected properties along Croydon Rd Warrandyte South and found no evidence of HV injection. Control Room notified customers OK to return to supply upon completion of repairs. | 34 CROYDON ROAD, CROYDON VIC 3136 | LIS 1203025 |  | Animal |  |  |  | Phase to earth |  | IMS 234762 - grass fire (2msq) reported in vicinity of AusNet Services assets | Conductor (bare);Crossarm (steel) | 2 | 2 | 2 |  | RWN31 | Animal Incident | Grassfire | 43228.8417 | 1 | Localised: less than 10 sq.m | 10261 |  |  | 20180806SPN_01 | Infrastructure (network-based) | -37.7661 | 145.2396 | 1 | AusNet Services Distribution | Report | 17790 | 0.0041944 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3136 | Croydon | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Service Conductor at its terminations The attending Powercor Fault Crew replaced the existing O/H Two Wire Grey Twisted Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 7 WINTER STREET, BELMONT VIC 3216 | 31013592 |  |  |  | Corrosion |  | Phase to earth |  | Mr Steven Reed was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his right hand on the metallic water tap and his bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GLE012 | Corroded service connection | Minor shock | 28/07/2018 8:00 |  |  | 10268 | Residential |  | 20180807PWA_02 | Infrastructure (customer connection) | -38.1898 | 144.347 | 1 | Powercor | Report | 12771 | 0.034917 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
SIte Made safe | 247 ST ALBANS ROAD, SUNSHINE NORTH VIC 3020 | Pa0063937 | Vandalism;Copper theft | [6 empty] | A member of the public reported a break in to an Indoor Substation, â€œSt Albans 247- Gilmourâ€ at a former City West Water Regional Office & depot at No. 247 St. Albans Rd. Sunshine North. The front metal wall of the customerâ€™s electrical building torn off, presumably by a vehicle. The Powercor Indoor substation room fully exposed but devoid of 500kVA transformer and all internal LV plant There was no fire, no reported injuries | Indoor | 2 | 1 | 2 |  | SSE011 | Vandalism, Copper theft | Damage to network assets | 43139.7125 |  |  | 10271 | Commercial |  | 20180808PWA_02 | Infrastructure (network-based) | -37.7667 | 144.8188 | 1 | Powercor | Report | 17364 | 0.011155 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Other
Fault crew sent to investigate. Fault crew isolated, made safe and carried out repairs. | 25 ABBOTT STREET, INVERLOCH VIC 3996 | LIS 2809995 |  |  |  | Defective component |  |  | 2 | IMS 234719 - report received of melted LV connection. Melted insulation found on the ground in the vicinity of the pole only and no fire observed and no evidence of fire. | Connection box;Dropper/bridge | 0 | 0 | 0 |  | WGI34 | Fault crew found 2 x LV leads/boxes with melted insulation and LV open wire damaged. White phase conductor had broken at IPC and conductor had to be repaired. White phase IPC replaced and 2x new LV fuse boxes/leads put up on the pole. No fire observed and no evidence of fire. Only melted insulation found on the ground in the vicinity of the pole | Melting or smoking only | 43139.034 |  |  | 10276 |  |  | 20180808SPN_05 | Infrastructure (network-based) | -38.6349 | 145.7188 | 1 | AusNet Services Distribution | Report | 13113 | 0.041488 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Connection
Fault crew and inspector dispatched to investigate. At time of visit premise was off supply with the service fuse remove and the supply neutral lifted and restrained. The property owner advised that the plumber who was engaged to repair the water service noticed a small spark when he attached his bonder. The customer rang an REC who did some checks and then rang AusNet Faults. The fault crew arrived and replaced the neutral IPC on the overhead ABC on pole LIS 1306643 and left the installation set up for testing prior to LEI attendance and, as a result, no reference voltages or current flows were available prior to repairs. NST test carried out at the Point Of Attachment and main switchboard both passed. Voltage tests between an independent earth and various points of the electrical installation also passed. It would appear that the work performed by the fault crew eliminated the problem. | 17 COLBY DRIVE, BELGRAVE VIC 3160 | LIS 1306644 |  |  |  | Neutral fault;Defective component |  | Phase to earth | 2 | IMS 234711 - REC reported electric shock | Connector/termination | 0 | 0 | 0 |  | BGE23 | The attending LEI performed all testing as would be done for a new connection plus additional testing of the plumbing and earthing system. The installation passed an NST test performed by the attending LEI. Installation left ON supply. fault crew attended prior to LEI arriving and replaced the neutral IPC on the overhead ABC on pole LIS 1306643. No fault could be identified and the work carried out by the fault crew previously appears to have rectified any fault that may have been present | Minor shock | 43108.4069 |  |  | 10279 |  |  | 20180809SPN_01 | Infrastructure (network-based) | -37.9218 | 145.3533 | 2 | AusNet Services Distribution | Report | 13112 | 0.0086609 | Low voltage AC (<1kV) | Moorabbin Airport | 3160 | Belgrave | Connection
10/04/2018 - The Victoria Police were in attendance for a drug bust and requested that a faults truck attend as an electricity bypass was suspected. A faults crew attended and contacted Formway Specialised Metering as an illegal bypass was suspected. Supply was isolated at pole No. LIS 7022727 and a defect notice left at the property. 08/08/2018 - REC Danny Fong LIC/REC No.12192 provided CES No. 508326404 advising the defect had been repaired and the CES was at the main switchboard. A faults truck attended and identified there was incorrect color coding for the wiring and it appeared the bypass remained in the roof and they requested that a LEI attend to investigate further. A LEI attended and confirmed the previous illegal bypass had not been removed as there was no continuity between the meter and the POA. Supply was isolated once again at pole number 7022727 and the customer left off supply. | 453 BURWOOD HIGHWAY, VERMONT SOUTH VIC 3133 | 7022727 | Misadventure |  |  | Fault on customer installation |  |  | 2 | Illegal bypass was identified and supply was isolated. A CES was received stating the bypass had been removed but the crew were unsure and requested a LEI attend. It was confirmed the bypass had not been removed and was still in place. | Customer installation | 0 | 0 | 0 |  |  | Illegal bypass and theft of electricity. Concerns with CES being provided by REC with defects still in place. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43320.4792 |  |  | 10282 | Residential |  | 20180809UTD_02 | Infrastructure (network-based) | -37.8555 | 145.1777 | 1 | United Energy Distribution | Report | 13120 | 0.012133 | Low voltage AC (<1kV) | Moorabbin Airport | 3133 | Vermont South | Other
Supply isolated for inspector to conduct tests. Defective neutral screened service cable was replaced. Retest to confirm safety. | 89 ESPLANADE, WILLIAMSTOWN VIC 3016 |  |  |  |  | Neutral fault |  |  | 2 | Resident received electric shock from taps while washing dishes. Additional information can be found in TechSafe report attached in '7.Notes & Findings' | Neutral screen | 2 | 2 | 2 |  |  | Neutral conductor was broken at termination on pole | Minor shock | 43381.4389 |  |  | 10292 |  |  | 20180810JEM_01 | Infrastructure (network-based) | -37.8666 | 144.8908 | 1 | Jemena | Report | 12804 | 0.022214 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown | Connection
Crews attended to ensure the site was safe. | 31 WILLSMERE ROAD, KEW VIC 3101 | 30176797 | Copper theft | [6 empty] | A builder reported that the UG cable from the pit to the pole at the incident location had been stolen. The cable was installed but not energized, ready for an upcoming new connection. Nearby building workers reported seeing a truck pull up to the pole in the preceding days, they said that men got out in high-visibility vests, and had orange flashing lights on their vehicle, these men then removed the UG cable and drove away, no Registration number was obtained. There were no injuries or other damage reported. | Services cable | 2 | 2 | 2 |  | Q002 | Copper theft | Damage to network assets | 43289.4403 |  |  | 10288 | Roadway |  | 20180810PWA_02 | Infrastructure (network-based) | -37.7978 | 145.0328 | 1 | CitiPower | Report | 12799 | 0.0015336 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Other
Fault crew dispatched to investigate and make safe. Attended street to access for any signs HV injection and identified a tree had fallen into HV conductors on the roadside next to no 7 Catherine Way, Belgrave. Having assessed damage to a number of switchboards, LEI proceeded to isolate properties to reconnect LV supply at sub. LEI carried out tests and connected properties after repairs were completed. Property damaged by fire was isolated from the network. Repairs carried out to overhead cabling and damaged services to properties and electrical meters replaced where required. | 18 LAURIE AVENUE, TECOMA VIC 3160 | LIS 1307802 |  | Fallen |  |  |  | Phase to earth |  | IMS 234828 - Tree has fallen into and brought down HV overhead conductors which clashed with LV conductors resulting in HV injection | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | HV injection;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43381.4993 |  |  | 10294 | Residential |  | 20180813SPN_01 | Infrastructure (network-based) | -37.9101 | 145.3432 | 1 | AusNet Services Distribution | Report | 12809 | 0.012472 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
On arrival crew isolated supply and carried out repairs LEI investigated HVI damage | 19 MAPLE STREET, SHEPPARTON VIC 3630 | 33090632 |  | Bird |  |  |  |  | 1 | A Magpie caused a flashover on a termination substation pole at the incident location. The resultant fault current cause the helical termination to fail allowing the red phase HV cable to fall into the LV circuit below. There was reported HVI damage to around 26 premises. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | SHN014 | Bird Incident | HV injection;Loss of supply;Damage to network assets | 13/08/2018 11:16 |  |  | 10302 |  |  | 20180815PWA_01 | Infrastructure (network-based) | -36.3654 | 145.4184 | 1 | Powercor | Report | 12871 | 0.028572 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3630 | Shepparton | Animal
The attending Powercor Fault Crew checked the condition of all conductors and disconnected and remade all terminations between the distribution system and the Point of Attachment (POA) of the installation. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an inherent voltage in the network neutral supply system likely caused by voltage drop on the 800M LV Street Circuit, resulting in a high impedance in the neutral reticulation system. A final NST test was carried out on the installation by the attending LEI which confirmed a Pass result. The Installation was left ON supply. The Customer was advised to arrange the services of an REC to bond the metallic waste water system to the installation earthing system by an equipotential earthing bonding conductor to eliminate any risk of a potential difference between conductive building mediums. | 17-21 MURPHYS LANE, MURRAYVILLE VIC 3512 | 32151143 |  |  |  | Out of balance load |  | Phase to earth |  | Mr Wayne Hand was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower tap and his bare feet while standing on the wet shower base, which was set into a timber floor with an old metal waste water outlet pipe. | Conductor (ABC);Customer installation | 2 | 2 | 2 |  | OYN001 | Voltage drop on the 800M LV Street Circuit | Minor shock | 43351.8542 |  |  | 10314 | Residential |  | 20180817PWA_02 | Infrastructure (network-based) | -35.268 | 141.1824 | 1 | Powercor | Report | 12889 | 0.0049896 | Low voltage AC (<1kV) | Mildura Airport | 3512 | Murrayville | Conductor
Site made safe. Installed new earth and cover guard. | CRANWELL STREET, BRAYBROOK VIC 3019 |  | Copper theft | [5 empty] | 2 | Copper theft of cabling running down side of pole towards substation. | Copper;Earth/earthing | 2 | 2 | 2 |  |  | Person unknown had stolen earth off the side of a pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 18/08/2018 14:03 |  |  | 10315 |  |  | 20180818JEM_01 | Infrastructure (network-based) | -37.7788 | 144.8653 | 1 | Jemena | Report | 13187 | 0.025954 | Earthing cable | Essendon Airport | 3019 | Braybrook | Other
On arrival crew carried out repairs | SHOWGROUNDS CARAVAN PARK, 331 KOROIT STREET, WARRNAMBOOL VIC 3280 | 30283657 |  | Bird |  |  |  |  | 1 | CFA reports a pole fire at the incident location. The crew identified a pole fire had occurred at switch pole 19B The site was safe and no ground fire, injuries or shocks were reported. | Pole (wood);Crossarm (steel) | 2 | 2 | 2 |  | WBL004 | Bird Incident | Pole-top fire | 43198.6632 | 1 | Negligible: no ground fire | 10317 |  |  | 20180820PWA_02 | Infrastructure (network-based) | -38.3769 | 142.4689 | 1 | Powercor | Report | 12893 | 0.01219 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
On arrival crew isolated supply and carried out repairs. | 39 CROOK COURT, BALLAN VIC 3342 | 33074144 | Working too close to underground cables | [6 empty] | Mr Troy Smith reported that a worker has hit an underground cable with an excavator outside 39 Crook Court Ballan. The cable supplies 38 Crook Court and resident is now complaining of voltage issues. On arrival the crew found that a excavator had contacted an underground LV service cable causing damage to the cable. There were no civil workers on site when the crew arrived . There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BMH003 | Excavation work | Loss of supply;No Go Zone (contact) | 16/08/2018 11:40 |  |  | 10321 |  |  | 20180820PWA_04 | Infrastructure (network-based) | -37.603 | 144.214 | 1 | Powercor | Report | 12899 | 0.037814 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Dug up
Fault crew dispatched to investigate and make safe. Isolated service, Customer advised REC required to repair damaged POA | 221 MYERS CREEK ROAD, HEALESVILLE VIC 3777 | LIS1410037 |  | Blown branch/vegetation |  |  |  | Phase to earth |  | IMS 234946 - customer reported receiving tingles from kitchen sink. | Service conductor | 0 | 0 | 0 |  | WYK24 | Vegetation: Trees Incident | Minor shock | 19/08/2018 20:59 |  |  | 10323 | Residential |  | 20180820SPN_04 | Infrastructure (network-based) | -37.6251 | 145.5164 | 1 | AusNet Services Distribution | Report | 12903 | 0.0023958 | Low voltage AC (<1kV) | Moorabbin Airport | 3777 | Healesville | Trees
Fault crew dispatched to make safe and Investigate. Fire Brigade in Attendance to extinguish fire and Fault crew carried out repairs | 50 CLARK ROAD, HEDLEY VIC 3967 | LIS2608426 and LIS573608 |  | Fallen |  |  |  | Phase to earth | 2 | IMS 234867 - Fallen tree and brought down HV conductor. 20mx15m grassfire observed in the vacinity of downed assets near pole LIS2604824 100mx10m grassfire observed in the vacinity of downed assets near poles LIS2608426 and LIS573608 | Conductor (bare) | 0 | 0 | 0 |  | FTR12 | Vegetation: Trees Incident | Grassfire | 15/08/2018 2:00 | 1 | Medium: 1000 sq.m - 10 ha | 10326 |  |  | 20180820SPN_06 | Infrastructure (network-based) | -38.6446 | 146.4919 | 1 | AusNet Services Distribution | Report | 12907 | 0.01791 | 22kV AC | Morwell (Latrobe Valley Airport) | 3967 | Hedley | Trees
Fault crew dispatched to make safe and investigate. Small ground fire extinguished and transformer isolated. Installation repaired and put back on supply | 770 OUTTRIM-LEONGATHA ROAD, OUTTRIM VIC 3951 | LIS 596635 |  |  |  | Overheated connection |  |  |  | IMS 234278 - LV fuse box melted and small fire ground fire observed | Connection box | 0 | 0 | 0 |  | LGA23 | LV fuse box melted on pole LIS 596635 (cause unknown) resulting in small ground fire in the vacinity | Other vegetation;Melting or smoking only | 43288.7889 | 1 | Localised: less than 10 sq.m | 10329 |  |  | 20180821SPN_01 | Infrastructure (network-based) | -38.5174 | 145.797 | 1 | AusNet Services Distribution | Report | 12910 | 0.00039352 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3951 | Outtrim | Fuse
On arrival crew confirmed isolations and arranged repairs. | 10 EYNESBURY ROAD, EYNESBURY VIC 3338 | 30247668 | Vandalism;Copper theft | [6 empty] | Melton City Council Employee reported Power cable on the ground , not sure if alive. On arrival crew found substation HV fuses open. There was evidence of vandalism and copper theft. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN011 | Vandalism and copper theft | Damage to network assets | 20/08/2018 11:25 |  |  | 10334 | Roadway |  | 20180822PWA_01 | Infrastructure (network-based) | -37.7713 | 144.5633 | 1 | Powercor | Report | 12916 | 0.010683 | Earthing cable | Laverton Raaf | 3338 | Eynesbury | Other
Jemena crew removed the service and meter. Confirmed with Network Connections the meter is listed as a permanent supply and meter exchange done in 2013. | 47 XAVIER STREET, OAK PARK VIC 3046 |  | Unauthorised work;Unauthorised access;Caused by REC/contractor |  |  |  | Not followed;Followed but inappropriate |  | 2 | Jemena crew attended site to abolish builder's temporary supply (BTS) and connecting overhead service. Upon arrival, crew suspected permanent meter has been relocated to a BTS pole by unauthorised persons. Suspicions were reported for investigation and confirmation. | Other meter;Connection to meter | 0 | 0 | 0 |  |  | Permanent meter has been relocated to a BTS pole by unauthorised persons. | Damage to network assets | 21/08/2018 9:42 |  |  | 10341 | Residential |  | 20180824JEM_01 | Infrastructure (network-based) | -37.7179 | 144.9183 | 1 | Jemena | Report | 12937 | 0.0048854 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Oak Park | Other
Field crew dispatched. Section isolated, made safe and repairs carried out | 206 SAVIGES ROAD, THORPDALE VIC 3835 |  |  | Fallen |  |  |  | Phase to earth |  | IMS 235039 - Tree brought wires down. Reported fire on ground approx. 25 square meters. | Conductor (bare) | 0 | 0 | 0 |  | MOE21 | Vegetation: Trees Incident | Grassfire | 15/08/2018 9:00 | 1 | Small: 10 - 1000 sq.m | 10342 | Agricultural |  | 20180827SPN_01 | Infrastructure (network-based) | -38.2805 | 146.1993 | 1 | AusNet Services Distribution | Report | 12941 | 0.021102 | 22kV AC | Morwell (Latrobe Valley Airport) | 3835 | Thorpdale | Trees
Substation was isolated to make safe. Crew replaced substation and cabling. | 860 SUMMERHILL ROAD, CRAIGIEBURN VIC 3064 |  | Vandalism;Copper theft | [5 empty] | 2 | Pole top transformer vandalised and cabling stolen | Copper;Transformer | 0 | 1 | 0 |  |  | Copper theft and vandalism by unknown person/s | Loss of supply;Damage to network assets | 28/08/2018 23:25 |  |  | 10357 | Agricultural |  | 20180828JEM_03 | Infrastructure (network-based) | -37.5698 | 144.9431 | 1 | Jemena | Report | 13013 | 0.037346 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Team of LEI's attended and assessed Transformer and damaged metering equipment replaced | ANGLESEA RECREATION CAMP, 1535 GREAT OCEAN ROAD, ANGLESEA VIC 3230 | 33041950 |  |  |  | Electrical breakdown |  |  | 1 | Customer rang to advise burnt smell coming from meter position following outage. A crew attended and found HV fuses at S/S P9 National Fitness had operated. LEI attended and found damage to premises. LV was isolated at the S/S and 45 customers left off O/N til crew could return to replace faulty TX and replace faulty meters. | Smart meter;Transformer | 0 | 0 | 0 |  | WPD021 | Internal fault in transformer | Loss of supply | 24/08/2018 16:55 |  |  | 10351 | Public space |  | 20180828PWA_03 | Infrastructure (network-based) | -38.4018 | 144.1954 | 1 | Powercor | Report | 13576 | 0.010965 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3230 | Anglesea | AF Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 15 Volts no load to 100 Volts maximum load. CTA/LEI performed NST at installation main switchboard with a fail result recorded. Fault Crew replaced the existing service with a new 2 wire ABC. Crew performed NST at the POA with a pass result recorded. CTA/LEI performed NST at installation main switchboard with a pass result recorded. Installation left ON supply. | 16 JABIRU CLOSE, OCEAN GROVE VIC 3226 |  |  |  |  | Corrosion |  | Phase to earth |  | Susen was standing at the back yard tap, when she felt a slight shock to her right hand adjusting the tap, with her left wet hand in the water flow from the hose and standing on wet soil. | Service conductor | 2 | 2 | 2 |  |  | Corroded service near POA | Minor shock | 43437.4583 |  |  | 9710 | Residential |  | 20180418PWA_02 | Infrastructure (network-based) | -38.2597 | 144.5292 | 1 | Powercor | Report | 11894 | 0.025461 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | OH Cable
On arrival crew isolated supply and carried out repairs. | BRIMBLE ROAD, LILLIMUR VIC 3420 | 32094204 |  |  |  | Leakage |  |  | 1 | Following a line outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 12.7kV pole which burnt the pole top only. Protection operated. There was no ground fire. There were no reported injuries or third party property damages. | Pole (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 16/04/2018 8:34 | 1 | Negligible: no ground fire | 9721 | Agricultural |  | 20180419PWA_02 | Infrastructure (network-based) | -36.3145 | 141.1166 | 1 | Powercor | Report | 11909 | 0.027941 | 12.7kV AC (SWER) | Horsham Aerodrome | 3420 | Lillimur | Pole
Site was made safe. On the day of the fault, Jemena faults crew repaired the HV conductor and replaced the failed connector to restore supply. On 21 April 2018, the asset performance team arranged for pole no. A067179 to be brought up to current standards i.e. replaced the five (5) shed post insulator and 22kV polymeric strains insulators with nine (9) shed post insulators and 66kV polymeric strain insulators. | 46 BARROW STREET, COBURG VIC 3058 | Pole no. A067109 |  | Bird |  |  |  | Phase to earth | 1 | High voltage conductor fell down to ground due to bird (magpie) strike across 5 shed insulator on concrete pole (footpath side) no. A067179, which is a concrete pole with steel crossarms. The bridging insulator between the top circuit and below tee-off is a five (5) shed post insulator and the strain insulators are rated at 22kV. Current JEN standards require 66kV polymeric strain insulators and nine (9) shed post insulators be used, to ensure adequate clearance between the conductor and steel crossarm. Due to the fault current from the bird contacting the live conductors, an upstream HV conductor was burnt through by a failed Ampac connector. The HV conductor on ground was the footpath phase copper conductor on Barrow Street north of Glengyle Street (between poles A123625 and A067109). Network protection had operated and the HV conductor on the ground was de-energised. Photos attached in "Notes & Findings" section | Conductor (bare);Connector/termination;Insulators | 0 | 0 | 0 |  | CS09 | Bird Incident | Loss of supply | 20/04/2018 10:43 |  |  | 9726 | Residential |  | 20180420JEM_01 | Infrastructure (network-based) | -37.7534 | 144.9711 | 1 | Jemena | Report | 12002 | 0.026574 | 22kV AC | Essendon Airport | 3058 | Coburg | Animal
CEOT dispatched a fault crew to make safe, investigate and repair. Also dispatched to the local DAO to investigate. Photos of the scene were taken by the attending DAO and attached to the IMS. No further action required. LV fuse replaced. | 1 SEMMENS STREET, TOONGABBIE VIC 3856 | 2602911 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | IMS233305. Initial report:Report of sparking power lines and a grass fire. Report of a possible contact by an excavator. Final report by attending DAO: I arrived on site at approx. 1445hrs following reports of LV wires sparking and starting a small grass fire and observed the following scene. There was a span of Open wire LV approx. 50m in length, crossing a road and a paddock. On the Western side of the LV (approx. 1.5m from, and parallel to, the conductor line) was a temporary construction fence approx. enclosing a parcel of land on which there was a sizeable area of excavation being preparation for a building foundation. Midway along this fence (provided by Super Safe Hire - tel 1300 132 731) was a sign indicating an Access Gate. There were no vehicles or plant on site, but there were excavator track marks running through this gate. These track marks extended to meet with truck wheel marks that were parallel with the line approx. 15-20m to the east. There were two burnt patches of grass, one approx. 4m x 6m and the other approx. 8m by 8m, both directly beneath the LV line and separated by approx. 15m of unburnt grass. Both burnt patches had excavator track marks and bucket scraping marks through them. I scanned the LV conductors with binoculars looking for any evidence of scorching or arcing and found no such evidence. Whilst I was on site, a member of the public approached me and claimed to live approx. 3 properties south of the incident site (at the end of the LV line). He said he heard a loud crack and some, but not all, of his power went out. He looked out at the LV line and saw it swaying. He came out to investigate, saw the fires and came down to assist with extinguishing them. He claimed that the excavator was well clear of the conductors when the operator heard a loud crack and turned to see two separate fires had started behind him. He was adamant that there was no burn marks / damage to the excavator. I didn't get the name / details of the member of the public, but he was driving a Nissan Patrol with the registration SWN071. | Conductor (bare) | 0 | 0 | 0 |  | tgn31 | Contact with overhead LVconductor by an excavator. | Grassfire;No Go Zone (contact) | 20/04/2018 13:08 | 1 | Localised: less than 10 sq.m | 9727 | Residential |  | 20180420SPN_01 | Infrastructure (network-based) | -38.0662 | 146.6233 | 1 | AusNet Services Distribution | Report | 11916 | 0.023781 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3856 | Toongabbie | Vehicle
Supply isolated and repairs commenced | 20 ROUEN STREET, HIGHTON VIC 3216 | 35241622 | Working too close to underground cables | [5 empty] | 1 | Electrical workers constructing retention basin spiked the cable with an insulated screwdriver and wearing LV gloves. No shock reported ACR operated to Lockout, and the loss of supply to approximately 2000 customers. There were no injuries or fire. | Cable | 2 | 2 | 2 |  | GLE021 | Excavation and land development works | Loss of supply;No Go Zone (contact);Damage to network assets | 24/04/2018 8:05 |  |  | 9736 | Construction |  | 20180424PWA_03 | Infrastructure (network-based) | -38.1577 | 144.3016 | 1 | Powercor | Report | 12374 | 0.018318 | 22kV AC | Avalon Airport | 3216 | Highton | Dug up
Faults have been called with a job number 163319 and a level 1 defect issued and fuse have removed. Defect notice J03019. | 4 LOCK STREET, FAWKNER VIC 3060 |  | Unauthorised work | [5 empty] | 2 | Compliance officer come across another site that appears to have non-authorised works completed. The meter is registered as a permanent connection with off peak hot water. On site is a BTS pole with a coiled up neutral screen service fed from a small pole box. BTS pole is in an unsafe state with excessive movement , stay not connected. There is NO certificate of electrical safety. Please refer to attached photos. | Neutral screen;Smart meter | 2 | 2 | 2 |  |  | Un-authorised work by unknown persons. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/04/2018 16:47 |  |  | 9754 | Residential |  | 20180427JEM_02 | Infrastructure (network-based) | -37.7108 | 144.9682 | 1 | Jemena | Report | 11951 | 0.034152 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | Other
On arrival crew isolated supply. There was damage to customers POA. Crew removed service until REC completed repairs. | 209 BOUNDARY ROAD, ROMSEY VIC 3434 | 33029537 | Working too close to overhead lines | Within clearances | [5 empty] | Customer reported that overhead service to property was brought down by a tree at the incident location. On arrival the crew found a tree which has fallen over a 3x35mm grey twisted service cable, prior to the crews arrival the energised service cable ( still connected at the substation end ) had been cleared from across the road & the tree removed. The customer â€œRobertâ€ stated that he dropped a branch in preparing the tree for removal & it was not the machinery that was responsible for the damaged to service cable. There were no reported injuries, no ground fire. | Service conductor | 2 | 2 | 2 |  | WND013 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 28/03/2018 15:06 |  |  | 9746 |  |  | 20180427PWA_01 | Infrastructure (network-based) | -37.314 | 144.7165 | 1 | Powercor | Report | 11943 | 0.036005 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3434 | Romsey | Trees
An underground faults crew attended and completed rectification work and supply was restored to the three affected properties following the completion of installation tests. | 70 WEST ROAD, LANGWARRIN SOUTH VIC 3911 | 3301177 | Vehicle |  |  | Electrical breakdown |  |  | 2 | A car has struck a pole and the CFA are in attendance. A car struck pole number LIS 3301177 located in Victoria Road, Langwarrin that damaged two LV pole to pit underground cables. The pole sustained no damage with the exception of scorch marks after the LV cables short circuited causing a small fire at the base of the pole. The damaged underground cables that supply 89, 97 and 99 Victoria Road were isolated pending an underground crew attending and completing repairs. | Services cable | 0 | 0 | 0 |  |  | A vehicle struck a pole that caused damaged to LV underground cables. | Grassfire | 43438.0014 | 1 | Localised: less than 10 sq.m | 9751 | Roadway |  | 20180427UTD_05 | Infrastructure (network-based) | -38.1939 | 145.2065 | 1 | United Energy Distribution | Report | 13058 | 0.031318 | Low voltage AC (<1kV) | Moorabbin Airport | 3911 | Langwarrin South | Vehicle
Area was isolated and repairs were made. | 51 YARRA STREET, HEIDELBERG VIC 3084 |  |  |  |  | HV injection |  |  | 1 | Truck hit Optus cables causing overhead high voltage conductors to contact low voltage conductors which resulted in high voltage injection at properties at 51 and 53 Yarra St, Heidelberg. | Conductor (bare);Service conductor | 0 | 0 | 0 |  | HB-31 | Truck contacting Optus overhead cables resulting in contact of between high voltage and low voltage conductors. | HV injection | 28/04/2018 15:12 |  |  | 9758 | Residential |  | 20180428JEM_01 | Infrastructure (network-based) | -37.7584 | 145.0659 | 1 | Jemena | Report | 11955 | 0.020419 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3084 | Heidelberg | Vehicle
On arrival crew arranged isolation from supply and removed tree. | 10 PLEASANT PLACE, GELLIBRAND VIC 3239 | 32065169 |  | Fallen | [5 empty] | Customer reported tree leaning on conductors in front of property. All conductors remained in the air. There was no report of fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | Vegetation: Trees Incident | Damage to network assets | 24/04/2018 8:37 |  |  | 9761 | Roadway |  | 20180430PWA_01 | Infrastructure (network-based) | -38.511 | 143.5411 | 1 | Powercor | Report | 11963 | 0.027433 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3239 | Gellibrand | Trees
Voltage test with an independent earth and various parts of the installation, including the MEN and metallic water pipe system and the Distribution assets, revealed a corroded neutral conductor connection located within the Pole End Junction Box. Pole box and service replaced with new 2 core Twisted Aluminium service by Powercor Faults Truck. NST Test passed at Customers Main switchboard and meter position by CTA. NST Test passed at POA by Powercor Faults Truck. | 4 MAWARRA DRIVE, DELACOMBE VIC 3356 | 30003683 |  |  |  | Corrosion |  | Phase to earth |  | Customer was showering when he received an electric shock as he made simultaneous contact between his hands on the shower taps and standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | BAS021 | Corroded connections | Minor shock | 23/03/2018 0:00 |  |  | 9768 | Roadway |  | 20180501PWA_02 | Infrastructure (network-based) | -37.5813 | 143.8222 | 1 | Powercor | Report | 11970 | 0.027226 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Delacombe | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a damaged & corroded O/H Service Neutral Screened Conductor, he attending Powercor Fault Crew replaced the damaged O/H Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 14 AIREY AVENUE, MANIFOLD HEIGHTS VIC 3218 | 30061068 |  | Council |  | Corrosion |  | Phase to earth |  | Mr Grant Baluch was in the Bathroom having a shower when he received an electric shock as he made simultaneous contact with his hand on the metal tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GLE021 | Vegetation: Trees Incident | Minor shock | 15/03/2018 17:00 |  |  | 9769 | Residential |  | 20180501PWA_03 | Infrastructure (network-based) | -38.1422 | 144.3349 | 1 | Powercor | Report | 11971 | 0.0054884 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Manifold Heights | Trees
The private tree was cut clear of the overhead conductors and the HV boric acid fuse replaced that restored supply to customers in the area. | 213 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7029110 |  | Wind;Alive |  |  |  |  | 1 | Tree fire on fire opposite 236 Burwood Highway. During strong winds, a private tree from Deakin University fell onto the LV overhead conductors. This caused the 15amp boric acid fuse to operate at "Burwood-Milford" substation. | Conductor (bare) | 0 | 0 | 0 |  | EB 11 | Vegetation: Trees Incident | Other vegetation | 18/03/2018 13:25 | 1 | Negligible: no ground fire | 9776 | Roadway |  | 20180501UTD_05 | Infrastructure (network-based) | -37.8497 | 145.1145 | 1 | United Energy Distribution | Report | 13045 | 0.012084 | Low voltage AC (<1kV) | Moorabbin Airport | 3125 | Burwood | Trees
The HV fuse flex and bail clamp were replaced along with the 16amp powder filled HV fuse. | 1 TERALBA CLOSE, DINGLEY VILLAGE VIC 3172 | 618974 |  | Animal |  |  |  |  | 1 | Caller reports the transformer is on fire outside this address. A possum made contact with the HV fuse units at "Spring-Teralba" pole type substation (pole No. LIS 0618974) that caused the connection to a HV fuse unit to fail where flames were witnessed as it burnt off. | Dropper/bridge | 0 | 0 | 0 |  | NP 12 | Animal Incident | Pole-top fire | 24/03/2018 10:50 | 1 | Negligible: no ground fire | 9777 | Roadway |  | 20180501UTD_06 | Infrastructure (network-based) | -37.9844 | 145.1413 | 1 | United Energy Distribution | Report | 13053 | 0.029126 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Animal
CEOT dispatched a fault crew to make safe, investigate and carry out/arrange for necessary repairs. CEOT also notified the local DAO. CFA onsite to put out fires. The crew isolated the private line and the owner has installed a new UG private line and this has been reconnected to supply. | 5870 GREAT ALPINE ROAD, ENSAY VIC 3895 | 1602484 | Working too close to overhead lines |  |  | Fault on customer installation |  | Phase to earth |  | IMS 233408. Initial report: Stock truck brought down service line - 3 fires observed on ground - 30m x 20m, 10m x 10m, and 1m x 1m. Final report: This was a private LV line (POEL). A truck carrying hay brought down a POEL to the shed. It was alive on the ground causing sparks. A fire in the vicinity was extinguished by the CFA. | Service conductor | 0 | 0 | 0 |  | bdl8 | A truck contacted a POEL. | Grassfire | 43105.4667 | 1 | Small: 10 - 1000 sq.m | 9778 | Agricultural |  | 20180502SPN_01 | Infrastructure (network-based) | -37.3254 | 147.7763 | 1 | AusNet Services Distribution | Report | 11983 | 0.040463 | Low voltage AC (<1kV) | Bairnsdale Airport | 3895 | Ensay | Vehicle
Upon completion, supply was restored to normal. | 499 STATION STREET, CARRUM VIC 3197 | 3304906 |  | Precipitation;Prone to salt deposition |  | Leakage |  |  | 1 | At 0017hrs on 20/03/2018, 22kV ACR FS0037 located in McLeod Road on feeder CRM 12, successfully reclosed and held. During light misty rain, HV fuse units at "Station P73-McLeod" pole type substation were tracking and flashed over on the concrete pole with a steel cross arm. The substation that is located in close proximity to Port Phillip Bay was placed under LV parallel and the HV fuse units replaced. | Insulators | 0 | 0 | 0 |  | CRM 12 | The substation pole is located in close proximity to Port Phillip Bay and tracking caused by salt borne contaminants was the probable cause. | Pole-top fire | 20/03/2018 0:17 | 1 | Negligible: no ground fire | 9779 | Roadway |  | 20180502UTD_01 | Infrastructure (network-based) | -38.0751 | 145.123 | 1 | United Energy Distribution | Report | 13050 | 0.000625 | 22kV AC | Moorabbin Airport | 3197 | Carrum | Fuse
Crew attended, isolated line and replaced cross-arm | 29 ALBERT STREET, SEBASTOPOL VIC 3356 | 30013047 |  |  |  | Leakage |  |  | 2 | A broken HV Xarm was reported . A crew attended and found a HV conductor with attached insulator and portion of burnt wooden Xarm was hanging above the LV conductor on pole. | Crossarm (wood) | 0 | 0 | 0 |  | BAS034 | Leakage current | Pole-top fire | 21/04/2018 16:43 | 1 | Negligible: no ground fire | 9787 | Roadway |  | 20180503PWA_03 | Infrastructure (network-based) | -37.5845 | 143.841 | 1 | Powercor | Report | 11994 | 0.035221 | 22kV AC | Ballarat Aerodrome | 3356 | Sebastopol | Crossarm
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded and broken O/H Neutral Screened Service Conductor at the Customer's Two Point Connection Box located at the POA, The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and Powercor FOLCB's at the Customer's POA and completed an NST Test which confirmed a Pass result. final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 120 HIGH STREET, DRYSDALE VIC 3222 | 30070998 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Jenny Nicholson was descending the stairs at the rear of her mothers property when she received an electric shock as she made simultaneous contact with her hand on the metallic Hand Rail and her feet while standing on the wet ground at the bottom of the stairs. | Service conductor | 2 | 2 | 2 |  | DDL022 | Corroded connections | Minor shock | 24/03/2018 14:00 |  |  | 9809 | Residential |  | 20180509PWA_03 | Infrastructure (customer connection) | -38.1788 | 144.56 | 1 | Powercor | Report | 12031 | 0.03234 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Drysdale | Connection
On arrival crew isolated supply. customer engaged REC to repair poa. | 45 LAKE STREET, MURTOA VIC 3390 | 32119358 | Vehicle | [6 empty] | A report was received from the customer at the above address that the service cable to the property had been hit by a high load on a trailer. The customer also advised that supply to the property had been interrupted and damage had been sustained to the point of attachment. On arrival the crew found that the customer was moving out of the house and had hit the service wire with a high load on a trailer. There was no shock, injury or fire start. | Service conductor | 2 | 2 | 2 |  | HSM001 | high load struck service | Loss of supply;Damage to network assets | 43224.6729 |  |  | 9811 | Residential |  | 20180509PWA_04 | Infrastructure (network-based) | -36.6217 | 142.4667 | 1 | Powercor | Report | 12033 | 0.033108 | Low voltage AC (<1kV) | Horsham Aerodrome | 3390 | Murtoa | Vehicle
On arrival crew isolated supply and carried out repairs | 68 HUME DRIVE, DELAHEY VIC 3037 | 34012453 | Working too close to underground cables | [6 empty] | A customer reported that the excavator on their site hit the cable at the incident location. On arrival the crew found that a contractor was operating an excavator and contacted a LV underground cable causing damage to the cable. There were no reported injuries or third party property damages. | Cable | 2 | 2 | 2 |  | SA011 | Excavations in roadway | No Go Zone (contact) | 43255.4646 |  |  | 9812 | Roadway |  | 20180509PWA_05 | Infrastructure (network-based) | -37.7099 | 144.7695 | 1 | Powercor | Report | 12034 | 0.028106 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Delahey | Dug up
On arrival crew confirmed that underground cable was not connected to supply. Other cables on pole were undisturbed. | UNIT 2 33 MACAULAY STREET, WILLIAMSTOWN NORTH VIC 3016 | 30112160 | Copper theft | [6 empty] | Report received from Police of copper theft from pole at the intersection of Churchill St and Macaulay St. Upon arrival the fault crew found that someone had attempted to steal a 4/c 35mm underground service installed between an LV service pit and LV service cablehead. Police were alerted to the incident initially by someone who reported suspicious activity and the use of an angle grinder near pole LIS-2740, which the Police then reported to Powercor. No injury, shock or third party damage to report. | Services cable | 2 | 2 | 2 |  | BLT033 | Attempted cable theft | Damage to network assets | 43224.4729 |  |  | 9814 | Roadway |  | 20180510PWA_01 | Infrastructure (network-based) | -37.8501 | 144.8632 | 1 | Powercor | Report | 12038 | 0.031693 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown North | Other
On arrival crew confirmed isolation and arranged repairs. | 5 DEEPDENE ROAD, DEEPDENE VIC 3103 | 30173349 | Copper theft | [6 empty] | A customer reported a vandalised cable on pole at the incident location. Upon arrival, Citipower fault crew found that a 16mm 4C service cables about 21m has been stolen. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | L002 | Copper theft | Damage to network assets | 43347.466 |  |  | 9815 | Roadway |  | 20180510PWA_02 | Infrastructure (network-based) | -37.8138 | 145.0619 | 1 | CitiPower | Report | 12039 | 0.01851 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Other
On arrival crew isolated supply and carried out repairs. | GALAH NORTH ROAD, OUYEN VIC 3490 | 32145208 |  |  |  | Leakage |  |  |  | Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 43134.3819 | 1 | Negligible: no ground fire | 9830 | Agricultural |  | 20180514PWA_02 | Infrastructure (network-based) | -35.082 | 142.1706 | 1 | Powercor | Report | 12059 | 0.016515 | 22kV AC | Mildura Airport | 3490 | Ouyen | Pole
On arrival crew isolated supply and carried out repairs | 161 FYANS STREET, SOUTH GEELONG VIC 3220 | 35407507 |  |  |  | Corrosion |  |  |  | Report from customer of Public Lantern on fire at incident location. There was no ground fire, no reported injuries and no third party property damage. | Public lighting | 2 | 2 | 2 |  | GLE033 | unable to clearly establish cause due to damage | Pole-top fire | 43407.3028 | 1 | Negligible: no ground fire | 9831 | Roadway |  | 20180514PWA_03 | Infrastructure (network-based) | -38.1653 | 144.367 | 1 | Powercor | Report | 12060 | 0.0038472 | Low voltage AC (<1kV) | Avalon Airport | 3220 | South Geelong | AF Other
Crew attended site to make safe and repair Conductor isolated and supply restored to customers affected. Construction sent out to re-sag conductor (5.3m from ground on the day off rectification/repair) | 220 MURRAY ROAD, CORA LYNN VIC 3814 | LIS 512817 | Vehicle |  |  |  |  | Phase to earth | 1 | IMS 233553 - Truck contacted 22kV line between poles LIS512817 and LIS523506. Conductor was sagged to approx. 6m above ground. No other damage or injuries sustained. Fuse operated at switch BW1202. | Conductor (bare) | 0 | 0 | 0 |  | PHM33 | Truck drove into overhead 22kV conductors. Truck was tipping mud with tip trailer, in the process of doing so he put the trailer into the HV, at the time of contact he drove forward, pulling the pole forward as well as blow a section of cable 8 bays down. Truck driver details not available but can confirm Truck was from "Eastern Plant Hire" with registration EPH-90 with trailer registration Y16584 | No Go Zone (contact) | 15/05/2018 12:00 |  |  | 9851 | Agricultural |  | 20180516SPN_01 | Infrastructure (network-based) | -38.153 | 145.6187 | 1 | AusNet Services Distribution | Report | 12516 | 0.0074838 | 22kV AC | Moorabbin Airport | 3814 | Cora Lynn | Vehicle
On arrival crew isolated supply and commenced repairs. | 21 WOODVALE CRESCENT, LANCEFIELD VIC 3435 | 33030123 |  |  |  | Overheated connection |  |  |  | Customer advised there appears to be a pole fire at incident location. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out. There was no ground fire, no reported injuries and no third party property damage. | Disconnector/isolator | 2 | 2 | 2 |  | WND013 | Insufficient remains to determine cause | Pole-top fire | 17/05/2018 19:05 | 1 | Negligible: no ground fire | 9862 | Roadway |  | 20180518PWA_01 | Infrastructure (network-based) | -37.2482 | 144.762 | 1 | Powercor | Report | 12132 | 0.036892 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3435 | Lancefield | Connection
Crew attended and isolated supply. cable from UG joint to pit subsequently replaced | 319 CENTENARY AVENUE, MELTON WEST VIC 3337 | 34031087 | Unauthorised access |  |  | Electrical overload |  |  | 2 | Metering crew attended site for investigations and found that metal meter box was energised whilst conducting testing for de-energized. No shock or injury. | Cable;Services pit | 0 | 0 | 0 |  | MLN023 | Interference resulting in overload | Melting or smoking only | 17/05/2018 15:55 |  |  | 9866 | Residential |  | 20180521PWA_02 | Infrastructure (network-based) | -37.6716 | 144.5605 | 1 | Powercor | Report | 12138 | 0.010965 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Isolated supply | 62BUCKHURST STREET, SOUTH MELBOURNE VIC 3205 | 30167753 | Copper theft | [5 empty] | 2 | Fault crew were investigating an outage and found that forced entry to a substation had occurred. The crew identified that LV fuses and copper mains had been removed. | Conductor (insulated);Copper;Indoor | 0 | 0 | 0 |  | MG019 | interference - copper theft | Loss of supply;Damage to network assets | 43439.4062 |  |  | 9867 | Other | Electricity substation | 20180521PWA_03 | Infrastructure (network-based) | -37.8296 | 144.9521 | 1 | CitiPower | Report | 12139 | 0.024948 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Other
crew attended and initiated repairs to LV cabling | 10 CADE STREET, YARRAWONGA VIC 3730 | 34009554 | Working too close to underground cables | [5 empty] | 2 | NBN reported underground cable had been dug up near electrical pit. Attending crew found that recent excavations had exposed and damaged low voltage wiring. | Services cable | 0 | 0 | 0 |  | CME014 | interference | Damage to network assets | 43378.7097 |  |  | 9868 | Roadway |  | 20180521PWA_04 | Infrastructure (network-based) | -36.0073 | 146.0189 | 1 | Powercor | Report | 17436 | 0.0089942 | Low voltage AC (<1kV) | Wangaratta Aero | 3730 | Yarrawonga | Dug up
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test | 392 ABERDEEN STREET, NEWTOWN VIC 3220 | 30075699 |  |  |  | Fatigue |  |  | 2 | Customer was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA, which was identified as the cause of the high impedance within the neutral conductor. | Service conductor | 0 | 0 | 0 |  | GL012 | connection failiure, | Minor shock | 43317.4167 |  |  | 9872 | Residential |  | 20180522PWA_02 | Infrastructure (customer connection) | -38.144 | 144.3251 | 1 | Powercor | Report | 12495 | 0.029744 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | Connection
Crew attended and replaced service | 32 JOAN STREET, SUNSHINE WEST VIC 3020 | 30104583 |  |  |  | Overheated connection |  |  | 2 | Daughter reports her mum received a shock in her left hand when she touched the laundry trough. A high impedance in the neutral service conductor caused current flow through the MEN and customers earthing system resulting in a voltage rise on the customers earthing system including connected plumbing. | Connector/termination | 0 | 0 | 0 |  | SU035 | Connection Malfunction, (tee clamp) LEI advice is that this occurred at the "Copper to Aluminium joint @ the connection to the open wire reticulation" older image shows neutral screened service connected through non isolating type pole box with copper leads tomains, service replaced. | Minor shock | 43409.4167 |  |  | 9874 | Residential |  | 20180522PWA_04 | Infrastructure (network-based) | -37.7895 | 144.8031 | 1 | Powercor | Report | 12505 | 0.0024236 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Connection
Crew attended Site secured Police advised | 542 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | 33111303 | Copper theft | [5 empty] | 1 | Powercor contractor â€œPower cablesâ€ reports that another break-in has occurred at this substation over the weekend. Thieves / vandals have smashed the thru the substation door to gain entry and further thefts have occurred. Other significant thefts / vandalism also occurred about two weeks ago. | Conductor (bare);Copper;Indoor;Transformer | 0 | 1 | 0 |  | DA026 | Criminal activity - copper thefts | Damage to network assets | 14/05/2018 12:35 |  |  | 9880 | Industrial |  | 20180522PWA_10 | Infrastructure (network-based) | -37.8076 | 144.9257 | 1 | CitiPower | Report | 12153 | 0.036994 | 11kV AC | Essendon Airport | 3003 | West Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 89 STUARTS ROAD, FRAMLINGHAM VIC 3265 | 30047279 |  |  |  | Overheated connection |  |  |  | Customer reported a fire on a pole at the incident location. On arrival, the crew found that a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 2 | 2 | 2 |  | TRG004 | Connection failure | Pole-top fire | 43409.5326 | 1 | Negligible: no ground fire | 9882 |  |  | 20180522PWA_11 | Infrastructure (network-based) | -38.25 | 142.6908 | 1 | Powercor | Report | 12155 | 0.037784 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Framlingham | Connection
Crew disconnected service | 109 BROOKLYN ROAD, MELTON SOUTH VIC 3338 | 33074002 |  | Within clearances |  |  |  |  | 2 | Melton CFA Brigade reported an overhead service on fire outside No. 109 Brooklyn Rd., Melton South. A Powercor crew attended and observed that a grey, twisted, 4c x 35mm Overhead service pole attached to pole LIS 108752 had sustained sheath and heat damage where contact had been made with neighbouring tree limbs. There was no sign of a fire within the tree, or, on the ground beneath. | Aluminium twisted (grey) | 0 | 0 | 0 |  | MLN013 | Vegetation: Trees Incident | Melting or smoking only;Damage to network assets | 43439.9514 |  |  | 9883 | Residential |  | 20180522PWA_12 | Infrastructure (network-based) | -37.7021 | 144.5652 | 1 | Powercor | Report | 12156 | 0.013062 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Trees
On arrival crew isolated supply and carried out repairs. | 12 GUM TREE TERRACE, DARLEY VIC 3340 | 30295395 | Working too close to underground cables | [6 empty] | Report received that workmen with an excavator had hit underground cable going to street light pole LIS-790220. Upon arrival the fault crew found that the civil contractor who was installing 2x LV underground mains cables as part of an Option 2 development at Summerfield Estate Stage 3B . There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BMH004 | Excavation near cable | No Go Zone (contact) | 43347.4458 |  |  | 9895 | Public space |  | 20180523PWA_08 | Infrastructure (network-based) | -37.6521 | 144.4187 | 1 | Powercor | Report | 12168 | 0.03059 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Darley | Dug up
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test | 37 COBB STREET, PENSHURST VIC 3289 | 32137720 |  |  |  | Corrosion |  |  | 2 | Mr Paul Wale was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole | Connector/termination | 0 | 0 | 0 |  | HTN003 | Corroded O/H Service Neutral Conductor termination | Minor shock | 23/04/2018 20:00 |  |  | 9896 | Residential |  | 20180523PWA_09 | Infrastructure (network-based) | -37.8779 | 142.2977 | 1 | Powercor | Report | 12169 | 0.018821 | Low voltage AC (<1kV) | Hamilton Airport | 3289 | Penshurst | Connection
Service truck carried out NST testing at POA and measured a high Active to Neutral loop impedance which they traced back to a corroded Aluminium to copper inline crimp at service pole. Service truck repaired conductor and left property off supply for CTA to attend. Fault crew repaired corroded connection in service line and CTA carried out NST testing and measurements | 261A NICHOLSON STREET, BRUNSWICK EAST VIC 3057 | 30156790 |  |  |  | Corrosion |  | Phase to earth |  | Chris McColmbe received an electric shock from the shower taps about week prior to report. | Connector/termination | 2 | 2 | 2 |  | BK002 | connection failure | Minor shock | 43255 |  |  | 9901 | Residential |  | 20180524PWA_02 | Infrastructure (network-based) | -37.7639 | 144.9791 | 1 | CitiPower | Report | 17380 | 0.031009 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole, The attending Powercor Fault Crew replaced the O/H Service Neutral PG Connector at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 10 BELTON STREET, ANGLESEA VIC 3230 | 30337053 |  |  |  | Corrosion |  | Phase to earth |  | Mr Shem Fitzgerald was turning on an external Tap when he received an electric shock as he made simultaneous contact between his hand on the metallic Tap and his bare feet whilst standing on the wet concrete drive. | Connector/termination | 2 | 2 | 2 |  | WPD021 | corroded connection | Minor shock | 43194.375 |  |  | 9904 | Residential |  | 20180524PWA_05 | Infrastructure (network-based) | -38.4142 | 144.172 | 1 | Powercor | Report | 17382 | 0.017083 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a damaged (Open Circuit) O/H Neutral Service Conductor adjacent the Mid Span Service connection to the Reticulation Conductors. The damage to the O/H Neutral Service Conductor was unable to be determined, which was discontinuous between the attachment to the Catenary Wire and the connection to the Reticulation Conductors. The attending Powercor Fault Crew reterminated the O/H Neutral Service Conductor and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 236 ECHUCA ROAD, MOOROOPNA VIC 3629 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Ben McCormick was in the Bathroom showering when he received an electric shock as he made simultaneous contact with one hand on the metallic Shower Tap and his bare feet while standing on the wet concrete shower base. | Service conductor | 2 | 2 | 2 |  |  | Service failure | Minor shock | 43163 |  |  | 9908 | Residential |  | 20180524PWA_07 | Infrastructure (network-based) | -36.3731 | 145.3467 | 1 | Powercor | Report | 12181 | 0.031279 | Low voltage AC (<1kV) | Shepparton Airport | 3629 | Mooroopna | OH Cable
The faults crew proceeded to remove the single phase XLPE overhead service and meter to complete the abolishment. The faults crew took photos and forwarded to their supervisor. | 2 LORNA STREET, SEAFORD VIC 3198 |  | Unauthorised work | [5 empty] | 2 | Caller reports live wire is down and touchable and the meters have been ripped out and are laying on the ground. A derelict house was being demolished and the single phase meter and switchboard had been removed from the enclosure. When the faults crew removed the service fuse cartridge from the POA, it was found the cartridge had a hole in it. When questioned, the person who was on-site (Peter Ellis 0427 689 218) stated the local council had instructed them to demolish the house and no contact had been made with United Energy or an Electricity Retailer for an abolishment request. No electric shocks or injuries were received. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised, unsafe electrical work to remove a meter when demolishing the house. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/05/2018 9:30 |  |  | 9905 | Residential |  | 20180524UTD_01 | Infrastructure (network-based) | -38.1225 | 145.1415 | 1 | United Energy Distribution | Report | 12178 | 0.035831 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Other
On arrival crew isolated supply and carried out repairs. | 5 ELLIS STREET, GUILDFORD VIC 3451 | 30038209 | Working too close to underground cables | [6 empty] | A contractor advised he has dug up an UG cable at the incident location. Upon arrival, the Powercor crew found that the UG main cable and the conduit had been damaged by an excavator. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | CMN001 | excavation work | Damage to network assets | 43347.5924 |  |  | 9917 | Roadway |  | 20180525PWA_04 | Infrastructure (network-based) | -37.1504 | 144.1611 | 1 | Powercor | Report | 12190 | 0.029448 | Low voltage AC (<1kV) | Bendigo Airport | 3451 | Guildford | Dug up
On arrival crew isolated supply and carried out repairs. | 47-49 CANNING STREET, CARLTON VIC 3053 | 30212971 |  |  |  | Fatigue |  |  |  | On the 24th of May 2018 a caller reported to Citipower that he has stumbled on a wire down, over a footpath and moved it as it was a tripping hazard. Citipower advised passer-by to not touch it again and to call the police, to isolate the area. Fault crew on arrival found a broken public lighting switching wire. The passer-by was fine however was checked by an ambulance as a precaution and not taken to hospital. The passer-by mentioned when he picked up the wire, he felt that the wire was rusty and was worried about tetanus. He was unsure if he received an electric shock, however he did mentioned that he did not feel any pain at any stage or felt a notable shock. There was no fire or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BQ066 | Fallen conductor (Switch wire) | Minor shock | 24/05/2018 19:14 |  |  | 9918 | Roadway |  | 20180525PWA_05 | Infrastructure (network-based) | -37.7987 | 144.9726 | 1 | CitiPower | Report | 12193 | 0.018449 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Conductor
Site made safe. Supply to Coolaroo zone substation was restored by control room within 25 minutes. Formal investigation was undertaken by Jemena's secondary plant team, please refer to a copy of the report (attached in the "Notes and Findings" section) which contains detailed analysis and corrective actions. | 175 SOMERTON ROAD, COOLAROO VIC 3048 | Coolaroo zone substation | Recreation - Helium (party) balloons |  |  | Not built/maintained to design |  |  | 1 | On Tuesday the 24th April 2018 at approximately 2241 hours, a fault at Coolaroo Zone Substation (COO) resulted in complete supply interruption to COO zone substation for approximately 25 minutes. This incident impacted approximately 16,611 customers including a number of HV customers. All supply was fully restored within approximately 25 minutes. The incident was triggered by a metallic balloon coming into contact with one of the two outdoor 66kV bus structure at Coolaroo zone substation. The fault was correctly isolated by 66kV bus protection scheme by isolating the faulted bus as per the design. Approximately at the same time, one of the Transformer protection also operated and isolated remaining healthy bus resulting in to complete loss of supply at Coolaroo zone substation. | Zone substation | 0 | 0 | 0 |  |  | Based on the available information the following factors are believed to have contributed to unwanted operation of Transformer protection scheme: 1. Saturation of 66kV Current Transformers (CTâ€™s); and 2. Incorrect implementation of non-standard transformer protection scheme by external turnkey contractor instead of dedicated unit protection as per Jemena standard. Saturation of 66kV CTâ€™s were predominately caused by: 1. Heavy DC offset current in fault current; 2. Possible CT remanence; and 3. Use of lower CT Tap for current measurement on the 66kV side. | Loss of supply | 24/04/2018 22:41 |  |  | 9926 | Industrial |  | 20180528JEM_01 | Infrastructure (network-based) | -37.6415 | 144.9341 | 1 | Jemena | Report | 12203 | 0.023135 | 66kV AC | Essendon Airport | 3048 | Coolaroo | Other
Reported for follow up | 211 BASTINGS STREET, NORTHCOTE VIC 3070 | 30191730 | Working too close to overhead lines | [5 empty] | 2 | Asset inspector advised that the service to a property had been propped up and there were building work in progress. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  | NC002 | interference | No Go Zone (contact) | 16/05/2018 16:05 |  |  | 9932 | Residential |  | 20180528PWA_05 | Infrastructure (network-based) | -37.7756 | 145.0139 | 2 | CitiPower | Report | 12209 | 0.020241 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Other
Inspector and fault truck organised to attend, investigate and make safe. | 330 COCHRANES ROAD, TRARALGON SOUTH VIC 3844 | LIS 2613884 |  |  |  | HV injection |  | Phase to earth |  | IMS 233715 - Bird contacted centre phase of 66kV line causing LV earth to be energised and customer meters damaged. | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  | TGN23 | Bird Incident | HV injection | 24/05/2018 8:05 |  |  | 9925 |  |  | 20180528SPN_01 | Infrastructure (network-based) | -38.2781 | 146.535 | 1 | AusNet Services Distribution | Report | 12202 | 0.012449 | Low voltage AC (<1kV);66kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon South | Animal
CEOT dispatched an AusNet Services' LEI to this installation after a report of a resident receiving an electric shock from shower taps. The LEI to make safe and investigate. Report from the attending LEI: On attending site I proceeded to test from independent earth with a multimeter: Ind E to neutral bar 0.4V. Bathroom plumbing 0.4V. Volts 232.4 V. Amps 15A. NST passed. Loop impedance test 0.28 Ohm, PSC 810A. 2nd test: Load test 20.9A /235V / 0.7 Volt on neutral. Loop test 0.26 Ohm, PSC 890A. NST passed. These results not showing anything significant, network supply was determined not to be the cause of the shock. Testing showed water pipes bonded. Testing to independent earth was not showing any voltage above that at the N Bar. LEI tested between shower set and wet tile floor - this showed 3.2V on the multimeter. LEI determined this was originating from a power circuit to the kitchen. LEI isolated this circuit and informed the customer they require the services of an REC to fix the associated wiring. Service crew installed a new aluminimum twisted XLPE type service line to the house. Completed supply tests. Supply tested OK and passed VESI requirements. Crew left site. The LEI continued to test house wiring. | 91 FRANKLIN STREET, ELTHAM VIC 3095 | 921469 |  |  |  | Fault on customer installation |  | Phase to earth |  | IMS 233383. CEOT received a call for a customer who states he received tingles from bathroom fittings. | Customer installation | 0 | 0 | 0 |  | elm33 | Faulty power final subcircuit. | Minor shock | 29/04/2018 19:56 |  |  | 9928 | Residential |  | 20180528SPN_02 | Infrastructure (network-based) | -37.7219 | 145.1482 | 1 | AusNet Services Distribution | Report | 12205 | 0.024803 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham | AF Other
Voltage tests with an independent earth and various parts of the installation, including the MEN and metallic water pipe system and the distribution assets, revealed a corroded neutral conductor connection located within the Pole End Junction Box. Pole box and service replaced with new 2 core Twisted Aluminium service by Powercor Faults Truck. No Stray voltages detected by CTA. NST Test passed at Customers Main switchboard and meter position by CTA. NST Test passed at POA by Powercor Faults Truck. | 1116 MARYBOROUGH-DUNOLLY ROAD, BET BET VIC 3472 | 30018671 |  |  |  | Corrosion |  | Phase to earth |  | Customer was showering when she received an electric shock as she made simultaneous contact between her hands on the shower taps whilst standing on the wet shower base. | Connection box | 2 | 2 | 2 |  | MRO005 | Corroded connection | Minor shock | 43408 |  |  | 9936 | Residential |  | 20180529PWA_01 | Infrastructure (network-based) | -36.9268 | 143.7572 | 1 | Powercor | Report | 12213 | 0.018323 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3472 | Bet Bet | Connection
On arrival crew isolated supply and carried out repairs. | 91-93 HOGAN STREET, TATURA VIC 3616 | 30140525 |  |  |  | Corrosion |  |  |  | CFA called to advise that sparks were coming from the pole. Upon arrival crew found that an EDO fuse had candled. Fuse remained in place and did not fall to ground. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | MNA021 | corroded fuse unit | Pole-top fire | 43316.4132 | 1 | Negligible: no ground fire | 9938 | Roadway |  | 20180529PWA_02 | Infrastructure (network-based) | -36.4398 | 145.226 | 1 | Powercor | Report | 12215 | 0.026854 | 22kV AC | Shepparton Airport | 3616 | Tatura | Fuse
On arrival crew isolated supplies. LEI on site testing for HVI | 38 KIRKWOOD ROAD, EAGLEHAWK VIC 3556 | 33023471 |  | Lightning | [5 empty] | VicFire advised wires down at the incident location. On arrival the crew found that the LV services down and also damages to third party properties. Crew believed lightning hit properties or services. There was no fire, no reported injuries. | Service conductor;Customer installation | 2 | 2 | 2 |  | BET001 | Lightning strike | HV injection;Loss of supply;Damage to network assets | 29/05/2018 9:30 |  |  | 9940 | Residential |  | 20180529PWA_03 | Infrastructure (network-based) | -36.7131 | 144.2523 | 1 | Powercor | Report | 12218 | 0.030341 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Eaglehawk | Lightning
On arrival crew arranged for isolation and pole was replaced. | WAKEFIELD ROAD, WALPEUP VIC 3507 | 32147316 |  | Lightning |  |  |  |  | 1 | A Powercor fault crew attending a Feeder fault found that a burnt pole. Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage | Pole (wood) | 2 | 2 | 2 |  | OYN001 | Lightning strike | Pole-top fire;Grassfire | 29/05/2018 13:56 | 1 | Localised: less than 10 sq.m | 9962 |  |  | 20180531PWA_05 | Infrastructure (network-based) | -35.0666 | 142.0351 | 1 | Powercor | Report | 12242 | 0.032972 | 12.7kV AC (SWER) | Mildura Airport | 3507 | Walpeup | Lightning
On arrival crew arranged for isolation and pole was replaced. | WAKEFIELD ROAD, WALPEUP VIC 3507 | 32147329 |  | Lightning |  |  |  |  | 1 | A Powercor fault crew attending a Feeder fault found that a burnt pole. Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage | Pole (wood) | 2 | 2 | 2 |  | OYN001 | Lightning strike | Pole-top fire;Grassfire | 29/05/2018 13:56 | 1 | Localised: less than 10 sq.m | 9963 | Agricultural |  | 20180531PWA_06 | Infrastructure (network-based) | -35.0636 | 142.0345 | 1 | Powercor | Report | 12243 | 0.012473 | 12.7kV AC (SWER) | Mildura Airport | 3507 | Walpeup | Lightning
CEOT dispatched a fault crew and an AusNet Services' LEI to make safe, investigate and carry out any necessary repairs. The attending AusNet Services' fault crew re-terminated the neutral connections at the customer's POA and connections along the LV open wire back to the single phase pole substation. An NST test was carried out after the repairs, directly at the substation, which indicated a Pass result. With neutral to earth voltage of 2..8 Volts. Voltage tests between an independent earth and various portions of the electrical installation showed a value of 1.8 Volts. An NST was carried out at the installation, which showed a Pass result. The installation was left ON supply and the customers were advised to report any future incidents as soon as possible. CEOT (report room) notified. | 105 FOREST STREET, YARRA GLEN VIC 3775 | 1006739 |  |  |  | Neutral fault |  |  |  | IMS 233444. Mrs Raelene Sharp advised that her and various other members of the family have been for around 3 years, receiving an slight electric shock while they were in the bathroom when they made simultaneous contact between the shower taps and the tiled bathroom floor. The house construction consists of a concrete slab. The problem has become worse over the last three months.This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 10.8 Volts on the water piping system. Supply arrangement originates from a single phase pole substation with 22kV and 230 V via an overhead service. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets could not clearly identify a specific fault in the supply neutral conductor which could be identified as the cause of the high impedance within the neutral service conductor. | Connector/termination | 0 | 0 | 0 |  | cpk12 | High impedance neutral but not exactly what caused this. Please see the details in the Incident and Action tabs. Likely high impedance connection rectified when connections were re-terminated. | Minor shock | 43164.4153 |  |  | 9949 | Residential |  | 20180531SPN_01 | Infrastructure (network-based) | -37.6473 | 145.3802 | 1 | AusNet Services Distribution | Report | 12227 | 0.011292 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Yarra Glen | AF Other
The attending AusNet Services' fault crew assisted by testing the LV overhead mains outside # 105 Forest St, The voltage on the neutral conductor fluctuated between 6V & 10V - an NST test failed. Each customer installation was isolated from the LV reticulation system one at a time, the voltage on the neutral conductor was retested each time an installation was isolated and the voltage remained between 6V & 10V. The final installation was isolated and the voltage on the overhead neutral conductor reduced to 0.5V approximately. The Fault Crew were asked to isolate Foster / Ellis Substation HV and LV, open the LV break on the earthing system and test the Substation LV earth. The subsequent earth test revealed that the LV earth had a resistance of greater than 800 Ohms, the HV earth was also tested and was also greater than 800 Ohms. The AusNet Services' Operations Control Room advised that the loading on â€œFoster / Ellisâ€ Substation was at 156%. The combination of a high resistance earthing system coupled with a heavily loaded Substation caused a voltage rise on the LV neutral. Advised AusNet Services Control Room â€œFoster / Ellisâ€ Substation to remain isolated until earthing system is replaced and that a Transformer upgrade is strongly recommended. LEI required to test on completion of rectification works to ensure there are no secondary issues. The customers were reconnected to supply via an LV parallel, # 105 Forest St was NST tested and passed and the voltage on the LV neutral was 2.7V. The Installation was left ON supply, customers advised to report any future incidents as soon as possible. Report room notified. | 105 FOREST STREET, YARRA GLEN VIC 3775 | 1006739 |  |  |  | Earth fault |  | Phase to earth |  | IMS 233516. Mrs Raelene Sharp and various other members of the family have been for around 3 years, receiving a slight electric shock while they were in the bathroom when they made simultaneous contact between the shower taps and the downstairs bathroom shower drain. (house construction concrete slab). The problem has become worse over the last three months. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 8.8 Volts on the water piping system the voltage was not constant and fluctuated. Supply arrangement originates from an single phase 25KVA pole sub, with 22kV and 230V via overhead service. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets could not clearly identify a specific fault in the supply neutral conductor which could be identified as the cause of the high impedance within the neutral service conductor. | Earth/earthing | 0 | 0 | 0 |  | cpk12 | The combination of a high resistance substation earthing system coupled with a heavily loaded substation transformer caused a voltage rise on the LV neutral. | Minor shock | 43378.3889 |  |  | 9972 | Residential |  | 20180604SPN_01 | Infrastructure (network-based) | -37.6473 | 145.3802 | 1 | AusNet Services Distribution | Report | 12253 | 0.020749 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Yarra Glen | AF Other
A tree branch was removed from the HV overhead conductors outside 3045 Frankston-Flinders Road that supposedly had burn marks. | 3045 FRANKSTON-FLINDERS ROAD, BALNARRING VIC 3926 | 1105857 |  | Blown branch/vegetation |  |  |  |  | 2 | The CFA advised of a pole on fire in Balnarring Beach Road near the corner of Sandy Point Road. During strong gusty winds, a caller reports that a tree branch or pole is on fire. | Conductor (bare) | 0 | 0 | 0 |  | MTN 32 | The event occurred in strong gusty winds with high fault activity at the time. | Other vegetation | 14/04/2018 10:24 | 1 | Negligible: no ground fire | 9987 | Roadway |  | 20180608UTD_02 | Infrastructure (network-based) | -38.3742 | 145.1254 | 1 | United Energy Distribution | Report | 13059 | 0.025833 | 22kV AC | Moorabbin Airport | 3045 | Balnarring | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 1506 FRANKSTON-FLINDERS ROAD, TYABB VIC 3913 | 1108046 |  | Precipitation |  | Leakage |  |  | 1 | At 1208hrs on 09/06/2018, 22kV feeder ACR MT 7521 located in Frankston-Flinders Road reclosed to lockout affecting 662 customers. The CFA report of a pole fire near the United petrol station in Frankston-Flinders Road near the corner of Maurice Drive. A pole fire occurred at the coach screw for the high voltage cross arm braces on timber pole No. LIS 1108046 located 3 poles south of the HV/LV tee-off to "Lima-Bettina" substation. It appeared the 22kV insulators were tracking internally down the pole from the top of the 22kV cross arm (transposition construction) to the public lighting bracket below the LV cross arm. The CFA requested the 66kV conductors (TBTS-MTN) to be de-energised as the pole continued burning and it was finally extinguished. The pole requires replacement but was deemed presently load worthy and is to be programmed at a later date. The 22kV insulators were replaced prior to supply being restored. | Pole (wood) | 0 | 0 | 0 |  | TBTS-MTN 66kV and HGS33 22kV | Probable tracking insulators during damp conditions. | Pole-top fire | 43318.5056 | 1 | Negligible: no ground fire | 9996 | Roadway |  | 20180612UTD_01 | Infrastructure (network-based) | -38.2567 | 145.1894 | 1 | United Energy Distribution | Report | 13071 | 0.016655 | 22kV AC | Moorabbin Airport | 3913 | Tyabb | Pole
Supply was isolated by the faults crew and the FOLCB was replaced. | 38 NORMANBY ROAD, SORRENTO VIC 3943 | 1306940 |  |  |  | Overheated connection |  |  | 2 | CFA on site. The pole is sparking and dropping embers into a nearby tree. A fire occurred at a three phase FOLCB at pole No. LIS 1306940 and no ground fire started. The probable cause was an overheated connection due to overload or a loose connection. | Connection box | 0 | 0 | 0 |  |  | The probable cause was an overheated connection due to overload or a loose connection. | Pole-top fire | 43349.716 | 1 | Negligible: no ground fire | 9998 | Roadway |  | 20180612UTD_02 | Infrastructure (network-based) | -38.3389 | 144.7305 | 1 | United Energy Distribution | Report | 13072 | 0.0044144 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Connection
The site was made safe and repairs will be conducted at a future date. | 12 WISEMAN STREET, HAWTHORN EAST VIC 3123 | 30201613 | Copper theft | [6 empty] | A customer (Martha Dessiniotis Ph 0412 677 561) reported damage to Powercor assets. On arrival the crew found that a Low Voltage (LV) service cable (Pole to pit) had been stolen from the pole where it had been installed and awaiting final connection to the customer. The damage to the installation was consistent with the cable being ties to a vehicle and reefed from the conduit. There were no reported injuries or other third party damage. | Services cable | 2 | 2 | 2 |  | CL011 | Copper theft | Damage to network assets | 23/05/2018 11:03 |  |  | 10033 | Roadway |  | 20180618PWA_06 | Infrastructure (network-based) | -37.837 | 145.0444 | 1 | CitiPower | Report | 12369 | 0.041185 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor which was detached from the Reticulation Conductors at the Reticulation Pole, The attending Powercor Fault Crew replaced the existing O/H Twisted Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 23 AMARINA ROAD, CLIFTON SPRINGS VIC 3222 | 30059972 |  |  |  | Corrosion |  | Phase to earth |  | Ms Brenda Hunter was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and her other hand on the metallic Kitchen sink. | Service conductor | 2 | 2 | 2 |  | DDL022 | corroded service connection | Minor shock | 25/05/2018 10:00 |  |  | 10036 | Residential |  | 20180618PWA_09 | Infrastructure (network-based) | -38.1649 | 144.5643 | 1 | Powercor | Report | 12372 | 0.0010046 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | Connection
The 6amp EDO fuse was replaced and supply restored to customers in the area. | 1 WELLINGTON ROAD, BITTERN VIC 3918 | 1107245 |  | Cold |  | Candled fuse |  |  | 2 | Two customers who reside in Wellington Road, Bittern advised of a loss of their electricity supply. A single phase EDO fuse candled at "Pearce-Wellington" pole type substation that caused a loss of supply to 2 customers in the vicinity. Pole No. LIS 1107245. | EDO fuse | 0 | 0 | 0 |  | HGS 23 | A EDO fuse candled. | Pole-top fire | 16/06/2018 6:32 | 1 | Negligible: no ground fire | 10041 | Residential |  | 20180619UTD_01 | Infrastructure (network-based) | -38.3584 | 145.1624 | 1 | United Energy Distribution | Report | 13075 | 0.015602 | 22kV AC | Moorabbin Airport | 3918 | Bittern | Fuse
Fault crew attended to isolate and make safe Installation repaired and fuses resized | 23 KALLARA ROAD, WARNEET VIC 3980 | 517474 |  |  |  | Electrical overload |  | Phase to phase |  | IMS - 234031 Krone box on fire at pole LIS 517474. No ground fire. | Connection box | 0 | 0 | 0 |  | CRE33 | Krone box failure resulting from overload | Other electricity related | 19/06/2018 18:58 | 1 | Negligible: no ground fire | 10046 |  |  | 20180620SPN_01 | Infrastructure (network-based) | -38.2241 | 145.3131 | 1 | AusNet Services Distribution | Report | 12841 | 0.029172 | Low voltage AC (<1kV) | Moorabbin Airport | 3980 | Warneet | Connection
Dispatched Electrical Inspector to investigate The attending LEI visually checked the condition of all conductors and terminations between the distribution system and the Point of attachment of the installation. This revealed an unsafe live active termination at the Customer POA service cable. Unable to complete any testing as was called after the fact and service crews had already replaced the damaged service. The damaged portion of the service cable was left onsite and this was identified as the fault and would account for the plumber receiving an electric shock. control room notified | UNIT 1 2 DAVEY ROAD, MONTMORENCY VIC 3094 | LIS 902558 |  |  |  | Mechanical breakdown |  | Phase to earth | 2 | IMS 234026 Plumber (Peter, surname unknown) was replacing gutters on a metal clad carport at the time he received an electric shock whilst simultaneously contacting the metal roofing structure and the metal guttering in the vicinity of customers POA with his right hand. He was standing on a metallic ladder on the damp ground at the time | Service conductor | 0 | 0 | 0 |  | SMG21 | Damaged insulation at POA active lead - Service side. | Minor shock | 19/06/2018 10:06 |  |  | 10058 | Residential |  | 20180626SPN_01 | Infrastructure (customer connection) | -37.7166 | 145.1151 | 1 | AusNet Services Distribution | Report | 12497 | 0.027432 | Low voltage AC (<1kV) | Essendon Airport | 3094 | Montmorency | Connection
CEOT dispatched a fault crew to attend, investigate, make safe and to arrange for repairs. The pole was checked and was found to be not damaged. The sidewalk pole stay needs to be replaced and also retie of 66kV, 22kV and LV conductors. A substantial amount of operational switching was required to be carried out. | 215 GLENFERN ROAD, UPWEY VIC 3158 | 1305298 | Vehicle | [5 empty] | 1 | IMS 233338. Initial report: CEOT received a report by emergency authorities of a vehicle impacting a pole. The pole was a 66kV/22kV pole and the collision caused 66kV conductor to come of its insulator and fall into a 22kV conductor. Final report: Car hit sidewalk stay and pole (Lis 1305298) breaking conductor ties on 66kV and 22kV and LV which tripped the feeder protection and resulted in a loss of supply to 767 customers. No Details of driver reported from field staff. There was no report of a HVI. | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  | fgy13 | Vehicle into HV pole stay. | Loss of supply;Damage to network assets | 24/04/2018 15:00 |  |  | 9739 | Residential |  | 20180426SPN_02 | Infrastructure (network-based) | -37.9142 | 145.3167 | 1 | AusNet Services Distribution | Report | 12373 | 0.038647 | 22kV AC;66kV AC | Moorabbin Airport | 3158 | Upwey | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 77-79 WETHERBY ROAD, DONCASTER VIC 3108 | 7061503 |  |  |  | HV injection;Overheated connection |  |  | 1 | At 0049hrs on 11/04/2018, 22kV feeder DC 03 circuit breaker reclosed to lockout affecting 4183 customers. The MFB were on site in Dunoon Street, Doncaster following a call advising of a fire at the base of the pole. A possum made contact with HV conductors at the open point in Dunoon Street, Doncaster at pole No. LIS 7061503. This caused a PG connection to fail on the corner of Dunoon Street and Wetherby Road causing the centre phase HV conductor on the west side of the pole to fall to the ground. The HV conductor appears to have made brief contact with the LV white and blue phases resulting in the LV fuses to operate at "Dunoon-Wetherby" pole type substation. The faults crew requested that a LEI attend to investigate as a HVI was suspected to customers supplied from "Dunoon-Wetherby" substation. The LEI confirmed a high voltage injection occurred (BWD 1807) affecting customers who reside in the vicinity that sustained minor damage to metering equipment and appliances. | Connector/termination | 0 | 0 | 0 |  | DC 03 | Animal Incident | HV injection;Loss of supply;Grassfire | 43408.034 | 1 | Localised: less than 10 sq.m | 9750 | Residential |  | 20180427UTD_04 | Infrastructure (network-based) | -37.7938 | 145.1422 | 1 | United Energy Distribution | Report | 13398 | 0.01472 | 22kV AC | Moorabbin Airport | 3108 | Doncaster | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. The LV red phase 315amp HRC fuse was replaced at "Keating-Fifth" substation following it's operation at the time of the fault. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 1 SURF AVENUE, BEAUMARIS VIC 3193 | 1811508 |  | Precipitation |  | HV injection;Leakage |  |  | 1 | At 1235hrs on 14/04/2018, 11kV feeder BR 04 circuit breaker reclosed to lockout affecting 1204 customers. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 1811508 located on the corner of Stawell Street and Keating Streets, Beaumaris in close proximity to Port Phillip Bay. A HV conductor made brief contact with the LV red phase conductor below when the cross arm broke and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Keating-Fifth" substation. The LEI confirmed a high voltage injection occurred (BWD 1808) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Crossarm (wood) | 0 | 0 | 0 |  | BR 04 | A crossarm fire occurred during light rain after a lengthy dry spell, | Pole-top fire;HV injection | 14/04/2018 12:35 | 1 | Negligible: no ground fire | 9760 | Residential |  | 20180430UTD_01 | Infrastructure (network-based) | -37.9827 | 145.0246 | 1 | United Energy Distribution | Report | 13060 | 0.017899 | 11kV AC | Moorabbin Airport | 3193 | Beaumaris | Crossarm
A LEI and faults truck attended and immediately identified the neutral service conductor had become detached for the overhead reticulation at the pole end. The faults crew cleaned, greased and re-terminated the service connections prior to the LEI re-testing the installation that confirmed the fault had been rectified. The occupier was advised of the rectification work and supply was left on. | 33 MILFORD CRESCENT, FRANKSTON VIC 3199 |  |  | Prone to salt deposition |  | Electrical breakdown |  | Phase to earth | 2 | At 12.09AM on 15/04/2018, an smart meter communicated a neutral problem at meter number 01262487. A short time later, the occupier advised that he had received a slight electric shock at the switchboard when checking the cause of the dimming lights. The occupier received an electric shock from the metal meter enclosure when checking the cause of the dim lights and contacted the United Energy faults and emergencies call centre. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | A detached neutral service conductor from the overhead reticulation. | Minor shock | 15/04/2018 10:00 |  |  | 9762 | Residential |  | 20180430UTD_02 | Infrastructure (network-based) | -38.1432 | 145.1657 | 1 | United Energy Distribution | Report | 11962 | 0.011603 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Conductor
Upon completion, supply was restored to normal. | 66 CLARENDON DRIVE, SOMERVILLE VIC 3912 | 1112407 |  | Precipitation |  | Leakage |  |  | 2 | Caller reports the powerlines in the street is sparking with flames on top of the pole. The customer still has power to her house. The 22kV HV fuse units at "Claredon-Mimi" substation were tracking during damp weather conditions and subsequently flashed over. The substation was isolated and placed under LV parallel where the HV fuse units were replaced under Access Authority conditions. | Insulators | 0 | 0 | 0 |  |  | Tracking HV assets following light rain after a long dry spell. | Pole-top fire | 17/03/2018 14:12 | 1 | Negligible: no ground fire | 9775 | Roadway |  | 20180501UTD_04 | Infrastructure (network-based) | -38.2275 | 145.1594 | 1 | United Energy Distribution | Report | 13039 | 0.026069 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Fuse
Disconnected supply and made safe. | 45 STANLEY STREET, GLENROY VIC 3046 |  | Unauthorised work | [5 empty] | 2 | Jemena crew attended 45 Stanley street Glenroy for a new connection. On site they found a multi-phase meter with only one phase connected. It is alleged that this is another case of interference with Jemena assets by non-authorised personnel. The service is a black twist overhead service , Meter is registered to a permanent supply but has been moved to a builders temporary supply. There are no details in the system of Jemena attending the site. Please refer to the attached photo. | Aluminium twisted (XLPE);Smart meter | 2 | 2 | 2 |  |  | Allegedly unknown person relocated overhead service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43136.6444 |  |  | 9784 | Residential |  | 20180503JEM_01 | Infrastructure (network-based) | -37.7126 | 144.9122 | 1 | Jemena | Report | 11989 | 0.0018125 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Other
crew attended and checked assets for damage, line height recorded . | 1449 CALDER HIGHWAY, MARONG VIC 3515 | 33018648 | Working too close to overhead lines | [5 empty] | 1 | A customer reported that a truck has struck a wire at the incident location. On arrival the crew found that a tip truck had been tipping off pebbles on the road reserve and contacted the overhead HV conductors causing the driver to receive an electric shock and blow a tyre on the truck. The driver was taken to hospital for observation and later discharged. | Conductor (bare) | 0 | 0 | 0 |  | BET001 | Interference | Minor shock;No Go Zone (contact) | 43195.316 |  |  | 9790 | Roadway |  | 20180504PWA_01 | Infrastructure (network-based) | -36.7326 | 144.1296 | 1 | Powercor | Report | 11998 | 0.017356 | 22kV AC | Bendigo Airport | 3515 | Marong | Vehicle
Crew attended and replaced pole | BRACEWELL STREET, EAGLEHAWK VIC 3556 | 30030525 | Vehicle | [5 empty] | 1 | Vicfire reported car hit pole, powerlines sparking and arcing, hanging very low No Shocks, No known property damage, Driver taken to Bendigo Hospital. | Pole (wood) | 0 | 0 | 0 |  | BET001 | Traffic event | Loss of supply;Medical attention (first aid/doctor/hospital) | 43164.9062 |  |  | 9791 | Roadway |  | 20180504PWA_02 | Infrastructure (network-based) | -36.7249 | 144.2424 | 1 | Powercor | Report | 12000 | 0.04153 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3556 | Eaglehawk | Vehicle
CEOT dispatched a fault crew. CFA required to attend and put out pole fire. DAO Terry Warnock advised. CFA extinguished fire in head of pole. Note CFA had to be called by fault crew after arrival, and wait further for back up with more powerful equipment to be despatched from Benalla. 22kV switched out overnight including customers ex Glenrowan West Iso because centre phase 66kV was down between 22kV phases. Pole replaced the following day Sunday 25 March. Because of the lean, and the uncertainty of the condition of the head of the pole that had burned below the 66kV crossarm kingbolt, and the change of stringing, and the close proximity to the adjacent 66kV line GNTS 1 line was also taken out under access permit, which meant that Wangaratta zss was supplied all day via Myrtleford. | 692 GLENROWAN ROAD, WANGARATTA SOUTH VIC 3678 | 3909511 |  | Lightning;Precipitation | [5 empty] | IMS 233001. Reported pole sparking. Lightning struck wood strain 66/22kV pole 3909511. Fault current path to earth through the guy caused GY3 insulator to 50% shatter. Pole fire resulted in head of pole, and burned until strain and bridging insulators fell on to steel 66kV crossarm. No injection to 22kV suspected. | Conductor (bare);Pole (wood);Pole top;Insulators | 0 | 0 | 0 |  | wn6 | Lightning strike to pole. | Pole-top fire | 24/03/2018 19:08 | 1 | Negligible: no ground fire | 9798 | Commercial |  | 20180507SPN_03 | Infrastructure (network-based) | -36.438 | 146.2478 | 1 | AusNet Services Distribution | Report | 12010 | 0.0074931 | 22kV AC;66kV AC | Wangaratta Aero | 3678 | Wangaratta South | Lightning
CEOT dispatched a fault crew to make safe, investigate and repair. Crew found burnt of Boric fuse at WL144 P2203567 to Giffard spur. Crew replaced Boric Acid Fuse with new Boric Acid Fuse. No fire on the ground or damage to any other asset. | 295 COSTELLOS ROAD, GIFFARD VIC 3851 | 2504316 |  |  |  | Candled fuse |  |  |  | IMS 232998. SWFUSE WL144 at P#2203567 found burnt out by the attending fault crew. No ground fire. No other damage. | Boric acid | 0 | 0 | 0 |  | sle31 | Burnt Boric Acid HV fuse tube. | Other electricity related | 24/03/2018 11:00 | 1 | Negligible: no ground fire | 9800 | Agricultural |  | 20180507SPN_04 | Infrastructure (network-based) | -38.4243 | 147.1068 | 1 | AusNet Services Distribution | Report | 12833 | 0.034096 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3851 | Giffard | Fuse
Site made safe. Section isolated and crew carried out repairs. | 33 ARGYLE STREET, RESERVOIR VIC 3073 | pole no. A033475 |  |  |  | Leakage |  |  | 1 | Pole top fire involving HV crossarm due to tracking, which resulted in slight charring to tip of HV crossarm on footpath side phase and the insulator resting on crossarm. Photos attached in "Notes & Findings" section. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | TT03 | Electrical leakage | Pole-top fire | 43378.509 | 1 | Negligible: no ground fire | 9821 | Residential |  | 20180510JEM_01 | Infrastructure (network-based) | -37.702 | 145.025 | 1 | Jemena | Report | 12049 | 0.016633 | 22kV AC | Essendon Airport | 3073 | Reservoir | Crossarm
On arrival crew isolated supply and carried out repairs. | MILLEWA ROAD, MERRINEE VIC 3496 | 32140161 |  |  |  | Leakage |  |  | 1 | Following on from a line patrol the crew found pole fire There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 43378.1146 | 1 | Negligible: no ground fire | 9819 | Agricultural |  | 20180510PWA_06 | Infrastructure (network-based) | -34.3667 | 141.9175 | 1 | Powercor | Report | 12045 | 0.0038241 | 22kV AC | Mildura Airport | 3496 | Merrinee | Pole
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral connection at the pole end. Fault truck checked all connection disconnected neutral connection and re-made neutral connection at the pole end. CTA re-tested property, all required VESI tests passed | 4 REVELL CRESCENT, ST ALBANS VIC 3021 | 33072312 |  |  |  | Corrosion |  | Phase to earth |  | Loang was showering at the time; he received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. | Service conductor | 2 | 2 | 2 |  | SA009 | Corroded connection | Minor shock | 43194.2917 |  |  | 9820 | Residential |  | 20180510PWA_07 | Infrastructure (network-based) | -37.7323 | 144.7873 | 1 | Powercor | Report | 12047 | 0.017352 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Connection
Fault truck dispatched to investigate and make safe. | MULLERS ROAD, TABILK VIC 3607 | 4705544 |  |  |  | Candled fuse |  |  | 0 | IMS 233134 - fuse candling | EDO fuse | 0 | 0 | 0 |  | smr8 | EDO fuse candling | Pole-top fire;Loss of supply | 43224.4132 | 1 | Small: 10 - 1000 sq.m | 9822 | Agricultural |  | 20180510SPN_01 | Infrastructure (network-based) | -36.8283 | 145.1241 | 1 | AusNet Services Distribution | Report | 12835 | 0.023568 | 22kV AC | Mangalore Airport | 3607 | Tabilk | Fuse
Site made safe, removed tree branch and repaired conductor. | 58 DOYLE STREET, AVONDALE HEIGHTS VIC 3034 | A095381 |  | Blown branch/vegetation |  |  |  |  | 2 | Tree branch has brought a live LV neutral conductor to ground. | Conductor (bare) | 0 | 0 | 0 |  | BY14 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43409.6181 |  |  | 9826 | Residential |  | 20180511JEM_01 | Infrastructure (network-based) | -37.7573 | 144.8578 | 1 | Jemena | Report | 12055 | 0.018373 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | Trees
Site made safe and conductor repaired. | 2 LAWLEY STREET, RESERVOIR VIC 3073 |  | Vehicle | [5 empty] | 2 | Vehicle hit pole causing LV conductor to come to ground | Conductor (bare) | 2 | 2 | 2 |  |  | Vehicle impacted pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/05/2018 15:42 |  |  | 9828 | Residential |  | 20180513JEM_01 | Infrastructure (network-based) | -37.7069 | 144.9922 | 1 | Jemena | Report | 12057 | 0.016914 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Vehicle
On arrival crew isolated supply and carried out repairs | 749 DUNCANS ROAD, WERRIBEE SOUTH VIC 3030 | 30112650 |  |  |  | Leakage |  |  |  | Reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WBE034 | Excessive leakage current | Pole-top fire | 43134.2958 | 1 | Negligible: no ground fire | 9829 | Roadway |  | 20180514PWA_01 | Infrastructure (network-based) | -37.9414 | 144.7089 | 1 | Powercor | Report | 12058 | 0.0024722 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Pole
On arrival crew isolated supply and carried out repairs. | 2-4 CHRISTIES ROAD, LEOPOLD VIC 3224 | 31012208 |  |  |  | Leakage |  |  |  | Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | DDL014 | Excessive leakage current | Pole-top fire | 18/03/2018 10:05 | 1 | Negligible: no ground fire | 9835 | Roadway |  | 20180515PWA_01 | Infrastructure (network-based) | -38.1912 | 144.4736 | 1 | Powercor | Report | 12098 | 0.022122 | 22kV AC | Avalon Airport | 3224 | Leopold | Pole
CEOT dispatched a fault crew to make safe, investigate and carry out / arrange for repairs. CEOT also notified the local DAO. The crew replaced the damaged 3 phase fused mains box at pole LIS 420557. The crew also replaced failing service pit connectors with new u/g IPCs connectors. NST test all passed. Left on supply. | 32 MOUNTAIN ROAD, COCKATOO VIC 3781 | 420555 |  |  |  | Overheated connection |  |  |  | IMS 233125. MFB reported pole fire. Fuse Mains Box (FOLCB) burnt out, fire on pole, no ground fire. Pole LIS 420557. | Any other type | 0 | 0 | 0 |  | bge22 | Pole FMB burnt out. Fire on pole. | Other electricity related | 43194.8424 | 1 | Negligible: no ground fire | 9839 | Residential |  | 20180515SPN_02 | Infrastructure (network-based) | -37.9265 | 145.5085 | 1 | AusNet Services Distribution | Report | 12102 | 0.023073 | Low voltage AC (<1kV) | Moorabbin Airport | 3781 | Cockatoo | Fuse
The fitter was taken to the nearest medical centre for assessment. HSEQ, CEOT and Supervisors were notified of the incident. WorkSafe were notified of the incident and will be attending site today. After sustaining the shock to his hand, the electrician was taken to Healesville Hospital for observation and an ECG Test. He was released a short time after. No visible physical injuries sustained. Following the investigation it is recommended that the wiring issue be rectified for both transformers and the circuit wire numbers are updated. Actions/recommendations: â€¢ Investigate wiring of the other transformers that share the same specification number (78/253) to ensure they do not have the same issue. â€¢ Review works practices around plant which has multiple AC supplies and neutrals. Suggest all AC supplies are isolated prior to work on a piece of plant. â€¢ Review works practices related to disconnection of AC neutrals. | 15 SYMES ROAD, WOORI YALLOCK VIC 3139 |  |  |  |  | Not built/maintained to design |  | Phase to earth |  | IMS 233141. At Woori Yallock (WYK) zone substation electrical fitter received a 240V AC electric shock while completing works associated with the REFCL project. A BMC electrical fitter was removing a 415V circuit that runs from a VRR scheme to the tap changer on one of the power transformers. Before removal they isolated the circuit and tested it. All three phases and neutral were at 0V. All phases were removed with no issue, but when the neutral was being removed the fitter suffered a shock to the hand. The significant contributing factors identified are: o Existing wiring of the transformer tap changer not as per design. The neutral of the 3 phase OLTC supply and single phase OLTC heater supply had been swapped incorrectly. o Wire numbers for the AC circuits were not unique making identification of the wiring issue difficult. | Transformer | 0 | 0 | 0 |  |  | Existing wiring of the transformer tap changer not as per design. | Minor shock | 43224.4375 |  |  | 9842 | Other | Zone Substation | 20180515SPN_04 | Infrastructure (network-based) | -37.7759 | 145.5287 | 1 | AusNet Services Distribution | Report | 12284 | 0.028595 | Low voltage AC (<1kV) | Moorabbin Airport | 3139 | Woori Yallock | AF Other
The attending LEI tested and disconnected all affected properties (numbers 36, 38 and 40) and called the report room to request a faults truck. The fault crew re-terminated the service neutral and the LEI conducted NST and polarity checks at the customer switchboard which recorded satisfactory results. Voltage tests between an independent earth and various points of the electrical installation, including the M.E.N. and metallic water pipe system and the distribution assets, revealed a constant voltage of 1 Volt. As a final test an NST was carried out on the installation by the attending LEI that indicated a Pass result. The Installation was left ON supply. | 36 HIGHPOINT CRESCENT, ELTHAM NORTH VIC 3095 |  |  |  |  | Neutral fault |  | Phase to earth |  | Matt was showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps while standing on the wet shower base. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified an open circuit neutral conductor at the reticulation service pole which supplied numbers 36, 38 and 40. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 36 Volts on the water piping system. | Connector/termination | 0 | 0 | 0 |  |  | The service neutral conductor had disconnected from the split bolt clamp | Minor shock | 15/04/2018 14:08 |  |  | 9847 | Residential |  | 20180515SPN_07 | Infrastructure (network-based) | -37.7055 | 145.1411 | 1 | AusNet Services Distribution | Report | 12114 | 0.024124 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham North | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 2 FRIEDA STREET, DROMANA VIC 3936 | 1317512 |  | Precipitation |  | Leakage |  |  | 1 | At 2319hrs on 09/05/2018, 22kV feeder ACR RB7532 located in Boundary Road, reclosed to lockout affecting 685 customers. Following light rain after a lengthy dry spell, a cross arm fire occurred at pole No. LIS 1317512 located outside 2 Frieda Street, Dromana. The pole is located near Port Phillip Bay and air blown salt contaminants contributed to the HV insulators tracking. There were additional reports of insulators tracking in the vicinity at the same time. | Crossarm (wood) | 0 | 0 | 0 |  | DMA 13 | The pole is located near Port Phillip Bay and air blown salt contaminants contributed to the HV insulators tracking. | Pole-top fire | 43348.9715 | 1 | Negligible: no ground fire | 9856 | Roadway |  | 20180517UTD_03 | Infrastructure (network-based) | -38.3385 | 144.9698 | 1 | United Energy Distribution | Report | 13064 | 0.02594 | 22kV AC | Moorabbin Airport | 3936 | Dromana | Crossarm
Crew isolated, bypassed and replaced LV earth | POLO CLUB, 192 AIRPORT ROAD, MITCHELL PARK VIC 3355 | 33000771 | Copper theft | [5 empty] | 2 | A Powercor contractor (Electrix) reported that the LV earth was stolen from the incident location. On arrival the crew found that a Low Voltage earth at Airport pole 16 S/Stn had been stolen. There were no reported injuries or other third paryt damage. | Earth/earthing | 0 | 0 | 0 |  | BAN002 | interference | Damage to network assets | 19/05/2018 15:00 |  |  | 9864 | Roadway |  | 20180521PWA_01 | Infrastructure (network-based) | -37.5163 | 143.7832 | 1 | Powercor | Report | 12134 | 0.024185 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Mitchell Park | Other
CEOT advised and site made safe. Underground Crew located, excavated and rectified the service tee. Neutral and Red phase connections rectified at Service tee, testing completed and installation passed at pit. | 184 CROSSS ROAD, TRARALGON VIC 3844 |  |  |  |  | Reverse polarity |  |  | 2 | IMS 233645 - New Connection team were to connect New Customer at 184 Cross's road Traralgon. Testing indicated Neutral alive to 240V (reverse polarity) it appears the Red Phase and the Neutral are crossed at Tee joint off LV mains. No customers or supplies are connected to this LV pit. | Services cable;Services pit | 0 | 0 | 0 |  |  | Red Phase and Neutral crossed at Tee joint off LV mains (now rectified) | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/05/2018 13:00 |  |  | 9865 | Residential |  | 20180521SPN_01 | Infrastructure (network-based) | -38.1819 | 146.5015 | 1 | AusNet Services Distribution | Report | 12524 | 0.0030579 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | AF Other
On arrival crew isolated supply and commenced repairs. | 205 COSGROVE-LEMNOS ROAD, COSGROVE VIC 3631 | 30132664 |  |  |  | Corrosion |  |  |  | Following a supply interruption there was a report of fallen Conductors and a small ground fire at incident location. There was a ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | STN024 | Localised corrosion at helical splice | Grassfire | 43105.1778 | 1 | Small: 10 - 1000 sq.m | 9876 | Roadway |  | 20180522PWA_06 | Infrastructure (network-based) | -36.3475 | 145.5966 | 1 | Powercor | Report | 12149 | 0.0094306 | 22kV AC | Shepparton Airport | 3631 | Cosgrove | Conductor
On arrival crew isolated supply and carried out repairs. | 19-23 HAWKINS STREET, SHEPPARTON VIC 3630 | 32189058 |  |  |  | Leakage |  |  | 1 | Vicfire reported pole fire on Hawkins Street, near Allen Street, Shepparton. Crew attended and found HV Intermediate crossarm had burnt the end of and was laying on LV crossarm of the substation. There was no ground fire, no injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHN012 | Excessive leakage current | Pole-top fire | 43164.975 | 1 | Negligible: no ground fire | 9877 | Roadway |  | 20180522PWA_07 | Infrastructure (network-based) | -36.3541 | 145.4055 | 1 | Powercor | Report | 12150 | 0.0088021 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Crossarm
The attending Powercor Fault Crew re-terminated the existing O/H Twisted Service Cable at the Reticulation Pole and completed an NST Test | 10 MACEDON AVENUE, CORIO VIC 3214 | 30146611 |  |  |  | Corrosion |  |  | 2 | On 28 April real estate agent advised that shocks had been received on 3 January . Tennant was operating an external Garden Tap at the rear of the property when he received an electric shock as he made simultaneous contact with his hand on the metal Tap and his wet bare feet wearing thongs whilst standing on the saturated ground. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded 'Open Circuit' O/H Service Neutral Conductor termination at the Reticulation Pole. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  | FNS012 | Corroded connection | Minor shock | 43160.375 |  |  | 9886 | Residential |  | 20180523PWA_01 | Infrastructure (network-based) | -38.0717 | 144.3716 | 1 | Powercor | Report | 12159 | 0.021429 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
Voltage tests conducted between an independent earth and various parts of the electrical installation recorded a result of 8V under no load and 60V under load. An impedance of 2.6 ohms was recorded on the neutral conductor feeding the installation also, which resulted in failed NST tests. Jemena crew called to investigate the issue further and identified a lose neutral connection at the distributors pole in which the customers overhead service was fed from. Attending crew rectified the problem by re-terminating the loose neutral connection and also tightening the active connection to the installation. Once repairs had been completed the attending L.E.I conducted an NST test and the customers F.O.L.C.B and switchboard, both recording a pass result. The impedance measured on the neutral conductor was now 0.07 ohms and all voltage tests between independent earth and various parts of the electrical installation (including the locations in which the shocks were received) now recorded 0 volts. The installation was left on supply. | 128 THE AVENUE, SPOTSWOOD VIC 3015 |  |  |  |  | Neutral fault |  |  |  | Customer was taking a shower when he received an electric shock as he made simultaneous contact between his hands on the shower taps whilst standing on the wet shower base. Other members of the household had noticed this also over the course of several months. Residents had also noticed dimming/flickering of lights. | Neutral screen | 0 | 0 | 0 |  |  | Loose neutral connection at pole | Minor shock | 24/05/2018 11:08 |  |  | 9910 | Residential |  | 20180524JEM_03 | Infrastructure (network-based) | -37.8259 | 144.8705 | 1 | Jemena | Report | 12183 | 0.024652 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Spotswood | Connection
Crew dispatched to isolate and make safe. Repairs completed and power restored | 1045 PLENTY ROAD, SOUTH MORANG VIC 3752 | LIS 15125256 | Vehicle |  |  |  |  | Three phase |  | IMS 233726 - Vehicle (truck) hit pole and live conductors on vehicle. Truck has backed into pole and insulated HV ABC has come down onto truck. Truck on side of road in construction zone for Mernda Rail | Conductor (insulated) | 0 | 0 | 0 |  |  | Vehicle hit pole. Truck backed into pole and insulated line has come down onto truck. Truck on side of road in construction zone for Mernda Rail. The driver of the tanker advised he was refuelling a light tower on site, which he had done a number of times before, and forgot that there was a pole behind him and reversed into it. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/05/2018 7:29 |  |  | 9921 |  |  | 20180525SPN_01 | Infrastructure (network-based) | -37.6342 | 145.0954 | 1 | AusNet Services Distribution | Report | 12532 | 0.0082755 | 22kV AC | Essendon Airport | 3752 | South Morang | Vehicle
A LEI and faults truck attended and completed a voltage test between an independent earth and the tap and measured 145v. The LEI instructed the faults crew to check the connections at the pole end (LIS No. 1305507) and they identified there was insulation damage on the service neutral conductor of the grey twisted overhead service cable that caused corrosion. The faults crew replaced the damaged service cable with a XLPE type and the LEI measured 2.7v at the rear garden tap and 1.5v at the main switchboard neutral bar. Supply was left on and the occupier advised of rectification work. | 525 DUNDAS STREET, ST ANDREWS BEACH VIC 3941 | 1305507 |  |  |  | Moisture ingress;Corrosion |  | Phase to earth | 2 | Caller reports the lights are dimming but no electric shocks have been received. Access is okay and someone will be in attendance. The occupier initially advised that no electric shocks occurred but later reported that a shock had been received while touching the water tap in the back yard. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | Insulation damage on the service neutral conductor of the grey twisted overhead service cable that caused corrosion. | Minor shock | 26/05/2018 16:30 |  |  | 9934 | Residential |  | 20180528UTD_02 | Infrastructure (network-based) | -38.4142 | 144.8237 | 1 | United Energy Distribution | Report | 12211 | 0.017859 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | St Andrews Beach | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and a Zinfra underground crew promptly attended and commenced repairs under Access Authority conditions. | ELGAR ROAD, BURWOOD VIC 3125 |  | Working too close to underground cables | [5 empty] | 1 | At 0853hrs on 28/05/2018, 22kV feeder EB 21 circuit breaker reclosed to lockout affecting 579 customers. Construction work was being completed at Deakin University and a private underground boring contractor has bored into a HV underground cable off Elgar Road into BH7250 in Deakin University, The company involved was Total Underground who were installing some new water pipes at Deakin University and came into contact with the 22KV live underground cable. No injuries or damage was sustained. The company had Dial Before You Dig plans on site although there wasn't a "No Go Zone" job logged nor a Permit to Work issued and therefore the cable had not been traced or identified before the commencement of work. The companyâ€™s owner is Ben Koutoukidis and contracted Mo from Specialised Fire (0421 462 514) and David from Crewther Plumbing (0418 882 077). Work Safe was contacted with reference number 280518-64-BH-JS provided. Zinfra No Go Zone representatives attended and gathered information and took photos - attached. | Cable | 0 | 0 | 0 |  | EB 21 | An underground boring contractor has bored into a HV underground cable whilst installing new water pipes at Deakin University and contacted the 22KV live underground cable. | Loss of supply;No Go Zone (contact);Damage to network assets | 28/05/2018 8:53 |  |  | 9935 | Construction |  | 20180528UTD_03 | Infrastructure (network-based) | -37.8468 | 145.111 | 1 | United Energy Distribution | Report | 12212 | 0.0074178 | 22kV AC | Moorabbin Airport | 3125 | Burwood | Dug up
On arrival crew isolated supply and carried out repairs. | CALDER HIGHWAY, SEA LAKE VIC 3533 | 32160325 |  |  |  | Leakage |  |  | 1 | A Powercor fault crew attending an outage found a partially burnt pole top. There was no ground fire, no injuries or third party property damage | Pole (wood) | 2 | 2 | 2 |  | OYN005 | excessive leakage current | Pole-top fire | 29/05/2018 15:17 | 1 | Negligible: no ground fire | 9964 | Roadway |  | 20180531PWA_07 | Infrastructure (network-based) | -35.4846 | 142.847 | 1 | Powercor | Report | 12244 | 0.026722 | 22kV AC | Swan Hill Aerodrome | 3533 | Sea Lake | Pole
Police advised and site/apparatus made safe. Installation of cameras for the site are being arranged. | 40 ZAKWELL COURT, COOLAROO VIC 3048 |  | Unauthorised access;Copper theft | [5 empty] | 2 | Unknown persons - unauthorised entry into zone substation Coolaroo (COO) and stole copper. Refer to attached photos. | Copper;Earth | 0 | 0 | 0 |  |  | Theft by unknown persons. | Damage to network assets | 43106.5896 |  |  | 9968 | Commercial |  | 20180601JEM_01 | Infrastructure (network-based) | -37.6424 | 144.9336 | 1 | Jemena | Report | 12248 | 0.039789 | 22kV AC;66kV AC | Essendon Airport | 3048 | Coolaroo | Other
On arrival crew isolated supply and carried out repairs. | 107 LA COTE ROAD, GREENDALE VIC 3341 | 30112192 |  |  |  | Overheated connection |  |  |  | Customer called in to advise transformer is on fire and the fire brigade has been called and are on the way. On arrival the crew has advised that a Three-Phase FOLCB had overheated and burnt out on LV Service Pole. As a result of this, the burnt out FOLCB has fallen onto the ground below. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Connection box | 2 | 2 | 2 |  | BMH003 | Insufficient remains to determine cause | Pole-top fire | 43225.7396 | 1 | Negligible: no ground fire | 9965 | Roadway |  | 20180601PWA_01 | Infrastructure (network-based) | -37.5635 | 144.321 | 1 | Powercor | Report | 12245 | 0.013152 | Low voltage AC (<1kV) | Avalon Airport | 3341 | Greendale | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | 2 WALWA STREET, MITCHAM VIC 3132 | 7029309 |  | Cold |  | Leakage |  |  | 1 | At 1655hrs on 31/05/2018, 22kV feeder RWT 34 circuit breaker reclosed to lockout affecting 3431 customers. A pole fire occurred at HV anchor pole No. LIS 7029309 located in Culwell Avenue on the corner of Walwa Street. The pole was burnt off approximately 1m from the top of the pole and requires replacement. | Pole (wood) | 0 | 0 | 0 |  | RWT 34 | Probable insulator tracking during cool and damp conditions. | Pole-top fire | 31/05/2018 16:55 | 1 | Negligible: no ground fire | 9967 | Roadway |  | 20180601UTD_01 | Infrastructure (network-based) | -37.8232 | 145.212 | 1 | United Energy Distribution | Report | 13070 | 0.03077 | 22kV AC | Moorabbin Airport | 3132 | Mitcham | Pole
A LEI and faults truck attended and completed a voltage test between an independent earth and the water tap to the metallic pipe and recorded 1.9v under no load and 2.7v with load applied. A NST test failed. The faults crew proceeded to check the connections at pole number LIS 3316194 and at the POA. The fault crew reported the neutral connector at the POA was not the suitable type and didn't make a good contact to the neutral conductor. The fault crew replaced the neutral connector and the LEI completed installation tests that confirmed the fault had been rectified with 0.5v measured under no load and full load at the point of contact. | 57 ASTER AVENUE, CARRUM DOWNS VIC 3201 | 3316194 |  |  |  | Defective component |  | Phase to earth | 2 | Business name: Battmans Insulation Services. REC advised that a plumber received a tingle from the metal piping at the property and believes there is a possible neutral fault as there is voltage in the earthing system. A plumber received a slight electric shock to his hand as he was repairing the metallic pipe for the fire hose. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | Incorrect neutral connection installed at the POA. | Minor shock | 29/05/2018 15:00 |  |  | 9969 | Residential |  | 20180601UTD_02 | Infrastructure (customer connection) | -38.0995 | 145.1657 | 1 | United Energy Distribution | Report | 12249 | 0.010743 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Connection
CEOT dispatched a fault crew to attend, make safe and investigate. ES advised. DAO advised. Work Crews attended, repaired and re-sagged HV line and supply restored | 47-51 YANNATHAN ROAD, NYORA VIC 3987 | LIS 2006260 and LIS 2006681 | Crane, excavator or other construction/farming equipment | Within clearances | Highly unlikely |  |  |  | 1 | IMS 233826. An excavator pushed a tree onto HV - Farley Excavations phone 0412 365428. Truck registration RFU 842. | Conductor (bare) | 0 | 0 | 0 |  | LLG12 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43106.4167 |  |  | 9970 |  |  | 20180603SPN_01 | Infrastructure (network-based) | -38.3273 | 145.6705 | 1 | AusNet Services Distribution | Report | 12628 | 0.035525 | 22kV AC | Moorabbin Airport | 3987 | Nyora | Vehicle
Fault crew replaced the neutral screen service | 110 CROSS STREET, WEST FOOTSCRAY VIC 3012 |  |  |  |  | Corrosion |  | Phase to neutral | 1 | Customer received electric shocks from appliances within residence | Aluminium;Neutral screen | 0 | 0 | 0 |  | FW17 | Corroded neutral bar on junction box at pole end and the service. | Minor shock | 43196.9035 |  |  | 9974 | Residential |  | 20180604JEM_01 | Infrastructure (network-based) | -37.8002 | 144.8779 | 1 | Jemena | Report | 12255 | 0.029066 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Connection
Field crews dispatched to location. Conductors isolated to make safe Repairs made to conductor | 19 SPEIGHT STREET, NEWPORT VIC 3015 |  |  | Wind |  | Conductor clashing |  |  | 1 | conductor clashing in Speight St Newport caused white and blue phase LV overhead line conductors to the ground for 3 bays west of Mirls St | Conductor (bare) | 2 | 2 | 2 |  | NT03 | conductor clashing due to wind | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43226.0069 |  |  | 9975 | Industrial |  | 20180605JEM_01 | Infrastructure (network-based) | -37.8429 | 144.8782 | 1 | Jemena | Report | 12256 | 0.035272 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Conductor
CEOT dispatched a fault crew to make safe, investigate and repair. Upon attendance the fault crew found a 6k Boric Acid fuse hung-up and candled. The fault crew replaced the Boric Acid fuse unit. | 100 ALCORN ROAD, LABERTOUCHE VIC 3816 | 2716712 |  |  |  | Candled fuse |  |  |  | IMS 233507. Ref Phase 6k Boric Acid fuse candled at BROWN P002 substation, lis 2716712. No fire had started anywhere else. | Boric acid | 0 | 0 | 0 |  | wgl21 | Candled Boric Acid fuse tube. | Other electricity related | 43378.4194 | 1 | Negligible: no ground fire | 9977 | Agricultural |  | 20180605SPN_02 | Infrastructure (network-based) | -38.0316 | 145.801 | 1 | AusNet Services Distribution | Report | 12258 | 0.024115 | 22kV AC | Morwell (Latrobe Valley Airport) | 3816 | Labertouche | Fuse
CEOT dispatched a fault crew and an AusNet Services' LEI to isolate, make safe and investigate. Please refer to ESV database OSIRIS number 20180604SPN_01 - (IMS 233516) which provides a full detail of the action taken for the previous incident on 10 May 2018. An action from the previous incident on 10 May 2018 was: "Advised AusNet Services' Control Room Foster / Ellis Substation to remain isolated until earthing system is replaced and that a Transformer upgrade is strongly recommended. LEI required to test on completion of rectification works to ensure there are no secondary issues." Further this request the following was actioned on 11 May 2018: a new substation was installed and new LV & HV earths were also installed. Test results: 238 Volts to Earth and 1.5 Volts on Neutral. There are no new records in IMS of any further incidents at this address. | 105 FOREST STREET, YARRA GLEN VIC 3775 | 1006740 |  |  |  | Earth fault |  | Phase to earth |  | IMS 233529. Raelene was doing dishes and received an electric shock from the tap. Please refer to ESV database OSIRIS number 20180604SPN_01 - (IMS 233516) which provides a full detail of the description of the previous incident on 10 May 2018 which did identify the cause, being "the AusNet Services' Operations Control Room advised that the loading on Foster / Ellis Substation was at 156%. The combination of a high resistance earthing system coupled with a heavily loaded Substation caused a voltage rise on the LV neutral." | Pole mounted;Earth/earthing | 0 | 0 | 0 |  | cpk12 | The combination of a high resistance substation earthing system coupled with a heavily loaded substation transformer caused a voltage rise on the LV neutral | Minor shock | 43409.3653 |  |  | 9978 | Residential |  | 20180605SPN_03 | Infrastructure (network-based) | -37.6473 | 145.3802 | 1 | AusNet Services Distribution | Report | 12506 | 0.009022 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Yarra Glen | AF Other
On arrival crew isolated supply and carried out repairs. | 121 HORACE STREET, SEA LAKE VIC 3533 | 31022293 |  |  |  | Leakage |  |  |  | Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate pole failed due to fire damage at the LV kingbolt position, resulting in the pole top assembly being suspended above the LV circuit below. There was no ground fire, no reported injuries, no 3rd party damage | Pole (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 43318.2639 | 1 | Negligible: no ground fire | 9994 | Roadway |  | 20180612PWA_01 | Infrastructure (network-based) | -35.5006 | 142.8495 | 1 | Powercor | Report | 12278 | 0.029089 | 22kV AC | Swan Hill Aerodrome | 3533 | Sea Lake | Pole
On arrival crew isolated supply and carried out repairs | 62 GRANITE HILL LANE, KYNETON VIC 3444 | 30139971 |  |  |  | Mechanical breakdown |  |  |  | Following a report of low voltages A crew attended incident location. On arrival it was found that a conductor had parted at the fargo sleeve and fallen to the ground. Crew confirmed that Fargo auto splice sleeve let go on load side of P10B resulting in load side HV conductor falling to ground. This allowed back feed of the load side conductor to ground via downstream transformers. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WND023 | Conductor parted at sleeve | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43195.2896 |  |  | 10003 | Agricultural |  | 20180613PWA_01 | Infrastructure (network-based) | -37.2298 | 144.4967 | 1 | Powercor | Report | 12291 | 0.026773 | 22kV AC | Wallan (Kilmore Gap) | 3444 | Kyneton | Conductor
On arrival crew isolated supply and carried out repairs. | 14 BOURNBANK AVENUE, BANNOCKBURN VIC 3331 | 34031992 | Working too close to underground cables | [5 empty] | 1 | Contractor rang to advise they had dug up and damaged a cable at the incident location. A crew attended and found the LV U/G main had been dug up and damaged. LV fuses had operated. Customer advises they had completed a dial before you dig request and received plans showing the cable present. A PTW was on issue. Contractor was installing a new gas main. There were no reported shocks, injuries or ground fire start. | Cable | 2 | 2 | 2 |  | GL012 | Excavation works | Loss of supply;No Go Zone (contact) | 27/04/2018 10:34 |  |  | 10004 | Roadway |  | 20180613PWA_02 | Infrastructure (network-based) | -38.054 | 144.1749 | 1 | Powercor | Report | 12292 | 0.0069201 | Low voltage AC (<1kV) | Avalon Airport | 3331 | Bannockburn | Dug up
Crew isolated supply and repaired cable. | 5 CLARKE STREET, SUNSHINE VIC 3020 | 41077321 | Vehicle | [5 empty] | 1 | Customer rang to advise they had damaged a cable using a forklift resulting in the loss of supply to a number of shops. Crew attended and found an LV mains cable had been damaged. Substation LV bus fuses had operated. There was no fire, no reported injuries or third party property damage. | Conductor (insulated) | 2 | 2 | 2 |  | SSE013 | Inadvertent contact with forklift | Loss of supply;Damage to network assets | 29/04/2018 14:58 |  |  | 10005 | Commercial |  | 20180613PWA_03 | Infrastructure (network-based) | -37.7855 | 144.8326 | 1 | Powercor | Report | 12295 | 0.01988 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Vehicle
The Crew isolated supply to make the site safe and allow for repairs to be carried out. | 319-391 LEAKES ROAD, PLUMPTON VIC 3335 | 30138502 | Copper theft | [6 empty] | A customer reported that their house had been burgled, and their meter box vandalized at the incident location. On arrival the crew found that thieves had stolen the customerâ€™s 4 core 50mm LV UG cable which was approx. 110m in length. The crew also reported that there was minor damage to the meter board, but no apparent damage to Powercor assets. The customer stated that the Police were to attend the site, and there was no theft of Powercor equipment. There was no ground fire or any reported injuries. | Customer installation | 2 | 2 | 2 |  | MLN021 | Theft of customer service cable | Loss of supply | 43105.3861 |  |  | 10006 | Residential |  | 20180613PWA_04 | Infrastructure (network-based) | -37.6722 | 144.6635 | 1 | Powercor | Report | 12296 | 0.031203 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Other
The site was made safe and the LV cable and pothead was repaired. | 51 CLAREMONT STREET, SOUTH YARRA VIC 3141 | 30215430 | Working too close to underground cables | [6 empty] | A customer called to say they had a partial outage. On arrival the crew found that a Low Voltage (LV) UG cable had been damaged by an excavator, which resulted in a failed pothead on LIS 35429. The excavating works were taking place to lay storm water drainage for Stonington Council. There were no reported injuries or other third party damage. | Cable | 2 | 2 | 2 |  | R035 | Excavation work | Loss of supply;Damage to network assets | 26/04/2018 23:50 |  |  | 10011 | Roadway |  | 20180614PWA_04 | Infrastructure (network-based) | -37.8364 | 144.9941 | 1 | CitiPower | Report | 12302 | 0.0094861 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Dug up
The site was made safe and repairs were carried out. | 99 STONEHILL DRIVE, MADDINGLEY VIC 3340 | 30344120 | Working too close to underground cables | [6 empty] | Steve from Comdain Infrastructure called to report they had hit a HV conduit with an excavator while doing works to install a water main. These works were under a permit to work. On arrival the crew found that the HV conduit had been creased when they were digging under it to install the water main. There were no reported injuries or other third party damage | Cable | 2 | 2 | 2 |  | BMH003 | Excavation near cable | No Go Zone (contact);Damage to network assets | 43164.5215 |  |  | 10012 | Roadway |  | 20180614PWA_05 | Infrastructure (network-based) | -37.687 | 144.4136 | 1 | Powercor | Report | 12303 | 0.023446 | 22kV AC | Avalon Airport | 3340 | Maddingley | Dug up
On arrival crew arranged isolation of supply and carried out repairs. | 17 CAROLANNE DRIVE, DRYSDALE VIC 3222 | 30547049 | Vehicle | [5 empty] | 1 | At 1:42am supply was lost to approximately 133 customers in the Drysdale area. At 2:26am Police notified Powercor of a vehicle accident with a pole at the incident location. When crews arrived on site they found that Police had cordoned off the area awaiting further investigation by the Vic Police - Major Collision Investigation Unit. Crews contacted their Team Leader to advise that on site Police reports indicate serious injury had occurred to one of the three vehicle occupants and at that stage it was viewed as a potential fatality. A passenger has sustained serious injuries and had been airlifted to Melbourne. At approx. 10am Powercor access was granted to the accident site. Pole and crossarm replacement was required. There was no fire . | Pole (wood) | 2 | 2 | 2 |  | DDL022 | Vehicle incident | Loss of supply;Damage to network assets | 43256.1014 |  |  | 10013 | Roadway |  | 20180614PWA_06 | Infrastructure (network-based) | -38.1707 | 144.569 | 1 | Powercor | Report | 12304 | 0.027985 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Drysdale | Vehicle
The crew reconnected the neutral and tested the light which was then working correctly. | 57 ENTERPRISE CIRCUIT, FRASER RISE VIC 3336 | 30328931 | Vandalism | [6 empty] | A public lighting crew attended a public lighting fault for a light out at the incident location. Upon arrival, the Electrix public lighting fault crew found that the neutral tail in the public lighting column which was feed via an underground pit had been disconnected and taped up in the column and the supply fuse blown. Its believe that an unknown person had interfered with the pole to reduce the lighting in the area. There was no shock, fire or damage to third party property. | Public lighting | 2 | 2 | 2 |  | SA011 | Unknown person disconnected lighting supply | Damage to network assets | 43438.9979 |  |  | 10019 | Roadway |  | 20180615PWA_03 | Infrastructure (network-based) | -37.7134 | 144.7315 | 1 | Powercor | Report | 12312 | 0.031998 | Low voltage AC (<1kV) | Melbourne Airport | 3336 | Fraser Rise | Other
CitiPower worker raised with site manger, crane had completed lift, packed up and departed | 8 CHANDLER HIGHWAY, KEW VIC 3101 | 30162709 | Working too close to overhead lines | [5 empty] | 2 | Citipower worker identified crane operators had blocked the road off to set their crane close to the high voltage cables. Matter raised with crane crew who proceeded to continue encroachment. | Conductor (bare) | 0 | 0 | 0 |  | Q019 | No Go Zone Breach | No Go Zone (no contact) | 15/06/2018 9:10 |  |  | 10020 | Construction |  | 20180615PWA_04 | Infrastructure (network-based) | -37.789 | 145.0262 | 1 | CitiPower | Report | 12314 | 0.011213 | 22kV AC | Essendon Airport | 3101 | Kew | Other
On arrival crew isolated supply and carried out repairs | 58 APPLETON STREET, RICHMOND VIC 3121 | 30184825 |  |  |  | Rot |  |  |  | Customer reported low wires in street and conductor sparking at the incident location. On arrival the crew found that an LV Xarm had broken resulting in conductors hanging low and contacting OPTUS cable on pole. Three premises point of attachments were damaged. There was no ground fire. There were no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | NR021 | crossarm failure | Loss of supply;Damage to network assets | 43409.5035 |  |  | 10021 | Roadway |  | 20180615PWA_05 | Infrastructure (network-based) | -37.8157 | 145.012 | 1 | CitiPower | Report | 12315 | 0.036027 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Crossarm
At the time of attendance the failure mechanism that resulted in the pole becoming live was not known. Fault crew removed service fuse to isolate supply to light to make safe (which resulted on voltage on pole going to 0V) and tagged mains box on pole and logged job for follow up by public lighting. | 336 LA TROBE STREET, MELBOURNE VIC 3000 | 30193752 | Vandalism |  |  | Electrical breakdown;Mechanical breakdown |  | Phase to earth |  | Milan reports receiving an electric shock when he touched the metal tramways pole as he was re-instating bitumen around its base. | Traction lines;Pole (steel) | 2 | 2 | 2 |  | JA042 | Interference - probable contact by plant with date and details unknown | Minor shock | 22/05/2018 20:00 |  |  | 10028 | Roadway |  | 20180618PWA_03 | Infrastructure (network-based) | -37.8107 | 144.9596 | 1 | CitiPower | Report | 12335 | 0.010442 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Connection
On arrival crew isolated supply and carried out repairs. | 50 GAMALITE DRIVE, HARKNESS VIC 3337 | 34030419 | Working too close to underground cables | [5 empty] | 1 | A Powercor fault crew attending an outage (MLN014 feeder) found that an UG HV cable had been contacted by a borer head at the incident location. Protection operated. No fire or injuries reported | Cable | 2 | 2 | 2 |  | MLN014 | Boring operations | No Go Zone (contact);Damage to network assets | 18/06/2018 12:38 |  |  | 10038 |  |  | 20180619PWA_01 | Infrastructure (network-based) | -37.6671 | 144.5637 | 1 | Powercor | Report | 12467 | 0.025454 | 22kV AC | Melbourne Airport | 3337 | Harkness | Dug up
Fault crew dispatched to make safe and repair Conductor repaired and terminations replaced to the correct 7/.064 make offs on pole 2201224. The crew then restored supply. | 79 STAFF ROAD, TANJIL SOUTH VIC 3825 | LIS2201224 |  |  |  | Not built/maintained to design |  |  | 2 | IMS 233939 - Bare LV on ground at pole LIS 2201224 with dead cow found in the vicinity | Conductor (bare) | 0 | 0 | 0 |  | MOE21 | 7/.064 LV copper conductors incorrectly terminated at pole 2201224 with 7/.080 copper make-offs resulting in the conductor slipping through the make-off and falling to the ground | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Fatality of livestock, pet or companion animal | 43440.2625 |  |  | 10042 | Agricultural |  | 20180619SPN_01 | Infrastructure (network-based) | -38.1415 | 146.2503 | 1 | AusNet Services Distribution | Report | 12557 | 0.027299 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Tanjil South | Connection
Site preserved until ESV attended | 104-108 BELLARINE HIGHWAY, NEWCOMB VIC 3219 | 30142490 |  |  |  |  | Inappropriate tools/plant/equipment;Failure to use correct PPE |  | 2 | Employee working on LV supply received serious burns when an electrical flashover occurred. | Disconnector/isolator | 0 | 0 | 0 |  | GLE024 | Short circuit occurring within the FSD | Medical attention (first aid/doctor/hospital) | 22/06/2018 12:30 |  |  | 10047 | Other | health centre | 20180622PWA_01 | Infrastructure (network-based) | -38.1718 | 144.3953 | 1 | Powercor | Report | 12481 | 0.018019 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Newcomb | AF Other
Electrical inspector attended and may the necessary tests and the fault crew replaced the faulty overhead service. | 29 TONGUE STREET, YARRAVILLE VIC 3013 |  |  |  |  | Age;Neutral fault |  |  | 2 | The customer received an electric shock while she was standing bare footed on the wet ground turning on the rear tap when she made simultaneous contact between her left hand on the tap and her bare feet on the wet ground. Jemena ref tbl# 165733 | Service conductor;Aluminium | 0 | 0 | 0 |  |  | broken neutral at service pole end | Minor shock | 23/06/2018 16:51 |  |  | 10048 | Residential |  | 20180624JEM_01 | Infrastructure (network-based) | -37.8119 | 144.8911 | 1 | Jemena | Report | 12483 | 0.027772 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | OH Cable
CLN22 feeder was successfully restored. DAO Peter Lye was informed. | 38 MOROAK CRESCENT, CLYDE NORTH VIC 3978 | LIS 508787 |  | Within clearances |  |  |  |  | 1 | IMS 234091. Fault Crew encountered Tree Clearing Crew while patrolling CLN22 Feeder after lockout. Fault crew was informed that a Tree branch had fallen from the tree while the Tree Clearing crew was working on the other side of a tree. Tree branch was disposed of by Tree Clearing crew. Burn marks found on conductor where Tree branch had allegedly fallen, bay between P#'s 508788 and 508787. Tree Clearing Crew was sub-contractor for Villawood Homes. contact Shannon, Assistant Development manager Mob. 0450 907 914. No damage occurred, no fire occurred, burn marks found on hv conductors | Conductor (bare) | 0 | 0 | 0 |  | CLN22 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/06/2018 9:19 |  |  | 10051 | Agricultural |  | 20180625SPN_01 | Infrastructure (network-based) | -38.115 | 145.347 | 1 | AusNet Services Distribution | Report | 12487 | 0.038701 | 22kV AC | Moorabbin Airport | 3978 | Clyde North | Trees
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern. | 67 BARKLY STREET, MORNINGTON VIC 3931 | 9833531 |  |  |  | Overheated connection |  |  | 2 | Per fire authority - pole fire behind Coles. A 150w HPS lantern on pole No. LIS 9833531 located in Barkly Street caught fire and was attended to by the CFA. | Public lighting | 0 | 0 | 0 |  |  | Probable loose connection overheated. | Pole-top fire | 43440.2826 | 1 | Negligible: no ground fire | 10055 | Roadway |  | 20180626UTD_01 | Infrastructure (network-based) | -38.2206 | 145.0406 | 1 | United Energy Distribution | Report | 13073 | 0.022604 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Connection
Fault crew attended to isolate, make safe and investigate. NST carried out at substation, voltage identified in stay and LV earth. Substation isolated and made safe before LA lead removed and repaired. All tests completed and passed following repair | 695 JACKSONS TRACK, JINDIVICK VIC 3818 | LIS 2718138 |  |  |  | HV injection |  | Phase to earth |  | IMS 233686 customer received electric shock from taps | Surge diverter;Dropper/bridge | 0 | 0 | 0 |  | WGL24 | Blown Lightning Arrestor lead made contact with the bushing cover of the transformer and livening up the LV earth. | Minor shock | 22/05/2018 19:23 |  |  | 10070 |  |  | 20180627SPN_05 | Infrastructure (network-based) | -38.0248 | 145.8629 | 1 | AusNet Services Distribution | Report | 12513 | 0.024274 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3818 | Jindivick | AF Other
The Powercor Fault Crew identified and repaired a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB located at the POA. The attending Powercor Fault Crew re-terminated the existing O/H Service Neutral Conductor at the Customerâ€™s FOLCB and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 73 EDOLS STREET, BALLAN VIC 3342 |  |  |  |  | Corrosion |  | Phase to earth |  | Mrs R Haywood was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | corroded connection | Minor shock | 43378.3542 |  |  | 10074 | Residential |  | 20180629PWA_01 | Infrastructure (customer connection) | -37.6027 | 144.2267 | 1 | Powercor | Report | 12519 | 0.020678 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Connection
The Powercor Fault Crew identified a corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB located at the POA, likely resulting in a higher than normal impedance within the neutral service conductor. An initial voltage measurement at the point of contact was unable to be determined as the corroded O/H Service Neutral Conductor at the new FOLCB had been reterminated prior to the LEI attending site. The attending Powercor Fault Crew replaced the existing O/H Service Cable which was terminated at the Customerâ€™s POA following replacement of the FOLCB by an REC and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 14 WILSON STREET, KYABRAM VIC 3620 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr David Newham was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | corroded connection | Minor shock | 18/05/2018 5:30 |  |  | 10075 | Residential |  | 20180629PWA_02 | Infrastructure (customer connection) | -36.3172 | 145.0389 | 1 | Powercor | Report | 12520 | 0.029601 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Kyabram | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 28 HUTCHESON AVENUE, HIGHTON VIC 3216 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr Nathan Mansour was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Rose and his bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  |  | Corroded cabel | Minor shock | 25/05/2018 7:00 |  |  | 10076 | Residential |  | 20180629PWA_03 | Infrastructure (network-based) | -38.1777 | 144.3214 | 1 | Powercor | Report | 12521 | 0.037352 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | OH Cable
Site made safe. Crew then replaced the strain cross arm, attached and re strung the HV conductors, and restored electricity supply | 1860 NHILL-YANAC ROAD, NHILL VIC 3418 | 32107074 |  |  |  | Leakage |  |  | 1 | Vic Fire reported a transformer on fire at the incident location. On arrival the crew found the end of a 22kV strain crossarm had burned off and HV conductors were on the ground. There was no ground fire. no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 43227.8729 | 1 | Negligible: no ground fire | 10091 | Agricultural |  | 20180706PWA_01 | Infrastructure (network-based) | -36.2506 | 141.5005 | 1 | Powercor | Report | 12544 | 0.040373 | 22kV AC | Horsham Aerodrome | 3418 | Nhill | Crossarm
Fault crew dispatched to investigate, make safe and carry out repairs Fault crew replaced failed fused mains box with a new FOLCB. | 1 WOOLRICH ROAD, OLINDA VIC 3788 | LIS 1309467 |  |  |  | Overheated connection |  |  |  | IMS 234714 - MFB reported fire on pole. Found to be failed fused mains box | Connection box | 0 | 0 | 0 |  | SFS1 | The customer was fed via an old private underground service from pole LIS 1309467 which fed directly into their installation. Loose connections in the fused mains box resulted in pole fire only and no ground fire was present. Fault crew replaced the failed fused mains box with a new FOLCB. Burn marks on the pole and small pieces of plastic on the ground from the burnt out fused mains box but no evidence of ground fire. | Pole-top fire | 43108.3653 | 1 | Negligible: no ground fire | 10281 |  |  | 20180809SPN_02 | Infrastructure (network-based) | -37.8604 | 145.3784 | 2 | AusNet Services Distribution | Report | 12943 | 0.024277 | Low voltage AC (<1kV) | Moorabbin Airport | 3788 | Olinda | Connection
CitiPower linesman repaired the service Neutral & CTA carried out N.S.T & Voltage tests following the repairs and normal results were obtained. | 14 ALBERT STREET, BRUNSWICK EAST VIC 3057 | 30160361 |  |  |  | Corrosion |  | Phase to earth |  | Carl received an electric shock when he simultaneously contacted the metallic tap with one hand and the metallic shower base trap with his foot | Service conductor | 2 | 2 | 2 |  | BK009 | Corroded connection | Minor shock | 43289.6875 |  |  | 10289 | Residential |  | 20180810PWA_03 | Infrastructure (customer connection) | -37.7709 | 144.9802 | 1 | CitiPower | Report | 12800 | 0.027611 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Connection
Supply was isolated to make safe. Krone switch was replaced, pole to pit cabling was replaced. | 10 BULLA ROAD, BULLA VIC 3428 |  | Copper theft | [5 empty] | 2 | Copper theft from krone switch and pole to pit cabling (both from same pole). | Cable;Copper;Circuit breaker | 0 | 0 | 0 |  |  | Copper theft from krone switch and pole to pit cabling by unknown persons. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/08/2018 12:30 |  |  | 10297 |  |  | 20180813JEM_01 | Infrastructure (network-based) | -37.6403 | 144.8143 | 1 | Jemena | Report | 12840 | 0.024884 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
On arrival crew isolated supply and carried out repairs. | 147 JACARANDA STREET, RED CLIFFS VIC 3496 | 31019705 |  |  |  | Leakage |  |  |  | Customer reported conductor laying on crossarm, at incident location. A crew attended and found a previous crossarm fire had occurs at incident location There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 43381.466 | 1 | Negligible: no ground fire | 10304 | Roadway |  | 20180815PWA_03 | Infrastructure (network-based) | -34.3161 | 142.1863 | 1 | Powercor | Report | 12875 | 0.014068 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
On arrival crew isolated supply, extinguished fire and carried out repairs. | 96 WESTGARTH STREET, FITZROY VIC 3065 | 30170306 |  |  |  | Corrosion |  |  |  | A Local resident advised loud explosion on black box attached to pole across the street, then small fire started on the pole. Crew attended to find a small fire burning on an overheated IPC. There was no ground fire, no reported injuries or third party property damage. | Connector/termination | 2 | 2 | 2 |  | CW011 | Overheated connection | Pole-top fire;Damage to network assets | 16/08/2018 18:45 | 1 | Negligible: no ground fire | 10312 | Roadway |  | 20180817PWA_01 | Infrastructure (network-based) | -37.7949 | 144.9796 | 1 | CitiPower | Report | 12886 | 0.0090567 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Connection
On arrival crew isolated supply and carried out repairs. Damage to one house at POA defect notice issued. | 336 DONCASTER ROAD, BALWYN NORTH VIC 3104 | 30222165 | Vehicle | [6 empty] | Renault, registration 1KG-7RO (police have driver's details) has collided with pole LIS 25941 outside 336 Doncaster Road, Balwyn North. Pole is lying across car driver trapped inside. Injured driver later removed from car and has been taken to hospital extent of injuries unknown No fire resulted from this incident. Has media attention reported on radio | Service conductor;Pole (wood) | 2 | 2 | 2 |  | WD031 | Vehicle collision with pole | Loss of supply;Significant disruption to the community;Damage to network assets | 17/08/2018 5:10 |  |  | 10324 | Roadway |  | 20180820PWA_05 | Infrastructure (network-based) | -37.7905 | 145.0979 | 1 | CitiPower | Report | 12904 | 0.023995 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Vehicle
Fault crew dispatched to investigate. Customer service disconnected and customer issued with defect noticed for REC to attend and make repairs | 76 GLYNNS ROAD, NORTH WARRANDYTE VIC 3113 | LIS 1205793 |  | Lightning |  |  |  |  | 2 | IMS 234947 - Customer reports lightning strike to house resulting in damaged switchboard and POA | Service conductor;Switchboard;Connection box;Customer installation | 0 | 0 | 0 |  | RWN26 | Lightning struck the house and damaged circuits at the meter board and point of attachment. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/08/2018 20:40 |  |  | 10322 |  |  | 20180820SPN_03 | Infrastructure (network-based) | -37.7249 | 145.2013 | 2 | AusNet Services Distribution | Report | 13188 | 0.038554 | Low voltage AC (<1kV) | Moorabbin Airport | 3113 | North Warrandyte | Lightning
HV fuses found to have operated at pole LIS 5103090 but no substation fuses were found to have operated. Control Room was notified of possible HV Injection and LEI dispatched to investigate. | 24 DETOUR ROAD, NORTH WANGARATTA VIC 3678 | LIS 5103090 |  | Lightning | [5 empty] | IMS 234943 - HV Injection following suspected lightning strike | Conductor (bare) | 0 | 0 | 0 |  | WN3 | The attending LEI inspected and assessed for suspected HV Injection damage and found evidence of HV injection. The LEI report advised that, due to inclement weather, a lighting strike made contact with the open high voltage line conductor at Detour road, which tracked through the high voltage conductor to Fraser lane. HV fuses found to have operated at pole LIS 5103090 but no substation fuses were found to have operated. No further damage found of AusNet Services assets, only customer appliances affected by lightning strike surge. | HV injection | 18/08/2018 17:59 |  |  | 10325 | Residential |  | 20180820SPN_05 | Infrastructure (network-based) | -36.3282 | 146.3522 | 1 | AusNet Services Distribution | Report | 12906 | 0.0023218 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3678 | North Wangaratta | Lightning