Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a dislodged neutral service conductor at the service pole. he attending service crew reconnected the service neutral to street neutral conductor. The attending LEI performed a NST test on the installation, the test passed. | 13 KLEMKE COURT, GROVEDALE VIC 3216 | 33043710 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Miss Davis was showering when she received an electric shock as she made simultaneous contact between her hand on the shower taps and the wet shower base. | Connector/termination | 2 | 2 | 2 |  | WPD012 | Connection dislodged | Minor shock | 16/08/2018 7:00 |  |  | 10335 | Residential |  | 20180822PWA_02 | Infrastructure (network-based) | -38.2022 | 144.3265 | 1 | Powercor | Report | 12917 | 0.024463 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Grovedale | Connection
Section was isolated to make safe. Repairs were undertaken to restore supply and re-instate damaged conductor. Work practices team investigated. | 65 HILLVIEW ROAD, GREENVALE VIC 3059 |  | Working too close to overhead lines |  |  |  | Not followed |  | 1 | Excavator (belonging to a tree clearing company) brought down a LV mains overhead conductor during the course of work. Note: excavator operator contact information as well as company contact information in '6. Other information sources' | Conductor (bare) | 0 | 0 | 0 |  |  | Private excavator contacted a LV overhead conductor whilst moving from one work site to another (crossing road), bringing it down. After investigating it was found that: - The work party did not have No Go Zone VESI Permit - The work party had failed to comply with Safe Approach Distances (SAD) - No spotter appointed while moving plant under power lines | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/08/2018 23:00 |  |  | 10340 | Roadway |  | 20180823JEM_01 | Infrastructure (network-based) | -37.6293 | 144.8866 | 1 | Jemena | Report | 12925 | 0.0020405 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Vehicle
Crew isolated both the LV and 11kV conductors and made repairs. | 206 MITCHELL STREET, NORTHCOTE VIC 3070 | 30192169 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customers report a truck with crane still in raised position has pulled down wires in Mitchell st. A crew attended and found a crane truck had pulled down lv conductors on the cnr of Mitchell and French Ave, Northcote. The LV conductors contacted the Citipower 11kV and Jemena 22kV conductors causing a reclose of the NC006 feeder CB. The neutral and white phase LV conductor broke and fell to the ground. No HV conductor broke and remained aloft. | Conductor (bare) | 0 | 0 | 0 |  | NC002 | interference crane truck contacted overhead line/s | Loss of supply;Damage to network assets | 23/08/2018 12:30 |  |  | 10350 | Roadway |  | 20180828PWA_02 | Infrastructure (network-based) | -37.7738 | 145.0133 | 1 | CitiPower | Report | 13005 | 0.038132 | Low voltage AC (<1kV);11kV AC;22kV AC | Essendon Airport | 3070 | Northcote | Vehicle
Crew attended and will be replacing Service Pit | 12 QUAIL DRIVE, LARA VIC 3212 | 60199932 | Working too close to underground cables | [5 empty] | 2 | 3rd party moved service pit exposing LV cable. | Services pit | 0 | 0 | 0 |  | FNS012 | Interference by persons unknown | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/08/2018 12:00 |  |  | 10355 | Residential |  | 20180828PWA_04 | Infrastructure (network-based) | -38.0132 | 144.4092 | 1 | Powercor | Report | 13011 | 0.028616 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Other
Emergency high voltage switching was completed and the capacitor bank was isolated the following day by opening the vacuum switches and the HV fuses with the use of a load buster. | 56 CLEELAND STREET, DANDENONG VIC 3175 | 637203 |  |  |  | Age;Candled fuse |  |  | 2 | Caller advised power lines were on fire and are now out - fire authority are attending. The centre phase HV fuse at Capacitor Bank "Cleeland-McFarland" located at pole No. LIS 37203 outside 56 Cleeland Street candled due to the centre phase HV dropper burning off at the older style vacuum switch. | Powder filled | 0 | 0 | 0 |  | LD 07 | Possible deteriorated connection to the HV fuse unit. | Pole-top fire | 17/08/2018 19:30 | 1 | Negligible: no ground fire | 10347 |  |  | 20180828UTD_01 | Infrastructure (network-based) | -37.982 | 145.2153 | 1 | United Energy Distribution | Report | 17511 | 0.0085162 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Connection
Fault crew dispatched to make safe and investigate | 19 GARIBALDI STREET, TRARALGON VIC 3844 | LIS 2603531 |  |  |  | Defective component |  |  |  | IMS 235112 - Pole fire reported | Connection box | 0 | 0 | 0 |  | TGN43 | The middle phase of the FSD unit has overheated and melted. Cause could not be determined. Melted plastic observed at the base of the pole but no evidence of fire | Pole-top fire | 30/08/2018 17:57 | 1 | Negligible: no ground fire | 10372 | Residential |  | 20180903SPN_06 | Infrastructure (network-based) | -38.1996 | 146.5254 | 1 | AusNet Services Distribution | Report | 13099 | 0.0027188 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Fuse
Fault Crew Dispatched. On arrival Site made safe for emergency authorities to access. Management advised, DAO advised and attended, ESV advised and attended. Incd # 10403103 | 170 MILNERS ROAD, LANG LANG EAST VIC 3984 | LIS 513752 and LIS 572849 | Working too close to overhead lines;Unauthorised access |  |  |  |  | Phase to earth | 1 | IMS 235140 - Customer was felling trees on his property when a tree fell in the wrong direction and came into contact with the HV line resulting in electrocution | Conductor (bare) | 0 | 0 | 0 |  | LLG11 | Vegetation: Trees Incident | Electrocution | 31/08/2018 16:44 |  |  | 10375 | Agricultural |  | 20180904SPN_01 | Infrastructure (network-based) | -38.2596 | 145.633 | 1 | AusNet Services Distribution | Report | 13394 | 0.023005 | 22kV AC | Moorabbin Airport | 3984 | Lang Lang East | Trees
On arrival crew isolated supply. conductor examined , no damage found | SOUTH BOUNDARY ROAD, KYABRAM VIC 3620 | 32188249 | Working too close to overhead lines | [5 empty] | 1 | While carrying out orchard farm work an excavator made contact with overhear 22kv conductors . The operator was not onsite when crew arrived. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | KYM003 | Farm excavation work | Loss of supply;No Go Zone (contact) | 43199.5958 |  |  | 10379 | Agricultural |  | 20180905PWA_01 | Infrastructure (network-based) | -36.3278 | 145.0743 | 1 | Powercor | Report | 13109 | 0.0029664 | 22kV AC | Shepparton Airport | 3620 | Kyabram | Vehicle
On arrival crew isolated supply and carried out repairs. | 1286 DOHERTYS ROAD, TARNEIT VIC 3029 | 32164866 | Vandalism;Copper theft | [6 empty] | Crew noticed stolen earths on pole at incident location. Thieves have stolen copper and destroyed lv underground cable and tx krone box. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | TNA023 | Vandalism and copper theft | Loss of supply;Damage to network assets | 43140.5833 |  |  | 10399 |  |  | 20180910PWA_04 | Infrastructure (network-based) | -37.816 | 144.6631 | 1 | Powercor | Report | 13140 | 0.025834 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Crew confirmed site safe, cable to be replaced when building ready for connection to supply. | 21 AVENUE ATHOL, CANTERBURY VIC 3126 | 30178086 | Copper theft | [6 empty] | Builder reported cable between pole to pit missing. crew attended and found copper U/G cable between pole and pit stolen. Damage to cable guards and conduit at pole end. Cable not energized at time of theft. Building awaiting completion before connection. Reported to police. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | L013 | Cable theft | Damage to network assets | 43290.334 |  |  | 10404 | Roadway |  | 20180911PWA_01 | Infrastructure (network-based) | -37.8191 | 145.0679 | 1 | CitiPower | Report | 13145 | 0.0090127 | Low voltage AC (<1kV) | Moorabbin Airport | 3126 | Canterbury | Other
On arrival crew confirmed site safe. Arrangements mad for replacement ACR unit. | 48 OLD WESTERN HIGHWAY, MELTON WEST VIC 3337 | 30111809 | Vandalism;Theft | [6 empty] | Powercor employee reported theft of pole mounted ACR. The ACR had been recently been erected and was yet to commissioned into service. It appears that a winch may have been used to remove the ACR from the Pole, with the mounting bolts being removed from pole and bent. The ACR Mounting bracket was left on the ground approximately 10m from the pole, there where vehicle track marks evident. THjere was no reported fire, no reported injuries or evidence of third party property damage. | Any other type | 2 | 2 | 2 |  | MLN022 | Theft | Damage to network assets | 43321.4604 |  |  | 10406 | Roadway |  | 20180911PWA_03 | Infrastructure (network-based) | -37.6862 | 144.5291 | 1 | Powercor | Report | 13147 | 0.019212 | 22kV AC | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and carried out repairs. LEI attended to check for HVI | 38-40 HARVESTER AVENUE, SUNSHINE NORTH VIC 3020 | 32177687 | Vehicle | [5 empty] | 1 | Following ACR trip to lockout a section of SSE032 feeder was patrolled. A vehicle has collided with a pole outside 38 Harvester rd Sunshine North. The resultant impact to this pole has caused the road-side and centre-phase 22kV conductors to break at the full tension sleeves approx. 2.0m west of the pole. HVI suspected. There was no fire reported. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SSE032 | Car struck pole | Loss of supply | 43352.7771 |  |  | 10410 | Roadway |  | 20180911PWA_04 | Infrastructure (network-based) | -37.7607 | 144.8372 | 1 | Powercor | Report | 13153 | 0.035481 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Vehicle
LEI dispatched to investigate Customer reportedly felt a shock from his TV sometime in the last 2 weeks. Spoke to REC who recommended calling the distributor. | 18 ESMOND STREET, WANGARATTA VIC 3677 | LIS5107041 |  |  |  | Mechanical breakdown |  | Phase to earth |  | E0000966 - Customer called to report an electric shock when touching TV aerial. | Service conductor | 0 | 0 | 0 |  | WN4 | LEI dispatched to site to investigate. Site passed NST test. Neutral volts were measured at 2.9Volts at a full house load of 38 Amps.. Some burning marks were noted on the neutral screen cable roller end above the POA where the cable had been rubbing on the building fascia. Overhead service was replaced with black twisted service and POA dropped to stop rubbing on building fascia. Tests carried out and passed at meter panel and MSB. | Minor shock | 43382.4514 |  |  | 10407 | Residential |  | 20180911SPN_01 | Infrastructure (network-based) | -36.3483 | 146.2973 | 2 | AusNet Services Distribution | Report | 13313 | 0.014285 | Low voltage AC (<1kV) | Wangaratta Aero | 3677 | Wangaratta | OH Cable
Fault truck dispatched and assessed the site. Determined HV conductor clearance adequate and no damage to 3/12 conductor. Internal action created to follow up with Tip truck driver regarding No go zone requirements. | 72B CAMMS ROAD, DENISON VIC 3858 | LIS2509154; LIS2510003 | Vehicle | [5 empty] | 1 | E0000679 - Truck contacted overhead HV conductor whilst in a tipping motion resulting in HV fuse and ACR operation | Conductor (bare) | 0 | 0 | 0 |  | MFA32 | Truck contacted overhead HV conductor and fault truck dispatched. Protection operated as designed, no one injured and no damage to assets. Truck Registration number 1EA 3RB | No Go Zone (contact) | 43199.1576 |  |  | 10409 | Agricultural |  | 20180911SPN_03 | Infrastructure (network-based) | -38.0151 | 146.8447 | 2 | AusNet Services Distribution | Report | 13154 | 0.024558 | 22kV AC | Morwell (Latrobe Valley Airport) | 3858 | Denison | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination located at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Service Cable between the Reticulation Pole and the Customerâ€™s POA and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 38 GLADSTONE STREET, WARRNAMBOOL VIC 3280 | 30350978 |  |  |  | Corrosion |  | Phase to earth |  | Mr Troy Rainbow was standing in front of the Main Switchboard and Meter Enclosure investigating dim lights at the property when he received an electric shock as he made simultaneous contact between his hand on the metal Meter Enclosure and his bare feet while standing on the damp concrete path. | Service conductor | 2 | 2 | 2 |  | WBL012 | Corroded connection | Minor shock | 29/08/2018 0:00 |  |  | 10414 | Residential |  | 20180912PWA_01 | Infrastructure (network-based) | -38.3925 | 142.5052 | 1 | Powercor | Report | 13159 | 0.017495 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
A LEI and faults truck attended and performed a series of tests to ensure the integrity of the electrical installation. A NST was completed that passed with 0.3ohms and 2.4v measured on the taps in the house to an independent earth with a 13amp load applied. The faults crew checked connections at the house and pole ends and identified the aluminium to copper crimp connection had exposed bare aluminium that was susceptible to moisture ingress inside the connection that could have caused deterioration via corrosion. The connections at the POA were re-terminated along with the cleaning and greasing of connections at the pole end. The LEI re-tested the installation that confirmed the fault had been rectified and supply was left on. | 9 LANTANA COURT, FRANKSTON VIC 3199 | 3317188 |  |  |  | Corrosion;Defective component | Poor workmanship | Phase to earth | 2 | Caller reports of receiving shocks from every tap and fixture in the house. Lights also flicker and the issue has been occurring for about 1 year and is progressively getting worse. The occupier will not be home after 3.00PM. The occupier advised the United Energy faults and emergencies call centre that tingles have been received from all taps in the house and have also noticed the lights dimming, This has apparently been happening for the last year, but they have not experienced any tingles in the last few months. | Aluminium twisted (XLPE);Connector/termination | 0 | 0 | 0 |  |  | The faults crew checked connections at the house and pole ends and identified the aluminium to copper crimp connection had exposed bare aluminium that was susceptible to moisture ingress inside the connection that could have caused deterioration via corrosion. The connections at the POA were re-terminated along with the cleaning and greasing of connections at the pole end. | Minor shock | 43229.4479 |  |  | 10429 | Residential |  | 20180916UTD_01 | Infrastructure (customer connection) | -38.1388 | 145.1541 | 1 | United Energy Distribution | Report | 13180 | 0.02798 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 12 LUMEAH ROAD, CAULFIELD NORTH VIC 3161 | 2302832 |  |  |  | Fatigue |  |  | 1 | At 2225hrs on 05/09/2018, 11kV feeder EL 07 circuit breaker successfully reclosed and held. Residents in the area reported hearing an explosion. A HV strain crossarm with HV isolators (OA 7010 Lumeah Road) broke and the white and blue phase blades fell and were in close proximity to the LV conductors with visible evidence of conductors clashing at pole No. LIS 2302832. The faults crew requested that a LEI attend to investigate as a HVI was suspected to customers supplied from "Lumeah-Glen Eira" substation. The LEI confirmed a high voltage injection occurred (KEY 1804) affecting customers connected to the LV blue phase conductor that sustained minor damage to electrical equipment and appliances. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | El 07 | Broken HV strain crossarm. | HV injection | 43229.934 |  |  | 10430 | Residential |  | 20180916UTD_02 | Infrastructure (network-based) | -37.8784 | 145.0137 | 1 | United Energy Distribution | Report | 13181 | 0.018806 | 11kV AC | Moorabbin Airport | 3161 | Caulfield North | Crossarm
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern with traffic control required. | 732 DONCASTER ROAD, DONCASTER VIC 3108 | 7061755 |  |  |  | Defective component;Overheated connection |  |  | 2 | Per Fire Authority - pole fire at pole number 7061755 in Doncaster Road. A 150w HPS lantern on pole No. LIS 7061755 located outside 732 Doncaster Road caught fire and was found to be burnt out and requiring replacement. | Public lighting | 0 | 0 | 0 |  |  | A probable loose connection that overheated. | Pole-top fire | 43290.784 | 1 | Negligible: no ground fire | 10432 | Roadway |  | 20180916UTD_04 | Infrastructure (network-based) | -37.7871 | 145.1344 | 1 | United Energy Distribution | Report | 13183 | 0.019653 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | Connection
On arrival crew isolated supply and carried out repairs. | HUDSONS HOTEL, 110 INGLIS STREET, BALLAN VIC 3342 | 30329039 | Vehicle | [5 empty] | 1 | Vic Fire reported that aq truck had brought down wires at the corner of Inglis and Stead streets . The wires are still draped over the truck and sparking. The driver is still in the vehicle. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BMH003 | Truck brushed pole | Loss of supply;Damage to network assets | 13/09/2018 17:24 |  |  | 10446 | Roadway |  | 20180919PWA_03 | Infrastructure (network-based) | -37.6001 | 144.228 | 1 | Powercor | Report | 13213 | 0.016169 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Vehicle
Isolated cables to make safe. Crew replaced damaged krone switch & mains box. | 110 MOMMSENS ROAD, CLARKEFIELD VIC 3430 |  | Copper theft | [5 empty] | 2 | Copper theft from pole to pit and damage to pole assets. | Copper;Circuit breaker;Earth/earthing | 0 | 0 | 2 |  |  | Copper theft by unknown person/s | Damage to network assets | 21/09/2018 15:00 |  |  | 10451 | Agricultural |  | 20180921JEM_01 | Infrastructure (network-based) | -37.5118 | 144.8397 | 1 | Jemena | Report | 13218 | 0.018579 | Low voltage AC (<1kV) | Melbourne Airport | 3430 | Clarkefield | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded (Open Circuit) O/H Neutral Service Conductor at the Customer's Two Point Mains Connection Box located at the POA. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 38 CAMBRIDGE STREET, BELMONT VIC 3216 | 30061811 |  |  |  | Corrosion |  | Phase to earth |  | Mr Ben Meadows was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GCY023 | Corroded connection | Minor shock | 15/09/2018 14:00 |  |  | 10455 | Residential |  | 20180925PWA_02 | Infrastructure (customer connection) | -38.1778 | 144.3378 | 1 | Powercor | Report | 13222 | 0.031458 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
On arrival crew isolated supply and carried out repairs . | 480 LYGON STREET, CARLTON VIC 3053 | 33111446 | Working too close to underground cables | [5 empty] | 1 | Report from Dept of Human Services that a plumber working at a block of units has cut though and damaged wiring in switch room while installing new sewer main. A crew attended and found plumber had cut through Powercor LV U/G mains in switch room. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BQ051 | Excavation works for plumbing | Loss of supply;No Go Zone (contact) | 14/09/2018 11:40 |  |  | 10457 | Commercial |  | 20180925PWA_04 | Infrastructure (network-based) | -37.7948 | 144.9689 | 1 | CitiPower | Report | 13224 | 0.033626 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Dug up
On arrival crew carried out repairs. | 267 GARRARDS LANE, MYRNIONG VIC 3341 | 33076944 | Copper theft | [6 empty] | Report received of copper theft at incident location. There was no reported fire, no injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BMH003 | Theft | Damage to network assets | 19/09/2018 14:54 |  |  | 10463 | Roadway |  | 20180927PWA_01 | Infrastructure (network-based) | -37.6255 | 144.3252 | 1 | Powercor | Report | 13233 | 0.039848 | Earthing cable | Avalon Airport | 3341 | Myrniong | Other
Emergency high voltage switching was completed and the repairs were completed under Access Authority conditions prior to supply being restored. | 2150 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 | 1314698 |  | Prone to salt deposition |  | Corrosion |  |  |  | Per CFA - pole fire near the corner of Boyds Road and Mornington-Flinders Road. At pole number LIS 1314698, a pole fire occurred caused by a burnt out HV fuse unit and lead at "Mtn Flinders - P10 Boyd" single phase pole substation. The 50kVA transformer also required replacement that supplied two customers. | EDO fuse;Transformer | 0 | 1 | 0 |  | DMA 23 | Probable deteriorated and corroded connection due to the pole type substation location near Bass Straight. | Pole-top fire | 43381.7646 | 1 | Negligible: no ground fire | 10468 | Residential |  | 20180929UTD_01 | Infrastructure (network-based) | -38.4571 | 144.99 | 1 | United Energy Distribution | Report | 18392 | 0.038573 | 22kV AC | Moorabbin Airport | 3929 | Flinders | Connection
The LV pillar in the URD was extensively damaged and required replacement. The LV circuit was made safe and the LV CHP bridges on the corner of Jolimont Avenue and Jacksons Road were lifted to minimise the number of customers affected. A Zinfra underground crew replaced the LV pillar and supply was restored upon completion. | 27 JOLIMONT AVENUE, MULGRAVE VIC 3170 |  | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customers supplied from the north circuit of "Chelsea-Jolimont" substation advised of a loss of their electricity supply. During construction activities, a LV pillar has been damaged by an excavator completing work for Melbourne District Demolitions - Phone 03 9448 8056. No injuries or damage to plant was sustained. | Cable;LV Pillar | 0 | 0 | 0 |  |  | An excavator made contact with a LV underground cable. | Damage to network assets | 43413.441 |  |  | 10470 | Residential |  | 20180929UTD_03 | Infrastructure (network-based) | -37.9353 | 145.1966 | 1 | United Energy Distribution | Report | 13244 | 0.023431 | Low voltage AC (<1kV) | Moorabbin Airport | 3170 | Mulgrave | Dug up
A faults truck attended and made the site safe. A glove and barrier crew were requested to attend to repair the failed connection and restrain the HV conductors to enable the restoration of supply to three transformers with customer left off supply. Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. | HOTHAM STREET, ELSTERNWICK VIC 3185 | 2306611 |  |  |  | Electrical breakdown |  |  | 1 | At 1016hrs on 12/09/2018, 11kV feeder EW 08 circuit breaker reclosed to lockout affecting 738 customers. A HV bridge was blown at the HV anchor pole located in Hotham Street at the corner of Hotham Grove caused by probable fault current following a HV underground cable fault ex OA2075. This connection failure caused molten metal from pole No. LIS 2306611 to fall into the grass below and a small fire to occur. | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | EW 08 | The cause was due to a HV underground cable fault. | Grassfire | 43443.4278 | 1 | Localised: less than 10 sq.m | 10474 | Residential |  | 20181001UTD_02 | Infrastructure (network-based) | -37.8802 | 144.9973 | 1 | United Energy Distribution | Report | 13248 | 0.0069317 | 11kV AC | Moorabbin Airport | 3185 | Elsternwick | UG Cable
On arrival crew isolated supply and carried out repairs. LEI attended HVI | 107 MILLERS ROAD, ALTONA NORTH VIC 3025 | 30104758 | Vehicle | [6 empty] | NAO received a report that customer at 107 Millers road Altona north, had been affected by a HV injection that occurred as a result of a vehicle hitting a pole at the corner of Millers road and Duosa road. On arrival the crew found that, due to the vehicle impact, the HV insulators were damaged and the HV conductors on the pole fell on top of the LV. There was a HV injection which affected the customer at #107 only. There was no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | BLT023 | Vehicle accident | HV injection;Loss of supply;Damage to network assets | 30/09/2018 6:05 |  |  | 10482 | Roadway |  | 20181002PWA_01 | Infrastructure (network-based) | -37.8272 | 144.8488 | 1 | Powercor | Report | 13263 | 0.0078588 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3025 | Altona North | Vehicle
On arrival crew isolated supply and carried out repairs. | 193-295 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 30293002 | Copper theft | [6 empty] | A contractor working near incident location reported the theft of copper public lighting cable. The thieves had opened a number of pits and removed the public lighting cable between them. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft | Damage to network assets | 24/09/2018 21:30 |  |  | 10487 | Roadway |  | 20181002PWA_04 | Infrastructure (network-based) | -37.6991 | 144.5424 | 1 | Powercor | Report | 13268 | 0.038641 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
A faults crew attended and placed the substation under LV parallel prior to replacing the white phase HV fuse. LV parallels were removed upon the fuse replacement and supply restored to normal for customers supplied from "Millgrove-George" substation. | 31 WESTBURN GROVE, SCORESBY VIC 3179 |  |  |  |  | Candled fuse | Poor workmanship |  |  | Passerby states wires at the top of the pole are arcing and sparking. The sparks are not making the ground and the electricity supply does not appear to be affected. A 22kV 16amp HV powder filled fuse candled at "Millgrove-George" pole type substation. The cause was attributed to the HV fuse unit not being properly closed. | Powder filled | 0 | 0 | 0 |  | MGE 21 | The cause was attributed to the HV fuse unit not being properly closed. | Pole-top fire | 27/09/2018 19:54 | 1 | Negligible: no ground fire | 10488 | Roadway |  | 20181002UTD_03 | Infrastructure (network-based) | -37.8891 | 145.2204 | 1 | United Energy Distribution | Report | 13269 | 0.030051 | 22kV AC | Moorabbin Airport | 3179 | Scoresby | Fuse
Site made safe and repairs conducted. | RIVERVIEW CLELAND, 445 OLD SYDNEY ROAD, BEVERIDGE VIC 3753 |  | Copper theft | [5 empty] | 2 | Crew attended site to repair after a call from the control room. The crew identified that the outage was a result of attempted copper theft. | Copper;Earth/earthing | 2 | 2 | 2 |  |  | Person unknown tried to steal copper assets from pole. | Damage to network assets | 43141.6458 |  |  | 10498 | Agricultural |  | 20181003JEM_01 | Infrastructure (network-based) | -37.4977 | 144.9045 | 1 | Jemena | Report | 13282 | 0.031925 | Low voltage AC (<1kV);Earthing cable | Wallan (Kilmore Gap) | 3753 | Beveridge | Other
On arrival crew isolated supply and carried out repairs. | 6738 NORTHERN HIGHWAY, ROCHESTER VIC 3561 | 30123594 | Vehicle | [6 empty] | Customer reports an unknown vehicle has pulled down service line at incident location. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | SHP012 | Vehicle struck service | Loss of supply;Damage to network assets | 25/09/2018 9:25 |  |  | 10491 | Roadway |  | 20181003PWA_01 | Infrastructure (network-based) | -36.3259 | 144.6879 | 1 | Powercor | Report | 13273 | 0.011096 | Low voltage AC (<1kV) | Bendigo Airport | 3561 | Rochester | Vehicle
Fault crew dispatched to repair | 9 HUME LANE, MOUNT DANDENONG VIC 3767 | LIS1304258 |  | Within clearances | [5 empty] | E0002471 - Tree clearer dropped a tree through 6.6KV HV ABC | Conductor (ABC) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43110.6042 |  |  | 10510 |  |  | 20181005SPN_02 | Infrastructure (network-based) | -37.8357 | 145.3579 | 2 | AusNet Services Distribution | Report | 13405 | 0.0068125 | 6.6kV AC | Moorabbin Airport | 3767 | Mount Dandenong | Trees
On arrival crew inspected damage and arranged repairs. | 141-159 DOHERTYS ROAD, ALTONA NORTH VIC 3025 | 33076030 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | A concrete pumping truck at the above incident location contacted a 66 kV line. The line reclosed. There was minor damage to the conductors. Some damages to the mixer and pumping truck have been observed. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BLTS-LVN | Concrete pumper | No Go Zone (contact);Damage to network assets | 43322.4097 |  |  | 10515 | Construction |  | 20181008PWA_03 | Infrastructure (network-based) | -37.8309 | 144.8148 | 1 | Powercor | Report | 13335 | 0.027971 | 66kV AC | Laverton Raaf | 3025 | Altona North | Vehicle
Supply isolated to make safe. Crew attended to replace burnt out public lighting luminaire | 35 VICTORIA STREET, PRESTON VIC 3072 | A078208 |  |  |  | Defective component |  |  | 2 | Public lighting luminaire high pressure sodium (HPS) fire No photo is available for this incident | Public lighting | 0 | 0 | 0 |  | EP37 | Public lighting luminaire high pressure sodium (HPS) failure | Other electricity related | 43229.0451 | 1 | Negligible: no ground fire | 10516 | Residential |  | 20181009JEM_01 | Infrastructure (network-based) | -37.7503 | 145.0161 | 1 | Jemena | Report | 17839 | 0.016081 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | AF Other
Site made safe and coordinated repairs. Reported that the customers REC will undertake repairs to bring adjacent building back on supply. | 87-105 RACECOURSE ROAD, NORTH MELBOURNE VIC 3051 | 33111375 | Vandalism;Copper theft | [6 empty] | Following reports of no supply around incident location an employee was dispatched to investigate fault at 95 Racecourse Road Substation. On site the employeeer heard noise in the substation room. Police where contacted who arrived on site. Persons that allegedly broke vandalized and stole from Substation are unknown at this point as they left the site before the police could question them. There was damage to vents and a broken sub door lock. The LV switch to supply the adjacent building was opened and copper was removed. -The HV breaker was opened however no copper was taken from the HV side. There was no fire, no reported injuries. | Indoor | 2 | 2 | 2 |  | LS020 | Vandalism & copper theft | Loss of supply;Significant disruption to the community;Damage to network assets | 30/09/2018 22:36 |  |  | 10517 | Commercial |  | 20181009PWA_01 | Infrastructure (network-based) | -37.7893 | 144.9385 | 1 | CitiPower | Report | 13312 | 0.031863 | Low voltage AC (<1kV);6.6kV AC | Essendon Airport | 3051 | North Melbourne | Other
On arrival crew isolated supply and carried out repairs | 482 MAUDE-SHE OAKS ROAD, MAUDE VIC 3331 | 30070761 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | An excavator hit power pole resulting clashing conductors in side the quarry near the incident location. Upon arrival the crew found that the broken conductors had fallen to the ground resulting in a small grass fire. CFA attended the site. There were no reported injuries or third party property damage. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | GL015 | Excavator struck pole | Grassfire | 43322.4049 | 1 | Small: 10 - 1000 sq.m | 10518 | Industrial |  | 20181009PWA_02 | Infrastructure (network-based) | -37.9271 | 144.1565 | 1 | Powercor | Report | 13314 | 0.020378 | 22kV AC | Avalon Airport | 3331 | Maude | Vehicle
Site isolated to make safe. Repairs were conducted and transformer was replaced. | 75 WHITES LANE, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Theft of pole to pit LV cable (Copper Theft), pole top transformer also damaged from theft and required replacing. | Cable;Copper;Pole mounted | 2 | 2 | 2 |  |  | Vandals stole pole to pit cable, damaging pole top transformer in the process. | Loss of supply;Damage to network assets | 43383.6799 |  |  | 10522 | Roadway |  | 20181010JEM_01 | Infrastructure (network-based) | -37.5861 | 144.8908 | 1 | Jemena | Report | 13322 | 0.027337 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
On arrival crew isolated supply and carried out repairs. | TUKI RETREAT, 60 STONEY RISES ROAD, SMEATON VIC 3364 | 30000141 |  |  |  | Corrosion |  |  |  | An employ of Tuki Trout farm phoned in to report fire on the substation pole which supplies the trout farm. Crew attended to find a burnt out low voltage junction box, fire had self extinguished. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAN009 | Overheated connection | Pole-top fire | 43444.5229 | 1 | Negligible: no ground fire | 10530 | Commercial |  | 20181012PWA_02 | Infrastructure (network-based) | -37.2481 | 143.96 | 1 | Powercor | Report | 13332 | 0.039233 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3364 | Smeaton | Connection
On arrival crew isolated supply and carried out repairs | DARLINGTON-TERANG ROAD, DARLINGTON VIC 3271 | 32061134 | Manned aircraft | [5 empty] | 1 | A report was received about a helicopter hitting power-lines at the incident location. On arrival the fault crew found that a helicopter (Rego: VH-HJT) involved in tree spraying operations, had struck the single phase 22kV conductors, causing both conductors to fall to the ground. The pilot was taken to hospital with lacerations to his legs,. There were no other injuries reported. There was no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | TRG002 | Helicopter struck conductors | Loss of supply;Medical attention (first aid/doctor/hospital);Damage to network assets | 13/10/2018 8:00 |  |  | 10533 | Agricultural |  | 20181015PWA_02 | Infrastructure (network-based) | -38.0285 | 143.0002 | 1 | Powercor | Report | 13336 | 0.00038079 | 22kV AC | Warrnambool Airport Ndb | 3271 | Darlington | Vehicle
On arrival crew isolated supply and carried out repairs. | 318 HIGH STREET, MELTON VIC 3337 | 30102707 |  |  |  | Corrosion |  |  |  | Customer, from 298 High street Melton, reported a pole fire at the incident location. On arrival the crew found that an Low Voltage Insulated Piercing Connectors (IPC) had overheated resulting in burning of the IPC and the LV ABC bridge into the krone box. There was a small fire on the pole but had self-extinguished. There was no reported injuries or third party property damage. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | MLN023 | Overheated connection | Pole-top fire;Loss of supply | 43200.7736 | 1 | Negligible: no ground fire | 10536 | Roadway |  | 20181015PWA_04 | Infrastructure (network-based) | -37.683 | 144.5833 | 1 | Powercor | Report | 13340 | 0.03833 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
Site made safe and service replaced. | 6 MONMOUTH STREET, AVONDALE HEIGHTS VIC 3034 |  |  |  |  | Age;Corrosion |  |  | 2 | Service to 6 Monmouth St Avondale Heights failed at house end, was live on ground across a road when crew arrived | Service conductor;Neutral screen | 0 | 0 | 0 |  |  | Live LV wire on ground due to failure of neutral screened service from age / corrosion. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/10/2018 21:22 |  |  | 10543 | Residential |  | 20181016JEM_02 | Infrastructure (network-based) | -37.7624 | 144.857 | 1 | Jemena | Report | 13350 | 0.0045602 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | Conductor
On arrival crew isolated supply and carried out repairs. | 690 INVERGORDON ROAD, INVERGORDON VIC 3636 | 30150931 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the substation pole ignited and burnt at bridging insulator. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | NKA001 | Excessive leakage current | Pole-top fire | 43383.6153 | 1 | Negligible: no ground fire | 10541 | Roadway |  | 20181016PWA_02 | Infrastructure (network-based) | -36.1442 | 145.5442 | 1 | Powercor | Report | 13348 | 0.015789 | 22kV AC | Shepparton Airport | 3636 | Invergordon | Pole
On arrival crew isolated supply | 223 COLLINS STREET, THORNBURY VIC 3071 | 30194048 | Copper theft | [6 empty] | A customer reported a stolen cable at the incident location. Upon arrival, the crew found a new customer service cable from a pole to UG pit had been cut away. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | FF097 | Copper theft | Damage to network assets | 43383.6375 |  |  | 10544 | Roadway |  | 20181017PWA_01 | Infrastructure (network-based) | -37.7565 | 145.0236 | 1 | CitiPower | Report | 13351 | 0.017741 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Other
On arrival crew isolated supply, transformer replaced. Customers underground supply isolated for rec repairs. | 1150 CARPENDEIT-BUNGADOR ROAD, SWAN MARSH VIC 3249 | 30056944 | Working too close to underground cables |  |  | Fault on customer installation |  |  | 1 | Following an ACR outage, a customer reported seeing smoke and sparks coming from the transformer at the front of the property at the incident location. Transformer replaced. Customers underground service was faulty. Evidence of excavation and tree removal on customers property suspected of causing fault. There was no fire or reported injuries | Services cable;Pole mounted;Customer installation | 2 | 2 | 2 |  | CLC006 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43444.3958 |  |  | 10555 |  |  | 20181018PWA_03 | Infrastructure (network-based) | -38.383 | 143.3325 | 1 | Powercor | Report | 13426 | 0.011207 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3249 | Swan Marsh | Dug up
On arrival crew isolated supply and carried out repairs. | 48 OLD WESTERN HIGHWAY, MELTON WEST VIC 3337 | 30111744 | Vandalism;Copper theft | [6 empty] | Electrix inspector reported that copper earth cables have been chopped off and are missing from substation at incident location. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BMH006 | copper theft & vandalism | Damage to network assets | 13/10/2018 10:00 |  |  | 10560 | Roadway |  | 20181019PWA_01 | Infrastructure (network-based) | -37.6851 | 144.5144 | 1 | Powercor | Report | 13367 | 0.035192 | Earthing cable | Laverton Raaf | 3337 | Melton West | Other
A LEI and faults truck attended and measured 36v on the shower taps with minimal load applied. A NST failed at the main switch and the faults crew identified the neutral connection to the overhead reticulation at the pole end had broken off. The service connection was cleaned, greased and re-terminated and the LEI re-tested the installation that confirmed the fault had been rectified with supply left on. | 35 HASTINGS ROAD, FRANKSTON VIC 3199 |  |  |  |  | Neutral fault;Overheated connection | Poor workmanship | Phase to earth | 2 | Caller received an electric shock earlier this morning at about 8.00AM from the shower tap. The supply seems to be okay and hasn't happened since. The occupier received a slight electric shock from a shower tap and contacted the United Energy faults and emergencies call centre. She experienced a strong sharp electrical feeling from the shower tap and could not turn off the water because of it, A towel was used but she still felt shocks as the towel was wet. Finally, she then went outside and turned off the circuit breakers and was then able to turn off the taps. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | The neutral connection to the overhead reticulation at the pole end had broken off. | Minor shock | 23/10/2018 8:00 |  |  | 10575 | Residential |  | 20181025UTD_02 | Infrastructure (network-based) | -38.1521 | 145.1324 | 1 | United Energy Distribution | Report | 13390 | 0.024074 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Carried out temporary repairs to Sub Station door and damaged fence. | 515-519 KOROROIT CREEK ROAD, ALTONA VIC 3018 | 33107470 | Vandalism;Copper theft | [6 empty] | PCA Operator advised of Intruder Alarms in Zone Sub AL. Initial investigations by PCA Operator and PCA Field Crew advised that up 10 on site earths have been stolen. Police attended site and PCA Operator attended Altona North Police Report for an official police incident report. | Zone substation | 2 | 2 | 2 |  |  | copper theft & vandalism | Damage to network assets | 19/10/2018 19:37 |  |  | 10586 | Other | Zone substation | 20181031PWA_02 | Infrastructure (network-based) | -37.8474 | 144.8089 | 1 | Powercor | Report | 13408 | 0.0026736 | Earthing cable | Laverton Raaf | 3018 | Altona | Other
Supply isolated and repairs carried out | 273 FURLONG ROAD, ST ALBANS VIC 3021 | 30115067 | Vehicle | [5 empty] | 1 | Powercor crews working only about 200m from the incident location heard a loud electrical noise and went to investigate. On arrival the crew found that a truck with a high load had contacted several communications cables in the street, with one cable flicking back over the 22kV HV overhead conductors. This then resulted in a small grassfire of approx. 10m2 on the nature strip. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | SU012 | High load struck communication cables | Grassfire | 43111.6264 | 1 | Small: 10 - 1000 sq.m | 10594 | Roadway |  | 20181102PWA_02 | Infrastructure (network-based) | -37.7591 | 144.8011 | 1 | Powercor | Report | 13418 | 0.023166 | 22kV AC | Melbourne Airport | 3021 | St Albans | Vehicle
Fault crew dispatched | 11 NEMOYA COURT, WALLAN VIC 3756 | LIS912718 |  |  |  | Candled fuse |  |  |  | E0004097 - report of EDO tube burnt in half | EDO fuse | 0 | 0 | 0 |  | KLO24 | Candled HV EDO fuse | Pole-top fire | 43142.0833 | 1 | Negligible: no ground fire | 10601 |  |  | 20181107SPN_01 | Infrastructure (network-based) | -37.4027 | 144.9773 | 2 | AusNet Services Distribution | Report | 13430 | 0.024808 | 22kV AC | Wallan (Kilmore Gap) | 3756 | Wallan | Fuse
Fault crew dispatched Fire brigade was on scene and extinguished the fire. | BENELONG, 90 HOLTS LANE, BUNDALAGUAH VIC 3851 | LIS2500389 and LIS2500388 |  | Fallen | [5 empty] | E0004173 - Ground fire reported between poles Lis 2500389 to 2500388. Fire brigade was on scene and extinguished the fire. | Conductor (bare) | 0 | 0 | 0 |  | SLE32 | Vegetation: Trees Incident | Grassfire | 43201.7493 | 1 | Small: 10 - 1000 sq.m | 10604 |  |  | 20181107SPN_03 | Infrastructure (network-based) | -38.0451 | 147.0314 | 2 | AusNet Services Distribution | Report | 17771 | 0.03615 | 22kV AC | Bairnsdale Airport | 3851 | Bundalaguah | Trees
On arrival crew isolated supply and carried out repairs. | 22 CLERK ROAD, CARLSRUHE VIC 3442 | 33108788 |  |  |  | Overheated connection |  |  |  | Vic fire attended this address and extinguished a fire on the pole and on the surrounding grass where burning debris had landed. Crew attended to find that the low voltage FOLCB had been burnt out,. There were no reported injuries. | Connection box | 2 | 2 | 2 |  | WND023 | Insufficient remains to reliably identify cause | Pole-top fire;Grassfire | 43354.4167 | 1 | Localised: less than 10 sq.m | 10612 | Agricultural |  | 20181109PWA_03 | Infrastructure (network-based) | -37.2911 | 144.5176 | 1 | Powercor | Report | 13520 | 0.036174 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Carlsruhe | Connection
The crew isolated supply to the substation and the CFA extinguished the fire. | 3 WOOD STREET, SOLDIERS HILL VIC 3350 | 30327257 |  |  |  | Leakage |  |  |  | Vicfire reported a connection on fire at the incident location. On arrival the crew found that a HV insulated lead had contacted a surge diverter on the transformer, resulting in the lead catching fire. There was no ground fire, no reported injuries or third party property damage. | Dropper/bridge | 2 | 2 | 2 |  | BAN013 | Excessive leakage current | Pole-top fire | 43262.4083 | 1 | Negligible: no ground fire | 10621 | Roadway |  | 20181109PWA_05 | Infrastructure (network-based) | -37.5432 | 143.8521 | 1 | Powercor | Report | 13457 | 0.015159 | 22kV AC | Ballarat Aerodrome | 3350 | Soldiers Hill | AF Other
Fault crew and LEI dispatched to investigate. Failed FOLCB removed and replaced with new., damaged dropper cables replaced. Supply restored. | 26 BAYNES PARK ROAD, MONBULK VIC 3793 | LIS1321322 |  |  |  | Defective component |  |  |  | CFA report of burnt /smoking FOLCB | Connection box | 0 | 0 | 0 |  | BGE011 | FOLCB has failed internally possibly as a result of poor neutral connections. Failed FOLCB removed and replaced with new, damaged dropper cables replaced and re-terminated. | Pole-top fire | 24/10/2018 15:22 | 1 | Negligible: no ground fire | 10618 | Roadway |  | 20181109SPN_04 | Infrastructure (network-based) | -37.8771 | 145.4001 | 1 | AusNet Services Distribution | Report | 13454 | 0.027074 | Low voltage AC (<1kV) | Moorabbin Airport | 3793 | Monbulk | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. | 27 WILMA AVENUE, DANDENONG VIC 3175 | 633695 |  | Precipitation |  | Leakage |  |  | 1 | At 1159hrs on 05/09/2018, 22kV feeder NP 36 circuit breaker reclosed to lockout affecting 400 customers. Following heavy rain, a pole fire occurred on a HV timber intermediate cross arm on pole No. LIS 0633695 located outside 27 Wilma Avenue that requires replacement. The HV conductor fell when the cross arm broke and fell on to the LV cross arm. The attending faults crew suspected that a HVI may have occurred and a LEI was dispatched to complete installation tests of properties in the vicinity. It was later confirmed that a HVI did not occur. The probable cause was attributed to insulator tracking due to the rain at the time of the event. | Crossarm (wood) | 0 | 0 | 0 |  | NP 36 | The probable cause was attributed to insulator tracking due to the rain at the time of the event. | Pole-top fire | 43231.4993 | 1 | Negligible: no ground fire | 10607 | Residential |  | 20181109UTD_01 | Infrastructure (network-based) | -37.9816 | 145.2023 | 1 | United Energy Distribution | Report | 13439 | 0.020903 | 22kV AC | Moorabbin Airport | 3175 | Dandenong | Crossarm
On arrival crew isolated supply and commenced repairs. | BLACKGATE ROAD, MOUNT DUNEED VIC 3217 | 32072179 | Vehicle | [5 empty] | 1 | Vic Fire reported wires down causing grass fire. On arrival at incident location crew found a vehicle registration No. YEU 948 had collided with LIS 33540 (Pole 6) knocking it down. A small grass fire started, | Pole (wood) | 2 | 2 | 2 |  | WPD022 | Vehicle struck pole | Grassfire | 43354.4583 | 1 | Small: 10 - 1000 sq.m | 10629 | Roadway |  | 20181112PWA_01 | Infrastructure (network-based) | -38.2878 | 144.3387 | 1 | Powercor | Report | 13479 | 0.03394 | 22kV AC | Avalon Airport | 3217 | Mount Duneed | Vehicle
Fault crew dispatched. Candling EDO fuse replaced | 2439 TRARALGON-MAFFRA ROAD, COWWARR VIC 3857 | LIS2601800 |  |  |  | Candled fuse |  |  | 0 | Reported candling EDO fuse | EDO fuse | 0 | 0 | 0 |  | TGN31 | Candling EDO fuse | Pole-top fire | 43354.9333 | 1 | Negligible: no ground fire | 10625 |  |  | 20181112SPN_01 | Infrastructure (network-based) | -38.0227 | 146.6691 | 2 | AusNet Services Distribution | Report | 17772 | 0.014491 | 22kV AC | Morwell (Latrobe Valley Airport) | 3857 | Cowwarr | Fuse
Fault crew dispatched. Fuses replaced and 10m of conductor was replaced on the phase that fell to the ground. The other phase was repaired using a splice | 910 DONNYBROOK ROAD, DONNYBROOK VIC 3064 | LIS932480 and LIS932481 | Crane, excavator or other construction/farming equipment |  |  | Candled fuse |  | Phase to earth |  | reported fuse candelling at LIS 932480 and midspan HV conductor brake between LIS932480 and LIS932481. | Conductor (bare);Boric acid | 0 | 0 | 0 |  | KLO14 | Fault crew believe conductor may have been hit by an excavator resulting in a mid span break of the O/H conductors and one fuse operating and another candling. 10m of conductor was replaced on the phase that fell to the ground and the other phase was repaired using a splice. There are no reported injuries or damage and the ground clearance of the O/H conductor was deemed to be sufficient/compliant. Details of the excavator and the operator are not available as the excavator had left the site prior to the fault crew arriving. | Pole-top fire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/10/2018 13:30 | 1 | Negligible: no ground fire | 10642 |  |  | 20181113SPN_02 | Infrastructure (network-based) | -37.5442 | 144.9804 | 2 | AusNet Services Distribution | Report | 17761 | 0.00028125 | 22kV AC | Wallan (Kilmore Gap) | 3064 | Donnybrook | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. LEI's investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 15 LARNE AVENUE, DONVALE VIC 3111 |  |  | Fallen |  | Conductor clashing;HV injection |  |  | 1 | At 1012hrs on 10/11/2018, 22kV feeder NW 13 circuit breaker reclosed to lockout affecting 3194 customers. A customer called and advised the pole outside 23 Larne Avenue was smoking after a loud explosion was heard. A private tree broke and fell over the HV overhead conductors at 15 Larne Avenue, Donvale that caused conductor clashing to occur between the HV and LV conductors and a HV cross arm to break. Customers in the vicinity advised of damaged appliances following the outage and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from the east circuit of "Conway-Larne" substation. The LEI confirmed a high voltage injection occurred (BWD 1813) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | NW 13 | Vegetation: Trees Incident | HV injection;Loss of supply | 43384.425 |  |  | 10645 | Residential |  | 20181114UTD_01 | Infrastructure (network-based) | -37.7939 | 145.1903 | 1 | United Energy Distribution | Report | 13494 | 0.038442 | 22kV AC | Moorabbin Airport | 3111 | Donvale | Trees
Citipower representatives attended and isolated sub-transmission line whilst bay of scaffolding was removed. After discussion worksafe arranged for ESV to attend. | 279 GRAHAM STREET, PORT MELBOURNE VIC 3207 | 30545334 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Work Safe Inspector was attending at site due to work place injury and noticed Scaffold in close proximity to power lines and advised that Scaffold appeared to be erected closer to power lines than clearances on PTW. | Conductor (bare) | 0 | 0 | 0 |  | FBTS-AP | non compliance with permit to work conditions | No Go Zone (no contact) | 26/10/2018 13:00 |  |  | 10647 |  |  | 20181115PWA_02 | Infrastructure (network-based) | -37.8386 | 144.9375 | 1 | CitiPower | Report | 13501 | 0.025494 | 66kV AC | Essendon Airport | 3207 | Port Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 3080 PYRENEES HIGHWAY, MOOLORT VIC 3465 | 30023598 |  |  |  | Mechanical vibration |  |  |  | Vic Fire reported grass fire and wire down at incident location. Crew found that the centre phase HV copper conductor had broken mid span at sleeve. There was a small grass fire (520 sqm), no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO007 | Mechanical fatigue failure of the copper conductor at the McIntyre sleeve | Grassfire | 16/11/2018 3:19 | 1 | Small: 10 - 1000 sq.m | 10658 | Roadway |  | 20181116PWA_01 | Infrastructure (network-based) | -37.0666 | 143.8937 | 1 | Powercor | Report | 13517 | 0.037038 | 22kV AC | Ballarat Aerodrome | 3080 | Moolort | Conductor
Fault crew dispatched and replaced burnt off fuse. | 644 PONKEEN CREEK ROAD, TARCOMBE VIC 3666 | LIS3902809 |  | Lightning |  |  |  |  | 2 | report of burnt fuse tube. Fault crew replaced burnt off fuse tube. Lightning reported in area. No ground fire. No pole fire. Fuse carrier was smouldering. | EDO fuse | 0 | 0 | 0 |  | BN1 | The EDO fuse operation was triggered by lightning in the area. The hung up of the fuse is due to accumulation of dry mud at the bottom of the fuse by insect/wasp. When the fuse link blows the tension is unable to be released causing the spring and the tube to hang up. | Pole-top fire | 43323.5861 | 1 | Negligible: no ground fire | 10655 | Agricultural |  | 20181116SPN_01 | Infrastructure (network-based) | -36.9371 | 145.4201 | 1 | AusNet Services Distribution | Report | 18189 | 0.019532 | 12.7kV AC (SWER) | Mangalore Airport | 3666 | Tarcombe | Fuse
A Zinfra substation crew attended, made the site safe and replaced the 11kV 1000kVA kiosk substation the following day. | 573 GLEN HUNTLY ROAD, ELSTERNWICK VIC 3185 | 2335013 | Vehicle | [5 empty] | 1 | Caller reports that she has backed into the green padmount transformer located in Glenhuntly road opposite Hoddle Street. She reported a small dent in her car and no injuries or sparking prior to the call dropping out. Car hit a kiosk substation causing significant damage to "Glenhuntly N573-Foster" substation to an extent where a member of the public could reach inside to live assets as thee kiosk substation had moved by an estimated three inches. | Pad mounted equipment/kiosk | 0 | 1 | 0 |  | EL 10 | Vehicle backed into kiosk with force. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/08/2018 15:55 |  |  | 10361 | Public space |  | 20180831UTD_01 | Infrastructure (network-based) | -37.8857 | 145.013 | 1 | United Energy Distribution | Report | 13082 | 0.00011458 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3185 | Elsternwick | Vehicle
On arrival crew isolated supply and carried out repairs | 394 VOSTI ROAD, WOODVALE VIC 3556 | 33017991 |  |  |  | Overheated connection |  |  | 1 | CFA and landowner reported flames and smoke coming from pole. On arrival, crew found a junction box had melted and a small patch of burnt ground at the base of the pole, approx. 30cm x 30cm. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | EHK024 | connection failure most probable | Grassfire | 43109.9549 | 1 | Localised: less than 10 sq.m | 10373 | Roadway |  | 20180903PWA_01 | Infrastructure (network-based) | -36.6683 | 144.1561 | 1 | Powercor | Report | 13101 | 0.02114 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | Woodvale | Connection
Fault crew removed existing service cable and replaced service with new 2/core service cable CTA re-tested property, all required VESI tests passed | 12 TALBOT STREET, SUNSHINE NORTH VIC 3020 | 33076105 |  |  |  | Corrosion |  | Phase to earth |  | Zoran was showering at the time; he received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. | Service conductor | 2 | 2 | 2 |  | SSE032 | Corroded connection | Minor shock | 17/08/2018 10:00 |  |  | 10376 | Residential |  | 20180904PWA_02 | Infrastructure (customer connection) | -37.7677 | 144.8401 | 1 | Powercor | Report | 13105 | 0.025554 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Connection
The branch was removed and it was determined that no further action is required. | 31 LACY STREET, BRAYBROOK VIC 3019 | A127303 |  | Blown branch/vegetation |  |  |  |  | 2 | Small branch, from a council responsible tree, broke during high winds and failed onto 2 phasaes of HV conductor | Conductor (bare) | 0 | 0 | 0 |  | BY15 | Vegetation: Trees Incident | Other vegetation | 18/08/2018 15:49 | 1 | Negligible: no ground fire | 10382 | Public space |  | 20180905JEM_01 | Infrastructure (network-based) | -37.7781 | 144.8604 | 1 | Jemena | Report | 17957 | 0.015821 | 22kV AC | Essendon Airport | 3019 | Braybrook | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Customerâ€™s first Private Service Pole forming part of a POEL. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1493 OLD LINDSAY ROAD, STRATHDOWNIE VIC 3312 | 32131367 |  |  |  | Corrosion |  | Phase to earth |  | Ms Denise Harvey was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | HTN002 | Corroded connection | Minor shock | 14/08/2018 0:00 |  |  | 10381 | Agricultural |  | 20180905PWA_03 | Infrastructure (customer connection) | -37.6463 | 141.0255 | 1 | Powercor | Report | 13117 | 0.041113 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3312 | Strathdownie | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Service Pole. The attending Powercor Fault Crew replaced the Pole Top Connection Box and re-terminated the existing O/H Service Cable at the Reticulation Service Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 53 OSWALD STREET, PORTLAND VIC 3305 | 32125138 |  |  |  | Corrosion |  | Phase to earth |  | Ms Jennifer Milich was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Rose and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | PLD004 | Corroded connection | Minor shock | 24/08/2018 0:00 |  |  | 10384 | Roadway |  | 20180907PWA_01 | Infrastructure (network-based) | -38.3394 | 141.5938 | 1 | Powercor | Report | 13123 | 0.026747 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 250w HPS lantern. A new order was created for the replacement of the defective lantern. | 344 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7050956 |  |  |  | Overheated connection |  |  | 2 | MFB advised of a pole fire at the street light in the centre median strip next to the tram tracks. The south side 250w HPS lantern on pole No. LIS 7050956 attached to a double spigot bracket over the tram tracks caught fire and was attended to by the MFB. The faults crew were unable to determine the supply point and the faulty lantern was isolated at the pole end. | Public lighting | 0 | 0 | 0 |  |  | The cause was a probable loose connection that overheated. | Pole-top fire | 43199.7083 | 1 | Negligible: no ground fire | 10394 | Roadway |  | 20180909UTD_06 | Infrastructure (network-based) | -37.8514 | 145.1249 | 1 | United Energy Distribution | Report | 13133 | 0.023628 | Low voltage AC (<1kV) | Moorabbin Airport | 3125 | Burwood | Connection
On arrival crew isolated supply and carried out repairs. Defect notice issued to customer | 598-632 BEATTYS ROAD, BONNIE BROOK VIC 3335 | 33109498 | Vandalism;Copper theft | [6 empty] | An LEI attending to an abolishment at this address has reported that the substation has been vandalized FLOCB smashed and copper earths have been stolen. No fire and no injury reported. | Connection box;Earth/earthing | 2 | 2 | 2 |  | MLN021 | Vandalism and copper theft | Loss of supply;Damage to network assets | 43229.5833 |  |  | 10400 | Roadway |  | 20180910PWA_05 | Infrastructure (network-based) | -37.7086 | 144.6858 | 1 | Powercor | Report | 13141 | 0.016749 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Bonnie Brook | Other
The power meter has been removed from the property and the premises have been isolated. Brad (Victoria police ) was in attendance during the inspection / meter removal. | 67 CALLAWAY BOULEVARD, SUNSHINE WEST VIC 3020 | 30276988 | Theft;Unauthorised work | [6 empty] | Tim Scott (LEI) following up on alleged power theft has determined that the meter at this premises has been illegally by-passed. In an attempt to reduce / eliminate power charges. There was no fire, no reported injuries or third party property damage. | Smart meter | 2 | 2 | 2 |  | SU035 | Power theft | Damage to network assets | 43229.6007 |  |  | 10402 | Residential |  | 20180910PWA_07 | Infrastructure (network-based) | -37.7938 | 144.7945 | 1 | Powercor | Report | 13143 | 0.018439 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Other
Jemena Network Operator isolated underground cable, issued Access Permit for Jemena Fault crew to inspect damage. Third Party contractor issued Permit to Work to resume works, hand digging to expose gas pipe and complete works. ESV Investigators onsite and granted permission to complete works. | 1 CROWN STREET, FOOTSCRAY VIC 3011 |  | Working too close to underground cables |  | Highly unlikely |  | Not followed;Ineffective planning/procedures/processes | Phase to earth | 1 | A third party contractor while carrying out gas maintenance works near Jemena assets damaged the insulation of a 22Kv underground cable For further information please contact John Vasilopoulos (Jemena Works Practices Specialist) Photos are attached in the "Notes & Findings" section. | Cable;Aluminium | 1 | 0 | 0 |  | FE06 | Third party contractor did not expose the gas pipe from the surrounding soil to clearly confirm no other assets were adjacent to the gas pipe prior to commencing to cut the pipe. | Loss of supply;Significant disruption to the community;Medical attention (first aid/doctor/hospital);No Go Zone (contact);Damage to network assets | 43382.3931 |  |  | 10411 | Public space |  | 20180911JEM_01 | Infrastructure (network-based) | -37.7986 | 144.8961 | 1 | Jemena | Report | 13158 | 0.026728 | 22kV AC | Essendon Airport | 3011 | Footscray | Dug up
On arrival crew isolated supply and carried out repairs. | 83 HIGH STREET, ARARAT VIC 3377 | 30339108 |  |  |  | Overheated connection |  |  |  | Report received of fuse on meter panel was smoking and sparking which has since stopped. On arrival crew found meter board fuse had melted and evidence of burning on meter board. There was no ground fire, no reported injuries or third party property damage. | Meter board (including fuses) | 2 | 2 | 2 |  | ART031 | Connection failure | Meter board | 43290.5174 | 1 | Negligible: no ground fire | 10405 | Commercial |  | 20180911PWA_02 | Infrastructure (customer connection) | -37.2828 | 142.9351 | 1 | Powercor | Report | 13146 | 0.033072 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Connection
Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a severely corroded service neutral conductor at the FOLCB. The attending service crew repaired the phase mains connection box neutral termination. Attending LEI performed an NST, obtaining a PASS result. Customer left SAFE - ON supply. | 47 RAGLAN STREET, DARLEY VIC 3340 | 30110288 |  |  |  | Corrosion |  | Phase to earth |  | Mr Fischer was showering when he received an electric shock as he made simultaneous contact between his hand and the metallic tap fixtures in the shower recess whilst standing bare foot on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | BMH005 | Corroded connection | Minor shock | 43260 |  |  | 10416 | Roadway |  | 20180912PWA_02 | Infrastructure (customer connection) | -37.6565 | 144.4386 | 1 | Powercor | Report | 13161 | 0.020992 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Darley | Connection
Site isolated of supply to make safe. | 235 BEATTYS ROAD, FRASER RISE VIC 3336 |  | Vandalism;Copper theft | [5 empty] | 2 | Damage to network assets and stolen LV earthing (Copper Theft). | Earth/earthing | 0 | 0 | 0 |  |  | Person/s unknown vandalised network assets and stole copper. | Damage to network assets | 13/09/2018 10:06 |  |  | 10425 |  |  | 20180913JEM_05 | Infrastructure (network-based) | -37.6984 | 144.7142 | 1 | Jemena | Report | 13193 | 0.027236 | Earthing cable | Melbourne Airport | 3336 | Fraser Rise | Other
Further investigation did not reveal any record of Jemena ever attending this address. The searches we did show this meter registered as 49 Bowes Ave and not 1/49 Bowes Ave. | 49 BOWES AVENUE, AIRPORT WEST VIC 3042 |  | Unauthorised work;Unauthorised access |  |  |  | Not followed |  | 2 | The crew attended a 3 unit site at the address listed below. The crew have NC SOâ€™s to meter unit 2 and unit 3. On site, they have found meter number 0115893 connected to unit 1 and unit 1 fully occupied. This meter has also been parallel connected in the mains control SB to both unit 1 and socket outlets (probably for temp builders supply). There is no sealing on any of the meter panel, fuses or neutral link. | Smart meter;Connection to meter | 0 | 0 | 0 |  |  | REC and the builder relocated the entire metering position from the front house location to its current location without any attendance and isolation from the distributor and no prescribed inspection or CES. | No Go Zone (no contact);Damage to network assets | 43320.5 |  |  | 10426 | Residential |  | 20180913JEM_06 | Infrastructure (network-based) | -37.7304 | 144.8847 | 1 | Jemena | Report | 13177 | 0.040782 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Airport West | Other
The Lumo Energy crew disconnected and removed the single phase XLPE overhead service the from the pole and issued a defect notice advising that a REC is required to complete repairs before supply can be restored. | 2 GREVILLEA STREET, DOVETON VIC 3177 |  | Unauthorised work | [5 empty] | 2 | Zinfra subcontractor Lumo Energy, identified a non-compliant connection as the POA has been removed from the existing house undergoing renovations and attached to a post in the front yard. The consumers mains run from the pole to the house in a unsafe manner. Field workers from Lumo Energy identified unsafe non-compliant wiring at a property in Doveton as they prepared for planned work activities in the area. An unknown person has detached their POA and attached it to a makeshift BSP. Notes on the customers account indicate they applied for a pole to pit in August, but it was rejected as the submitted paperwork was incomplete. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Unauthorised interference with assets. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43260.3333 |  |  | 10431 | Residential |  | 20180916UTD_03 | Infrastructure (network-based) | -37.9971 | 145.2304 | 1 | United Energy Distribution | Report | 13182 | 0.038212 | Low voltage AC (<1kV) | Moorabbin Airport | 3177 | Doveton | Other
None required as Indoor substation has already been isolated LV & HV since 2013. | 28-44 ALBERT STREET, PRESTON VIC 3072 |  | Copper theft | [5 empty] | 2 | Copper theft at Indoor substation that has been isolated LV & HV since 2013 due to the building it serviced being demolished. | Indoor | 0 | 0 | 0 |  |  | Copper theft by person/s unknown. | Damage to network assets | 17/09/2018 14:39 |  |  | 10437 |  |  | 20180918JEM_01 | Infrastructure (network-based) | -37.7498 | 145.0217 | 1 | Jemena | Report | 13330 | 0.01491 | Earthing cable | Essendon Airport | 3072 | Preston | Other
On arival crew isolated supply. Defect notice issued to customer. | 183-195 WESTCOTT PARADE, ROCKBANK VIC 3335 | 33076261 | Vandalism;Copper theft | [6 empty] | Reported outage to property at No. 183 Westcott Parade, Rockbank, 3335. Upon arrival the PCA Field Crew have discovered, that an unknown person has removed the pit lid, from the LV Service Pit on the boundary. They have cut through the LIVE LV Customer Mains Cables , they have then proceeded to the customer Switchboard, and have cut the tails of the LV Customer Mains Cables and have tried to pull out the LV Customer Mains Cables from the pit, but where unsuccessful. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Vandalism & copper theft. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/09/2018 14:29 |  |  | 10449 | Residential |  | 20180920PWA_02 | Infrastructure (network-based) | -37.7291 | 144.6551 | 1 | Powercor | Report | 13216 | 0.022334 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Inspector testing revealed severely corroded neutral of the service cable. Service was replaced and testing was redone to confirm safe. Full Techsafe report can be found in section "7. Notes & Findings" | 13 NORFOLK STREET, MAIDSTONE VIC 3012 |  |  |  |  | Corrosion |  |  | 2 | Plumbing contractor received mild shock while repairing water pipe. Techsafe attended site to investigate. Full Techsafe report can be found in section "7. Notes & Findings" | Neutral screen | 2 | 2 | 2 |  |  | Severely corroded neutral part of service. | Minor shock | 21/09/2018 16:00 |  |  | 10452 | Residential |  | 20180921JEM_02 | Infrastructure (network-based) | -37.789 | 144.8818 | 1 | Jemena | Report | 13219 | 0.014017 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | OH Cable
On arrival crew isolated supply and carried out repairs. | 20 HIGH ROAD, HALLS GAP VIC 3381 | 30080847 | Working too close to overhead lines | [6 empty] | A call was received that an excavator had hit and damaged an overhead service at the above location. On arrival the crew found that an excavator had hit and damaged the overhead service to the above property. There was no shock, injury or third party damage. | Service conductor | 2 | 2 | 2 |  | STL005 | Excavation works | Loss of supply;No Go Zone (contact);Damage to network assets | 16/09/2018 11:45 |  |  | 10458 | Public space |  | 20180925PWA_05 | Infrastructure (network-based) | -37.1521 | 142.5222 | 1 | Powercor | Report | 13225 | 0.030964 | Low voltage AC (<1kV) | Horsham Aerodrome | 3381 | Halls Gap | Vehicle
On arrival crew isolated supply and carried out repairs. | 45 FISCHER STREET, TORQUAY VIC 3228 | 32087132 |  |  |  | Overheated connection |  |  |  | CFA communications reported a pole fire. Attending crew found that a pole mounted LV fuse box had overheated There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | WPD032 | Insufficient Remains to determine cause. | Pole-top fire;Loss of supply | 16/09/2018 20:13 | 1 | Negligible: no ground fire | 10459 |  |  | 20180926PWA_01 | Infrastructure (network-based) | -38.3262 | 144.3237 | 1 | Powercor | Report | 13328 | 0.041161 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Fuse
Fault crew dispatched. No damage to conductor, bridging at the fuses replaced and crossarm straightened. Conductor height checked and confirmed to be above minimum requirement. Conversation with Fulton Hogan regarding driver training in no-go zones. | 1270 PRINCES HIGHWAY, NICHOLSON VIC 3882 | LIS1900027 | Vehicle |  |  |  |  | Phase to earth |  | E0002296 - Report of truck clipping overhead HV conductors. No damage to conductor and no injuries reported | Conductor (bare) | 0 | 0 | 0 |  | BDL6 | Driver was unloading with his trailer up when he struck the conductor. He confirmed he was unaware of a power line in the area. Conductor ground clearance was above minimum requirement and appropriate signage was in place. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/09/2018 12:40 |  |  | 10466 |  |  | 20180927SPN_01 | Infrastructure (network-based) | -37.8209 | 147.7769 | 2 | AusNet Services Distribution | Report | 13240 | 0.0080463 | 22kV AC | Bairnsdale Airport | 3882 | Nicholson | Vehicle
CTA and fault crew attended and matched pole based on photo provided via City of Melbourne 88760 and checked and was unable to find any reason that might have explained why someone received an electric shock. All power poles outside and opposite 575 Bourke St Melbourne were checked using an independent earth and no voltage was measureable on any of the poles. | 575 BOURKE STREET, MELBOURNE VIC 3000 | 30182393 |  |  |  | Unknown technical factor |  | Phase to earth |  | A member of the public (unknown) reports receiving an electric shock from a pole outside 575 Bourke St Melb. The report came via City of Melbourne . There was no reported fire, no third party property damage. | Pole (steel) | 2 | 2 | 2 |  | LQ055 | No cause located | Minor shock | 26/09/2018 0:00 |  |  | 10473 | Roadway |  | 20181001PWA_01 | Infrastructure (network-based) | -37.8163 | 144.9565 | 1 | CitiPower | Report | 13247 | 0.0054144 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 26 WILSON STREET, CHELTENHAM VIC 3192 | 1814983 |  |  |  | Electrical breakdown;Leakage |  |  |  | At 0942hrs on 15/09/2018, 22kV feeder ACR CH 8639 located in Herald Street reclosed to lockout affecting 620 customers. The MFB reported a pole fire at pole number 1814983. During light drizzly rain, a cross arm fire occurred on a HV strain cross arm with HV isolators and brown disc insulators attached on pole No. LIS 1814983 located outside 26 Wilson Street. The cross arm fire occurred at the HV strain cross arm strap that burnt through. | Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | HT 11 | Tracking on the HV brown disc insulators was the most probable cause. | Pole-top fire | 15/09/2018 9:42 | 1 | Negligible: no ground fire | 10476 | Roadway |  | 20181001UTD_03 | Infrastructure (network-based) | -37.9626 | 145.0603 | 1 | United Energy Distribution | Report | 13251 | 0.033685 | 22kV AC | Moorabbin Airport | 3192 | Cheltenham | Crossarm
On arrival crew isolated supply and carried out repairs | 256 KNOWSLEY-BARNADOWN ROAD, KNOWSLEY VIC 3523 | 30040888 |  |  |  | Overheated connection |  |  |  | Customer reported fire in meter box. On arrival crew found fire out and damage to meter board and fuse unit. There was no ground fire, no reported injuries or third party property damage. | Meter board (including fuses) | 2 | 2 | 2 |  | BGO023 | Overheated connection | Meter board | 24/09/2018 11:12 | 1 | Negligible: no ground fire | 10483 | Residential |  | 20181002PWA_02 | Infrastructure (customer connection) | -36.7807 | 144.5673 | 1 | Powercor | Report | 13264 | 0.039708 | Low voltage AC (<1kV) | Bendigo Airport | 3523 | Knowsley | Connection
On arrival crew isolated supply and arranged repairs. | 18 HUTCHINSON STREET, CRESWICK VIC 3363 | 33065017 | Working too close to overhead lines | [5 empty] | 1 | A grader has hit guy wire at the incident location, as a result two poles and conductor were damaged. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | BAN009 | Grader | Loss of supply;Damage to network assets | 24/09/2018 8:30 |  |  | 10485 | Roadway |  | 20181002PWA_03 | Infrastructure (network-based) | -34.4712 | 142.3539 | 1 | Powercor | Report | 13266 | 0.013899 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3363 | Creswick | Vehicle
On arrival crew isolated supply. Customer engaged REC to repair POA | 57 FELSTEAD AVENUE, SUNSHINE WEST VIC 3020 | 32171391 | Working too close to overhead lines | [6 empty] | A customer reported a garbage truck has pulled down a service line and damaged the point of attachment. There was no fire and no reported injuries. | Service conductor | 2 | 2 | 2 |  | SSE014 | Garbage truck | Loss of supply;Damage to network assets | 25/09/2018 10:59 |  |  | 10492 | Roadway |  | 20181003PWA_02 | Infrastructure (network-based) | -37.8032 | 144.8166 | 1 | Powercor | Report | 13274 | 0.017648 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
This Incident has been reported to ESV who instructed Jemena to notify the event to Worksafe. To mitigate the risk, Jemena have installed visual warnings on the live overhead cable. Informed the builder of the NGZ requirements when working near live electrical apparatus. Requested the builder install physical barriers beneath the affected overhead power lines and remove two large trucks parked adjacent to the overhead power line. We also attempted to contact the neighbouring business to advice of the risk but no persons were available and no phone numbers on display. | 210 HOLT PARADE, THOMASTOWN VIC 3074 |  | Building too close or within the No Go Zone |  | Highly likely |  | Not followed |  | 2 | On the 3/10/18 Jemena identified that during the third party construction stages of a commercial building in Holt Parade (Next door to 210 Holt Parade), Thomastown, The integrity of the live electrical overhead assets had been compromised. Firstly the builder (Leo) has reduced the clearance between ground and the live 66kV overhead cable by backfilling (raising) the ground beneath the Jemena overhead cables. Secondly the builder has removed two ground stay wires which were used to secure electrical pole, causing the pole to move/lean, lowering the height of the live 66kV overhead cable between the 2 adjacent poles. Both of these actions have resulted in the live 66kV overhead cable lowering to a ground height of 4.8 meters between one bay and 6 meters between another bay, below the 6.7 meter minimum ground clearance required. Jemena can provide evidence in October 2017 these ground clearances were confirmed to be at the required heights. A site assessment conducted indicated, while the pole is at no immediate risk of falling the pole needs to be supported as soon as practicable. De-energisation of the live cable is not deemed practicable as this could result in the loss of power to a large number of customers and critical infrastructure. Immediately after 4 Jemena technical specialist left the holt parade worksite and passing along the adjacent Dalton road at 8:40 on the 4/10/18. it was observed that work had recommenced using two scissor lifts adjacent to the overhead power lines within the 3-6.4 meter no go zone informed to the builder. In addition, this is the second incident on this worksite, with the same builder making contact with a live cable with an excavator in October 2017. | Conductor (bare);Guy wire | 0 | 0 | 2 |  |  | failure to adhere to No Go Zone safety clearances. Did not contact or advise Jemena of works. | No Go Zone (no contact);Damage to network assets | 43200.3646 |  |  | 10501 | Commercial |  | 20181004JEM_01 | Infrastructure (network-based) | -37.6956 | 145.0254 | 1 | Jemena | Report | 13286 | 0.032819 | 66kV AC | Essendon Airport | 3074 | Thomastown | Other
Isolated HV & made site safe. Transformer replacement arranged. | 115 BASSETT ROAD, MELBOURNE AIRPORT VIC 3045 |  | Copper theft | [5 empty] | 2 | Copper theft and vandalism of pole assets. LV earth, krone switch, and pole top transformer bushings removed by vandals. | Circuit breaker;Pole mounted;Earth/earthing | 0 | 2 | 0 |  |  | Copper theft and vandalism by unknown person/s. | Damage to network assets | 43200.6278 |  |  | 10507 | Agricultural |  | 20181004JEM_03 | Infrastructure (network-based) | -37.6698 | 144.8163 | 1 | Jemena | Report | 13293 | 0.020583 | Low voltage AC (<1kV);Earthing cable | Melbourne Airport | 3045 | Melbourne Airport | Other
On arrival crew isolation at the distribution pole across the road to make safe and carried out repairs. | 86 DAVIS STREET, WARRNAMBOOL VIC 3280 | 33099752 |  |  |  | Corrosion;Neutral fault;Electrical breakdown |  | Phase to earth |  | Electric shock injuries were reported from two adjacent houses in Warrnambool. One of the persons sustaining an electric shock and burns was a toddler who was touching a metal window frame at #88 Davis St. The supplies suffered 2 separate but interlinked faults on the distribution network which caused the neutral and earthing systems of both houses to become energised. Multiple faults were detected after a power down was reported on AMI meters installed at # 86 and #88 Davis Street. A subsequent call was received advising of a loud explosion and no power at # 86. Later advice from the occupant at #86 also indicated she had received an electric shock from plumbing fixtures. Powercorâ€™s fault crew and LEI attended to find a ruptured service at #86 Davis street and a corroded neutral was found on the incoming supply to both #86 and #88. The supply to the pole feeding both #86 and #88 was then isolated It was also reported that a lady in #86 received a shock as she made simultaneous contact between her hands on the Kitchen Tap and the metal Sink. | Service conductor;Connection box | 2 | 2 | 2 |  | WBL004 | Dual causes Neutral connection to the LV reticulation / supply substation became disconnected mechanically through corrosion Insulation failure between active and neutral of service line to #86 | Minor shock | 43169.375 |  |  | 10499 | Residential |  | 20181004PWA_01 | Infrastructure (network-based) | -38.3807 | 142.4587 | 1 | Powercor | Report | 13303 | 0.024727 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival crew isolation at the distribution pole across the road to make safe and carried out repairs. | 88 DAVIS STREET, WARRNAMBOOL VIC 3280 | 33099752 |  | Prone to salt deposition |  | Corrosion;Neutral fault;Electrical breakdown |  | Phase to earth |  | Electric shock injuries were reported from two adjacent houses in Warrnambool. One of the persons sustaining an electric shock and burns was a toddler who was touching a metal window frame at #88 Davis St. The supplies suffered 2 separate but interlinked faults on the distribution network which caused the neutral and earthing systems of both houses to become energised. Multiple faults were detected after a power down was reported on AMI meters installed at # 86 and #88 Davis Street. A subsequent call was received advising of a loud explosion and no power at # 86. Later advice from the occupant at #86 also indicated she had received an electric shock from plumbing fixtures. Powercorâ€™s fault crew and LEI attended to find a ruptured service at #86 Davis street and a corroded neutral was found on the incoming supply to both #86 and #88. The supply to the pole feeding both #86 and #88 was then isolated The window frame at #88 was electrically inter-connected to the installation earth electrode through the metal foil insulation installed on that house. | Service conductor;Connection box | 2 | 2 | 2 |  | WBL004 | Dual causes Neutral connection to the LV reticulation / supply substation became disconnected mechanically through corrosion Insulation failure between active and neutral of service line to #86 | Medical attention (first aid/doctor/hospital) | 43169.375 |  |  | 10504 | Residential |  | 20181004PWA_03 | Infrastructure (network-based) | -38.3807 | 142.4587 | 1 | Powercor | Report | 13302 | 0.024503 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Assets isolated to make safe. Crew conducted repairs and replaced substation. | 365 RIDDELL ROAD, SUNBURY VIC 3429 |  | Vandalism;Copper theft | [5 empty] | 2 | 4 core UG cable has been stolen from pole to pit (Copper theft). Vandalism damage has also been done to substation on pole. | Cable;Copper;Pole mounted | 0 | 0 | 0 |  |  | Vandalism and copper theft by unknown person/s. | Damage to network assets | 43322.5625 |  |  | 10514 | Peri-urban |  | 20181008JEM_01 | Infrastructure (network-based) | -37.5555 | 144.701 | 1 | Jemena | Report | 13308 | 0.0067708 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
The LV circuit was isolated and the boom safely removed prior to supply being restored to the circuit and the white phase 250amp LV fuse replaced at "Kenji-Fugi" substation. A faults crew returned later in the morning and the damaged sections of the LV white and blue conductors were sleeved. | 26 VIRGINIA STREET, MORNINGTON VIC 3931 | 9297026 | Crane, excavator or other construction/farming equipment;Misadventure | [5 empty] | 1 | Caller reports crane boom resting on overhead conductors outside number 26. Unknown persons moved a portable lift that caused the boom lift basket to make contact with the aluminium LV overhead conductors. It was undetermined if it was simply an act of vandalism or an attempted theft. The LV white phase fuse had operated at "Kenji-Fugi" substation and there appeared to be no damage to the boom lift. | Conductor (bare);Aluminium | 0 | 0 | 0 |  |  | Unknown persons moved a portable lift that caused the boom lift basket to make contact with the aluminium LV overhead conductors and a LV fuse to operate. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43353.2847 |  |  | 10521 | Construction |  | 20181010UTD_01 | Infrastructure (network-based) | -38.2324 | 145.0498 | 1 | United Energy Distribution | Report | 13321 | 0.013444 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Vehicle
Site isolated to make safe for crew to conduct repairs. Cable and krone switch replaced. | 639-645 BLACK HILL ROAD, TOOLERN VALE VIC 3337 |  | Copper theft | [5 empty] | 2 | Theft of LV earth cable from pole and damage to krone switch. | Cable;Copper;Circuit breaker | 2 | 2 | 2 |  |  | Copper theft by unknown person/s | Damage to network assets | 43414.4896 |  |  | 10526 | Roadway |  | 20181011JEM_02 | Infrastructure (network-based) | -37.5934 | 144.6326 | 1 | Jemena | Report | 13326 | 0.041416 | Earthing cable | Melbourne Airport | 3337 | Toolern Vale | Other
Upon arrival the crew removed the branch. There was no damage to assets found. | 3566 MURRAY VALLEY HIGHWAY, PIANGIL VIC 3597 | 32157328 |  | Blown branch/vegetation |  |  |  |  | 2 | A passer-by reported arcing and some intermittent flame from a small branch blown into conductors at incident location. On arrival there was no evidence of ground fire, minor charring found on branch. There was no ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | SHL002 | Vegetation: Trees Incident | Other vegetation;Singeing or local charring/blackening only | 43169.7646 | 1 | Negligible: no ground fire | 10527 | Roadway |  | 20181012PWA_01 | Infrastructure (network-based) | -35.0416 | 143.3238 | 1 | Powercor | Report | 13327 | 0.024153 | 22kV AC | Swan Hill Aerodrome | 3566 | Piangil | Trees
Site made safe. UG crew rectified damaged asset. | 1345 MICKLEHAM ROAD, YUROKE VIC 3063 |  | Copper theft | [5 empty] | 2 | Copper theft of pole to pit underground cabling. | Cable;Copper | 0 | 0 | 0 |  |  | Copper theft by unknown person/s | Damage to network assets | 14/10/2018 9:05 |  |  | 10531 | Roadway |  | 20181014JEM_01 | Infrastructure (network-based) | -37.602 | 144.8823 | 1 | Jemena | Report | 13333 | 0.01947 | Low voltage AC (<1kV) | Melbourne Airport | 3063 | Yuroke | Other
Isolated LV supply to make safe. Crew conducted repairs. | 19 CALDER HIGHWAY, DIGGERS REST VIC 3427 |  |  |  |  | Mechanical breakdown |  |  | 2 | Live LV wires on ground after conductor was rubbed through by spreader mid span. | Conductor (bare) | 0 | 0 | 0 |  |  | Friction between conductor and spreader mid span caused the conductor to be rubbed through and fall to ground. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/10/2018 16:33 |  |  | 10542 | Residential |  | 20181016JEM_01 | Infrastructure (network-based) | -37.6251 | 144.7178 | 1 | Jemena | Report | 13349 | 0.021163 | Low voltage AC (<1kV) | Melbourne Airport | 3427 | Diggers Rest | Conductor
On arrival crew isolated supply and carried out repairs. | 2 GHERINGHAP STREET, GEELONG VIC 3220 | 30059216 | Vandalism | [6 empty] | Fire Brigade called to report that a chair had been thrown onto the LV open wire at the incident location. On arrival the fault crew found that an unknown person had thrown a metal framed chair from an adjacent balcony onto the LV open wire conductors, resulting in the conductors falling to the ground alive. Police attended and were investigating. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GL012 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/10/2018 13:54 |  |  | 10556 | Roadway |  | 20181018PWA_04 | Infrastructure (network-based) | -38.1435 | 144.3594 | 1 | Powercor | Report | 13363 | 0.038751 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Geelong | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | OLD WELLS ROAD, PATTERSON LAKES VIC 3197 | 3305659 |  | Lightning |  |  |  |  | 1 | At 1829hrs on 16/10/2018, 22kV feeder circuit breaker CRM 21 successfully reclosed and held. At the same time, 66kV feeder circuit breaker CRM-FTN-LWN also reclosed. During storm activity, lightning struck the CRM 21 cable exit CHP located in Old Wells Road at pole No. LIS 3305659. The lightning arrestors were severely damaged and customers in the vicinity advised of damaged appliances following the lightning strike. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Wells-Kurrawa" substation. The LEI confirmed a high voltage injection occurred (MOR 1804) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. In addition, LV HRC fuses operated on the blue phase on the north circuit at "Wells-Kurrawa" substation with meters damaged that required replacement. | Conductor (bare);Smart meter;Surge diverter | 0 | 0 | 0 |  | CRM 21 | Lightning struck a HV/LV pole that caused a HVI to occur. | HV injection;Loss of supply | 16/10/2018 18:29 |  |  | 10559 | Roadway |  | 20181019UTD_01 | Infrastructure (network-based) | -38.0717 | 145.1496 | 1 | United Energy Distribution | Report | 13366 | 0.034922 | 22kV AC | Moorabbin Airport | 3197 | Patterson Lakes | Lightning
On arrival crew isolated supply and carried out repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298010 | Vandalism;Copper theft | [6 empty] | Following an external report investigation found removal and theft of power cables, North of the Western Freeway in Bulmans Rd Melton West. The cables stolen also supply a Vic Roads lighting control box. There was no fire, no reported injuries or third party property damage. | Cable;Services cable | 2 | 2 | 2 |  | MLN022 | copper theft & vandalism | Loss of supply;Damage to network assets | 18/10/2018 9:39 |  |  | 10579 | Roadway |  | 20181026PWA_02 | Infrastructure (network-based) | -37.6871 | 144.5494 | 1 | Powercor | Report | 13396 | 0.019351 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew carried out repairs | BACK ST ARNAUD ROAD, CHARLTON VIC 3525 | 33015547 |  | Bird | [5 empty] | Vic fire reported small grass fire at incident location. On arrival crew found a bird has flashed over on ACR structure and fallen to ground igniting grass. there was no injuries or reported third party property damage | Crossarm (steel);Surge diverter | 2 | 2 | 2 |  | CTN006 | Bird Incident | Grassfire | 30/10/2018 20:03 | 1 | Small: 10 - 1000 sq.m | 10587 | Agricultural |  | 20181031PWA_03 | Infrastructure (network-based) | -36.2813 | 143.3558 | 1 | Powercor | Report | 13409 | 0.035679 | 22kV AC | Swan Hill Aerodrome | 3525 | Charlton | Animal
Emergency high voltage switching was completed and the faults crew replaced the damaged HV powder filled fuse unit at the CHP that supplied "MT-Princes" indoor substation under Access Authority conditions. | 893-895 PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 9227806 |  |  |  | Electrical breakdown |  |  | 1 | At 0742hrs on 31/10/2018, 22kV feeder circuit breaker SVW45 successfully reclosed and held. The MFB reports that a transformer is on fire at 893 Princes Highway, Springvale. The white phase 22kV HV powder filled fuse unit was damaged at DN0545 following a flash over that caused the feeder to reclose with the cause unknown. | Powder filled | 0 | 0 | 0 |  | SVW45 | The cause was unknown. | Pole-top fire | 31/10/2018 7:42 | 1 | Negligible: no ground fire | 10591 | Industrial |  | 20181101UTD_01 | Infrastructure (network-based) | -37.9287 | 145.1493 | 1 | United Energy Distribution | Report | 13414 | 0.025553 | 22kV AC | Moorabbin Airport | 3171 | Springvale | AF Other
On arrival crew isolated supply and carried our repairs. | 617 LAURIE STREET, GOLDEN POINT VIC 3350 | 32006305 |  |  |  | Corrosion |  |  | 1 | Vic Fire reported wires sparking at the above address, on arrival the crew found a LV paper lead Cable head had failed, There was a small ground fire <1sqm, no reported injuries, or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS023 | Overheated connection | Grassfire | 31/10/2018 16:30 | 1 | Localised: less than 10 sq.m | 10593 |  |  | 20181102PWA_01 | Infrastructure (network-based) | -37.5738 | 143.8595 | 1 | Powercor | Report | 13417 | 0.023285 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Golden Point | Connection
On arrival crew isolated supply and carried out repaires | PAMBILLY, 450 CHUTE-WATERLOO ROAD, WATERLOO VIC 3373 | 30012734 |  | Alive;MEC |  |  |  |  | 1 | Vic Fire reported a wire down and a grass fire at the incident location. On arrival the fault crew found that a cypress tree had fallen over HV conductors, which made contact with a post & wire fence, starting a grass fire - estimated at 4,000 square meters. The fire had been extinguished by the CFA when the fault crew arrived. There were no injuries or any other damage reported. | Conductor (bare) | 2 | 2 | 2 |  | BAS011 | Vegetation: Trees Incident | Grassfire | 43111.7194 | 1 | Medium: 1000 sq.m - 10 ha | 10596 | Agricultural |  | 20181102PWA_03 | Infrastructure (network-based) | -37.3467 | 143.4085 | 1 | Powercor | Report | 13421 | 0.030984 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3373 | Waterloo | Trees
LEI dispatched to investigate. After the faulty service was replaced the LEI has installed the service fuse and completed required tests before energizing the supply. | 48 KIEWA EAST ROAD, TANGAMBALANGA VIC 3691 | LIS 5202135 |  |  |  | Neutral fault |  | Phase to earth |  | E0004242 - customer reported electric shock from kitchen tap | Service conductor | 0 | 0 | 0 |  | WOTS11 | The injury was received as the neutral screen was damaged. | Minor shock | 43262.3847 |  |  | 10603 | Residential |  | 20181107SPN_02 | Infrastructure (customer connection) | -36.2526 | 147.0294 | 1 | AusNet Services Distribution | Report | 13432 | 0.04101 | Low voltage AC (<1kV) | Wangaratta Aero | 3691 | Tangambalanga | OH Cable
On arrival crew isolated supply and carried out repairs. | 32 SMITH ROAD, ROBINVALE VIC 3549 | 30095478 |  |  |  | Leakage |  |  | 1 | Customers reported power failure. During patrol of line crew found a HV crossarm burnt off at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RVL001 | Excessive leakage current | Pole-top fire | 43262.2771 | 1 | Negligible: no ground fire | 10610 | Roadway |  | 20181109PWA_02 | Infrastructure (network-based) | -34.5985 | 142.7893 | 1 | Powercor | Report | 13442 | 0.023155 | 22kV AC | Mildura Airport | 3549 | Robinvale | Crossarm
On arrival crew isolated supply and carried out repairs. | 89 KERRS ROAD, MADDINGLEY VIC 3340 | 32175165 |  |  |  | Leakage |  |  |  | Report received from a passerby of transformer fire on a pole. On arrival the fault crew found the centre 22kV crossarm had burnt through. There was no ground fire, no reported injuries or third party property damage.. | Crossarm (wood) | 2 | 2 | 2 |  | BMH006 | Excessive leakage current | Pole-top fire | 43262.2833 | 1 | Negligible: no ground fire | 10619 | Roadway |  | 20181109PWA_04 | Infrastructure (network-based) | -37.7009 | 144.4167 | 1 | Powercor | Report | 13455 | 0.039148 | 22kV AC | Avalon Airport | 3340 | Maddingley | Crossarm
Fault crew dispatched | 1560 MURRAY RIVER ROAD, TALGARNO VIC 3691 | LIS5214010 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0004111 - Damage to O/H conductor. Suspected contact by excavator | Conductor (bare) | 0 | 0 | 0 |  | WOT12 / WOT13 | WO284 TRIPPED AND LOCKED OUT, FAULT TRUCK DISPATCHED AND FOUND DAMAGED HV CONDUCTOR AT POLE 5214010 REQUIRING REPAIR. A NEARBY EXCAVATOR IS BELIEVED TO HAVE RUBBED THE HV CONDUCTOR. NO INJURIES HAVE BEEN REPORTED. Operator of excavator unknown and not available | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43142.3333 |  |  | 10623 | Agricultural |  | 20181109SPN_07 | Infrastructure (network-based) | -36.0593 | 147.1959 | 2 | AusNet Services Distribution | Report | 13462 | 0.015172 | 12.7kV AC (SWER) | Wangaratta Aero | 3691 | Talgarno | Vehicle
Site made safe & steps taken to have earth replaced. | 127A METROLINK CIRCUIT, CAMPBELLFIELD VIC 3061 |  | Copper theft | [5 empty] | 2 | Copper theft of LV earthing leads of Ring Main Unit at kiosk substation. | Earth/earthing | 0 | 0 | 0 |  | ST13 | Copper theft by unknown person/s | Damage to network assets | 43415.4861 |  |  | 10624 | Industrial |  | 20181111JEM_01 | Infrastructure (network-based) | -37.6495 | 144.9709 | 1 | Jemena | Report | 13463 | 0.0045671 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole, The attending Powercor (Downer) Fault Crew replaced the Grey Twisted O/H Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 74 RIPPON ROAD, HAMILTON VIC 3300 | 33057281 |  |  |  | Corrosion |  | Phase to earth | 2 | Tim and Michelle Hallam were in the Ensuite showering on several different occasions when he/she received an electric shock as he/she made simultaneous contact between his/her hand on the shower taps and his/her bare feet while standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | HTN003 | Corroded connection | Minor shock | 24/10/2018 0:00 |  |  | 10631 | Roadway |  | 20181112PWA_02 | Infrastructure (network-based) | -37.7526 | 142.0379 | 1 | Powercor | Report | 13475 | 0.01787 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination in the Pole Type Connection Box located at the Reticulation Pole, The attending Powercor Fault Crew re-terminated the O/H Service Neutral Conductor at the Pole Type Connection Box located at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1 FAIRVIEW STREET, BELMONT VIC 3216 | 30074973 |  |  |  | Corrosion |  | Phase to earth |  | Ms Seeja Kuriosc was in the Bathroom washing her hands in the Ceramic Basin when she received an electric shock as she made simultaneous contact between her hand on the metal tap and her other hand in contact with the wet Ceramic Basin. | Service conductor;Connection box | 2 | 2 | 2 |  | GCY023 | Corroded service connection | Minor shock | 28/10/2018 17:00 |  |  | 10646 | Residential |  | 20181115PWA_01 | Infrastructure (network-based) | -38.1754 | 144.3331 | 1 | Powercor | Report | 13500 | 0.026707 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable. The corrosion of the O/H Service Cable was the result of water entering the outer sheath where damaged by a tree in the front of the property. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 52 ULEY STREET, BENDIGO VIC 3550 | 31005050 |  | Property owner/customer |  | Corrosion |  | Phase to earth |  | Ms Kim Spearing was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and the other hand in contact with the Kitchen Sink. | Service conductor | 2 | 2 | 2 |  | EHK033 | Vegetation: Trees Incident | Minor shock | 25/10/2018 0:00 |  |  | 10653 | Residential |  | 20181115PWA_08 | Infrastructure (network-based) | -36.7482 | 144.2868 | 1 | Powercor | Report | 13507 | 0.021003 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | OH Cable
Fault crew dispatched to make safe and repair | 40 LEANE DRIVE, ELTHAM VIC 3095 | 'LEANE KIRWAN' substation |  |  |  | Defective component;Overheated connection |  |  |  | report of kiosk transformer burning | Transformer | 0 | 1 | 0 |  | ELM15 | Kiosk transformer failed as a result of failed/damaged connections leading to insulation heating up and subsequently catching fire. | Plant/equipment | 29/08/2018 18:34 | 1 | Negligible: no ground fire | 10657 |  |  | 20181116SPN_03 | Infrastructure (network-based) | -37.698 | 145.1622 | 1 | AusNet Services Distribution | Report | 17760 | 0.01073 | 22kV AC | Essendon Airport | 3095 | Eltham | Connection
On arrival crew isolated supply and carried out repairs | 427 OLD KERANG ROAD, KERANG VIC 3579 | 30025444 |  |  |  | Leakage |  |  | 1 | Following on from a feeder operation to lockout a crew found a pole fire had occurred at the incident location. The crossarm had burnt through allowing the conductor to fall to ground. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | KGT004 | Excessive leakage current | Pole-top fire | 13/11/2018 22:58 | 1 | Negligible: no ground fire | 10662 | Roadway |  | 20181119PWA_03 | Infrastructure (network-based) | -35.7781 | 143.8925 | 1 | Powercor | Report | 13522 | 0.02991 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | Pole
Site made safe and transformer replaced | 400 DONNYBROOK ROAD, MICKLEHAM VIC 3064 |  | Copper theft | [6 empty] | During a regular inspection, Jemena worker noticed 50kva transformer and lv under cable stolen | Equipment | 0 | 1 | 0 |  |  | 50kva transformer and lv ugc was stolen. copper theft. | Damage to network assets | 20/11/2018 13:41 |  |  | 10672 |  |  | 20181120JEM_03 | Infrastructure (network-based) | -37.5367 | 144.9148 | 1 | Jemena | Report | 13532 | 0.036185 | 22kV AC | Melbourne Airport | 3064 | Mickleham | Other
Crew have replaced connectors in pits. Cables have been placed back into the pits and closed safely. | 16 FARROW PLACE, MADDINGLEY VIC 3340 | 30343800 | Vandalism;Copper theft | [6 empty] | A crew found underground public lighting supply cables removed from six sites (LIS 850544, 850545, 850547, 850548, 850549 & 850550) with exposed live wires left at sites There was nof fire, no reported injuries or third party property damage, | Services cable;Services pit | 2 | 2 | 2 |  | BMH005 | copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/10/2018 8:04 |  |  | 10668 | Roadway |  | 20181120PWA_05 | Infrastructure (network-based) | -37.6822 | 144.4205 | 1 | Powercor | Report | 13528 | 0.024126 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Other
Crew made repairs replaced stolen cable and re-instated the public lighting. | 92-130 ABEY ROAD, COBBLEBANK VIC 3338 | 30336485 | Vandalism;Copper theft | [6 empty] | Crew attended incident site after reports of public lights not working. Crew found two pits had been interfered with. Cable between them had been stolen, six lights not operating. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN011 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/10/2018 0:01 |  |  | 10670 | Roadway |  | 20181120PWA_06 | Infrastructure (network-based) | -37.7048 | 144.5858 | 1 | Powercor | Report | 13530 | 0.0038762 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
Isolated and made safe. Repairs made and supply restored. | 30 LINDSAY STREET, MACLEOD VIC 3085 | A144137 |  | Wind |  | Conductor clashing |  |  | 1 | Strong winds led to HV conductors being down during a thunderstorm (corner of Somers Avenue and Lindsay Street). | Conductor (bare) | 0 | 0 | 0 |  | NH02 | Having considered related events and multiple ACR operations it is suspected that preform failed due to a fault caused by conductor clashing. Strong winds and lightning storms were reported in the area on 20 November 2018. The resultant fault current caused the preform to fail disconnecting one phase (footpath site) of the HV conductor from the HV strain insulator. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2018 16:52 |  |  | 10676 | Residential |  | 20181121JEM_03 | Infrastructure (network-based) | -37.7176 | 145.0778 | 1 | Jemena | Report | 14980 | 0.033837 | 22kV AC | Essendon Airport | 3085 | Macleod | Conductor
The crew isolated the damaged assets, completed repairs. Supply restored. | 1750 WALSHS BRIDGE ROAD, NUMURKAH VIC 3636 | 33087281 |  | Lightning | [5 empty] | Vicfire reported grass fire under pole at the incident location. Grass fire has been extinguished. Powercor fault crew found lightning had struck the overhead 22kV line causing damage to the pole top assets, debris from the strike has fallen onto grass igniting a small fire. There was no reported injuries, no third party property damage. | Crossarm (steel);Pole (concrete) | 2 | 2 | 2 |  | NKA002 | Lightning strike | Grassfire | 20/11/2018 15:10 | 1 | Small: 10 - 1000 sq.m | 10674 | Roadway |  | 20181121PWA_01 | Infrastructure (network-based) | -36.099 | 145.3982 | 1 | Powercor | Report | 13534 | 0.026317 | 22kV AC | Shepparton Airport | 3636 | Numurkah | Lightning
On arrival crew isolated supply and carried out repairs. LEI organised to check for HVI | 55 RESERVOIR ROAD, STRATHDALE VIC 3550 | 32051959 |  | Blown branch/vegetation |  |  |  |  | 1 | During storm Customer reports of supply outage and tree damaged at incident location. Crew found a tree branch broken from tree and had damaged conductors. Suspected HVI There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BGO022 | Vegetation: Trees Incident | HV injection;Loss of supply;Damage to network assets | 20/11/2018 18:19 |  |  | 10683 | Roadway |  | 20181121PWA_07 | Infrastructure (network-based) | -36.7729 | 144.3114 | 1 | Powercor | Report | 13753 | 0.0001875 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3550 | Strathdale | Trees
On arrival crew isolated supply and carried out repairs | BALLAN ROAD, WYNDHAM VALE VIC 3024 | 30337996 | Copper theft | [6 empty] | A powercor employee reported a public lighting cable had been stolen between a number of pits at the incident location. A number of pit lids had been removed and service cable left exposed. there was no fire, no reported injuries or third party property damage | Services cable;Services pit | 2 | 2 | 2 |  | WBE014 | copper theft | Damage to network assets | 43142.4431 |  |  | 10684 |  |  | 20181121PWA_08 | Infrastructure (network-based) | -37.8557 | 144.5897 | 1 | Powercor | Report | 13546 | 0.039235 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
Jemena dispatched Network Operator, Faults Crew and Work Practices to investigate and assist. Site was made safe and assets were evaluated for damage. | 530 CRAIGIEBURN ROAD, WOLLERT VIC 3750 |  | Working too close to overhead lines |  |  |  | Not followed | Phase to earth | 1 | HV customer's crane operator made contact with high voltage overhead conductors (customer side) | Conductor (bare) | 0 | 0 | 1 | High Voltage customer |  | Crane operator had boom fully extended and raised making contact with overhead conductors | Medical attention (first aid/doctor/hospital) | 21/11/2018 14:23 |  |  | 10685 |  |  | 20181122JEM_01 | Infrastructure (network-based) | -37.6024 | 144.9727 | 1 | Jemena | Report | 13926 | 0.041148 | 22kV AC | Essendon Airport | 3750 | Wollert | Vehicle
The crew isolated the damaged underground cable and made repairs, supply restored | 380 LONSDALE STREET, MELBOURNE VIC 3000 | 12696279 | Working too close to underground cables | [5 empty] | 1 | Citipower received a call from a contractor working adjacent 380 Lonsdale Street, Melbourne, 3000. Contractor advised that an underground cable had been damaged by an electric jack hammer and the person operating it had received an electric shock. | Cable | 0 | 0 | 0 |  | JA011 | Interference -Cable struck by jack hammer during plumbing works | Loss of supply | 23/11/2018 14:10 |  |  | 10695 | Commercial |  | 20181126PWA_02 | Infrastructure (network-based) | -37.8124 | 144.9612 | 1 | CitiPower | Report | 13564 | 0.016176 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew checked conductors, no damage found | 1421 BOALS ROAD, NUMURKAH VIC 3636 | 30347324 | Blown detritus | Wind |  |  |  |  | 1 | Vic Fire reported a grass fire at incident location. On arrival crew found wind blown fencing material had struck line causing fire. There were no injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | NKA006 | Wind blown fencing material | Grassfire | 26/11/2018 11:48 | 1 | Small: 10 - 1000 sq.m | 10696 | Roadway |  | 20181127PWA_01 | Infrastructure (network-based) | -36.0527 | 145.3499 | 1 | Powercor | Report | 17608 | 0.013154 | 22kV AC | Shepparton Airport | 3636 | Numurkah | Other
Isolated supply so MFB could put out fire. Pole was replaced due to fire damage | 767-769 SYDNEY ROAD, COBURG NORTH VIC 3058 |  | Unknown external/community factor | Fire |  |  |  |  | 1 | LV ABC down due to a factory fire. Fire also damaged the pole | Conductor (ABC) | 2 | 2 | 2 |  |  | Factory fire bring down LV ABC | Damage to network assets | 43112.7194 |  |  | 10711 |  |  | 20181201JEM_02 | Infrastructure (network-based) | -37.7328 | 144.9646 | 1 | Jemena | Report | 17754 | 0.039634 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg North | Other
service cable replaced | UNIT 1 17 WESTMINSTER DRIVE, WERRIBEE VIC 3030 | 30108975 |  |  |  | Moisture ingress;Corrosion;Neutral fault |  |  |  | Customer received an electric shock as he made simultaneous contact between his hands on the meter box and his feet while standing on the wet ground. | Service conductor | 0 | 0 | 0 |  | WBE023 | Perforated and corroded service cable - mid span | Minor shock | 43442.4167 |  |  | 10721 | Residential |  | 20181204PWA_03 | Infrastructure (customer connection) | -37.8933 | 144.6358 | 1 | Powercor | Report | 13599 | 0.029157 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | OH Cable
Neutral connection replaced | 8 COLLARD STREET, NEWINGTON VIC 3350 | 32001037 |  |  |  | Corrosion;Neutral fault |  |  |  | The customer was having a shower at the time and received an electric shock when she contacted the metallic water tap with her hands and her feet were simultaneously in contact with the shower waste. | Service conductor | 0 | 0 | 0 |  | BAS014 | Corroded neutral connection at POA | Minor shock | 43170.6042 |  |  | 10723 | Residential |  | 20181204PWA_05 | Infrastructure (customer connection) | -37.5646 | 143.8316 | 1 | Powercor | Report | 13601 | 0.0020185 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Newington | Connection
Service replaced | 15 ALBERT STREET, ST KILDA VIC 3182 | 30213023 | Vehicle | [5 empty] | 2 | Customer went to have a shower and received an electric shock while touching the tap with her hand and simultaneously standing bare foot on the wet concrete shower base. Residents had also noticed lights flickering and appliances not functioning properly at the property. | Service conductor | 0 | 0 | 0 |  | SK001 | Service cable to house appeared to have been struck by a vehicle resulting in a break of the neutral conductor. | Minor shock | 43323.7708 |  |  | 10734 | Residential |  | 20181204PWA_16 | Infrastructure (network-based) | -37.8665 | 144.9804 | 1 | CitiPower | Report | 13612 | 0.030119 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Vehicle
Service replaced | 181 ROSLYN ROAD, BELMONT VIC 3216 | 30071172 |  |  |  | Corrosion;Neutral fault |  |  | 2 | Customer received an electric shock from the bath tap whilst exiting the shower when her hand made simultaneous contact with the metal tap whilst standing on the saturated bathtub. | Service conductor | 0 | 0 | 0 |  | GCY023 | Corroded neutral connection | Minor shock | 23/11/2018 8:45 |  |  | 10739 | Residential |  | 20181204PWA_21 | Infrastructure (customer connection) | -38.1741 | 144.331 | 1 | Powercor | Report | 13617 | 0.010137 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
On arrival crew carried out repairs. | MOOROOKYLE, 3071 CRESWICK-NEWSTEAD ROAD, SMEATON VIC 3364 | 30000828 | Vandalism;Copper theft | [6 empty] | An Electrix Asset Inspector reported a length of copper earth conductor had been cut and removed from a Powercor pole at the incident location. The copper earth conductor had been cut above the ground and at the top of the possum guard on the pole, and had been removed. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN009 | Copper theft | Damage to network assets | 17/11/2018 7:34 |  |  | 10745 | Roadway |  | 20181205PWA_04 | Infrastructure (network-based) | -37.2914 | 143.9556 | 1 | Powercor | Report | 13628 | 0.011346 | Earthing cable | Ballarat Aerodrome | 3071 | Smeaton | Other
Fault crew dispatched. Fuse replaced | 778 WHITELAWS TRACK, BUFFALO VIC 3958 | LIS2024579 |  |  |  | Candled fuse |  |  |  | report of possible fuse candling | EDO fuse | 0 | 0 | 0 |  | FTR21 | Candling fuse. | Pole-top fire | 43292.7188 | 1 | Negligible: no ground fire | 10746 |  |  | 20181205SPN_02 | Infrastructure (network-based) | -38.6354 | 146.1125 | 2 | AusNet Services Distribution | Report | 17860 | 0.015444 | 22kV AC | Morwell (Latrobe Valley Airport) | 3958 | Buffalo | Fuse
A faults crew assessed the site and determined the is safe for tonight but tree cutters are required to attend and clear trees tomorrow. 27/11/2018 - ESV on site today with a United Energy vegetation team member and they walked through the span. United Energy have completed the majority of tree cutting using Live Line techniques and there is a further bit of tidy up work required tomorrow as one span requires more clearance but in summary, all spans are compliant. The railway spans are programmed to be completed on Thursday as Live Line suppression and traffic control is required. The work was completed and all spans are now compliant. | COOK ROAD, HMAS CERBERUS VIC 3920 | 8826921 |  | Alive;MEC | [5 empty] | HMS Cerberus Defence Base - Large tree branch on the wires causing sparking on the corner of Stony Point Road and Cook Road. A large cypress hedge located at the defence force base is growing close to 6 bays of HV overhead conductors between pole No's LIS 8826921 and 1110586. Emergency services were on site following a burnt branch being identified. | Conductor (bare) | 0 | 0 | 0 |  | HGS 31 | Vegetation: Trees Incident | Other vegetation | 21/11/2018 21:22 | 1 | Negligible: no ground fire | 10760 | Roadway |  | 20181206UTD_06 | Infrastructure (network-based) | -38.3656 | 145.2015 | 1 | United Energy Distribution | Report | 18387 | 0.034133 | 22kV AC | Moorabbin Airport | 3920 | Hmas Cerberus | Trees
On arrival crew isolated supply and carried out repairs. | LEAKES ROAD, TARNEIT VIC 3029 | 30548328 | Working too close to underground cables | [5 empty] | 1 | Gary Shortland from Winslow Infrastructure Pty Ltd advise that a HV cable had been pulled up with a grader at the incident location. Crew found that a recently installed and commissioned HV cable associated with a line relocation project had been damaged. There was no fire, no reported injuries or third party property damage.. | Cable | 2 | 2 | 2 |  | TNA013 | Cable dug up during road construction works | No Go Zone (contact);Damage to network assets | 43263.3965 |  |  | 10766 | Roadway |  | 20181207PWA_01 | Infrastructure (network-based) | -37.8347 | 144.6961 | 1 | Powercor | Report | 13657 | 0.025012 | 22kV AC | Laverton Raaf | 3029 | Tarneit | Dug up
Following the shock the Technician immediately contacted his Supervisor and was taken for medical assessment which did not identify any health impacts. Additionally the incident scene was preserved and WorkSafe were notified of the incident by Telephone (Ref 260218-3-AH-BM). Safety Gram SG2018006 communicated to the business. | 412 COMMERCIAL ROAD, MORWELL VIC 3840 | [5 empty] | Ineffective planning/procedures/processes | Phase to earth |  | IMS 232583. Secondary technician was cable tying a newly installed wiring loom he came in contact with a live 240V ac supply stud in a CT marshalling cubical receiving a shock to the back of his hand. | CT Marshalling box in switchyard;Other | 0 | 0 | 0 |  |  | The technician was securing the cable loom to a panel with cable ties when he inadvertently contacted a live (240V AC) stud with the back of his hand resulting in an electric shock. The JSA discussion for the work did not include the task of cable tying the loom or adjacent live contact points; and insulated caps were not fitted to the live studs (contact points). | Minor shock | 26/02/2018 19:15 |  |  | 10065 | Industrial |  | 20180627SPN_01 | Infrastructure (network-based) | -38.2541 | 146.4146 | 1 | AusNet Services Transmission | Report | 12508 | 0.018402 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Other
The crew took photos and advised their supervisor of the unsafe situation. Supply was isolated and a defect notice issued. Zinfra advised New Connections of the defect and that a new CES is required for this job to go ahead. The crew and their supervisor requested that ESV are advised to follow up with the REC (Mohammed 0418 205 657). | 15 BELVEDERE AVENUE, WHEELERS HILL VIC 3150 |  | Caused by REC/contractor |  |  | Fault on customer installation |  |  | 2 | A Burwood Metering and Servicing crew had a new connection to complete at a group meter panel at 15 Belvedere Avenue, Wheelers Hill on 22/06/2018. Upon arrival they found the group meter panel had been livened up via the BSP, including the sub mains from the Group Meter panel to unit 1 where there are customers living. There is evidence of live wires being connected in the Group Meter panel illegally. The crew tested all connections and confirmed the sub mains are alive from the Group Meter Panel to Unit 1. | Customer installation | 0 | 0 | 0 |  |  | The group meter panel had been energised by wiring from the Builders Supply Pole to the new meter enclosure and an occupancy energised. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/06/2018 13:30 |  |  | 10068 | Construction |  | 20180627UTD_01 | Infrastructure (network-based) | -37.8968 | 145.1766 | 1 | United Energy Distribution | Report | 12686 | 0.028344 | Low voltage AC (<1kV) | Moorabbin Airport | 3150 | Wheelers Hill | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a damaged and corroded O/H Service Active Conductor on the line side of the Service Protection Device at the POA. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 9 BARRAND STREET, APOLLO BAY VIC 3233 |  |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr Craig Philp received an electric shock from a metallic enclosure placed around the timber Meter Panel at the side of the property when his hand made simultaneous contact with the metallic enclosure whilst standing on the wet ground wearing work boots. | Service conductor | 2 | 2 | 2 |  |  | The damage to the O/H Service Active Conductor was caused by the metal Roof Gutter in contact with the O/H Service which had rubbed through the insulating sheath of the Active Conductor energising the metallic Roof Gutter and conductive building fixtures. | Minor shock | 24/05/2018 14:30 |  |  | 10077 | Residential |  | 20180629PWA_04 | Infrastructure (network-based) | -38.7575 | 143.6624 | 1 | Powercor | Report | 12522 | 0.0098657 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | OH Cable
Crew attended and replaced missing cable. Reported to local police. | SUNSET DRIVE, EPPALOCK VIC 3551 | 32053864 | Vandalism;Copper theft | [6 empty] | Employee report vandalism and copper cable stolen from meter box at Apex Park , Sunset Dr, Eppalock that feeds BBQâ€™s. There were no shocks, injuries or ground fire start. | Services cable | 2 | 2 | 2 |  | BET005 | Vandalism and Theft | Damage to network assets | 43106.4792 |  |  | 10085 | Public space |  | 20180704PWA_02 | Infrastructure (network-based) | -36.868 | 144.5022 | 1 | Powercor | Report | 12536 | 0.0086701 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Eppalock | Other
On arrival crew isolated supply and carried out repairs | 2 MARIA STREET, LAVERTON NORTH VIC 3026 | 30224019 | Working too close to overhead lines | [6 empty] | Customer, (Gibson Austwide Pty Ltd.), reported that one of their personnel had inadvertently contacted a 4c x95mm sq LVABC overhead service while maneuvering earth moving plant on their property at No.2 Maria St Laverton. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | LVN022 | Excavator struck service | No Go Zone (contact);Damage to network assets | 43165.4792 |  |  | 10086 | Industrial |  | 20180704PWA_03 | Infrastructure (network-based) | -37.8378 | 144.7837 | 1 | Powercor | Report | 12537 | 0.019411 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Other
Site made safe Circuit at substation isolated to conduct repairs | 1A LAWSON STREET, RESERVOIR VIC 3073 |  |  |  | Highly unlikely | Defective component |  |  | 2 | LV conductor cut mid span due to friction against spreader (spreader clip detached) causing conductor to come to ground. | Conductor (bare) | 0 | 0 | 0 |  |  | friction between conductor and spreader (spreader clip detached) causing conductor to come to ground | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43288.3979 |  |  | 10095 | Residential |  | 20180707JEM_01 | Infrastructure (network-based) | -37.7193 | 145.0146 | 1 | Jemena | Report | 12550 | 0.019598 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Conductor
A faults crew attended and made the site safe and the electrical infrastructure repaired under Access Authority conditions. Supply was restored upon completion. The crew were instructed by their supervisor to take photos and the event will be reported to Energy Safe Victoria. | 57 ELLERINA ROAD, MOUNT MARTHA VIC 3934 |  | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Customers who reside in Ellerina Road advised they have lost their electricity supply and a passerby reports there are powerlines down on the nature strip in front of 55 and 57 Ellerina Road. An excavator has contacted the white and blue phase LV conductors and brought them down along with two LV cross arms located on the HV/LV poles at either side of the conductor span. The driver of the excavator refused to provide his licence and advised his name was Peter Ellis and the company was Impact Demolitions. There were no injuries, electric shocks or damage to plant sustained. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  |  | Breach of clearances whist operating an excavator. | No Go Zone (contact);Damage to network assets | 28/06/2018 9:30 |  |  | 10104 | Residential |  | 20180709UTD_05 | Infrastructure (network-based) | -38.3008 | 144.9971 | 1 | United Energy Distribution | Report | 12563 | 0.033115 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | Vehicle
Section was isolated and made safe. | 100 OLYMPIA STREET, TOTTENHAM VIC 3012 | pole no. A033114 |  |  |  | Rot | Followed but inappropriate |  | 1 | During restoration works, as the faults crew was applying earths to Intermediate Tee off Pole A033113 for the access permit to replace HV Cable Head Termination Pole A033114 (for details of this pole failure, refer to OSIRIS incident report 20171206JEM_02), pole A033113 - which is the adjacent to pole A033114 - also failed just below ground line. No personnel were injured as a result of the second pole failing. A copy of the investigation report is attached in the "Notes & Findings" section. | Conductor (bare);Pole (wood);Cable;Aluminium;Disconnector/isolator;Connector/termination | 1 | 0 | 0 |  | TH12 | The independent post failure assessment of pole A033113 was conducted at the Tullamarine depot suggesting the previous pole condition based on sound wood and girth measurements as accurate. This assessment found that the pole failed 410mm below ground level with a girth of 640mm with extensive internal and external decay of the pole, below prescribed excavation depths. Jemenaâ€™s own assessment by the Network Integrity & Performance team, found that significant decay was evident on the pole at approximately 200mm below ground level. Had the inspector correctly identified this decay it would have categorised the pole as Unserviceable or Limited Life. It is likely that the inspector did not excavate to prescribed depths or measure the girth at required levels during the last inspection as the post failure assessment measured a significantly lower girth at fracture (640mm at 410mm below ground level). The JEN Asset Inspection Manual requires inspectors to excavate down to 300mm below ground line to assess pole condition. Girth measurements are to be taken at the minimum diameter below ground level (Refer to Chapter 4 Jemena Asset Inspection Manual). The investigation team recommends that Jemena consider an instruction for deeper excavation in cases where decay appears to proceed below 300mm from ground level. In this instruction, for example, a maximum depth cap and observable decay patterns should be considered. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 42778.3597 |  |  | 10109 | Industrial |  | 20180710JEM_02 | Infrastructure (network-based) | -37.804 | 144.8568 | 1 | Jemena | Report | 12568 | 0.015435 | 22kV AC | Essendon Airport | 3012 | Tottenham | Pole
A LEI and faults truck attended and tested between the main neutral bar and the metal meter box and measured 150 volts to an independent earth. After further investigation, it was noted that the grey twisted service cable was showing signs of damage midway between the pole and the POA where it had previously been damaged by a tree on the customers property. The faults crew commenced to replaced the damaged grey twisted service and identified the neutral conductor was completely worn through with the active conductor having only two strands left. Once the single phase aerial cable had been replaced by the faults crew, the LEI performed an NST that passed and also re-tested the voltage on the main neutral bar and the metal meter enclosure and measured 2v with load applied. Supply was left on. | 2 FORBES STREET, RYE VIC 3941 |  |  | Within clearances |  | Electrical breakdown |  | Phase to earth | 2 | Caller advised they received a slight electric shock from the main switchboard a short time ago. The lights had been flickering and dimming with intermittent supply. The customer went to the main switchboard to check the supply and experienced a minor electric shock to his hand when he touched the metal meter enclosure whilst standing on the wet ground. The occupier proceeded to contact the United Energy faults and emergencies call centre. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Minor shock | 30/06/2018 11:30 |  |  | 10119 | Residential |  | 20180711UTD_01 | Infrastructure (network-based) | -38.3935 | 144.8109 | 1 | United Energy Distribution | Report | 12578 | 0.02816 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Trees
A LEI and faults truck attended and commenced an investigation. On arrival the LEI performed a series of tests around the area the dog apparently received the shock. The nearest pit located on the left hand side of 20 Heather Avenue was opened and various parts inside the pit enclosure were tested. 20v was measured leaking out of the ports within the pit to an independent earth including 30v from the pit located outside number 18 Heather Avenue. The underground supply to the pits was isolated at the FOLCB's and connections checked on the poles. The underground cables were taken out of the ports in the pits, checked and reterminated. There appeared to be signs of insulation discolouring at the ends where the cables had been inside the ports which may be a sign of compromised insulation. After the cables were reterminated, NST was completed at the installations that passed and the voltage within the pits had reduced to acceptable levels. No voltage was measured outside of the pits before or after the repairs. As the crew was packing up, a resident come out and advised the dog received the shock near the Telstra pillar on the corner. The LEI tested around the structure and no stray voltages were identified. As there was insufficient factual information available or forthcoming in respect to the circumstances involved, no conclusive finding was ascertained, therefore the cause is classified as being undetermined. | SALISBURY ROAD, ASHWOOD VIC 3147 | 2312412 |  | Precipitation |  | Leakage |  | Phase to earth | 2 | The City of Monash provided a second hand report that one of their residents dog was electrocuted at the pit located on the corner of Salisbury Road and Heather Avenue. The local council reported that a residents dog apparently received a severe electric shock at the front of the property on the corner of Salisbury Road and Heather Avenue. | Cable | 0 | 0 | 0 |  |  | The cause was undetermined although there was a voltage measured at electricity pits near the corner where the event occurred. | Fatality of livestock, pet or companion animal | 43138.3542 |  |  | 10123 | Roadway |  | 20180711UTD_02 | Infrastructure (network-based) | -37.8727 | 145.1096 | 1 | United Energy Distribution | Report | 12593 | 0.029896 | Low voltage AC (<1kV) | Moorabbin Airport | 3147 | Ashwood | UG Cable
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 1 Volt no load to 60 Volts maximum load. Fault Crew discovered the loose and corroded termination of the 4 wire grey twisted service neutral conductor into the neutral terminal of the customers FOLCB at the POA. Crew replaced the existing grey service with a 4 wire ABC service. Crew performed NST at the POA with pass result recorded. CTA/LEI performed NST at the installation main switchboard with a pass result recorded. Installation left ON supply. | 40 BRISTOL ROAD, TORQUAY VIC 3228 | 33042136 |  |  |  | Corrosion |  | Phase to earth |  | James was standing at the ensuite sink when he felt a slight tingle to his right hand adjusting the tap, with his mouth under the flow of water. | Service conductor | 2 | 2 | 2 |  | WPD032 | Corroded connection | Minor shock | 43257.3125 |  |  | 10127 | Residential |  | 20180712PWA_04 | Infrastructure (customer connection) | -38.3311 | 144.3201 | 1 | Powercor | Report | 12597 | 0.004912 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an unstable voltage inherent in the neutral reticulation system, which is likely resulting from inconsistent load balancing on the LV Reticulation Circuit. The attending Powercor Fault Crew checked the condition of all conductors and disconnected and remade all terminations between the distribution system and the Point of Attachment (POA) of the installation. Further work was undertaken by the Supply Quality Group to break and remake all network neutral supply connections back to the Sub-station. Subsequent voltage testing recorded a marginal improvement to 5.0 Volts following initial network reticulation remediation work to ensure the integrity of the neutral supply system. A final NST test was carried out on the installation which confirmed a Pass result. The Installation was left ON supply. | 40 MORGAN STREET, TIMBOON VIC 3268 | 30045575 |  |  |  | Out of balance load |  | Phase to earth |  | Mr Brad Kerr, Plumbing Contractor was under the house installing a gas pipe when he received an electric shock as he made simultaneous contact with the metallic frame of a structural support beam and his wet knees while kneeling on the wet ground. | Conductor (bare) | 2 | 2 | 2 |  | TRG003 | Circuit imballance | Minor shock | 22/05/2018 11:00 |  |  | 10129 | Residential |  | 20180712PWA_06 | Infrastructure (network-based) | -38.4789 | 142.9802 | 1 | Powercor | Report | 12599 | 0.035706 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Timboon | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customerâ€™s POA. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 17 EAST STREET, KERANG VIC 3579 | 30028492 |  |  |  | Corrosion |  | Phase to earth |  | Mr Steven Walsh was standing on the back Veranda opening the Fridge Door when he received an electric shock as he made simultaneous contact between his hand on the metal handle of the Fridge while standing on the concrete veranda. | Service conductor | 2 | 2 | 2 |  | KGT002 | Corroded connection | Minor shock | 43440.75 |  |  | 10130 | Residential |  | 20180712PWA_07 | Infrastructure (customer connection) | -35.7224 | 143.9187 | 1 | Powercor | Report | 12600 | 0.01639 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3579 | Kerang | Connection
On arrival crew confirmed site safe and arranged repairs | PAPAS VIEW, WYNDHAM VALE VIC 3024 | Pa0163525 | Copper theft | [6 empty] | Employee attending the new uncommissions KSS Papas Stanmore in the new Jubilee estate at Wyndham Vale, found that thieves had opened both locked doors of the KSS and stolen copper earth cables from the LV end on the S/S, including copper bus bars. There was no fire, no reported injuries or third party property damage. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | WBE014 | Cable theft | Damage to network assets | 43318.3653 |  |  | 10133 | Roadway |  | 20180713PWA_01 | Infrastructure (network-based) | -37.847 | 144.5932 | 1 | Powercor | Report | 12603 | 0.026345 | Earthing cable | Laverton Raaf | 3024 | Wyndham Vale | Other
Crew isolated HV supply to substation pole and ground type transformer removed from site. | 99 DERBY ROAD, SUNSHINE VIC 3020 | 30119153 | Copper theft | [6 empty] | Customer reports theft of cables at ground type substation site. Crew attended and found copper earths and LV mains cables cut and removed from site. Site is being demolished by contractors and substation has been listed for abolishment in the next month. HV supply was still connected when theft occurred. Crew found a length of timber with a bracket attached that was used to open powder filled HV fuses at the substation.. Contractor advises thieves stole copper in building switch room a week prior. There were no shocks, injuries or ground fire start. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | SSE034 | Copper Theft | Damage to network assets | 13/06/2018 11:08 |  |  | 10135 | Industrial |  | 20180713PWA_02 | Infrastructure (network-based) | -37.791 | 144.8332 | 1 | Powercor | Report | 12606 | 0.013193 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine | Other
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard resulted in a reading of 1 Volt no load to 12 Volts maximum load. Fault Crew discovered the loose and corroded termination of the 4 wire XLPE U/G service neutral conductor into the neutral terminal of the FOLCB on the POWERCOR pole. Crew replaced the FOLCB and re-terminated the neutral conductors. CTA/LEI performed voltage test from an independent earth spike to neutral bar and earth bar of the MSB resulted in a reading of 1 Volt no load to 2.5 Volts maximum load. Installation left ON supply. | 40 CLOVER STREET, LARA VIC 3212 | 30278617 |  |  |  | Corrosion |  | Phase to earth |  | Melissa was having a shower when she felt a slight tingle to her right hand adjusting the shower tap, while standing bare foot on the shower base in the flow of the water. | Connection box | 2 | 2 | 2 |  | FNS012 | The incident occurred due to a loose and corroded termination of the 4 wire XLPE U/G service neutral conductor into the neutral terminal of the FOLCB on the POWERCOR pole | Minor shock | 43410.9167 |  |  | 10136 | Residential |  | 20180713PWA_03 | Infrastructure (network-based) | -38.0205 | 144.4199 | 1 | Powercor | Report | 12608 | 0.030946 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Connection
Fault crew dispatched to make safe and investigate. On arrival, crew found and extinguished small ground fire about 10cm sq. Shutdown organised for a construction crew to replace the leads on TN099 and restore supply. | 440 FIRMINS LANE, HAZELWOOD NORTH VIC 3840 | TN099 / LIS2615217 |  |  |  | Mechanical breakdown |  | Phase to earth |  | IMS 234390 - flash over at pole (switch TN099). Small (approx 30cm sq) burnt area observed at the base of the pole | Any other type | 0 | 0 | 0 |  | MWT32 / TGN23 | Fault crew called to fault and small fire at Firmins lane Hazelwood. XLPE leads have been rubbing together at the gas switch causing one phase to rub through resulting in a fault to the earth screed of the other phase. Shutdown organised for a construction crew to replace the leads on TN099 and restore supply. | Other electricity related | 43441.8465 | 1 | Localised: less than 10 sq.m | 10134 | Agricultural |  | 20180713SPN_01 | Infrastructure (network-based) | -38.2541 | 146.476 | 1 | AusNet Services Distribution | Report | 12605 | 0.023098 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Hazelwood North | AF Other
On arrival crew isolated supply and carried out repairs. | 178-198 PAYNES ROAD, THORNHILL PARK VIC 3335 | 30238216 | Vandalism;Copper theft | [6 empty] | A Powercor fault crew reported a vandalised customer service at the incident location. The crew found that a customer UG cables from the pit to meter (this is a temporary supply, BTS) had been stolen and the meter door was opened. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | TNA013 | Vandalism, Copper theft | Loss of supply;Damage to network assets | 18/06/2018 10:09 |  |  | 10150 | Roadway |  | 20180716PWA_06 | Infrastructure (network-based) | -37.7184 | 144.6358 | 1 | Powercor | Report | 12626 | 0.0092894 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Other
Voltage test with an independent earth and various parts of the electrical installation including the Powercor assets, revealed a loose service neutral termination at the pole end. The neutral conductor termination split bolt was found loose and corroded. Neutral service termination removed and replaced by Powercor faults truck. NST Test by Powercor fault truck at POA OK passed. NST Test at meter position by Powercor fault truck OK passed. NST Test at customers main switch board by CTA OK passed. | 558 DAYLESFORD-TRENTHAM ROAD, MUSK VIC 3461 | 30015078 |  |  |  | Mechanical breakdown |  | Phase to earth |  | The customer was showering at the time when she received an electric shock when she simultaneously contacted the metallic water taps with her hands whilst standing on the wet shower base. | Connector/termination | 2 | 2 | 2 |  | BAN011 | Loose connection | Minor shock | 15/06/2018 0:00 |  |  | 10155 | Residential |  | 20180716PWA_08 | Infrastructure (network-based) | -37.3726 | 144.1953 | 1 | Powercor | Report | 12633 | 0.036297 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3461 | Musk | Connection
The faults crew isolated "Victoria-Middle" substation and replaced the LV earth. Supply was restored upon completion. | VICTORIA ROAD, PEARCEDALE VIC 3912 | 3302144 | Theft | [5 empty] | 2 | A faults crew attended HV spur fusing FS1247 located on the corner of Victoria and Middle Roads and replaced the HV red phase 16amp powder filled fuse that operated as a result of a possum on the concrete pole - LIS No. 3302144. When in attendance for a fault, the crew identified the copper LV earth had been removed from the pole by unknown persons. | Copper;Earth/earthing | 0 | 0 | 0 |  | HGS33 | Copper theft. | Damage to network assets | 43166.4132 |  |  | 10146 | Roadway |  | 20180716UTD_02 | Infrastructure (network-based) | -38.1946 | 145.228 | 1 | United Energy Distribution | Report | 12619 | 0.0013704 | 12.7kV AC (SWER) | Moorabbin Airport | 3912 | Pearcedale | Animal
A LEI attended and performed installation tests and no faults were identified. No voltages were identified on the water tap with no current flowing through the water mains with load and no applied. A NST passed and supply was left on with the occupier advised of the investigations findings. | 2 WHITESIDE STREET, SPRINGVALE VIC 3171 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | Customer called to advise that he received an electric shock from the outside tap today. He is okay and they have no electricity supply problems. The occupier received an electric shock from the front external water tap and proceeded to contact the United Energy faults and emergencies call centre. The victim advised the LEI the shock occurred when he attempted to turn the tap on when the water company contractors were replacing the street water mains at the time. When he turned the tap off moments later, no shock was felt. | Customer installation | 0 | 0 | 0 |  |  | No cause was identified but it was noted that water company workers were working in the street at the time of the fault. | Minor shock | 43227.5208 |  |  | 10152 | Residential |  | 20180716UTD_03 | Infrastructure (network-based) | -37.9358 | 145.1545 | 2 | United Energy Distribution | Report | 12629 | 0.027803 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Other
On arrival crew isolated supply and carried out repairs. | 3-5 ROCKLEY ROAD, SOUTH YARRA VIC 3141 | 30218878 | Working too close to underground cables | [5 empty] | 1 | Customer rang to report loss of supply to building and people stuck in elevator. Crew observed U/G boring contractor in street at that time in the vicinity of U/G cable in street. Boring crew unaware of any contact with cable. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | TK002 | Boring operations | Loss of supply;No Go Zone (contact);Damage to network assets | 27/06/2018 14:45 |  |  | 10179 | Roadway |  | 20180719PWA_02 | Infrastructure (network-based) | -37.8387 | 144.9996 | 1 | CitiPower | Report | 12666 | 0.015155 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Dug up
All premises where on supply at that time. Crew isolated each premises in the pits and issued defect notice for repairs. | 12 MUSCOVY WAY, WERRIBEE VIC 3030 |  | Vandalism;Copper theft | [6 empty] | Report from REC of 10 new houses in subdivision with damage to wiring at meter position of each house. There was no fire, no reported injuries. | Customer installation | 2 | 2 | 2 |  |  | Copper theft | Loss of supply | 27/06/2018 10:53 |  |  | 10180 | Residential |  | 20180719PWA_03 | Infrastructure (network-based) | -37.9076 | 144.6072 | 1 | Powercor | Report | 12668 | 0.03277 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H neutral screen conductor between the POA and the service pole. The attending Powercor Fault Crew replaced the O/H Service Neutral screen conductor with a new twisted service wire. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 278 PAKENHAM STREET, ECHUCA VIC 3564 | 32180565 |  |  |  | Corrosion |  | Phase to earth |  | Mr Dubeurg was turning on the front garden tap when he received an electric shock as he made simultaneous contact with one hand on the metal tap and the wet ground which he was standing on. | Service conductor | 2 | 2 | 2 |  | ECA003 | Corroded service | Minor shock | 29/06/2018 8:45 |  |  | 10182 | Residential |  | 20180719PWA_05 | Infrastructure (network-based) | -36.1287 | 144.7466 | 1 | Powercor | Report | 12671 | 0.023198 | Low voltage AC (<1kV) | Shepparton Airport | 3564 | Echuca | OH Cable
Fault crew arrived to make safe and carried out repairs | 115 MILLAR ROAD, YANAKIE VIC 3960 | LIS 2016596 |  |  |  | Corrosion;Defective component |  | Phase to earth | 2 | IMS 234157 -Field crew arrived at a fault job and found a live 22kV conductor touching the ground holding up by flex and D at Tee off pole number LIS 2016596. | Conductor (bare) | 0 | 0 | 0 |  |  | The steel conductor was found to be corroded at the damper on pole LIS 2016596. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/06/2018 5:42 |  |  | 10192 | Agricultural |  | 20180720SPN_01 | Infrastructure (network-based) | -38.8203 | 146.1987 | 1 | AusNet Services Distribution | Report | 12682 | 0.02331 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Yanakie | Conductor
LEI dispatched to make safe and investigate NST test carried out and passed. Voltage from independent earth to water meter was measured at 0.9 volts and 0A through water pipes at meter. Water meters checked along Tunbridge Street and all below 1V except for Number 12 Tunbridge Street, (Closest to Substation) voltage from independent earth to water meter was 5V 0A. Check substation LV Earth to independent earth measured 6 Volts and current ranged between 3 - 4.5amps over 1 hour period. Fault Truck called in for more testing of substation and found out of balance (White phase). LV services in street re-balanced as close as possible with permanent residences. Poly logger installed on substation to check/monitor of balance of LV circuit. | 14 TUNBRIDGE STREET, RHYLL VIC 3923 | LIS2805593 |  |  |  | Out of balance load |  | Phase to earth | 2 | IMS 234220 - Water meter reader reported receiving a tingle off the water meter. | Service conductor | 0 | 0 | 0 |  | PHM11 | Substation found to be unbalanced resulting in voltage rise on customer earth leading to electric shock. There were no faults which would otherwise account for the electric shock. Fault Truck found substation out of balance (White phase). LV services in street re-balanced as close as possible with permanent residences. NST test performed which passed. Voltage from independent earth to water meter was measured at 0.9 volts and 0A through water pipes at meter. | Minor shock | 43197.5222 |  |  | 10193 | Residential |  | 20180720SPN_02 | Infrastructure (network-based) | -38.4699 | 145.2974 | 1 | AusNet Services Distribution | Report | 14954 | 0.0052188 | Low voltage AC (<1kV) | Moorabbin Airport | 3923 | Rhyll | AF Other
substation isolated and replaced | 159 STUDLEY COURT, DERRIMUT VIC 3030 | PA0128151 |  |  |  | Electrical breakdown |  |  | 1 | Report received of a loud bang and loss of supply. Bird contact at cable head pole caused primary fault Secondary faults occurred during re-energisation and resulted in separate ground and kiosk substation fires. This report relates to kiosk substation fire only | Pad mounted equipment/kiosk;Dropper/bridge | 0 | 1 | 0 |  | SU013 | Secondary fault due to fault current | Plant/equipment | 43316.7049 | 1 | Negligible: no ground fire | 10199 | Roadway |  | 20180723PWA_05 | Infrastructure (network-based) | -37.7916 | 144.784 | 1 | Powercor | Report | 12691 | 0.019056 | 22kV AC | Laverton Raaf | 3030 | Derrimut | Animal
On arrival crew inspected assets for damage, non found No sign of fire found | 144 BARKERS ROAD, HAWTHORN VIC 3122 | 30178382 |  | Blown branch/vegetation |  |  |  |  | 1 | A small dead branch was blown onto high voltage overhead conductors of the Q10 11kV feeder causing a number of flashovers. The Q10 11kV feeder CB tripped to lockout. There was no fire and no injuries as a result of this incident. Very windy at time of the incident. | Conductor (bare) | 2 | 2 | 2 |  | Q010 | Wind blown debris | Loss of supply;Significant disruption to the community | 23/07/2018 8:29 |  |  | 10202 | Roadway |  | 20180724PWA_01 | Infrastructure (network-based) | -37.8141 | 145.0303 | 1 | CitiPower | Report | 12694 | 0.0064074 | 11kV AC | Essendon Airport | 3122 | Hawthorn | Trees
On arrival crew isolated supply and carried out repairs. | 476 FLINDERS LANE, MELBOURNE VIC 3000 | 30288013 | Working too close to underground cables | [5 empty] | 1 | CitiPower fault crew attending an outage (JA010) found a HV UG line (JA010) was dug up by a contractor while they were digging a trench for a drainage line at the incident location. The cable was damaged by a Jack Hammer . There was no fire, no reported injuries or third party property damage | Cable | 2 | 2 | 2 |  | JA010 | Excavation works | Loss of supply;No Go Zone (contact);Damage to network assets | 23/07/2018 11:04 |  |  | 10203 | Roadway |  | 20180724PWA_02 | Infrastructure (network-based) | -37.8187 | 144.9577 | 1 | CitiPower | Report | 12695 | 0.020829 | 11kV AC | Essendon Airport | 3000 | Melbourne | Dug up
Corroded neutral clamp was replaced and voltage was retested to confirm safety. | 104 CANTERBURY STREET, FLEMINGTON VIC 3031 |  |  |  |  | Corrosion |  |  | 1 | Resident of location felt mild electric shocks from kitchen sink during dish washing. Further Investigation revealed severely corroded clamp at neutral termination point. | Neutral screen | 0 | 0 | 0 |  |  | Severely corroded clamp at neutral termination point causing a loose connection. | Minor shock | 25/07/2018 16:17 |  |  | 10218 | Residential |  | 20180725JEM_01 | Infrastructure (customer connection) | -37.7812 | 144.9228 | 1 | Jemena | Report | 12876 | 0.03966 | Low voltage AC (<1kV) | Essendon Airport | 3031 | Flemington | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a deteriorated O/H Service Cable Termination Device â€œDog Boneâ€ where the sharp end of the inner metallic rod was exposed and made contact with the energised Active Conductor of the O/H Twisted Service Cable at the Customerâ€™s POA. The attending Powercor Fault Crew replaced the Single Phase O/H Twisted Aluminium Service Cable and the Termination Device and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 5 BURKITT STREET, NUMURKAH VIC 3636 | 31025979 |  |  |  | Electrical breakdown |  | Phase to earth |  | Mr Glen Miles was standing on a metal ladder cleaning the Roof Spouting when he received an electric shock as he made simultaneous contact with one hand on the metallic Roof Spouting and his other hand on a metal ladder which was in contact with the wet ground. | Service conductor | 2 | 2 | 2 |  | NKA004 | Deteriorated O/H Service Cable Termination Device â€œDog Boneâ€ | Minor shock | 43440 |  |  | 10208 | Residential |  | 20180725PWA_02 | Infrastructure (network-based) | -36.0789 | 145.4511 | 1 | Powercor | Report | 12701 | 0.040566 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | AF Other
A faults crew attended and identified there was some minor aluminium conductor damage and a glove and barrier followed up and completed a minor repair. | 3804 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1307193 |  | Blown branch/vegetation |  |  |  |  | 2 | The Fire Authority are on site and advised that a tree branch is on the power lines and was on fire. During strong winds, a tree branch fell over the HV road side conductor outside 3804 Point Nepean Road and started to burn before dropping clear of the overhead conductors. No ground fire occurred. | Conductor (bare) | 0 | 0 | 0 |  | STO 13 | Vegetation: Trees Incident | Other vegetation | 23/07/2018 12:08 | 1 | Negligible: no ground fire | 10215 | Roadway |  | 20180725UTD_01 | Infrastructure (network-based) | -38.3195 | 144.7105 | 1 | United Energy Distribution | Report | 18388 | 0.00020718 | 22kV AC | Avalon Airport | 3804 | Portsea | Trees
ON arrival crew isolated supply and carried out repairs. HVI suspected but checks by LEI confirmed no HVI occurred. | 43 DOUGLAS ROAD, MOUNT MACEDON VIC 3441 | 32042312 |  | Wind;Alive;Fallen |  |  |  |  | 1 | A Customer called advising that a large gum tree had come down in the wind and had brought down with it the adjacent HV and LV bare open wire conductors. The fallen tree which was approximately 35 meters tall and 18 meters away from the line was removed after the line was confirmed safe. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GSB014 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 23/07/2018 5:59 |  |  | 10228 | Roadway |  | 20180727PWA_02 | Infrastructure (network-based) | -37.399 | 144.5838 | 1 | Powercor | Report | 12725 | 0.012473 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3441 | Mount Macedon | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. LEI's investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 165 WOOLLEYS ROAD, BITTERN VIC 3918 | 1109352 |  | Blown branch/vegetation |  | HV injection |  |  | 1 | At 1856hrs on 23/07/2018, 22kV feeder HGS 31circuit breaker reclosed to lockout affecting 2170 customers. A local resident from 165 Woolleys Road advised the meter has blown up and the smoke alarms melted when the electricity supply went off. During strong winds, a large tree branch from a council tree contacted the 22kV conductors that resulted in a HV conductor to contact the LV conductors below near pole No. LIS 1109352. The faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Hamilton-Woolleys" substation. The LEI confirmed a high voltage injection occurred (MOR 1802) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | HGS 31 | Vegetation: Trees Incident | HV injection;Loss of supply | 23/07/2018 18:56 |  |  | 10226 | Roadway |  | 20180727UTD_02 | Infrastructure (network-based) | -38.3389 | 145.1818 | 1 | United Energy Distribution | Report | 12721 | 0.010222 | 22kV AC | Moorabbin Airport | 3918 | Bittern | Trees
Voltage tests between an independent earth and various parts of the electrical installation, did not identify any defective electrical wiring or equipment at or within the installation. Further testing of the network assets indicated a potential voltage drop and or load imbalance on the LV Street Circuit and the Sub-station resulting in an inherent voltage in the network neutral supply system. The attending Powercor Fault Crew checked the condition of all conductors and replaced the existing O/H Service Cable between the LV Reticulation Pole and the POA and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply.he Installation was left ON supply. The LEI also completed a visual inspection and relevant testing of the Sandwich Press and confirmed the appliance was safe and fit for service. | 24 GRANT STREET, NEWTOWN VIC 3220 | 30060620 |  |  |  | Out of balance load |  | Phase to earth |  | Miss Mikeala Hotker was in the Kitchen when she received an electric shock as she made simultaneous contact with one hand on the metal sink and her other hand on the exposed metal of the sandwich press. | Conductor (bare) | 2 | 2 | 2 |  | GL021 | Potential load imbalance on the Sub-station and or voltage drop on the LV Street Circuit resulting in an inherent voltage in the network neutral supply system. | Minor shock | 43258.7917 |  |  | 10233 | Residential |  | 20180730PWA_02 | Infrastructure (network-based) | -38.153 | 144.3281 | 1 | Powercor | Report | 12729 | 0.027848 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Screened Service Conductor and a corroded Bridge Connection at the Reticulation Tee Pole, The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and repaired the corroded Bridge connection at the Reticulation Tee Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 12 MILLBANK STREET, BACCHUS MARSH VIC 3340 | 32171289 |  |  |  | Corrosion |  | Phase to earth |  | Mr Lachlan Page was in the Bathroom bathing when he received an electric shock as he made simultaneous contact with one hand on the metallic Bath Tap and his bare feet touching the metallic waste outlet. | Connector/termination | 2 | 2 | 2 |  | BMH004 | Corroded bridge connection | Minor shock | 15/07/2018 9:00 |  |  | 10235 | Residential |  | 20180730PWA_03 | Infrastructure (network-based) | -37.6762 | 144.4324 | 1 | Powercor | Report | 12731 | 0.0096192 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Bacchus Marsh | Connection
A faults crew promptly attended and proceeded to isolate and remove the fire damaged 150w HPS lantern. A new order was created for the replacement of the defective lantern. | 73 CLAYTON ROAD, OAKLEIGH EAST VIC 3166 | 600362 |  |  |  | Overheated connection |  |  | 2 | Caller reports of a pole fire in Clayton Road near the corner of Strelden Avenue, Clayton. A 150w HPS lantern on pole No. LIS 600369 located outside 73 Clayton Road caught fire and was found to be burnt out and required replacement. | Public lighting | 0 | 0 | 0 |  |  | The cause was a probable loose connection that overheated. | Pole-top fire | 28/07/2018 18:00 | 1 | Negligible: no ground fire | 10231 | Roadway |  | 20180730UTD_01 | Infrastructure (network-based) | -37.9048 | 145.1233 | 1 | United Energy Distribution | Report | 17510 | 0.0083507 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh East | Connection
The faults crew attended and advised the REC that its not permissible for an REC to open Distribution Company equipment attached to substation poles. Furthermore, they advised the REC that a Prescribed CES is required and supply was left off. Later that day, the REC provided Prescribed CES No. 404389701. The faults crew re-attended and reconnected supply following the completion of installation tests. | 251 BONEO ROAD, ROSEBUD VIC 3939 | 9885356 |  |  |  | Fault on customer installation |  |  | 1 | REC Richard Armstrong (Licence No. 1395 - Phone 0419 350 063) called to report there is no supply at the property and believes the cause is a blown fuse. Customer has provided pole number 1312060 which is a substation pole. The HV red and white phase 5amp fuses at the spur fusing RB0306 located in Boneo Road had operated and the cause was unknown. It was found the REC had unsafely opened the LV krone box at the United Energy substation pole that he's not authorised to touch. There was no defect on the premise and he replaced the meter panel, repaired the customers mains and installed mater panel fuses. The REC provided a non prescribed CES for the work that he completed that supplied a pump shed. | Pole mounted | 0 | 0 | 0 |  |  | Unauthorised opening of a Distribution Company asset. | Loss of supply | 43139.5139 |  |  | 10256 | Residential |  | 20180803UTD_02 | Infrastructure (network-based) | -38.383 | 144.8891 | 1 | United Energy Distribution | Report | 12965 | 0.015706 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Other
The attending crew contacted their supervisor and proceeded to replace the copper earth conductor at the pole type substation and made the site safe. | 22 BANDO ROAD, SPRINGVALE VIC 3171 |  | Copper theft | [5 empty] | 2 | The Zinfra crew had a job allocated for a reconnection of supply (fuse insert - CT metering) at the commercial property in Bando Road, Springvale. When in attendance for planned work, the Zinfra crew identified the copper earth conductor at "Bando N22 Brear" pole type substation had been removed from the pole by unknown persons. | Copper;Earth/earthing | 0 | 0 | 0 |  |  | Copper cable theft. | Damage to network assets | 43139.6181 |  |  | 10259 | Commercial |  | 20180803UTD_03 | Infrastructure (network-based) | -37.9439 | 145.1421 | 1 | United Energy Distribution | Report | 12758 | 0.021309 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Other
Voltage tests between an independent earth and various parts of the electrical installation, in addition to a visual inspection of the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole. The attending Powercor Fault Crew removed the O/H Service Cable prior to the LEI arriving on site, therefore initial voltage testing of the corroded O/H Service Cable in service was unable to be completed. The attending Powercor Fault Crew replaced the existing O/H Twisted Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 6 WINDSOR COURT, KENNINGTON VIC 3550 | 30167753 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Karen Tatnall was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metallic shower tap and her bare feet while standing on the wet shower base and metallic waste water outlet. | Service conductor | 2 | 2 | 2 |  | BGO012 | Corroded connection | Minor shock | 23/07/2018 0:00 |  |  | 10264 | Residential |  | 20180806PWA_03 | Infrastructure (network-based) | -37.8304 | 144.9514 | 1 | Powercor | Report | 12766 | 0.018778 | Low voltage AC (<1kV) | Essendon Airport | 3550 | Kennington | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, did not identify any defective electrical wiring or equipment, however an inherent network neutral voltage was observed at the time of the investigation. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 9 WATERFORD AVENUE, PORTLAND VIC 3305 | 30089370 |  |  |  | Out of balance load |  | Phase to earth | 2 | Ms Sophie McNielly was in the Bathroom showering when she received a minor electric shock as she made simultaneous contact between her hand on the metal shower tap and her bare feet while standing on the wet shower base. | Conductor (bare) | 2 | 2 | 2 |  | PLD006 | Suspect load imbalance on network | Minor shock | 20/07/2018 0:00 |  |  | 10265 | Residential |  | 20180806PWA_04 | Infrastructure (network-based) | -38.3617 | 141.61 | 1 | Powercor | Report | 12767 | 0.035057 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | AF Other
On arrival crew isolated supply and carried out repairs | 53-65 SLOUGH ROAD, ALTONA VIC 3018 | 30141768 |  | Animal |  |  |  |  | 1 | A customer reported an explosion from power pole outside 9 Slough rd Altona. On arrival the crew found a possum had bridged across 11kv connections damaging cable termination. The fault current caused a HV conductor bridge to burn off nearby ( LIS 934164 53-65 Slough st)) falling particles ignited a grass fire at the base of the pole. Fault current damage was also sustained to islolators at pole ( Lis 1777) outside 2 Ajax rd altona, hot debris caused minor damage to a number of cars. There was no reported injuries. | Dropper/bridge | 2 | 2 | 2 |  | AL011 | Animal Incident | Loss of supply;Grassfire;Damage to network assets | 43259.234 | 1 | Small: 10 - 1000 sq.m | 10267 | Roadway |  | 20180807PWA_01 | Infrastructure (network-based) | -37.8606 | 144.8003 | 1 | Powercor | Report | 12770 | 0.01577 | 11kV AC | Laverton Raaf | 3018 | Altona | Animal
15/06/2018 - A faults crew attended and contacted Formway Specialised Metering as an illegal bypass was suspected. Supply was isolated at pole No. LIS 2332701 and a defect notice left at the property. 22/06/2018 - The site was monitored and it appears the illegal bypass had never been removed, or was reconnected. The United Energy Metering Projects Manager contacted Victoria Police as its suspected the occupancy is a crop house. | 3 STIRLING AVENUE, MALVERN EAST VIC 3145 | 2332701 | Unauthorised access |  |  | Fault on customer installation |  |  | 2 | 15/06/2018 - Worker from Ventia completing a gas mains upgrade in the street for Multinet Gas contacted the United Energy faults and emergencies call centre advising there was a live gas fitting and no electric shocks had been received. The gas meter had been disconnected but the fitting line was alive. 22/06/2018 - REC Duc Phang LIC/REC No.22484 provided CES No. 15157980 advising that he had removed the faulty wiring. A faults crew attended and restored supply following the completion of installation tests. | Customer installation | 0 | 0 | 0 |  |  | Illegal bypass was detected and supply isolated at the pole end. A CES was received stating the bypass had been removed and supply was reconnected. It was later identified the bypass may have not been removed and was still in place. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/06/2018 12:30 |  |  | 10280 | Residential |  | 20180809UTD_01 | Infrastructure (network-based) | -37.8739 | 145.0872 | 2 | United Energy Distribution | Report | 12805 | 0.018522 | Low voltage AC (<1kV) | Moorabbin Airport | 3145 | Malvern East | Other
HV switching ceased and network returned to normal once it was identified that scaffold had already been removed. | 61 KERFERD ROAD, ALBERT PARK VIC 3206 | 30213499 | Working too close to overhead lines | [5 empty] | 2 | During switching for the issued of a permit to work , it was found that the scaffolding had been removed 1-2 weeks earlier whilst the HV line was in service. | Conductor (bare) | 0 | 0 | 0 |  | AP008 | in-appropriate scaffolding practice | No Go Zone (no contact) | 43351.375 |  |  | 10286 | Construction |  | 20180810PWA_01 | Infrastructure (network-based) | -37.8444 | 144.9579 | 1 | CitiPower | Report | 12797 | 0.040369 | 11kV AC | Essendon Airport | 3206 | Albert Park | Other
Informed contractor on site and attended hospital to get checked over and given the all clear. | 13 THOMAS MITCHELL DRIVE, WODONGA VIC 3690 |  |  |  |  | Fault on customer installation |  | Phase to earth |  | IMS 234821 - Employee felt warm tingling sensation when she inadvertently made contact with electrical cord with her boot. | Customer appliance | 0 | 0 | 0 |  |  | Employee inadvertently stepped backwards and made brief contact with an electrical extension cord with her right foot. She immediately felt a warm, tingling sensation in her foot and up through her right leg and into the right side of her back. Employee was wearing safety boots and insulated gloves although her boots were quite muddy. Upon inspection it was identified that a 1 cm section of insulation was missing. | Minor shock | 43381.3854 |  |  | 10290 |  |  | 20180810SPN_01 | Infrastructure (network-based) | -36.1264 | 146.89 | 2 | AusNet Services Distribution | Report | 13167 | 0.0060914 | Low voltage AC (<1kV) | Wangaratta Aero | 3690 | Wodonga | Other
On arrival crew isolated supply and carried out repairs. LEI engaged to check out customers premises | 4 MERKEL NOOK, SHEPPARTON EAST VIC 3631 | 30131592 |  |  |  | Unknown technical factor |  |  |  | A HV crossarm failed at pole 71 Dookie line Resulting in the HV conductor falling onto LV circuit below. There was a HV injection resulting in damage to customers installations . There was no fire or reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | STN024 | Unable to determine due to crossarm not being retained | HV injection | 43381.6757 |  |  | 10293 |  |  | 20180813PWA_01 | Infrastructure (network-based) | -36.3775 | 145.4724 | 1 | Powercor | Report | 12808 | 0.01189 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3631 | Shepparton East | Crossarm
Crew isolated HV supply to site by breaking both bridges on either cable head poles supplying site. Local Police have been notified of latest break in and flash over. | 247 ST ALBANS ROAD, SUNSHINE NORTH VIC 3020 | Pa0063937 | Vandalism;Copper theft | [5 empty] | 1 | Following recent theft reported as 20180808PWA_02 , another break in occurred at this site. The thieves broke into the live 22kV switching rooms, resulting in a flash over causing the feeder CB ( SSE011 ) to open. There was no fire, The attending operators, have suggested that site marks and tools abandoned at site may indicate that unauthorised persons may have sustained some form of injury. No persons were located at site. | Indoor | 2 | 2 | 2 |  | SSE011 | Copper theft, Vandalism | Loss of supply;Damage to network assets | 43351.7097 |  |  | 10296 | Commercial |  | 20180813PWA_02 | Infrastructure (network-based) | -37.7667 | 144.8188 | 1 | Powercor | Report | 12866 | 0.0052315 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Other
Fault crew and LEI dispatched to investigate. LEI assessed damage and proceeded to isolate properties where damage had occurred. O/H conductors repaired, damaged services replaced and electrical meters replaced where required. LEI carried out tests prior to re-connecting properties following completion of repairs. | 16 LAURIE AVENUE, TECOMA VIC 3160 | LIS1307802 |  | Blown branch/vegetation | [5 empty] | Report of tree contacting O/H HV conductors resulting in suspected HVI. | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | HV injection | 43381.5229 |  |  | 10295 | Roadway |  | 20180813SPN_02 | Infrastructure (network-based) | -37.9097 | 145.3432 | 1 | AusNet Services Distribution | Report | 12811 | 0.015538 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
On arrival crew isolated supply and carried out repairs | 157-159 DOMAIN ROAD, SOUTH YARRA VIC 3141 | 30194191 | Working too close to underground cables | [6 empty] | Richard 0422 155 636 from Mikcomm Communications called to advise he was drilling out on footpath and has hit underground cable causing one of the restaurants at this address to lose supply. There was no fire, no reported injuries or third party property daqmage. | Services cable | 2 | 2 | 2 |  | FR016 | Drilling works | Loss of supply;No Go Zone (contact);Damage to network assets | 43351.3653 |  |  | 10298 | Roadway |  | 20180814PWA_01 | Infrastructure (network-based) | -37.8342 | 144.9814 | 1 | CitiPower | Report | 12888 | 0.033189 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Other
On arrival crew confirmed site safe, repairs organised. | 2 FORDHAM AVENUE, CAMBERWELL VIC 3124 | 30176280 | Vandalism;Copper theft | [6 empty] | Passerby reported a suspicious truck stealing LV cable from pole. Upon crew arrival, crew confirm pole-to-pit LV 35mm cable was stolen which was ready to service an empty lot of the above address. There was no reported fire, shock or injuries | Services cable | 2 | 2 | 2 |  | RD001 | Copper theft | Damage to network assets | 43412.5556 |  |  | 10299 | Roadway |  | 20180814PWA_02 | Infrastructure (network-based) | -37.834 | 145.0731 | 1 | CitiPower | Report | 12864 | 0.0031794 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Other
ON arrival crew isolated supply and carried out repairs | SHOP 1 230 GRATTAN STREET, PARKVILLE VIC 3052 | 30199704 | Working too close to underground cables | [6 empty] | Contractor reported plumbers digging with an excavator hit a pit and smoke coming out at the incident location. Upon arrival, CitiPower crew found the LV UG cable had been damaged. | Cable | 2 | 2 | 2 |  | BQ046 | Excavation works | Loss of supply;No Go Zone (contact);Damage to network assets | 13/08/2018 10:00 |  |  | 10300 | Roadway |  | 20180814PWA_03 | Infrastructure (network-based) | -37.8002 | 144.9625 | 1 | CitiPower | Report | 12865 | 0.0071424 | Low voltage AC (<1kV) | Essendon Airport | 3052 | Parkville | Dug up
Site made safe and crossarm repaired. | 12 SUSSEX STREET, PASCOE VALE SOUTH VIC 3044 | Pole no. A048681 |  |  |  | Leakage |  |  | 2 | HV cross-arm charred. See attached photos. | Crossarm (wood) | 0 | 0 | 0 |  | CS02 | Tracking/Electrical leakage | Pole-top fire | 42923.5743 | 1 | Negligible: no ground fire | 10310 | Residential |  | 20180817JEM_01 | Infrastructure (network-based) | -37.7383 | 144.9488 | 1 | Jemena | Report | 13237 | 0.038036 | 22kV AC | Essendon Airport | 3044 | Pascoe Vale South | Crossarm
Site made safe and repairs carried out. | 598 MELBOURNE ROAD, SPOTSWOOD VIC 3015 | pole no. A059775 |  |  |  | Leakage |  |  | 2 | HV crossarm fire. Refer to attached photos. SAP notification 10281595 | Crossarm (wood) | 0 | 0 | 0 |  | YVE012 | Tracking/Electrical leakage | Pole-top fire | 43106.4569 | 1 | Negligible: no ground fire | 10311 | Roadway |  | 20180817JEM_02 | Infrastructure (network-based) | -37.8306 | 144.8817 | 1 | Jemena | Report | 12884 | 0.010413 | 22kV AC | Essendon Airport | 3015 | Spotswood | Crossarm
On arrival crew isolated supply and carried out repairs. | L 1 271 ROYAL PARADE, PARKVILLE VIC 3052 | 30212087 |  |  |  | Not built/maintained to design |  |  | 1 | XPower (Sub-contractor for Landlease) reported they have hit an underground cable. Upon crew arrival, crew confirmed that an underground LV service cable was hit and damaged . There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | VM004 | Excavation works | Loss of supply;Damage to network assets | 15/08/2018 15:51 |  |  | 10316 | Roadway |  | 20180820PWA_01 | Infrastructure (network-based) | -37.7875 | 144.9578 | 1 | CitiPower | Report | 13172 | 0.024375 | Low voltage AC (<1kV) | Essendon Airport | 3052 | Parkville | Dug up
On arrival the crew isolated supply and carried out repairs | 25 STOKES ROAD, WARRENHEIP VIC 3352 | 32002534 |  |  |  | Mechanical breakdown;Mechanical vibration |  |  | 1 | Vic Fire reported sparking coming from pole, with broken insulator resting on the crossarm at the incident location . On arrival crew found that the centre phase 66kV insulator pin has sheared off at the "P" bracket, allowing the insulator with conductor attached to fall. The conductor fell and lay on the steel crossarm. The hanging insulator brushed the wood pole and burned the pole, requiring it to be replaced. There was no ground fire or any other damage caused by this incident. | Pole (wood);Insulators | 2 | 2 | 2 |  | BATS BAS 2 | Insulator stud failure due to fatigue | Pole-top fire | 19/08/2018 12:59 | 1 | Negligible: no ground fire | 10318 | Roadway |  | 20180820PWA_03 | Infrastructure (network-based) | -37.5799 | 143.924 | 1 | Powercor | Report | 13189 | 0.011229 | 66kV AC | Ballarat Aerodrome | 3352 | Warrenheip | Pole
crew and LEI investigated customer equipment electrical fault. faulty equipment unplugged. | 110 BASTINGS STREET, NORTHCOTE VIC 3070 | 30188556 | Recreation - Helium (party) balloons | [5 empty] | 1 | Resident reported burning smell from either home computer or telephone which has blown up and no power at the premises. Fault crew and LEI attended and indicated it was customer equipment electrical fault. LEI also reported that crew inspecting lines fed from adjacent substation had noticed balloon that may have contacted HV conductors. No damage consistent with High voltage injection was found. | Conductor (bare) | 0 | 0 | 0 |  | NC002 | Cause not found. Some potential for airborne debris ( Balloons) contact | Loss of supply | 18/08/2018 8:43 |  |  | 10339 | Residential |  | 20180823PWA_01 | Infrastructure (network-based) | -37.7751 | 145.0071 | 1 | CitiPower | Report | 12924 | 0.025242 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3070 | Northcote | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Bridge Connection at the Reticulation Pole. The attending Powercor Fault Crew replaced the corroded O/H Neutral Bridge Conductor at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 106 LARTER STREET, GOLDEN POINT VIC 3350 | 30234758 |  |  |  | Corrosion |  | Phase to earth |  | Mr Jacob Stewart was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metallic Shower Tap and his bare feet whilst standing on the wet shower base. | Dropper/bridge | 2 | 2 | 2 |  | BAS023 | Corroded connection | Minor shock | 31/05/2018 7:30 |  |  | 10092 | Residential |  | 20180706PWA_02 | Infrastructure (network-based) | -37.5699 | 143.8722 | 1 | Powercor | Report | 12547 | 0.02731 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Golden Point | Connection
Cross-arm replaced, possible HVI investigated. | 3296 FOURTEENTH STREET, IRYMPLE VIC 3498 | 30098208 |  |  |  | Leakage |  |  | 1 | Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire | 43350.1319 | 1 | Negligible: no ground fire | 10107 |  |  | 20180710PWA_02 | Infrastructure (network-based) | -34.2496 | 142.2084 | 1 | Powercor | Report | 12566 | 0.014152 | 22kV AC | Mildura Airport | 3296 | Irymple | Crossarm
On arrival crew isolated supply | 111 WOLLAHRA RISE, WYNDHAM VALE VIC 3024 | 30119450 | Vandalism;Copper theft | [6 empty] | Customer reports pole broken (private pole) and wire on ground sparking. Crew attended and found customers private service pole broken off and private U/G mains cable from building to customer private pole on property removed. End of service cable alive and on ground sparking There was no ground fire and no reported injuries. | Private overhead electric line (POEL);Service conductor | 2 | 2 | 2 |  | WBE014 | Copper theft | Loss of supply;Damage to network assets | 43257.3653 |  |  | 10110 | Roadway |  | 20180710PWA_04 | Infrastructure (network-based) | -37.8664 | 144.6282 | 1 | Powercor | Report | 12569 | 0.022894 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral connection at the FMJB. Fault truck repaired the neutral connection at POA and service passed a NST. CTA re-tested property, all required VESI tests and the installation failed aNSTt test at the meter panel Incoming main neutral at meter panel failed neutral impedance test (too high ) damaged neutral cable Left off and issued defect notice to the customer on site | UNIT 1 18 GURNER STREET, ST KILDA VIC 3182 | 30547005 |  |  |  | Corrosion |  | Phase to earth |  | Brenton was showering at the time; he received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. | Connection box | 2 | 2 | 2 |  | SK013 | Corroded connection | Minor shock | 43257.625 |  |  | 10111 | Residential |  | 20180710PWA_05 | Infrastructure (customer connection) | -37.8614 | 144.9811 | 1 | CitiPower | Report | 12570 | 0.04111 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located on the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 39 KEAM STREET, MILDURA VIC 3500 | 30097157 |  |  |  | Corrosion |  | Phase to earth |  | Mr Paul Pickering was in the Bathroom bathing when he received an electric shock as he made simultaneous contact between his right hand on the Bath Taps and his body in contact with the wet Bath base. | Service conductor | 2 | 2 | 2 |  | MDA022 | Corroded connection | Minor shock | 43137.8542 |  |  | 10113 | Residential |  | 20180710PWA_07 | Infrastructure (network-based) | -34.2012 | 142.157 | 1 | Powercor | Report | 12572 | 0.0016458 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Connection
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, found high impedance connections located at the service pit. Fault truck disconnected neutral connections at service pit and re-made all connections CTA re-tested property, all required VESI tests passed | 7 SPRINGBANK WAY, BROOKFIELD VIC 3338 | 30110415 |  |  |  | Corrosion |  | Phase to earth |  | Janise was showering at the time; she received an electric shock when he made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Services cable | 2 | 2 | 2 |  | MLN013 | Corroded connection | Minor shock | 43225.25 |  |  | 10117 | Residential |  | 20180710PWA_09 | Infrastructure (network-based) | -37.703 | 144.5534 | 1 | Powercor | Report | 12576 | 0.018898 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions during daylight hours. | 118 RACECOURSE ROAD, MOUNT MARTHA VIC 3934 | 9751716 |  | Cold |  | Leakage |  |  | 2 | Pole fire reported on the corner of Harrap and Racecourse Roads. During heavy fog conditions, a pole fire occurred at pole No. LIS 9751716 due to polymeric insulators tracking via the steel HV cross arm and king bolt. The fire started in the poles interior and caused sufficient damage to require the HV/LV tee-off pole replacement. | Pole (wood) | 0 | 0 | 0 |  | MTN 24 | Tracking of HV insulators during a heavy fog. | Pole-top fire | 26/06/2018 23:58 | 1 | Negligible: no ground fire | 10114 | Roadway |  | 20180710UTD_01 | Infrastructure (network-based) | -38.2589 | 145.0542 | 1 | United Energy Distribution | Report | 13078 | 0.028972 | 22kV AC | Moorabbin Airport | 3934 | Mount Martha | Pole
Crew to replace surge arrestors and repair earth cable. | 180 HOBBS ROAD, WYNDHAM VALE VIC 3024 | 30274107 | Copper theft | [6 empty] | Employee reports finding copper earth cable on pole pulled out of ground and broken. Cable wrapped around stay on pole. All surge arrestors on pole broken. Suspect third party attempted to pull cable off pole with vehicle, breaking cable and wrapping it round stay wire, breaking surge arrestors in process. Crew to replace surge arrestors and repair earth cable. | Earth/earthing | 2 | 2 | 2 |  | TNA023 | Copper Theft | Damage to network assets | 13/07/2018 14:53 |  |  | 10139 | Roadway |  | 20180716PWA_01 | Infrastructure (network-based) | -37.8504 | 144.6131 | 1 | Powercor | Report | 12611 | 0.0035127 | Earthing cable | Laverton Raaf | 3024 | Wyndham Vale | Other
On arrival crew isolated supply and carried out repairs | 33 BALD HILLS ROAD, CRESWICK VIC 3363 | 32012808 | Vehicle | [6 empty] | A customer reported a vehicle hit pole at the incident location and the transformer dislodged. Upon arrival, the Powercor crew found that the transformer sitting on the back side of the vehicle roof. The vehicle driver was not at the scene. There was no fire, no reported injuries or third party property damage. | Pole mounted | 2 | 2 | 2 |  | BAN009 | Truck struck transformer | Damage to network assets | 18/06/2018 14:44 |  |  | 10141 | Roadway |  | 20180716PWA_03 | Infrastructure (network-based) | -37.4249 | 143.8831 | 1 | Powercor | Report | 12613 | 0.0044051 | 22kV AC | Ballarat Aerodrome | 3363 | Creswick | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Service Pole The attending Powercor Fault Crew replaced the existing O/H Four Wire Neutral Screened Service Cable between the Reticulation Pole and the Service Pole on the Road Reserve and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 88 BELLARINE HIGHWAY, NEWCOMB VIC 3219 | 32074259 |  |  |  | Corrosion |  | Phase to earth |  | Ms Rose Dalhlhaus was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Tap and her bare feet while standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GLE024 | Corroded connection | Minor shock | 20/06/2018 10:30 |  |  | 10160 | Residential |  | 20180717PWA_04 | Infrastructure (network-based) | -38.1713 | 144.3937 | 1 | Powercor | Report | 12639 | 0.0077465 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Newcomb | Connection
The crew made the site safe and necessary repairs. | 40 MANRESA ROAD, CURLEWIS VIC 3222 | 32081605 | Working too close to overhead lines | [5 empty] | 1 | The CFA received reports that a tree had fallen on a HV powerline with wires sparking. On arrival, the crew identified a tree had fallen into the HV conductor between Pole 4 (LIS-8199) and Pole 5 (LIS-8198). Causing one phase to snap and fall to the ground. There was no ground fire, shocks or injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | DDL014 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact);Damage to network assets | 15/07/2018 20:12 |  |  | 10170 | Agricultural |  | 20180718PWA_02 | Infrastructure (network-based) | -38.1672 | 144.5116 | 1 | Powercor | Report | 12652 | 0.017816 | 22kV AC | Avalon Airport | 3222 | Curlewis | Trees
No action taken by CitiPower as yet, Work Safe has issued notice restricting all access to the scaffold | 231 ESPLANADE EAST, PORT MELBOURNE VIC 3207 | 30205007 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Worksafe inspector upon inspection of site found that the scaffold that has been erected on site is not compliant with the guidelines stated on the Permit to Work. Scaffold has been erected over the service cable feeding the property next door without an isolation, the service cable passes through the scaffold, also scaffold did not meet hoarding requirements stated on the Permit to Work. | Conductor (bare) | 0 | 0 | 0 |  | AP007 | interference | No Go Zone (no contact) | 43411.4688 |  |  | 10172 |  |  | 20180718PWA_04 | Infrastructure (network-based) | -37.8381 | 144.9451 | 1 | CitiPower | Report | 12654 | 0.028814 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Other
On arrival crew isolated supply and carried out repairs | 2 FOREST STREET, COLAC EAST VIC 3250 | 32064073 |  |  |  | Leakage |  |  |  | A Powercor contractor, Electrix, reported a P1 fault that was a pole fire at the incident location. Upon arrival, the Powercor crew found that the cross arm had been burnt through some time ago There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CLC003 | Excessive leakage current | Pole-top fire | 17/07/2018 8:24 | 1 | Negligible: no ground fire | 10174 | Roadway |  | 20180718PWA_05 | Infrastructure (network-based) | -38.3359 | 143.6068 | 1 | Powercor | Report | 12656 | 0.028372 | 22kV AC | Ballarat Aerodrome | 3250 | Colac East | Crossarm
Zinfra HSEQ attended the site and an investigation commenced. A fellow worker confirmed that 240v was measured at the termination. The worker who received that minor electric shock went to the local hospital for precautionary checks and was discharged with nil injuries. Zinfra commenced a detailed investigation to determine the cause. | GILBY ROAD, MOUNT WAVERLEY VIC 3149 |  |  |  |  | Electrical breakdown |  | Phase to earth | 2 | Electrical work was being completed at NO (Nottinghill) Zone Substation and a substation fitter received a minor electric shock to his hand. MEC worker was completing planned maintenance works on Transformer Number 2 and was checking secondary wiring terminations on the on-load tap changer. When he placed a spanner onto the nut when he received a minor electrical shock to his right hand and fingers. The work crew advised their supervisor and work ceased. | Zone substation | 0 | 1 | 0 |  |  | The cause is under investigation. | Minor shock | 43441.375 |  |  | 10176 | Other | Zone substation | 20180718UTD_01 | Infrastructure (network-based) | -37.8987 | 145.1359 | 1 | United Energy Distribution | Report | 12658 | 0.018083 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | AF Other
Made contact with the builder and communicated with to stop work immediately. Builder has made contact with Jemena to rectify the breach and has had JEN assets relocated. | 64 NORTH STREET, HADFIELD VIC 3046 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | No Go Zone assessor was driving pass and identified that builder has erected timber frame for new dwelling approximately 400mm away from LV overhead bare conductor. | Conductor (bare) | 0 | 0 | 0 |  |  | Builder erected new timber frame for new dwelling too close to LV overhead bare conductor | No Go Zone (no contact) | 19/07/2018 8:59 |  |  | 10184 | Residential |  | 20180719JEM_01 | Infrastructure (network-based) | -37.7049 | 144.9445 | 1 | Jemena | Report | 12868 | 0.038856 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
Faults crew isolated the substation and made safe. | 60 CLIFFORDS ROAD, SOMERTON VIC 3062 |  | Unauthorised access;Copper theft | [5 empty] | 1 | Unknown persons unauthorised entry into CLIFFORDS-BRIGHT STL distribution substation and attempt to steal copper. Attempted to cut through live high voltage cable resulting in protection operating. | Indoor | 0 | 0 | 0 |  |  | Unknown persons attempted to steal copper | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 20/07/2018 4:31 |  |  | 10188 | Industrial |  | 20180720JEM_01 | Infrastructure (network-based) | -37.6366 | 144.9395 | 1 | Jemena | Report | 12679 | 0.013492 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3062 | Somerton | Other
The fire was extinguished repairs completed. | 135 BARKERS ROAD, KEW VIC 3101 | 30178382 |  |  |  | Leakage |  |  |  | Customer reports fire on pole. Crew attended and found tree branch had struck the HV insulator at P05E Barker Denmark, breaking a disc insulator. This resulted in leakage current flowing to the wood crossarm starting a crossarm fire. No shock, injuries or ground fire start. | Crossarm (wood) | 2 | 2 | 2 |  | Q010 | Excessive leakage current | Pole-top fire | 19/07/2018 13:36 | 1 | Negligible: no ground fire | 10186 | Roadway |  | 20180720PWA_01 | Infrastructure (network-based) | -37.8138 | 145.0299 | 1 | CitiPower | Report | 12675 | 5.6713e-05 | 11kV AC | Essendon Airport | 3101 | Kew | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded U/G Service Neutral Conductor termination at the Reticulation Pole, causing a higher than normal impedance within the neutral service conductor. The U/G Service Neutral Conductor termination at the Bi-metal Connector was found to be loose and corroded. The attending Powercor Fault Crew replaced the corroded U/G Service Neutral and White Phase Bi-metal Connectors at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 198 NOBLE STREET, NEWTOWN VIC 3220 | 32085833 |  |  |  | Corrosion |  | Phase to earth |  | Mr Graeme Jude was ascending an aluminium ladder to clean the Roof Gutter when he received an electric shock as he made simultaneous contact with one hand on the metallic Down Pipe and the other hand on the aluminium ladder. | Services cable | 2 | 2 | 2 |  | GL021 | Corroded connection | Minor shock | 27/06/2018 8:30 |  |  | 10191 | Residential |  | 20180720PWA_02 | Infrastructure (network-based) | -38.152 | 144.3305 | 1 | Powercor | Report | 12761 | 0.0031308 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | OH Cable
A LEI and faults crew attended, tested around the pole, checked all connections and found no evidence to support any electric shock being received. No voltage was detected on the pole or on any adjacent conductive material on or around the pole. The faults crew patrolled the area and identified the red phase HV insulated dropper lead in close proximity (~10mm) to the LV conductor at "Darrandaul-Barak" pole type substation adjacent to the incident pole. Also on this particular pole, there is a neutral connection to the optic fibre steel catenary wire with the conductive fixing screwed directly into the timber pole. The LEI reasoned that at the time the dog sniffed the base of the pole, the HV dropper may have touched the LV neutral causing it to be momentary energised and tracked down the pole if the pole had been damp at the time. A notification was created to divert the HV dropper away from the LV neutral conductor. | 46 BARAK STREET, BULLEEN VIC 3105 | 7056848 |  |  |  | Leakage |  |  | 2 | Customers claims that her dog received an electric shock from the base of the pole next to the property located near the corner of Barak Street and Darrandaul Drive. This occurred last Sunday and the dog now has trouble walking. A person walking their Maltese Terrier dog in Barak Street on 15/07/2018, believes the dog received an electric shock from the pole - LIS No. 7056848. The dog was sniffing the grass at the base of the pole, jumped backwards and was shivering on the concrete footpath. The dog sustained an injury when landing onto the concrete that prevented it's legs from properly functioning. | Pole mounted;Dropper/bridge | 0 | 0 | 0 |  | WD 36 | The LEI tested around the structure and no stray voltages were identified. The cause is classified as being undetermined although there was no conclusive finding ascertained with an assumption to the cause. | Shock to livestock, pet or companion animal | 20/07/2018 11:00 |  |  | 10201 | Roadway |  | 20180724UTD_01 | Infrastructure (network-based) | -37.772 | 145.087 | 1 | United Energy Distribution | Report | 12693 | 0.032313 | 22kV AC | Essendon Airport | 3105 | Bulleen | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, did not identify any defective electrical wiring or equipment at or within the installation. Further testing of the network assets identified a corroded Active Bridge Conductor between the Transformer Bus and the FOLCB on the Reticulation Pole, he attending Powercor Fault Crew replaced the corroded Active Conductor Bridge and swapped the existing O/H Service Active Conductor to the least loaded Blue Phase and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the LEI which also confirmed a Pass result. The Installation was left ON supply. | 4 MONTGOMERY AVENUE, HAMLYN HEIGHTS VIC 3215 | 30057960 |  |  |  | Corrosion;Out of balance load |  | Phase to earth |  | Mr William Hickey was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Rose and his bare feet whilst standing on the wet shower base. | Conductor (bare);Dropper/bridge | 2 | 2 | 2 |  | GL015 | Potential load imbalance on the Sub-station and the LV Street Circuit | Minor shock | 43411.7083 |  |  | 10223 | Residential |  | 20180726PWA_05 | Infrastructure (network-based) | -38.1219 | 144.3338 | 1 | Powercor | Report | 12718 | 0.026545 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | AF Other
The high voltage feeder was patrolled and supply restored after the Melbourne Water Eastern Treatment Plant assets were checked. | 600M Thompsons Road, Carrum Downs VIC 3201, Australia | 9679025 |  | Wind |  | Conductor clashing |  |  | 1 | At 1931hrs on 23/05/2018, 22kV feeder CRM 11 circuit breaker opened and locked out as there was no auto reclose. During strong winds, it is suspected that HV conductors clashed in Thompsons Road approx.6 poles west of "Thompson P277-MMBW" substation. As a result, hot molten metal fell into the grass below and a small grass fire started that required the CFA to attend. | Conductor (bare) | 0 | 0 | 0 |  | CRM 11 | There was strong winds at the time of the event. | Grassfire | 23/07/2018 19:31 | 1 | Localised: less than 10 sq.m | 10224 | Other | Sewerage plant | 20180727UTD_01 | Infrastructure (network-based) | -38.0672 | 145.1585 | 2 | United Energy Distribution | Report | 18417 | 0.03531 | 22kV AC | Moorabbin Airport | 3201 | Carrum Downs | Conductor
1330 - (approx) Luma Energy G&B crew reported the incident to the UE Network Control Centre to ensure immediate isolation of the HV conductors. 1335 - Luma Energy G&B Crew reported incident to Luma Energy General Manager. 1340 - Luma Energy GM reported incident to Zinfra External Works Overhead Team Leader. 1350 - Luma Energy Operations Manager departed to attend incident site and an investigation commenced. Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions - EAP No. 32168. LEI's investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. | 121 ABBOTT STREET, SANDRINGHAM VIC 3191 | [5 empty] | Inappropriate tools/plant/equipment |  | 1 | At 1327hrs on 31/07/2018, 11kV feeder SR11 circuit breaker locked out as the auto reclose function was suppressed due to live line activities on the overhead conductors. A Luma Energy Glove and Barrier crew were in the process of sleeving out defective 'fargo' leeves on 11kV feeder SR 11 using live line techniques. The work crew had completed the sleeve replacement on the 19/2.00 copper conductors and were in the process of removing the lugall and hopper from the overhead HV conductors when the newly installed sleeve failed resulting in the centre phase copper HV conductor falling and briefly contacting the LV conductors below. No persons were injured as a result of this incident. The faults crew that attended requested that a LEI attend as a HVI was suspected to customers supplied from the east circuit of "Gladstone-Abbott" substation. The LEI confirmed a high voltage injection did not occur. | Conductor (bare);Copper | 0 | 0 | 0 |  | SR 11 | The investigation revealed: â€¢ The Compression Sleeve and Die Sizes chart provided to the Luma Energy crew was not correct for Copper conductor. This resulted in the work crew selecting the wrong size die for the sleeve installed. (Photo 1) o Luma Energy sourced from â€œThe Energy Networkâ€ (TEN) Die Charts (Charts 1 & 2) that clearly demonstrates the difference in the Dies to be used for the different manufactured sleeves for Copper Overhead Mains; CABAC 14.8mm (70PT) Die are suitable for 19/.083 Cu HT Sleeves manufactured by CABAC only; Sleeves manufactured by Utilux for 19/.083 Cu HT are smaller and require the use of Utilux Die (13mm). NB. There is only differences in Die sizes for Copper Overhead Mains. Aluminium die sizes are identical for both Utilux and CABAC manufactured sleeves. â€¢ Some of the Luma Energy management team and work crew were unaware that there was a difference in the size of Die to be used for different manufacturers. â€¢ Both Utilux and CABAC sleeves are issued from United Energy and are labelled with the same â€œItem Number.â€ â€¢ Visually there is a distinct difference in the crimped sleeve utilising the different Die size (Photo 4) â€¢ The work crew stated that after the completion of the crimp and prior to the incident they did not notice that the Sleeve was not crimped correctly on the centre phase and that they had relied on the Die chart. The work crew completed the crimp and slid the hard covers back over the sleeve before moving to the footpath phase. | Loss of supply | 31/07/2018 13:27 |  |  | 10245 | Roadway |  | 20180801UTD_01 | Infrastructure (network-based) | -37.9499 | 145.0147 | 1 | United Energy Distribution | Report | 12942 | 0.013275 | 11kV AC | Moorabbin Airport | 3191 | Sandringham | AF Other
A LEI and faults truck attended and isolated supply at pole number LIS 1305992 after a NST failed with 152ohms measured on the neutral and 81v identified on the garage door including 215v at the meter enclosure to an independent earth. During the work at the pole end, it was identified that connections in the pole mounted junction box were corroded and the neutral conductor had broken off. The faults crew replaced the pole box and the LEI was able to complete installation tests that confirmed the fault had been rectified and supply was left on. | 7 PARADISE DRIVE, ST ANDREWS BEACH VIC 3941 | 1305992 |  | Prone to salt deposition |  | Corrosion |  | Phase to earth | 2 | A builder working at the property received an electric shock from the garage door. The builder called a REC who completed tests and believed the problem is from the street wires. The REC turned off the main switch and the property has been locked up and access will not be available until morning. A builder was visiting the work site and felt a slight electric shock when he opened the garage door. A REC attended and checked the installation before contacting the United Energy faults and emergencies call centre. | Cable;Connection box | 0 | 0 | 0 |  |  | A LEI and faults truck attended and isolated supply at pole number LIS 1305992 after a NST failed with 152ohms measured on the neutral and 81v identified on the garage door including 215v at the meter enclosure to an independent earth. During the work at the pole end, it was identified that connections in the pole mounted junction box were corroded and the neutral conductor had broken off. The faults crew replaced the pole box and the LEI was able to complete installation tests that confirmed the fault had been rectified and supply was left on. | Minor shock | 25/07/2018 17:30 |  |  | 10247 | Residential |  | 20180801UTD_02 | Infrastructure (network-based) | -38.4254 | 144.8391 | 1 | United Energy Distribution | Report | 12744 | 0.024313 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | St Andrews Beach | Connection
On arrival crew isolated supply and carried out repairs. | 18 NELSON ROAD, POINT LONSDALE VIC 3225 | 33044427 |  |  |  | Candled fuse |  |  |  | Customers reported to Powercor "dim lights and motor driven appliances struggling to work". When crews arrived they found a EDO fuse carrier had candled on pole type transformer at the incident location. No evidence of ground fire was found. No injuries or 3rd party property damage was reported. | EDO fuse | 2 | 2 | 2 |  | DDL012 | Moisture ingress | Pole-top fire | 28/07/2018 13:09 | 1 | Negligible: no ground fire | 10248 | Roadway |  | 20180802PWA_01 | Infrastructure (network-based) | -38.2727 | 144.6193 | 1 | Powercor | Report | 12745 | 0.027926 | 22kV AC | Avalon Airport | 3225 | Point Lonsdale | Fuse
Supply isolated at the FMB on the pole. The meter was also removed from the site by the crew. | 11 STRONG STREET, SOUTH GEELONG VIC 3220 | 30066921 | Unauthorised work;Unauthorised access | [5 empty] | 2 | Report from LEI that a premises had been demolished by unknown person at the incident location. Crew attended the site to find a meter box with meter inside still live, laying on the ground, with the building having been demolished. There was no fire, no reported injuries. | Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | GLE032 | Demolition of building by unknown persons | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/07/2018 11:26 |  |  | 10249 | Residential |  | 20180802PWA_02 | Infrastructure (network-based) | -38.1629 | 144.3642 | 1 | Powercor | Report | 12746 | 0.04101 | Low voltage AC (<1kV) | Avalon Airport | 3220 | South Geelong | Other
Low voltage circuit isolated, damage has been repaired and customers restored. | 12 RANDALL WAY, ASCOT VIC 3551 | 30345902 |  |  |  |  | Inappropriate tools/plant/equipment |  | 1 | A contractor engaged by Powercor was exposing a live low voltage underground cable in a new estate, readying connection for the next stage. During excavation his excavator has damaged a live low voltage under ground cable. Low voltage fuses operated to clear the faulted equipment,. There was no there were no injuries or fire. | Cable | 2 | 2 | 2 |  | EHK022 | Excavation work, cable in unexpected position | Loss of supply;No Go Zone (contact);Damage to network assets | 43108.4306 |  |  | 10250 | Roadway |  | 20180802PWA_03 | Infrastructure (network-based) | -36.6936 | 144.3273 | 1 | Powercor | Report | 12760 | 0.0029618 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Ascot | Dug up
On arrival crew isolated supply and carried our repairs. | 2259 KEILOR-MELTON ROAD, MELTON VIC 3337 | 30117598 | Working too close to underground cables | [6 empty] | Employee reports section of street lights out. Crew attended and found LV U/G supply to street light scheme had been dug up and damaged. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | MLN021 | Excavation work | Loss of supply;No Go Zone (contact);Damage to network assets | 19/07/2018 14:26 |  |  | 10251 | Roadway |  | 20180802PWA_04 | Infrastructure (network-based) | -37.6865 | 144.6064 | 1 | Powercor | Report | 12750 | 0.017957 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Melton | Dug up
fault truck attended to make safe and isolate the street light. Isolating supply to the light stopped the fire | 43 TURNER STREET, LEONGATHA VIC 3953 | LIS 2005194 |  |  |  | Defective component |  |  | 2 | IMS 234792 -VIC Country Fire reported street light pole fire on pole | Public lighting | 0 | 0 | 0 |  | LGA21 | Attending Fault crew found that the Active was disconnected and the it caught fire in head of light as a result of arching from moisture believed to be in the ballast. | Pole-top fire | 43289.9542 | 1 | Negligible: no ground fire | 10272 |  |  | 20180808SPN_01 | Infrastructure (network-based) | -38.4722 | 145.949 | 1 | AusNet Services Distribution | Report | 17802 | 0.041417 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha | Pole
Crew Isolated the VT and made safe. | 1410 PLENTY ROAD, MERNDA VIC 3754 | LIS 917511 |  |  |  | Defective component |  |  |  | IMS 234756 - After closing the LV fuse on HV Cap Plenty Road the crew heard the Sec VT arcing. The crew then saw smoke just before the VT caught fire and went out on it's own. | Transformer | 0 | 0 | 0 |  | DM012 | The cap bank was installed and testing completed by AusNet testers. Installation was then livened, LV fuses closed before crew heard the Sec VT arcing and smoke observed just before the VT caught fire and self extinguished. Testers confirmed all the equipment was wired correctly and it appears to be equipment failure. | Pole-top fire | 43167.5979 | 1 | Negligible: no ground fire | 10274 |  |  | 20180808SPN_03 | Infrastructure (network-based) | -37.6034 | 145.095 | 1 | AusNet Services Distribution | Report | 17909 | 0.024317 | Low voltage AC (<1kV) | Essendon Airport | 3754 | Mernda | AF Other
A crew attended and isolated the supply to the pit ( only the 1 customer fed from this pit ) | 1090 LEAKES ROAD, MOUNT COTTRELL VIC 3024 | 30103574 | Vandalism;Copper theft | [6 empty] | A Powercor meter technician attended site to investigate a no comms issue from meter at the above location. Comms failed on 19.06.2018 @ 02:04hrs. He found the building 1/2 demolished and the pit at base on P2 Leakes Rd with its lid removed. He observed the customers mains in the pit had been cut and the customers mains back to the house removed. The live ends of the Underground cable in the pit had been taped up but left out of the pit. . The meter at the property was not found. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | TNA023 | Copper theft, vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 19/06/2018 2:04 |  |  | 10278 | Residential |  | 20180809PWA_01 | Infrastructure (network-based) | -37.8292 | 144.6496 | 1 | Powercor | Report | 12785 | 0.023441 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
Fault crew dispatched to investigate. DOA attended the site in daylight hours. Light had not been fixed and there were very small burn marks on the ground with bits of melted plastic in the vicinity of the burnt areas. | 33 HEARN STREET, DROUIN VIC 3818 | LIS 2704071 |  |  |  | Defective component |  |  | 2 | IMS 234718 - report of failed 150W street light | Public lighting | 0 | 0 | 0 |  | WGL21 | DOA attended the site in daylight hours. Light had not been fixed and there were very small burn marks on the ground with bits of melted plastic in the vicinity of the burnt areas. Unable to determine cause of street light failure. | Grassfire;Melting or smoking only | 43139.0194 | 1 | Negligible: no ground fire | 10284 |  |  | 20180809SPN_04 | Infrastructure (network-based) | -38.1241 | 145.8449 | 2 | AusNet Services Distribution | Report | 13114 | 0.016469 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3818 | Drouin | AF Other
A faults crew attended and placed the substation under LV parallel prior to replacing the red phase HV fuse. LV parallels were removed upon the PPF fuse replacement and supply restored to normal for customers supplied from "Miller-Avondale" substation. | MILLER CRESCENT, MOUNT WAVERLEY VIC 3149 | 8802801 |  |  |  | Candled fuse |  |  | 2 | Per MFB - Pole fire. A 11kV HV powder filled fuse (PFF) candled at "Miller-Avondale" pole type substation that caused a loss of supply to customers in the vicinity. | Powder filled | 0 | 0 | 0 |  | BW 33 | A 11kV HV powder filled fuse candled at a pole type substation. | Pole-top fire | 24/07/2018 18:45 | 1 | Negligible: no ground fire | 10287 | Roadway |  | 20180810UTD_01 | Infrastructure (network-based) | -37.8751 | 145.1249 | 1 | United Energy Distribution | Report | 12798 | 0.018137 | 11kV AC | Moorabbin Airport | 3149 | Mount Waverley | Fuse
Crew isolated damaged equipment and repaired line. tree removed. | 212 BARRINGO ROAD, NEW GISBORNE VIC 3438 | 33023842 |  | Alive;Fallen |  |  |  |  | 1 | A Tree fell across conductors Between poles 9 and 10 of the water trust spur line. The conductors contacted the ground causing a 20 square metre grass fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | GSB012 | Vegetation: Trees Incident | Grassfire | 15/08/2018 1:53 | 1 | Small: 10 - 1000 sq.m | 10303 | Roadway |  | 20180815PWA_02 | Infrastructure (network-based) | -37.4424 | 144.6051 | 1 | Powercor | Report | 12874 | 0.0061551 | 22kV AC | Melbourne Airport | 3438 | New Gisborne | Trees
Site made safe and repairs carried out. | 57 BARBARA CRESCENT, AVONDALE HEIGHTS VIC 3034 | Pole no. A094363 |  |  | Unlikely | Age |  |  | 2 | Small grass fire due to failure of the LV ABC switch. No Photos available. | Any other type | 0 | 0 | 0 |  | BY14 | LV ABC switch failed. | Grassfire | 28/02/2018 14:55 | 1 | Localised: less than 10 sq.m | 10308 | Residential |  | 20180816JEM_01 | Infrastructure (network-based) | -37.773 | 144.8563 | 1 | Jemena | Report | 13232 | 0.011359 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole. The attending Powercor Fault Crew re-terminated the existing O/H Service Cable at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 58 HYLAND STREET, WARRNAMBOOL VIC 3280 | 30259898 |  |  |  | Corrosion |  | Phase to earth |  | Mr Adam Loft was in the bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metallic Shower Taps and his bare feet while standing on the wet shower base. | Service conductor;Connection box | 2 | 2 | 2 |  | WBL004 | Corroded neutral connection | Minor shock | 31/07/2018 0:00 |  |  | 10305 | Residential |  | 20180816PWA_01 | Infrastructure (network-based) | -38.3763 | 142.4703 | 1 | Powercor | Report | 12877 | 0.039722 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Conductor
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customer's POA. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 100 SUNSET STRIP, JAN JUC VIC 3228 | 30074899 |  |  |  | Corrosion |  | Phase to earth |  | Mr Lance Edwards was outside washing his car when he received an electric shock from the external Garden Tap at the front of the property as he made simultaneous contact with his hand on the metal Tap and his feet in damp runners whilst standing on the wet ground. | Service conductor | 2 | 2 | 2 |  | WPD021 | Corroded connection | Minor shock | 43198.6667 |  |  | 10307 | Residential |  | 20180816PWA_02 | Infrastructure (customer connection) | -38.35 | 144.2921 | 1 | Powercor | Report | 12880 | 0.0036123 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
Crew dispatched to make safe, investigate and rectify. MFB onsite and pole alive to 190V. Supply isolated in pit, light repaired and put back into service. | 309 STUD ROAD, WANTIRNA SOUTH VIC 3152 | LIS1224715 |  |  |  | Defective component |  | Phase to earth | 2 | IMS 234965 - report of street light fire on pole LIS 1224715 | Public lighting | 0 | 0 | 0 |  | BRA21 | Internal light fitting fault. It would appear that the top cover dropped off some time ago leaving the internal control gear and wires exposed, causing the wiring to deteriorate and the PE base to fill up with water, Over time this caused a short to the body of the lantern livening up the concrete pole. | Pole-top fire | 20/08/2018 10:47 | 1 | Negligible: no ground fire | 10319 |  |  | 20180820SPN_01 | Infrastructure (network-based) | -37.8661 | 145.237 | 1 | AusNet Services Distribution | Report | 12896 | 0.018763 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna South | AF Other
Service crew and LEI dispatched to investigate, make safe and repair LEI proceeded to test metal downpipe and gutter and measured Voltage of 215V at down pipe next to meterbox to earth Service crew proceeded to isolate supply and repair service cable. LEI carried out and confirmed all tests passed. Customer left on supply | 20 BOWNESS COURT, CROYDON HILLS VIC 3136 | LIS1215378 |  | Blown branch/vegetation |  |  |  | Phase to earth |  | IMS 234829 - Customer reported electric shock from downpipe | Service conductor | 0 | 0 | 0 |  | CPK11 | Vegetation: Trees Incident | Minor shock | 43412.4715 |  |  | 10327 | Residential |  | 20180820SPN_07 | Infrastructure (network-based) | -37.7707 | 145.2712 | 1 | AusNet Services Distribution | Report | 13168 | 0.038372 | Low voltage AC (<1kV) | Moorabbin Airport | 3136 | Croydon Hills | Conductor
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded and loose Underground Service Neutral Conductor termination at the FOLCB on the Reticulation Pole. he attending Powercor Fault Crew reterminated the Underground Service Cable at the Reticulation Pole and completed an NST Test at the customer connection pillar which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 89-91 CHURCH STREET, GEELONG WEST VIC 3218 | 31013052 |  |  |  | Corrosion |  | Phase to earth |  | Mr Vikrant Trivedi was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet whilst standing on wet shower base. | Services cable | 2 | 2 | 2 |  | GL023 | Corroded connection | Minor shock | 19/08/2018 23:00 |  |  | 10328 | Residential |  | 20180821PWA_01 | Infrastructure (network-based) | -38.1314 | 144.3432 | 1 | Powercor | Report | 12909 | 0.039631 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Connection
Faulty appliance immediately disconnected from supply and shift manager informed The headset and base station was removed from service and quarantined. Employee did not sustain any injuries and did not need any medical attention. Faulty equipment to be sent off to ascertain if failure can be identified. | 452 FLINDERS STREET, MELBOURNE VIC 3000 |  |  |  |  | Fault on customer installation |  | Phase to earth | 2 | IMS 234724 - While reaching out for headset that was on charger received minor electric shock CEOT member was in the action of removing a wireless headset from its docking station and advised that a popping sound was heard and an electrical discharge was felt by the individual. | Customer appliance | 0 | 0 | 0 |  |  | Faulty headset base/charging station. | Minor shock | 43139.4306 |  |  | 10332 |  |  | 20180821SPN_03 | Infrastructure (network-based) | -37.8192 | 144.9585 | 2 | AusNet Services Distribution | Report | 12913 | 0.017289 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
Tree cleared and construction made necessary repairs. Supply restored following repairs | STARVATION CREEK ROAD, MCMAHONS CREEK VIC 3799 | LIS 1408875 |  | Within clearances |  |  |  | Phase to earth |  | IMS 235020 - Crew found cut tree fallen through 22kV conductors. | Conductor (bare) | 0 | 0 | 0 |  | WYK23 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/08/2018 10:00 |  |  | 10338 |  |  | 20180823SPN_01 | Infrastructure (network-based) | -37.7178 | 145.8001 | 2 | AusNet Services Distribution | Report | 13257 | 0.022476 | 22kV AC | Moorabbin Airport | 3799 | Mcmahons Creek | Trees
The crews removed the overhead service that was attached to the concrete pole and there was no meter on site. | 1 ROBERTS STREET, NOBLE PARK VIC 3174 | 631175 | Unauthorised work | [5 empty] | 2 | A Select Solutions Asset Inspector advised the United Energy Resource Coordinator that a overhead service has been removed and left hanging alive 3m from the ground at pole number LIS No. 631175. An abolishment has taken place at 1 Roberts Street, Noble Park and unknown persons have removed the single phase overhead service and left it hanging alive attached to the pole. A review of United Energy records indicate that no abolishment request had been received. | Service conductor | 0 | 0 | 0 |  |  | An abolishment has taken place and unknown persons have removed the single phase overhead service and left it hanging alive attached to the pole. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/08/2018 10:00 |  |  | 10345 | Roadway |  | 20180827UTD_03 | Infrastructure (network-based) | -37.9667 | 145.1777 | 1 | United Energy Distribution | Report | 12998 | 0.0036875 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Conductor
replaced service, strut removed strut found to have reappeared at later check | 954 BURKE ROAD, DEEPDENE VIC 3103 | 30167815 | Unauthorised work | [5 empty] | 2 | A crew attend the premises at 954 Bourke Rd to replace a service cable. On arrival, the crew found the pre existing service cable to premises at 954 Bourke Rd had been propped up with a piece of timber attached to the fence line to allow the neighbor to access 956 Bourke Rd with large equipment to demolish the premises on that site. The service was observed to be very tight with the prop installed. The crew removed the prop and retired the old service cable to 954 Bourke rd. When the crew attempted to re energize the premises at 954 follow a new service cable being installed, the premises failed an NST test. The crew observed the barge board and fuse box on the house at 954 had started to come away from the house and suspected an issue with the customer mains. An REC attended and made repairs. The crew completed another NST test. This time it passed. Supply to the premises at 954 was restored. | Aluminium twisted (grey);Aluminium twisted (XLPE) | 0 | 0 | 0 |  | L022 | interference with neighbours service | Loss of supply | 23/08/2018 11:06 |  |  | 10348 | Residential |  | 20180828PWA_01 | Infrastructure (customer connection) | -37.8096 | 145.0609 | 1 | CitiPower | Report | 13003 | 0.031022 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Connection
A faults truck attended and isolated the defective and burnt out 80w MV lantern. They returned during daylight the following day and replaced the lantern and burnt out wiring. | 45 BOONONG AVENUE, SEAFORD VIC 3198 | 3308283 |  |  |  | Overheated connection |  |  | 2 | Fire authority advised there is a street light on fire at the corner of Boonong and Kirkwood Avenues. A 80w MV lantern caught fire on pole No. LIS 3308283 located on the corner of Boonong and Kirkwood Avenues, Seaford. | Public lighting | 0 | 0 | 0 |  | FTN14 | The cause was a probable loose and overheated connection within the lantern. | Pole-top fire | 18/08/2018 1:26 | 1 | Negligible: no ground fire | 10349 | Roadway |  | 20180828UTD_02 | Infrastructure (network-based) | -38.126 | 145.13 | 1 | United Energy Distribution | Report | 18390 | 0.029118 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
The faults crew proceeded to replace the FOLCB on pole No. LIS 1817885 and supply was restored No. 20 upon completion and supply was left off to No. 22 pending the LEI investigation. | 22 QUEENS SQUARE, SANDRINGHAM VIC 3191 | 1817885 |  |  |  | Overheated connection |  |  | 2 | Pole fire on the overhead lines outside 22 Queens Square and the fire brigade are on their way. A pole mounted three phase FOLCB that contained an underground service that supplied 20 and 22 Queens Square caught on fire and proceeded to self-extinguish. The cause was unknown but most likely a loose connection that overheated. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. There appeared to be minor damage to the main switchboard at number 22 that had slight burn marks. A LEI was to be sent in daylight to make an assessment for any damage sustained. | Cable;Connection box | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. | Pole-top fire | 24/08/2018 3:50 | 1 | Negligible: no ground fire | 10352 | Roadway |  | 20180828UTD_03 | Infrastructure (network-based) | -37.947 | 145.0063 | 1 | United Energy Distribution | Report | 13008 | 0.014668 | Low voltage AC (<1kV) | Moorabbin Airport | 3191 | Sandringham | OH Cable
The crew disconnected and made safe the installation and completed the abolishment of supply and metering. | 27 A INDWE STREET, WEST FOOTSCRAY VIC 3012 |  | Vandalism | [5 empty] | 2 | Crew attended address for an abolishment of supply and metering. The supply and metering was found to be in a partially destroyed state and laying on the ground. Please note that it was still live upon arrival. Please see attached photos in section '7. Notes & Findings' to better illustrate how installation was found upon arrival. | Other meter;Connection to meter | 0 | 0 | 0 |  |  | Exact cause is unknown but it is likely to be Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/08/2018 12:00 |  |  | 10360 | Residential |  | 20180831JEM_01 | Infrastructure (network-based) | -37.8041 | 144.8648 | 1 | Jemena | Report | 13080 | 0.00084606 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Other
LEI dispatched to investigate and make safe | 5 DOVER COURT, DIAMOND CREEK VIC 3089 | LIS 5653187 |  |  |  | Induction;Fault on customer installation |  | Phase to earth |  | IMS 235071 - report of customer and REC receiving electric shock | No failed asset;Customer installation | 0 | 0 | 0 |  | ELM15 | Mr Dunnleavy was installing Polycarb to a section of his roof when he experienced a sensation that he believe may have been a slight electric shock or fright when he made contact with his hands to his roof whilst standing on a Aluminium ladder Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, did not reveal any defective conditions or equipment that would account for the voltage rise on the house roof. At the time of the investigation the only scenario identified that would account for voltage rise on the roof was induced voltage caused by the Transmission Lines in close proximity to the house roof. This was validated by measurement of the 210 volts by a very low burden instrument on the roof sheets which reduced to zero as the Roof was bonded | Minor shock | 29/08/2018 11:17 |  |  | 10368 |  |  | 20180903SPN_02 | Infrastructure (network-based) | -37.6639 | 145.1602 | 1 | AusNet Services Distribution | Report | 13262 | 0.03687 | Low voltage AC (<1kV) | Essendon Airport | 3089 | Diamond Creek | Installation
CEOT advised of incident and fault crew dispatched to make safe and investigate. Crew involved in incident have been stood down | 31 DAVIES ROAD, WARRENBAYNE VIC 3670 | LIS 3908519 and LIS 3907791 |  | Within clearances |  |  | Followed but inappropriate |  |  | IMS 235072 - Whilst clearing tree vegetation, a tree branch was cut and made contact with HV conductors between LIS 3908519 and LIS 3907791. Branch made contact only and no conductor damage or fire reported | Conductor (bare) | 0 | 0 | 0 |  | BN6 | Vegetation: Trees Incident | No Go Zone (no contact) | 29/08/2018 12:28 |  |  | 10369 |  |  | 20180903SPN_03 | Infrastructure (network-based) | -36.7028 | 145.8678 | 1 | AusNet Services Distribution | Report | 13261 | 0.041561 | 22kV AC | Wangaratta Aero | 3670 | Warrenbayne | Other
Crew Supervisor arrived at incident site, made safe and contacted AusNet Construction Coordinator and HDD management. AusNet representatives arrived on site and Crew Supervisor contacted relevant electricity faults department and advised Worksafe of incident. The IP contacted his supervisor to advise of the incident. The crew supervisor has then directed another crew member to take IP to hospital in the company vehicle. Commencing the drive to hospital, IP has called an ambulance to meet along the way. IP and crew member were met in Dixons Creek by ambulance which then transported IP to Maroondah Hospital for observation. Results from the hospital indicated high pulse and blood pressure. ECG indicated no irregular heart condition and was released from hospital. Following this incident, the following has been undertaken: Safetygram for awareness and review of Safe to Approach procedures for civil workers. Technical Bulletin to be released re findings. Training to be implemented. Awareness and Toolbox re incident rolled out to civil contractors. | 83 CASTELLA ROAD, CASTELLA VIC 3777 | LIS 1400846 |  |  |  |  | Not followed |  | 2 | Enablon E0000991 (IMS 235076) - report of earth dug up/exposed resulting in electric shock | Earth/earthing | 0 | 0 | 0 |  | KLK1 | A civil worker (IP) was conducting works to install a new underground HV cable between Pole 1400846 and Pole 1400845 at Castella Rd, Castella as part of the AusNet PRF project. During the excavation to Pole 1400846, (22kV transformer pole with hanging type transformer fitted) the crew has encountered an earthing cable at the base of the pole which was cut to facilitate an easier installation of the HV cable to the pole. After the HV cable has been attached to the pole, the IP has made contact with the pole end of the earthing cable and received an electric shock. The action of cutting the HV earth has caused a capacitance build up on the screen creating 11KV reading on the Modiwark and an Over limit reading on the LV tester. | Minor shock;Medical attention (first aid/doctor/hospital) | 29/08/2018 13:47 |  |  | 10370 |  |  | 20180903SPN_04 | Infrastructure (network-based) | -37.5229 | 145.4321 | 1 | AusNet Services Distribution | Report | 13260 | 0.0032083 | 22kV AC | Wallan (Kilmore Gap) | 3777 | Castella | Dug up
Zinfra linesman lowered the EWP bucket to the ground, exited EWP and sought attention. Relevant parties notified. Zinfra personnel assessed the situation and employee was taken to the local hospital for precautionary medical check and monitoring. ECG results were all clear. The pole was lowered into its final position which discharged induction from the suspended load (pole). A toolbox has been held with all project personnel and subcontractors to discuss the incident and corrective action. | WAVERLEY PARK DRIVE, MULGRAVE VIC 3170 |  |  |  |  | Induction |  | Phase to earth | 2 | IMS 235050 - Zinfra employee received electric shock (induction) | Crossarm (steel) | 0 | 0 | 0 |  |  | Zinfra Transmission power projects were currently working on the 220kV deviation project at Waverly Park in Mulgrave. While the suspended top section of a newly installed structure (pole) was being lowered into position, one of the linesmen working from the Elevated Work Platform (EWP) touched the end of the suspended top section cross arm. He received induction discharged from the suspended structure. Due to the location of the existing earthwire the tagline snagged against the earthwire which prevented the pole from slewing into its right position. All equipment EWP/ Crane were earthed to a common earth. Pole being erected was 12 metres away from the nearest live circuit which is outside the 6.4 metre NO GO ZONE. | Minor shock | 26/08/2018 11:16 |  |  | 10371 |  |  | 20180903SPN_05 | Infrastructure (network-based) | -37.9231 | 145.1888 | 2 | AusNet Services Transmission | Report | 13097 | 0.018301 | 220kV AC | Moorabbin Airport | 3170 | Mulgrave | Other
On arrival crew isolated supply and carried out repairs | 4 NORTHEY ROAD, GRAHAMVALE VIC 3631 | 30305074 |  | Bird |  |  |  |  | 1 | A pelican struck conductors, breaking conductors and initiating a small grass fire. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | SHN024 | Bird Incident | Loss of supply;Grassfire;Damage to network assets | 43199.5882 | 1 | Localised: less than 10 sq.m | 10380 | Roadway |  | 20180905PWA_02 | Infrastructure (network-based) | -36.333 | 145.4318 | 1 | Powercor | Report | 13116 | 0.030759 | 22kV AC | Shepparton Airport | 3631 | Grahamvale | Animal
Isolated supply to make safe. Attending crew conducted repairs and replaced the public lighting luminaire | 10 THE STRAND, WILLIAMSTOWN VIC 3016 | A024432 |  |  |  | Defective component |  |  | 2 | Public lighting luminaire high pressure sodium (HPS) fire No photo is available for this incident | Public lighting | 0 | 0 | 0 |  | NT04 | Public lighting luminaire failure | Other electricity related | 43109.059 | 1 | Negligible: no ground fire | 10387 | Residential |  | 20180907JEM_01 | Infrastructure (network-based) | -37.858 | 144.9021 | 1 | Jemena | Report | 17838 | 0.022911 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | AF Other
Network Connections was called and confirmed the meter is registered as a permanent meter installed in 2002. It was reconfigured for solar in 2012 and there is no record of attendance after 2012. Crew have disconnected the service and returned the meter, leaving the site off supply, Site is still under construction with no residence at this time. | 87 LAHINCH STREET, BROADMEADOWS VIC 3047 |  | Unauthorised work;Unauthorised access | [5 empty] | 2 | Crew attended an appointment at 87 Lahinch street Broadmeadows for a supply alteration from single phase to three phase (permanent connection). When they arrived the service was connected to a BTS pole (temporary connection). | Connection to meter | 0 | 0 | 0 |  |  | Suspected that there has been network asset interference by unauthorised personnel. | Damage to network assets | 43229.5 |  |  | 10388 | Residential |  | 20180907JEM_02 | Infrastructure (network-based) | -37.6877 | 144.9239 | 1 | Jemena | Report | 13127 | 0.021495 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Other
A faults truck attended and cut the surge diverter clear to make the site safe. The crew will return later in daylight and replace the faulty surge diverter. The cause was unknown with the weather calm at the time of the fault. | 7 ORMOND ROAD, ORMOND VIC 3204 | 2322622 |  |  |  | Defective component |  |  | 2 | Caller reports power lines are arcing and sparking outside the units. Pole No. 2322622. A 11kV surge diverter failed at pole No. LIS 2322622 that caused a pole fire. | Surge diverter | 0 | 0 | 0 |  | BT 09 | The cause was unknown with the weather calm at the time of the fault. | Pole-top fire | 28/08/2018 19:46 | 1 | Negligible: no ground fire | 10390 | Roadway |  | 20180909UTD_02 | Infrastructure (network-based) | -37.9034 | 145.0452 | 1 | United Energy Distribution | Report | 13129 | 0.0085775 | 11kV AC | Moorabbin Airport | 3204 | Ormond | Fuse
On arrival crew isolated supply and carried out repairs. | UNIT 1 2-4 CRELLIN AVENUE, LAVERTON VIC 3028 | 60069221 | Vandalism | [6 empty] | The customer, Michael Miller, at 2-4 Crellin Avenue Laverton reported loss of electrical supply. Powercor Fault crew attended found the service cable cut and removed between the pillar connection stud and ground level inside the pillar. There was fire, no reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | LV007 | Vandalsim | Loss of supply;Damage to network assets | 28/08/2018 9:20 |  |  | 10398 | Commercial |  | 20180910PWA_03 | Infrastructure (network-based) | -37.8687 | 144.7551 | 1 | Powercor | Report | 13139 | 0.022338 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Laverton | Other
Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, revealed a defective neutral and active conductor at the service pole which had fused together to create a dead short. he attending service crew replaced the single phase twisted pair service cable. All mandatory tests performed, a PASS result was obtained. Installation left ON supply. | 51 BUNGANOWEE DRIVE, CLIFTON SPRINGS VIC 3222 | 30244273 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr McConnell received an electric shock while he was Kneeling on the wet front lawn turning on the front tap when he made simultaneous contact between the tap and the wet front lawn. | Service conductor | 2 | 2 | 2 |  | DDL022 | Active and Neutral conductors of a twisted pair service conductor have been rubbing against each other | Minor shock | 19/08/2018 15:00 |  |  | 10413 | Roadway |  | 20180911PWA_05 | Infrastructure (network-based) | -38.1613 | 144.5699 | 1 | Powercor | Report | 13157 | 0.033547 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Clifton Springs | OH Cable
Fault crew dispatched and found transformer damaged due to possible Lighting strike. Crew replaced the Single phase 25kVA transformer and transported the damaged transformer in spill tray back to depot - Site clean up arranged by supervisor on call and completed | 230 JUMBUK ROAD, YINNAR SOUTH VIC 3869 | 2618516 |  | Lightning | [5 empty] | E0000844 - Transformer reported damaged due to possible Lighting strike. | Transformer | 0 | 1 | 0 |  | MWT31 | Transformer reported damaged due to possible Lighting strike , lost oil and requires replacing. No fire | Damage to network assets | 43290.1181 |  |  | 10408 |  |  | 20180911SPN_02 | Infrastructure (network-based) | -38.3318 | 146.3504 | 1 | AusNet Services Distribution | Report | 17781 | 0.018712 | 22kV AC | Morwell (Latrobe Valley Airport) | 3869 | Yinnar South | Lightning
Voltage tests by attending inspector revealed a severely corroded main neutral connection at pole. Attending fault crew repaired and reconnected main neutral conductor. Final tests were conducted for assurance, site PASSED. | FLEMINGTON RACECOURSE, 428-550 EPSOM ROAD, FLEMINGTON VIC 3031 |  |  |  |  | Corrosion;Neutral fault |  |  | 2 | Person received a shock from taps and metal fixtures. Techsafe attended to investigate. Full Techsafe report can be found in "7. Notes & Findings" | Aluminium twisted (XLPE);Connection box | 2 | 2 | 2 |  |  | Severely corroded neutral connection within connection box on network pole. | Minor shock | 43443.25 |  |  | 10415 | Commercial |  | 20180912JEM_01 | Infrastructure (network-based) | -37.7871 | 144.9206 | 1 | Jemena | Report | 13160 | 0.012906 | Low voltage AC (<1kV) | Essendon Airport | 3031 | Flemington | Connection
Supply was isolated to affect area and repairs carried out. | 3 COBDEN STREET, CAMPBELLFIELD VIC 3061 |  | Vehicle | [5 empty] | 2 | B-double truck clipped and bought down LV ABC. Truck driver details unavailable, however the police on site was SNR Medwin badge no 41907 from Broadmeadows. | Conductor (ABC) | 0 | 0 | 0 |  |  | Driver of large truck inadvertently clipped and bought down LV ABC. | Loss of supply | 14/09/2018 11:29 |  |  | 10428 | Residential |  | 20180914JEM_02 | Infrastructure (network-based) | -37.6677 | 144.949 | 1 | Jemena | Report | 13186 | 0.0084595 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Vehicle
Fault crew dispatched. Failed FOLCB isolated and replaced | 1 ECHO STREET, VENUS BAY VIC 3956 | LIS2804698 |  |  |  | Defective component |  |  |  | FOLCB reportedly caught fire. MFB onsite | Connection box | 0 | 0 | 0 |  | WGI24 | Fault crew attended and found melted pole mounted FOLCB. Crew isolated and replaced the failed FOLCB. FOLCB suffered melting only and there was no evidence fire. | Melting or smoking only | 43138.0208 |  |  | 10656 | Residential |  | 20181116SPN_02 | Infrastructure (network-based) | -38.7045 | 145.8287 | 2 | AusNet Services Distribution | Report | 17757 | 0.0066991 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3956 | Venus Bay | Connection
On arrival crew isolated supply for REC to repair POA, service then replaced | 6 DIGGORA PARADE, NUMURKAH VIC 3636 | 33080424 | Working too close to overhead lines | [6 empty] | A customer reported tree branches fell onto the service and damaged to POA at the incident location. Upon arrival, the Powercor crew found that the service and POA had been damaged by the cut down tree branches. There was no fire, no reported injuries | Service conductor | 2 | 2 | 2 |  | NKA004 | Vegetation: Trees Incident | No Go Zone (contact);Damage to network assets | 30/10/2018 12:50 |  |  | 10671 | Roadway |  | 20181120PWA_07 | Infrastructure (network-based) | -36.0853 | 145.4408 | 1 | Powercor | Report | 13531 | 0.029631 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Trees
Isolated and made safe. Repairs conducted and supply restored. | 3 MELISSA COURT, VIEWBANK VIC 3084 | A118631 |  | Wind;Fallen |  |  |  |  | 2 | Bay of LV OH conductors brought down by tree and strong winds. | Conductor (bare) | 0 | 0 | 0 |  | NH02 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2018 16:35 |  |  | 10675 | Residential |  | 20181121JEM_02 | Infrastructure (network-based) | -37.7309 | 145.1003 | 1 | Jemena | Report | 13535 | 0.0386 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Viewbank | Trees
Crews attended and arranged for a contractor to replace the earths. | 120 COMMON ROAD, INVERLEIGH VIC 3321 | 32064312 | Working too close to underground cables | [6 empty] | A Powercor crew discovered that an unknown person had performed drainage works within the vicinity of a Powercor Substation pole, damaging the earthing system of the substation. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | WIN013 | Unauthorised excavation near Powercor assets. | Damage to network assets | 43111.559 |  |  | 10682 | Roadway |  | 20181121PWA_06 | Infrastructure (network-based) | -38.0914 | 144.0606 | 1 | Powercor | Report | 13543 | 0.015774 | Earthing cable | Avalon Airport | 3321 | Inverleigh | Dug up
On arrival crew isolated supply and carried out repairs. There was suspected HVI but check by LEI found none. | 93 MCINTYRE ROAD, SUNSHINE NORTH VIC 3020 | 30110146 | Vehicle | [5 empty] | 1 | The MFB advised the contact center that a truck has collided with a pole on the corner of McIntyre Road and Warick Road in Sunshine, wires on the ground. A Powercor crew attended site to find a truck had collided with pole LIS 15146 breaking it at its base and causing the center phase conductor to break and fall onto the ground. The circuit breaker tripped to remove the faulted equipment from the system. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SSE011 | Truck struck pole | Damage to network assets | 23/11/2018 7:39 |  |  | 10693 | Roadway |  | 20181126PWA_01 | Infrastructure (network-based) | -37.7681 | 144.8303 | 1 | Powercor | Report | 13560 | 0.027541 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Vehicle
Fault crew dispatched. Police onsite | 137 NARRE WARREN ROAD, CRANBOURNE VIC 3977 | LIS505740; BW1387 | Vehicle | [6 empty] | E0005192 - report of car colliding with pole | Pole (concrete) | 0 | 0 | 0 |  | CRE32 | Police reported car collided with pole in residential street with 60kmh speed limit. Vehicle Ford ute with registration RQX-055 Car impact has damaged the base of the concrete pole, pole is damaged but serviceable and is being schedule for replacement. | Damage to network assets | 25/11/2018 1:04 |  |  | 10694 |  |  | 20181126SPN_01 | Infrastructure (network-based) | -38.1034 | 145.2916 | 1 | AusNet Services Distribution | Report | 13563 | 0.010803 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne | Vehicle
Fault crew dispatched to investigate and repair. Fault rectified. Warning devices have now been placed (refer to photo) on site. As per the photo evidence of TX damage. | 1-11 THE LINK, MILL PARK VIC 3082 | LIS 905523 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | E0005307 - Report of accidental contact with HV with an excavator contacting a transformer. Excavator contacted transformer LA (on Blue phase) and HV BA fuse (15k) operated. | Pole mounted | 0 | 1 | 0 |  | SMG31 | Excavator breached SADs and came into contact with the line apparatus (surge arrestors) of the Substation pole resulting in HV fuse operation. Warning devices were in place. Excavator operator details not known and not available. | No Go Zone (contact) | 27/11/2018 14:17 |  |  | 10703 | Residential |  | 20181128SPN_01 | Infrastructure (network-based) | -37.6593 | 145.0753 | 1 | AusNet Services Distribution | Report | 14992 | 0.027689 | 22kV AC | Essendon Airport | 3082 | Mill Park | Vehicle
On arrival crew isolated supply and carried out repairs. | 350 MILLERS ROAD, ALTONA NORTH VIC 3025 | 30116049 |  |  |  | Leakage |  |  | 1 | Vic Fire reported pole on fire near the intersection of Millers Road and Kororoit Creek Road. On arrival the crew found that a pole fire at the base of the 66kV center phase bridging insulator on pole LIS 5414 had caused it to break of and fall onto the cross-arm causing a 66kV line reclose. There was no ground fire, no reported injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | BTS-AL | Excessive leakage current | Pole-top fire | 29/11/2018 4:58 | 1 | Negligible: no ground fire | 10705 | Roadway |  | 20181129PWA_01 | Infrastructure (network-based) | -37.8496 | 144.844 | 1 | Powercor | Report | 13578 | 0.010385 | 66kV AC | Laverton Raaf | 3025 | Altona North | Pole
Crew fixed door to the transformer and filled in hole made by vandals | 30 FOX HOLLOW DRIVE, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Attempted copper theft of underground cable | Cable | 2 | 2 | 2 |  |  | Vandals attempted to steal copper underground cable to street lighting | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/11/2018 22:31 |  |  | 10710 | Public space |  | 20181201JEM_01 | Infrastructure (network-based) | -37.613 | 144.7325 | 1 | Jemena | Report | 13584 | 0.03303 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Repaired both HV and LV earth with 1 copper, along with putting new covers gaurds | 490 BARKLY STREET, FOOTSCRAY VIC 3011 |  | Theft | [5 empty] | 2 | Earth missing on pole A061978 SUMMERHILL-BARKLY | Earth/earthing | 2 | 2 | 2 |  |  | Whilst undergoing other type works crew called through a missing earth on A061978 looks as though earths had been cut away | Damage to network assets | 43112.6361 |  |  | 10712 |  |  | 20181201JEM_03 | Infrastructure (network-based) | -37.7977 | 144.8816 | 1 | Jemena | Report | 13909 | 0.041628 | Earthing cable | Essendon Airport | 3011 | Footscray | Other
On arrival crew isolated supply and carried out repairs. | 80 BUSHBYS ROAD, BARONGAROOK VIC 3249 | 33038382 |  | Blown branch/vegetation |  |  |  |  | 1 | During a severe wind storm a tree branch has contacted the 22kv conductors at the incident location. One conductor was brought to ground, tree debris remained in contact with other phase. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CLC007 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43112.7889 |  |  | 10720 | Roadway |  | 20181204PWA_02 | Infrastructure (network-based) | -38.4056 | 143.6243 | 1 | Powercor | Report | 13597 | 0.020737 | 22kV AC | Ballarat Aerodrome | 3249 | Barongarook | Trees
On arrival crew isolated supply and carried out repairs | 24-34 GLADSTONE STREET, SOUTHBANK VIC 3006 | 30167592 | Working too close to underground cables | [5 empty] | 1 | Contractor installing customer's service cable has bored into and damaged a high voltage underground cable of the MG018 11kV feeder. The feeder tripped to lockout as designed to remove the damaged cable from the Network. There was no injury of fire as a result of this incident. | Cable | 2 | 2 | 2 |  | MG018 | boring activities | Damage to network assets | 43292.5146 |  |  | 10722 |  |  | 20181204PWA_04 | Infrastructure (network-based) | -37.8289 | 144.9521 | 1 | CitiPower | Report | 13600 | 0.039498 | 11kV AC | Essendon Airport | 3006 | Southbank | Dug up
Damaged powercor underground service cable replaced | 6 SARSFIELD STREET, SEPARATION CREEK VIC 3234 | 32067020 | Working too close to underground cables | [5 empty] | 2 | Civil Construction received an electric shock from the Underground Service Cable in the Road Reserve when his crowbar punctured the Conduit and damaged the Insulation of the White Phase Conductor whilst undertaking drainage works near the property boundary. | Services cable | 0 | 0 | 0 |  | CLC007 | Interference | Minor shock | 43445.6042 |  |  | 10735 | Roadway |  | 20181204PWA_17 | Infrastructure (network-based) | -38.629 | 143.899 | 1 | Powercor | Report | 13613 | 0.0017535 | Low voltage AC (<1kV) | Avalon Airport | 3234 | Separation Creek | Dug up
Replaced the existing service cable to the property | 8 MALVEN CLOSE, WERRIBEE VIC 3030 | 30108851 |  |  |  | Corrosion;Neutral fault |  |  | 2 | Person received an electric shock when she made simultaneous contact between the metallic taps with her hands and the shower waste and floor with her feet. | Service conductor | 0 | 0 | 0 |  | WBE023 | Corroded Service Neutral Connection | Minor shock | 43415.6458 |  |  | 10737 | Residential |  | 20181204PWA_19 | Infrastructure (customer connection) | -37.89 | 144.6348 | 1 | Powercor | Report | 13615 | 0.013826 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
Fault crew dispatched to make safe and investigate. Circuit isolated from RW1673 and HV fuses pulled | 1-11 WALKER ROAD, WONGA PARK VIC 3115 | LIS1203478 |  | Blown branch/vegetation |  |  |  | Phase to earth |  | E0005618 - report of blown-in tree branch contacting powerline and subsequent ground fire in vicinity of pole | Conductor (bare) | 0 | 0 | 0 |  | CPK11 | Vegetation: Trees Incident | Grassfire | 43143.4444 | 1 | Localised: less than 10 sq.m | 10743 | Roadway |  | 20181205SPN_01 | Infrastructure (network-based) | -37.7466 | 145.262 | 1 | AusNet Services Distribution | Report | 13722 | 0.024499 | 22kV AC | Moorabbin Airport | 3115 | Wonga Park | Trees
The section is to be isolated by breaking bridges and a follow up will be required to replace trifurcating box & HV X-Arm. HV crossarm was replaced, the site was evaluated and made safe and all customers are restored. There is a program in place to remove and replace the ageing pitch filled metal trifurcating boxes with modern cable terminations on JEN network. Only a preliminary investigation was done to confirm the fire start. | 2 DOVER STREET, FLEMINGTON VIC 3031 | A028095 |  |  |  | Electrical breakdown |  |  | 2 | Fire at pole top due to cable termination failure No photo is available for this incident | Connector/termination | 0 | 0 | 0 |  | FT11 | Gas Switch #28214 the Pot Head has failed. The root cause of failure of the pothead, i.e. fabricated metal trifurcating boxes is the ingress of moisture resulting in the deterioration of the paper insulation. With time, paper can become brittle and absorb moisture which reduces its dielectric strength giving way to partial discharges. Degradation of paper also occurs from heating of the copper conductor, especially during times of peak demand as more current is pushed through the conductors. These partial discharges break down and weaken the paper insulation ultimately resulting in flashover. | Other electricity related | 43263.7396 | 1 | Negligible: no ground fire | 10765 | Public space |  | 20181206JEM_01 | Infrastructure (network-based) | -37.7833 | 144.9278 | 1 | Jemena | Report | 17753 | 0.029587 | 11kV AC | Essendon Airport | 3031 | Flemington | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | NEPEAN PLACE, PORTSEA VIC 3944 | 1307258 |  | Precipitation |  | Leakage |  |  | 2 | The CFA reported a pole fire in Point Nepean Road, Portsea. During light drizzly rain, a pole fire occurred at a HV/LV strain pole LIS No. 1307258 located in Nepean Place. Pole top tracking had caused the pole to burn where the king bolt is attached at the LV cross arm. As the pole is located near the ocean, it was suspected that tracking on the pole top assembly was the cause that contributed to the pole fire. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | STO 22 | As the pole is located near the ocean, it was suspected that tracking on the pole top assembly was the cause that contributed to the pole fire. | Pole-top fire | 23/11/2018 10:55 | 1 | Negligible: no ground fire | 10758 | Roadway |  | 20181206UTD_05 | Infrastructure (network-based) | -38.3204 | 144.7135 | 1 | United Energy Distribution | Report | 13648 | 0.034475 | 22kV AC | Avalon Airport | 3944 | Portsea | Pole
Regulator isolated for replacement | 1728 COLAC-LAVERS HILL ROAD, KAWARREN VIC 3249 | 32065329 |  |  |  | Electrical breakdown |  |  | 1 | CFA reported substation exploded , was smoking and oil leaking to ground. On arrival crew found that regulator had apparently faulted in the tap changer, ruptured the sight glass and expelled a volume of transformer oil from the tap changer mechanism tank. No evidence of fire found. No injury or third party damage. | Voltage regulator | 0 | 1 | 0 |  | CLC006 | Internal fault in tap changer | Loss of supply | 43263.8125 |  |  | 10776 | Other | Network Enclosure | 20181210PWA_03 | Infrastructure (network-based) | -38.4915 | 143.5671 | 1 | Powercor | Report | 15084 | 0.017991 | 22kV AC | Ballarat Aerodrome | 3249 | Kawarren | AF Other
Crew re-terminated the service neutral at the POA. | UNIT 1 181 ROSLYN ROAD, BELMONT VIC 3216 | 30071172 |  |  |  | Neutral fault |  |  | 2 | Customer was having a bath when she felt a slight tingle to her left hand when adjusting the hot water tap. Her body was fully immersed in the bath water at the time. | Aluminium twisted (XLPE);Connection box | 0 | 0 | 0 |  | GCY023 | Loose connection | Minor shock | 30/11/2018 19:00 |  |  | 10778 | Residential |  | 20181210PWA_05 | Infrastructure (customer connection) | -38.1742 | 144.331 | 1 | Powercor | Report | 13674 | 0.018403 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
CFA attended fire incident. AusNet Services fault crew attended to make safe. | 173-175 HIGH STREET, MANSFIELD VIC 3722 | LIS 3916716 & LIS 3916717 |  | Blown branch/vegetation |  |  |  | Phase to earth |  | E0006056 - Report of O/H service line down and subsequent ground fire | Neutral screen | 0 | 0 | 0 |  | MSD4 | Vegetation: Trees Incident | Grassfire | 43293.6819 | 1 | Small: 10 - 1000 sq.m | 10771 |  |  | 20181210SPN_01 | Infrastructure (network-based) | -37.0499 | 146.0807 | 1 | AusNet Services Distribution | Report | 13895 | 0.028657 | Low voltage AC (<1kV) | Wangaratta Aero | 3722 | Mansfield | Trees
Upon arrival the fault crew found confirmed the believe the earthing cable had been damaged some time ago. The crew carried out repairs. | 1761 MCIVOR HIGHWAY, LONGLEA VIC 3551 | 30255311 | Working too close to underground cables | [6 empty] | A contractor reported an earthing dug up at the incident location. The contractor claimed that the cable had already been damaged prior to works There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BET005 | Excavation work | Damage to network assets | 26/11/2018 10:36 |  |  | 10790 | Agricultural |  | 20181212PWA_01 | Infrastructure (network-based) | -36.778 | 144.4568 | 1 | Powercor | Report | 13689 | 0.018486 | Earthing cable | Bendigo Airport | 3551 | Longlea | Dug up
Service line isolated and subsequently replaced | 2 HARROW ROAD, EDENHOPE VIC 3318 | 32094372 |  |  |  | Corrosion |  |  |  | Customer was in the Kitchen washing her hands at the sink when she received an electric shock as she made simultaneous contact between one hand on the Kitchen Tap and her other hand on the metallic Sink. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | CHM011 | Corroded O/H Service Neutral Conductor termination | Minor shock | 43293.5 |  |  | 10792 | Residential |  | 20181212PWA_03 | Infrastructure (network-based) | -37.0367 | 141.3022 | 1 | Powercor | Report | 13692 | 0.020653 | Low voltage AC (<1kV) | Horsham Aerodrome | 3318 | Edenhope | OH Cable
Crew replaced cable and restored supply to intersection. | 20 LANCEFIELD ROAD, BULLA VIC 3428 |  | Copper theft | [5 empty] | 2 | Jemena linesman reports all pits are open supplying street lights at cnr Lancefield and Sunbury Rds. 4 core U/G service cables have been stolen by vandals and need to be replaced as major intersection and no main road lighting because of damage.ref tbl# 173807 | Copper | 0 | 0 | 0 |  |  | Copper theft and street light cables were stolen from street light pits. | Loss of supply | 43446.659 |  |  | 10795 |  |  | 20181213JEM_01 | Infrastructure (network-based) | -37.5964 | 144.7602 | 1 | Jemena | Report | 13698 | 0.0027049 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
Emergency high voltage switching was completed to isolate the faulted area, and the electrical infrastructure was repaired under Access Authority conditions. LEI's investigated the amount of damage that occurred to customers appliances and equipment. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 23 NEPEAN STREET, GLEN IRIS VIC 3146 | 2311922 |  | Blown branch/vegetation |  |  |  |  | 1 | A branch from a tree located on the nature strip outside 23 Nepean St Glen Iris broke and caused the HV conductors to come into contact with the transformer at Nepean Park DSS. This caused a high voltage injection into the LV network on both the east and west side of the circuit. The feeder CB K8 reclosed and opened to lock-out. | Conductor (bare);Transformer | 0 | 1 | 0 |  | K8 | Vegetation: Trees Incident | HV injection | 43112.5743 |  |  | 10799 | Roadway |  | 20181213UTD_01 | Infrastructure (network-based) | -37.8485 | 145.056 | 1 | United Energy Distribution | Report | 13703 | 0.013697 | 11kV AC | Moorabbin Airport | 3146 | Glen Iris | Trees
Emergency high voltage switching was completed to isolate the faulted area and the electrical infrastructure was repaired under Access Authority conditions. LEI's investigated the amount of damage that occurred to customers appliances and equipment . Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 6 OLD WELLS ROAD, PATTERSON LAKES VIC 3197 | 3305657 |  | Wind |  | Defective component |  |  | 1 | During stormy weather, a connector failed on a cable head pole, allowing the HV connector cable to drop and make contact with LV conductor. The feeder protection operated, however HV injection resulted from the contact between HV and LV conductors. | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | CRM21 | Failed connector on HV dropper during stormy weather. | HV injection | 43143.1562 |  |  | 10801 | Roadway |  | 20181213UTD_03 | Infrastructure (network-based) | -38.0719 | 145.1496 | 1 | United Energy Distribution | Report | 13706 | 0.0077049 | 22kV AC | Moorabbin Airport | 3197 | Patterson Lakes | Connection
Fault crew dispatched to investigate and repair. | 45 MCGRETTONS ROAD, HEALESVILLE VIC 3777 | LIS 1403502 |  | Fallen | [5 empty] | E0006156 - Tree contacted HV & LV conductors. Ground fire reported in the area. | Conductor (bare) | 0 | 0 | 0 |  | LDL23 | Vegetation: Trees Incident | Grassfire | 43416.1653 | 1 | Localised: less than 10 sq.m | 10806 | Agricultural |  | 20181214SPN_02 | Infrastructure (network-based) | -37.6591 | 145.5027 | 2 | AusNet Services Distribution | Report | 13717 | 0.014387 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3777 | Healesville | Trees
Fault crew dispatched. Street light isolated and replaced | 56 RYELANDS DRIVE, NARRE WARREN VIC 3805 | LIS5693444 |  |  |  | Defective component |  |  |  | Street Light Fire reported. | Public lighting | 0 | 0 | 0 |  | NRN13 | Cause of street light failure not known. Light fitting replaced. Street light head fire only and no ground fire present | Pole-top fire | 43112.9896 | 1 | Negligible: no ground fire | 10809 |  |  | 20181214SPN_05 | Infrastructure (network-based) | -38.0169 | 145.3181 | 1 | AusNet Services Distribution | Report | 17762 | 0.026626 | Low voltage AC (<1kV) | Moorabbin Airport | 3805 | Narre Warren | AF Other
Substation decommissioned and equipment removed. | 1-5 LAKE DRIVE, DINGLEY VILLAGE VIC 3172 | Oak Willow indoor substation | Vandalism;Theft;Unauthorised access;Copper theft | [5 empty] | 2 | Factory sub station (Oak-Willow DSS) broken into. The hasp & staple was damaged for entry into substation. The substation equipment all ok, only the LV isolators to factory supply were opened. The customer's factory was vandalised, copper cables cut and stolen, other equipment smashed or pulled apart. | Disconnector/isolator;Indoor;Customer installation | 2 | 2 | 0 |  | SS24 | Copper theft | Loss of supply | 43202 |  |  | 10810 | Industrial |  | 20181214UTD_01 | Infrastructure (network-based) | -37.9804 | 145.1114 | 1 | United Energy Distribution | Report | 13826 | 0.025091 | Low voltage AC (<1kV) | Moorabbin Airport | 3172 | Dingley Village | Other
On arrival crew isolated supply and carried out repairs. | 454 ELAINE-MORRISONS ROAD, MORRISONS VIC 3334 | 30001236 |  |  |  | Unknown technical factor |  |  |  | A report was received from a customer that there was a fuse box fire on the transformer pole at the above location. A Powercor crew attended and determined that the LV fuse box on Simpson Spur Pole 4 had caught fire and melted. A small section of the pole sustained minor burn damage. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS022 | Insufficient remains to identify cause | Pole-top fire | 16/12/2018 18:25 | 1 | Negligible: no ground fire | 10813 | Roadway |  | 20181217PWA_02 | Infrastructure (network-based) | -37.7741 | 144.0836 | 1 | Powercor | Report | 13731 | 0.022306 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3334 | Morrisons | Fuse
The customer has extinguished the fire using a fire extinguisher. Crew isolated supply and carried out repairs. | 355 WILLOW GROVE ROAD, KOTTA VIC 3565 | 33079969 |  |  |  | Fuse failed to eject |  |  |  | Customer phoned in to report a grass fire has started outside the front of her property, caused by falling debris from the pole. On arrival the crew found that a EDO HV Fuse unit became overheated and dropped hot debris onto the dry grass below igniting a ground fire. Fire area was around 3 x 150m There was no reported injuries. | EDO fuse | 2 | 2 | 2 |  | ECA012 | Corrossion | Grassfire | 17/12/2018 13:40 | 1 | Small: 10 - 1000 sq.m | 10815 | Roadway |  | 20181217PWA_04 | Infrastructure (network-based) | -36.1666 | 144.571 | 1 | Powercor | Report | 13734 | 0.0378 | 22kV AC | Bendigo Airport | 3565 | Kotta | Fuse
Dispatched fault crew to investigate and make safe. Replaced fuse. New follow up notification raised to upgrade fuse to BA type and animal proof substation. | 275 NERRENA HALL ROAD, NERRENA VIC 3953 | Pole 2001171 |  | Animal | [5 empty] | E0006540 - Candled HV EDO Fuse. Possum blown Fuse. Wood pole ,o other damage. Refer to the photo of the failed fuse. | EDO fuse | 0 | 0 | 0 |  | LGA14 | Animal Incident | Pole-top fire | 17/12/2018 10:35 | 1 | Negligible: no ground fire | 10816 | Agricultural |  | 20181218SPN_01 | Infrastructure (network-based) | -38.5157 | 145.9825 | 1 | AusNet Services Distribution | Report | 17910 | 0.011275 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3953 | Nerrena | Animal
Fault crew dispatched. Candling BA fuse replaced | 32 DICKENS ROAD, EVERTON UPPER VIC 3678 | 4501721 |  |  |  | Candled fuse |  |  | 0 | E0006717 - report of fuse candling | Boric acid | 0 | 0 | 0 |  | WN5 | HV fuse candled. It appears the striker pin may not have operated to drop the Boric Acid fuse out. There was no evidence of ground fire. | Pole-top fire | 18/12/2018 6:00 | 1 | Negligible: no ground fire | 10822 |  |  | 20181218SPN_03 | Infrastructure (network-based) | -36.3897 | 146.5227 | 2 | AusNet Services Distribution | Report | 17907 | 0.010991 | 12.7kV AC (SWER) | Wangaratta Aero | 3678 | Everton Upper | Fuse
On arrival crew isolated supply and carried out repairs. | 15 PETER DRIVE, SUNSHINE WEST VIC 3020 | 34015047 | Vehicle | [6 empty] | MRS CHRISTINE GULMEN, 0418 115 110, from No. 15 Peter Drive, Sunshine West 3020, has phoned in to advise that a car has hit pillar on nature strip can see exposed wires, no supply issues. On arrival the crew found that a vehicle had lost control and struck fence and pillar. There was no fire or reported injuries. | LV Pillar | 2 | 2 | 2 |  | SU035 | Vehicle collision | Damage to network assets | 43143.2688 |  |  | 10827 | Roadway |  | 20181219PWA_01 | Infrastructure (network-based) | -37.798 | 144.8016 | 1 | Powercor | Report | 13751 | 0.0020278 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Vehicle
Fault crew dispatched to make safe and carry out repairs | 66 BEARD STREET, ELTHAM VIC 3095 | LIS918697 |  |  |  | Defective component |  |  | 2 | E0006823 - MFB reported pole fire | Pole (wood);Connector/termination | 0 | 0 | 0 |  | ELM13 | white phase fused isol appears to have burnt at the 'U' bolt resulting in a small fire at base of pole | Grassfire | 19/12/2018 19:32 | 1 | Localised: less than 10 sq.m | 10830 |  |  | 20181220SPN_01 | Infrastructure (network-based) | -37.7046 | 145.1606 | 2 | AusNet Services Distribution | Report | 17906 | 0.0064259 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham | Connection
Line isolated and crews replaced cross-arm under EAP. | 38 GLENOLA ROAD, CHELSEA VIC 3196 | 3306114 |  | Bird |  |  |  |  | 1 | Received report of wire sparking on the ground. Fault crews attended and found live bare HV wire on ground due to failed cross-arm due to white ant infestation. Crews made safe, LEI dispatched to inspect nearby premises, and confirmed no HVI. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | CRM14 | Failed cross-arm | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/12/2018 16:05 |  |  | 10829 | Roadway |  | 20181220UTD_01 | Infrastructure (network-based) | -38.0555 | 145.1232 | 1 | United Energy Distribution | Report | 13756 | 0.0018299 | 22kV AC | Moorabbin Airport | 3196 | Chelsea | Animal
Crew attended and replaced LV isolator | 43 FAIRBAIRN DRIVE, CORIO VIC 3214 | 31012734 |  |  |  | Overheated connection |  |  | 2 | CFA crew attending a house fire at #33 Fairbairn drive identified a second fire on a nearby pole. Attending crew found broken LV isolator. discussion with CFA fire investigator and review of AMI information confirmed that LV isolator fire was unrelated to house fire. House fire is being treated as suspicious and CFA supporting VICPOL forensic investigations | Any other type | 0 | 0 | 0 |  | FNS012 | Overheated connection | Pole-top fire | 19/12/2018 4:02 | 1 | Negligible: no ground fire | 10835 | Residential |  | 20181221PWA_02 | Infrastructure (network-based) | -38.0632 | 144.3769 | 1 | Powercor | Report | 13764 | 0.013139 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
A lightning strike on pole No. LIS 1233313 located outside 611 Balcombe Road and subsequently damaged surge diverters with small pole top fire evident for a short time. A faults crew attended and the defective surge diverters were cut clear and supply restored to customers in the vicinity. | 611 BALCOMBE ROAD, BLACK ROCK VIC 3193 | 1812587 |  | Lightning |  |  |  |  | 1 | Per MFB - transformer on fire near the corner of Beach Road and Edward Street. During stormy conditions at 1019hrs on 06/11/2018, 11kV ACR CH7525 located in Bluff Road reclosed to lockout affecting 667 customers. | Surge diverter | 0 | 0 | 0 |  | BR 4 | Lightning struck a HV cable head pole. | Pole-top fire | 43262.4299 | 1 | Negligible: no ground fire | 10842 | Roadway |  | 20181224UTD_01 | Infrastructure (network-based) | -37.9756 | 145.0166 | 1 | United Energy Distribution | Report | 18389 | 0.034973 | 11kV AC | Moorabbin Airport | 3193 | Black Rock | Lightning
A faults truck attended and completed rectification work under Access Permit conditions. The timber pole was assessed and deemed to be okay but the damaged steel HV cross arm required replacement. | 14 GREENLAW CRESCENT, MOUNT MARTHA VIC 3934 | 1102908 | Vehicle | [5 empty] | 1 | At 1747hrs on 14/12/2018, 22kV ACR MT 7681 located in Bay Road, reclosed to lockout affecting 440 customers. There were reports of a vehicle contacting a pole in Greenlaw Crescent and the CFA and police are in attendance. A vehicle struck timber pole No. LIS 1102908 located in Greenlaw Crescent with a steel HV cross arm and intermediate/angle type construction. The steel cross arm was bent and the white phase HV conductor was knocked from the insulator and made contact with a nearby cypress tree that burnt two branches. | Conductor (bare);Crossarm (steel) | 0 | 0 | 0 |  | DMA 24 | A vehicle made contact with a HV LV intermediate/angle pole in Greenlaw Crescent, Mount Martha. | Other vegetation | 14/12/2018 17:47 | 1 | Negligible: no ground fire | 10845 | Roadway |  | 20181227UTD_01 | Infrastructure (network-based) | -38.2755 | 145.0246 | 1 | United Energy Distribution | Report | 13778 | 0.0049618 | 22kV AC | Moorabbin Airport | 3934 | Mount Martha | Vehicle
HV fuses opened to isolate. Repairs made during the following day. | 308 HARRINGTONS ROAD, GLENORMISTON NORTH VIC 3265 | 32054677 |  |  |  | Mechanical vibration;Overheated connection |  |  |  | Vicfire reported wires down causing approximately 100m x 100m grass fire, a crew dispatched to investigate. Upon arrival to the incident location, the lineworker identified evidence of a grassfire and a HV lead had come loose and burnt away from the HV bushing on the pole Tx. Made safe for repairs to be made during daylight hours. | Dropper/bridge | 0 | 0 | 0 |  | TRG001 | Connection at transformer HV bushing parted | Grassfire | 31/12/2018 13:46 | 1 | Medium: 1000 sq.m - 10 ha | 10854 | Agricultural |  | 20190102PWA_01 | Infrastructure (network-based) | -38.1382 | 143.0049 | 1 | Powercor | Report | 13788 | 0.023553 | 22kV AC | Warrnambool Airport Ndb | 3265 | Glenormiston North | Connection
On arrival crew isolated supply - service replaced | 2154 BEAUFORT-LEXTON ROAD, LEXTON VIC 3352 | 30011244 |  |  |  | Electrical breakdown;Mechanical breakdown |  |  |  | Vicfire reported a pole fire caused a grass fire at incident location. On arrival crew found that a neutral screen service had ruptured at the pole end had started a grass fire. There were no reported injuries | Service conductor | 2 | 2 | 2 |  | BAN006 | Ruptured service cable | Grassfire | 31/12/2018 13:38 | 1 | Medium: 1000 sq.m - 10 ha | 10857 | Agricultural |  | 20190102PWA_04 | Infrastructure (customer connection) | -37.297 | 143.4998 | 1 | Powercor | Report | 13796 | 0.029837 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Lexton | OH Cable
On arrival crew isolated supply and carried out repairs. | 10 COCOPARRA CRESCENT, TAYLORS LAKES VIC 3038 | 60066957 | Working too close to underground cables | [6 empty] | A report was received by Powercor of an LV pillar being damaged by a bobcat at the incident location. On arrival the crew observed that a LV pillar assembly located in the front of the property had been damaged. There was no fire, no reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | SA010 | Landscaping operations using bobcat | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43497.6597 |  |  | 10859 | Public space |  | 20190103PWA_01 | Infrastructure (network-based) | -37.7095 | 144.7996 | 1 | Powercor | Report | 13798 | 0.026395 | Low voltage AC (<1kV) | Melbourne Airport | 3038 | Taylors Lakes | Vehicle
Repairs and testing completed prior to commissioning | 2-4 ST GEORGES ROAD, FITZROY NORTH VIC 3068 | 30163082 | Unauthorised work;Unauthorised access | [6 empty] | Kare Group contractor moved pillar after completion of Citi power works and re terminated cables. This occurred prior to commissioning of supply There was no fire, no reported injuries or third party property damage. | Services cable;Connection box | 2 | 2 | 2 |  | F033 | interference to CP assets prior to commissioning | Damage to network assets | 27/09/2018 7:20 |  |  | 10861 | Commercial |  | 20190103PWA_03 | Infrastructure (network-based) | -37.7916 | 144.9765 | 1 | CitiPower | Report | 13800 | 0.030966 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Other
service replaced | 26 CROFTON STREET, GEELONG WEST VIC 3218 | 30252202 |  |  |  | Corrosion |  |  |  | Customer was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower tap and her bare feet while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | GL012 | Corroded Neutral Conductor in the O/H Neutral Screened Service Cable | Minor shock | 43293.375 |  |  | 10866 | Residential |  | 20190103PWA_08 | Infrastructure (customer connection) | -38.1432 | 144.3395 | 1 | Powercor | Report | 13805 | 0.013855 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | OH Cable
On arrival crew isolated supply and carried out repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298011 | Vandalism;Copper theft | [6 empty] | Customer report of pits open at incident location and public lighting underground cables stolen or damaged There was no fire and no reported injuries | Cable;Services cable | 2 | 2 | 2 |  | MLN023 | copper theft & vandalism | Loss of supply;Damage to network assets | 43385.5222 |  |  | 10873 | Roadway |  | 20190104PWA_07 | Infrastructure (network-based) | -37.6866 | 144.5495 | 1 | Powercor | Report | 13813 | 0.035291 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and replaced transformer | 105 MOUNT VIEW ROAD, GREAT WESTERN VIC 3374 | 32116024 |  | Lightning | [5 empty] | Customer reported pole was sparking and this caused a ground fire of approximately 1mÂ² in the vicinity of the base of the pole. On arrival crew found that the transformer had failed. There was no reported injuries or third party property damage | Transformer | 2 | 1 | 2 |  | ART031 | Transformer failure attributed to lightning activity | Grassfire | 43525.7326 | 1 | Localised: less than 10 sq.m | 10879 | Agricultural |  | 20190104PWA_13 | Infrastructure (network-based) | -37.1247 | 142.8461 | 1 | Powercor | Report | 13819 | 0.017703 | 12.7kV AC (SWER) | Horsham Aerodrome | 3374 | Great Western | Lightning
On arrival crew isolated supply. Transformer and edo fuse unit replaced | 585 DERWENT JACKS ROAD, BERRINGA VIC 3351 | 30272578 |  | Lightning |  | Fuse failed to eject |  |  |  | Customer reported following a lightning strike there was a pole fire at the incident location. On arrival crew found EDO fuse hung up and fire extinguished by rain. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | BAS021 | Lightning strike, EDO fuse hung up and caught fire | Pole-top fire | 30/12/2018 9:50 | 1 | Negligible: no ground fire | 10897 | Agricultural |  | 20190107PWA_13 | Infrastructure (network-based) | -37.7712 | 143.6873 | 1 | Powercor | Report | 13840 | 0.039772 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3351 | Berringa | Lightning
On arrival crew isolated supply and replaced surge diverter | 48 PALM AVENUE, SPRING GULLY VIC 3550 | 32053216 |  | Blown branch/vegetation |  |  |  |  | 1 | Vic fire reported tree branch had contacted power lines no arcing or sparking, smoke was reported at incident location. On arrival the crew found that a tree branch had fallen and made brief contact with a surge diverter on a cable head pole causing it to flashover. There was no fire, no reported injuries or third party property damage. | Cable;Surge diverter | 2 | 2 | 2 |  | BET007 | Vegetation: Trees Incident | Loss of supply;Singeing or local charring/blackening only | 23/12/2018 16:33 |  |  | 10900 | Residential |  | 20190108PWA_02 | Infrastructure (network-based) | -36.7895 | 144.2918 | 1 | Powercor | Report | 13844 | 0.014272 | 22kV AC | Bendigo Airport | 3550 | Spring Gully | Trees
Fault crew dispatched and candling fuse replaced | 437 BOLGERS ROAD, DEVON NORTH VIC 3971 | LIS2624660 |  |  |  | Candled fuse |  |  |  | Candling fuse reported | Boric acid | 0 | 0 | 0 |  | FTR12 | fuse candling | Pole-top fire | 43586.9771 | 1 | Negligible: no ground fire | 10906 |  |  | 20190108SPN_02 | Infrastructure (network-based) | -38.5258 | 146.5983 | 2 | AusNet Services Distribution | Report | 17903 | 0.023241 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Devon North | Fuse
the substation was isolated to make safe and repairs have been undertaken | 555 RESERVOIR ROAD, SUNBURY VIC 3429 |  | Copper theft | [6 empty] | Vandals have removed copper cable from substation pole. | Cable;Copper | 0 | 0 | 0 |  |  | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43739.559 |  |  | 10916 |  |  | 20190110JEM_01 | Infrastructure (network-based) | -37.5685 | 144.6743 | 1 | Jemena | Report | 13867 | 0.032012 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
The crew carried out repairs to the damaged cable and restored supply to the customer. | 600 YANKEE FLAT ROAD, MOUNT HELEN VIC 3350 | 33000825 | Working too close to underground cables | [6 empty] | A Powercor crew responded to a customer call relating to an All Supply Failure. After extensive investigation, the crew determined that an unknown contractor had damaged the LV U/G service cable to this property whilst installing a telecommunications cable along the road reserve. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BAS013 | Unknown person damaged service cable at previous time. | Loss of supply;Damage to network assets | 15/12/2018 6:33 |  |  | 10911 | Roadway |  | 20190110PWA_01 | Infrastructure (network-based) | -37.6357 | 143.9138 | 1 | Powercor | Report | 13862 | 0.0058912 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Mount Helen | OH Cable
Fault crew attended site same day to complete necessary repairs. | 503 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 30283246 | Vandalism;Copper theft | [5 empty] | 2 | Chris from Electrix was undertaking maintenance activities and called to report the theft of approx. 3m of HV earth at incident location. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN022 | Copper theft | Damage to network assets | 17/12/2018 8:18 |  |  | 10913 | Roadway |  | 20190110PWA_03 | Infrastructure (network-based) | -37.6876 | 144.5305 | 1 | Powercor | Report | 13864 | 0.036987 | Earthing cable | Laverton Raaf | 3338 | Brookfield | Other
Crew dispatched to investigate and make site safe. Crew replaced failed EDO fuses. A follow on maintenance notification was raised to replace EDO fuses with BA's and to inspect transformer bushings. | 37 THOMAS LANE, CORRYONG VIC 3707 | LIS 5782002 |  |  |  | Unknown technical factor |  |  |  | Hung up 6k EDO fuse on concrete pole. Unknown reason for fuse operations and multiple fuse hang-ups. Substation is fully animal proofed, fuses are 6k EDO's and are on stand off insulators. No evidence of fire or burning at base of pole. No photos available. | EDO fuse | 0 | 0 | 0 |  | WOTS24 | Hung-up fuse only. Unable to find the root cause. Follow up maintenance raised to check TX bushings. | Hung-up fuse only | 18/12/2018 14:32 |  |  | 10918 |  |  | 20190110SPN_02 | Infrastructure (network-based) | -36.1849 | 147.9139 | 2 | AusNet Services Distribution | Report | 17758 | 0.017978 | 22kV AC | Wangaratta Aero | 3707 | Corryong | AF Other
Hung-up EDO fuse replaced | THISTLE DOWN, 61 ADAMS LANE, STAGHORN FLAT VIC 3691 | 5202029 |  |  |  | Fuse failed to eject |  |  |  | hung up fuse | EDO fuse | 0 | 0 | 0 |  | WOTS11 | hung up fuse | Hung-up fuse only | 43466.4097 |  |  | 10921 |  |  | 20190111SPN_01 | Infrastructure (network-based) | -36.2618 | 146.9662 | 1 | AusNet Services Distribution | Report | 13876 | 0.030715 | 22kV AC | Wangaratta Aero | 3691 | Staghorn Flat | Fuse
Fault crew dispatched | 1320 MAIN ROAD, ELTHAM VIC 3095 | LIS928838 |  |  |  | Defective component |  |  |  | E0007097 - pole box caught fire melted | Connection box | 0 | 0 | 0 |  | ELM15 | FOLCB on Pole LIS928838 had caught fire and subsequently melted. There was no structural damage to the pole, only slight cosmetic damage where the fire had scorched it. As a result of the fire the remains of the FOLCB had melted and fell onto the ground in scattered pieces. There was a small ground fire as a consequence approx. 20cm by 10cm in length. The cause of the fire was not load related as the overhead service was still in tact (2x25mm O/H service. It appears as though the fire had started via a loose connection and high humidity which led to a spark ignited inside the FOLCB. No damage to the customers property occurred. All damage was located in road reserve. | Pole-top fire | 27/12/2018 20:34 | 1 | Localised: less than 10 sq.m | 10924 |  |  | 20190111SPN_03 | Infrastructure (network-based) | -37.7031 | 145.164 | 1 | AusNet Services Distribution | Report | 13880 | 0.028487 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Eltham | Connection
Fault crew dispatched to investigate and make safe. Fault crew attended and advised the incident happened as a light drizzle of rain had started after the hot day. The fault crew replaced the lead, connection and the possum proofing. | 14 PETERKIN STREET, TRARALGON VIC 3844 | SW823715; LIS2604877 |  | Precipitation |  | Leakage |  |  |  | E0007157 - Report of pole fire - Fire on switch connections/leads caused feeder outage. Initiated at the connection at the switch and the fault caused the possum proofing to catch fire. The fire was out by the time the crew arrived. | Connector/termination | 0 | 0 | 0 |  | TGN12 | Animal Incident | Pole-top fire | 29/12/2018 20:16 | 1 | Negligible: no ground fire | 10928 |  |  | 20190111SPN_07 | Infrastructure (network-based) | -38.1943 | 146.5449 | 1 | AusNet Services Distribution | Report | 15117 | 0.021851 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
On arrival crew isolated supply and carried out repairs. | 6 TOWNSING COURT, ALTONA MEADOWS VIC 3028 | 33076260 | Working too close to underground cables | [6 empty] | A report was received that a worker for City west water has hit an underground cable with an excavator outside 16 Townsing Crt, Altona Meadows. Cable appeared to be unbroken but was pulled out of ground. There were no civil workers on site when the crew arrived and found the damaged cable was exposed inside the trench. There was a mesh barricade surrounding the trench. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | LV003 | Excavator digging to repair water service disturbed LV service cable | No Go Zone (contact);Damage to network assets | 23/12/2018 10:33 |  |  | 10933 | Roadway |  | 20190114PWA_02 | Infrastructure (network-based) | -37.8776 | 144.7754 | 1 | Powercor | Report | 13894 | 0.016177 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Dug up
The section was isolated and area was made safe. Zinfra faults crew organised the replacement of the pole under access permit on the same day. Failed pole and the butt was quarantined at the Tullamarine depot for post failure pole assessment and further investigation. As part of the process subsequent to a pole failure, the adjacent poles were re-inspected. Of these, two poles were assessed as Limited Life (LL) and will be subjected to the relevant inspection regime. Poles that were re-inspected are as follows: A019257, A019258, A019259, A019260, A061559, A061558 | 22 PARK STREET, FOOTSCRAY VIC 3011 | Pole no. A019256 |  |  |  | Rot | Followed but inappropriate |  | 1 | TBL# 174872 - Emergency services reported a wire down LV termination pole A019256 failed at ground level and was resting on the ground with LV conductors. The pole broke at base and fell onto the nearby property. The failed pole was a 30'/A, Class 3, Messmate species with an install date of January 1966 recorded in GIS. The pole was assessed as Serviceable at its last inspection on 11 May 2017. For photos of the incident and details of the formal investigation and analysis, refer the investigation report attached in the "Notes & Findings" section. | Conductor (covered uninsulated);Pole (wood) | 0 | 0 | 0 |  | FE09 | A formal incident investigation concluded that the pole failure was due to the extent of internal wood degradation at and below the ground line. Further, the pole condition assessment was identified to be incorrect in the most recent inspection, which had mis-identified the pole condition. A number of actions are recommended to minimise the likelihood of the root cause responsible for this pole failure from recurring. Asset inspectors are reminded of the need to: - Be vigorous when conducting external probing of a pole; white rote and white pocket rot is more easily identifiable if extensive external probing is conducted - Adjust sound wood measurements for the drilling angle - Measure the girth below ground line where the extent of external wood decay is greatest to ensure minimum circumference is recorded (girth measurement must be adjusted by subtracting the size of wood checks) - Consider appropriate drilling locations for inspection hole (do not automatically drill inspection holes between 100-150mm below ground, sounding and probing may indicate defects and therefore a more appropriate location for the inspection hole) | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/01/2019 4:35 |  |  | 10946 | Residential |  | 20190115JEM_01 | Infrastructure (network-based) | -37.7892 | 144.8888 | 1 | Jemena | Report | 16870 | 0.0028009 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Crossarm
Fault crew dispatched to investigate. Area made safe and LV connection was repaired. Refer to attached photos. | 47 MORGANS ROAD, BOISDALE VIC 3860 | LIS 2513039 |  |  |  | Overheated connection |  |  |  | E0007916 - Ground Fire reported at pole 2513039. Fault crew found a Hot connection on LV Isolators which had dropped debris on to the ground at LIS 2513039. Burning around the pole approximately 25 x 8 metres. | Disconnector/isolator | 0 | 0 | 0 |  | MFA21 | Degraded hot connection | Grassfire | 15/01/2019 15:35 | 1 | Small: 10 - 1000 sq.m | 10953 |  |  | 20190115SPN_06 | Infrastructure (network-based) | -37.857 | 146.9933 | 1 | AusNet Services Distribution | Report | 13937 | 0.027753 | Low voltage AC (<1kV) | Bairnsdale Airport | 3860 | Boisdale | Connection
During light misty sea fog conditions, a cross arm fire occurred at pole No. LIS 1303949 located outside 58 Peninsula Avenue, Rye. The pole fire occurred on a angle type one construction pole with brown fog insulators that tracked in the moist conditions due to salt borne contaminants. Emergency high voltage switching was completed to minimise the number of customers affected and the cross arm was replaced under Access Authority conditions. | 58 PENINSULA AVENUE, RYE VIC 3941 | 1303949 |  | Prone to salt deposition |  | Leakage |  |  | 2 | Emergency services advise a power pole is smoking and the CFA are on their way. | Crossarm (wood) | 0 | 0 | 0 |  | STO 14 | The pole fire occurred in the moist foggy conditions caused by salt borne contaminants due to the closeness of Port Phillip Bay. | Pole-top fire | 15/01/2019 7:31 | 1 | Negligible: no ground fire | 10939 | Roadway |  | 20190115UTD_01 | Infrastructure (network-based) | -38.3779 | 144.8064 | 1 | United Energy Distribution | Report | 14956 | 0.016057 | 22kV AC | Avalon Airport | 3941 | Rye | Crossarm
On arrival crew isolated supply and carried out repairs | 240 FORD ROAD, GRAHAMVALE VIC 3631 | 33096318 |  |  |  | Corrosion;Overheated connection |  |  |  | An IPC overheated at incident location. Hot particles caused a small fire at base of pole. There was no reported injuries or third party property damage. | Connector/termination | 2 | 2 | 2 |  | SHN024 | corroded overheated connection | Grassfire | 15/01/2019 21:45 | 1 | Small: 10 - 1000 sq.m | 11959 |  |  | 20190117PWA_01 | Infrastructure (network-based) | -36.3475 | 145.4255 | 1 | Powercor | Report | 14951 | 0.04163 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Grahamvale | Connection
On arrival crew isolated supply and carried out repairs. | 38-42 FLORA AVENUE, MILDURA VIC 3500 | 31034166 |  |  |  | Overheated connection |  |  |  | Report received of pole fire at incident location. On arrival crew found a transformer had failed, causing burning to conduits, leads and pole. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Pole mounted | 2 | 1 | 2 |  | MBN023 | Transformer overheated | Pole-top fire | 14/01/2019 18:45 | 1 | Negligible: no ground fire | 11967 | Roadway |  | 20190118PWA_02 | Infrastructure (network-based) | -34.1652 | 142.1374 | 1 | Powercor | Report | 14961 | 0.029319 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3500 | Mildura | AF Other
On arrival crew inspected assets no damage found. | 4810 BOORT-KERANG ROAD, KERANG VIC 3579 | 33019798 |  | Fire |  |  |  |  | 1 | Vicfire reported a grass fire and a loud bang at the incident location. On arrival the crew found a grass fire of approx. 0.5 Ha, with mostly road reserve, a small section of private land burnt, and minor damage to fences. The crew could find no evidence of a cause for the fire. There was a successful reclose on the feeder controlling this area. There were no injuries or other damage reported. | Conductor (bare) | 2 | 2 | 2 |  | KGT004 | No cause found - Assume external fire | Grassfire | 22/01/2019 13:37 | 0 | Medium: 1000 sq.m - 10 ha | 11985 | Roadway |  | 20190122PWA_04 | Infrastructure (network-based) | -35.7354 | 143.8915 | 1 | Powercor | Report | 14996 | 0.028207 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | Other
On arrival crew isolated supply and carried out repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30291861 | Vandalism;Copper theft | [6 empty] | A passer-by reported opened electrical pits and exposed wires at the incident location. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | vandalism and copper theft | Damage to network assets | 43647.4965 |  |  | 11987 | Roadway |  | 20190123PWA_02 | Infrastructure (network-based) | -37.6892 | 144.549 | 1 | Powercor | Report | 14998 | 0.041412 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew carried out repairs | GREEN HILL ROAD, EYNESBURY VIC 3338 | 30105815 | Vandalism;Copper theft | [6 empty] | Contractor for PAL found earthing and underground lighting cable stolen at incident location. There was no fire, no reported injuries and no third party property damage. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN011 | Vandalism and copper theft | Damage to network assets | 43739.4889 |  |  | 11994 | Roadway |  | 20190124PWA_01 | Infrastructure (network-based) | -37.7451 | 144.5512 | 1 | Powercor | Report | 15005 | 0.027062 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3338 | Eynesbury | Other
Service replaced | UNIT 3 104 ST GEORGES ROAD, NORTHCOTE VIC 3070 | 30198663 |  |  |  | Corrosion |  |  | 2 | Customer received an electric shock when she simultaneously contacted the metallic tap with one hand and the metallic shower base trap with her foot. | Service conductor | 0 | 0 | 0 |  | NC010 | Corroded service neutral at POA | Minor shock | 18/01/2019 15:30 |  |  | 12003 | Residential |  | 20190124PWA_07 | Infrastructure (customer connection) | -37.7734 | 144.9907 | 1 | CitiPower | Report | 15014 | 0.0065035 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
truck attended and replaced service cable | UNIT 4 339 BLACKSHAWS ROAD, ALTONA NORTH VIC 3025 | 30114464 |  |  |  | Electrical breakdown |  |  |  | person reports receiving tingles and an electric shock when she touched her shower and bath taps | Service conductor;Neutral screen | 0 | 0 | 0 |  | BLT021 | A high impedance neutral connection in the service cable | Minor shock | 18/01/2019 16:00 |  |  | 12004 | Residential |  | 20190124PWA_08 | Infrastructure (customer connection) | -37.8316 | 144.8515 | 1 | Powercor | Report | 15015 | 0.023166 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | OH Cable
On arrival crew isolated supply and Carried out repairs | 4 HUME AVENUE, MELTON SOUTH VIC 3338 | 30111841 |  |  |  | Corrosion |  |  |  | Resident reported that pole outside his house had exploded, showering sparks on to the nature strip below resulting in a small grass fire (approx. 1.5m2 in total). Upon arrival the fault crew found that the Aluminium conductor bridging in one of the LV transformer bus isolators at pole LIS-108994 had melted and burnt through. There was no reported injuries or third party injuries. | Conductor (bare);Disconnector/isolator | 2 | 2 | 2 |  | MLN011 | Overheated connection | Grassfire | 24/01/2019 20:24 | 1 | Localised: less than 10 sq.m | 12011 | Roadway |  | 20190125PWA_02 | Infrastructure (network-based) | -37.7129 | 144.5636 | 1 | Powercor | Report | 15023 | 0.035435 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Connection
A faults crew attended, repaired the ampact connection and restored supply to customers supplied from "Nepean-Milroy" substation. | MILROY STREET, BRIGHTON EAST VIC 3187 |  |  | Heat |  | Overheated connection |  |  | 2 | REC David called the United Energy faults and emergencies call centre and advised that he heard a crack from the brick substation on the corner of Milroy Street and a small fire started outside the brick fence on the Nepean Highway side. An Ampact connection on the LV blue phase at the CHP failed and molten metal fell into the dry naturestrip grass below outside NB zone substation causing a small grass fire that was quickly extinguished. | Conductor (bare);Cable | 0 | 0 | 0 |  |  | The fault occurred during very warm conditions and it's highly probable that a loose connection overheated and failed. | Grassfire | 24/01/2019 13:22 | 1 | Localised: less than 10 sq.m | 12009 | Roadway |  | 20190125UTD_02 | Infrastructure (network-based) | -37.9064 | 145.0089 | 1 | United Energy Distribution | Report | 15021 | 0.021954 | Low voltage AC (<1kV) | Moorabbin Airport | 3187 | Brighton East | Connection
inspector call to site to investigate an electric shock. Inspector performed the required tests and identified on "open circuit" on the neutral service conductor. Jemena crew reconnected the over head neutral to the street main neutral conductor. | 11 SIMMINGTON CIRCUIT, GREENVALE VIC 3059 |  |  |  |  | Neutral fault |  |  | 2 | Customer received an electric shock from the garden tap at the rear of the house. | Service conductor | 0 | 0 | 0 |  | COO11 | Broken neutral at pole end. | Minor shock | 28/01/2019 22:11 |  |  | 12024 | Residential |  | 20190128JEM_01 | Infrastructure (network-based) | -37.6418 | 144.8893 | 1 | Jemena | Report | 15154 | 0.010963 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Connection
On arrival crew isolated supply and carried out repairs | 81 HAIRES LANE, BULLENGAROOK VIC 3437 | 32043180 |  | Blown branch/vegetation |  |  |  |  | 1 | Vic Fire reported trees down over wires and caused grass fire at incident location. On arrival crew found tree through single phase 22kv conductors and small grass fire between P3 & P4 . CFA extinguished 5m x 35m grass fire. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GSB011 | Vegetation: Trees Incident | Grassfire | 26/01/2019 2:06 | 1 | Small: 10 - 1000 sq.m | 12026 | Agricultural |  | 20190129PWA_01 | Infrastructure (network-based) | -37.4963 | 144.5169 | 1 | Powercor | Report | 15047 | 0.0082998 | 22kV AC | Melbourne Airport | 3437 | Bullengarook | Trees
On arrival crew isolated supply and carried out repairs | 920 LILFORD ROAD, GILLIESTON VIC 3616 | 30127687 |  |  |  | Leakage |  |  | 1 | Following a 66kv line trip to lockout a PAL crew found a crossarm fire at the incident location. Crew found at SHTS KYM No 1 66kV Line P164, the road side insulator burnt off the x-arm, dropped down and clashed with another phase, small grass fire approximately 300mm x 300mm. There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHTS-KYM1 | Excessive leakage current | Pole-top fire;Grassfire | 27/01/2019 9:22 | 1 | Localised: less than 10 sq.m | 12029 | Roadway |  | 20190129PWA_03 | Infrastructure (network-based) | -36.3431 | 145.2089 | 1 | Powercor | Report | 17367 | 0.013874 | 66kV AC | Shepparton Airport | 3616 | Gillieston | Crossarm
On arrival crew isolated supply and carried out repairs. | 32 KOOKABURRA STREET, ALTONA VIC 3018 | 32167630 |  |  |  | Corrosion |  |  |  | Report received from Vic fire of wire down, arching and sparking. Upon arrival the fault crew found the copper tail on the white phase bus fused LV isolator had burnt through due to corrosion. Some sparks were splashed on to the dry grass below, with a very small area of grass scorched. There was no reported injuries or third party property damage. | Conductor (bare);Disconnector/isolator | 2 | 2 | 2 |  | AL006 | corroded connection | Grassfire | 25/01/2019 16:33 | 1 | Localised: less than 10 sq.m | 12031 | Roadway |  | 20190129PWA_04 | Infrastructure (network-based) | -37.8706 | 144.8056 | 1 | Powercor | Report | 15054 | 0.040375 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Connection
Crew repaired a a severely corroded network neutral connection on FOLCB. | 36 DAWSON STREET, RESERVOIR VIC 3073 |  |  |  |  | Age;Corrosion |  |  | 2 | Customer received an electric shock by making simultaneous contact with the metallic tap and the grass at the rear of the property. | Aluminium twisted (grey) | 2 | 2 | 2 |  |  | Severely corroded network neutral connection on FOLCB | Minor shock | 30/01/2019 13:27 |  |  | 12047 | Residential |  | 20190130JEM_01 | Infrastructure (customer connection) | -37.6989 | 144.9855 | 1 | Jemena | Report | 15076 | 0.030205 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Connection
On arrival crew isolated supply and carried out repairs. | 585 MURRAY VALLEY HIGHWAY, TYNTYNDER SOUTH VIC 3586 | 30100125 | Crane, excavator or other construction/farming equipment | [6 empty] | Landowner reported 3 wires suspended off ground but low enough to touch after tractor had hit a pole located in middle of paddock. When crew arrived they identified that 2 of 3 phases of HV conductor had been broken at the tee off pole at sleeves and from the droppers. Crew spoke to landowner who said a contractor had been in the tractor and a dust storm had reduced visibility when he hit the pole. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SHL004 | Tractor struck pole | Loss of supply;Damage to network assets | 18/01/2019 17:03 |  |  | 12046 | Agricultural |  | 20190130PWA_05 | Infrastructure (network-based) | -35.2898 | 143.5301 | 1 | Powercor | Report | 15074 | 0.038809 | 22kV AC | Swan Hill Aerodrome | 3586 | Tyntynder South | Vehicle
Fault crew dispatched and Candled HV EDO Fuse replaced | KALIMNA HOTEL, 21 KALIMNA JETTY ROAD, KALIMNA VIC 3909 | LIS1901592 |  |  |  | Candled fuse |  |  |  | E0008761 - Candled HV Fuse | EDO fuse | 0 | 0 | 0 |  | BDL6 | Candled EDO fuse, no evidence of ground fire. Fuse replaced. | Pole-top fire | 28/01/2019 9:57 | 1 | Negligible: no ground fire | 12041 |  |  | 20190130SPN_04 | Infrastructure (network-based) | -37.8779 | 147.9582 | 1 | AusNet Services Distribution | Report | 15068 | 0.00070833 | 22kV AC | Bairnsdale Airport | 3909 | Kalimna | Fuse
A faults crew promptly attended and found the surge diverters were slightly blackened on the south side of the ACR switch but remained intact and in service. | FRANKSTON-DANDENONG ROAD, CARRUM DOWNS VIC 3201 | 3318989 |  | Bird |  |  |  |  | 1 | At 2.48PM on 28/01/2019, 22kV feeder DVY24 successfully reclosed and held. A caller to the United Energy faults and emergencies call centre advised that a transformer is on fire in Carrum Downs. Emergency Services rang afterwards reporting there isn't a pole fire but a grass fire has started at the base of the pole. A bird made contact with the red and blue phase surge diverters at pole number LIS 3318989 (ACR FS0047) located in Frankston-Dandenong Road. The bird was on fire and fell into the dry grass below and a 50sqm grass fire started that was extinguished by the CFA. | Surge diverter | 0 | 0 | 0 |  | DVY24 | Bird Incident | Grassfire | 28/01/2019 14:48 | 1 | Small: 10 - 1000 sq.m | 12044 | Roadway |  | 20190130UTD_02 | Infrastructure (network-based) | -38.0823 | 145.1862 | 1 | United Energy Distribution | Report | 15072 | 0.029597 | 22kV AC | Moorabbin Airport | 3201 | Carrum Downs | Animal
Electrical inspector performed voltage tests between an independent earth and various parts of the electrical installation, including the tap and the distribution assets recorded 4.2 volts, identified loose split bolt clamp at the reticulation pole. The attended Jemena fault crew tighten the loose split bolt clamp at reticulation pole. | 49 BRENTWOOD AVENUE, PASCOE VALE SOUTH VIC 3044 |  |  |  |  | Earth fault |  |  | 2 | Customer reported that received an electric shock while she turned off the water tap next to the swimming pool whilst she made simultaneous contact between the tap while standing bare footed on the ground. | Conductor (bare) | 2 | 2 | 2 |  |  | Loose neutral split bolt clamp at reticulation pole resulting in return current path finding the best connection i.e. the earthed taps | Minor shock | 30/01/2019 15:11 |  |  | 12053 | Residential |  | 20190131JEM_03 | Infrastructure (network-based) | -37.7475 | 144.9297 | 1 | Jemena | Report | 15371 | 0.025877 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale South | AF Other
On arrival crew temp stayed pole and carried out repairs. | 221 FALA PARK ROAD, WARRNAMBOOL VIC 3280 | 30134915 |  |  |  | Corrosion;Fatigue |  |  | 1 | A Powercor crew were called to an outage at the incident location at around 1am in the morning. On arrival the crew found three HV fuses blown on the tee-off pole, upon investigation they found a stay rod had failed below the ground at P13 Westfala Spur allowing the pole to lean forward significantly, resulting in the 22kV conductors being low to the ground. The farmer called Powercor to inform us that he had found several deceased cattle in the paddock where the conductors had been low the night before. Six young cattle were found deceased in and around a hay feeder ring in the middle of the span, with evidence of the HV conductors contacting the hay feeder ring. There was no reported fire or other third party damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | WBL005 | Stay rod failure | Fatality of livestock, pet or companion animal | 29/01/2019 0:18 |  |  | 12057 | Roadway |  | 20190131PWA_04 | Infrastructure (network-based) | -38.3354 | 142.4978 | 1 | Powercor | Report | 15360 | 0.0084514 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
Fault crew removed the candling BA Fuses and replaced | 280 MCDONALDS TRACK, LANG LANG VIC 3984 | LIS 2703396 |  |  |  | Candled fuse |  |  |  | E0009016 - Fault crew attending a fault nearby found BA Fuses had begun to candle. | Boric acid | 0 | 0 | 0 |  | LLG12 | Candling HV fuse. Fuse replaced and supply restored. No evidence of ground fire | Pole-top fire | 31/01/2019 5:31 | 1 | Negligible: no ground fire | 12055 | Agricultural |  | 20190131SPN_03 | Infrastructure (network-based) | -38.275 | 145.5729 | 1 | AusNet Services Distribution | Report | 17882 | 0.033238 | 22kV AC | Moorabbin Airport | 3984 | Lang Lang | Fuse
Attending JEN fault crew identified a severely corroded active and neutral connector at pole junction box. Crews repaired and re-terminated as required. The attending JEN crew also checked customer FOLCB, which identified a slightly loose connection at the customer side main neutral. Crews rectified as required. Connections checked at Main Neutral Link on meter panel, installation switchboard, MEN and main earth. All subsequent connections checked in switchboard. Following rectification and repairs, the attending LEI performed all subsequent voltage tests on the earthing system including at the point of contact, <3 V (ac) was measured under normal and loaded conditions. A final NST was performed which returned a PASS result. Customer Stephen was advised to contact an REC to earth bond all metallic parts of the installation including metallic roofing material to eliminate induced voltages. | 15 DALGARNO STREET, WILLIAMSTOWN VIC 3016 |  |  |  |  | Corrosion |  |  |  | Mr. Stephen Eastwood received a minor electric tingle when he made simultaneously contacted the metallic down-pipe whilst standing bare foot on the wet timber decking. Testing of the electrical installation with a voltage tester and independent earth to various parts of the point of contact, neutral bar and various parts of the earthing system which recorded a voltage of 5 -12V (ac) under loaded conditions. The attending LEI performed an NST test at the main switchboard which recorded a FAIL result. JEN Fault crew was dispatched as requested by the attending LEI. | Service conductor | 0 | 0 | 0 |  |  | REPAIRED CORRODED CONNECTION ON SERVICE TO NUETRAL AT POLE. | Minor shock | 43293.8021 |  |  | 10768 | Residential |  | 20181208JEM_01 | Infrastructure (network-based) | -37.8525 | 144.8962 | 1 | Jemena | Report | 13896 | 0.007125 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Connection
Supply isolated and leads replaced | 37 PRESIDENTS AVENUE, OCEAN GROVE VIC 3226 | 33042035 |  |  |  | Overheated connection |  |  | 1 | VICFIRE reported transformer on fire at this address. Attending crew found that HV insulated leads had overheated. No ground fire. | Dropper/bridge | 0 | 0 | 0 |  | DDL011 | Overheated connection | Pole-top fire;Loss of supply | 43263.6694 | 1 | Negligible: no ground fire | 10774 | Roadway |  | 20181210PWA_02 | Infrastructure (network-based) | -38.2605 | 144.5245 | 1 | Powercor | Report | 13668 | 0.030045 | 22kV AC | Avalon Airport | 3226 | Ocean Grove | Connection
roofing iron removed under outage | 352 COWRA AVENUE, NICHOLS POINT VIC 3501 | 33067395 | Blown detritus | Wind |  |  |  |  | 1 | winds blew roofing iron off house and into overhead HV lines | Conductor (bare) | 0 | 0 | 0 |  | MDA024, MDA - BNG | Airborne debris | Loss of supply | 43263.5951 |  |  | 10777 | Roadway |  | 20181210PWA_04 | Infrastructure (network-based) | -34.2025 | 142.1813 | 1 | Powercor | Report | 13857 | 0.036715 | 22kV AC;66kV AC | Mildura Airport | 3501 | Nichols Point | Other
Fault crew dispatched. EDO fuse replaced and Noti raised to install BA Units | 180 MAIN NEERIM ROAD, DROUIN VIC 3818 | LIS2717457 |  |  |  | Candled fuse |  |  |  | E0006073 - report of candling HV fuse. No fire was evident. | EDO fuse | 0 | 0 | 0 |  | WGL21 | Candling HV fuse on pole s/stn. | Pole-top fire | 43355.5111 | 1 | Negligible: no ground fire | 10773 |  |  | 20181210SPN_02 | Infrastructure (network-based) | -38.1074 | 145.8504 | 2 | AusNet Services Distribution | Report | 13667 | 0.032308 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Drouin | Fuse
open wire service replaced | 77 SHAMROCK STREET, BRUNSWICK WEST VIC 3055 | 30156393 |  |  |  | Neutral fault;Mechanical breakdown |  |  |  | Plumber attended site to carry out repair on the solar hot water heat pump and also repair a leaking water pipe. He received a mild shock from a water pipe in the vicinity of the solar hot water heat pump when he made simultaneous contact with his hand on the pipe and his knees on the damp ground. | Service conductor | 0 | 0 | 0 |  | WB002 | Broken neutral dropper cable from service | Minor shock | 43324.4375 |  |  | 10785 | Residential |  | 20181211PWA_06 | Infrastructure (customer connection) | -37.7555 | 144.9517 | 1 | CitiPower | Report | 13683 | 0.01688 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | OH Cable
On arrival crew isolated supply and carried out repairs | 699 NEALE ROAD, DEANSIDE VIC 3336 | 31023328 | Vandalism;Copper theft | [6 empty] | A customer reported a cable pulled out from the pole and also the meter board at the incident location. The attended crew found that the service had been vandalised and cut off from both pole end and the meter board. There also appears to be potential sign of fire at the pole end adjacent to FOLCB. There was no injuries reported. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Vandalism & copper theft | Pole-top fire;Loss of supply;Damage to network assets | 26/11/2018 12:55 | 1 | Negligible: no ground fire | 10791 | Roadway |  | 20181212PWA_02 | Infrastructure (network-based) | -37.7409 | 144.701 | 1 | Powercor | Report | 13691 | 0.026593 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Other
LEI attended and inspected premises for damage. Damaged pole was replaced by fault crews. | 45 MAIN STREET, BLACKBURN VIC 3130 | 7028097 |  | Lightning |  |  |  |  | 1 | At approximately 12.00 hours, lightning struck pole in front of 45 Main St Blackburn, causing HVI affecting two properties (45 and 47). The pole was also damaged (split). | Service conductor;Pole (wood) | 1 | 0 | 0 |  | BH11 | Lightning hit pole | HV injection | 43143.5035 |  |  | 10800 | Residential |  | 20181213UTD_02 | Infrastructure (network-based) | -37.8242 | 145.1496 | 1 | United Energy Distribution | Report | 13705 | 0.02958 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Lightning
The Powercor crew isolated supply to the area and arranged repairs. | GIBSON STREET, RUPANYUP VIC 3388 | 32096251 |  |  |  | Leakage |  |  | 1 | At approx. 19:10hrs on 13/12/18 the Glenorchy ACR P125 tripped to Lockout. The Powercor patrolled the line and found that a X-arm fire had occurred on Gibson Street Pole 2. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | STL006 | Excessive leakage current | Pole-top fire | 13/12/2018 19:16 | 1 | Negligible: no ground fire | 10803 | Roadway |  | 20181214PWA_01 | Infrastructure (network-based) | -36.6284 | 142.6319 | 1 | Powercor | Report | 13712 | 0.030159 | 22kV AC | Horsham Aerodrome | 3388 | Rupanyup | Crossarm
Remade active and took pics of active connection. | 49 HILLMARTIN LANE, DIAMOND CREEK VIC 3089 | LIS 926857 |  | Heat |  | Electrical breakdown |  |  | 2 | E0006263 - Ground Fire - Reported grass fire at base of pole near 40 Hillmartin Lane, Diamond Creek Fault crew attended and report "Grass fire. Fire occurred on customers front paddock. Grass fire only, no damage to the customers property. | Service conductor | 0 | 0 | 0 |  | ELM12 | Cause of fire was poor connection of tape on the active. Due to the dry nature of the area this resulted in a fire starting. | Grassfire | 43446.6965 | 1 | Small: 10 - 1000 sq.m | 10808 |  |  | 20181214SPN_04 | Infrastructure (network-based) | -37.6684 | 145.1365 | 1 | AusNet Services Distribution | Report | 13721 | 0.0091447 | Low voltage AC (<1kV) | Essendon Airport | 3089 | Diamond Creek | Conductor
On arrival crew isolated supply and carried out repairs | 21 OLD CARTONS LANE, GORDON VIC 3345 | 30141466 |  |  |  | Rot |  |  | 1 | A customer reported a conductor on the ground at the incident location. Upon arrival, the crew found that the HV steel conductor was hanging in the mid air due to broken cross arm. There was no fire, no reported injuries or third party property damage | Crossarm (wood) | 2 | 2 | 2 |  | BAN011 | Internal Deterioration | Loss of supply;Damage to network assets | 14/12/2018 14:20 |  |  | 10811 | Agricultural |  | 20181217PWA_01 | Infrastructure (network-based) | -37.5775 | 144.1226 | 1 | Powercor | Report | 13728 | 0.022544 | 22kV AC | Ballarat Aerodrome | 3345 | Gordon | Crossarm
On arrival crew isolated supply and carried out repairs. | 53 MERVYN STREET, NEWTOWN VIC 3220 | 33040999 |  | Bird | [5 empty] | A report was received a bird contact at the incident location. On arrival crew found that a bird had flashed over across a powder filled a fuse unit (footpath side). Two fuse units operated. Passing pedestrians were showered with particles from the flashover. There was no fire, no reported third party property damage. | Powder filled | 2 | 2 | 2 |  | GL022 | Bird Incident | Damage to network assets | 14/12/2018 16:25 |  |  | 10814 | Roadway |  | 20181217PWA_03 | Infrastructure (network-based) | -38.1566 | 144.3042 | 1 | Powercor | Report | 13733 | 0.017172 | 22kV AC | Avalon Airport | 3220 | Newtown | Animal
Fault crew dispatched to make safe and investigate. Pole and stay replaced with new and supply restored | 287 MILL ROAD, WOOLAMAI VIC 3995 | LIS2800409 |  |  |  | Defective component;Mechanical overload |  | Phase to earth |  | E0006525 - Pole and stay failure | Conductor (bare);Guy wire;Pole (wood) | 0 | 0 | 0 |  | WGI34 | Fault crew attended and identified that a pole had snapped off approx. 4 m above ground and cables laying across the paddock and low across the road. The Stay Rod Eyelet and termination were buried ans the stay failed at the helical preform termination on the ground stay rod, just above the eyelet. This resulted in a shock load on the pole causing it to break 2.9 metres above ground level and fall towards the long span and pole 2800410 into the paddock. Pole was last inspected in 24/05/2014 and staked. As the pole was staked it was drilled 600mm below the top of the stake or 1 metre AGL and found to be serviceable with 70mm of sound wood | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/12/2018 8:27 |  |  | 10812 |  |  | 20181217SPN_01 | Infrastructure (network-based) | -38.5196 | 145.5418 | 1 | AusNet Services Distribution | Report | 15291 | 7.2917e-05 | 22kV AC | Moorabbin Airport | 3995 | Woolamai | Pole
On arrival crew isolated supply and carried out repairs | 1663-1755 GISBORNE-MELTON ROAD, TOOLERN VALE VIC 3337 | 30542849 | Vandalism;Copper theft | [6 empty] | PAL received a report of Attempted theft of Underground service cable. On arrival crew found disconnected underground service cable lying on the ground, the FOLCB disconnected and removed from the pole. There was no fire, no reported injuries or third party property damage | Services cable | 2 | 2 | 2 |  | MLN012 | attempted copper theft and vandalism | Damage to network assets | 29/11/2018 12:22 |  |  | 10818 | Roadway |  | 20181218PWA_02 | Infrastructure (network-based) | -37.6455 | 144.6022 | 1 | Powercor | Report | 13739 | 0.035491 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
Fault crew sent to investigate and make safe. On arrival they found a Boric Acid tube burnt in half. The bottom section of the fuse was still in the holder and the top section laying at the base of the pole (refer to the attached photos of the failed unit). The damaged section of fuse tube was removed from the fuse unit. A new fuse was installed and supply restored. | 16 FLYNNS LANE, OSBORNES FLAT VIC 3691 | LIS 5626316 |  |  |  | Candled fuse |  |  |  | E0006713 - Report of fuse candling - Crew found a Boric Acid fuse tube burnt in half. Droplets of metal found at base of pole but no fire on the ground. It appears the striker pin did not operate to let the Boric Acid fuse fall out. | Boric acid | 0 | 0 | 0 |  | WOTS11 | Degraded internal connection. It appears the striker pin did not operate to let the Boric Acid fuse fall out. | Pole-top fire | 18/12/2018 1:21 | 1 | Negligible: no ground fire | 10821 |  |  | 20181218SPN_02 | Infrastructure (network-based) | -36.3207 | 146.8989 | 2 | AusNet Services Distribution | Report | 17908 | 0.0094757 | 12.7kV AC (SWER) | Wangaratta Aero | 3691 | Osbornes Flat | Fuse
Fault crew dispatched to investigate and make safe. Crew replaced candled EDO fuse on site. | 33 ABECKETT ROAD, BUNYIP VIC 3815 | LIS 522029 |  |  |  | Candled fuse |  |  |  | report of candling fuse | EDO fuse | 0 | 0 | 0 |  | WGL12 | Candled HV Fuse. Unable to establish root cause. No evidence of ground fire. | Pole-top fire | 14/12/2018 9:33 | 1 | Negligible: no ground fire | 10828 | Residential |  | 20181219SPN_01 | Infrastructure (network-based) | -38.0945 | 145.7267 | 2 | AusNet Services Distribution | Report | 18281 | 0.015029 | 22kV AC | Moorabbin Airport | 3815 | Bunyip | Fuse
On arrival crew isolated supply and carried out repairs | 3587 MCEWEN ROAD, WARANGA SHORES VIC 3612 | 30127581 |  |  |  | Rot |  |  |  | Vic-fire reports conductor down and grass fire at incident location. Crew attended to find that a low voltage termination cross-arm had broken There was a small ground fire, no reported injuries | Crossarm (wood) | 2 | 2 | 2 |  | SHP014 | deteriorated cross-arm | Grassfire | 20/12/2018 14:50 | 1 | Small: 10 - 1000 sq.m | 10834 | Public space |  | 20181221PWA_01 | Infrastructure (network-based) | -36.5193 | 145.0324 | 1 | Powercor | Report | 15359 | 0.017083 | Low voltage AC (<1kV) | Shepparton Airport | 3587 | Waranga Shores | Crossarm
Crew replaced broken neutral service and corroded connections at FOLCB. Site was made safe. | 1 RICHARDSON AVENUE, SUNBURY VIC 3429 | 10164878 |  |  |  | Age;Corrosion |  |  | 2 | Customer received electric shock from tap at back of his house. | Service conductor | 0 | 0 | 0 |  | SBY24 | Broken neutral service and corroded connection at FOLCB. | Minor shock | 24/12/2018 14:40 |  |  | 10844 | Residential |  | 20181225JEM_01 | Infrastructure (customer connection) | -37.572 | 144.705 | 1 | Jemena | Report | 13777 | 0.011494 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Connection
The white phase 315amp DIN fuse was replaced at "Hammond-Hampton" substation that operated as a result of the pole mounted three phase junction box failing. The three phase neutral screen service and damaged pole mounted junction box were replaced with supply restored to all affected customers. | 18 HAMMOND STREET, BRIGHTON VIC 3186 |  |  |  |  | Corrosion;Electrical breakdown |  |  | 1 | Caller saw a flash from the pole and the neighbours overhead service line is now resting in a tree. A grass fire was extinguished and customers supplied from "Hammond-Hampton" substation advised of a loss of their electricity supply. A pole mounted three phase junction box with copper neutral screen at a service pole failed that caused molten metal to fall onto the grass below and a small grass fire occurred that was promptly extinguished. | Service conductor;Neutral screen;Connection box | 0 | 0 | 0 |  |  | The cause was probable corrosion that caused the neutral screen service to fail inside the junction box. | Grassfire | 17/12/2018 7:01 | 1 | Localised: less than 10 sq.m | 10846 | Roadway |  | 20181227UTD_02 | Infrastructure (network-based) | -37.9164 | 145.0049 | 1 | United Energy Distribution | Report | 13779 | 0.0046146 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | OH Cable
The site was made safe and replaced with neutral screen single phaseXLPE 4core 25mm service | 512-520 GEELONG ROAD, TOTTENHAM VIC 3012 |  | Vehicle | [5 empty] | 1 | It is assumed a Truck/ crane has hit mains cable bringing down service. No details of the vehicle can be confirmed | Service conductor | 0 | 0 | 0 |  |  | The cause could not be conclusively determined at the time of repairs. Though it is assumed that a vehicle may have made contact to result in failure | Loss of supply | 28/12/2018 18:28 |  |  | 10851 | Roadway |  | 20181228JEM_02 | Infrastructure (network-based) | -37.8143 | 144.8569 | 1 | Jemena | Report | 13784 | 0.012918 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Tottenham | Vehicle
The crew made safe and appropriate repairs undertaken. | 22 GREAT OCEAN ROAD, APOLLO BAY VIC 3233 | 32062525 |  |  |  | Overheated connection |  |  | 2 | Vic Fire reports a pole fire at the incident location, On arrival, the crew finds bare LV conductor has broken off and is laying on the ground, across the highway. Burns to the grass at the base of the pole were reported. | Conductor (bare) | 0 | 0 | 0 |  | CLC006 | LV conductor reportedly broken off at connection | Loss of supply;Grassfire | 30/12/2018 21:52 | 1 | Localised: less than 10 sq.m | 10856 | Roadway |  | 20190102PWA_03 | Infrastructure (network-based) | -38.7607 | 143.6718 | 1 | Powercor | Report | 13791 | 0.040809 | Low voltage AC (<1kV) | Avalon Airport | 3233 | Apollo Bay | Connection
Reported to ESV and site visit requested Negotiations for relocation of line have been in progress. | 63 MANNINGHAM STREET, PARKVILLE VIC 3052 | 30181314 | Working too close to overhead lines | [5 empty] | 2 | A permit to work was issued for mobile plant and scaffolding at this site. A site visit identified that stated conditions of the PTW were not being complied with. There was also some doubt that the final clearance of the building would meet statutory clearances. | Conductor (bare) | 0 | 0 | 0 |  | WMTS-WB | Interference - construction works in vicinity of overhead line | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/12/2018 10:55 |  |  | 10858 | Construction |  | 20190102PWA_05 | Infrastructure (network-based) | -37.7866 | 144.9419 | 2 | CitiPower | Report | 13795 | 0.022787 | 66kV AC | Essendon Airport | 3052 | Parkville | Other
On arrival crew isolated supply and carried out repairs | 570 JOHNSON ROAD, STANHOPE VIC 3623 | 30256538 |  |  |  | Leakage;Candled fuse |  |  | 0 | Customer reported a possible fire on pole at incident location. On arrival the crew found a boric acid fuse had burnt out and failed to operate correctly. There was no ground fire, no reported injuries or third party property damage. | Boric acid | 2 | 2 | 2 |  | SHP021 | Boric acid fuse hung up | Pole-top fire | 43355.5215 | 1 | Negligible: no ground fire | 10864 | Roadway |  | 20190103PWA_06 | Infrastructure (network-based) | -36.471 | 144.9959 | 1 | Powercor | Report | 13803 | 0.03148 | 22kV AC | Shepparton Airport | 3623 | Stanhope | Fuse
Attending crew re-terminated twisted wire service | 93 MUST STREET, PORTLAND VIC 3305 | 32138116 |  |  |  | Corrosion |  |  | 2 | customer was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic shower tap and her bare feet while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | PLD006 | Corroded Overhead Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole | Minor shock | 16/12/2018 11:00 |  |  | 10874 | Residential |  | 20190104PWA_08 | Infrastructure (customer connection) | -38.3597 | 141.6032 | 1 | Powercor | Report | 13814 | 0.012266 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | OH Cable
On arrival crew isolated supply and carried out repairs | 54 THISTLE STREET, BENDIGO VIC 3550 | 30239616 |  |  |  | Overheated connection |  |  |  | Vicfire reported transformer fire at incident location. On arrival Crew found that the low voltage fuse unit had failed. There was no ground fire, no property damage and no injuries | Connection box | 2 | 2 | 2 |  | BET008 | Overheated connection in FSD | Pole-top fire | 21/12/2018 13:30 | 1 | Negligible: no ground fire | 10882 | Roadway |  | 20190107PWA_02 | Infrastructure (network-based) | -36.7666 | 144.2663 | 1 | Powercor | Report | 13822 | 0.018683 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | Connection
On arrival crew isolated supply and carried out repairs. | 227 CLARKS ROAD, GLEN PARK VIC 3352 | 30015277 |  |  |  | Unknown technical factor |  |  |  | Vic Fire reported at pole fire at the incident address. on arrival crew found that a FOLCB had burnt at the substation pole. There was no ground fire, no injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAN008 | FOLCB fire - Insufficient remains to determine a cause. | Pole-top fire | 43617.4833 | 1 | Negligible: no ground fire | 10891 | Roadway |  | 20190107PWA_09 | Infrastructure (network-based) | -37.504 | 143.9344 | 1 | Powercor | Report | 13837 | 0.024376 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Glen Park | Connection
On arrival crew isolated supply and arranged for pole replacement. | LAH EAST ROAD, LAH VIC 3393 | 32113994 |  | Lightning | [5 empty] | A customer reported that a pole had been hit by lightning and was on fire. On arrival crew found pole partially destroyed, had been hit by lightning . Pole had caught fire but fire was extinguished by rain. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | HSM003 | Pole destroyed by lightning, resulting in pole fire | Pole-top fire;Loss of supply | 30/12/2018 9:30 | 1 | Negligible: no ground fire | 10896 | Agricultural |  | 20190107PWA_12 | Infrastructure (network-based) | -36.1277 | 142.4582 | 1 | Powercor | Report | 13839 | 0.0044965 | 12.7kV AC (SWER) | Horsham Aerodrome | 3393 | Lah | Lightning
LEI attended, confirmed HVI and isolated affected properties in Herald St and Kayden St. | 93 HERALD STREET, CHELTENHAM VIC 3192 |  |  |  |  | Defective component;Insulator |  |  | 1 | HVI occurred when crew were attempting to close HV fuses when centre phase fuse unit broke and caused the HV conductor to detach and make contact with the sub pole and burn out the earthing and also make contact on the LV red phase. | Conductor (bare);Pole mounted | 0 | 0 | 0 |  |  | HV fuse unit broke when being operated | HV injection | 21/12/2018 17:30 |  |  | 10886 | Roadway |  | 20190107UTD_02 | Infrastructure (network-based) | -37.9567 | 145.0729 | 1 | United Energy Distribution | Report | 13828 | 0.032425 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3192 | Cheltenham | Fuse
On arrival crew inspected asset for damage and restored supply | 368 PARTRIDGES ROAD, HAMILTON VIC 3300 | 32128531 |  | Bird | [5 empty] | A customer reported a bird made contact with line at the incident location causing a small grass fire. Upon arrival, crew found that a bird flashover on SWER substation pole resulting in a small fire surrounding the pole base. The grass fire caused a minor damage to the property fence. There was no damage to the pole base. There was no reported injuries. | Pole mounted | 2 | 2 | 2 |  | HTN006 | Bird Incident | Loss of supply;Grassfire | 43647.6403 | 1 | Small: 10 - 1000 sq.m | 10899 |  |  | 20190108PWA_01 | Infrastructure (network-based) | -37.6729 | 141.9616 | 1 | Powercor | Report | 13842 | 0.034909 | 12.7kV AC (SWER) | Hamilton Airport | 3300 | Hamilton | Animal
On arrival crew isolated supply and carried repairs. | 38 CARTER STREET, KATUNGA VIC 3640 | 33081610 |  | Wind;Fallen |  |  |  |  | 1 | Customers reported low conductors, sparking and partial loss of supply at the incident address. Upon arrival fault crew found that localised thunderstorm activity and strong winds brought down a tree from outside the clearance space, falling over LV conductors. Initial customer reports all indicated that LV conductors which were sparking were only 2.0M above ground level. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | NKA006 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 30/12/2018 18:50 |  |  | 10901 |  |  | 20190108PWA_03 | Infrastructure (network-based) | -35.9996 | 145.454 | 1 | Powercor | Report | 13845 | 0.020579 | Low voltage AC (<1kV) | Shepparton Airport | 3640 | Katunga | Trees
Fault crew attended site same day to assess damage and determined that no customers are connected from the substation pole. The fault crew isolated supply and made safe pending a decision whether to repair or retire structure. | 493-519 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 30111941 | Vandalism;Copper theft | [6 empty] | Chris from Electrix was undertaking maintenance activities and called to report the theft HV earth and damage to LV cables at incident location. | Earth/earthing | 2 | 2 | 2 |  | MLN022 | Copper theft from substation pole | Damage to network assets | 17/12/2018 8:07 |  |  | 10912 | Roadway |  | 20190110PWA_02 | Infrastructure (network-based) | -37.6889 | 144.5303 | 1 | Powercor | Report | 13863 | 0.028557 | Earthing cable | Laverton Raaf | 3338 | Brookfield | Other
Repairs undertaken to restore supply and make safe supply to both lights and the Vicroads cabinet. | 238 BULMANS ROAD, MELTON WEST VIC 3337 | 30298009 | Vandalism;Copper theft | [6 empty] | PAL received a report of Public lighting cable theft along Bulmans Rd, just north of the Western Fwy overpass. Thieves have cut and stolen Public lighting cables in various pits. Repairs undertaken to restore supply and make safe supply to both lights and the Vicroads cabinet. There was no fire , no reported injuries or third party property damage. | Cable;Services pit | 2 | 2 | 2 |  | MLN022 | copper theft and vandalism | Damage to network assets | 19/12/2018 0:31 |  |  | 10914 | Roadway |  | 20190110PWA_04 | Infrastructure (network-based) | -37.6876 | 144.5493 | 1 | Powercor | Report | 13865 | 0.015125 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Fault crew dispatched to investigate, make safe and repair | 17 PANFIELD AVENUE, RINGWOOD VIC 3134 | LIS1209065 |  |  |  | Defective component |  |  | 2 | report of Krone box fire on pole | Connection box | 0 | 0 | 0 |  | RWN33 | Krone box had melted and caused burnt plastic to fall onto the ground. No damage to any customers property and no ground fire present. All damage was caused in road reserve. Fire was cause by a fault in the Krone box due to severe weather and rain earlier on during the day | Pole-top fire | 43262.6618 | 1 | Negligible: no ground fire | 10917 |  |  | 20190110SPN_01 | Infrastructure (network-based) | -37.799 | 145.2413 | 1 | AusNet Services Distribution | Report | 17861 | 0.0060451 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Ringwood | Connection
The line was made safe and the insulator was replaced with a stretch 9 shed insulator. | 775 KING PARROT CREEK ROAD, STRATH CREEK VIC 3658 | LIS 4704598 |  | Bird |  |  |  |  | 1 | Grass fire - Fault crew dispatched to investigate and make safe: Crew onsite found at angle pole 4704598 on the property side, where conductors are closest to pole. A damaged 5 shed insulator & bird cover. Also what looks to be the remains a magpie, still in place between the bird cover & the conductor (refer to photos). At the bottom of the pole there was a 450 square meter burnt area of a grass. The crew assess that the insulator required changing. | Insulators | 0 | 0 | 0 |  | SMR14 | Bird Incident | Grassfire | 22/12/2018 18:04 | 1 | Small: 10 - 1000 sq.m | 10919 |  |  | 20190110SPN_03 | Infrastructure (network-based) | -37.2094 | 145.2368 | 1 | AusNet Services Distribution | Report | 17858 | 0.024608 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Strath Creek | Animal
On arrival Crew found centre phase on three phase tee off burnt through and conductor was only holding on by flex. supply isolated and pole replaced. | 970 BLACK SWAMP ROAD, BULLAROOK VIC 3352 | 32013164 |  |  |  | Leakage |  |  |  | Powercor received a report from a customer advising while attending to a pump for stock water he found a nearby wooden pole with evidence of a fire. He believed it had occurred in the last two days, almost burnt through and cross arm barely holding on, wires very low. Supply is still on. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | BAN008 | Pole fire caused by excessive leakage current | Pole-top fire | 43709.8438 | 1 | Negligible: no ground fire | 10922 | Agricultural |  | 20190111PWA_01 | Infrastructure (network-based) | -37.4899 | 144.0266 | 1 | Powercor | Report | 13877 | 0.011809 | 22kV AC | Ballarat Aerodrome | 3352 | Bullarook | Crossarm
Fault crew dispatched | 14 MARGARET STREET, KINGLAKE WEST VIC 3757 | LIS 1411055 |  |  |  | Candled fuse |  |  |  | E0007627 - Report of candling fuse | EDO fuse | 0 | 0 | 0 |  | KLK2 | 22kV EDO fuse is suspected to have hung-up and candled. There was no evidence of ground fire | Pole-top fire | 43739.7097 | 1 | Negligible: no ground fire | 10923 |  |  | 20190111SPN_02 | Infrastructure (network-based) | -37.4797 | 145.2732 | 2 | AusNet Services Distribution | Report | 13879 | 0.019494 | 22kV AC | Wallan (Kilmore Gap) | 3757 | Kinglake West | Fuse
Fault crew dispatched to investigate and make safe. Crew replaced the failed dropper and connection. Supply restored | FAIRFIELD, 886 ROSEDALE-FLYNNS CREEK ROAD, FLYNN VIC 3844 | LIS2622484 |  | Heat |  | Electrical breakdown |  |  |  | Report of burnt HV dropper | Dropper/bridge | 0 | 0 | 0 |  | TGN41 | Degraded Hot connection Crew attended site and found a connection had caused the centre phase dropper to overheat and fail. This happened after the hot day and rain had started. No evidence of ground fire | Melting or smoking only | 30/12/2018 3:48 |  |  | 10929 | Agricultural |  | 20190111SPN_08 | Infrastructure (network-based) | -38.1937 | 146.7082 | 1 | AusNet Services Distribution | Report | 18136 | 0.024653 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Flynn | Connection
Fault crew dispatched. Site made safe & supply restored | 55 ZIG ZAG ROAD, ELTHAM VIC 3095 | LIS918744 |  | Blown branch/vegetation | [5 empty] | E0007238 - Grass fire reported in the vicinity of AusNet Assets | Conductor (bare) | 0 | 0 | 0 |  | ELM15 | Vegetation: Trees Incident | Other electricity related | 43556.625 | 1 | Localised: less than 10 sq.m | 10930 |  |  | 20190111SPN_09 | Infrastructure (network-based) | -37.6998 | 145.1586 | 1 | AusNet Services Distribution | Report | 15267 | 0.03108 | 22kV AC | Essendon Airport | 3095 | Eltham | Trees
A possum made contact with the LV conductors and krone box at the LV bus pole for "Newman-Springfield" pole type substation that caused the possum and pole to catch on fire when the flash over occurred. Emergency high voltage switching was completed and the repairs were completed under Access Authority conditions prior to supply being restored. | 303 SPRINGFIELD ROAD, NUNAWADING VIC 3131 |  |  | Animal |  |  |  |  | 1 | At 3.51PM on 05/12/2018, a caller reports that on the corner of Springfield and Newman Roads there was a loud bang and the pole is now smoking. A moment later, the was another huge bang and lots of sparks. Mentions there is a transformer on the pole that is still smoking and is charred. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  | NW 21 | Animal Incident | Pole-top fire | 43232.6604 | 1 | Negligible: no ground fire | 10934 | Roadway |  | 20190114UTD_01 | Infrastructure (network-based) | -37.8129 | 145.1733 | 1 | United Energy Distribution | Report | 13899 | 0.00040509 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Nunawading | Animal
LEI attended with fault crew, and isolated the consumers mains at service pole at front of property. | 280 ERAMOSA ROAD W, MOOROODUC VIC 3933 |  |  |  |  | Fault on customer installation | Ineffective planning/procedures/processes | Phase to earth | 1 | A Fencing contractor struck underground consumers mains whilst using a tractor to drill fence holes. The contractor claimed he received a tingle. | Customer installation | 2 | 2 | 2 |  |  | using a tractor to drill fence holes | Minor shock | 43678.6424 |  |  | 10943 | Residential |  | 20190115UTD_02 | Infrastructure (network-based) | -38.2148 | 145.1164 | 1 | United Energy Distribution | Report | 15143 | 0.0012153 | Low voltage AC (<1kV) | Moorabbin Airport | 3933 | Moorooduc | Dug up
Made site safe, replaced LV mains and notified the council. | 45 BURKE STREET, BRAYBROOK VIC 3019 |  |  | Council |  |  |  |  | 2 | Council tree branch fallen causing conductor to clash which resulted in live LV mains conductor on the ground | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/01/2019 16:42 |  |  | 11958 | Public space |  | 20190116JEM_01 | Infrastructure (network-based) | -37.7775 | 144.8497 | 1 | Jemena | Report | 15306 | 0.0042627 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Trees
On arrival crew isolated supply and carried out repairs. | 16 REEVES ROAD, WOOLSTHORPE VIC 3276 | 33101473 |  |  |  | Fuse failed to eject |  |  |  | A Powercor fault crew reported a candled EDO unit at the incident location. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | KRT012 | EDO fuse hung up and burnt | Pole-top fire | 43709.5028 | 1 | Negligible: no ground fire | 11957 | Roadway |  | 20190116PWA_05 | Infrastructure (network-based) | -38.1797 | 142.4225 | 1 | Powercor | Report | 14943 | 0.0076806 | 22kV AC | Warrnambool Airport Ndb | 3276 | Woolsthorpe | Fuse
Jemena Servicing crew removed extension lead from switchboard at 39 Delacy St Maidstone, refitted missing switchboard covers at adjoining properties at 41 Delacy St and 18 Havelock St Maidstone to make safe from 'live' exposed terminals , | 39 DELACEY STREET, MAIDSTONE VIC 3012 |  | Caused by REC/contractor |  |  | Fault on customer installation |  | Phase to earth | 2 | Jemena Service attended a property 39 Delacy St Maidstone to install metering and servicing connection and found the covers removed from the switchboard and an extension lead connected to the switchboard, the extension lead was not 'live'. They noticed the adjacent properties 41 Delacy St and 18 Havelock St also had the meter/switchboard covers removed and had 'live' exposed terminals. The 3 properties are under the same Builder and REC. 39 | Switchboard | 0 | 0 | 0 |  |  | REC is connecting extension lead to main switchboard of new installation. (39 Delacy St Maidstone) REC has removed switchboard covers from 'live' switchboard ( 41 Delacy St and 18 Havelock St Maidstone). Unsafe practice of connecting extension lead to 'new' installation for the purpose of energising prior to network servicing and metering was completed. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/01/2019 12:05 |  |  | 11962 | Construction |  | 20190117JEM_01 | Infrastructure (network-based) | -37.7855 | 144.8802 | 1 | Jemena | Report | 14952 | 0.041103 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | Other
On arrival crew isolated supply and carried out repairs | KAREELA, 292 KOORINGAL ROAD, HAWKESDALE VIC 3287 | 30347516 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a grass fire due to a pole fire at the incident location. When crews arrived they found a small grass fire (10m x 20m) had been started at the base of a pole by a failed LV junction box. There was no reported injuries. | Connection box | 2 | 2 | 2 |  | KRT013 | Connection box overheated, insufficient remains to determine cause | Grassfire | 16/01/2019 17:55 | 1 | Small: 10 - 1000 sq.m | 11965 | Agricultural |  | 20190118PWA_01 | Infrastructure (network-based) | -38.0622 | 142.3584 | 1 | Powercor | Report | 14959 | 0.023375 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3287 | Hawkesdale | Connection
On arrival crew isolated supply and carried out repairs | WILGAH, 60 OLD DARGALONG SCHOOL ROAD, WAHRING VIC 3608 | 32192254 |  | Wind;Alive;Fallen;MEC |  |  |  |  | 1 | CFA reported tree on conductors and ground fire underneath. On arrival crew identified that a large tree of some 35 metres in height had fallen breaking conductors and starting a small ground fire. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | MNA034 | Vegetation: Trees Incident | Grassfire | 19/01/2019 15:03 | 1 | Medium: 1000 sq.m - 10 ha | 11973 | Agricultural |  | 20190121PWA_01 | Infrastructure (network-based) | -36.6653 | 145.2462 | 1 | Powercor | Report | 14975 | 9.2593e-06 | 22kV AC | Mangalore Airport | 3608 | Wahring | Trees
Section of U/G cable was already isolated due to a planned outage in the area. Repaired the damaged U/G cable | 56 BURGE DRIVE, SUNBURY VIC 3429 |  | Working too close to underground cables | [6 empty] | LV U/G cable dug up by 3rd party workers. No responsible parties were on site when the crew arrived. There was no No Go Zone request raised for the location. | Cable | 0 | 0 | 0 |  |  | It is assumed that LV U/G cable is dug up by 3rd party workers (maybe an excavator but there is no evidence to be sure it was). No details of the responsible party could be confirmed and obtained | No Go Zone (no contact) | 22/01/2019 9:25 |  |  | 11983 | Public space |  | 20190122JEM_02 | Infrastructure (network-based) | -37.5921 | 144.7026 | 1 | Jemena | Report | 15310 | 0.010381 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Dug up
Supply isolated to facilate repairs. | 1388 MOUNT COTTRELL ROAD, MOUNT COTTRELL VIC 3024 | 30107263 | Vandalism | [6 empty] | Police Comms (Ph 9363 4635) contacted Powercor to advise of exposed wiring at roadside and stolen cables. A Powercor crew attended the site and noted exposed underground cabling at a customer LV pit and cut/missing customer LV mains to a customer metering point. There was no fire and no reported injuries. | Customer installation | 2 | 2 | 2 |  | MLN011 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/12/2018 17:06 |  |  | 11982 | Residential |  | 20190122PWA_02 | Infrastructure (network-based) | -37.7465 | 144.6131 | 1 | Powercor | Report | 14987 | 0.030566 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival crew isolated supply to allow repairs to be carried out. | 7 JACKSON STREET, RICHMOND VIC 3121 | 30315219 |  | Blown branch/vegetation | [5 empty] | Customer reported tree branch had fallen across service line, still attached at pole end. Initially reported as fire, but on arrival crew found no sign of fire. There were no reported injuries, some damage to customers point of attachment. | Service conductor | 2 | 2 | 2 |  | NR007 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43556.5333 |  |  | 11984 | Residential |  | 20190122PWA_03 | Infrastructure (network-based) | -37.8225 | 145.0115 | 1 | CitiPower | Report | 14989 | 0.0075868 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Trees
On arrival crew isolated supply and carried out repairs | WILTSHIRE ROAD, MACEDON VIC 3440 | 30141744 | Vandalism;Copper theft | [6 empty] | TELSTRA reported attempted copper theft and cable damage at incident location. Crew found underground cable damaged as a result of attempted copper theft, no injuries, no ground fire and no property damage. | Services cable | 2 | 2 | 2 |  | WND011 | copper theft and vandalism | Damage to network assets | 43678.5542 |  |  | 11988 | Roadway |  | 20190123PWA_03 | Infrastructure (network-based) | -37.4374 | 144.5512 | 1 | Powercor | Report | 14999 | 0.027062 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
The attending Powercor Fault Crew re-terminated the O/H Service Neutral conductor at the Pole Top Connection Box | 9 MOORHOUSE STREET, LORNE VIC 3232 | 30301331 |  |  |  | Fatigue |  |  |  | Customer was in the Kitchen washing dishes when he received an electric shock as he made simultaneous contact with his hands between the Kitchen Taps and the metal Sink. | Service conductor | 0 | 0 | 0 |  | CLC005 | â€œOpen Circuitâ€ O/H Service Neutral Conductor which was detached at its termination in the Pole Top Connection Box | Minor shock | 43647.3333 |  |  | 11993 | Residential |  | 20190123PWA_08 | Infrastructure (customer connection) | -38.5435 | 143.9715 | 1 | Powercor | Report | 15004 | 0.014069 | Low voltage AC (<1kV) | Avalon Airport | 3232 | Lorne | OH Cable
On arrival crew isolated supply and carried out repairs. | 100-128 FERRIS ROAD, COBBLEBANK VIC 3338 | 34015306 |  |  |  | Unknown technical factor |  |  |  | Report from Vicfire of street light pole smoking. On arrival crew advised that lantern had failed internally which had caused the lantern to smoke. There was no ground fire, no reported injuries or third party property damage. | Public lighting | 2 | 2 | 2 |  | MLN021 | Unable to determine due to damage to lantern. | Pole-top fire | 14/01/2019 15:34 | 1 | Negligible: no ground fire | 12001 | Roadway |  | 20190124PWA_06 | Infrastructure (network-based) | -37.7052 | 144.6021 | 1 | Powercor | Report | 15012 | 0.024073 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | AF Other
On arrival crew isolated supply and carried out repairs. | 99 FAIRFAX CIRCUIT, ALBANVALE VIC 3021 | 30103829 |  |  |  | Corrosion |  |  |  | Resident reported they heard a loud bang from the pole and smoke coming from the pole outside their property, and that there was a fire at the bottom of the pole and grass. The residents extinguished the small grass fire (approx 1m2) in the nature stri. When the fault crew arrived they found that the red phase LV transformer bus fused isolator at pole LIS-014081 had burnt out at the copper to aluminium connector connecting the isolator to the overhead conductor. There were no reported injuries or third party property damage reported. | Connector/termination | 2 | 2 | 2 |  | SU022 | Overheated connection | Grassfire | 24/01/2019 18:44 | 1 | Localised: less than 10 sq.m | 12008 | Roadway |  | 20190125PWA_01 | Infrastructure (network-based) | -37.7497 | 144.7637 | 1 | Powercor | Report | 17609 | 0.028649 | Low voltage AC (<1kV) | Laverton Raaf | 3021 | Albanvale | Connection
Dispatched fault crew to investigate, make safe and carry out repairs. Fire brigade on site when fault crew arrived | DANDENONG RANGES NATIONAL PARK, 70 MONBULK ROAD, SHERBROOKE VIC 3789 | LIS 1305203 |  | Blown branch/vegetation | [5 empty] | E0008623 - Tree brought down and broke 2 bays of LV ABC. Small 1M x 1M grass fire observed in the area. | Conductor (ABC) | 0 | 0 | 0 |  | BGE11 | Vegetation: Trees Incident | Grassfire | 24/01/2019 19:18 | 1 | Localised: less than 10 sq.m | 12012 |  |  | 20190125SPN_03 | Infrastructure (network-based) | -37.887 | 145.3703 | 2 | AusNet Services Distribution | Report | 15026 | 0.00314 | Low voltage AC (<1kV) | Moorabbin Airport | 3789 | Sherbrooke | Trees
A faults crew attended, made the site safe and replaced the LV blue phase transformer lead that had failed due to overload as the conditions were very warm at the time of the fault. At the time of the fault, molten metal fall to the dry grass below and a 1-1.5sqm fire started that was extinguished when the faults crew attended. | 31 DALNY ROAD, MURRUMBEENA VIC 3163 |  |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | Customers supplied from "Dalny-Marma" pole type substation contacted the United Energy faults and emergencies call centre advising they have lost their electricity supply. One caller from 31 Dalny Road mentioned there are burn marks on the grass out side her property. | Conductor (insulated);Copper;Pole mounted | 0 | 0 | 0 |  | OR 35 | The LV transformer lead failed due to probable overload as the conditions were very warm at the time of the fault. | Grassfire | 24/01/2019 19:46 | 1 | Localised: less than 10 sq.m | 12010 | Roadway |  | 20190125UTD_03 | Infrastructure (network-based) | -37.9024 | 145.0685 | 1 | United Energy Distribution | Report | 15022 | 0.018022 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Murrumbeena | AF Other
Dispatched fault crew to investigate. Cause of the fire appears to be a burnt out fuse box, not conductors clashing. | 334 GENTLE ROAD, GUNDOWRING VIC 3691 | LIS 5201242 |  |  |  | Electrical breakdown |  |  |  | Fuse Box_FOLCB burnt | Any other type | 0 | 0 | 0 |  | WOTS11 | Customer drawing 40 amps of load regularly. Appears connections in FOLCB on pole have dried and deteriorated resulting in the failure of the box | Grassfire | 27/01/2019 3:00 | 1 | Localised: less than 10 sq.m | 12022 |  |  | 20190128SPN_01 | Infrastructure (network-based) | -36.2742 | 147.0572 | 1 | AusNet Services Distribution | Report | 17776 | 0.02778 | Low voltage AC (<1kV) | Wangaratta Aero | 3691 | Gundowring | Connection
Crew arrived on site and made safe. New cable was installed later. | 225 DONNYBROOK ROAD, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Unknown persons stole copper street light cables. | Cable | 2 | 2 | 2 |  |  | Unknown person has stolen the copper street light cable. | Loss of supply;Damage to network assets | 29/01/2019 8:34 |  |  | 12028 | Roadway |  | 20190129JEM_02 | Infrastructure (network-based) | -37.5358 | 144.9056 | 1 | Jemena | Report | 15051 | 0.015307 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
The Fault crew isolated supply and made the site safe. An Asset Inspector was immediately dispatched to check other street light poles in the area and ensure no risk of other pole fails could occur. | 73 ARGYLE STREET, TRARALGON VIC 3844 | LIS 5648266 |  |  |  | Corrosion |  |  |  | E0008755 - Report of 10m/1kN slip base street light pole installed on the centre median strip fell over and came in to contact with a passing vehicle. The vehicle sustained damage to the rear left pillar, rear left quarter panel and the rear windscreen was also damaged. An AusNet Services fault crew and Emergency Services attended site. No report of injury. | Public lighting | 0 | 0 | 0 |  |  | The street light pole failed due to corrosion of the bolts and washer at the base between the pole and slip base sections. The level of corrosion around the slip base section of the street light pole was sufficient enough to seize the bolts that secure the light pole to the slip base. This corrosion prevented the Asset Inspector from re-tensioning the bolts as per the Asset Inspection Manual which states flange bolts should be checked for a minimum tension and adjusted if necessary. All street light poles in the area have been checked to ensure no rust or loose bolts are present. | Less than $50k damage;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/01/2019 22:06 |  |  | 12039 | Roadway |  | 20190130SPN_03 | Infrastructure (network-based) | -38.1934 | 146.5474 | 1 | AusNet Services Distribution | Report | 15066 | 0.032615 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | AF Other
Operator attended and isolated substation LV and HV to make safe. Section isolated and conductor repaired. | 270 SUSSEX STREET, PASCOE VALE VIC 3044 |  |  |  |  | Age;Corrosion |  |  | 2 | One phase of high voltage conductor fell to the ground outside 270 Sussex street, Pascoe Vale. | Conductor (bare) | 2 | 2 | 2 |  |  | Deterioration of connection due to degradation. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/01/2019 15:11 |  |  | 12049 | Residential |  | 20190131JEM_02 | Infrastructure (network-based) | -37.7216 | 144.9514 | 1 | Jemena | Report | 15078 | 0.021687 | 22kV AC | Essendon Airport | 3044 | Pascoe Vale | Connection
Dispatched fault crew to investigate and make safe. Ground fire had been extinguished by the landowner prior to the fault crews arrival. HV conductors were repaired and supply restored | 130 LYE AND DIXON ROAD, RIPPLEBROOK VIC 3818 | LIS 2703396 |  | Fallen | [5 empty] | E0009015 - Tree branch failed, falling into and bringing down O/H HV lines as it fell to ground resulting in a ground fire approx 170m x 33m | Conductor (bare) | 0 | 0 | 0 |  | WGL11 | Vegetation: Trees Incident | Grassfire | 31/01/2019 5:32 | 1 | Medium: 1000 sq.m - 10 ha | 12054 | Agricultural |  | 20190131SPN_02 | Infrastructure (network-based) | -38.173 | 145.7796 | 2 | AusNet Services Distribution | Report | 15494 | 0.0043403 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Ripplebrook | Trees
The HV overhead conductors were isolated and ESV advised. The crew checked the 3/12 steel conductors for contact damage and were deemed to be load worthy. A 16amp HV powder filled fuse had operated at DN0921 in Illawarra Avenue that was replaced following an ESV representative attending and subsequent investigation. | ILLAWARRA AVENUE, ROWVILLE VIC 3178 | 9339466 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | Heat |  |  |  |  | 1 | Caller reports that an excavator has hit the power lines and started a fire. Emergency services are on site outside the Wetlands. An large excavator was being loaded onto a trailer and the boom contacted the overhead 3/12 steel 22kV conductors in the Melbourne Water owned property (Rowville Wetlands). Approximately a total of 10sqm of the dry grass on each side of the trailer caught on fire (total 20sqm) as a result of the two chains that hold the ramp acting as earths creating a path for the high voltage to ground. No damage or injuries were sustained but the excavator operator was distressed by the event. | Conductor (bare);Steel | 0 | 0 | 0 |  | LD06 | An excavator contacted a HV overhead conductor as it was being loaded onto a trailer. The excavator was being loaded onto the trailer directly under the 22kV overhead conductors. | Grassfire;No Go Zone (contact) | 30/01/2019 13:28 | 1 | Localised: less than 10 sq.m | 12059 | Public space |  | 20190131UTD_02 | Infrastructure (network-based) | -37.934 | 145.2173 | 1 | United Energy Distribution | Report | 18398 | 0.020029 | 22kV AC | Moorabbin Airport | 3178 | Rowville | Vehicle
Emergency high voltage switching was completed to minimise the number of customers affected. The damaged electrical infrastructure was repaired under Access Authority conditions and supply restored upon completion. Following the restoration of supply, the LEI inspected properties supplied from "Taylors-Bayliss" substation and confirmed that a HVI did not occur. | 875 TAYLORS ROAD, DANDENONG SOUTH VIC 3175 | 622594 |  | Lightning;Wind;Heat;Alive |  | Conductor clashing |  |  |  | At 5.28PM on 30/01/2019, 22kV feeder DVY 24 circuit breaker reclosed to lockout. Emergency services advised of a large tree over the powerlines near the corner of Bayliss and Taylors Roads. During storm activity with strong gusty winds, a private tree from 845 Taylors Road broke and fell over the HV/LV conductors that caused crossarms to break and conductors to clash. Molten metal fell into the dry grass below and caused a 2sqm grass fire that self extinguished in the rain. A LEI was called to investigate as a HVI was suspected to customers supplied from "Taylors-Bayliss" substation. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | DVY 24 | Vegetation: Trees Incident | Grassfire | 30/01/2019 17:38 | 1 | Localised: less than 10 sq.m | 12060 | Roadway |  | 20190131UTD_03 | Infrastructure (network-based) | -38.046 | 145.2265 | 1 | United Energy Distribution | Report | 18399 | 0.029591 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Trees
On arrival crew isolated supply and carried out repairs | 110 EDGECOMBE STREET, KYNETON VIC 3444 | 30320555 | Vandalism;Copper theft | [6 empty] | Thieves / vandals have gained entry to public lighting pits and removed service cables between 2 pits at the incident location. Site left vandalised and presenting a public safety risk. No fire or reported injuries due to this incident. | Services cable;Services pit | 2 | 2 | 2 |  | WND023 | copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/01/2019 10:49 |  |  | 12069 |  |  | 20190201PWA_03 | Infrastructure (network-based) | -37.2433 | 144.4648 | 1 | Powercor | Report | 15105 | 0.034884 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3444 | Kyneton | Other
On arrival supply isolated and repairs carried out when emergency services cleared the site | 1903-1919 MOUNT COTTRELL ROAD, MOUNT COTTRELL VIC 3024 | 30107297 | Vehicle | [5 empty] | 1 | A customer reported a car had hit a pole outside 1903 Mount Cottrell road. The vehicle was reported as travelling in a southerly direction. The force of the impact was severe. The driver and sole occupant of the vehicle, died at the scene There was no fire, no electrical contact. | Pole (wood) | 2 | 2 | 2 |  | MLN011 | Vehicle struck power pole | Damage to network assets | 31/01/2019 16:06 |  |  | 12071 | Roadway |  | 20190201PWA_05 | Infrastructure (network-based) | -37.7806 | 144.6071 | 1 | Powercor | Report | 15107 | 0.035644 | 22kV AC | Laverton Raaf | 3024 | Mount Cottrell | Vehicle
the work crew treated the service and after investigation the service was retired | WEEROOMA, 76 BRAMLEY LANE, GUYS FOREST VIC 3709 | pole 5211704 |  |  |  | Not built/maintained to design |  |  |  | E0008896 - Live services coiled around stake in ground | Service conductor | 0 | 0 | 0 |  | TRC01 | Poor workmanship | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/01/2019 8:43 |  |  | 12085 |  |  | 20190204SPN_06 | Infrastructure (network-based) | -36.0806 | 147.6497 | 1 | AusNet Services Distribution | Report | 15138 | 0.00083796 | Low voltage AC (<1kV) | Wangaratta Aero | 3709 | Guys Forest | Other
Successful reclose of 66kv Line at time of strike. Grass fire was extinguished before crew arrived on site. Approx 5m2 of burnt out grass around base of pole. Area made safe. Crew advised conductor strands were broken in the bridge of this tower. The damaged conductor in the bridge was replaced. | 108 BROOK STREET, SUNBURY VIC 3429 | A005293 |  | Lightning |  |  |  |  | 1 | The event was caused by lightning striking the tower 245 (A005293) (probably the conductor) resulting in conductor strands broken in the bridge at this tower. Since there were a few strands connected the feeder held until the crews effected the repairs about 2 weeks after the lightning event. The damaged conductor in the bridge was replaced. Confirmed minor grass fire. See photos attached in the "Notes & Findings" section | Connector/termination | 0 | 0 | 0 |  | KTSSBY | Lightning strike hit tower 245 (A005293). Molten particles from the broken conductor in the bridge fell to ground resulting in grass fire. | Grassfire | 43648.9174 | 1 | Localised: less than 10 sq.m | 12116 | Peri-urban |  | 20190207JEM_05 | Infrastructure (network-based) | -37.5891 | 144.7428 | 1 | Jemena | Report | 17751 | 0.033729 | 66kV AC | Melbourne Airport | 3429 | Sunbury | Lightning
On arrival crew isolated supply and carried out repairs. | 406 HARKNESS ROAD, MELTON WEST VIC 3337 | 30227130 | Copper theft | [6 empty] | Report received from resident that the pole in front of their property in the street looks damaged, with metal hanging off and wiring exposed. Upon arrival the fault crew found that someone has attempted to steal the underground pole to pit service cable by removing the cover guard, breaking the conduit, and perhaps attaching the service to their car before attempting to drive away with it. Approximately 20m of cable has been stolen. The cable was not in service as around 3 months ago the same fault crew attended the same property (which is an unoccupied fire damaged house) where a similar theft was attempted when the service was still alive. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN022 | Copper theft | Damage to network assets | 25/01/2019 18:45 |  |  | 12109 | Roadway |  | 20190207PWA_05 | Infrastructure (network-based) | -37.6692 | 144.534 | 1 | Powercor | Report | 15170 | 0.00489 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and carried out repairs. An LEI attended and found no HVI had occurred. | 11 BATEY DRIVE, INVERGORDON VIC 3636 | 33081082 |  | Fallen | [5 empty] | A customer reported bright sparks from pole at incident location. On arrival crew found a limb from a tree outside the clearance space had fallen across LV conductors,, damaging crossarms. The conductors did break and were suspended low over driveway but not able to be reached from the ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Crossarm (wood);Pole mounted | 2 | 2 | 2 |  | NKA001 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 27/01/2019 2:58 |  |  | 12114 |  |  | 20190207PWA_07 | Infrastructure (network-based) | -36.1501 | 145.6084 | 1 | Powercor | Report | 15178 | 0.029448 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Invergordon | Trees
On arrival crew isolated supply and carried out repairs. | 2317 PRINCES HIGHWAY, STONYFORD VIC 3260 | 31009370 |  | Lightning |  | Fuse failed to eject |  |  |  | Customer reported Transformer on pole has blown, making a "cooking noise" before it went off and is now quite dark and damaged at incident location. On arrival crew found one fuse blown and one hung up. There was a small fire at the base of the pole (1 sq metre). The fire was extinguished by the customer There was no reported injuries or third party property damage. | EDO fuse;Pole mounted | 2 | 2 | 2 |  | CDN002 | EDO fuse hung up following transformer failure. | Grassfire | 43648.5736 | 1 | Localised: less than 10 sq.m | 12117 | Roadway |  | 20190208PWA_01 | Infrastructure (network-based) | -38.3134 | 143.3245 | 1 | Powercor | Report | 15182 | 0.0088183 | 22kV AC | Warrnambool Airport Ndb | 3260 | Stonyford | Fuse
The attending Powercor Fault Crew replaced stay rod and restrained the damaged Guy Wire on the SWER Transformer Termination Pole and restored supply to the Transformer and completed an NST test which confirmed a Pass result. | 2410 WHINFIELD ROAD, PINE GROVE VIC 3573 | 30256887 |  | Animal |  | Fatigue |  |  |  | Person was in the yard external to the house when he received an electric shock as he touched the Pressure Pump in the yard with his hand and similarly when he touched the Compressor which was also in the yard. A visual inspection following isolation of the HV to the Transformer by the Fault Crew identified a broken Guy Wire on the SWER Transformer Termination Pole which was wrapped around the pole and the earthed substation and in contact with the insulated HV Dropper and the LV Bushing on the Substation. | Guy wire;Transformer | 0 | 0 | 0 |  | ECA012 | Stay rod broken off by cattle - rubbing against stay | Minor shock | 43770.5 |  |  | 12135 | Agricultural |  | 20190211PWA_04 | Infrastructure (network-based) | -36.223 | 144.4641 | 1 | Powercor | Report | 15206 | 0.01903 | 12.7kV AC (SWER) | Bendigo Airport | 3573 | Pine Grove | AF Other
UE fault crews attended with an LEI and undertook inspection for damage at neighbouring premises. The LEI confirmed that a high voltage injection occurred affecting customers supplied from "O'Briens Cottonwood" substation. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 15 OBRIENS LANE, TEMPLESTOWE VIC 3106 | 7057699 |  | Blown branch/vegetation |  |  |  |  | 1 | During storm event, a tree branch broke and fell onto the HV reticulation conductors snapping one which then contacted the white and blue phase conductors causing a high voltage injection into the LV reticulation circuit. | Conductor (bare) | 0 | 0 | 0 |  | DC01 | Vegetation: Trees Incident | HV injection | 30/01/2019 18:00 |  |  | 12127 | Roadway |  | 20190211UTD_02 | Infrastructure (network-based) | -37.7526 | 145.1495 | 1 | United Energy Distribution | Report | 15195 | 0.032137 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3106 | Templestowe | Trees
The LV connection was repaired and supply restored. | STEVENS ROAD, VERMONT VIC 3133 | 7031909 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | During very hot conditions, customers supplied from "Stevens-Woodcrest" substation advised of a loss of supply and a faults truck was dispatched. They identified the white phase ampact connection for the south circuit of "Stevens-Woodcrest" substation had burnt off due to probable overload at pole number LIS 7031909. Molten metal had fallen into the dry grass below and a 2sqm fire started that self extinguished. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  |  | Probable overload during hot and windy weather. | Grassfire | 43526.6132 | 1 | Localised: less than 10 sq.m | 12133 | Roadway |  | 20190211UTD_04 | Infrastructure (network-based) | -37.8397 | 145.1836 | 1 | United Energy Distribution | Report | 15204 | 0.0022546 | Low voltage AC (<1kV) | Moorabbin Airport | 3133 | Vermont | Connection
The LEI checked all electrical appliances and equipment and no damage was sustained however, the meter appeared to have suffered fire damage and requires replacement. A faults crew replaced the fire damaged meter and supply restored after the 80amp service fuse was replaced at the POA as it operated at the time of the event. | 265A HODGINS ROAD, HASTINGS VIC 3915 |  |  | Lightning |  |  |  |  | 1 | At 9.53AM on 18/01/2019, 22kV feeder HGS23 circuit breaker successfully reclosed and held. At the same time, 66kV feeder circuit breaker TBTS-DMA also successfully reclosed and held. During storm activity with severe lightning, many locations were struck with multiple feeder reclosures along the Morning Peninsula area. Also in the vicinity, "Hodgins P77-Coolart" substation was struck by lightning and the 3 phase 25kVA transformer requires replacement. Lightning appears to have struck a home at 265A Hodgins Road Hastings and a LEI was sent to investigate for damage. | Pole top | 0 | 0 | 0 |  | HGS 23 | Lightning struck the property and surrounding electrical infrastructure. | Meter board | 18/01/2019 9:53 | 1 | Negligible: no ground fire | 12136 | Roadway |  | 20190211UTD_06 | Infrastructure (network-based) | -38.3002 | 145.1531 | 1 | United Energy Distribution | Report | 15207 | 0.021501 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Lightning
On arrival crew isolated supply and carried out repairs | 10 SEGTNAN COURT, BOLWARRA VIC 3305 | 33204908 |  |  |  | Overheated connection |  |  |  | REC reported meter board fire due to burn fuse. There was no reported injuries | Meter board (including fuses) | 2 | 2 | 2 |  | PLD001 | Overheated fuse | Meter board | 43441.3833 | 1 | Negligible: no ground fire | 12150 |  |  | 20190213PWA_02 | Infrastructure (network-based) | -38.2551 | 141.6247 | 1 | Powercor | Report | 15229 | 0.013367 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Bolwarra | Fuse
On arrival crew carried out repairs | CHINKAPOOK-NYAH WEST ROAD, NYRRABY VIC 3585 | 32155442 |  |  |  | Leakage |  |  |  | During outage crew located a pole fire at pole 88 Manangatang line There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | SHL002 | Excessive leakage current | Pole-top fire | 18/09/2018 21:28 | 1 | Negligible: no ground fire | 12155 | Agricultural |  | 20190213PWA_06 | Infrastructure (network-based) | -35.186 | 143.2639 | 1 | Powercor | Report | 15235 | 0.0043519 | 22kV AC | Swan Hill Aerodrome | 3585 | Nyrraby | Pole
Service line replaced | 19 VIRGILIA DRIVE, HOPPERS CROSSING VIC 3029 | 30118379 |  |  |  | Corrosion |  |  |  | Person received an electric shock when she simultaneously contacted the metallic tap with one hand and the metallic shower base trap with her foot. | Service conductor;Neutral screen | 0 | 0 | 0 |  | LV001 | Corroded service neutral at Point Of Attachment | Minor shock | 26/01/2019 10:30 |  |  | 12160 | Residential |  | 20190213PWA_07 | Infrastructure (customer connection) | -37.8589 | 144.6845 | 1 | Powercor | Report | 15243 | 0.015118 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
The faults crew proceeded to replace the FOLCB on pole No. LIS 3303088 and supply was restored after the LV fuses were replaced at "Nepean N519-Newberry" substation. The single phase aerial service cable supplying No. 10 was also replaced. | 10 NEWBERRY AVENUE, BONBEACH VIC 3196 | 3303088 |  | Prone to salt deposition |  | Overheated connection |  |  | 2 | The neighbour reports there is a fire on top of the pole and pieces of plastic are falling down from the pole. The fire authority will be called to attend. A pole mounted three phase FOLCB that contained an underground service that supplied 10-12 Newbury Ave caught on fire and proceeded to self-extinguish with molten plastic falling to the ground below. The cause was unknown but most likely a loose connection that overheated. This event also caused the 250amp white and blue phase LV fuses at "Nepean N519-Newberry" substation to operate. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. The single phase XLPE aerial service supplying No. 10 was also damaged and required replacement. | Service conductor;Services cable;Connection box | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated. In addition, the location of the pole is in close proximity to Port Phillip Bay and there may have been corroded connections that also contributed. | Pole-top fire | 26/08/2018 22:00 | 1 | Negligible: no ground fire | 10353 | Roadway |  | 20180828UTD_04 | Infrastructure (network-based) | -38.0615 | 145.1181 | 1 | United Energy Distribution | Report | 13191 | 0.010117 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Bonbeach | Conductor
A faults truck attended and replaced the meter and supply was restored with the faults crew claiming the meter was faulty. The following day the REC was questioned by the United Energy metering team asking what he was doing at the time, and was he responsible whilst completing work at the grouped meter panel. According to the REC, he was in attendance for a customers call for intermittent supply when the meter caught fire. United Energy became suspicious when the REC was asked about putting in a claim for his time and the REC said no. The meter was sent to the manufacture "Secure" to determine what the cause of the fire was. The results of the investigation were returned to United Energy that found the cause was attributed to a loose active terminal connection. Apparently the top screw wasn't tightened and the bottom screw very loose that caused the connection to overheat and the meter connection to catch on fire at exactly the same time as the REC was in attendance. | UNIT 8 105 ATHERTON ROAD, OAKLEIGH VIC 3166 |  |  |  |  | Overheated connection | Poor workmanship |  | 1 | REC No. 11811 advised the meter caught on fire and he has removed the service fuse and the fire stopped. A REC was working at the site when coincidently an AMI 501 meter caught fire. The meter panel service fuse for unit 8 was removed by the REC and the fire self extinguished. | Connection to meter | 0 | 0 | 0 |  |  | The cause was attributed to a loose active terminal connection. | Meter board | 31/07/2018 21:24 | 1 | Negligible: no ground fire | 10356 | Residential |  | 20180828UTD_05 | Infrastructure (customer connection) | -37.8994 | 145.0955 | 1 | United Energy Distribution | Report | 13012 | 0.0066331 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh | Connection
fault crew dispatched to investigate and repair. Found LV neutral not correctly connected at sub station | 36 CURRAWONG ROAD, MONTROSE VIC 3765 | LIS 1005040 |  |  |  | Neutral fault;Defective component |  |  |  | IMS 234817 - Dim lights and damaged appliances reported by customers. Possible HVI | Equipment;Connector/termination | 0 | 1 | 0 |  | CYN21 | The construction crew were called to replace the S/S instead they found the LV neutral ABC crimp lug had failed and fallen apart at the s/stn leaving the circuit without a neutral. | Less than $50k damage | 43351.8521 |  |  | 10359 | Residential |  | 20180829SPN_01 | Infrastructure (network-based) | -37.8191 | 145.344 | 2 | AusNet Services Distribution | Report | 13121 | 0.011594 | Low voltage AC (<1kV) | Moorabbin Airport | 3765 | Montrose | AF Other
Pending any further substation removal work, the security fence was replaced to ensure the site is safe until the available options are assessed. | 23 OSBORNE AVENUE, SPRINGVALE VIC 3171 | 611837 | Misadventure | [5 empty] | 2 | Ground type substation has the mesh security fence pulled down and access can be easily obtained. Zinfra substation subcontractor, Qmain attended "Osborne-Princess" ground type substation and they noticed that one whole side of the fence and gate were missing. The removal of the fence and gate has been done neatly and there is no sign of theft or tampering. Unknown persons had removed the fencing at "Osborne-Princess" ground type substation that left live 22kV assets exposed to unauthorised persons. The building is presently vacant and there appears to have been no theft or untoward activities. The factory has been vacant for a couple of years now and front gates are secure. The length of fence missing is 9.7m including gate way of 1.1m. It was recommend that united Energy retire the ground type substation as this is the second time in 3 years the site has been broken into. Options are to install a pole substation on site and this option will be assessed. The substation presently supplies traffic signals in the road reserve and a Telstra communication tower. | Outdoor | 0 | 0 | 0 |  | SS22 | Zinfra substation subcontractor, Qmain attended "Osborne-Princess" ground type substation and they noticed that one whole side of the fence and gate were missing. The removal of the fence and gate has been done neatly and there is no sign of theft or tampering. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/08/2018 9:00 |  |  | 10364 | Commercial |  | 20180902UTD_01 | Infrastructure (network-based) | -37.946 | 145.146 | 1 | United Energy Distribution | Report | 13085 | 0.019791 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Other
On arrival crew isolated supply and carried out repairs | 4056 CRESWICK-NEWSTEAD ROAD, ALLENDALE VIC 3364 | 30139831 | Vehicle | [5 empty] | 1 | SCADA reported a lock out of the Creswick P178 ACR. A crew patrolled line and found a car that had collided with P241 Creswick S/L. Ambulance, fire and police attended. Driver taken to Melbourne in serious condition. Driver died of injuries next day. There was no fire at incident site. | Pole (wood) | 2 | 2 | 2 |  | BAN009 | Car struck pole | Loss of supply;Damage to network assets | 28/08/2018 4:28 |  |  | 10374 | Roadway |  | 20180904PWA_01 | Infrastructure (network-based) | -37.3696 | 143.9279 | 1 | Powercor | Report | 13192 | 0.0099873 | 22kV AC | Ballarat Aerodrome | 3364 | Allendale | Vehicle
Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a loose neutral connection at the FMJB Fault truck removed existing service and replaced with new service cable CTA re-tested property, all required VESI tests passed | 33 GORDON GROVE, NORTHCOTE VIC 3070 | 30184469 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Ken was showering at the time; he received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. | Service conductor | 2 | 2 | 2 |  | NC010 | Loose connection at FMJB | Minor shock | 43412.5 |  |  | 10377 | Residential |  | 20180904PWA_03 | Infrastructure (customer connection) | -37.775 | 144.992 | 1 | CitiPower | Report | 13106 | 0.023363 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded and damaged O/H Service Neutral Conductor termination at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 3 ROCKLEY CLOSE, CORIO VIC 3214 | 33045616 |  |  |  | Corrosion |  | Phase to earth |  | Mr Yohana Theip was in the Bathroom Showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | CRO013 | Corroded connection | Minor shock | 15/08/2018 18:30 |  |  | 10383 | Roadway |  | 20180906PWA_01 | Infrastructure (network-based) | -38.071 | 144.3457 | 1 | Powercor | Report | 13122 | 0.036061 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
Tests using an independent earth to various points of the installation including the reported points of contact found 3V on the customers earthing system and distribution neutral. It was traced back to a possible fault in the Powercor Lawrence Blanche pole mounted substation. Up to 3V was measured at the transformer star point and LV neutral at the substation Substation switched out and street circuit put under parallel. Follow up request put in to have substation tested. | 43 LAWRENCE STREET, ARDEER VIC 3022 | 32166679 |  |  |  | Unknown technical factor |  | Phase to earth |  | Siobhan reports receiving a slight shock in her the thumb of her left hand that had a cut when she touched the shower taps. | Transformer | 2 | 2 | 2 |  | SU021 | Suspected transformer fault | Minor shock | 29/08/2018 8:00 |  |  | 10386 | Residential |  | 20180907PWA_02 | Infrastructure (network-based) | -37.7784 | 144.8024 | 1 | Powercor | Report | 13125 | 0.022821 | Low voltage AC (<1kV) | Laverton Raaf | 3022 | Ardeer | AF Other
ESV Notified at 15:56, Reference No 10431682. VicPol attended and notified WorkSafe who did not attend. Faults crew attended and made the site safe pending an investigation. There was evidence of slight flash burns on a HV conductor. ESV representative attended (Greg Johnson) and met Adam Beel (UE). A No Go Zone permit was on issue at the construction site and the injured person was transported to hospital with severe burns to his feet. | 3 BEND ROAD, KEYSBOROUGH VIC 3173 |  | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | While installing a length of metal fascia on a new house, a roofing plumber has made contact with the live 22kV overhead conductors. | Conductor (bare) | 0 | 0 | 0 |  | KBH35 | A roofing plumber has made contact with the live 22kV aluminium conductors with a length of metal fascia. | Medical attention (first aid/doctor/hospital) | 43260.4465 |  |  | 10385 | Construction |  | 20180907UTD_01 | Infrastructure (network-based) | -38.0029 | 145.1813 | 1 | United Energy Distribution | Report | 13307 | 0.032061 | 22kV AC | Moorabbin Airport | 3173 | Keysborough | Other
On arrival Service removed pending repairs to customer's fuse box. | 20 MORTOO STREET, SWAN HILL VIC 3585 | 33068444 | Working too close to overhead lines | [6 empty] | A Tip truck owned by Swan Hill City council was dropping sand when it snagged the low voltage service line. Service was damaged, fascia and customers POA was damaged. There was no fire and no reported injuries. | Service conductor | 2 | 2 | 2 |  | SHL007 | Tip truck contacted service line | Loss of supply;No Go Zone (contact);Damage to network assets | 43229.6042 |  |  | 10401 | Roadway |  | 20180910PWA_06 | Infrastructure (network-based) | -35.3441 | 143.5421 | 1 | Powercor | Report | 13142 | 0.028104 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Vehicle
On arrival crew confirmed isolation. Supply left off until access to building can be arranged. Building vacant. | 153 MAIN STREET, STAWELL VIC 3380 | 31016170 | Vehicle | [6 empty] | CFA report a high load had pulled down wires in street. A crew attended and found a high load had pulled the service to 153 Main St off the pole end and service laying on ground. Police and CFA in attendance. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | STL004 | Suspected high load | Loss of supply;Damage to network assets | 43229.7535 |  |  | 10403 | Commercial |  | 20180910PWA_08 | Infrastructure (network-based) | -37.055 | 142.782 | 1 | Powercor | Report | 13144 | 0.030954 | Low voltage AC (<1kV) | Horsham Aerodrome | 3380 | Stawell | Vehicle
The attending Powercor Fault Crew disconnected the existing O/H Service Cable at the Reticulation Service Pole and abolished the supply to the property. Subsequent voltage tests between an independent earth and various remains of the electrical installation confirmed Zero Volts following removal of the existing O/H Service Cable. The Installation was left OFF supply. | 42 WALLACE STREET, MEREDITH VIC 3333 | 30222383 | Unauthorised work |  |  |  |  | Phase to earth |  | A person unknown was standing on a ladder at the POA on the Dwelling and received an electric shock to his hands when he intentionally cut through a Live Overhead Service Cable attached to a partially deconstructed dwelling which was being demolished by Mr Scott Wallace the Owner of the property. This action was witnessed by a neighbouring resident, Mr Christian Bourke who repeatedly warned the person of the dangers associated with his proximity to the O/H Service Cable. The person unknown failed to respond to Mr Bourkeâ€™s warnings and stated he received an electric shock from one hand to the other as he cut through the O/H Service Cable. The rear section of the structure had been previously abolished, however the front portion of the building remained with the O/H Service Cable attached as at 7 September 2018. The attending LEI observed the structure completely demolished on 9 September 2018 and confirmed the O/H Service Cable laying on the ground was energised at 230 Volts AC to an independent earth. | Service conductor | 2 | 2 | 2 |  | GL015 | illegal abolishment | Minor shock;No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43290.625 |  |  | 10417 | Roadway |  | 20180912PWA_03 | Infrastructure (network-based) | -37.8503 | 144.0763 | 1 | Powercor | Report | 13162 | 0.035039 | Low voltage AC (<1kV) | Avalon Airport | 3333 | Meredith | Other
Supply isolated pole removed | 6206 MIDLAND HIGHWAY, CLARENDON VIC 3352 | 31037826 |  | Precipitation;Wind |  |  | Poor workmanship |  |  | A new wooden pole was erected mid-span between Buninyong-P211 and P211A . During the night strong winds have pushed conductors against this pole (conductors had not yet been tied to insulators / pole undressed) resulting in pole catching fire. There was no ground fire and no injuries as a result of this incident. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | BAS022 | Error of Judgement - works incomplete due to Storm conditions | Pole-top fire | 43443.2292 | 1 | Negligible: no ground fire | 10422 | Public space |  | 20180913PWA_01 | Infrastructure (network-based) | -37.7051 | 143.9809 | 1 | Powercor | Report | 17606 | 0.0067824 | 22kV AC | Ballarat Aerodrome | 3352 | Clarendon | Conductor
On arrival supply isolated and repairs undertaken. | 49 LINTON-NARINGHIL ROAD, LINTON VIC 3360 | 30009044 |  | Wind;MEC;Dead | [5 empty] | A tree fell down across conductors between Lintonpark P1 & P2. The conductor on the ground has caused grass and dead tree to ignite resulting in a small fire about 3m2 area burnt. There was no injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | BAS021 | Vegetation: Trees Incident | Grassfire | 43443.4167 | 1 | Localised: less than 10 sq.m | 10423 | Agricultural |  | 20180913PWA_02 | Infrastructure (network-based) | -37.699 | 143.559 | 1 | Powercor | Report | 17435 | 0.017486 | 22kV AC | Ballarat Aerodrome | 3360 | Linton | Trees
The faults crew proceeded to replace the FOLCB and attached services with supply restored to all customers supplied from "Sudholz-Bennett" substation after 3 x 200amp LV fuses were replaced. | 16 SUDHOLZ STREET, BITTERN VIC 3918 | 8823764 |  |  |  | Overheated connection |  |  | 1 | The CFA reported a pole fire in Sudholz Street, Bittern and callers advise they have lost their electricity supply. A pole mounted three phase FOLCB that contained an underground service that supplied 16 and 18 Sudholz Street caught on fire and melted the service cables under the crossarm at pole No. LIS 8823764. The fire damaged FOLCB subsequently fell to the ground and caused a 6msq grass fire. The cause was unknown but most likely a loose connection that overheated. | Connection box | 0 | 0 | 0 |  |  | The cause was unknown but most likely a loose connection that overheated. | Grassfire | 43352.7833 | 1 | Localised: less than 10 sq.m | 10434 | Residential |  | 20180916UTD_06 | Infrastructure (network-based) | -38.3375 | 145.175 | 1 | United Energy Distribution | Report | 13185 | 0.015913 | Low voltage AC (<1kV) | Moorabbin Airport | 3918 | Bittern | Connection
On arrival crew isolated supply and carried out repairs | 1909 DOGWOOD ROAD, MURRA WARRA VIC 3401 | 32104928 | Working too close to overhead lines | [5 empty] | 1 | A crane truck (working on a Wind Farm construction site) while traversing with a suspended load struck a SWER overhead conductor. The conductor was broken resulting in a substation pole snapping and falling to ground. There was no fire start, no reported injuries or third party property daqmage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | HSM005 | Crane truck struck conductor | Loss of supply;No Go Zone (contact);Damage to network assets | 13/09/2018 13:58 |  |  | 10435 | Roadway |  | 20180917PWA_01 | Infrastructure (network-based) | -36.4259 | 142.2913 | 1 | Powercor | Report | 13196 | 0.0038657 | 12.7kV AC (SWER) | Horsham Aerodrome | 3401 | Murra Warra | Vehicle
On arrival crew isolated supply and carried out repairs. | 100 OCONNELL ROAD, MERRIMU VIC 3340 | 33072519 |  |  |  | Overheated connection |  |  |  | A passerby reported pole in front of this premise is on fire. Upon arrival the crew had found that the Pole Box/FOLCB opposite, 100 Oconnell Road, Merrimu, had overheated, causing the FOLCB to melt and burn away. The resultant hot melted plastic from the FOLCB above had fallen onto the ground below causing a small grass fire near the base of the pole approximately 50mÂ² total area. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BMH006 | connection failure | Loss of supply;Grassfire;Damage to network assets | 14/09/2018 18:17 | 1 | Small: 10 - 1000 sq.m | 10438 |  |  | 20180918PWA_01 | Infrastructure (network-based) | -37.6562 | 144.4639 | 1 | Powercor | Report | 13199 | 0.033684 | Low voltage AC (<1kV) | Laverton Raaf | 3340 | Merrimu | Connection
On arrival crew isolated supply damaged conductors replaced. LEI attended to investigate potential damage. | 148 LOWAN AVENUE, RED CLIFFS VIC 3496 | 30096459 |  | Blown branch/vegetation | [5 empty] | During strong winds a Tree branch has broken and rested on the LV conductors below. The active conductors were in contact with the neutral circuit for some undetermined time resulting in suspected damage to customers switch boards. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | RCT022 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 15/09/2018 15:16 |  |  | 10439 | Agricultural |  | 20180918PWA_02 | Infrastructure (network-based) | -34.3314 | 142.1617 | 1 | Powercor | Report | 13495 | 0.036678 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | Trees
Supply isolated. Earthing system repaired | 724 SPRINGHILL ROAD, SPRING HILL VIC 3444 | 30309236 | Working too close to underground cables |  |  |  | Ineffective planning/procedures/processes |  |  | While excavation around a SWER isolating substation the crew inadvertently made contact with the SWER earth line as they approached too closely to the earth and in so doing severed it. The Earth was previously located with a locator and marked. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | WND024 | Excavation too close to earth | Loss of supply;No Go Zone (contact) | 43199.6431 |  |  | 10443 | Roadway |  | 20180918PWA_03 | Infrastructure (network-based) | -37.3148 | 144.3525 | 1 | Powercor | Report | 13306 | 0.039104 | Earthing cable | Bendigo Airport | 3444 | Spring Hill | Vehicle
On arrival crew isolated supply and carried out repairs. | 1310-1334 LEAKES ROAD, ROCKBANK VIC 3335 | 30108618 | Vandalism;Copper theft | [6 empty] | Customer reported outage. On arrival the crew observed that an unknown person has cut right through, possibly with an axe or cutter of some type, the 4/c 35mm LV UG Service Cable on the pole at approximately 1.5m from ground level. The Service Cable was LIVE upon arrival, with the top section connected to the FOLCB above and the bottom section lying on the grassed area below. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | MLN021 | Theft and Vandalism | Loss of supply;Damage to network assets | 15/09/2018 1:25 |  |  | 10448 |  |  | 20180920PWA_01 | Infrastructure (network-based) | -37.7391 | 144.6512 | 1 | Powercor | Report | 13320 | 0.02389 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply and carried out repairs. | 335 TYNTYNDER CENTRAL ROAD, TYNTYNDER VIC 3586 | 32156894 |  |  |  | Leakage |  |  |  | Vic-fire reported pole fire at incident location, upon arrival found that a cross-arm fire had commenced at the HV kingbolt position of an intermediate substation pole. The CFA extinguished the fire using an interrupted spray, stopping the fire prior to the cross-arm failing. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 18/09/2018 21:39 | 1 | Negligible: no ground fire | 10450 | Roadway |  | 20180920PWA_03 | Infrastructure (network-based) | -35.2515 | 143.5367 | 1 | Powercor | Report | 13217 | 0.036363 | 22kV AC | Swan Hill Aerodrome | 3586 | Tyntynder | Crossarm
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Connection Box located at the Reticulation Pole. The attending Powercor Fault Crew replaced the existing O/H Single Phase Twisted Aluminium Service Cable and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 65 POPLAR AVENUE, SHEPPARTON VIC 3630 | 33097605 |  |  |  | Corrosion |  | Phase to earth |  | Mr Domenic Lagana was in the Bathroom showering when he received an electric shock as he made simultaneous contact with one hand on the metallic water tap and his bare feet whilst standing on the metallic waste water outlet in the shower base. | Connection box | 2 | 2 | 2 |  | STN021 | Corroded neutral connection | Minor shock | 43260 |  |  | 10453 | Roadway |  | 20180924PWA_01 | Infrastructure (network-based) | -36.3989 | 145.4171 | 1 | Powercor | Report | 13220 | 0.011377 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA, The attending Powercor Fault Crew reterminated the broken O/H Service Neutral Conductor at the Three Point Mains Connection Box located at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 99 LAURA AVENUE, BELMONT VIC 3216 | 31011327 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr Jamie Erving was in the Kitchen washing dishes when he received an electric as he made simultaneous contact with one hand on the metallic Kitchen Tap and his other hand on the metal sink. | Service conductor | 2 | 2 | 2 |  | GCY014 | Broken connection | Minor shock | 43321.4167 |  |  | 10454 | Residential |  | 20180925PWA_01 | Infrastructure (customer connection) | -38.179 | 144.3271 | 1 | Powercor | Report | 13221 | 0.039227 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 10 HIGGINS COURT, BREAKWATER VIC 3219 | 32069116 |  |  |  | Corrosion |  | Phase to earth |  | Ms Sue Pope was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hands on the shower taps and her bare feet whilst standing on the wet shower base. | Service conductor | 2 | 2 | 2 |  | GLE032 | Corroded service | Minor shock | 24/09/2018 0:00 |  |  | 10460 | Residential |  | 20180926PWA_02 | Infrastructure (network-based) | -38.1762 | 144.3794 | 1 | Powercor | Report | 13227 | 0.041572 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Breakwater | OH Cable
On arrival crew isolated supply and carried out repairs. | 11-23 KHARTOUM STREET, RICHMOND VIC 3121 | 30303273 | Working too close to underground cables | [6 empty] | A contractor dug-up LV UG cable at the incident location. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | NR002 | Excavation work | Loss of supply;No Go Zone (contact) | 17/09/2018 7:45 |  |  | 10461 | Construction |  | 20180926PWA_03 | Infrastructure (network-based) | -37.8253 | 145.0118 | 1 | CitiPower | Report | 13228 | 0.03011 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Dug up
Fault crew dispatched Fire was out on arrival. Checked in with customer upon arrival and they were safe and no damage was done to live stock. | 220 CASTELLA ROAD, CASTELLA VIC 3777 | 1400651 |  | Blown branch/vegetation |  |  |  | Phase to phase |  | IMS 234509 - Report of a ground fire in the vicinity of AusNet assets as a result of a tree branch coming in contact with the LV bushings of a transformer. | Transformer | 0 | 1 | 0 |  | KLK1 | Vegetation: Trees Incident | Grassfire | 17/07/2018 14:24 | 1 | Small: 10 - 1000 sq.m | 10462 |  |  | 20180926SPN_01 | Infrastructure (network-based) | -37.5122 | 145.426 | 1 | AusNet Services Distribution | Report | 17912 | 0.025561 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3777 | Castella | Trees
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | CARLINGA DRIVE, VERMONT VIC 3133 | 7031165 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 1 | Per MFB - Wires are sparking and tree is on fire caused by a truck hitting a tree. Customers who reside in Carlinga Drive advised of a loss of supply. A truck struck a council tree located on the corner of Carlinga Drive and Devlin Street that caused a branch to make contact with the HV overhead conductors near pole No. LIS 7031165 and two HV fuses to operate at the spur fusing at BH1396 located in Carlinga Drive. | Conductor (bare) | 0 | 0 | 0 |  | RWT 35 | Vegetation: Trees Incident | Other vegetation | 25/09/2018 11:53 | 1 | Negligible: no ground fire | 10484 | Roadway |  | 20181002UTD_01 | Infrastructure (network-based) | -37.8415 | 145.2002 | 1 | United Energy Distribution | Report | 18396 | 0.020991 | 22kV AC | Moorabbin Airport | 3133 | Vermont | Vehicle
On arrival crew confirmed site safe | 240 DORCAS STREET, SOUTH MELBOURNE VIC 3205 | 30344001 | Working too close to overhead lines | [5 empty] | 1 | A Fault crew were patrolling following a successful Auto Reclose on AP-6 Feeder. They narrowed the area down to a small section near the incident location, where they were then approached by a person from the construction site at the incident location, who informed them that a piece of pipe hand rail had made contact with the 11kV HV conductors in the street. The construction crew onsite informed the Fault crew that they had already had the person involved checked by an ambulance including an ECG and given the all clear. They also said that they had called Worksafe and ESV, and quoted ESV reference No10563847. There was no fire or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | AP006 | Dislodged hand rail. It is unclear if the hand rail dislodged or was moved. | No Go Zone (contact) | 43169.6465 |  |  | 10502 | Roadway |  | 20181004PWA_02 | Infrastructure (network-based) | -37.8332 | 144.9595 | 1 | CitiPower | Report | 13289 | 0.012492 | 11kV AC | Essendon Airport | 3205 | South Melbourne | Other
On arrival crew isolated supply and carried out repairs. No evidence of high load onsite | 26 BRAEBURN PLACE, WERRIBEE VIC 3030 | 30117963 | Vehicle | [6 empty] | A customer reported wire on ground. A crew attended and suspect a high load has struck and broken 3 LV conductors on the cnr of Braeburn and Brousard St's, Werribee. Red phase LV conductor was stall aloft but with reduced clearance over road. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE023 | Suspect high load | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/09/2018 10:44 |  |  | 10506 | Roadway |  | 20181004PWA_05 | Infrastructure (network-based) | -37.9236 | 144.6323 | 1 | Powercor | Report | 13292 | 0.023376 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
On arrival the crew arranged isolation of supply and carried out repairs. There was suspicion of HVI but tests by LEI found none. | 537 BALLARAT ROAD, ALBION VIC 3020 | 30113459 | Vehicle | [5 empty] | 1 | Report received of pole hit by car at the incident location. On arrival crew found a vehicle had collided with a public lighting pole, which fell and contacted the 22kv fdr. The feeder operated to lockout. There was no fire. | Pole (steel) | 2 | 2 | 2 |  | SSE014 | Vehicle struck pole . | Loss of supply;Damage to network assets | 43230.4535 |  |  | 10537 | Roadway |  | 20181015PWA_05 | Infrastructure (network-based) | -37.7763 | 144.8204 | 1 | Powercor | Report | 13341 | 0.026472 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Albion | Vehicle
On arrival crew carried out repairs | 490-528 COBURNS ROAD, KURUNJANG VIC 3337 | 30315247 | Copper theft | [6 empty] | Report received of disturbed underground cables and missing pit lids. On arrival crew found that pit lids had been opened and public lighting cable disturbed or stolen. Seven pits were found disturbed around the incident location . There was no fire, no reported injuries or third party paroperty damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN014 | Copper theft, Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43322.4972 |  |  | 10540 | Roadway |  | 20181016PWA_01 | Infrastructure (network-based) | -37.6551 | 144.5738 | 1 | Powercor | Report | 13347 | 0.021963 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Other
United Energy management was notified and ESV (Sam) advised. The LV circuit supplied from "Darling-Dandenong" substation along with the double circuit 22kV HV conductors was isolated whilst the Worksafe investigation took place and to enable the safe dismantling of the top section of scaffolding. Supply was restored at 12.15AM the following morning. | 1060 DANDENONG ROAD, CARNEGIE VIC 3163 | 2333479 | Working too close to overhead lines;Vehicle | [5 empty] | 1 | Caller reports that a truck has contacted on-site scaffolding for the building site and brought it down on the powerlines. A Kenworth truck making deliveries made contact with scaffolding at the construction site caused it to fall and make contact with the LV overhead conductors supplied from "Darling-Dandenong" indoor substation. No shocks, injuries or damage to plant occurred and Worksafe were in attendance. A Permit to Work (PTW) was on issue for the No Go Zone activities and the scaffolding was clear of the HV/LV conductors prior to being struck with hoarding in place as a further engineering control. In addition, there were protective "tiger battens" on the LV blue phase conductor as part of the PTW conditions. LV fuses operated at ""Darling-Dandenong" substation and there some some LV conductor damage due to clashing when the scaffolding made contact. | Conductor (bare) | 0 | 0 | 0 |  |  | A Kenworth truck making deliveries made contact with scaffolding at the construction site that caused it to fall and make contact with the LV overhead conductors. | Loss of supply;No Go Zone (contact) | 13/10/2018 13:40 |  |  | 10551 | Construction |  | 20181018UTD_01 | Infrastructure (network-based) | -37.884 | 145.056 | 1 | United Energy Distribution | Report | 13358 | 0.028979 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | Vehicle
The indoor substation was secured and the site left safe. | 560 CLAYTON ROAD, CLAYTON SOUTH VIC 3169 |  | Unauthorised access;Copper theft | [5 empty] | 2 | REC on site states the onsite substation has been vandalised and they have lost part of their electricity supply after wires had been cut. Unknown persons had gained entry by cutting away the gate mesh fence at "Clayton N560 - Osborne" indoor substation. They opened the fused isolators possibly with a broom or similar, and proceeded to remove the consumers copper underground cables. It appeared that no electric shocks or injuries were sustained. | Conductor (insulated);Copper;Indoor | 0 | 0 | 0 |  | SS21 | Unknown persons had gained entry into the indoor substation and proceeded to remove the consumers copper underground cables. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/10/2018 11:00 |  |  | 10552 | Industrial |  | 20181018UTD_02 | Infrastructure (network-based) | -37.9434 | 145.1164 | 1 | United Energy Distribution | Report | 13359 | 0.0065694 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Other
The 10amp EDO fuse was replaced and supply restored to the customer. | 2216 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 |  |  | Precipitation |  |  |  |  | 2 | Caller reports an all supply failure at 2216 Mornington-Flinders Road, Flinders. A 10amp HV EDO fuse candled at "Mtn-Flind P7 Boyds" single phase pole type substation. The cause was attributed to the closeness of Bass Strait and possible salt borne contaminants. | EDO fuse | 0 | 0 | 0 |  | DMA23 | The cause was attributed to the closeness of Bass Strait and possible salt borne contaminants. | Hung-up fuse only;Plant/equipment | 16/10/2018 9:28 | 1 | Negligible: no ground fire | 10553 | Roadway |  | 20181018UTD_03 | Infrastructure (network-based) | -38.4626 | 144.9942 | 1 | United Energy Distribution | Report | 18140 | 0.030131 | 22kV AC | Moorabbin Airport | 3929 | Flinders | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. | 42 SALMON STREET, HASTINGS VIC 3915 | 1109493 |  | Precipitation;Prone to salt deposition |  | Leakage |  |  |  | Caller from 42 Salmon Street states there was a small fire at the top of the pole. The fire is out but now they have dim lights. At the same time, a number of meters connected to "Salmon-Warranquite" substation commenced to communicate low volts below 180v. During light drizzly rain, a pole fire occurred on a HV strain crossarm with a LV termination crossarm attached on pole No. LIS 1109493 located opposite 42 Salmon Street. The staked pole was burnt behind the LV crossarm king bolt with tracking identified from the HV crossarm to the LV arm. The pole was severely damaged and required replacement and the probable cause was attributed to the closeness of Western Port Bay and salt borne contaminants. | Pole (wood);Pole top | 0 | 0 | 0 |  | HGS32 | The probable cause was attributed to the closeness of Western Port Bay and salt borne contaminants. | Pole-top fire | 16/10/2018 20:29 | 1 | Negligible: no ground fire | 10557 | Residential |  | 20181018UTD_04 | Infrastructure (network-based) | -38.3168 | 145.1939 | 1 | United Energy Distribution | Report | 13437 | 0.0041181 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Crossarm
On arrival crew isolated supply and commenced repairs. An LEI was assessing for HVI damage. | 22 ISABELLA STREET, GEELONG WEST VIC 3218 | 33045918 |  | Bird |  |  |  |  | 1 | Powercor Fault crews patrolling following a feeder outage and Customer calls, found that a large fruit bat had caused a flashover at the incident location. This resulted in a HV conductor falling onto the White phase of the LV conductors below. A HV Injection to multiple customers resulted , the full extent of the damage still being investigated. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | GL023 | Bird Incident | HV injection;Loss of supply;Damage to network assets | 17/10/2018 21:30 |  |  | 10561 | Roadway |  | 20181019PWA_02 | Infrastructure (network-based) | -38.133 | 144.3472 | 1 | Powercor | Report | 13369 | 0.00021991 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3218 | Geelong West | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor of an Aluminium Neutral Screened Service Cable . The attending Powercor Fault Crew replaced the O/H Multi Phase Aluminium Neutral Screened Service Cable and the Termination Devices and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 3 4 ERSKINE STREET, SHEPPARTON VIC 3630 | 31028313 |  |  |  | Corrosion |  | Phase to earth |  | Ms Kirsty Naylor was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metallic Shower Tap and her bare feet whilst standing on the wet metallic waste water outlet in the shower base. | Service conductor | 2 | 2 | 2 |  | SHN012 | corroded service neutral | Minor shock | 43110 |  |  | 10562 | Residential |  | 20181019PWA_03 | Infrastructure (network-based) | -36.3719 | 145.3971 | 1 | Powercor | Report | 13370 | 0.0074259 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | OH Cable
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | GLADYS STREET, NUNAWADING VIC 3131 | 7032815 | Recreation - Helium (party) balloons |  |  | Insulator |  |  | 1 | At 1320hrs on 27/09/2018, 22kV feeder circuit breaker NW 21 successfully reclosed and held. Caller reports of a pole fire in Gladys Street. A bunch of helium balloons contacted the HV overhead conductors at pole No. LIS 7032815 on the corner of Gladys Street and Closter Avenue that caused damage to the HV disc insulators and two HV termination crossarms that required replacement. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | NW 21 | Helium balloons made contact with the 22kV overhead conductors causing a flash over. | Pole-top fire | 27/09/2018 13:20 | 1 | Negligible: no ground fire | 10563 | Residential |  | 20181019UTD_02 | Infrastructure (network-based) | -37.812 | 145.174 | 1 | United Energy Distribution | Report | 13371 | 0.016775 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Other
The faults crew deemed the pole was load worthy but requires replacement at the earliest opportunity. Traffic control will be required for the pole replacement due to the busy location on Neerim Road. | 396 NEERIM ROAD, CARNEGIE VIC 3163 | 2327331 |  | Precipitation |  | Leakage |  |  |  | Per MFB - Pole fire. During light rain, a pole fire occurred on the pole with a HV timber strain cross arm with 11kV HV isolators (OA5122) and LV offset intermediate cross arm construction attached on pole No. LIS 2327331 located outside 396 Neerim Road. The staked pole was burnt behind the LV cross arm and requires replacement. The probable cause was attributed to tracking due to the light rain at the time of the event. | Pole (wood);Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | EM 10 | The cause was attributed to tracking due to the light rain at the time of the event. | Pole-top fire | 20/10/2018 10:51 | 1 | Negligible: no ground fire | 10565 | Commercial |  | 20181022UTD_01 | Infrastructure (network-based) | -37.89 | 145.0651 | 1 | United Energy Distribution | Report | 13374 | 0.021711 | 11kV AC | Moorabbin Airport | 3163 | Carnegie | Pole
Fault crews attended site to isolate the faulted equipment and complete repairs. Cable replaced with Bare Conductor | 60 HARCOURT ROAD, ALTONA VIC 3018 | 30236687 |  |  |  | Electrical breakdown |  |  | 1 | A fault on the LVN22 feeder at 12:32 caused a feeder trip. A grass fire adjacent to pole LIS 994554 outside 70-72 Harcort Road, Altona was ignited when a high voltage ABC overhead cable (Non-metallic screened) faulted, then to fell onto the ground. There was no reported injuries or third party property damage. | Conductor (ABC) | 2 | 2 | 2 |  | LVN022 | Arcing caused by insulation deterioration | Grassfire | 22/10/2018 12:32 | 1 | Small: 10 - 1000 sq.m | 10568 | Roadway |  | 20181023PWA_01 | Infrastructure (network-based) | -37.8487 | 144.7809 | 1 | Powercor | Report | 17440 | 0.034488 | 22kV AC | Laverton Raaf | 3018 | Altona | OH Cable
On arrival crew extinguished fire. no conductor damage observed | KOROROIT CREEK ROAD, ALTONA VIC 3018 | 32173435 |  |  |  | Conductor clashing |  |  | 1 | An ABC conductor faulted and fell to ground outside 60 - Harcort Road, Altona. Secondary fault currents caused clashing of conductors adjacent to Kororoit creek rd which ignited two small grass fires on the nature strip. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | LVN022 | Secondary fault current from ABC conductor fault | Grassfire | 22/10/2018 12:32 | 1 | Small: 10 - 1000 sq.m | 10569 | Public space |  | 20181023PWA_02 | Infrastructure (network-based) | -37.8446 | 144.7884 | 1 | Powercor | Report | 13380 | 0.034694 | 22kV AC | Laverton Raaf | 3018 | Altona | Conductor
Damage area isolated repairs made and supply restored. | 176 WERRIBEE VALE ROAD, MADDINGLEY VIC 3340 | 31030445 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | An excavator traversing along defined track contacted a phase of the high voltage overhead line adjacent Myrniong-P21. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BMH003 | Excavator traversing track | Loss of supply;Damage to network assets | 22/10/2018 10:45 |  |  | 10570 | Agricultural |  | 20181023PWA_03 | Infrastructure (network-based) | -37.6771 | 144.4109 | 1 | Powercor | Report | 13382 | 0.017845 | 22kV AC | Avalon Airport | 3340 | Maddingley | Vehicle
The crossarm was replace and the conductor repaired. | 113 SIMPSON STREET, EAST MELBOURNE VIC 3002 | 30205809 |  |  |  | Rot |  |  | 1 | VicFire notified CitiPower of a conductor on the ground on the corner of Gipps and Simpson Streets, East Melbourne. On arrival the crew found an LV crossarm had failed allowing one conductor to fall to ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | MP055 | Crossarm failure | Loss of supply;Damage to network assets | 21/10/2018 16:20 |  |  | 10571 | Roadway |  | 20181023PWA_04 | Infrastructure (network-based) | -37.8134 | 144.9882 | 1 | CitiPower | Report | 13383 | 0.020251 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Crossarm
On arrival crew isolated supply and arranged for repairs to be done. | 28-32 BROOKLYN PARK DRIVE, BROOKFIELD VIC 3338 | 30112005 | Vandalism;Copper theft | [5 empty] | 2 | A passer-by reported cables on the ground at the incident location. upon arrival, the Powercor crew found that a service cable from the pole to house had been stolen. The pit and the fuse board were vandalised. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN022 | Copper theft & vandalism | Loss of supply;Damage to network assets | 16/10/2018 14:34 |  |  | 10572 | Roadway |  | 20181023PWA_05 | Infrastructure (network-based) | -37.6974 | 144.5256 | 1 | Powercor | Report | 13384 | 0.0079734 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew made arrangements to access meter position. Supply isolated at pit. | 68-88 SINCLAIRS ROAD, DEANSIDE VIC 3336 | 30105360 | Working too close to underground cables;Unauthorised work | [6 empty] | Report received of damaged service cable When digging holes it appears that post hole digger has become entangled with underground service cable. This entanglement has caused damage to meterboard and fuses. It is unclear exactly when this interference occurred. There was no fire, no reported injuries | Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | MLN021 | Post hole digger | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 14/10/2018 10:39 |  |  | 10576 | Commercial |  | 20181025PWA_01 | Infrastructure (network-based) | -37.727 | 144.7088 | 1 | Powercor | Report | 13391 | 0.022021 | Low voltage AC (<1kV) | Melbourne Airport | 3336 | Deanside | Dug up
On arrival crew isolated supply and carried out repairs | 101 DOUGHERTIES ROAD, PORTLAND WEST VIC 3305 | 32134359 | Working too close to overhead lines | [5 empty] | 1 | Customer reported contractor (Rons Bobcats, Portland) was removing tree which fell onto line and brought it down. On arrival crew found one conductor of a single phase span between pole 6&7 had been broken and brought to ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | PLD006 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact);Damage to network assets | 24/10/2018 16:46 |  |  | 10577 | Agricultural |  | 20181025PWA_02 | Infrastructure (network-based) | -38.3366 | 141.5425 | 1 | Powercor | Report | 13393 | 0.014716 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland West | Other
On arrival crew isolated supply and carried out repairs | 113 BURNLEY STREET, RICHMOND VIC 3121 | 30193328 | Vehicle | [6 empty] | An unidentified truck pulled down service cable. On arrival the crew found service one meter above the roadway. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | RTS-CW | Vehicle struck service | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/10/2018 14:30 |  |  | 10578 | Roadway |  | 20181026PWA_01 | Infrastructure (network-based) | -37.8158 | 145.0089 | 1 | CitiPower | Report | 13395 | 0.041495 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Vehicle
On arrival crew isolated supply and carried out repairs. | 2491 BACCHUS MARSH-BALLIANG ROAD, ROWSLEY VIC 3340 | 30348941 | Vandalism;Copper theft | [6 empty] | Passer by reported black cover down the bottom has come off and wires exposed. On arrival crew found attempted copper theft and vandalism to underground public lighting services There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BMH005 | Copper theft & vandalism | Loss of supply;Damage to network assets | 19/10/2018 15:20 |  |  | 10580 | Roadway |  | 20181026PWA_03 | Infrastructure (network-based) | -37.7386 | 144.3917 | 1 | Powercor | Report | 13397 | 0.0045995 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Rowsley | Other
A voltage test between the tap and the conductive metallic shower screen resulted with 27 Volts and various points of the installation with reference to an independent earth including the distribution assets revealed the service neutral conductor was damaged. Powercor linesman repaired the service neutral & CTA carried out N.S.T & Voltage tests following the repairs and normal results were obtained. | 1 SERPENTINE COURT, WERRIBEE VIC 3030 | 30109645 |  |  |  | Corrosion |  | Phase to earth |  | Russell received an electric shock when he simultaneously contacted the metallic tap with one hand and the metallic shower base trap with his foot. | Service conductor | 2 | 2 | 2 |  | WBE032 | Service neutral connection | Minor shock | 13/10/2018 14:00 |  |  | 10584 |  |  | 20181030PWA_01 | Infrastructure (network-based) | -37.8852 | 144.6619 | 1 | Powercor | Report | 13403 | 0.039074 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | OH Cable
On arrival crew isolated supply and carried out repairs. | BALD HILLS ROAD, CRESWICK VIC 3363 | 30014934 | Vandalism;Copper theft | [5 empty] | 2 | An asset Inspector reported a Substation pole had the LV earth Stolen. On arrival the fault crew found that the LV earth on the substation had been removed by an unknown persons. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | BAN009 | Copper theft | Damage to network assets | 19/10/2018 14:00 |  |  | 10585 | Roadway |  | 20181031PWA_01 | Infrastructure (network-based) | -37.424 | 143.8562 | 1 | Powercor | Report | 13406 | 5.9028e-05 | Earthing cable | Ballarat Aerodrome | 3363 | Creswick | Other
Removed service and disconnected at pole, issued defect for broken BTS pole. | 41 FABIO COURT, CAMPBELLFIELD VIC 3061 |  | Vehicle | [5 empty] | 2 | Live service wire on ground after BTS pole broke. | Aluminium twisted (grey) | 2 | 2 | 2 |  |  | Service wire hit by vehicle causing BTS pole to snap and resulting in live wire falling on nature strip. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43111.4458 |  |  | 10590 | Commercial |  | 20181101JEM_01 | Infrastructure (network-based) | -37.6768 | 144.952 | 1 | Jemena | Report | 13413 | 0.01761 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Vehicle
Fault crew dispatched | 1 KALPARRIN AVENUE, GREENSBOROUGH VIC 3088 | LIS903803 and LIS903804 | Vehicle |  |  |  |  | Phase to earth |  | E0004005 - Truck contacted and brought down OH LV lines resulting in ground fire. | Conductor (bare) | 0 | 0 | 0 |  | WT5 | Unknown truck contacted and brought down O/H LV lines resulting in ground fire. Truck and driver details unknown and not available. It is not known what the truck was doing when it contacted the O/H conductor | Grassfire | 31/10/2018 12:40 | 1 | Small: 10 - 1000 sq.m | 10592 | Public space |  | 20181101SPN_01 | Infrastructure (network-based) | -37.6999 | 145.1027 | 1 | AusNet Services Distribution | Report | 14972 | 0.014899 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | Vehicle
On arrival crew inspected pole for damage. | MORTLAKE-ARARAT ROAD, ROSSBRIDGE VIC 3377 | 33049204 |  | Bird |  |  |  |  | 1 | Vic Fire reported a grass fire at the incident location. On arrival the fault crew found that a bird had flashed over a 22kV insulator, attached to a steel crossarm on a concrete pole. | Conductor (bare);Crossarm (steel);Pole (concrete) | 2 | 2 | 2 |  | ART033 | Bird Incident | Grassfire | 43111.8681 | 1 | Medium: 1000 sq.m - 10 ha | 10597 | Roadway |  | 20181102PWA_04 | Infrastructure (network-based) | -37.4972 | 142.8466 | 1 | Powercor | Report | 13422 | 0.021226 | 22kV AC | Hamilton Airport | 3377 | Rossbridge | Animal
A Zinfra substation crew attended and completed repairs to secure the site. The lock was repaired and an additional lock fitted to the substation door to deter further break-ins. There is another indoor substation at the large industrial development and an additional lock was also fitted to "Oak-Willow" substation as a precaution. The site project manager engaged a REC and a SILV was issued on the customer cables at both indoor substations. | 1-5 LAKE DRIVE, DINGLEY VILLAGE VIC 3172 |  | Unauthorised access;Copper theft |  |  | Fault on customer installation |  |  | 2 | Zinfra notified United Energy that an indoor substation at 3 Lake Drive, Dingley Village had been broken into. The doors have been damaged and the LV isolators have been opened and the customers LV copper cables stolen. A Zinfra No Go Zone assessor attended "Lake-Boundary" indoor substation for a underground cable location as the industrial site will be redeveloped over the next few months with the incoming LV and HV cables remaining alive. The No Go Zone assessor discovered the indoor substation had been broken into with the customers LV isolators opened by unknown persons and the customers un-metered copper cables cut and stolen. The police were notified and an investigation revealed the site was broken into at 3:17AM on 31/10/2018. It appeared that no electric shocks or injuries were sustained. | Cable;Copper;Indoor | 0 | 0 | 0 |  |  | Unknown persons broke into the live United Energy indoor substation and proceeded to cut and remove the consumers copper cables. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43111.375 |  |  | 10595 | Industrial |  | 20181102UTD_01 | Infrastructure (network-based) | -37.9804 | 145.1114 | 1 | United Energy Distribution | Report | 13419 | 0.010763 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3172 | Dingley Village | Other
On arrival crew isolated supply and carried out repairs. | 234 RUSSELL STREET, MELBOURNE VIC 3000 | 35415217 |  |  |  | Overheated connection |  |  |  | Multiple customers reported power outages on Belman Pl. On arrival it was found that a service box on a building wall had caught fire. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | WA035 | Moisture ingress | Plant/equipment | 43292.6944 | 1 | Negligible: no ground fire | 10608 | Roadway |  | 20181109PWA_01 | Infrastructure (customer connection) | -37.8112 | 144.9675 | 1 | CitiPower | Report | 13440 | 0.0042951 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Connection
Crew attended, investigated and replaced Krone Box. | 320 DOCKERTYS ROAD, WY YUNG VIC 3875 | LIS 1603550 |  |  |  | Corrosion |  |  |  | E0004423 - All Supply Failure reported, on arrival crew found burnt out kronebox and small grass fire approx. 4m x 4m | Connection box | 0 | 0 | 0 |  | BDL44 | Degradation of Krone Box | Grassfire | 43323.4688 | 1 | Small: 10 - 1000 sq.m | 10616 |  |  | 20181109SPN_02 | Infrastructure (network-based) | -37.826 | 147.5809 | 2 | AusNet Services Distribution | Report | 13450 | 0.027324 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Wy Yung | Connection
A faults crew remained on site until the substations group attends to replace the locks to the substation. The substation doors have been re-secured with heavy duty locks and an â€œALIVEâ€ sign placed on the door to remind unauthorised persons of the electrical dangers. | 1-5 LAKE DRIVE, DINGLEY VILLAGE VIC 3172 |  | Vandalism;Unauthorised access | [5 empty] | 2 | On site caller advised the substation at 3 Lake Drive, Dingley Village has been broken into again and the staples the crew put on last week to secure the doors have been removed. The doors are closed but not secured. The substation is near Lake Drive and Boundary Road. Refer to previous Incident Report 20181102UTD_01 provided to ESV where copper thieves had removed customers cables from the abandoned building at Lake Drive, Dingley. On this abandoned site that is being redeveloped, are two indoor substations - â€œOak-Willowâ€ and â€œLake-Boundaryâ€. Earlier today, unknown persons have pried open the steel substation doors of â€œLake-Boundaryâ€ substation but nothing was disturbed inside. The developer contacted the police who were onsite completing a report. The site is being redeveloped with 26 factories over the next 6 months and the long term plan is to use the two indoor substations to supply the factories. | Indoor | 0 | 0 | 0 |  |  | Unauthorised entry into indoor substation but nothing stolen. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43323.2917 |  |  | 10615 | Construction |  | 20181109UTD_05 | Infrastructure (network-based) | -37.9804 | 145.1114 | 1 | United Energy Distribution | Report | 13448 | 0.011712 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Other
A LEI and faults truck was dispatched to investigate the cause and an initial NST failed with 4.1ohm and 21v on the neutral and taps with load applied. The faults crew proceeded to check all connections but on obvious issues were identified. The faults crew replaced the neutral screen service and pole junction box between pole numbers LIS 8807999 and 18218770 with a XLPE service and connected directly onto the overhead reticulation. It was concluded the neutral screen service was in a deteriorated condition as electrical installation tests demonstrated the fault had been rectified with a NST pass and 1v measured on the neutral. It appears the high impedance in the service neutral impressed a voltage rise on the neutral which in turn impressed the same voltage rise on the earthing system due to the MEN connection in the MSB. This voltage rise on the earthing system impressed a voltage rise on the vanity taps due to the equipotential earthing connection to the water pipes within the installation and as a result, the occupier received an electric shock from the taps. The LEI confirmed the electrical installation was safe and supply was restored. | 48 LONSDALE AVENUE, HAMPTON EAST VIC 3188 | Between 8807999 and 18218770 |  |  |  | Electrical breakdown |  | Phase to earth | 2 | Meter number 00943189 communicated an unsafe situation and an automatic safety disconnect occurred with impedance measurement of 2.46ohm while a 90 day running impedance was 0.83ohm. Meter detected a potential safety issue with the customers electricity supply and a safety disconnect was performed as a precaution. The United Energy faults and emergencies call centre contacted the customer who also advised that she has experienced mild electric shocks from the bathroom taps and noticed some dimming of lights when appliances were switched on recently. | Services cable;Neutral screen | 0 | 0 | 0 |  |  | Defective aluminium neutral screen overhead service. | Minor shock | 43323.8333 |  |  | 10632 | Residential |  | 20181112UTD_02 | Infrastructure (network-based) | -37.9339 | 145.0287 | 1 | United Energy Distribution | Report | 13476 | 0.035197 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton East | OH Cable
Removed cable from pole to pit, site made safe. | 60 GREEN STREET, BULLA VIC 3428 |  | Vandalism;Copper theft | [5 empty] | 2 | Attempted copper theft of cabling down side of pole to UG pit. | Services cable;Services pit;Copper | 2 | 2 | 2 |  |  | Attempted copper theft, vandals cutting service cable from pole to pit in attempt to steal it. | Damage to network assets | 13/11/2018 11:37 |  |  | 10640 | Agricultural |  | 20181113JEM_04 | Infrastructure (network-based) | -37.632 | 144.8075 | 1 | Jemena | Report | 13487 | 0.040825 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
On arrival crew isolated supply and carried out repairs. | 179-193 COLAC ROAD, GROVEDALE VIC 3216 | 30068071 |  |  |  | Overheated connection |  |  | 2 | CFA reported wire down and arcing and sparking. On arrival crew found that a HV ampac connection had over heated. Hot debris fell to ground resulting in a small grassfire (60m2) | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | WPD012 | corrossion | Grassfire | 43445.8035 | 1 | Small: 10 - 1000 sq.m | 10638 | Roadway |  | 20181113PWA_02 | Infrastructure (network-based) | -38.2007 | 144.3128 | 1 | Powercor | Report | 13484 | 0.013426 | 22kV AC | Avalon Airport | 3216 | Grovedale | Connection
CTA/LEI performed voltage test from an independent earth spike to the neutral bar and earth bar of main switchboard Fault crew identified the exposed and corroded Neutral Screen conductor of the Neutral Screen Service cable just prior to the pole J Box. Crew replaced the service with a new 2 Wire ABC. Crew performed NST at the POA with a pass result recorded. CTA/LEI performed NST at the installation main switchboard with a pass result recorded. | 33 KANSAS AVENUE, BELL POST HILL VIC 3215 | 30067888 |  |  |  | Corrosion |  | Phase to earth |  | Sheldon was having a shower when he felt a slight tingle to his top lip when it touched the shower rose whilst brushing his teeth. He was standing bare foot on the shower base in the flow of water. | Service conductor | 2 | 2 | 2 |  | CRO022 | Corroded service | Minor shock | 28/10/2018 8:00 |  |  | 10639 | Residential |  | 20181113PWA_03 | Infrastructure (network-based) | -38.0956 | 144.3311 | 1 | Powercor | Report | 15472 | 0.037186 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | OH Cable
Crew attended, reconnected as CoES and EWR were on site | 397A BELMORE ROAD, BALWYN VIC 3103 | 30194456 | Caused by REC/contractor | [5 empty] | 2 | LEW called us asking for a reconnection job to be raised. The LEW advised that his boss told him to take the meter off and replace the meter panel and he was then calling us to get the meter put back on | Meter board (including fuses) | 0 | 0 | 0 |  | WD032 | Interference | Interference;Other | 19/10/2018 7:34 |  |  | 10648 | Residential |  | 20181115PWA_03 | Infrastructure (network-based) | -37.8032 | 145.1022 | 1 | CitiPower | Report | 13502 | 0.035031 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Other
The site was made safe overnight and the line crew and LEI returned the following day to remove all the affected assets and install a new POA and mains box to keep other impacted customer on supply. | 63 HIGH STREET, NORTHCOTE VIC 3070 | 30190553 | Building too close or within the No Go Zone | [5 empty] | 2 | A CitiPower line worker reported noticed a veranda had been removed and CitiPower assets had been left in an unsafe and unstable state. On attendance it was found that an unknown party had removed the veranda and cables, conduits, under veranda box and an asbestos conduit had been left crudely attached to the building. The cable that had been interfered with also fed through verandas to other premises. | Aluminium twisted (XLPE);Connector/termination | 0 | 0 | 0 |  | NC001 | Interference | Damage to network assets | 31/10/2018 12:00 |  |  | 10649 | Commercial |  | 20181115PWA_04 | Infrastructure (network-based) | -37.7806 | 144.9965 | 1 | CitiPower | Report | 13503 | 0.0074688 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored after 2 x 65amp Boric Acid HV fuses were replaced at the spur fusing at RB0398 located at Cherry Road. The 160amp LV red phase fuse was also replaced at "Cherry-Russel" substation that had also operated. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 38 CHERRY ROAD, RED HILL SOUTH VIC 3937 | 1308047 |  | Wind;Alive;Property owner/customer |  |  |  |  | 1 | During strong gusty winds, a private tree from a residence at 38 Cherry Road failed and fell over the high voltage overhead conductors. During strong winds, a private tree located at 38 Cherry Road broke and fell over the HV and LV conductors bringing the neutral conductor down to the ground at pole No. LIS 1308047. Electrical infrastructure was damaged and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Cherry-Russel" substation. The LEI confirmed a high voltage injection occurred (MOR 1803) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | DMA 15 | Vegetation: Trees Incident | HV injection;Loss of supply | 43352.15 |  |  | 10433 | Residential |  | 20180916UTD_05 | Infrastructure (network-based) | -38.3914 | 145.0137 | 1 | United Energy Distribution | Report | 13184 | 0.00088194 | 22kV AC | Moorabbin Airport | 3937 | Red Hill South | Trees
Fault crew dispatched. Found hung up fuse and no evidence of fire. Tube and fuse was replaced. | 13 HERITAGE DRIVE, BROADFORD VIC 3658 | LIS4718013 |  | Bird |  |  |  |  | 0 | Enablon E0001527 - Reported Pole Fire | EDO fuse | 0 | 0 | 0 |  | SMR3 | The EDO fuse had hung up due to mud in the bottom of the tube not releasing the blown fuse. The mud comes from wasps using the hollow of the tube as a good nesting site. When HV fuse link blew under fault conditions the tension of the fuse was unable to be released due to the build up of mud and failed to fall open. Fuse tube caused some arcing as reported by customer but this had ceased by the time the crew arrived. The tube was still fully whole with no burnt or burning parts falling to the ground. Tube and fuse was replaced. | Hung-up fuse only | 15/09/2018 6:30 |  |  | 10441 |  |  | 20180918SPN_02 | Infrastructure (network-based) | -37.2077 | 145.0639 | 2 | AusNet Services Distribution | Report | 13204 | 0.013678 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Broadford | Animal
On arrival crew arranged isolation of line and removed limb | 135 HENDY MAIN ROAD, GNARWARRE VIC 3221 | 32070631 |  | Within clearances | [5 empty] | CFA reported HV conductor contacting vegetation during high winds. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WPD011 | Vegetation encroachment | Loss of supply | 43413.9326 |  |  | 10444 | Roadway |  | 20180919PWA_01 | Infrastructure (network-based) | -38.1765 | 144.1874 | 1 | Powercor | Report | 13211 | 0.0093646 | 22kV AC | Avalon Airport | 3221 | Gnarwarre | Trees
The crew isolated supply to the address. The customers REC is required to carry out the necessary repairs | 41 WARRAK ROAD, ARARAT VIC 3377 | 31013981 |  |  |  | Fault on customer installation |  |  |  | Powercor received a report that a plumber had dug up an underground service cable at the incident location. On arrival the crew found that a plumber had been digging a trench for the installation of new water pipes at the above address and had struck and damaged the underground consumer mains on the customers property. There was no fire or reported injuries. | Customer installation | 2 | 2 | 2 |  | ART023 | Excavation works | Loss of supply | 13/09/2018 14:49 |  |  | 10445 | Residential |  | 20180919PWA_02 | Infrastructure (network-based) | -37.2729 | 142.9701 | 1 | Powercor | Report | 13212 | 0.03005 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Dug up
On arrival crew isolated supply and arranged repairs. | 702 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | 30185688 | Vehicle | [6 empty] | Vic Fire reported that a semi-trailer truck cut the corner on Footscray Rd, West Melbourne and hit pole LIS - 87593. The pole had snapped at the base causing it to lean on a 45 degree angle. Additionally 2 bays of the LV ABC was bought to ground from the broken pole. There was no fire, no reported injuries, no third party property damage. | Conductor (ABC) | 2 | 2 | 2 |  | DA026 | Truck struck pole | Damage to network assets | 13/09/2018 9:33 |  |  | 10447 | Roadway |  | 20180919PWA_04 | Infrastructure (network-based) | -37.8066 | 144.91 | 1 | CitiPower | Report | 13214 | 3.4722e-06 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Vehicle
ESV and worksafe advised | 556-558 LONSDALE STREET, MELBOURNE VIC 3000 | 30207472 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Customer requested a No go zone site visit to enable them to erect a gantry but upon supply of information from customer photos indicated parts of gantry already erected and warning tape fitted to public lighting cable crossing laneway and in extremely close proximity to erected gantry. Timing unknown | Conductor (covered uninsulated) | 0 | 0 | 0 |  | JA18 | interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/09/2018 14:00 |  |  | 10456 | Construction |  | 20180925PWA_03 | Infrastructure (network-based) | -37.814 | 144.9558 | 2 | CitiPower | Report | 13368 | 0.016236 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 202 DON STREET, BENDIGO VIC 3550 | 30026909 |  |  |  | Overheated connection |  |  |  | Emergency services reported a pole fire at incident location. On arrival crew found overheated LV connection had ignited part of the pole top.. There was no ground fire, no reported injuries or third party property damage. | Connector/termination;Connection box | 2 | 2 | 2 |  | BET002 | Corroded connection | Pole-top fire | 20/09/2018 19:15 | 1 | Negligible: no ground fire | 10464 | Roadway |  | 20180927PWA_02 | Infrastructure (network-based) | -36.7584 | 144.2683 | 1 | Powercor | Report | 13236 | 0.031392 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | Connection
On arrival crew isolated supply and carried out repairs | TARNEIT ROAD, TARNEIT VIC 3029 | 30106767 | Vandalism;Copper theft | [6 empty] | A field crew found attempted copper theft and vandalism at incident site. There was no ground fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | TNA023 | Copper theft & vandalism | Damage to network assets | 21/09/2018 17:01 |  |  | 10465 | Roadway |  | 20180927PWA_03 | Infrastructure (network-based) | -37.8187 | 144.6752 | 1 | Powercor | Report | 13238 | 0.018731 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs. | 171 WOODS ROAD, TRUGANINA VIC 3029 | 33103247 | Vandalism;Copper theft | [6 empty] | A field crew reported attempted copper theft and vandalism at incident location. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | LV002 | Copper theft & vandalism | Damage to network assets | 21/09/2018 17:01 |  |  | 10467 | Roadway |  | 20180927PWA_04 | Infrastructure (network-based) | -37.8215 | 144.7213 | 1 | Powercor | Report | 13241 | 0.028708 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. Clashing mitigation work is underway with a revisit to ACR MT7521 planned to determine if further animal proofing required. | FRANKSTON-FLINDERS ROAD, HASTINGS VIC 3915 | 1105560 |  | Animal |  | Conductor clashing |  |  | 1 | At 1959hrs on 11/09/2018, 22kV feeder HGS 33 circuit breaker reclosed to lockout. This resulted in 4,204 customers off supply for an average of 44 minutes. At the same time, 66kV feeder TBTS-DMA reclosed and held. A caller advised the United Energy faults and emergencies call centre that a transformer on the Frankston-Flinders Road near where it turns into Marine Parade at the railway line, blew up and was on fire. A possum made contact between the lightning arrestor connections and the ACR droppers at the supply side of ACR MT7521 located in Frankston-Flinders Road. This caused the 22kV and 66kV conductors to clash at pole No. LIS 1105560 and molten metal to fall into the grass below and a small 6sqm fire to start. In addition, lightning arrestors and HV fuses operated on 22kV feeder HGS 33 due to the 22kV conductors briefly making contact with the 66kV conductors. | Conductor (bare);Surge diverter | 0 | 0 | 0 |  | HGS 33 and TBTS-DMA | Animal Incident | Grassfire | 43413.8326 | 1 | Localised: less than 10 sq.m | 10471 | Roadway |  | 20180929UTD_04 | Infrastructure (network-based) | -38.2842 | 145.1885 | 1 | United Energy Distribution | Report | 13245 | 0.0015301 | 22kV AC;66kV AC | Moorabbin Airport | 3915 | Hastings | Animal
On arrival crew arranged isolation and repairs | 19 PAW PAW ROAD, BROOKLYN VIC 3012 | 30117783 |  |  |  | Overheated connection |  |  | 1 | Report from Fire services of pole fire and bin fire. There was also damage to a vehicle parked at the kerb. There was a ground fire (bin) . no reported injuries. | Disconnector/isolator | 2 | 2 | 2 |  | BLT016 | Connection on Switch failed | Loss of supply;Property | 24/09/2018 8:37 | 1 | Localised: less than 10 sq.m | 10477 | Roadway |  | 20181001PWA_02 | Infrastructure (network-based) | -37.8225 | 144.8344 | 1 | Powercor | Report | 17607 | 0.039727 | 22kV AC | Laverton Raaf | 3012 | Brooklyn | AF Other
Fault crew disptached to investigate and repair. Faulty transformer found to be at fault Transformer replaced | 73 MIRRABOOKA ROAD, MALLACOOTA VIC 3892 | LIS 1909076 |  |  |  | Defective component |  |  | 2 | Enablon E0002320 - Possible HVI reported | Transformer | 0 | 1 | 0 |  | CNR2 | Unknown Transformer fault was found to be the cause. Transformer replaced and issue resolved. | HV injection | 28/09/2018 17:19 |  |  | 10475 |  |  | 20181001SPN_01 | Infrastructure (network-based) | -37.5483 | 149.7502 | 2 | AusNet Services Distribution | Report | 13496 | 0.029296 | Low voltage AC (<1kV);22kV AC | Gabo Island Lighthouse | 3892 | Mallacoota | AF Other
A faults crew attended and deemed the site was safe but isolated the multiphase service at the pole end as a precaution. They suggested to wait for the abolishment request to be forwarded to United Energy as the builder was trying to short cut the system and potentially created an unsafe situation. 12/09/2018 - Greg Johnson (ESV) contacted United Energy and requested that supply is abolished to the property. The faults crew re-attended and removed the overhead service and the two meters at the property. | 18 LANDSCAPE COURT, BALNARRING VIC 3926 |  | Working too close to overhead lines | [5 empty] | 2 | Builder Steve advised they have demolished half of the building and are concerned the structure will not hold up in the strong wind and have requested the site is made safe. No abolishment request was received and the majority of the old occupancy had been demolished. The existing overhead service was left connected to the property and the builder was concerned that it may fall in strong winds. The meters remained in the enclosure but the majority of the wiring had been removed. | Service conductor | 0 | 0 | 0 |  |  | Abolishment had taken place with no contact with United Energy and a unsafe situation was created as a result. | No Go Zone (no contact) | 43413.5625 |  |  | 10472 | Residential |  | 20181001UTD_01 | Infrastructure (network-based) | -38.3698 | 145.1171 | 1 | United Energy Distribution | Report | 13246 | 0.025101 | Low voltage AC (<1kV) | Moorabbin Airport | 3926 | Balnarring | Other
A faults truck attended and had no option but to remove the meters that were hanging off the wall, along with the main switch board and disconnected the consumers mains from the under veranda fuse break. The crew took photos and requested the unsafe abolishment activities are provided to ESV and/or Worksafe. | 2A MACKIE ROAD, BENTLEIGH EAST VIC 3165 |  | Misadventure | [5 empty] | 2 | REC (Will 0447 326 103) advised that a builder has called him to a job where the builder has commenced demolishing a wall that has the switchboard installed on it and the metering is now exposed. The shop is on the corner of 929 Centre Road and 2A Mackie Street and the REC and builder will remain on site. No abolishment request was received and the old premise was partially demolished that left an unsafe environment. The builder was trying to short cut the system with no contact made with United Energy until the abolishment work commenced. | Switchboard;Meter board (including fuses) | 0 | 0 | 0 |  |  | Builder had commenced an abolishment prior to the isolation of supply and the removal of the metering equipment. | Damage to network assets | 21/09/2018 13:30 |  |  | 10481 | Construction |  | 20181001UTD_07 | Infrastructure (network-based) | -37.9226 | 145.0735 | 1 | United Energy Distribution | Report | 13337 | 0.0079525 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Other
Revised 1-2 22kV Bus Tie CB Def. Time and Inv. Time BUEF stage 1 settings will be applied at RWTS. | 63 HEATHERDALE ROAD, RINGWOOD VIC 3134 |  |  |  |  | Incorrect design |  |  | 1 | E0002321 - Loss of supply to the No.2 & 3 22kV Buses at RWTS | Terminal substation | 0 | 0 | 0 |  |  | At 09:27hrs on the 30/09/2018, test staff carried out routine trip checks on No1 220kV Bus at RWTS. The trip checks tripped all CBs on No1 220kV Bus as expected. The L3 Transformer remained energised from its 22kV side only. Approximately 3 seconds later, the RWTS 1-2 22kV Bus Tie CB tripped and all supply to No2 and No3 22kV Buses was interrupted. The incident resulted in a power outage to 12,240 AusNet Services distribution customers for around 6 minutes. The loss of supply to the No2 and No3 22kV Buses also affected 4 UE feeders and 2 PTC (railway) feeders. All supply was restored at 09:33hrs (6 minutes) by closing the RWTS 1-2 22kV Bus Tie CB. The investigation found that the 1-2 22kV Bus Tie CB opened from its Back-Up Earth Fault protection when the L3 Transformer remained back-energised from the 22kV bus during the No1 220kV Bus trip checks. The RWTS BUEF protection was implemented in 2015 during a station rebuild project which introduced a common Neutral Earthing Resistor in the neutrals of L2 and L3 Transformers. BUEF stage 1 is non-directional whereas stage 2 and stage 3 are directional. | Loss of supply;Significant disruption to the community | 30/09/2018 9:27 |  |  | 10489 | Other | Terminal Station | 20181002SPN_01 | Infrastructure (network-based) | -37.8249 | 145.2133 | 2 | AusNet Services Distribution | Report | 14963 | 0.037676 | 22kV AC | Moorabbin Airport | 3134 | Ringwood | AF Other
On arrival crew confirmed isolation of supply. damage to be repaired if supply required. | 127-175 HARDYS ROAD, MELTON WEST VIC 3337 | 30111426 | Vandalism;Copper theft | [6 empty] | An REC reported that the underground service line to an abandoned house had been cur away and stolen. The meter had been removed from the wall and meter board smashed. There was no fire, no reported injuries. | Services cable;Meter board (including fuses) | 2 | 2 | 2 |  | MLN022 | Copper theft & vandalism | Loss of supply;Damage to network assets | 25/09/2018 14:23 |  |  | 10493 | Residential |  | 20181003PWA_03 | Infrastructure (network-based) | -37.6674 | 144.5237 | 1 | Powercor | Report | 13275 | 0.023319 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and carried out repairs. | 1743 STURT STREET, ALFREDTON VIC 3350 | 32009847 |  |  |  | Overheated connection |  |  |  | Customers reported a conductor on the ground at the incident location. There were reports of supply interruption. Police were on site. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BAS024 | Corroded IPC connector | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/09/2018 18:06 |  |  | 10496 | Roadway |  | 20181003PWA_05 | Infrastructure (network-based) | -37.5516 | 143.808 | 1 | Powercor | Report | 13343 | 0.0071169 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Alfredton | Connection
On arrival crew isolated supply and carried out repairs. | 23 EDWARDS ROAD, WERRIBEE VIC 3030 | 32009847 | Working too close to underground cables | [6 empty] | A Plumber rang to advise they had dug up a cable. A crew attended and found the plumber had dug up and damaged the cable and conduit to a pit at 23 Edwards St. There was no fire start, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE034 | Plumber using excavator | Loss of supply;No Go Zone (contact);Damage to network assets | 26/09/2018 16:14 |  |  | 10497 | Roadway |  | 20181003PWA_06 | Infrastructure (network-based) | -37.9075 | 144.6779 | 1 | Powercor | Report | 13373 | 0.034047 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
CNR2 feeder CB tripped, Crew leader advised everybody Ok and no damage to conductor The Crew Leader confirmed all members of the work crew were ok. AusNet CEOT contacted the Crew Leader confirmed CNR2 had tripped and enquired if all personnel on site were ok. Site was made safe and CNR2 Feeder was remotely restored some 12 minutes later. No injuries or damage to assets. Crew then contacted DTL to advise of incident. | 1615 MONARO HIGHWAY, NOORINBEE NORTH VIC 3890 | LIS1905380 |  |  |  |  | Not followed | Phase to earth | 1 | E0002557 - report of HV conductor on ground | Conductor (bare) | 0 | 0 | 0 |  | CNR2 | A Glove & Barrier (G&B) crew were tasked with replacing a 22kV bisect strain pole with a 12.5m/12 concrete pole using Live Working Techniques. The work method chosen was to erect the new pole adjacent to the existing pole; pole erection between the Roadside & Centre Phases. As the pole was being raised through the live conductors, (pole was at approximately 45 degrees to the ground), a G&B Lineworker working aloft in an EWP lost his grip of the insulated mat that was covering the hard cover of the roadside conductor which subsequently made contact and/or came into close proximity of an uninsulated section of the pole or crossarm. Consequently CNR2 feeder tripped to lockout. Live Line Sequence (LLS) was enabled and Low Set Instantaneous Over Current (LSIOC) protection enabled. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43169.4708 |  |  | 10494 |  |  | 20181003SPN_01 | Infrastructure (network-based) | -37.4382 | 149.1993 | 1 | AusNet Services Distribution | Report | 13499 | 0.032347 | 22kV AC | Gabo Island Lighthouse | 3890 | Noorinbee North | Other
Fault crew dispatched. Conductors repaired and supply restored | 265 KENNYS LANE, BROADFORD VIC 3658 | LIS4703523 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0002571 - Excavator contacted and brought down overhead HV conductors | Conductor (bare) | 0 | 0 | 0 |  | SMR22 | Excavator driver was attempting to move from one sludge pond to another and, whilst moving with the bucket raised, he contacted the HV conductors. Two HV conductors came to the ground, tripping the feeder | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43169.6097 |  |  | 10500 | Commercial |  | 20181004SPN_01 | Infrastructure (network-based) | -37.178 | 145.0644 | 1 | AusNet Services Distribution | Report | 13412 | 0.019538 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Broadford | Vehicle
Site investigated. Scaffold erected without CitiPower involvement within the No Go Zone . No one onsite, further attempts being made to contact parties. | 79 ARDEN STREET, NORTH MELBOURNE VIC 3051 | 30181507 | Working too close to overhead lines | [5 empty] | 2 | A report was received from public member advising scaffold close to powerlines. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | VM004 | Breached VESI Guidelines . No NGZ application for a PTW | No Go Zone (no contact) | 43443 |  |  | 10509 | Construction |  | 20181005PWA_01 | Infrastructure (network-based) | -37.801 | 144.9479 | 2 | CitiPower | Report | 17438 | 0.015719 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Other
On arrival crew isolated supply and carried out repairs. | 7 CHINOOK WAY, POINT COOK VIC 3030 | 34030537 | Vehicle | [6 empty] | Lend Lease employee reported a fire at the incident location, Upon arrival the crew found that the LV pillar partially burnt out. The fire was extinguished by the caller. The crew also observed that the pillar had been struck by a third party vehicle but no details are available. There was no ground fire, no reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | LV010 | Unknown vehicle | Plant/equipment | 43230.4271 | 1 | Negligible: no ground fire | 10511 | Roadway |  | 20181005PWA_02 | Infrastructure (network-based) | -37.8798 | 144.7333 | 1 | Powercor | Report | 13301 | 0.034304 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Vehicle
Cap bank and faulty CT replaced | RACECOURSE ROAD, PAKENHAM VIC 3810 | 503172 |  |  |  | Defective component |  |  |  | E0002634 - PHM No2 Capacitor Reactor Failure. Whilst closing the No2 Cap Bank and it's No2 Step Switch, the Reactor caught fire tripping both the CB and Step Switch on Earth Fault. | Equipment;Switchyard;Zone substation | 0 | 0 | 0 |  | PHM | Whilst closing the No. 2 Cap Bank and it's No2 Step Switch, the cap bank CT failured resulting in fire at the cap bank tripping both the CB and Step Switch on Earth Fault. Asset failure report not available | Other electricity related;Damage to network assets | 43169.7028 | 1 | Negligible: no ground fire | 10508 | Other | Zone Substation | 20181005SPN_01 | Infrastructure (network-based) | -38.071 | 145.494 | 2 | AusNet Services Distribution | Report | 17914 | 0.031306 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | AF Other
Crew attended, Isolated and repaired conductor | 1351 WARRNAMBOOL-CARAMUT ROAD, WINSLOW VIC 3281 | 32198425 | Working too close to overhead lines | [5 empty] | 1 | Powercor received a report that a wire had been brought down by a truck. The attending crew found that a tip truck had contacted a HV line and had brought down the centre phase conductor. | Conductor (bare) | 0 | 0 | 0 |  | KRT012 | Tip Truck contacted line | Grassfire | 43261.5 | 1 | Small: 10 - 1000 sq.m | 10512 | Agricultural |  | 20181008PWA_01 | Infrastructure (network-based) | -38.253 | 142.466 | 1 | Powercor | Report | 13304 | 0.0057049 | 22kV AC | Warrnambool Airport Ndb | 3281 | Winslow | Vehicle
On arrival crew isolated supply and carried out repairs. | 51 CHAPMANS LANE, HEATHCOTE VIC 3523 | 33031625 |  |  |  | Fuse failed to eject;Candled fuse |  |  |  | Customer reported supply interruption, upon arrival crew found that a EDO fuse tube had candled and burnt through. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | BGO023 | corrosion | Pole-top fire | 28/09/2018 17:40 | 1 | Negligible: no ground fire | 10513 | Roadway |  | 20181008PWA_02 | Infrastructure (network-based) | -36.9265 | 144.6876 | 1 | Powercor | Report | 13305 | 0.025384 | 22kV AC | Bendigo Airport | 3523 | Heathcote | Fuse
On arrival crew isolated supply and carried out repairs. | 231-319 FAULKNERS ROAD, MOUNT COTTRELL VIC 3024 | 32167519 |  |  |  | Corrosion |  |  | 1 | Customers at incident location reported loss of supply. On arrival a field crew found that a FSD had overheated and melted. Burning debris fell to ground and caused a small grass fire which self extinguished. There was no reported injuries or third party property damaged. | Connection box | 2 | 2 | 2 |  | MLN011 | Overheated connection | Grassfire | 43322.5632 | 1 | Small: 10 - 1000 sq.m | 10519 | Agricultural |  | 20181010PWA_01 | Infrastructure (network-based) | -37.7632 | 144.6218 | 1 | Powercor | Report | 13317 | 0.034938 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Connection
On arrival work crew observed interference, site was assessed for immediate safety. Supply was left on. | 870 MT POLLOCK ROAD, BUCKLEY VIC 3240 | 32068432 | Unauthorised work | [5 empty] | 2 | A field crew arrived to carry out a prelim assessment of a service line for maintenance replacement. On arrival there was observed substantial interference to the service line, Point of entry, adjacent wiring and metering position. There was no fire, no reported injuries. | Service conductor;Meter board (including fuses);Customer installation | 2 | 2 | 2 |  | WIN012 | Interference | No Go Zone (contact) | 43383.4215 |  |  | 10520 | Residential |  | 20181010PWA_02 | Infrastructure (network-based) | -38.2385 | 144.0728 | 2 | Powercor | Report | 13319 | 0.027051 | Low voltage AC (<1kV) | Avalon Airport | 3240 | Buckley | Other
Investigation revealed a poor active connection at the customer's FOLCB. Connection was re-terminated and all conductors checked. Tests were repeated to confirm safe, resulting in a pass. Full Techsafe report can be found in "7. Notes & Findings" | 52 PROSPECT STREET, PASCOE VALE VIC 3044 |  |  |  | Neutral | Mechanical breakdown |  |  | 2 | Customer received minor electric shock from kitchen tap, sink, and dishwasher. Techsafe attended to investigate. Full Techsafe report can be found in "7. Notes & Findings" | Aluminium twisted (grey);Connector/termination | 0 | 0 | 0 |  |  | Poor active connection at customer FOLCB. | Minor shock | 43383.4507 |  |  | 10523 | Residential |  | 20181011JEM_01 | Infrastructure (customer connection) | -37.7278 | 144.9339 | 1 | Jemena | Report | 13323 | 0.040374 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Connection
On arrival crew isolated supply and carried out repairs. | 171 GOODMAN ROAD, WOORINEN VIC 3589 | 32160058 |  |  |  | Leakage |  |  | 2 | Vic fire reported a pole fire at incident location. The crossarm broke resulting in a small ground fire. There was no injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire;Grassfire | 43353.8187 | 1 | Localised: less than 10 sq.m | 10524 | Roadway |  | 20181011PWA_01 | Infrastructure (network-based) | -35.247 | 143.4713 | 1 | Powercor | Report | 13324 | 0.021883 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen | Crossarm
On arrival crew arranged for repairs to be carried out | 380 LONSDALE STREET, MELBOURNE VIC 3000 | 30206968 | Working too close to underground cables | [6 empty] | ESV informed a person received injures while he was digging with Jackhammer at the incident location. However, there was no power outage was reported. Upon arrival, The crew found that the cable had been damaged by the Jackhammer. Burn marks were evident on the cable. It was reported one person was injured. There was no fire or third party property damage. | Cable | 2 | 2 | 2 |  | JA011 | Cable struck with jackhammer | Medical attention (first aid/doctor/hospital) | 43383.5312 |  |  | 10525 | Public space |  | 20181011PWA_02 | Infrastructure (network-based) | -37.8125 | 144.9612 | 1 | CitiPower | Report | 13325 | 0.011221 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. The 66kV feeders were isolated for proximity and a set of 22kV bridges broken at the corner of Ferntree Gully Road and Avonhurst Road. | 509 FERNTREE GULLY ROAD, GLEN WAVERLEY VIC 3150 | 611790 |  | Precipitation |  | Leakage |  |  | 2 | Per MFB - High Voltage pole is on fire near the corner of Westerfield Drive and Ferntree Gully Road. A pole fire occurred at HV/LV pole No. LIS 0611790 located outside 509 Ferntree Gully Road at the start of the transmission line easement. The pole was a dual circuit 66kV strain pole (SVTS-GW and SVTS-EB) with a 22kV and LV intermediate cross arms. The 22kV intermediate cross arm was burnt and required replacement. The MFB attended and extinguished the pole fire. | Crossarm (wood) | 0 | 0 | 0 |  | GW 05 | Pole fire with the probable cause attributed to tracking on the brown fog type insulators. | Pole-top fire | 43353.8597 | 1 | Negligible: no ground fire | 10528 | Roadway |  | 20181012UTD_01 | Infrastructure (network-based) | -37.9019 | 145.1501 | 1 | United Energy Distribution | Report | 13329 | 0.041588 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Crossarm
The damaged earth cables were reinstated and a CES was provided from Nilsen. Both Nilsen and Insitugroup Construction Managers notified United Energy of the damaged cabling during the trenching work. Zinfra substations group went to site to confirm the site was safe and the earth grid was not compromised. At the time of this event, no formal handover of the assets had been agreed to with ongoing discussions between Coles and United Energy. | 800-838 TOORAK ROAD, HAWTHORN EAST VIC 3123 |  | Working too close to underground cables;Caused by REC/contractor | [5 empty] | 2 | Coles head office on Toorak Road have elected to move from being a LV Customer to a HV Customer and commenced work pending the formal handover of the High Voltage conversion at the Coles Data Centre facility. Insitugroup were given the task by Coles to trench from the new Coles energy centre to the existing transformer location at "Toorak 830-Tooronga" indoor substation. As part of this work, Insitugroup were advised to scan the area to be trenched to prove services and they proceeded to saw cut the concrete so it could be removed prior to the trenching work commencing. Nilsen were on site after the concrete had been removed and identified there was an earth stake in the middle of the trench with a bare earth wire and Cad welded to the earth stake. The earth cable disappeared underneath the concrete slab on one side of the trench and was broken/cut heading in the other direction. Nilsen spoke to Insitugroup informing them they'd cut though the earthing ring around the indoor substation and commenced an investigation that revealed there was a number of earth stakes damaged and broken. As a matter of precaution, Nilsen reinstated the earth stakes that could be replaced and Cad welded a new bare 120mm earth wire onto the existing grid to re-establish the earth ring. This work was completed but some of the earth stakes could not be in-instated and proceeded to inform Greg Johnson (ESV) and Darshana Paranagama (UE) regarding the issue. No shocks or injuries were reported during the unsafe work practices. | Indoor | 0 | 0 | 0 |  |  | Insitugroup failed to locate assets in the vicinity of the Indoor substation and continued work after breaking earthing cables and earth stakes. | Damage to network assets | 43353.6667 |  |  | 10529 | Commercial |  | 20181012UTD_02 | Infrastructure (network-based) | -37.8454 | 145.0479 | 1 | United Energy Distribution | Report | 13404 | 0.015609 | Earthing cable | Moorabbin Airport | 3123 | Hawthorn East | Dug up
On arrival crew made arrangements to inspect cable for damage. | 20 GILLMAN STREET, HAWTHORN EAST VIC 3123 | 30179553 | Working too close to underground cables | [6 empty] | Amy Ridgeway from APS Drainage advised that they were carrying out excavation work at the incident location and have dug up UG cable and damaged conduit leaving cables exposed. On arrival the fault crew found that the trench had been backfilled, Crew arranged excavation to inspect cable for damage. There were no reported injuries or fire. | Services cable | 2 | 2 | 2 |  | CL038 | excavation work | No Go Zone (contact);Damage to network assets | 43141.491 |  |  | 10534 | Roadway |  | 20181015PWA_03 | Infrastructure (network-based) | -37.8257 | 145.0516 | 1 | CitiPower | Report | 13338 | 0.011639 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | Dug up
A LEI attended and tested various points around the house including the kitchen sink and the main neutral bar and measured 1.5 volts on all earthed equipment to an independent earth. Tightened the consumer mains neutral connection at the Neutral Link as it was found to be slightly loose. Retested exposed metal surfaces with the installation under load and found the voltage had dropped to.0.4 volts. A NST was completed that passed and the customer left on supply. | LONG ISLAND RET VLGE, UNIT 114 1 OVERTON ROAD, SEAFORD VIC 3198 |  |  |  |  | Neutral fault;Electrical breakdown |  | Phase to earth | 2 | The resident rang and advised that she received electric shocks from the mobile charger, laptop and the spout in the kitchen earlier this afternoon. REC was in attendance on Thursday and checked the hot water unit. Location is the Stockland Long Island Village. A resident who resides at the Long Island Retirement Village, received an electric shock when she made simultaneous contact between the kitchen tap and the kitchen sink and proceeded to contact the United Energy faults and emergencies call centre. | Meter board (including fuses) | 0 | 0 | 0 |  |  | Loose neutral connection at the meter panel neutral link. | Minor shock | 43444.9167 |  |  | 10535 | Residential |  | 20181015UTD_01 | Infrastructure (customer connection) | -38.1259 | 145.127 | 1 | United Energy Distribution | Report | 13425 | 0.0060185 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
The red phase HV lead was cut away by the faults crew using live line techniques and repairs will be completed at eth earliest opportunity. | 196 BOORAN ROAD, ORMOND VIC 3204 | 2322822 |  |  |  | Overheated connection |  |  | 2 | Caller reports that powerlines are sparking after being on fire and now a white flame is visible. Capacitor Bank "Booran-Beatty" located at pole No. LIS 2322822 outside 196 Booran Road failed due to the red phase HV dropper burning off at the vacuum switch. The fault apparently caused a brief fire at the pole top but there was no fire damage to the pole. | Pole top | 0 | 0 | 0 |  | CFD 25 | The cause was probable connection failure that subsequently overheated. | Pole-top fire | 15/10/2018 10:37 | 1 | Negligible: no ground fire | 10538 | Roadway |  | 20181016UTD_01 | Infrastructure (network-based) | -37.8976 | 145.0362 | 1 | United Energy Distribution | Report | 13344 | 0.01702 | 11kV AC | Moorabbin Airport | 3204 | Ormond | Connection
On arrival crew isolated supply | 5 SUNDEW COURT, GISBORNE VIC 3437 | 30348617 | Working too close to underground cables | [6 empty] | Builder called to advise underground cable had been struck while digging in customers front yard and exposed live wires. On arrival, crew found that a post hole digger had hit the customers consumer mains. There was no fire, no reported injuries. | Customer installation | 2 | 2 | 2 |  | GSB011 | Excavation on customers property | No Go Zone (contact) | 43383.7389 |  |  | 10545 | Residential |  | 20181017PWA_02 | Infrastructure (network-based) | -37.5056 | 144.5971 | 1 | Powercor | Report | 13352 | 0.038252 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Dug up
On arrival crew isolated supply and carried out repairs. | 76 FERSFIELD ROAD, GISBORNE VIC 3437 | 30317825 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer reported that their power went out when an excavator started digging at a new development across the road. On arrival the crew found that the excavator owned by Man Civil Constructions 0418 310 166 had contacted a steel cover guard on the pole, crushing the LV UG cable inside, damaging the insulation and causing an outage. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | GSB013 | Excavator contacting cover guard | Loss of supply;Damage to network assets | 43414.3375 |  |  | 10546 | Roadway |  | 20181017PWA_03 | Infrastructure (network-based) | -37.4967 | 144.5933 | 1 | Powercor | Report | 13353 | 0.020649 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Dug up
Police blocked the road, Powercor Crews attended and performed repairs. | 59 KINGS ROAD, KINGS PARK VIC 3021 | 33074715 | Vehicle | [6 empty] | Vic fire reported a truck had hit something and a pole and wires were down on the road at the incident location. On arrival the crew found that an LV service pole was broken at the base and laying on the road. The truck had struck a Telstra cable that was attached to the pole, thereby pulling the pole to the ground. There was no fire, no reported injuries. | Pole (concrete) | 2 | 2 | 2 |  | SSE031 | Suspected high load | Damage to network assets | 43414.4764 |  |  | 10547 |  |  | 20181017PWA_04 | Infrastructure (network-based) | -37.7354 | 144.7804 | 1 | Powercor | Report | 13354 | 0.026969 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kings Park | Vehicle
The crew isolated the service for driver to move truck and kindergartento arrange REC to repair raiser bracket. | BENNETT ROAD, HORSHAM VIC 3400 | 30079732 | Vehicle | [6 empty] | Customer reports a delivery truck has hit O/H wires at the above location and wire resting on truck. A crew attended and found a delivery truck had struck a service cable to the Kindergarten and damaged the buildings raiser bracket at the POA and damaged the service cable. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | HSM010 | Truck struck service | Loss of supply;Damage to network assets | 43414.6771 |  |  | 10549 |  |  | 20181017PWA_05 | Infrastructure (network-based) | -36.7174 | 142.1877 | 1 | Powercor | Report | 13356 | 0.00025694 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Vehicle
Supply confirmed isolated. disconnected and issued defect notice to customer. | 11 FISHBONE AVENUE, WERRIBEE VIC 3030 | 30354141 | Working too close to underground cables |  |  | Fault on customer installation |  |  |  | Fencing contractor using digger struck customers underground service cable, pulling it out of pit and disconnecting supply. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE023 | digging operations | Loss of supply;No Go Zone (contact) | 43414.5931 |  |  | 10550 | Residential |  | 20181018PWA_01 | Infrastructure (network-based) | -37.921 | 144.6311 | 1 | Powercor | Report | 13357 | 0.039612 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
On arrival crew isolated supply and arranged for cable replacement. | CLARKES ROAD, BROOKFIELD VIC 3338 | 30289899 | Vandalism;Copper theft | [6 empty] | Report of Interference with and theft of wire / copper from six low voltage underground pits located in Clarkes Road by persons unknown. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft & Vandalism | Damage to network assets | 43414.5 |  |  | 10554 | Roadway |  | 20181018PWA_02 | Infrastructure (network-based) | -37.6909 | 144.5487 | 1 | Powercor | Report | 13361 | 0.020273 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
Supply was isolated and repairs to earthing carried out. | 423 THREE CHAIN ROAD, TUNGAMAH VIC 3728 | 32186331 | Working too close to underground cables;Caused by REC/contractor |  |  |  |  | Phase to earth | 2 | A field crew attended an appointment to change over a farm supply from overhead supply to underground servicing. There was an open trench from the meter box to the pole. The servicing work was completed, during NST testing unusual voltages were obtained. Further investigation was carried out using a Modiwark and detected 240volts on lv earth at the base of the pole. It appears the earthing system was damaged during trenching works carried out by the REC. There appears to be no record of isolation request from the REC to enable these trenching works to be carried out in the vicinity of the SWER substation. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | CME016 | excavation work with trencher | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 15/10/2018 10:30 |  |  | 10581 |  |  | 20181029PWA_01 | Infrastructure (network-based) | -36.1369 | 145.9326 | 1 | Powercor | Report | 13399 | 0.011927 | Low voltage AC (<1kV) | Wangaratta Aero | 3728 | Tungamah | Dug up
On arrival crew isolated supply and carried out repairs. | MELBOURNE ROAD, CRESWICK VIC 3363 | 30016683 | Vandalism;Copper theft | [5 empty] | 2 | An asset Inspector reported a Substation pole had the LV earth Stolen. On arrival the fault crew found that the LV earth on the substation had been removed by an unknown person,. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | BAN009 | Copper theft | Damage to network assets | 19/10/2018 13:35 |  |  | 10588 | Roadway |  | 20181031PWA_04 | Infrastructure (network-based) | -37.4448 | 143.9195 | 1 | Powercor | Report | 13410 | 0.010378 | Earthing cable | Ballarat Aerodrome | 3363 | Creswick | Other
On arrival crew isolated supply and carried out repairs. | 994 LEAKES ROAD, TARNEIT VIC 3029 | 30344211 | Vandalism;Copper theft | [6 empty] | Following on from a report a PCA Faults Crew have advised that an unknown person(s) have cut and removed 16mm LV Service cable from the pits at the base of three adjacent Public lighting poles. There was also live cables left exposed. There was no fire, no reported injuries or third party damage. | Cable;Services pit | 2 | 2 | 2 |  | TNA023 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/10/2018 15:16 |  |  | 10589 | Roadway |  | 20181031PWA_05 | Infrastructure (network-based) | -37.83 | 144.6554 | 1 | Powercor | Report | 13411 | 0.026894 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs. | 144 GRANT STREET, SEBASTOPOL VIC 3356 | 33003486 |  |  |  | Corrosion |  |  | 2 | Following a report a fault crew attended the incident location. On arrival the crew found that Low Voltage flying bridges had failed causing sparks to drop into the grass on the edge of the road, igniting a small grass fire - in to order of 4 square meters. There were no injuries or any other damage. The fire had extinguished when the fault crew arrived. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | BAS022 | Overheated connection | Grassfire | 43111.5972 | 1 | Localised: less than 10 sq.m | 10598 | Roadway |  | 20181102PWA_05 | Infrastructure (network-based) | -37.5987 | 143.8313 | 1 | Powercor | Report | 13423 | 0.012378 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Sebastopol | Connection
They immediately isolated supply to pole , called supervisor and isolatedÂ supply to make safe | COSGROVE DRIVE, MADDINGLEY VIC 3340 | 30355494 | Working too close to underground cables |  |  |  | Inappropriate tools/plant/equipment |  | 2 | Civil contractor was excavating hole to allow Low voltage cable to be jointed. During excavation, the excavator contacted a public lighting cable, pulling the cable from a conduit and causing the cable to be pulled out of the connections inside the lighting pole. The crew attending to complete the jointing identified the damage in the trench and testing found the pole was LIVE. They immediately isolated supply to pole LIS 862941, called supervisor and isolatedÂ supply to make safe. There was no fire, no reported injuries. | Cable;Pole (steel) | 2 | 2 | 2 |  | BMH003 | human error - contractor dig slightly deeper than anticipated | Damage to network assets | 43111.4625 |  |  | 10599 | Roadway |  | 20181102PWA_06 | Infrastructure (network-based) | -37.6876 | 144.4123 | 1 | Powercor | Report | 13856 | 0.039675 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Maddingley | Dug up
The employee immediately descended the ladder and notified the work crew what had occurred. | SEC SUB STATION - 1478, 6 NOTT ROAD, ARARAT VIC 3377 | 30253127 |  |  |  |  | Not followed |  | 2 | A Power Systems Electrician (fitter) was sent to ART ZSS to complete profile testing and oil sampling of ART ZSS Circuit Breakers. Whilst preparing to take an oil sample of ART 66KV CB B, the fitter placed a ladder against the CB and proceeded to open the oil tap. When contact was made with the oil tap the employee heard a buzz / crack sound and experienced a tingling sensation in the arm and through his body. | Circuit breaker | 2 | 2 | 2 |  | CB B | Human error - Safe approach distance from oil tap ( energised ) was not maintained. | Minor shock | 43231.4792 |  |  | 10600 | Other | Network enclosure | 20181107PWA_01 | Infrastructure (network-based) | -37.2684 | 142.9242 | 1 | Powercor | Report | 13737 | 0.041541 | 66kV AC | Ballarat Aerodrome | 3377 | Ararat | Other
On arrival crew isolated supply to enable CFA to extinguish the fire. Pole replaced | 2221 LODDON VALLEY HIGHWAY, MACORNA VIC 3579 | 31005685 |  |  |  | Corrosion |  |  | 2 | A customer reported fire at base of pole. On arrival crew found that their was a small fire near the base of a SWER substation. There was no ground fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | KGT003 | Earth fault | Pole-top fire | 43142.8535 | 1 | Negligible: no ground fire | 10605 | Agricultural |  | 20181108PWA_01 | Infrastructure (network-based) | -35.9329 | 143.924 | 1 | Powercor | Report | 13436 | 0.03884 | Earthing cable | Swan Hill Aerodrome | 3579 | Macorna | AF Other
On arrival crew isolated supply and carried out repairs. | 2040 ECHUCA ROAD, UNDERA VIC 3629 | 33104985 |  | Blown branch/vegetation |  |  |  |  | 1 | Vic fire reported sparking branch on line. On arrival crew found branch across conductors an done conductor on the ground. Protection operated. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | KYM003 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43142.8611 |  |  | 10606 | Agricultural |  | 20181108PWA_02 | Infrastructure (network-based) | -36.264 | 145.2047 | 1 | Powercor | Report | 13438 | 0.023799 | 22kV AC | Shepparton Airport | 3629 | Undera | Trees
Fault crew dispatched. Isolated supply and replaced Krone box. | 85 WINDMILL LANE, LINDENOW VIC 3865 | 1608131 |  |  |  | Defective component |  |  |  | E0004360 - Fuse blew on pole and started small fire . Fire self extinguished and was out when fault crew arrived | Connection box | 0 | 0 | 0 |  | BDL44 | Crew attended site and found LV Krone box had melted and a small burnt area was evident at the base of the pole. Fire was out when crew arrived. Isolated supply and replaced Krone box. | Grassfire | 28/08/2018 10:01 | 1 | Localised: less than 10 sq.m | 10620 |  |  | 20181109SPN_05 | Infrastructure (network-based) | -37.8043 | 147.4904 | 2 | AusNet Services Distribution | Report | 17916 | 0.0057164 | Low voltage AC (<1kV) | Bairnsdale Airport | 3865 | Lindenow | Fuse
The Police were also on site completing an investigation and the faults crew secured the site and placed a new padlock on the kiosk substation door. There was no damage to the kiosk substation. | VICTORIA STREET, HASTINGS VIC 3915 |  | Vandalism;Unauthorised access | [5 empty] | 2 | At 3.35AM on 07/11/2018, meters communicated an outage to customers supplied from "Victoria Kmart-Elizabeth" kiosk substation and a faults crew was dispatched to investigate. Unknown persons broke into "Victoria Kmart-Elizabeth" kiosk substation by cutting a padlock. They proceeded to turn off the LV main isolator and it was alleged they were trying to break into the EB Games Store located in close proximity. It appeared that no electric shocks or damage was sustained to the unauthorised persons. | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | HGS 32 | Attempted theft with supply interrupted to disable shop alarm systems. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43292.1493 |  |  | 10611 | Commercial |  | 20181109UTD_03 | Infrastructure (network-based) | -38.309 | 145.1904 | 1 | United Energy Distribution | Report | 13443 | 0.034603 | 22kV AC | Moorabbin Airport | 3915 | Hastings | Other
Fault crew dispatched to investigate. No signs of damage to any assets and no repairs required. | 48 HEYINGTON AVENUE, THOMASTOWN VIC 3074 | LIS910335 | Unknown external/community factor |  |  | Unknown technical factor |  |  |  | Vic Fire report pole fire spreading to trees | Conductor (bare);Any other type | 0 | 0 | 0 |  | TT5 | Vegetation: Trees Incident | Pole-top fire | 19/10/2018 21:13 | 1 | Localised: less than 10 sq.m | 10626 | Roadway |  | 20181112SPN_02 | Infrastructure (network-based) | -37.6828 | 145.0196 | 2 | AusNet Services Distribution | Report | 13468 | 0.021062 | 22kV AC | Essendon Airport | 3074 | Thomastown | Pole
Fault crew dispatched and repairs carried out | 364 DORSET ROAD, BORONIA VIC 3155 | LIS 5625975 |  |  |  | Defective component |  |  |  | Report of Street light fire | Public lighting | 0 | 0 | 0 |  |  | Street light head caught fire. Cause of failure unknown | Pole-top fire | 43138.7764 | 1 | Negligible: no ground fire | 10628 |  |  | 20181112SPN_04 | Infrastructure (network-based) | -37.8501 | 145.2857 | 2 | AusNet Services Distribution | Report | 18190 | 0.040821 | Low voltage AC (<1kV) | Moorabbin Airport | 3155 | Boronia | AF Other
On arrival crew isolated supply and carried out repairs. | ELSWORTH STREET W, GOLDEN POINT VIC 3350 | 33002388 |  | Bird |  |  |  |  | 1 | Powercor received a call from the CFA that a fire had started at the rear of the Soverign Hill complex by a Powercor Pole. A crew attended and determined that a bird had flashed over on a Boric Acid fuse unit. The bird fell to the ground starting a small ground fire (10 x 30 mtrs). There was no injuries or third party property damage. | Boric acid | 2 | 2 | 2 |  | BAS013 | Bird Incident | Grassfire | 43445.6215 | 1 | Small: 10 - 1000 sq.m | 10637 | Public space |  | 20181113PWA_01 | Infrastructure (network-based) | -37.5832 | 143.8644 | 1 | Powercor | Report | 13483 | 0.007478 | 22kV AC | Ballarat Aerodrome | 3350 | Golden Point | Animal
Fault crew dispatched. CFA in attendance no ground fire or property damage. Fuse replaced | 17 CHURCH STREET, LAKES ENTRANCE VIC 3909 | LIS1901962; SW 844566 |  |  |  | Candled fuse |  |  |  | E0003359 - report of fuse candling | EDO fuse | 0 | 0 | 0 |  | BDL41 | Blown EDO fuse appears to have been candling. No fire | Pole-top fire | 19/10/2018 10:55 | 1 | Negligible: no ground fire | 10641 |  |  | 20181113SPN_01 | Infrastructure (network-based) | -37.8791 | 147.9877 | 2 | AusNet Services Distribution | Report | 18188 | 0.020037 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | Fuse
Fault crew dispatched. Replaced EDO fuse | 3 UPPER GRIEVE ROAD, AVONSLEIGH VIC 3782 | LIS 420243 |  |  |  | Candled fuse |  |  |  | reported fuse candling | EDO fuse | 0 | 0 | 0 |  | BG166 | candling EDO fuse. No ground fire. | Pole-top fire | 15/11/2018 13:45 | 1 | Negligible: no ground fire | 10654 |  |  | 20181115SPN_01 | Infrastructure (network-based) | -37.9225 | 145.4757 | 2 | AusNet Services Distribution | Report | 18117 | 0.014032 | 22kV AC | Moorabbin Airport | 3782 | Avonsleigh | Fuse
On arrival crew isolated supply and carried out repairs | 69 WESTMELTON DRIVE, MELTON WEST VIC 3337 | 30328586 | Vandalism;Copper theft | [6 empty] | On arrival the PCA Faults Crew have advised that an unknown person(s) have vandalised and damaged the service pits. Service cable had been cut and removed. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN014 | copper theft & vandalism | Damage to network assets | 24/10/2018 12:45 |  |  | 10664 | Roadway |  | 20181120PWA_01 | Infrastructure (network-based) | -37.6761 | 144.5605 | 1 | Powercor | Report | 13524 | 0.022338 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Isolated and made safe. LV conductor replaced and supply restored. | 2 CLOVELLY COURT, VIEWBANK VIC 3084 | A079959 |  | Wind;Fallen |  |  |  |  | 2 | Tree falling brought down one phase of LV OH conductor. | Conductor (bare) | 0 | 0 | 0 |  | NH08 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2018 16:30 |  |  | 10673 | Residential |  | 20181121JEM_01 | Infrastructure (network-based) | -37.7309 | 145.0914 | 1 | Jemena | Report | 13565 | 0.034399 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Viewbank | Trees
On arrival crew isolated supply and carried out repairs | 7840 MURRAY VALLEY HIGHWAY, KOYUGA VIC 3622 | 30125489 |  | Lightning | [5 empty] | Vic Fire reported a grass fire at the incident location. Upon arrival, the fault crew found that the power pole top( LIS 26100) had been struck by lightning. The fallen debris caused small grass fire (10Sqm). There were no reported injuries or third party property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | KYM-ECA2 | Lightning strike | Grassfire | 20/11/2018 14:04 | 1 | Localised: less than 10 sq.m | 10677 | Roadway |  | 20181121PWA_02 | Infrastructure (network-based) | -36.1954 | 144.9138 | 1 | Powercor | Report | 13537 | 0.0053981 | 22kV AC;66kV AC | Shepparton Airport | 3622 | Koyuga | Lightning
On arrival crew confirmed isolation and carried out repairs. | 1310-1334 LEAKES ROAD, ROCKBANK VIC 3335 | 30108618 | Vandalism;Copper theft | [6 empty] | Customer advised that property at the above address had been vandalised. Mains have been ripped out, switchboard smashed, meter stolen, conduit ripped off near pole at front. There was no fire, no reported injuries. | Services cable;Connection box;Meter board (including fuses) | 2 | 2 | 2 |  | MLN021 | vandalism, copper theft | Damage to network assets | 31/10/2018 11:10 |  |  | 10678 | Residential |  | 20181121PWA_03 | Infrastructure (network-based) | -37.7389 | 144.6514 | 1 | Powercor | Report | 13538 | 0.0067477 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Fault crew and LEI attended to investigate and made safe. Crew replaced transformer, test&connected, NST passed, left on supply. | 618 BORALMA-TARRAWINGEE ROAD, LONDRIGAN VIC 3678 | Chris 2 S/S |  | Lightning | [5 empty] | E0005104 - report of HV injection as a result of lightning strike. | Transformer | 0 | 1 | 0 |  | WN3 | Substation was struck by lightning resulting in high voltage injection. Evidence of damage to customer installation. Inspector attended and made safe. | HV injection | 22/11/2018 19:00 |  |  | 10691 |  |  | 20181123SPN_01 | Infrastructure (network-based) | -36.3359 | 146.4585 | 1 | AusNet Services Distribution | Report | 13555 | 0.012473 | 22kV AC | Wangaratta Aero | 3678 | Londrigan | Lightning
Fault crew dispatched. Control room notified. ECG carried out at local hospital which passed and contractor determined fit to resume work. Fault crew repaired damaged earth | 90 PHEASANT CREEK ROAD, PHEASANT CREEK VIC 3757 | LIS1401388; PHEASANT CK BURTON | Working too close to underground cables |  |  | Defective component |  | Phase to earth |  | E0005047 - LV underground cable jointer received a shock off single phase pole type substation. | Earth/earthing;Transformer | 0 | 1 | 0 |  | KLK2 | UCS LV underground cable jointer received a shock off 'PHEASANT CK BURTON' single phase pole type substation. The fault crew has reported back the HV earth was cut where the conduit for LV U/G service conduit crossed the path. The VESI civil contractor for the Developer is Diamond Valley Excavations CW209. Preparing for allocated electrical distribution works when tradesperson conducted a safe to approach on an existing electrical asset. Contractor approached LV CHP and proceeded to move grass and weeds away to look at cable guards when contractor brushed hands on the exposed HV earth and received an electric shock. Control room notified. ECG carried out at local hospital which passed and contractor determined fit to resume work. Fault crew repaired damaged earth | Minor shock;Damage to network assets | 23/11/2018 12:00 |  |  | 10692 |  |  | 20181123SPN_02 | Infrastructure (network-based) | -37.4748 | 145.2918 | 1 | AusNet Services Distribution | Report | 14990 | 0.023637 | 22kV AC | Wallan (Kilmore Gap) | 3757 | Pheasant Creek | Dug up
Site was made safe and repairs undertaken. | 1 MARIBYRNONG STREET, FOOTSCRAY VIC 3011 |  | Vehicle | [5 empty] | 2 | A passerby reported of a bay of LV ABC is down and alive. Earlier a tip truck was observed around the location. Cause unknown. | Conductor (ABC) | 0 | 0 | 0 |  |  | Works Practices advised. Currently under investigation, report of tip truck causing 1 bay of LV ABC to come down. Details of the tip truck could not be confirmed | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/11/2018 11:08 |  |  | 10708 |  |  | 20181129JEM_01 | Infrastructure (network-based) | -37.8102 | 144.9053 | 1 | Jemena | Report | 13928 | 0.035198 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
On arrival crew isolated supply and carried out repairs. | 19 CEMETERY ROAD, TERANG VIC 3264 | 32058085 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the LV junction box on the pole caught fire. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | TRG005 | Insufficient remains to determine cause. | Pole-top fire | 14/11/2018 11:49 | 1 | Negligible: no ground fire | 10706 | Industrial |  | 20181129PWA_02 | Infrastructure (network-based) | -38.2508 | 142.9183 | 1 | Powercor | Report | 13579 | 0.0077384 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3264 | Terang | Connection
On arrival crew isolated supply and carried out repairs | 527 TESBURY ROAD, TESBURY VIC 3260 | 33036162 |  |  |  | Overheated connection |  |  |  | Report received of pole fire at incident location. On arrival crew found burnt out FSD. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | CDN002 | insufficient remains to determine cause | Pole-top fire | 25/11/2018 7:24 | 1 | Negligible: no ground fire | 10707 | Agricultural |  | 20181129PWA_03 | Infrastructure (network-based) | -38.2931 | 143.1605 | 1 | Powercor | Report | 13580 | 0.020525 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3260 | Tesbury | Connection
Construction Contractor contacted Jemena Project Manager who contacted Jemena Emergency Control Room. Faults crews dispatched to make safe and undertake repairs. | 27 YOUELL STREET, FOOTSCRAY VIC 3011 |  | Working too close to overhead lines | [5 empty] | 2 | A tip truck raised the trailer tub and drove forward making contact with the overhead insulted low voltage cable. The cable disconnected from the pole to ground level. | Conductor (ABC) | 0 | 0 | 0 |  |  | Driver of tip truck drove forward with tipper tub extended to full height making contact with overhead ABC | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/11/2018 10:41 |  |  | 10714 | Other | Car Park | 20181203JEM_01 | Infrastructure (network-based) | -37.8101 | 144.9036 | 1 | Jemena | Report | 14955 | 0.026814 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
On arrival crew isolated supply CFA extinguished fire Customer issued with defect notice to trim tree prior to re connection of supply. | 2103 PRINCES HIGHWAY, SWAN MARSH VIC 3249 | 30046605 |  | Within clearances | [5 empty] | Vic Fire reported a grass fire at the above incident location. When crews arrived they found a OH Service wire was in contact (rubbing) with a branch. A small grass fire had started on road reserve (4x 55m). there was no injuries or property damage reported. | Service conductor | 2 | 2 | 2 |  | CDN002 | Vegetation: Trees Incident | Grassfire | 43112.6576 | 1 | Small: 10 - 1000 sq.m | 10713 | Roadway |  | 20181203PWA_01 | Infrastructure (network-based) | -38.3374 | 143.3577 | 1 | Powercor | Report | 13590 | 0.0034954 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3249 | Swan Marsh | Trees
on arrival crew isolated supply and carried out repairs | 315-317 COVENTRY STREET, SOUTH MELBOURNE VIC 3205 | 30169787 | Working too close to underground cables | [5 empty] | 1 | Contractors installing a drain using a boring machine have contacted an underground cable belonging to the AP11 11 kV feeder. Crew on site advise plans provided to the work party appear to show the cable at an incorrect depth. There was no fire, no injuries or third party property damage. | Cable | 2 | 2 | 2 |  | AP011 | boring operations | No Go Zone (contact);Damage to network assets | 43445.5819 |  |  | 10733 | Roadway |  | 20181204PWA_15 | Infrastructure (network-based) | -37.833 | 144.9569 | 1 | CitiPower | Report | 13611 | 0.030576 | 11kV AC | Essendon Airport | 3205 | South Melbourne | Dug up
Powercor fault crew attended site and have replaced 18 meters of four core low voltage cable between pole and pit. | 6 SARSFIELD STREET, SEPARATION CREEK VIC 3234 | 32067022 | Working too close to underground cables |  |  |  |  | Phase to earth |  | A report was received that a contractor , has struck an underground cable with a crow bar causing damage to the cable and its conduit. The person who caused the damage reported feeling tingling in his hand and was advised to report to a medical specialist to be examined. There was no fire and no reported third party property damage. | Services cable | 2 | 2 | 2 |  | CLC007 | manual digging operations | Minor shock;Damage to network assets | 43445.6181 |  |  | 10736 | Roadway |  | 20181204PWA_18 | Infrastructure (network-based) | -38.6288 | 143.8988 | 1 | Powercor | Report | 13614 | 0.018453 | Low voltage AC (<1kV) | Avalon Airport | 3234 | Separation Creek | Dug up
A faults crew attended and removed the meter and overhead service. Details of the demolition company were taken and the faults crew requested that ESV are notified of the unsafe activities. | 25 HANSWORTH STREET, MULGRAVE VIC 3170 | 24547 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | Report from a neighbour - the wire is still connected to the house but is hanging low enough to be touched from the ground. A demolition company (Major Demolition and Excavation) has contacted the overhead service and pulled the POA and facia board down during the abolishment of the old home. In addition, the Optus and Telstra communication wires have also been felled and the gas meter removed. | Service conductor | 0 | 0 | 0 |  |  | A demolition company contacted the overhead service and pulled the POA and facia board down during a home abolishment. | No Go Zone (contact) | 20/11/2018 16:00 |  |  | 10753 | Residential |  | 20181206UTD_01 | Infrastructure (network-based) | -37.9301 | 145.1702 | 1 | United Energy Distribution | Report | 13641 | 0.039454 | Low voltage AC (<1kV) | Moorabbin Airport | 3170 | Mulgrave | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 3 DENVER CRESCENT, ROWVILLE VIC 3178 | 196889 |  | Wind |  |  |  |  | 1 | At 1627hrs on 20/11/2018, 22kV feeder circuit breaker MGE 32 successfully reclosed and held. During strong winds, a council tree located outside 3 Denver Crescent broke and fell over the HV and LV conductors near pole No. LIS 0600431. Electrical infrastructure was damaged and the faults crew requested that a LEI attend as a HVI was suspected to customers supplied from "Third-Denver" substation. The LEI confirmed a high voltage injection occurred (BWD 1814) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. | Conductor (bare) | 0 | 0 | 0 |  | MGE 32 | Vegetation: Trees Incident | HV injection | 20/11/2018 16:27 |  |  | 10754 | Residential |  | 20181206UTD_02 | Infrastructure (network-based) | -37.9179 | 145.2307 | 1 | United Energy Distribution | Report | 13642 | 0.013815 | 22kV AC | Moorabbin Airport | 3178 | Rowville | Trees
Fault crew and LEI attended. The LEI confirmed a high voltage injection occurred affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 7 FEATHERTOP AVENUE, TEMPLESTOWE LOWER VIC 3107 | 7058199 |  | Blown branch/vegetation |  |  |  |  | 1 | A tree branch from a large private tree from property 7 Feathertop Ave fell onto HV conductors and caused HV injection into the LV cct. | Conductor (bare) | 0 | 0 | 0 |  | BU10 | Vegetation: Trees Incident | HV injection | 24/01/2019 23:10 |  |  | 12058 | Roadway |  | 20190131UTD_01 | Infrastructure (network-based) | -37.7672 | 145.108 | 1 | United Energy Distribution | Report | 15092 | 0.020303 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3107 | Templestowe Lower | Trees
On arrival crew isolated supply and carried out repairs. | 1690-1730 GISBORNE-MELTON ROAD, TOOLERN VALE VIC 3337 | 30542849 | Vandalism;Copper theft | [6 empty] | A customer, reported possible cable stolen from pit and live wires exposed at pit. On arrival crew found underground cables cut in pit and ripped down from pole end. Approximately 50 meter's of underground cables stolen. | Services cable;Services pit | 2 | 2 | 2 |  | MLN012 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 19/01/2019 10:29 |  |  | 12066 | Roadway |  | 20190201PWA_02 | Infrastructure (network-based) | -37.6454 | 144.6015 | 1 | Powercor | Report | 15102 | 0.010162 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
On arrival crew isolated supply and carried out repairs. | 727 HIGH STREET, MELTON WEST VIC 3337 | 30283100 | Copper theft | [6 empty] | A Powercor employee was investigating a meter issue at the incident location and discovered that an approx. 200m section of the LV 4 wire 16mm UG service cable had been stolen. This section of underground feeds street lights in the area, including lights on the Clarke St overpass of the Western Highway. There was no fir, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN022 | Copper theft | Damage to network assets | 22/01/2019 10:20 |  |  | 12070 | Roadway |  | 20190201PWA_04 | Infrastructure (network-based) | -37.6858 | 144.5493 | 1 | Powercor | Report | 15106 | 0.015771 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
A faults crew attended and identified the road side 66kV insulator on the HV termination crossarm was leaning over and the crossarm was burnt and requires replacement. The crossarm wasn't on fire when the crew arrived on-site. | NORTH ROAD, CLAYTON VIC 3168 | 2332439 |  | Lightning;Wind |  |  |  |  | 2 | During stormy conditions at 6.53PM on 30/01/2019, a caller reports that a cross arm is on fire and about to fall down. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | OE-SVTS | During storm conditions, a 66kV insulator had fallen onto the termination crossarm and started to burn. | Pole-top fire | 30/01/2019 18:53 | 1 | Negligible: no ground fire | 12068 | Roadway |  | 20190201UTD_02 | Infrastructure (network-based) | -37.9135 | 145.1167 | 1 | United Energy Distribution | Report | 15104 | 0.028628 | 66kV AC | Moorabbin Airport | 3168 | Clayton | AF Other
Crew removed the conductor from the road and made safe. | 7 PARKER STREET, FOOTSCRAY VIC 3011 |  | Vehicle | [5 empty] | 2 | Low voltage conductor on ground possibility brought down by truck. | Conductor (bare) | 2 | 2 | 2 |  |  | Most likely cause is a truck as evidence point to not being a failure due to age or deterioration. Refer to photos. | Loss of supply | 43526.5563 |  |  | 12074 | Roadway |  | 20190203JEM_01 | Infrastructure (network-based) | -37.807 | 144.9028 | 1 | Jemena | Report | 15111 | 0.038823 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
Crew attended and assessed the out of commission cable. Underground cable is scheduled to be removed. | FRANCIS STREET, YARRAVILLE VIC 3013 |  | Copper theft | [5 empty] | 2 | Unknown persons attempted copper theft of an out of commission underground cable. | Cable | 2 | 2 | 2 |  |  | Unknown person attempted to steal copper underground cable. | Damage to network assets | 43557.5035 |  |  | 12081 | Roadway |  | 20190204JEM_01 | Infrastructure (network-based) | -37.8168 | 144.8505 | 1 | Jemena | Report | 15485 | 0.024843 | Low voltage AC (<1kV) | Laverton Raaf | 3013 | Yarraville | Other
On arrival crew inspected site , no damage to PAL assets | 62 PIPE ROAD, LAVERTON NORTH VIC 3026 | 33075857 | Vehicle | [6 empty] | Mike from DIAMOND VALLEY PORK PTY LTD reported a truck has clipped the mains wire in street, wire now down on ground across driveway, wire sparking. Power to this property is still on. On arrival the crew found that a truck had hit an Optus Service Cable, this resulted in the Optus cable detaching from one of the poles and falling down to the ground across the driveway of #62 Pipe road, Laverton. The crew advised that most likely the Optus Service Cable flicked up into the LV Bare Mains, causing sparking on the LV conductors as they noticed some splash marks on the red phase & neutral conductors. The sparks and probably hot debris that fell to the ground started a small ground fire on the dry grass, the fire extinguished by itself. There were no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | LVN032 | Unknown truck struck Optus cable | Grassfire | 43526.6014 | 1 | Localised: less than 10 sq.m | 12080 | Roadway |  | 20190204PWA_01 | Infrastructure (network-based) | -37.8231 | 144.8065 | 1 | Powercor | Report | 15120 | 0.014704 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Vehicle
replaced wood pole damaged by lightning and replaced vaporized section of the conductor | 2346 BENALLA-YARRAWONGA ROAD, DEVENISH VIC 3726 | pole 3904366 & 3903372 |  | Lightning |  |  |  |  | 1 | E0009020 - wires down due to lightning | Conductor (bare) | 0 | 0 | 0 |  | Husband pole SWER line ex. BN2 | lightning | Grassfire | 30/01/2019 15:52 | 1 | Localised: less than 10 sq.m | 12079 |  |  | 20190204SPN_05 | Infrastructure (network-based) | -36.334 | 145.9633 | 1 | AusNet Services Distribution | Report | 17911 | 0.034601 | 12.7kV AC (SWER) | Wangaratta Aero | 3726 | Devenish | Lightning
On arrival crew isolated supply to allow REC to complete repairs | 653-701 GREIGS ROAD, FIELDSTONE VIC 3024 | 30340130 | Vandalism;Copper theft | [6 empty] | Customer reported possible attempt to steal copper cable leaving cable exposed. Upon arrival, the crew found the mains cut at meter board in an attempt to steal copper. There was no fire and no reported injuries. | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft mains cut at meter board | Loss of supply;Damage to network assets | 22/01/2019 15:17 |  |  | 12090 | Roadway |  | 20190205PWA_03 | Infrastructure (network-based) | -37.7458 | 144.6491 | 1 | Powercor | Report | 15149 | 0.038409 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Fieldstone | Other
On arrival crew carried out repairs. REC engaged to repair customers POA | 630 LANCASTER-MOOROOPNA ROAD, GILLIESTON VIC 3616 | 32191858 | Vehicle | [6 empty] | Vicfire reported fire caused by network assets. Upon arrival the fault crew found that a truck hit grey twisted service cable crossing the road, the cable broke approximately 30cm from the supply pole end, prior to the LV fuses operating arcing has occurred between active's & neutral conductors & material ejected by the arcing commenced a ground fire emanating at base of pole at the incident location. The CFA attended and extinguished the grass fire. There was no reported injuries. | Service conductor | 2 | 2 | 2 |  | KYM003 | Unknown vehicle hit service cable | Grassfire | 43557.6958 | 1 | Small: 10 - 1000 sq.m | 12092 | Roadway |  | 20190206PWA_01 | Infrastructure (network-based) | -36.3138 | 145.2018 | 1 | Powercor | Report | 17611 | 0.040257 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Gillieston | Vehicle
The attending Powercor Fault Crew checked the condition of all conductors and disconnected and remade all terminations between the distribution system and the Point of Attachment (POA) of the installation and completed an NST Test which confirmed a Pass result. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact reconfirmed up to 5.0 Volts under normal load conditions following the disconnection and reconnection of various O/H network assets as a precautionary measure. | 7 WESTCLIFFS AVENUE, RED CLIFFS VIC 3496 | 32144231 |  |  |  | Out of balance load |  |  | 2 | person was outside operating the rear external Garden Tap when she received an electric shock as she made simultaneous contact with her hand on the metal Tap and her wet feet wearing rubber thongs while standing on the wet lawn. | Conductor (bare) | 0 | 0 | 0 |  | RCT023 | Neutral voltage rise - An inherent voltage in the Network Neutral Reticulation system is apparent | Minor shock | 15/01/2019 17:00 |  |  | 12097 | Residential |  | 20190206PWA_05 | Infrastructure (network-based) | -34.3089 | 142.1836 | 1 | Powercor | Report | 15158 | 0.01123 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | AF Other
Dispatched fault crew to investigate and make safe. Fuse replaced | 50 JAMES ROAD, BENA VIC 3946 | 2007971 |  |  |  | Candled fuse |  |  |  | E0009466 - Customer reported supply issues. Fault crew attended and found candled HV Fuse at pole 2007971. | Boric acid | 0 | 0 | 0 |  | LGA23 | Candled fuse and no evidence of ground fire. Fuse replaced | Pole-top fire | 43587.5243 | 1 | Negligible: no ground fire | 12106 | Agricultural |  | 20190207SPN_01 | Infrastructure (network-based) | -38.4447 | 145.7534 | 2 | AusNet Services Distribution | Report | 15171 | 0.023772 | 22kV AC | Morwell (Latrobe Valley Airport) | 3946 | Bena | Fuse
Aluminium Neutral Service replaced by faults truck. | 224 KENNEDYS ROAD, HADDON VIC 3351 | 30003041 |  |  |  | Corrosion |  |  |  | The customer was having a shower at the time and received an electric shock when she simultaneously contacted the metallic water tap with her hands whilst standing in the shower ( as advised by owner, tenant not on site) Voltage test between an independent earth and various parts of the electrical installation, including the distribution assets revealed a corroded Aluminium Neutral Screen service. | Service conductor;Neutral screen | 0 | 0 | 0 |  | BAS021 | Corroded Aluminium Neutral Screen Service | Minor shock | 23/01/2019 12:00 |  |  | 12139 | Residential |  | 20190211PWA_05 | Infrastructure (customer connection) | -37.6018 | 143.7348 | 1 | Powercor | Report | 15211 | 0.01267 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Haddon | OH Cable
The faults crew replaced the failed 20 amp HV powder filled fuse. | PAMELA GROVE, TEMPLESTOWE LOWER VIC 3107 | 7068515 |  | Heat |  | Fatigue;Candled fuse |  |  | 2 | Customers supplied from "Pamela-Airds" substation advised of a loss of supply. There were reports the lights flashed a couple of times before the power failure. The blue phase 20 amp 22KV powder filled fuse had candled that caused hot fuse elements to fall to the dry grass below and a small grass fire to occur that was estimated to be 2sqm in size. In addition, a garbage bin was also heat affected by the small grass fire. | Powder filled | 0 | 0 | 0 |  | BU 6 | The HV fuse candled during hot weather as customers returned home switching on their air-conditioning. | Grassfire | 43557.7431 | 1 | Localised: less than 10 sq.m | 12134 | Roadway |  | 20190211UTD_05 | Infrastructure (network-based) | -37.7583 | 145.1085 | 1 | United Energy Distribution | Report | 15205 | 0.015965 | 22kV AC | Essendon Airport | 3107 | Templestowe Lower | Fuse
Replaced the HVABC between poles 4707373 & 4707375. | 2583 WHITTLESEA-YEA ROAD, FLOWERDALE VIC 3658 | LIS 4707366 & 4704662 |  |  |  | Age |  |  |  | E0010152 - 35mm NMS HV ABC fault. Cable insulation damage. A burnt area of grass approx. 2m x 2m. found under the overhead line [being HV ABC & bare open wire LV] between poles 4707366 & 4704662. CFA and police was on site when the fault intervention crew arrived. | Conductor (ABC) | 0 | 0 | 0 |  | SMR14 | Cable insulation degradation due to age. | Grassfire | 43771.7153 | 1 | Localised: less than 10 sq.m | 12142 |  |  | 20190212SPN_01 | Infrastructure (network-based) | -37.3739 | 145.2795 | 1 | AusNet Services Distribution | Report | 17803 | 0.032569 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Flowerdale | OH Cable
On arrival crew carried out repairs. | 168 THIRTEENTH STREET, MILDURA VIC 3500 | 32140356 |  |  |  | Leakage |  |  |  | During patrol crew found burnt crossarm There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MDA032 | Excessive leakage current | Pole-top fire | 24/08/2018 9:23 | 1 | Negligible: no ground fire | 12154 | Roadway |  | 20190213PWA_05 | Infrastructure (network-based) | -34.1893 | 142.1499 | 1 | Powercor | Report | 15234 | 0.00041782 | 22kV AC | Mildura Airport | 3500 | Mildura | Crossarm
Fault crew dispatched to investigate.. Burnt LV supply pillar replaced and supply restored. | 17 COROWA CRESCENT, GREENSBOROUGH VIC 3088 | 5720978 |  |  |  | Age |  |  |  | E0009621 - report of LV supply pillar on fire and subsequent ground fire around | LV Pillar | 0 | 0 | 0 |  | WT13 | LV supply pillar in customer's front yard has failed internally resulting in a small shrub, adjacent to the pillar, being burnt, No damage to customer property. Pillar appears to have failed due to age (approx. 40 years old) | Grassfire | 43618.5417 | 1 | Localised: less than 10 sq.m | 12157 | Residential |  | 20190213SPN_03 | Infrastructure (network-based) | -37.6893 | 145.1006 | 1 | AusNet Services Distribution | Report | 17786 | 0.030345 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | AF Other
The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable | 44 RIVER STREET, LITTLE RIVER VIC 3211 | 32070004 |  |  |  | Mechanical breakdown |  |  | 2 | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Rose and his bare feet whilst standing on the conductive wet shower base. | Service conductor | 0 | 0 | 0 |  | FNS022 | Connection malfunction - Broken O/H Service Neutral Conductor at the Reticulation Pole. | Minor shock | 43557.3333 |  |  | 12165 | Roadway |  | 20190214PWA_02 | Infrastructure (customer connection) | -37.9625 | 144.5022 | 1 | Powercor | Report | 15250 | 0.015412 | Low voltage AC (<1kV) | Avalon Airport | 3211 | Little River | OH Cable
Om arrival crew isolated supply and carried out repairs | CLARKES ROAD, BROOKFIELD VIC 3338 | 30289901 | Copper theft | [6 empty] | Employee reported theft of underground service cable at incident location. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft | Damage to network assets | 27/01/2019 1:58 |  |  | 12167 | Roadway |  | 20190214PWA_04 | Infrastructure (network-based) | -37.6901 | 144.5488 | 1 | Powercor | Report | 15252 | 0.0019456 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
Emergency high voltage switching took place and the HV and LV crossarms were replaced under Access Authority conditions. | MARIE STREET, DOVETON VIC 3177 |  |  | Precipitation |  | Leakage |  |  | 1 | Caller reports they heard a bang from the substation at the end of the street and lights are dimming. A pole fire occurred at a HV/LV pole located in Marie Street, 1 pole north of Louis Street as a result of the centre phase HV insulator tracking down the pole. The white phase 31.5amp powder filled fuse HV fuse operated at DN7521 spur fusing in Marie Street. The pole was burnt internally down to the Telstra box but was deemed to be okay. | Pole top;Insulators | 0 | 0 | 0 |  | DN10 | The cause of the pole fire was HV insulator tracking following light rain. | Pole-top fire | 43618.3965 | 1 | Negligible: no ground fire | 12168 | Roadway |  | 20190214UTD_01 | Infrastructure (network-based) | -37.9843 | 145.2447 | 1 | United Energy Distribution | Report | 15253 | 0.023074 | 22kV AC | Moorabbin Airport | 3177 | Doveton | Pole
Fault crew dispatched to make safe and carry out repairs | 13 MARKET STREET, LILYDALE VIC 3140 | LIS1008581 |  | Bird |  |  |  | Phase to earth |  | E0010602 - scorch marks on ground 0.1m square where bird fell to ground after contacting cable head | Pole (wood) | 0 | 0 | 0 |  | LDL12 | Bird Incident | Grassfire | 43467.5542 | 1 | Localised: less than 10 sq.m | 12183 |  |  | 20190218SPN_01 | Infrastructure (network-based) | -37.7565 | 145.3524 | 2 | AusNet Services Distribution | Report | 15270 | 0.035539 | 22kV AC | Moorabbin Airport | 3140 | Lilydale | Animal
Fault crew dispatched and candled EDO fuse tube replaced with new | 615 MT BULLER ROAD, MANSFIELD VIC 3722 | LIS 3917428 |  |  |  | Candled fuse |  |  |  | E0009249 - reported candling fuse | EDO fuse | 0 | 0 | 0 |  | MSD1 | EDO HV Fuse candling. There had been lightning in the area prior to the event. When the crew arrived they checked the LV volts which were fluctuating and it was noticed one of the HV fuses had candled. Fuse tube was replaced and supply restored. There was no fire or burn marks at the base of the pole. | Pole-top fire | 43467.5417 | 1 | Negligible: no ground fire | 12193 |  |  | 20190219SPN_02 | Infrastructure (network-based) | -37.0653 | 146.1457 | 2 | AusNet Services Distribution | Report | 15475 | 0.025046 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Fuse
On arrival crew isolated supply and arranged for repairs. | 335 HARKNESS ROAD, HARKNESS VIC 3337 | 30111403 | Vandalism;Copper theft | [6 empty] | A customer advised that a cable has been stolen at the incident location. Upon arrival, Powercor crew found that the 16mm service cables approx. 50m from a pit had been stolen. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN022 | Copper theft and vandalism | Damage to network assets | 31/01/2019 8:37 |  |  | 12205 |  |  | 20190221PWA_01 | Infrastructure (network-based) | -37.666 | 144.5347 | 1 | Powercor | Report | 15303 | 0.015322 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Harkness | Other
On arrival crew isolated supply and carried out repairs. | 121-125 FARM ROAD, WERRIBEE VIC 3030 | 30106473 | Vehicle | [6 empty] | Report was received that a truck from Excell Gray Bruni Pty Ltd. (Construction company), has driven into pole outside 121 Farm road Werribee. The pole is now laying on the nature strip On arrival, the crew found that a truck has hit a service pole, the pole snapped at the base. There was no ground fire or reported injuries. | Service conductor;Pole (wood);Services cable | 2 | 2 | 2 |  | WBE033 | Truck hit service pole | Loss of supply;Damage to network assets | 43557.6215 |  |  | 12207 | Roadway |  | 20190221PWA_03 | Infrastructure (network-based) | -37.9163 | 144.6479 | 1 | Powercor | Report | 15305 | 0.039632 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Vehicle
Removed exposed cables and replaced pit lids. | ELIZABETH DRIVE, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown persons removed low voltage underground cables supplying streetlights. | Services cable | 0 | 0 | 0 |  |  | Unknown persons removed low voltage underground cables supplying streetlights. | Loss of supply | 22/02/2019 11:48 |  |  | 12212 | Roadway |  | 20190222JEM_03 | Infrastructure (network-based) | -37.5572 | 144.734 | 1 | Jemena | Report | 15317 | 0.023981 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew isolated supply and carried out repairs to insulator string. | 770 HORSESHOE BEND ROAD, MOUNT DUNEED VIC 3217 | 33041574 |  | Animal | [5 empty] | Vic Fire reported a grass fire start due to an animal fault at the incident location. When crews arrived they found a possum fault on a HV concrete anchor pole had started a grass fire (50m x 20m) mainly in the road reserve and onto farm land. The fire was extinguished by CFA crews. No injury, or 3rd party property damage other than superficial burning to some farm boundary fence posts and railings. | Insulators | 2 | 2 | 2 |  | WPD024 | Animal Incident | Grassfire | 23/02/2019 0:26 | 1 | Small: 10 - 1000 sq.m | 12215 | Roadway |  | 20190225PWA_02 | Infrastructure (network-based) | -38.2698 | 144.3503 | 1 | Powercor | Report | 17001 | 0.0048553 | 22kV AC | Avalon Airport | 3217 | Mount Duneed | Animal
The crew isolated the cable and a defect notice issued. | 16 ALBERT STREET, CAULFIELD NORTH VIC 3161 | 30219855 | Vehicle | [6 empty] | Fire Brigade reported a wire down at the incident location. Upon arrival, the CitiPower crew found that the cable and POA had been brought down by an unknown vehicle. No vehicle details available There was no fire or reported injuries. | Service conductor | 2 | 2 | 2 |  | EL009 | Unknown vehicle pulled down service line and damaged customers point of attachment. | Loss of supply;Damage to network assets | 14/02/2019 14:30 |  |  | 12217 | Roadway |  | 20190225PWA_04 | Infrastructure (network-based) | -37.8706 | 145.0238 | 1 | CitiPower | Report | 15322 | 0.01611 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Vehicle
On arrival crew isolated supply and carried out repairs | 85-87 ARCHIMEDES AVENUE, LARA VIC 3212 | 32085956 |  |  |  | Unknown technical factor |  |  |  | Vicfire reported a pole fire at the incident location. On arrival the crew found that a 3 phase Fused mains box had overheated resulting in melted debris falling to the ground. Due to green vegetation and bare earth at the base of the pole, the melted debris did not result in a ground fire. There were no reported injuries or third party damage. | Connection box | 2 | 2 | 2 |  | FNS022 | Insufficient remains to determine cause. | Pole-top fire | 16/02/2019 13:35 | 1 | Negligible: no ground fire | 12222 | Roadway |  | 20190226PWA_02 | Infrastructure (network-based) | -38.0291 | 144.4189 | 1 | Powercor | Report | 15327 | 0.019197 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Connection
On arrival crew inspected site. Further inspection and repairs to be undertaken by crews on Wednesday 27/2. | MURROON ROAD, PENNYROYAL VIC 3235 | 30260049 |  |  |  | Overheated connection |  |  | 2 | CFA reported grass fire at incident location and requested Powercor attendance to check equipment as possible ignition source. When crews arrived they inspected the Regulator structure at P159 CLC-LRN line and found evidence of a hot spot on the center phase lead to the top of the disconnect switch on the south side of the pole. Molten PVC tubing was found on the ground. A grass fire of 30m2 had burnt along the road reserve and into private paddock and was extinguished by CFA crews. No injuries or property damage reported | Dropper/bridge | 2 | 2 | 2 |  | WIN011 | Overheated dropper | Grassfire | 26/02/2019 20:37 | 1 | Small: 10 - 1000 sq.m | 12236 | Roadway |  | 20190227PWA_01 | Infrastructure (network-based) | -38.4196 | 143.8372 | 1 | Powercor | Report | 15345 | 0.0098403 | 22kV AC | Avalon Airport | 3235 | Pennyroyal | Connection
The faults crew attended promptly and replaced the white phase LV fused isolator and the 315amp HRC fuse. Supply was restored to normal upon completion. | 44 OGRADYS ROAD, CARRUM DOWNS VIC 3201 |  |  |  |  | Overheated connection |  |  | 2 | Customers supplied from "Ogrady-Shearwater" substation advised of a loss of their electricity supply. One customer advised the transformer was sparking before the supply went off. The white phase LV fused isolator copper lead to the reticulation had burnt off and caused a small 1sqm grass fire at the base of the pole as molten metal fell to the ground. | Conductor (insulated);Copper;Dropper/bridge | 0 | 0 | 0 |  | FTN 24 | The cause was undetermined but most likely a loose connection that overheated. | Grassfire | 25/02/2019 20:05 | 1 | Localised: less than 10 sq.m | 12235 | Roadway |  | 20190227UTD_02 | Infrastructure (network-based) | -38.1062 | 145.1722 | 1 | United Energy Distribution | Report | 15343 | 0.036201 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Connection
On arrival crew isolated supply and carried out repairs. | 54 DURHAM ROAD, SURREY HILLS VIC 3127 | 30187129 |  | Fallen;Property owner/customer | [5 empty] | Police reported that there were wires down at the incident location. When Citipower crew attended they found out that 3 wires were brought down by a tree branch on corner of Durham Rd and Dome St Surrey Hills. There was a small fire (4m x 1m), on the side walk. No other damages or injuries. | Conductor (bare) | 2 | 2 | 2 |  | RD006 | Vegetation: Trees Incident | Grassfire | 28/02/2019 15:21 | 1 | Localised: less than 10 sq.m | 12249 | Roadway |  | 20190301PWA_01 | Infrastructure (network-based) | -37.8308 | 145.0902 | 1 | CitiPower | Report | 15368 | 0.025016 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | Trees
Fault crew dispatched. Supply isolated, site made safe and street light head replaced | 194 CHILDS ROAD, MILL PARK VIC 3082 | LIS5813564 |  |  |  | Defective component |  |  |  | E0012290 - CFA report street light fire. | Public lighting | 0 | 0 | 0 |  | EPG34 | Fault crew attended and found a 150W HPS street light head burnt out. No external fire damage and fault contained within light head. No evidence of ground fire | Pole-top fire | 43468.0722 | 1 | Negligible: no ground fire | 12258 | Roadway |  | 20190304SPN_03 | Infrastructure (network-based) | -37.6622 | 145.0458 | 2 | AusNet Services Distribution | Report | 15381 | 0.027148 | Low voltage AC (<1kV) | Essendon Airport | 3082 | Mill Park | AF Other
Fault crew dispatched to investigate, make safe and carry out repairs | 17 WAINEWRIGHT AVENUE, MOOROOLBARK VIC 3138 | 1012598 |  |  |  | Defective component |  |  |  | E0012763 - report of small ground fire (approx. 3x4m) following HV dropper failure | Dropper/bridge | 0 | 0 | 0 |  | CPK13 | A suspected centre phase HV dropper lead supplying a ground type substation failed at the pole resulting in a small ground fire as hot molten metal and debris fell to ground. | Grassfire | 43558.4868 | 1 | Localised: less than 10 sq.m | 12271 |  |  | 20190304SPN_11 | Infrastructure (network-based) | -37.7685 | 145.323 | 1 | AusNet Services Distribution | Report | 17783 | 0.0047303 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | AF Other
On arrival crew isolated supply and carried out repairs. | 1225 BACCHUS MARSH ROAD, ANAKIE VIC 3213 | 30228255 | Crane, excavator or other construction/farming equipment | [6 empty] | CIVILEX VICTORIA reports while completing road works, an excavator in travelling mode has contacted an overhead conductor causing it to break and fall to ground. On arrival crew found Excavator hit line at driveway of 1225 Bacchus Marsh Road Anakie between LIS 986123 and LIS 986124. One conductor has fallen , there are burn marks at 7 individual sites where small fires started mostly spots. The fires were upstream caused by backfeed. There were no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | FNS011 | Excavator in travelling mode struck conductors | Loss of supply;No Go Zone (no contact);Grassfire | 43468.3924 | 1 | Localised: less than 10 sq.m | 12272 | Construction |  | 20190305PWA_01 | Infrastructure (network-based) | -37.9724 | 144.3485 | 1 | Powercor | Report | 15404 | 0.014576 | 22kV AC | Avalon Airport | 3213 | Anakie | Vehicle
Crew made safe and created a FFU for the underground construction crew to attend to replace the stolen cable | 1213-1257 LEAKES ROAD, ROCKBANK VIC 3335 | 30108647 | Vandalism;Copper theft | [6 empty] | Customer called to advised all power fail. Powercor crew attended to find stolen, low voltage underground cable (about 100meters removed) at incident location. There were no reported injuries or fire due to this incident. | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft low voltage services cable | Damage to network assets | 43771.591 |  |  | 12277 | Roadway |  | 20190305PWA_04 | Infrastructure (network-based) | -37.7334 | 144.6525 | 1 | Powercor | Report | 15409 | 0.014059 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Site made safe, carried out the repairs | 76 RYAN STREET, FOOTSCRAY VIC 3011 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stolen copper neutral earth bar and low voltage bonding leads from Ryan-Leeds kiosk substation. | Equipment;Pad mounted equipment/kiosk;Earth/earthing | 0 | 0 | 0 |  |  | Unknown person(s) stolen copper neutral earth bar and low voltage bonding leads from Ryan-Leeds kiosk substation. | Damage to network assets | 43649.4597 |  |  | 12301 | Commercial |  | 20190307JEM_01 | Infrastructure (network-based) | -37.7985 | 144.9006 | 1 | Jemena | Report | 15436 | 0.041617 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Other
On arrival crew isolated supply and carried out repairs. | DOHERTYS ROAD, TARNEIT VIC 3029 | 32178565 | Vandalism;Copper theft | [6 empty] | A member of the public reported that someone had tampered with the underground pits in the area. On arrival the crew found that several hundred metres of 4 core 25mm2 underground cable supplying at least 10 street lights had been stolen. There were no reported injuries or other third party damage. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Copper theft and vandalism | Damage to network assets | 18/02/2019 8:47 |  |  | 12297 | Roadway |  | 20190307PWA_02 | Infrastructure (network-based) | -37.8196 | 144.693 | 1 | Powercor | Report | 15431 | 0.032339 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Following the notification to their supervisor, the Zinfra crew made the site safe after taking photos and proceeded to install the meters. | 124 CLAYTON ROAD, CLAYTON VIC 3168 |  | Theft;Unauthorised work;Caused by REC/contractor | [5 empty] | 2 | A Zinfra Meter and Servicing crew attended 124 Clayton Road to connect 11 meters at the multiple occupancy development. Upon arrival they identified a temporary builders supply pole (BSP) for the site had been illegally connected and was being used by the builders. Unknown persons had installed steel reinforcement off cut bars into the pole mounted fused disconnector to energise an underground cable into the development site via the service pit. The consumers mains from the pit supplied the BSP directly to a three phase meter and energised the switchboard. The Zinfra crew notified their supervisor who duly contacted United Energy who requested photos and an overview of what the crew found. Zinfra checked their records and there had been no request to connect the BSP. Further investigation identified the meter (0995070) in the BSP was originally installed at 27 Hillingdon Crescent, Doncaster. Zinfra had a request to abolish supply by 19/09/2016 and when the crew arrived at the site, the house, meter and overhead service had been removed with the site vacant and ready for the construction of a new home. It was unknown if the builder or REC were involved in the Hillingdon construction activities. Their details can be found on the attached EWR and CES. | Cable;Services pit;Disconnector/isolator | 0 | 0 | 0 |  |  | Theft of electricity and interference with network assets by unknown persons. | Damage to network assets | 43649.375 |  |  | 12307 | Construction |  | 20190308UTD_02 | Infrastructure (network-based) | -37.9087 | 145.123 | 1 | United Energy Distribution | Report | 15493 | 0.023635 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Other
On arrival crew isolated supply and carried out repairs. | 163 MCCORMICKS ROAD, FOSTERVILLE VIC 3551 | 33019088 |  |  |  | Electrical breakdown |  |  | 1 | Fosterville mine reported a grass fire coinciding with a part supply failure. Upon arrival the crew found that the transformer mounted porcelain surge diverter had failed & subsequently started a small ground fire of approximately 2M x 1M in size. The mine staff extinguished the fire, no injuries or 3rd party damage reported, | Surge diverter | 2 | 2 | 2 |  | EHK031 | Surge diverter failure | Grassfire | 43741.6833 | 1 | Localised: less than 10 sq.m | 12315 | Industrial |  | 20190312PWA_02 | Infrastructure (network-based) | -36.726 | 144.5047 | 1 | Powercor | Report | 16738 | 0.031542 | 22kV AC | Bendigo Airport | 3551 | Fosterville | Fuse
Fault crew dispatched. CFA on site when crew arrived. Crew arrived with conductor still live. Arranged for it to be isolated. Permit raised and crew then re-attached the conductor (no damage to conductor) to the insulator with a new tie. Vibration dampers to be installed | 195 PATERSON ROAD, YANAKIE VIC 3960 | LIS 2027889 |  | Blown branch/vegetation |  | Defective component;Mechanical breakdown;Mechanical vibration |  | Phase to earth |  | E0013804 - conductor has detatched from insulator during high winds resulting in grassfire as conductor came to ground | Conductor (bare);Insulator tie wires/connections | 0 | 0 | 0 |  | FTR22 | Conductor has detached from insulator at pole. 35-45km/h winds in the area. Conductor found hanging approx. 3m from ground height. Small vegetation in vicinity of conductor and scorch marks on vegetation and grass fire approx. 100mx2m long. CFA attended to put out grass fire. There were no signs of corrosion on the tie and it is believed high winds caused the tie to fatigue and fail. In order to restore supply, a new tie was installed however further assessment to be carried out to determine if vibration dampers and/or armour rods are to be installed in this location. No asset failure report available due to nature of incident. | Grassfire | 43741.1875 | 1 | Small: 10 - 1000 sq.m | 12321 |  |  | 20190312SPN_03 | Infrastructure (network-based) | -38.7987 | 146.2205 | 2 | AusNet Services Distribution | Report | 17795 | 0.022641 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Yanakie | AF Other
on arrival crew isolated supply and carried out repairs. | 90-110 SINCLAIRS ROAD, DEANSIDE VIC 3336 | 30105340 | Vandalism;Copper theft | [6 empty] | Report of Public Lighting not working at incident location. Crew found underground cable is missing from supply 197558 to pole 107557. Located live cable at damaged FOLCB install pit connector and make safe. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 14/02/2019 14:05 |  |  | 12327 | Roadway |  | 20190314PWA_01 | Infrastructure (network-based) | -37.7291 | 144.7084 | 1 | Powercor | Report | 15474 | 0.0066586 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Other
Area made safe and fire extinguished. The operator who was first on the scene reported that the LV was still on supply when he arrived, so no protection operated. A licensed electrical inspector (LEI) inspected all accessible properties on the circuit for evidence of damage and high voltage injection - nothing was discovered. Once repairs were completed, the LEI instructed the linesmen to reconnect the LV circuit and the LEI checked a number of installations to ensure the supply was reinstated without any issues. | 25 FODEN AVENUE, CAMPBELLFIELD VIC 3061 | A080873 | Vehicle |  |  | Conductor clashing |  |  | 2 | An unmarked rubbish truck has driven down Nathan Drive with its arms up and come into contact with overhead LV ABC which crossed the street at the intersection of Foden Avenue, causing the LV to flick up into the 22kV bare conductors above. This caused feeder to trip and subsequent HV conductor clashing upstream caused small grass fire approximately 3 square metres. No further damage was caused. The TechSafe report is attached in the "Notes and Findings" section and it contains a photo of the damaged neutral conductor. | Conductor (bare) | 0 | 0 | 0 |  | ST12 | An unmarked rubbish truck has driven down Nathan Drive with its arms up and come into contact with an LV ABC which crossed the street at the intersection of Foden Ave causing the LV to flick up into the 22kV bare conductors above. Airborne debris caused a small grass fire, approximately 3 square metres. | Grassfire | 19/03/2019 19:55 | 1 | Localised: less than 10 sq.m | 12348 | Industrial |  | 20190319JEM_01 | Infrastructure (network-based) | -37.6483 | 144.9423 | 1 | Jemena | Report | 17750 | 0.0020023 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Vehicle
Fault crew dispatched to investigate and found candling fuse and 50 sq m ground fire. Customers advised that to keep clear off Isolating transformer and not to store rubbish/tree branched near it. | 147 GARFIELD NORTH ROAD, GARFIELD NORTH VIC 3814 | LIS510683 |  | Bird |  | Candled fuse |  | Phase to earth |  | E0015009 - Received call from emergency services reporting sparking SWER ISO and ground fire in vicinity. Crew sent to investigate and found candling fuse and 50 sq m ground fire. | Any other type;Transformer | 0 | 0 | 0 |  | WGL12 | Vegetation: Trees Incident | Grassfire | 15/03/2019 20:04 | 1 | Small: 10 - 1000 sq.m | 12345 |  |  | 20190319SPN_05 | Infrastructure (network-based) | -38.0626 | 145.6765 | 2 | AusNet Services Distribution | Report | 15514 | 0.033721 | 12.7kV AC (SWER) | Moorabbin Airport | 3814 | Garfield North | Animal
On arrival crew isolated supply repairs and cleanup initiated. | 373 BAWDEN ROAD, WOODEND VIC 3442 | 33104598 | Vandalism;Copper theft | [6 empty] | Electrician reported damage to Powercor assets as a result of copper theft of Vic Roads assets. On Arrival crew identified that an LV bushing had been torn off a tank and that oil has spilled on the ground. The LV Neutral was hanging down the pole and the Vic Roads cables had been detached from the point of supply at the LV cross-arm on the pole. There was no fire or reported injuries. | Services cable;Transformer;Customer installation | 2 | 1 | 2 |  | WND012 | Copper theft & vandalism | Loss of supply;Damage to network assets | 26/02/2019 15:55 |  |  | 12353 | Roadway |  | 20190320PWA_03 | Infrastructure (network-based) | -37.382 | 144.551 | 1 | Powercor | Report | 15527 | 0.028429 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Other
Crew dispatched made safe and replaced EDO fuse | 150 TOWONG HILL ROAD, TOWONG VIC 3707 | LIS5216213 |  |  |  | Candled fuse |  |  |  | E0015832 - EDO fuse candling | EDO fuse | 0 | 0 | 0 |  | WOTS24 | 6A EDO fuse candled. Fuse replaced | Pole-top fire | 19/03/2019 20:30 | 1 | Negligible: no ground fire | 12355 |  |  | 20190320SPN_02 | Infrastructure (network-based) | -36.1559 | 148.0066 | 1 | AusNet Services Distribution | Report | 15530 | 0.024162 | 22kV AC | Wangaratta Aero | 3707 | Towong | Fuse
Crews attended, works instigated to remove RMU from substation enclosure. | 3 WILLOW STREET, DINGLEY VILLAGE VIC 3172 |  | Vandalism;Copper theft | [5 empty] | 2 | Vandals have entered substation Oak-Willow, likely to steal copper. This substation has previously been targeted, and UE has removed all LV assets, leaving only the HV cable and RMU. As there was no copper to steal, the HV RMU was vandalized. | Any other type;Equipment;Indoor | 2 | 2 | 2 |  | SS14 | Unknown persons made unauthorized entry into substation presumably for the purpose of copper theft. As substation had been previously targeted, all LV assets had been removed. Unknown persons proceeded to vandalise the HV RMU within the substation enclosure. | Damage to network assets | 43649.5972 |  |  | 12356 | Commercial |  | 20190320UTD_01 | Infrastructure (network-based) | -37.9804 | 145.1114 | 1 | United Energy Distribution | Report | 15531 | 0.020606 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Other
Emergency high voltage switching took place and the HV crossarm was replaced under Access Authority conditions. An EIO was also dispatched to check for damage due to HVI. No damage was found. | 44 NEW STREET, BRIGHTON VIC 3186 | 1805858 |  | Precipitation |  | Leakage |  |  | 1 | A cross-arm fire occurred resulting in HV conductor and conductor making contact with LV conductor. The feeder CB operated to isolate supply. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MR32 | The cause of the cross arm fire was HV insulator tracking following light rain. | Pole-top fire;Loss of supply | 43741.6771 | 0 | Negligible: no ground fire | 12360 | Roadway |  | 20190320UTD_03 | Infrastructure (network-based) | -37.9267 | 144.9945 | 1 | United Energy Distribution | Report | 15537 | 0.022348 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Crossarm
Field crew and supervisor attended site and noted the dumping of material directly below the HV lines. Customer was advised the danger of this activity and was instructed to cease this practice immediately. | 675 DUNNS CREEK ROAD, DROMANA VIC 3936 | 1307507 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | A tip truck was delivering soil material; to property and hit and damaged a high voltage line, with conductor falling to the ground. A small fire (size of a hand) occurred as a result of this incident. An upstream HV fuse operated to isolate supply. | Conductor (bare) | 0 | 0 | 0 |  | DMA15 | The delivery and dumping of soil material directly beneath the HV line was the cause of this event. | Grassfire | 19/03/2019 12:24 | 1 | Localised: less than 10 sq.m | 12368 | Agricultural |  | 20190321UTD_01 | Infrastructure (network-based) | -38.3334 | 145.0192 | 1 | United Energy Distribution | Report | 18395 | 0.039859 | 22kV AC | Moorabbin Airport | 3936 | Dromana | Vehicle
On arrival crew isolated supply and carried out repairs | 310 DIGGORA ROAD, ROCHESTER VIC 3561 | 33081172 |  |  |  | Overheated connection |  |  |  | A customer reported that when they turned off their irrigation pump on Tuesday (19th March) the power pole started sparking and arcing, made a loud bang, and started a small grassfire. This was not reported to Powercor until Thursday (21st March). On arrival the crew found a porcelain fuse box on the substation pole had overheated and dropped hot debris to the ground resulting in a small grassfire of approx. 10m x 16m= 160m2 in size. There were no reported injuries or third party damage. | Connection box | 2 | 2 | 2 |  | SHP012 | Overheated porcelain fuse box | Grassfire | 19/03/2019 0:00 | 1 | Small: 10 - 1000 sq.m | 12371 | Roadway |  | 20190322PWA_01 | Infrastructure (network-based) | -36.3521 | 144.6563 | 1 | Powercor | Report | 15559 | 0.040565 | Low voltage AC (<1kV) | Bendigo Airport | 3561 | Rochester | Fuse
Site made safe Supply was isolated and replaced transformer LV isolators and krone box under access permit | 4 WOODLAND DRIVE, GISBORNE VIC 3437 | pole no. A055573 | Copper theft | [5 empty] | 2 | Copper stolen from pole no. A055573 and damaged transformer LV isolators and krone box | Disconnector/isolator;Connection box | 0 | 0 | 0 |  | SBY23 | Copper theft | Damage to network assets | 25/03/2019 11:31 |  |  | 12391 | Peri-urban |  | 20190325JEM_04 | Infrastructure (network-based) | -37.5198 | 144.581 | 1 | Jemena | Report | 15586 | 0.020374 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
Crew attended, Damaged service cable and light fitting replaced. | 64 CARMICHAEL STREET, HAMILTON VIC 3300 | 31019447 | Vehicle | [5 empty] | 2 | Transport company reported making contact with pole, damaging wire at incident location. Crew found the trucks load had made contact with the pole, damaging a 2 wire service cable supplying a street light, made safe and marked for fault follow-up to repair. No injuries or ground fire. | Pole (wood) | 0 | 0 | 0 |  | HTN004 | Very large & long load unable to navigate around corner | Damage to network assets | 20/03/2019 6:16 |  |  | 12382 | Roadway |  | 20190325PWA_01 | Infrastructure (network-based) | -37.7446 | 142.0148 | 1 | Powercor | Report | 15572 | 0.036812 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Vehicle
Tee off cross-arm replaced | 135-137 POINT LONSDALE ROAD, POINT LONSDALE VIC 3225 | 31012844 |  | Prone to salt deposition |  | Leakage |  |  | 2 | Passerby reports burnt cross- arm on pole 11924. Attending crew found end had burnt off from lower HV cross-arm on pole. No HVI identified | Crossarm (wood) | 0 | 0 | 0 |  | DDL012 | excessive leakage current | Pole-top fire;Loss of supply | 24/03/2019 11:44 | 1 | Negligible: no ground fire | 12386 | Roadway |  | 20190325PWA_02 | Infrastructure (network-based) | -38.2826 | 144.6148 | 1 | Powercor | Report | 16976 | 0.026774 | 22kV AC | Avalon Airport | 3225 | Point Lonsdale | Crossarm
crew attended, isolated supply, removed tree and completed repairs | WEERING, 280 POORNEET ROAD, WEERING VIC 3251 | 30262672 |  | Alive;Fallen |  |  |  |  | 1 | Fire brigade reports of tree bringing down conductors impacting on easterly traffic. attending crew found eucalyptus in private wind break had broken at base and fallen onto conductor in road reserve. | Conductor (bare) | 0 | 0 | 0 |  | CLC003 | Vegetation: Trees Incident | Loss of supply | 23/03/2019 16:12 |  |  | 12388 | Roadway |  | 20190325PWA_04 | Infrastructure (network-based) | -38.0728 | 143.7233 | 1 | Powercor | Report | 15583 | 0.036361 | 22kV AC | Ballarat Aerodrome | 3251 | Weering | Trees
Damaged/failed LV leads replaced and new LV Krone/Isolator box installed. | 1691 MELBA HIGHWAY, DIXONS CREEK VIC 3775 | LIS1007398 |  |  |  | Defective component |  |  |  | E0015034 - ground and pole fire reported on s/stn pole | Connection box;Dropper/bridge | 0 | 1 | 0 |  | LDL14 | The fire appears to have been caused by worn exposed non-covered LV leads from the LV bushings of the s/stn to the LV fuses. Cause of failire unknown. LV leads were replaced and a new LV Krone/Isolator box installed. | Pole-top fire;Grassfire | 17/03/2019 7:30 | 1 | Small: 10 - 1000 sq.m | 12383 |  |  | 20190325SPN_01 | Infrastructure (network-based) | -37.6247 | 145.4096 | 2 | AusNet Services Distribution | Report | 17898 | 0.013377 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Dixons Creek | Connection
Fault crew dispatched and isolated supply. CFA already attended site and extinguished fire in 4 separate locations. | 2 MAURICE ROAD, GRUYERE VIC 3139 | LD317; LIS1002272 |  | Fallen |  | Defective component |  | Phase to earth |  | report of ground fire in vicinity of AusNet assets following a tree branch contacting O/H Hv conductors. CFA already attended site and extinguished fire in 4 separate locations. | Conductor (bare);Dropper/bridge | 2 | 2 | 2 |  | LDL23 | Vegetation: Trees Incident | Grassfire | 25/03/2019 15:04 | 1 | Medium: 1000 sq.m - 10 ha | 12403 |  |  | 20190326SPN_02 | Infrastructure (network-based) | -37.7649 | 145.4305 | 1 | AusNet Services Distribution | Report | 15721 | 0.023975 | 22kV AC | Moorabbin Airport | 3139 | Gruyere | Trees
Emergency high voltage switching took place and the HV crossarm was replaced under Access Authority conditions. Inspection of the neighbouring properties confirmed no HVI. | 17 SIBTHORPE STREET, MORDIALLOC VIC 3195 | 9116184 |  | Precipitation |  | Leakage |  |  | 1 | In light rain conditions, a cross arm fire occurred resulting in a HV conductor falling onto LV mains. The feeder CB protection operated to isolate the HV. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MC9 | The cause of the crossarm fire was HV insulator tracking following light rain. | Pole-top fire;Loss of supply | 43802.4819 | 1 | Negligible: no ground fire | 12410 | Roadway |  | 20190328UTD_01 | Infrastructure (network-based) | -37.9884 | 145.1024 | 1 | United Energy Distribution | Report | 18397 | 0.031795 | 22kV AC | Moorabbin Airport | 3195 | Mordialloc | Crossarm
crew attended and isolated | 367 MINIMAY-FRANCES ROAD, MINIMAY VIC 3413 | 33054660 | Crane, excavator or other construction/farming equipment | [6 empty] | A B Double tip truck, while unloading gypsum fertilizer on a farming property, made contact with overhead SWER conductor; bringing the conductor to the ground. The truck was driving forward with the tipper up, and the driver did not check for clearance from the overhead SWER conductor. The electrical discharge through the truck ignited a grass fire on this property - burning an area approx. 50m x 10m There were no injuries to the truck driver or any other damage caused by this incident. | Conductor (bare) | 0 | 0 | 0 |  | HSM004 | plant contact | Grassfire | 28/03/2019 16:21 | 1 | Small: 10 - 1000 sq.m | 12421 | Agricultural |  | 20190329PWA_05 | Infrastructure (network-based) | -36.7321 | 141.1823 | 1 | Powercor | Report | 17613 | 0.020612 | 12.7kV AC (SWER) | Horsham Aerodrome | 3413 | Minimay | Vehicle
On arrival crew isolated supply and carried out repairs. | 177 WESTCLIFFS AVENUE, RED CLIFFS VIC 3496 | 32146224 |  |  |  | Leakage |  |  |  | Report received of a pole fire at the incident location. On arrival crew found that the top of the pole and crossarm had been burnt. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 24/03/2019 10:19 | 1 | Negligible: no ground fire | 12423 | Roadway |  | 20190401PWA_01 | Infrastructure (network-based) | -34.3113 | 142.1658 | 1 | Powercor | Report | 15639 | 0.035449 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Police diverted traffic around the scene, they also notified the railways, and they stopped all trains and provided busses to get passengers around the site. The CFA extinguished the fire and made the site safe. Powercor crews attended, isolated supply and performed repairs. | 287-307 MELBOURNE ROAD, NORTH GEELONG VIC 3215 | 31012241 |  |  |  | Leakage |  |  | 1 | Vicfire called to report a pole hit by lightning, conductors down and a grass fire at the incident location. On arrival the crew found that a cross-arm fire had occurred on the 66kV cross arm, causing the 66kV conductors to fall on the 22kV conductors, which subsequently resulted in one phase of the 22kV falling to the ground. The 22kV conductor that fell, landed across the Princes Highway blocking the road, and also fell across the Geelong-Melbourne Railway causing the trains to be stopped. A small ground fire was ignited at the base of the pole. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | GB031 | Excessive leakage current | Pole-top fire;Grassfire | 29/03/2019 11:49 | 1 | Localised: less than 10 sq.m | 12433 | Roadway |  | 20190402PWA_02 | Infrastructure (network-based) | -38.1148 | 144.3535 | 1 | Powercor | Report | 17614 | 0.016777 | 22kV AC;66kV AC | Avalon Airport | 3215 | North Geelong | Lightning
restored conductor and re-tied conductor | GNARPURT ROAD, LESLIE MANOR VIC 3260 | 32060870 |  | Wind |  | Fatigue |  |  | 2 | Crew attending to faults after storm found SWER conductor had dislodged from pole and was brushing against pole. no fire | Insulator tie wires/connections | 0 | 0 | 0 |  | CDN004 | storm conditions and broken line tie | Loss of supply | 27/03/2019 20:00 |  |  | 12439 | Agricultural |  | 20190402PWA_08 | Infrastructure (network-based) | -38.0498 | 143.345 | 1 | Powercor | Report | 15661 | 0.02555 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3260 | Leslie Manor | Connection
On arrival crew isolated supply and carried out repairs | 8A JARVER CLOSE, COLAC VIC 3250 | 60335249 | Working too close to underground cables | [6 empty] | A contractor reported an UG pit damage at the incident location during housing lot site rubbish removal. Upon arrival the Powercor crew found that the UG pit had been damaged by an excavator. There was no fire, no reported injuries or third party property damage | Services pit | 2 | 2 | 2 |  | CLC004 | Pit damaged during housing lot site preparation | Damage to network assets | 43588.65 |  |  | 12448 | Roadway |  | 20190403PWA_04 | Infrastructure (network-based) | -38.353 | 143.5895 | 1 | Powercor | Report | 15674 | 0.031272 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | Dug up
Fault crew dispatched. Supply was isolated and the burnt wooden HV x-arm was replaced with a steel LW10 HV x-arm and 9 shed insulators. No evidence of ground fire and CFA did not attend | 27 STRATHCOLE DRIVE, TRARALGON VIC 3844 | LIS2613976 |  | Precipitation |  | Electrical breakdown;Leakage |  |  |  | E0018046 - customer reported pole fire outside property. | Crossarm (wood) | 0 | 0 | 0 |  | TGN11 | Light rain in the area at the time of the incident resulting in possible tracking causing the wooden HV x-arm to smoulder around where x-arm brace attached to the x-arm. There was no damage to the HV conductors. Wood HV crossarm replaced with steel | Pole-top fire | 29/03/2019 23:57 | 1 | Negligible: no ground fire | 12441 |  |  | 20190403SPN_01 | Infrastructure (network-based) | -38.1896 | 146.5558 | 1 | AusNet Services Distribution | Report | 16906 | 0.040097 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Crossarm
Candled HV fuse replaced. No other damage to DB assets identified | 47 BAYSWATER ROAD, CROYDON VIC 3136 | LIS5736585 |  | Bird |  | Candled fuse |  |  |  | E0018113 - candling HV fuse reported following bird contacting O/H HV assets | Boric acid | 0 | 0 | 0 |  | CYN32 | Bird Incident | Pole-top fire | 31/03/2019 21:30 | 1 | Negligible: no ground fire | 12445 |  |  | 20190403SPN_03 | Infrastructure (network-based) | -37.8048 | 145.2727 | 2 | AusNet Services Distribution | Report | 15670 | 0.030649 | 22kV AC | Moorabbin Airport | 3136 | Croydon | Animal
The attending Powercor Fault Crew re-terminated the broken Neutral Bridge Conductor at the Reticulation Transformer Pole | 215-229 TOWNSEND ROAD, MOOLAP VIC 3224 | 32069563 |  |  |  | Mechanical breakdown |  |  | 2 | person was opening the Roller Door to his Shed when he received and electric shock as he made simultaneous contact with one hand on the metallic Roller Door and his other hand in contact with the metal structure of the Shed. | Dropper/bridge | 0 | 0 | 0 |  | GLE024 | Broken neutral bridge at transformer pole | Minor shock | 28/02/2019 8:00 |  |  | 12451 |  |  | 20190404PWA_01 | Infrastructure (network-based) | -38.1831 | 144.4068 | 1 | Powercor | Report | 15678 | 0.027405 | Low voltage AC (<1kV) | Avalon Airport | 3224 | Moolap | Connection
On arrival crerw isolated supply and arranged repairs. | 136-146 ABEY ROAD, COBBLEBANK VIC 3338 | 30336481 | Copper theft | [6 empty] | A Powercor fault crew found vandalised street light cables at the incident location. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN011 | Copper theft | Damage to network assets | 43680.4306 |  |  | 12458 | Roadway |  | 20190404PWA_08 | Infrastructure (network-based) | -37.704 | 144.5823 | 1 | Powercor | Report | 15685 | 0.01815 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
On arrival crew isolated supply and carried out repairs | TAYLORS ROAD, CAROLINE SPRINGS VIC 3023 | 30234985 | Copper theft | [6 empty] | Passerby called to report removal of pit lids and wires exposed on Taylors Rd between Orbis Ave and Botanical Dr. Upon arrival the fault crew found that approx. 170m of 4/c 16mm underground P/L service cable between P/L poles LIS-992759, LIS-992760, LIS-992761 and LIS-992762 had been cut and pulled out of the conduits between each pole. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | SA009 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43711.366 |  |  | 12460 | Roadway |  | 20190404PWA_10 | Infrastructure (network-based) | -37.7217 | 144.7314 | 1 | Powercor | Report | 16996 | 0.0063403 | Low voltage AC (<1kV) | Melbourne Airport | 3023 | Caroline Springs | Other
Service isolated for inspection re-arrangement of services to new service | 25 DARIAN ROAD, TORQUAY VIC 3228 | 32070132 | Building too close or within the No Go Zone | [5 empty] | 2 | Crew went on site to install tiger tails as part of a permit to work. When arrival on site crew found building had been built hard up against our service which was alive. | Service conductor | 0 | 0 | 0 |  | WPD022 | intereference - building to close to line | No Go Zone (contact) | 43559.5 |  |  | 12468 | Construction |  | 20190405PWA_05 | Infrastructure (network-based) | -38.3232 | 144.3264 | 1 | Powercor | Report | 15698 | 0.026215 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | Other
CEOT notified of vandalism/theft. Isolated 3 x circuits to make Electrically safe. Underground Crew attended and identified multiple locations where IPCâ€™s had been cut away and removed. Repairs undertaken and damage rectified. Advised New connections Team Police report filed | 7 BRUIN STREET, CLYDE NORTH VIC 3978 |  | Vandalism;Theft | [5 empty] | 2 | E0007249 - When street lights in new estate were found to have no neutral it was discovered that AusNet assets (IPC and Cable) had been stolen from service pits in the area. | Services cable;Services pit;Connector/termination | 0 | 0 | 0 |  | CLN22 | Unknown Party or Parties removed AusNet Services Assets (IPCâ€™s and Cable) without permission and left in an Electrically unsafe condition, with Street lights ALIVE without connected Neutrals. UG cables had been cut when energised by unknown parties | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 28/12/2018 17:40 |  |  | 12466 |  |  | 20190405SPN_01 | Infrastructure (network-based) | -38.0873 | 145.3434 | 1 | AusNet Services Distribution | Report | 15694 | 0.027147 | Low voltage AC (<1kV) | Moorabbin Airport | 3978 | Clyde North | Other
Site made safe, repaired U/G service cable | 4 HUME DRIVE, SYDENHAM VIC 3037 |  | Vandalism | [5 empty] | 2 | Underground services to streetlights damaged by unknown person | Services cable | 0 | 0 | 0 |  |  | Underground services to streetlights damaged by unknown person | Damage to network assets | 43620.6861 |  |  | 12470 | Public space |  | 20190406JEM_02 | Infrastructure (network-based) | -37.7109 | 144.7798 | 1 | Jemena | Report | 15700 | 0.015946 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Sydenham | Other
On arrival crew isolated supply and carried out repairs | MANSFIELD BRIDGE ROAD, LEITCHVILLE VIC 3567 | 31038390 |  |  |  | Leakage |  |  |  | Report of pole fire and ground fire at incident location. Crew found a pole fire had started a 1 acre grass fire, no property damage, no injuries. | Pole (wood) | 2 | 2 | 2 |  | CHA005 | Excessive leakage cause pole top to burn off | Grassfire | 43650.5188 | 1 | Medium: 1000 sq.m - 10 ha | 12472 |  |  | 20190408PWA_02 | Infrastructure (network-based) | -35.9238 | 144.2065 | 1 | Powercor | Report | 16945 | 0.0038831 | 22kV AC | Bendigo Airport | 3567 | Leitchville | Pole
On arrival crew isolated supply and carried out repairs. | 27 MAIN STREET, BRIDGEWATER ON LODDON VIC 3516 | 30028650 |  |  |  | Leakage |  |  |  | Vic Fire reported pole on fire, sparks everywhere. Crew found pole fire/burnt HV strain xarm, no ground fire, no property damage, no injuri | Crossarm (wood) | 2 | 2 | 2 |  | BET001 | Excessive leakage current caused crossarm fire. | Pole-top fire | 43712.0507 | 1 | Negligible: no ground fire | 12486 | Roadway |  | 20190409PWA_03 | Infrastructure (network-based) | -36.6027 | 143.9429 | 1 | Powercor | Report | 15722 | 0.0082604 | 22kV AC | Bendigo Airport | 3516 | Bridgewater On Loddon | Crossarm
On arrival crew isolated supply and commenced repairs | 246 SIMON ROAD, PANITYA VIC 3512 | 32146042 |  |  |  | Leakage |  |  |  | Customer advised fuse down on pole located on Panitya North Rd. Crew found SWER pole had burnt down 2m from top, There was a small stubble fire , no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | OYN001 | excessive leakage current caused pole fire | Pole-top fire;Grassfire | 43712.6278 | 1 | Small: 10 - 1000 sq.m | 12489 | Agricultural |  | 20190410PWA_01 | Infrastructure (network-based) | -35.1589 | 141.0413 | 1 | Powercor | Report | 15725 | 0.023578 | 12.7kV AC (SWER) | Mildura Airport | 3512 | Panitya | Pole
Site made safe and repairs planned | LOT 1 REDSTONE HILL ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Copper theft of streetlight underground service cable (Redstone Hill Rd corner Sunbury Rd, Sunbury) | Services cable | 0 | 0 | 0 |  | SBY32 | Unknown persons stole copper underground service | Damage to network assets | 14/04/2019 8:00 |  |  | 13504 | Roadway |  | 20190414JEM_01 | Infrastructure (network-based) | -37.599 | 144.7543 | 1 | Jemena | Report | 16750 | 0.036924 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Crew made safe and repaired earth cable, the other severed cable was found to be redundant substation earth. | 12 LAKE ROAD, KYABRAM VIC 3620 | 32187708 | Working too close to underground cables | [6 empty] | Project Manager Rowan Ferrier from Northern Constructions Group reported an earth cable running from pole has been pulled up but not severed, another cable has been severed, no one is injured, unsure if supply is effected, area taped off, between 9-15 Lake Road Kyabram, Crew also observed an excavator working close to LV without a spotter and discussed with civil crew on site. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | KYM005 | Contractor uncovered earthing cable | No Go Zone (contact) | 20/03/2019 12:53 |  |  | 13515 | Roadway |  | 20190416PWA_02 | Infrastructure (network-based) | -36.3152 | 145.0456 | 1 | Powercor | Report | 16984 | 0.023015 | Earthing cable | Shepparton Airport | 3620 | Kyabram | Dug up
Fault crew dispatched and candled BA HV fuse replaced. | 317 YARRAM-PORT ALBERT ROAD, LANGSBOROUGH VIC 3971 | LIS2608590 |  |  |  | Candled fuse |  |  |  | Customer called to report arcing / sparking at pole. Fault crew attended and found candled BA fuse | Boric acid | 0 | 0 | 0 |  | FTR23 | Candled BA HV fuse. No evidence of ground fire | Pole-top fire | 13/04/2019 20:40 | 1 | Negligible: no ground fire | 13513 |  |  | 20190416SPN_03 | Infrastructure (network-based) | -38.6445 | 146.6722 | 2 | AusNet Services Distribution | Report | 17768 | 0.02377 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Langsborough | Fuse
Installed service pit and new service cable from pole, issue defect to customer for new UG mains to pit. | 17 EDDYSTONE STREET, MCCRAE VIC 3938 | 1316264 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Third party contractor performing excavation work in street has hit and damaged an underground service conductor in conduit. | Services cable | 0 | 0 | 0 |  |  | The third party contractor was undertaking plumbing works in the street. While undertaking excavation works, the excavator hit and amaged the UG service cable approximately 1.5 m from pole. | Loss of supply;Damage to network assets | 27/03/2019 12:30 |  |  | 13519 | Roadway |  | 20190416UTD_02 | Infrastructure (network-based) | -38.3509 | 144.9275 | 1 | United Energy Distribution | Report | 17031 | 0.039616 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | Dug up
Fault crew dispatched. Candled 6k BA HV fuse replaced and supply restored | 6 VALLEY ROAD, WATTLE GLEN VIC 3096 | LIS921018 |  |  |  | Candled fuse |  |  |  | candled BA HV fuse reported. No ground fire | Boric acid | 0 | 0 | 0 |  | ELM15 | Candled 6k Boric Acid HV fuse. No evidence of ground fire | Pole-top fire | 16/04/2019 21:10 | 1 | Negligible: no ground fire | 13529 |  |  | 20190417SPN_01 | Infrastructure (network-based) | -37.6682 | 145.1877 | 2 | AusNet Services Distribution | Report | 17769 | 0.010064 | 22kV AC | Essendon Airport | 3096 | Wattle Glen | Fuse
Crew replaced pole box | UNIT 3 18 STRODE STREET, RICHMOND VIC 3121 | 30192552 |  |  |  | Overheated connection |  |  | 2 | Person was installing cladding on a second storey roof when he noticed sparking as he removed the rain head and also received an electric shock. He was working off a metallic ladder on the first storey metallic roof. | Service conductor | 0 | 0 | 0 |  | NR024 | Neutral screen cable burnt out at pole box supplying underground feed to property | Minor shock | 14/03/2019 9:00 |  |  | 13543 |  |  | 20190418PWA_05 | Infrastructure (network-based) | -37.8194 | 144.9907 | 1 | CitiPower | Report | 17008 | 0.022655 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Connection
On arrival crew isolated supply and carried out repairs | CALDER HIGHWAY, MACEDON VIC 3440 | 32049435 | Copper theft | [6 empty] | Vicroads called Powercor to report a vandalised site, with wire down around the pole and copper stolen at the incident location. On arrival the crew found that an unknown person had attached a webbing strap to the underground cables and apparently attached it to a vehicle and drove away. This resulted in damage to the Vicroads cabinet and internal equipment, the low voltage isolators on the substation pole, and the LV cable itself was subsequently cut and a section of 4 pieces of approx. 4 metres of 95mm2 copper cable was stolen. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | GSB014 | Copper theft | Damage to network assets | 13/02/2019 9:48 |  |  | 12169 | Public space |  | 20190214PWA_05 | Infrastructure (network-based) | -37.4152 | 144.5448 | 1 | Powercor | Report | 15254 | 0.017179 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
On arrival crew carried out repairs. | 30 SUTHERLAND ROAD, COSGROVE VIC 3631 | 30129547 |  |  |  | Candled fuse |  |  | 0 | A passer-by reported a ground fire at the incident location. Upon arrival, the Powercor crew found that the HV fuse hung-up and approx. 2150Ssqm grass had been burnt and extinguished by the CFA. There was no reported injuries. | Boric acid | 2 | 2 | 2 |  | STN024 | Hung up Boric Acid fuse | Grassfire | 14/02/2019 11:06 | 1 | Medium: 1000 sq.m - 10 ha | 12172 | Roadway |  | 20190214PWA_07 | Infrastructure (network-based) | -36.3098 | 145.6283 | 1 | Powercor | Report | 17612 | 0.0077593 | 12.7kV AC (SWER) | Shepparton Airport | 3631 | Cosgrove | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI inspected properties supplied from "Kirkwood-Melbourne" substation and confirmed that a HVI did not occur. . | MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316290 |  | Precipitation |  | Leakage |  |  | 1 | At 8.49AM on 06/02/2019, 22kV feeder STO 21 circuit breaker successfully reclosed and held. At the same time, ACR RE2212 located at the Rye Landfil Co-Gen site reclosed to lockout as there was no auto reclose available. A passerby reports the transformer is arcing and sparking in Kirkwood Street and the fire brigade are on their way. Following drizzly rain, a pole fire occurred at pole number LIS 1316290 located in Melbourne Road on the corner of Kirkwood Street. The HV tee-off cross arm had burnt through and the HV conductor was resting near the LV conductors and a HVI was suspected to customers supplied from "Kirkwood-Melbourne" substation. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | STO 21 | The pole fire occurred following light drizzly rain at a location in close proximity to Bass Strait and susceptible to salt borne contaminants. | Pole-top fire | 43618.3674 | 1 | Negligible: no ground fire | 12171 | Roadway |  | 20190214UTD_02 | Infrastructure (network-based) | -38.3679 | 144.7696 | 1 | United Energy Distribution | Report | 15256 | 0.040888 | 22kV AC | Avalon Airport | 3942 | Blairgowrie | Crossarm
On arrival crew isolated supply and carried out repairs. | 445 CONGUPNA EAST ROAD, CONGUPNA VIC 3633 | 33090392 |  |  |  | Candled fuse |  |  |  | Customer reported red glow from top of transformer pole. On arrival crew found EDO fuse hung up and glowing. CFA attended site. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | SHN024 | corrosion | Pole-top fire | 28/01/2019 16:54 | 1 | Negligible: no ground fire | 12182 | Roadway |  | 20190218PWA_01 | Infrastructure (network-based) | -36.2992 | 145.4852 | 1 | Powercor | Report | 15268 | 0.0034757 | 22kV AC | Shepparton Airport | 3633 | Congupna | Fuse
On arrival crew isolated supply and carried out repairs. | OLD PETERBOROUGH ROAD, PETERBOROUGH VIC 3270 | 30251712 |  | Bird | [5 empty] | A Powercor Fault crew patrolling following an outage, discovered a dead swan in a paddock, beside a downed HV conductor. The conductor falling on the ground resulted in two small grassfires of approx. 600m2 total in size on private property. The fire self extinguished, due to dewy conditions. There were no reported injuries or other third party damage. | Conductor (bare) | 2 | 2 | 2 |  | WBL012 | Bird Incident | Grassfire | 16/02/2019 0:26 | 1 | Small: 10 - 1000 sq.m | 12190 | Agricultural |  | 20190219PWA_01 | Infrastructure (network-based) | -38.5662 | 142.8599 | 1 | Powercor | Report | 15279 | 0.017965 | 22kV AC | Warrnambool Airport Ndb | 3270 | Peterborough | Animal
Substation doors were repaired Repairs carried out. | 1-15 RATHDOWNE STREET, CARLTON VIC 3053 | Cp0011219 | Vandalism;Copper theft | [6 empty] | A customer called the CitiPower report room advising of a loss of supply. On attendance the CitiPower faults crew found the substation doors with significant damage, the HV RMU in the open position and the copper from the building supply on the LV board removed from the white and blue phases. No thieves found on site. Police were called. No shock, no injuries, no third party damage. | Indoor | 2 | 2 | 2 |  | BQ047 | Vandalism and copper theft | Loss of supply;Damage to network assets | 43557.6201 |  |  | 12208 | Commercial |  | 20190221PWA_04 | Infrastructure (network-based) | -37.8071 | 144.9686 | 1 | CitiPower | Report | 15307 | 0.0054711 | Low voltage AC (<1kV) | Essendon Airport | 3053 | Carlton | Other
On arrival crew inspected assets, no damage found | 390 DEWINGS BRIDGE ROAD, GERANGAMETE VIC 3249 | 33039445 |  | Bird | [5 empty] | Vic-fire report fire under pole at incident location, caused by HV Fuse unit. On arrival crew found a burnt grass patch which had been caused by a crow which had flashed over on the center phase HV fuse unit. There was no reported injuries. | EDO fuse | 2 | 2 | 2 |  | CLC013 | Bird Incident | Grassfire | 22/02/2019 14:20 | 1 | Small: 10 - 1000 sq.m | 12214 | Roadway |  | 20190225PWA_01 | Infrastructure (network-based) | -38.4476 | 143.7256 | 1 | Powercor | Report | 15319 | 0.009125 | 22kV AC | Avalon Airport | 3249 | Gerangamete | Animal
On arrival crew isolated supply and carried out repairs. | 139 CAROLYN WAY, MAIDEN GULLY VIC 3551 | 30328625 | Working too close to underground cables | [6 empty] | A contractor reported that he has dug up an UG service cable at the incident location. Upon arrival, the Powercor crew found that the UG cable from a pole to pit had been damaged while the contractor was upgrading the driveway crossing. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | BET001 | Excavatior damaged underground service. | Damage to network assets | 14/02/2019 12:17 |  |  | 12216 |  |  | 20190225PWA_03 | Infrastructure (network-based) | -36.7459 | 144.1965 | 1 | Powercor | Report | 15321 | 0.021866 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Maiden Gully | Dug up
On arrival crew replace fuse | 94 NORTH WALLACEDALE ROAD, WALLACEDALE VIC 3303 | 31017267 |  |  |  | Fuse failed to eject |  |  |  | Customer reported a transformer fire and CFA in attendance at incident site. When crews arrived they found a HV Boric Acid fuse had "hung up. This resulted in a small grass fire (40m x 2m) along the road reserve that was extinguished by the CFA. No injuries or property damage reported | Boric acid | 2 | 2 | 2 |  | HTN002 | Boric acid fuse hung up | Grassfire | 25/02/2019 20:41 | 1 | Small: 10 - 1000 sq.m | 12220 | Roadway |  | 20190226PWA_01 | Infrastructure (network-based) | -37.9117 | 141.7838 | 1 | Powercor | Report | 15325 | 0.034203 | 22kV AC | Hamilton Airport | 3303 | Wallacedale | Fuse
On arrival crew isolated supply and carried out repairs. | 42 EVRAH DRIVE, HOPPERS CROSSING VIC 3029 | 33072797 |  |  |  | Overheated connection |  |  |  | PCA Faults Crew attended a fault call have advised that a burnt out Blue Phase Cu to Al D-Loop connection at incident location has overheated and caused sparks to fall onto the dry grassed area below. This has caused a small grass fire near the base of the pole. There was no reported injury or shocks as a result of this incident. | Connector/termination;Dropper/bridge | 2 | 2 | 2 |  | LV009 | Overheated connection from CU D loop to isolator | Grassfire | 27/02/2019 18:51 | 1 | Small: 10 - 1000 sq.m | 12247 | Roadway |  | 20190228PWA_03 | Infrastructure (network-based) | -37.8593 | 144.6991 | 1 | Powercor | Report | 15362 | 0.017494 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
On arrival crew isolated supply and carried out repairs. | 115 GIBSON ROAD, NANNEELLA VIC 3561 | 30121480 |  |  |  | Unknown technical factor |  |  |  | Vicfire reported pole fire at incident location. On arrival the crew found that the pole mounted junction box had overheated and melted, Debris from this had fallen to ground and started a ground fire approximately 3m by 50m. Superficial damage to fencing posts. There was no reported injuries. | Connection box | 2 | 2 | 2 |  | KYM001 | Insufficient remains to determine cause | Pole-top fire;Grassfire | 43558.459 | 1 | Small: 10 - 1000 sq.m | 12260 | Roadway |  | 20190304PWA_05 | Infrastructure (network-based) | -36.347 | 144.7958 | 1 | Powercor | Report | 15385 | 0.041634 | Low voltage AC (<1kV) | Shepparton Airport | 3561 | Nanneella | Connection
Fault crew dispatched, site made safe and supply restored. CFA extinguished fire prior to fault crew arrival. | 7 WHITEGUM DRIVE, EAST WARBURTON VIC 3799 | LIS1408778 |  |  |  | Defective component |  |  |  | Report of small fire (approx. 4 sq m) at base of pole. | Surge diverter | 0 | 0 | 0 |  | WYK13 | During REFCL testing, WYK13 feeder CB tripped to lockout and a fire was reported and extinguished by CFA. A 22kV road side (white phase) lighting arrestor has failed during REFCL testing resulting in a small 2mx2m grass fire as debris fell to ground. | Grassfire | 43468.6521 | 1 | Localised: less than 10 sq.m | 12259 |  |  | 20190304SPN_04 | Infrastructure (network-based) | -37.7243 | 145.7642 | 1 | AusNet Services Distribution | Report | 17770 | 0.032797 | 22kV AC | Moorabbin Airport | 3799 | East Warburton | AF Other
Fault crew dispatched to investigate and carry out repairs | 22 COLLINS STREET, DIAMOND CREEK VIC 3089 | LIS 926701 |  | Blown branch/vegetation |  |  |  | Phase to phase |  | E0012577 - Report of small ground fire (2mx2.5m) resulting from tree branch contacting O/H LV conductors | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | ELM12 | Vegetation: Trees Incident | Grassfire | 43468.8826 | 1 | Localised: less than 10 sq.m | 12262 |  |  | 20190304SPN_06 | Infrastructure (network-based) | -37.6717 | 145.1498 | 2 | AusNet Services Distribution | Report | 15389 | 0.010237 | Low voltage AC (<1kV) | Essendon Airport | 3089 | Diamond Creek | Trees
Fault crew dispatched to investigate and carry out repairs. Repair works consisted of replacing with double transformer leads and substation split circuit fusing. | 2 ANZAC AVENUE, YARRA GLEN VIC 3775 | LIS1005807 |  |  |  | Electrical overload |  |  |  | E0012619 - Report of pole fire and subsequent ground fire from a suspected transformer conductor lead failed | Dropper/bridge | 0 | 0 | 0 |  | CPK12 | A suspected transformer conductor lead failed due to high electrical demand resulting in a small ground fire (approx. 1m x 3m) as hot molten metal and plastic fell to ground. Repair works consisted of replacing with double transformer leads and substation split circuit fusing. | Pole-top fire;Grassfire | 43527.7708 | 1 | Localised: less than 10 sq.m | 12269 |  |  | 20190304SPN_09 | Infrastructure (network-based) | -37.6562 | 145.3693 | 2 | AusNet Services Distribution | Report | 17899 | 0.030465 | Low voltage AC (<1kV) | Moorabbin Airport | 3775 | Yarra Glen | AF Other
Fault crew dispatched. LV lead and isolator replaced | 24 GREENBROOK DRIVE, EPPING VIC 3076 | LIS916606 |  |  |  | Defective component |  |  |  | E0012682 - Report of fire at base of pole | Disconnector/isolator;Dropper/bridge | 0 | 0 | 0 |  | EPG34 | An LV isolator and transformer lead failed on pole LIS916606 resulting in 2 small grass fires (approx 1m sq and 12m sq) as hot molten metal fell to ground. | Grassfire | 43527.6875 | 1 | Small: 10 - 1000 sq.m | 12270 |  |  | 20190304SPN_10 | Infrastructure (network-based) | -37.6468 | 145.0367 | 2 | AusNet Services Distribution | Report | 15401 | 0.0028519 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | AF Other
LEI carried out voltage tests between an independent earth and the neutral bar, MEN system and metallic water piping system identified a voltage of 43.5 on the shower taps and shower rose. Truck crew replaced a corroded neutral connection at pole top connection box along with replacing the deteriorated overhead aluminium neutral screen service cable to the property. | 179A SUNSHINE ROAD, WEST FOOTSCRAY VIC 3012 |  |  |  |  | Age;Corrosion;Neutral fault |  |  | 2 | The customer was showering when she received an electric shock whilst making simultaneous contact between her wet hands on the shower taps and the wet shower base. | Service conductor | 0 | 0 | 0 |  |  | Corroded neutral connection at pole top connection box along with a deteriorated overhead aluminium neutral screen service cable | Minor shock | 43558.5375 |  |  | 12282 | Residential |  | 20190305JEM_04 | Infrastructure (network-based) | -37.7997 | 144.862 | 1 | Jemena | Report | 15415 | 0.034524 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Connection
On arrival crew isolated supply and carried out repairs | 63 POWERS CREEK ROAD, EDENHOPE VIC 3318 | 33053008 |  | Bird |  |  |  |  | 1 | A report was received that bird has flashed over the HV EDO unit at the pole at the incident location. The bird fell to ground on fire and ignited a ground fire near the pole 20m by 60m ((1200m2). Fire extinguished by the CFA. There was no report of injury or third party property damage. | EDO fuse;Pole mounted | 2 | 2 | 2 |  | CHM011 | Bird Incident | Grassfire | 43558.6507 | 1 | Medium: 1000 sq.m - 10 ha | 12276 | Roadway |  | 20190305PWA_03 | Infrastructure (network-based) | -37.0415 | 141.2873 | 1 | Powercor | Report | 15408 | 0.037008 | 22kV AC | Horsham Aerodrome | 3318 | Edenhope | Animal
Site made safe, cable to be replaced | AITKEN BOULEVARD, GREENVALE VIC 3059 |  | Copper theft | [6 empty] | Unknown persons stole underground service cable supplying street lights | Cable | 0 | 0 | 0 |  |  | Unknown persons stole underground service cable supplying street lights | Damage to network assets | 43619.6646 |  |  | 12295 | Roadway |  | 20190306JEM_04 | Infrastructure (network-based) | -37.63 | 144.912 | 1 | Jemena | Report | 17045 | 0.026414 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
On arrival crew isolated supply and carried out repairs | BULMANS ROAD, MELTON WEST VIC 3337 | 30293682 | Vandalism;Copper theft | [6 empty] | A member of the public emailed Powercor to report a damaged pit in Bullmans Rd. On arrival the crew found that several underground cable pits were open at the incident location with live cables exposed, and approx. 200m of LV UG cable had been stolen. There were no reported injuries or fires. | Services cable | 2 | 2 | 2 |  | MLN023 | Vandalism & copper theft | Damage to network assets | 43771.541 |  |  | 12285 | Roadway |  | 20190306PWA_01 | Infrastructure (network-based) | -37.6652 | 144.5535 | 1 | Powercor | Report | 15418 | 0.0025289 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Melton West | Other
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. No high voltage injection occurred. | UNIT 1 112 WARRIGAL ROAD, PARKDALE VIC 3195 | 1809079 |  | Heat |  | Leakage |  |  | 1 | At 6.03PM on 02/03/2019, 11kV feeder M35 circuit breaker successfully reclosed and held but customers reported dim lights. At 6.19PM, M35 circuit breaker reclosed to lockout with reports of wires down and a grass fire on the corner of Como Parade West and Warrigal Road. It appears a pole fire occurred at a HV intermediate cross arm on pole No. LIS 1809079 located outside 112 Warrigal Road. There appears to have been probable HV conductor clashing with fault current causing wires down at 5 locations in the vicinity following connection failures as follows: 1. Two poles south of HV switch CH7904 (Molten metal caused a 1sqm grass fire at this location) 2. CHP in Palermo Street ex CH4272 3. CH0713 in Napels Road, 3 leads have blown off the switch 4. CH7952 in Warrigal Road on the south side 5. Como Parade West at CHP ex CH0546 | Conductor (bare);Crossarm (wood);Dropper/bridge | 0 | 0 | 0 |  | M35 | Brown fog insulator tracking. | Pole-top fire;Grassfire | 43499.7632 | 1 | Localised: less than 10 sq.m | 12284 | Roadway |  | 20190306UTD_01 | Infrastructure (network-based) | -37.9831 | 145.0714 | 1 | United Energy Distribution | Report | 15417 | 0.028924 | 11kV AC | Moorabbin Airport | 3195 | Parkdale | AF Other
At 5.21AM, emergency high voltage switching was completed with a small section of 22kV feeder DMA24 interrupted to remove a large piece of bark on "Ami-Moorooduc" pole type substation on pole No. LIS 1104930. The pole wasn't damaged by the fire and there was no further asset damage. | OLD MOOROODUC ROAD, DROMANA VIC 3936 | 1104930 |  | Blown branch/vegetation |  |  |  |  | 1 | At 2.28AM on 04/03/2019, 66kV feeder MTN-DMA successfully reclosed and held. A short time afterwards at 3.18AM, the CFA reported a grass fire in Old Moorooduc Road near Nepean Highway that has affected a pole in the vicinity. In summary, it appears the bark initially contacted the 66kV conductors and possible sparks have fallen and ignited the dry grass at the base of the pole causing a 30 x 40m grass fire. When the HV Operator attended, the bark was found resting on the centre phase 22kV conductor and in contact with the steel crossarm. The 66kV and 22kV conductors are on the same pole. | Conductor (bare);Pole mounted | 0 | 0 | 0 |  | MTN-DMA 66kV and DMA24 22kV feeders | A large piece of bark fell onto the overhead high voltage conductors. When the bark was removed, it was found to have significant burn marks. | Grassfire | 43558.1028 | 1 | Small: 10 - 1000 sq.m | 12291 | Roadway |  | 20190306UTD_03 | Infrastructure (network-based) | -38.3086 | 145.0322 | 1 | United Energy Distribution | Report | 15424 | 0.022432 | 22kV AC;66kV AC | Moorabbin Airport | 3936 | Dromana | Trees
On arrival crew isolated supply and carried out repairs. | 442-542 MT ATKINSON ROAD, TRUGANINA VIC 3029 | PA0122064 | Vandalism;Copper theft | [6 empty] | Report received of copper theft at incident location. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Copper theft and vandalism | Loss of supply;Damage to network assets | 17/02/2019 15:34 |  |  | 12296 | Roadway |  | 20190307PWA_01 | Infrastructure (network-based) | -37.7931 | 144.6793 | 1 | Powercor | Report | 15430 | 0.041625 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
On arrival crew confirmed isolation, repairs organised. | 480 BLACKSHAWS ROAD, ALTONA NORTH VIC 3025 | 30117148 | Copper theft | [6 empty] | Customer reports copper wiring from pit to pole stolen (wasn't connected as new build). No exposed wires." No fire or reported injuries. | Services cable | 2 | 2 | 2 |  | BLT021 | Copper theft | Damage to network assets | 19/02/2019 15:59 |  |  | 12298 | Residential |  | 20190307PWA_03 | Infrastructure (network-based) | -37.8295 | 144.8346 | 1 | Powercor | Report | 15432 | 0.018193 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
Fault crew dispatched and isolated supply upon arrival and extinguished what was left of pole fire. HV Cable capped below ground and declared Out Of Commission. Pole was scarred but not damaged. | 163 PRINCES DRIVE, MORWELL VIC 3840 | LIS2618799 |  |  |  | Defective component;Electrical breakdown |  |  |  | 22kV cable failed half way up the pole resulting in a pole fire. No evidence of ground fire and no damage to private assets. | Cable | 0 | 0 | 0 |  | MWT11 | Cable fault has occured and cable has failed half way up the cable head resulting in pole fire. No evidence of ground fire. Cause of cable fault unknown but most likely due to external damage. No asset failure report done for faults of this nature (only for major faults). | Pole-top fire | 43619.7715 | 1 | Negligible: no ground fire | 12309 |  |  | 20190308SPN_03 | Infrastructure (network-based) | -38.2357 | 146.3952 | 1 | AusNet Services Distribution | Report | 16736 | 0.016549 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI attended and confirmed that a high voltage injection did not occur to customers connected to the north circuit of "Verdon-Nepean" substation. In addition, the UE Network Performance team will assess the viability of replacement of copper conductor or ampacts on the HV overhead section close to feeder exit. | PALM GROVE, DROMANA VIC 3936 | 8825277 |  | Heat |  | Conductor clashing;Overheated connection |  |  | 1 | At 1.04AM on 05/03/2019, 66kV feeder DMW-RBD No. 2 circuit breaker successfully reclosed and held. At the same time, 22kV feeder DMA 21 circuit breaker reclosed to lockout. This event resulted in 3,034 customers off supply for an average of 71 minutes. The initial cause appears to have been a connection failure that caused conductor clashing and HV conductors to fall at the corner of Heales Street and Point Nepean Road, Dromana. A HVI was suspected to customers connected to the north circuit of "Verdon-Nepean" substation. The conductor clash occurred at pole No. LIS 8825277 near the corner of Peninsula Link and Seacombe Street that resulted in 66kV feeder DMA-RBD No. 2 to successfully reclose and hold. It was suspected that sparking occurred that ignited dry grass below and a 15sqm fire to start. | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | 22kV DMA 21 and 66kV RBD-DMA No. 2 | Conductor clashing caused molten metal to fall and ignite dry grass. | Grassfire | 43588.0444 | 1 | Small: 10 - 1000 sq.m | 12303 | Roadway |  | 20190308UTD_01 | Infrastructure (network-based) | -38.3352 | 144.9764 | 1 | United Energy Distribution | Report | 15552 | 0.035604 | 22kV AC;66kV AC | Moorabbin Airport | 3936 | Dromana | Conductor
Site made safe | 250 ELIZABETH DRIVE, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stole public lighting underground cable. | Cable | 2 | 2 | 2 |  |  | Unknown person(s) stole underground lighting cable | Damage to network assets | 43802.3444 |  |  | 12318 | Residential |  | 20190312JEM_01 | Infrastructure (network-based) | -37.5571 | 144.734 | 1 | Jemena | Report | 15460 | 0.0080613 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew isolated supply and commenced repairs. | 216 BIGGS STREET, ST ALBANS VIC 3021 | 30232994 |  |  |  | Mechanical vibration;Leakage |  |  | 1 | Calls received from residents to report an outage in the area, with wires down and grass fire in Biggs St, St Albans. Upon arrival the fault crew found that a HV ABC had broken mid span and come to ground on the nature strip below, resulting in a grass fire on the nature strip as well as the grass within the front yard of unit 1 of 216 Biggs St. There was no reported injuries. | Conductor (ABC) | 2 | 2 | 2 |  | SA009 | Abrasion and subsequent tracking. The movement of the insulated cables against the catenary cable eventually results in rubbing and the development of electrical tracking prior to insulation breakdown. | Grassfire | 43711.5347 | 1 | Small: 10 - 1000 sq.m | 12314 | Roadway |  | 20190312PWA_01 | Infrastructure (network-based) | -37.7362 | 144.7972 | 1 | Powercor | Report | 15455 | 0.027444 | 22kV AC | Melbourne Airport | 3021 | St Albans | OH Cable
Fault crew dispatched to investigate and repair. The remaining branch above the point of failure is leaning away from the line & not hazardous to AusNet assets | 43 TRARALGON-BALOOK ROAD, TRARALGON SOUTH VIC 3844 | LIS 2605225 |  | Blown branch/vegetation | [5 empty] | E0013787 - report of tree branch falling into and bringing conductors to ground resulting in ground fire. Evidence of fire in 2 areas - Midspan (2x5m), and around the pole & stay wire (2 x 10m). | Conductor (bare) | 0 | 0 | 0 |  | TGN23 | Vegetation: Trees Incident | Grassfire | 43711.7986 | 1 | Small: 10 - 1000 sq.m | 12320 |  |  | 20190312SPN_02 | Infrastructure (network-based) | -38.3076 | 146.5412 | 2 | AusNet Services Distribution | Report | 15556 | 0.0036562 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon South | Trees
Attending crew secured the area and proceeded to re-attachÃ© the conductor. The LV fuse did not operate. Further investigation indicates that a high fault impedance was in play and reduced the fault current to a level where the fuse did not operate. | 4 LANKESTER STREET, TEMPLESTOWE VIC 3106 |  |  |  |  | Mechanical breakdown;Unknown technical factor |  |  | 1 | Report received of main wire down on naturestrip, with loss of supply. On attendance, fault crew found bare LV conductor had broken off at one pole end and was live on the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Connector failure occurred, however the cause of the failure is unknown. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/02/2019 13:00 |  |  | 12322 | Roadway |  | 20190312UTD_01 | Infrastructure (network-based) | -37.7559 | 145.1239 | 1 | United Energy Distribution | Report | 15467 | 0.031479 | Low voltage AC (<1kV) | Essendon Airport | 3106 | Templestowe | Conductor
supply restored, bird had fallen clear | 647 YATCHAW ROAD, YATCHAW VIC 3301 | 30092292 |  | Bird |  |  |  |  | 1 | Bird flashed over on Yatchaw Rd P27E S/Stn, it came to ground and resulted in a ground fire in the road reserve of approximately 20 M X 100 M. | EDO fuse | 0 | 0 | 0 |  | HTN003 | Bird Incident | Grassfire | 16/03/2019 12:35 | 1 | Medium: 1000 sq.m - 10 ha | 12334 | Roadway |  | 20190318PWA_01 | Infrastructure (network-based) | -37.8099 | 142.1083 | 1 | Powercor | Report | 15523 | 0.032326 | 22kV AC | Hamilton Airport | 3301 | Yatchaw | Animal
Fault crew dispatched to carry out repairs. Pillar repaired and supply restored | 64 AMERSHAM DRIVE, WANTIRNA VIC 3152 | 1031581 | Vehicle | [6 empty] | E0015065 - Fault crew attended to investigate power outage and found vehicle had hit paralleling pillar resulting in a small grass fire of less than 0.25sqm in area in vicinity. | LV Pillar | 0 | 0 | 0 |  | BRA21 | Unknown vehicle reported to have lost control and hit paralleling pillar outside 64 Amersham Drive, Wantirna resulting in a small grass fire of less than 0.25sqm. | Grassfire | 17/03/2019 18:50 | 1 | Localised: less than 10 sq.m | 12347 |  |  | 20190319SPN_07 | Infrastructure (network-based) | -37.8567 | 145.2263 | 2 | AusNet Services Distribution | Report | 17779 | 0.038275 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | Vehicle
The crew made site safe and repaired the damaged conductors. | 26 MAY AVENUE, ALTONA MEADOWS VIC 3028 | 33076190 |  |  |  | Corrosion;Overheated connection |  |  | 2 | Vic fire reported a pole fire at the incident location. On arrival the crew found that a connection on to LV ABC conductors had burnt at the pole . Small pieces of debris had landed on the ground below. There were no reported injuries or third party damage. | Conductor (ABC) | 0 | 0 | 0 |  | LV003 | ruptured connection most likley associated with corrosion | Pole-top fire | 18/03/2019 3:37 | 1 | Negligible: no ground fire | 12351 | Residential |  | 20190320PWA_02 | Infrastructure (network-based) | -37.8796 | 144.7741 | 1 | Powercor | Report | 15522 | 0.031047 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Connection
On arrival crew isolated supply and arranged repairs | 373 BAWDEN ROAD, WOODEND VIC 3442 | 33104596 | Vandalism;Copper theft | [6 empty] | Electrician reported damage to Powercor assets as a result of copper theft of Vic Roads assets. On Arrival crew identified damage to the LV FSD on the pole and customer consumer mains were missing. Crew isolated substation and raised fault follow up. | Services cable;Connection box;Customer installation | 2 | 2 | 2 |  | WND012 | Vandalism & copper theft | Loss of supply;Damage to network assets | 26/02/2019 15:58 |  |  | 12354 | Roadway |  | 20190320PWA_04 | Infrastructure (network-based) | -37.3802 | 144.5508 | 1 | Powercor | Report | 15528 | 0.012515 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Other
Fault crew and LEI dispatched to investigate and carry out repairs. LEI checked customers Metering & Switchboards for any evidence of a possible injection from the incident and confirmed no damage to customer installations. Damaged equipment on pole repaired by fault truck. Telstra notified | 2 RANKINS ROAD, MONBULK VIC 3793 | LIS1320835 |  | Animal |  |  |  | Phase to earth |  | damage to street light and telstra junction box following possum contacting O/H HV and LV assets resulting in flashover. No damage to customer installations or other assets | Communication cable/equipment;Connection box;Public lighting | 0 | 0 | 0 |  | BGE11 | Animal Incident | HV injection;Melting or smoking only;Singeing or local charring/blackening only | 18/03/2019 0:41 |  |  | 12352 |  |  | 20190320SPN_01 | Infrastructure (network-based) | -37.8816 | 145.4208 | 1 | AusNet Services Distribution | Report | 17773 | 0.0075787 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3793 | Monbulk | Animal
On arrival crew isolated supply and carried out repairs. | 49 BENT STREET, ALTONA VIC 3018 | 60159959 | Vandalism;Copper theft | [6 empty] | Report received that pit outside 49 Bent St, Altona has been vandalised. Upon arrival the PCA Field Crew have advised, that an unknown person has removed the recently installed pit lid, from the LV Service Pit at and have vandalized and have cut through and attempted to steal the LV Service Cable. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | AL014 | Copper theft & vandalism | Damage to network assets | 27/02/2019 15:04 |  |  | 12363 | Roadway |  | 20190321PWA_01 | Infrastructure (network-based) | -37.8653 | 144.8323 | 1 | Powercor | Report | 15544 | 0.01288 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
Site made safe - capped in pit adjacent to pole no. A128263 | 1800 MICKLEHAM ROAD, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Copper theft underground LV cable | Cable | 0 | 0 | 0 |  | COO11 | Copper theft | Damage to network assets | 22/03/2019 6:38 |  |  | 12373 | Peri-urban |  | 20190322JEM_02 | Infrastructure (network-based) | -37.565 | 144.8765 | 1 | Jemena | Report | 15561 | 0.011465 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
crew attended and isolated supply for LEI investigation investigations are continuing | 29 GORDON STREET, BALWYN VIC 3103 | 30356235 |  | Blown branch/vegetation | [5 empty] | MFB reported fire in the vicinity of Cnr King and Gordon St Balwyn. Attending crews found high winds caused tree limb to fall across hv and lv near pole 863057 HVI damage was identified. An overheated connection was also found on pole 14139 , with a small fire also being reported at the base of this pole. | Conductor (bare) | 0 | 0 | 0 |  | L001 | Vegetation: Trees Incident | HV injection;Loss of supply;Grassfire | 24/03/2019 15:39 | 1 | Localised: less than 10 sq.m | 12387 | Roadway |  | 20190325PWA_03 | Infrastructure (network-based) | -37.8071 | 145.0628 | 1 | CitiPower | Report | 17010 | 0.014863 | 11kV AC | Essendon Airport | 3103 | Balwyn | Trees
Crew attended and cleared tree from conductor | 438 FOLEYS ROAD, GORAE WEST VIC 3305 | 32128379 | Working too close to overhead lines | Within clearances |  |  |  |  | 1 | Powercor received a report of outage . Upon arrival, the crew found that the SWER line conductor had been brought to ground by a large plantation tree that had fallen . There was no fire or other damage found. | Conductor (bare) | 0 | 0 | 0 |  | PLD003 | Vegetation: Trees Incident | Loss of supply | 25/03/2019 8:20 |  |  | 12402 | Forest - plantation |  | 20190326PWA_04 | Infrastructure (network-based) | -38.2798 | 141.5197 | 1 | Powercor | Report | 16896 | 0.0034954 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3305 | Gorae West | Trees
Fault crew dispatched | 180 EDENS ROAD, CALDERMEADE VIC 3984 | LIS513552 |  |  |  | Candled fuse | Not followed;Poor workmanship |  |  | E0014035 - report of candled HV fuse | Boric acid | 0 | 0 | 0 |  | LLG11 | Candled Boric Acid HV fuse identified. The fuse base appears to not have been installed correctly, connections were loose and no grease as per manufactures requirements. A technical bulletin is being prepared to highlight this issue and ensure this equipment is installed correctly. | Pole-top fire | 43649.5236 | 1 | Negligible: no ground fire | 12404 |  |  | 20190326SPN_03 | Infrastructure (network-based) | -38.2262 | 145.5414 | 2 | AusNet Services Distribution | Report | 15607 | 0.032856 | 22kV AC | Moorabbin Airport | 3984 | Caldermeade | Fuse
Crew attended site and found small fire around pole. Line was already de-energised | MCINTOSHS ROAD, BONEGILLA VIC 3691 | LIS5235758 |  | Lightning |  |  |  |  | 1 | E0016292 - 66KV pole on WOTS-HPS line struck by lightning. Crew responded to find two broken insulators and a small fire that had already been extinguished by rain. | Insulators | 0 | 0 | 0 |  | 66kV WOTS-HPS | 66KV pole on WOTS-HPS line struck by lightning | Grassfire | 22/03/2019 9:31 | 1 | Localised: less than 10 sq.m | 12405 |  |  | 20190327SPN_01 | Infrastructure (network-based) | -36.1229 | 146.9862 | 1 | AusNet Services Distribution | Report | 15611 | 0.020501 | 66kV AC | Wangaratta Aero | 3691 | Bonegilla | Lightning
Emergency high voltage switching took place and the pole and the HV crossarm were replaced under Access Authority condition. | 2 NEPEAN HIGHWAY, DROMANA VIC 3936 | 8825074 |  | Wind |  | Leakage |  |  | 1 | During high winds, UE received report of pole fire. No loss of supply occurred. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | DMA14 | After a long dry spell, insulator leakage was the causal factor for the asset fire. | Pole-top fire | 25/03/2019 17:49 | 1 | Negligible: no ground fire | 12411 | Roadway |  | 20190328UTD_02 | Infrastructure (network-based) | -38.3287 | 144.9735 | 1 | United Energy Distribution | Report | 15622 | 0.017976 | 22kV AC | Moorabbin Airport | 3936 | Dromana | Crossarm
On arrival crew isolated supply and commenced repairs Licenced electrical inspector attended to assess installation safety. | 98 SAGO HILL ROAD, BUNKERS HILL VIC 3352 | 30282752 |  | Wind;Heat;Alive;Fallen;MEC |  |  |  |  | 1 | Vicfire reported wire down and a grass fire at the incident location. Crew found a tree had fallen and damaged a bare overhead conductor. | Conductor (bare) | 2 | 2 | 2 |  | BAS011 | Vegetation: Trees Incident | Grassfire | 29/03/2019 14:12 | 1 | Large: more than 10 ha | 12431 | Roadway |  | 20190402PWA_01 | Infrastructure (network-based) | -37.5705 | 143.7427 | 1 | Powercor | Report | 15650 | 0.010882 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3352 | Bunkers Hill | Trees
Isolated OH replaced broken cross-arm | 320 MCCRAE ROAD, NOORAT VIC 3265 | 30045583 |  | Wind |  |  |  |  | 1 | Vicfire advised tree brought down power line.. Attending crew found willow had broken in high winds , contacted and brought down conductor | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | TRG002 | Vegetation: Trees Incident | Loss of supply | 24/03/2019 18:17 |  |  | 12438 | Roadway |  | 20190402PWA_07 | Infrastructure (network-based) | -38.1838 | 142.8941 | 1 | Powercor | Report | 15659 | 0.039097 | 22kV AC | Warrnambool Airport Ndb | 3265 | Noorat | Trees
On arrival crew isolated supply and carried out repairs. | 325-341 GREIGS ROAD, TRUGANINA VIC 3029 | 32168013 | Vandalism;Copper theft | [6 empty] | A customer reported a power outage at the incident location. Upon arrival, a Powercor crew found that the UG service and pit had been vandalised. The service cable approx. 100m was missing. The customer cable also damaged so a defect notice issued. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft | Loss of supply;Damage to network assets | 43588.4861 |  |  | 12446 |  |  | 20190403PWA_03 | Infrastructure (network-based) | -37.746 | 144.676 | 1 | Powercor | Report | 15671 | 0.025321 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
On arrival crew isolated supply and carried out repairs. | 947-1053 EXFORD ROAD, EXFORD VIC 3338 | 30257137 | Copper theft | [6 empty] | Report of public lights not working at incident location. Crew found underground cables missing on both sides of Exford Rd. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN011 | Copper theft | Loss of supply;Damage to network assets | 43588.3632 |  |  | 12450 |  |  | 20190403PWA_05 | Infrastructure (network-based) | -37.7446 | 144.5491 | 1 | Powercor | Report | 15677 | 0.028897 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Exford | Other
Fault truck dispatched to investigate. Wood HV crossarm had burnt had failed. Supply de-energised and repaired | 7 WATTLE DRIVE, WATSONIA VIC 3087 | LIS906803 |  |  |  | Defective component |  |  |  | E0018047 - report of HV crossarm fire. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | WT09 | Old brown pin type fog insulator has failed resulting in tracking causing the cross arm to burn and fail | Pole-top fire | 29/03/2019 10:11 | 1 | Negligible: no ground fire | 12443 |  |  | 20190403SPN_02 | Infrastructure (network-based) | -37.7171 | 145.0808 | 1 | AusNet Services Distribution | Report | 15667 | 0.026315 | 22kV AC | Essendon Airport | 3087 | Watsonia | AF Other
Attend site and make safe. Repaired conductor. | 31 HUON CREEK ROAD, WODONGA VIC 3690 | span pole: 5202909 to 5202910 |  | Fallen | [5 empty] | E0018410 - A council owned poplar tree in a declared area (council responsibility) suffered total root plate failure and has brought multiple spans of conductor to the ground. Poplar tree has failed at ground level, at base of tree and taken down a span of HV. This has caused other spans to fail. There was a small fire on the nature strip approx. 2m sq around transformer pole 5209208. | Conductor (bare) | 0 | 0 | 0 |  | WOTS25 | Vegetation: Trees Incident | Grassfire | 43802.8125 | 1 | Localised: less than 10 sq.m | 12447 |  |  | 20190403SPN_04 | Infrastructure (network-based) | -36.144 | 146.8802 | 2 | AusNet Services Distribution | Report | 15673 | 0.0025046 | 22kV AC | Wangaratta Aero | 3690 | Wodonga | Trees
Fault Crew broke and remade the O/H Service Cable connections at the Reticulation Pole | 25 DUNSMORE ROAD, HIGHTON VIC 3216 | 30058441 |  |  |  | Corrosion |  |  | 2 | person received an electric shock from a Water Urn when he made simultaneous contact with his hand on the metal casing of the Water Urn and his bare feet whilst standing on the ground. | Aluminium twisted (grey) | 0 | 0 | 0 |  | GCY014 | Corroded O/H Service Neutral Conductor termination at the Reticulation Pole. | Minor shock | 43527.5833 |  |  | 12452 | Residential |  | 20190404PWA_02 | Infrastructure (customer connection) | -38.1766 | 144.3132 | 1 | Powercor | Report | 15679 | 0.039875 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
On arrival creww isolated supply and arranged repairs. | 417 DERRIMUT ROAD, TARNEIT VIC 3029 | 30226559 | Copper theft | [6 empty] | Contractor advises pits along Derrimut Road have been tampered with cables exposed. Cables stolen from multiple pits on Derrimut Road between Rebecca Promenade to Sayers Road along service lane. Pits exposed. There was no fire or reported injuries | Services cable;Services pit | 2 | 2 | 2 |  | LV001 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43649.625 |  |  | 12457 | Roadway |  | 20190404PWA_07 | Infrastructure (network-based) | -37.8467 | 144.688 | 1 | Powercor | Report | 15684 | 0.0076771 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
LEI attended. Supply quality monitoring subsequently conducted. no supply anomalies found | 445 TURNBULL ROAD, ARDMONA VIC 3629 | 32191252 |  |  |  | nil;Other |  |  | 2 | customer believes his Staff and Dairy Cows were experiencing electric shocks that were coming through the ground when in close proximity to an adjacent 220,000 Volt Transmission Line on his property. | Customer installation | 0 | 0 | 0 |  | MNA013 | No anomalies found. some minor dips in voltage apparently due to 30kW motor starting direct on line. | customer concern;Other | 20/02/2019 8:20 |  |  | 12459 | Agricultural |  | 20190404PWA_09 | Infrastructure (network-based) | -36.3704 | 145.3136 | 1 | Powercor | Report | 17003 | 0.026115 | Low voltage AC (<1kV) | Shepparton Airport | 3629 | Ardmona | Installation
on arrival crew isolated supply and carried out repairs | KILMORE ROAD, GISBORNE VIC 3437 | 30338661 | Copper theft | [6 empty] | Passer by reported electrical hazard at the incident address. Upon arrival fault crew found that unknown person/s stole 50M of 4 core 16mm copper wire from public lighting circuit between pole LIS 845162 & 845163. It is believed that a vehicle was used to pull the cable out from the conduit, one end had been cut adjacent to LIS 845162. No injuries or fires resulted from the actions of the thieves. | Services cable | 2 | 2 | 2 |  | GSB013 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43711.0833 |  |  | 12461 | Roadway |  | 20190404PWA_11 | Infrastructure (network-based) | -37.4726 | 144.5915 | 1 | Powercor | Report | 16998 | 0.017248 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
crew have made site safe Details have been captured so that repairs can be made | 1 BANKS DRIVE, DIGGERS REST VIC 3427 |  | Copper theft | [5 empty] | 2 | Copper theft of service cable supplying street lights | Services cable | 0 | 0 | 0 |  | SHM11 | Copper theft | Damage to network assets | 43681.6222 |  |  | 12481 | Residential |  | 20190408JEM_01 | Infrastructure (network-based) | -37.6213 | 144.7046 | 1 | Jemena | Report | 15714 | 0.021828 | Low voltage AC (<1kV) | Melbourne Airport | 3427 | Diggers Rest | Other
On arrival crew isolated supply,. Supply to be restored when remaining trees cut. | 359 FOLEYS ROAD, GORAE WEST VIC 3305 | 32128662 | Working too close to overhead lines | Within clearances | [5 empty] | Vicfire advised of grass fire caused by a large plantation gum tree falling across conductors. On arrival crew found that a large gum tree had fallen across SWER conductors causing a grass fire There was no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | PLD003 | Vegetation: Trees Incident | Grassfire | 43589.5938 | 1 | Small: 10 - 1000 sq.m | 12474 | Forest - plantation |  | 20190408PWA_03 | Infrastructure (network-based) | -38.288 | 141.5173 | 1 | Powercor | Report | 17044 | 0.022553 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3305 | Gorae West | Trees
Site isolated and repairs carried out to make site safe Supply to 1 customer restored | 1 HARVEST HOME ROAD, DARLEY VIC 3340 | Pole no. A007431 | Vandalism;Theft | [5 empty] | 1 | HV pole no. A007431 cut down by chainsaw and pole-mounted transformer stolen HV fuses operated and 1 customer lost supply | Pole (wood);Steel;Pole mounted | 0 | 0 | 0 |  | ST11 | Vandalism and theft | Loss of supply;Damage to network assets | 43681.6319 |  |  | 12484 | Peri-urban |  | 20190409JEM_02 | Infrastructure (network-based) | -37.6052 | 144.9716 | 1 | Jemena | Report | 15717 | 0.013531 | 22kV AC | Essendon Airport | 3340 | Darley | Other
On arrival crew isolated supply and carried out repairs. | 475 TELEGRAPH ROAD, MOUNT PROSPECT VIC 3364 | 31001430 |  |  |  | Defective component |  |  |  | Vicfire reported lines down, grass fire caused by lines down, wires sparking at incident location. Crew found a broken xarm and a broken conductor There was a ground fire of 2 x 30m2,, no injuries, no property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | BAN008 | Conductor tensile failure | Grassfire;Damage to network assets | 43681.5986 | 1 | Small: 10 - 1000 sq.m | 12485 | Roadway |  | 20190409PWA_02 | Infrastructure (network-based) | -37.3913 | 144.0575 | 1 | Powercor | Report | 15720 | 0.027478 | 22kV AC | Ballarat Aerodrome | 3364 | Mount Prospect | Crossarm
On arrival crew inspected assets for damage | 406 PAKINGTON STREET, NEWTOWN VIC 3220 | 32087669 |  | Animal |  |  |  |  | 1 | Powercor received a report from Vic FIre of an explosion and pole on fire in Pakington St. When crews arrived they found a possum had shorted across the HV switch. This resulted in some grass igniting on the pole which had grown up the pole along the earth cable and behind the possum guard approx. 1.5m above ground level. This was also the location of the end of the HV switch handle and it appears that an arc had occurred been the switch handle and possum guard. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Disconnector/isolator | 2 | 2 | 2 |  | GLE022 | Animal Incident | Pole-top fire | 43681.5986 | 1 | Negligible: no ground fire | 12487 | Roadway |  | 20190409PWA_04 | Infrastructure (network-based) | -38.1616 | 144.3445 | 1 | Powercor | Report | 15723 | 0.018362 | 22kV AC | Avalon Airport | 3220 | Newtown | Animal
On arrival crew carried out repairs | 19 WALSH STREET, DEEPDENE VIC 3103 | 30172368 | Working too close to overhead lines | [6 empty] | Customer at this address is renovating his house, while carrying a large piece of timber he has contacted the low voltage service which was then detached from the POA and fell onto the nature strip There was no fire. no reported injuries. | Service conductor | 2 | 2 | 2 |  | L009 | Uncontrolled movement of timber beam. | Loss of supply;Damage to network assets | 16/03/2019 12:20 |  |  | 13498 |  |  | 20190411PWA_04 | Infrastructure (network-based) | -37.8132 | 145.0668 | 1 | CitiPower | Report | 17009 | 0.034269 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Other
On arrival supply isolated. LEI investigating HVI reports Repairs arranged | TELSTRA TELEPHONE EXCHANGE, 3 WHITEHORSE ROAD, MOUNT CLEAR VIC 3350 | 33007773 |  |  |  | Mechanical vibration |  |  |  | Customers reported a power outage at the incident location . Upon arrival the crew found that a HV conductor on an intermediate pole fell on to below LV neutral. HVI reported in the area and the damages are being investigated. There was no fire, no reported injuries. | Conductor (bare);Insulator tie wires/connections | 2 | 2 | 2 |  | BAS034 | The tie broke, due to fatigue cracking, at the first wrap-on point, and then unwrapped completely as the conductor fell off the insulator. | HV injection;Loss of supply | 43803.4875 |  |  | 13505 | Roadway |  | 20190415PWA_01 | Infrastructure (network-based) | -37.6032 | 143.8678 | 1 | Powercor | Report | 16752 | 0.041549 | 22kV AC | Ballarat Aerodrome | 3350 | Mount Clear | Conductor
Fire brigade attended incident and put out fire safely Jemena work crew made area safe by isolating high voltage assets Jemena faults crew conducted repairs to HV conductor on the same day | 1 WATFORD CRESCENT, CRAIGIEBURN VIC 3064 | A026749 |  | Bird |  |  |  | Phase to earth | 1 | A bird caused a fault on high voltage conductors in Dorchester Street corner Watford Crescent (Craigieburn), causing the HV tie to burn off. ACR 12417 Craigieburn Road successfully reclosed twice. Burning fragments from the electrical explosion ignited a small grassfire on the opposite side of the road (Watford Crescent). A crow was found at the base of pole footpath, HV tie was broken and HV conductor came off insulator and was resting on crossarm. Photos are attached in the "Notes & Findings" section. | Dropper/bridge | 0 | 0 | 0 |  | ST33 | Bird Incident | Grassfire | 16/04/2019 9:19 | 1 | Localised: less than 10 sq.m | 13518 | Residential |  | 20190416JEM_01 | Infrastructure (network-based) | -37.595 | 144.9211 | 1 | Jemena | Report | 17745 | 0.030616 | 22kV AC | Melbourne Airport | 3064 | Craigieburn | Animal
Crew attended and inspected the cable for damage and ensured the site was safe. | 32 WATER STREET, BROWN HILL VIC 3350 | 30283126 | Vehicle | [6 empty] | A crew investigating an outage found that an unknown vehicle had contacted a communications cable above Water St, The force of the impact caused the communications cable to contact the overhead LV conductors. This resulted in hot debris falling to the ground, starting a small grass fire. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BAN015 | Unknown vehicle hit communication cable which in turn struck LV | Grassfire | 15/04/2019 14:52 | 1 | Localised: less than 10 sq.m | 13511 | Roadway |  | 20190416PWA_01 | Infrastructure (network-based) | -37.5552 | 143.8973 | 1 | Powercor | Report | 16938 | 0.02006 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Brown Hill | Vehicle
On arrival crew isolated supply and carriedout repairs | GOLF COURSE ROAD, EAST BENDIGO VIC 3550 | 30026717 |  |  |  | Leakage |  |  |  | Report received of a pole fire at incident location. On arrival crew found a crossarm with the end burnt off . There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | EHK022 | Excessive leakage current | Pole-top fire | 23/03/2019 10:17 | 1 | Negligible: no ground fire | 13528 | Roadway |  | 20190416PWA_07 | Infrastructure (network-based) | -36.7172 | 144.3496 | 1 | Powercor | Report | 16967 | 0.014019 | 22kV AC | Bendigo Airport | 3550 | East Bendigo | Crossarm
Fault crew and LEI dispatched to investigate. LEI carried out tests and found premise did not have a continuous Neutral Service Conductor back to the pole. Fault crew replaced faulty Neutral Screen service and restored supply | 26 WATTLE AVENUE, MONTMORENCY VIC 3094 | LIS930733 |  |  |  | Defective component |  | Phase to earth |  | E0018665 - Customer's REC reported plumber reported shock from water pipe at customer's premises. | Neutral screen | 0 | 0 | 0 |  | ELM31 | Apprentice Plumber Kristian Dockett received a shock from the conductive water pipe under the house. They said when they removed the Bonders from across the pipe a large blue spark occurred. Home owner was then notified of the incident and he contacted REC who had recently replaced the switchboard and main Earth back in January. Once onsite REC then contacted AusNet. Tests found premise did not have a continuous Neutral Service Conductor back to the pole. Further testing on the overhead neutral screen service cable once it was removed, found it was faulty. (neutral continuity was intermittent when the cable was disturbed). Fault truck replaced faulty service and all tests passed. Supply restored | Minor shock | 43773.5451 |  |  | 13510 | Residential |  | 20190416SPN_01 | Infrastructure (network-based) | -37.7146 | 145.1206 | 1 | AusNet Services Distribution | Report | 16758 | 0.018375 | Low voltage AC (<1kV) | Essendon Airport | 3094 | Montmorency | Other
Fault crew dispatched and replaced failed/melted Krone box | 2 DIXON STREET, SURF BEACH VIC 3922 | LIS2809076 |  |  |  | Defective component |  |  |  | E0018698 - fire reported at base of pole | Connector/termination | 0 | 0 | 0 |  | PHI11 | Krone box has failed on the pole resulting in small ground fire (1mx1m) at base of the pole. Cause of failure unknown | Grassfire | 43803.4688 | 1 | Localised: less than 10 sq.m | 13512 | Roadway |  | 20190416SPN_02 | Infrastructure (network-based) | -38.5066 | 145.2839 | 2 | AusNet Services Distribution | Report | 17809 | 0.010889 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Surf Beach | Connection
Fault crew dispatched to investigate. Red/White phase fuses had operated which fault crew replaced with BA fuses to restore supply. Normal protection operation and no repairs required | 195 DOLLAR ROAD, DUMBALK VIC 3956 | LIS2005307 |  | Unknown environment factor |  | Unknown technical factor |  |  | 1 | Customer reported hearing a loud noise in his paddock and noticed a small grass fire between poles 19 and 20 (LIS2005307). | Conductor (bare);Boric acid;No failed asset | 0 | 0 | 0 |  | LGA13 | Bird Incident | Grassfire | 15/04/2019 16:28 | 1 | Localised: less than 10 sq.m | 13514 |  |  | 20190416SPN_04 | Infrastructure (network-based) | -38.5189 | 146.1199 | 1 | AusNet Services Distribution | Report | 17048 | 0.033631 | 22kV AC | Morwell (Latrobe Valley Airport) | 3956 | Dumbalk | Animal
Supply to pit isolated and suction excavator used to expose conduits. | 37-39 MUNDY STREET, BENDIGO VIC 3550 | 60220124 | Unauthorised work | [5 empty] | 2 | REC received a shock when assisting to locate a buried pit and conduit. works were to isolate a streetlight supply from a pit so a unmetered supply could be installed for cctv camera. While excavating around the pit to locate the conduit to the pole the REC reached down to clean out some dirt with his hands and received a shock. | Services cable;Services pit | 0 | 0 | 0 |  | BGO024 | Cable insulation damaged during previous unauthorized works | Minor shock | 43742.5208 |  |  | 13537 | Roadway |  | 20190417PWA_06 | Infrastructure (network-based) | -36.7586 | 144.2842 | 1 | Powercor | Report | 17058 | 0.017575 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | Other
On arrival crew found no damage to conductors. | 1992 COLAC-BALLARAT ROAD, BEEAC VIC 3251 | 30052273 |  | Blown branch/vegetation | [5 empty] | A customer called concerned about a tree branch that had fallen onto the High Voltage conductors and started a fire. On arrival the crew found that a tree branch had fallen and contacted the HV conductors and then onto the ground. This caused a ground fire of approx. 750m2. The CFA did not notify Powercor of the fire at the time of their attendance. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CLC003 | Vegetation: Trees Incident | Grassfire | 16/04/2019 9:32 | 1 | Small: 10 - 1000 sq.m | 13540 | Roadway |  | 20190418PWA_02 | Infrastructure (network-based) | -38.1456 | 143.6297 | 1 | Powercor | Report | 16796 | 0.018552 | 22kV AC | Ballarat Aerodrome | 3251 | Beeac | Trees
Fault crew and LEI dispatched. Tree removed from O/H conductor and blown fuse replaced. No damage to DB assets. LEI confirmed HVI, affected customers isolated and meters replaced. | 42-44 ENNISMORE CRESCENT, PARK ORCHARDS VIC 3114 | LIS1205347 & LIS1204273 |  | Fallen | [5 empty] | E0018956 - report of tree contacting O/H HV conductors resulting in HVI | Conductor (bare) | 0 | 0 | 0 |  | RWN26 | Vegetation: Trees Incident | HV injection | 20/04/2019 19:30 |  |  | 13560 | Residential |  | 20190422SPN_04 | Infrastructure (network-based) | -37.7851 | 145.2177 | 2 | AusNet Services Distribution | Report | 16924 | 0.010514 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3114 | Park Orchards | Trees
all sites made safe and remedial action taken | 620 MT ATKINSON ROAD, TRUGANINA VIC 3029 | 30150413 | Vandalism;Copper theft | [6 empty] | Copper theft reported at various locations along Mount Atkinson Road, Truganina; Patrolling crew found vandalism and theft at following: Stolen copper [pole to pit] and LV leads from tranny to fuse box at lis LIS948948, Stolen pole to pit, LV u/g cable at LIS 948950. Stolen copper at LIS 987513, LV leads from Transformer made safe . There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 28/03/2019 14:25 |  |  | 13564 | Roadway |  | 20190423PWA_02 | Infrastructure (network-based) | -37.7976 | 144.6786 | 1 | Powercor | Report | 16961 | 0.032013 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Crew isolated and repaired. | 24 BOURKE STREET, KYNETON VIC 3444 | 34027420 | Vandalism;Copper theft | [6 empty] | Employee report of exposed live wires at public lighting columns on the Calder Hwy at the Trio Rd off-ramp. On arrival, crew found that 2 pits had been opened up and cables had been cut and attempted to be removed. The cables had been isolated in the attempt to remove the copper. One of the pit lids had been broken. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WND023 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/03/2019 16:54 |  |  | 13566 | Roadway |  | 20190423PWA_04 | Infrastructure (network-based) | -37.2582 | 144.4705 | 1 | Powercor | Report | 16959 | 0.011722 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3444 | Kyneton | Other
Fault crew attended and made safe. Follow-up required to repair damage. | 137 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 60320643 | Vandalism;Copper theft | [6 empty] | Theft of cable from pits/public lighting poles. No reported injuries or fire. Adrian (Maintenance Manager at school) reported there are 3 pits at the front of the school along Brooklyn Road that are open with exposed wiring, he believes some theft may have occurred. At least 6 pit lids have been taken off between Cahill drive and Coburns Rd along Brooklyn Rd. The wires have been pulled out and are exposed | Services cable | 2 | 2 | 2 |  | MLN013 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/03/2019 9:03 |  |  | 13571 | Roadway |  | 20190423PWA_07 | Infrastructure (network-based) | -37.701 | 144.5588 | 1 | Powercor | Report | 16955 | 0.018944 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
Underground crews are replacing the stolen cable. | 124-158 MANOR LAKES BOULEVARD, MANOR LAKES VIC 3024 | 30250325 | Vandalism;Copper theft | [6 empty] | Powercor crew report low voltage underground cable thefts between Balcombe Drive and Dalrymple Boulevard, Manor Lakes. Estimated 300meters + of cable stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | WBE024 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43469 |  |  | 13573 | Roadway |  | 20190423PWA_09 | Infrastructure (network-based) | -37.8769 | 144.5993 | 1 | Powercor | Report | 17358 | 0.0044248 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Other
On arrival crew isolated supply and commenced repairs. HVI being investigated | 396-402 SANDILONG AVENUE, IRYMPLE VIC 3498 | 30100024 |  |  |  | Leakage |  |  | 1 | pole fire reported at the incident location. Upon arrival, that the crew found HV cross arm bunt through. There were no injuries or ground fire. HVI reported. | Crossarm (wood) | 2 | 2 | 2 |  | MDA024 | Excessive leakage current | Pole-top fire;HV injection | 23/04/2019 14:48 | 1 | Negligible: no ground fire | 13580 | Roadway |  | 20190424PWA_02 | Infrastructure (network-based) | -34.2113 | 142.1806 | 1 | Powercor | Report | 16936 | 0.019537 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Emergency switching was undertaken to isolate the section, and the cross-arm was replaced under access authority conditions. | 2811 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302637 |  | Prone to salt deposition |  | Mechanical breakdown |  |  | 1 | A report was received of a HV cross arm requiring urgent replacement. The cross-arm had deteriorated at the bracing bolt due to constant tracking. | Crossarm (wood) | 0 | 0 | 0 |  | STO23 | Tracking had occurred over a period of time at the arm brace bolt deteriorating the cross-arm timber at that location. | Plant/equipment | 31/03/2019 18:18 | 1 | Negligible: no ground fire | 13575 | Roadway |  | 20190424UTD_01 | Infrastructure (network-based) | -38.3617 | 144.7808 | 1 | United Energy Distribution | Report | 17514 | 0.025182 | 22kV AC | Avalon Airport | 3942 | Blairgowrie | Crossarm
Service crew attended with an EIO. There was no access to unit 3 tenancy switchboard and due to meter damage was decided to isolate supply at service fuse on panel and remove and terminate load side tails at meter and issue defect notice. | UNIT 3 44 PICKETT STREET, DANDENONG VIC 3175 |  | Vandalism | [5 empty] | 2 | A UE service crew attended site for a service connection and found the meter had been tampered with and damaged. The meter had been pulled off panel as well as lower terminal cover broken off at fixing screw, neutral link cover on this panel had also been removed. | Smart meter | 2 | 2 | 2 |  |  | I(t is apparent that vandalism is the cause. | Damage to network assets | 43469.7708 |  |  | 13577 | Residential |  | 20190424UTD_03 | Infrastructure (network-based) | -37.9841 | 145.2081 | 1 | United Energy Distribution | Report | 17029 | 0.020714 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong | Other
Repaired underground cable | 1 NORMANBY DRIVE, GREENVALE VIC 3059 |  | Copper theft | [5 empty] | 2 | ref tbl# 179810 - Customer reported pit lids removed and exposed cables. Crew arrived to find copper theft in area and affected street lights | Cable;Services pit | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 27/04/2019 15:36 |  |  | 13588 | Residential |  | 20190427JEM_01 | Infrastructure (network-based) | -37.6517 | 144.8981 | 1 | Jemena | Report | 18440 | 0.028465 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
Crew isolated supply and replaced crossarm | BENDIGO-PYRAMID ROAD, MITIAMO VIC 3573 | 31005276 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. A fault crew found that the cross arm burnt through and fallen debris caused a ground fire approx. 7*100 Sqm area. | Crossarm (wood) | 0 | 0 | 0 |  | CHA006 | excessive leakage current | Pole-top fire | 26/04/2019 14:36 | 1 | Negligible: no ground fire | 13590 | Roadway |  | 20190429PWA_01 | Infrastructure (network-based) | -36.2675 | 144.2321 | 1 | Powercor | Report | 16935 | 0.031932 | 22kV AC | Bendigo Airport | 3573 | Mitiamo | Crossarm
Fault crew dispatched. HV line isolated and supply restored following conductor repair and re-sagging. Follow up visit has been organised to fit armour rods on all poles in this street. Further investigation underway to determine root cause of conductor break | 25 MARINE STREET, CAPE PATERSON VIC 3995 | WGI22 |  |  |  | Mechanical breakdown |  | Phase to earth | 0 | E0019058 - report of live HV conductor on the ground | Conductor (bare) | 0 | 0 | 0 |  | LIS2028039 | Existing HV Conductor broke under the tie at pole LIS2028039 and fell to ground. Protection failed to operate and HV conductor remained alive on ground. Police in attendance to protect public. HV line isolated and supply restored following conductor repair and re-sagging. Follow up visit has been organised to fit armour rods on all poles in this street. Cause of conductor break unknown at this stage and further investigation is currently underway to determine root cause of conductor break. Asset inspection procedures being reviewed to ensure similar conductor breaks are identified and rectified | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/04/2019 8:30 |  |  | 13595 | Roadway |  | 20190429SPN_02 | Infrastructure (network-based) | -38.6722 | 145.6082 | 1 | AusNet Services Distribution | Report | 16922 | 0.018752 | 22kV AC | Moorabbin Airport | 3995 | Cape Paterson | Conductor
CFA extinguished the grass fire, approximately 1 sq m. Attending faults crew replaced the pole transformer and undertook environmental clean up of oil. | 71 EAST ROAD, PEARCEDALE VIC 3912 | 3300039 |  |  |  | Electrical breakdown |  |  | 1 | Customer reported transformer made loud bang and blowing smoke. On attendance, fault crew found CFA had extinguished a small grass fire at the base of the pole. | Pole mounted | 1 | 1 | 0 |  | HGS33 | The 50kVA transformer sustained an internal flashover with the tank rupturing and oil spilliung onto the grass below and starting a small fire. | Loss of supply;Grassfire | 43559.3958 | 1 | Localised: less than 10 sq.m | 13596 | Roadway |  | 20190429UTD_02 | Infrastructure (network-based) | -38.2189 | 145.2415 | 1 | United Energy Distribution | Report | 17027 | 0.04008 | 22kV AC | Moorabbin Airport | 3912 | Pearcedale | AF Other
Fault truck removed existing service cable to property and installed new service cable CTA re-tested property, all required VESI tests passed | 27 GUTHRIE STREET, BRUNSWICK WEST VIC 3055 | 30158221 |  |  |  | Corrosion |  | Phase to earth |  | Brenda was showering at the time; she received an electric shock when she made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Service conductor | 2 | 2 | 2 |  | WB013 | Corroded connection at pole end | Minor shock | 29/10/2018 7:00 |  |  | 10650 | Residential |  | 20181115PWA_05 | Infrastructure (network-based) | -37.7732 | 144.943 | 1 | CitiPower | Report | 13504 | 0.03544 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Connection
crew attended, referred to ESV Re- attended and advised that scaffolding is not to be disturbed in vicinity of service line until covering applied and a PTW issued by CitiPower, refer appended document. | 91 GRANGE ROAD, TOORAK VIC 3142 | 30216271 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | CitiPower officer attending site to assess conditions for a permit to work found scaffolding had been erected in vicinity of service line prior to covering or permit to work issue. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  | TK001 | unauthorized work | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/11/2018 10:00 |  |  | 10651 | Residential |  | 20181115PWA_06 | Infrastructure (network-based) | -37.834 | 145.0118 | 1 | CitiPower | Report | 13505 | 0.040668 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Other
A signed CES was available. Site was deemed safe to connect so supply was restored. | 89 SHACKLETON STREET, BELMONT VIC 3216 | 32074165 | Unauthorised work;Caused by REC/contractor | [5 empty] | 2 | M&S crew attended appointment and found the REC had already removed the fuse and meterbox so that he could replace the meterbox. A signed CES was onsite. The REC was also onsite doing other work. | Meter board (including fuses) | 0 | 0 | 0 |  | GCY014 | Interference | Damage to network assets | 23/10/2018 12:00 |  |  | 10652 | Residential |  | 20181115PWA_07 | Infrastructure (network-based) | -38.1724 | 144.332 | 1 | Powercor | Report | 13645 | 0.010911 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Other
On arrival crew isolated supply and carried out repairs | 174 BISH ROAD, MURRAWEE VIC 3586 | 32161431 |  |  |  | Leakage |  |  |  | Customer reported a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase intermediate substation pole had a pole fire which burnt the intermediate crossarm. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 13/11/2018 21:51 | 1 | Negligible: no ground fire | 10660 | Roadway |  | 20181119PWA_01 | Infrastructure (network-based) | -35.3101 | 143.5246 | 1 | Powercor | Report | 13519 | 0.023597 | 22kV AC | Swan Hill Aerodrome | 3586 | Murrawee | Pole
On arrival crew isolated supply and carried out repairs | 4686 MURRAY VALLEY HIGHWAY, PIANGIL VIC 3597 | 32157511 |  |  |  | Leakage |  |  |  | Vicfire report pole fire near the incident location. Upon arrival fault crew found a pole fire had occurred, the pole had burnt internally. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | BBD014 | Excessive leakage current | Pole-top fire | 13/11/2018 20:50 | 1 | Negligible: no ground fire | 10661 | Roadway |  | 20181119PWA_02 | Infrastructure (network-based) | -35.0162 | 143.3125 | 1 | Powercor | Report | 13521 | 0.037442 | 22kV AC | Swan Hill Aerodrome | 3597 | Piangil | Pole
The crew made safe then repaired the damage to eight sites. The public lights were returned to service. | GREEN HILL ROAD, EYNESBURY VIC 3338 | 35214236 | Vandalism | [6 empty] | Crew were requested to investigate issues with public lights at the incident sites (X8). On arrival the crew found that vandals / thieves had removed the covers from a number of public lighting pits and vandalized the contents. Connectors and had been removed from the affected pits. No copper was stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN011 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 26/10/2018 22:58 |  |  | 10665 | Roadway |  | 20181120PWA_02 | Infrastructure (network-based) | -37.7451 | 144.5531 | 1 | Powercor | Report | 13525 | 0.0064444 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Eynesbury | Other
Crew attended site and the pit was isolated then removed / site made safe. | 15 FULHAM AVENUE, SOUTH YARRA VIC 3141 | 30216663 | Vandalism;Copper theft | [6 empty] | Customer phoned in to advise that the pit in front of their premise has been pulled out of the ground and vandalised. The cable between the pit and the krone switch on the pole had been ripped out of the ground causing damage to the krone switch. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | TK001 | Copper theft & vandalism | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/10/2018 8:04 |  |  | 10666 | Roadway |  | 20181120PWA_03 | Infrastructure (network-based) | -37.8385 | 145.0035 | 1 | CitiPower | Report | 13526 | 0.020958 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Other
Police attended the site and official police incident report is with Williamstown Police. Carried out temporary repairs to Sub Station door and damaged fence. | 515-519 KOROROIT CREEK ROAD, ALTONA VIC 3018 |  | Vandalism;Copper theft | [6 empty] | Joel Guy, System Operation Planner Operator advised of Intruder Alarms in Zone Sub AL. On arrival the Operator advised that unknown people have forced open and broken into AL ZSS Operator advised that possible copper wire may have been stolen. There was no fire, no reported injuries | Zone substation | 2 | 2 | 2 |  | AL | Copper theft | Damage to network assets | 27/10/2018 7:30 |  |  | 10667 | Industrial |  | 20181120PWA_04 | Infrastructure (network-based) | -37.8474 | 144.8089 | 1 | Powercor | Report | 13527 | 0.030912 | Not applicable | Laverton Raaf | 3018 | Altona | Other
Conductors isolated for repairs to be made and inspectors inspecting properties for signs of HVI Damage. | 201 WAIORA ROAD, HEIDELBERG HEIGHTS VIC 3081 |  |  | Blown branch/vegetation | Highly unlikely |  |  |  | 2 | HV and LV bare OH conductors down in various places along Wiora road. High Voltage Injection confirmed on white and red phases (south circuit of WIORA-DOUGHARTY substation). | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | HV injection;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2018 17:55 |  |  | 10680 | Residential |  | 20181121JEM_04 | Infrastructure (network-based) | -37.7322 | 145.0602 | 1 | Jemena | Report | 13547 | 0.024251 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3081 | Heidelberg Heights | Conductor
On arrival crew isolated supply and carried out repairs | 40 HOBBS ROAD, WYNDHAM VALE VIC 3024 | 30347412 | Copper theft | [6 empty] | Powercor employee reported copper stolen from up to 10 pits at the incident locations. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | WBE014 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/10/2018 14:40 |  |  | 10679 | Roadway |  | 20181121PWA_04 | Infrastructure (network-based) | -37.8668 | 144.6102 | 1 | Powercor | Report | 13539 | 0.013604 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
On arrival crew isolated supply and carried out repairs. | 89 STEVENSON STREET, KEW VIC 3101 | 30193114 | Vandalism;Copper theft | [6 empty] | Cathy Binos of (Rattray Group) advised damage to steel shroud on pole outside this property. Crew on site found damaged cable shroud, cabling between the pole krone switch and low voltage pit had been stolen. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | RTS-CW | Copper theft | Damage to network assets | 31/10/2018 10:08 |  |  | 10681 | Roadway |  | 20181121PWA_05 | Infrastructure (network-based) | -37.8092 | 145.0167 | 1 | CitiPower | Report | 13542 | 0.024376 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Other
Yarra tramway worker stopped work and made site safe by insulating AC spliced connection with high visibility insulating tape. Yarra tramway worker driven to hospital to be monitored and was discharge within two hours with no injuries and returned to work. Yarra trams contacted Jemena, and reported to ESV and WorkSafe. Jemena construction crew onsite replaced street light service cable and re-insulated street service connections. ESV's David Clarke has followed up with Jemena Works Practices (John Vasilopoulos) and Asset Risk & Assurance (Kit Lui) to obtain further information and assurances that the new connection is appropriate for the service. A copy of Jemena's response is reproduced below. ESV question #1 Can you look at the photo attached and confirm if this is an appropriate connection for the service. Jemena response I have consulted with Jemenaâ€™s asset management team and can confirm that this connection, and the previous connection prior to the work being conducted, are appropriate for public lighting services. ESV question #2 Recently a Yarra Trams employee received an electric shock from bare connections on this service and this photo was taken after repairs by Jemena. I am unsure if this is an acceptable method of connection with the electrical tape as insulation when IPCs may have been a better solution. Jemena response In regards to whether this is an acceptable method of connection, please note that the regulations and Jemena standards do allow for bare connections at pole tops. Further, all poles owned by tramways â€“ where Jemena assets are also attached â€“ receive a visual inspection of the Jemena assets on a cycle not exceeding five (5) years. Therefore, defects are unlikely to remain undetected and in this case, the inspector correctly identified no defect prior to the work being conducted. IPCs are also an acceptable method of connection where the conductor meets the minimum size required for an IPC. In this case, the public lighting service is far smaller than any IPC available to Jemena. To prevent recurrence of electric shock in future, Jemena would strongly recommend the following: â€¢ Tramways personnel re-train in the identification of live electrical assets, correct assessment of risk, and the correct application of control measures â€¢ ESV in consultation with WorkSafe confirm that the Yarra Trams SWMS is appropriate for this type of activity. ESV question #3 Also unsure if the service should be attached to the Yarra Trams asset. Jemena response With reference to Jemena assets attached to Yarra Trams poles, the alternative is untenable for both Jemena and Yarra Trams. There are cases where Yarra Trams assets are attached to Jemena poles, and conversely where Jemena assets to Yarra Trams poles. These mutual benefits are reflected in the longstanding arrangement where both parties are able to use a single pole rather than two poles being planted within centimetres of each other. | 106 MARIBYRNONG ROAD, MOONEE PONDS VIC 3039 |  |  |  |  | Age |  | Phase to earth | 2 | Tramway worker completing maintenance works on a tramway pole, reported receiving a shock to the back of his hand whilst adjusting the trolley cables and made contact with Jemena's service conductor. The service conductor electrical tape insulation was found to be spliced and deteriorated. Email correspondence with David Clarke of ESV has been attached in the "Notes and Findings" section Please also note that: This incident was assessed against Jemena's incident investigation procedure and did not warrant a formal investigation report. If ESV has further concerns, Jemena would be happy to discuss these face to face instead of via email. | Service conductor | 0 | 0 | 0 |  |  | Tramway worker inadvertently made contact with Jemena asset on tramways pole. The deteriorated electrical insulation tape on the service connection has since been replaced according to Jemena standards. | Minor shock | 17/11/2018 9:00 |  |  | 10686 | Roadway |  | 20181122JEM_02 | Infrastructure (customer connection) | -37.7716 | 144.916 | 1 | Jemena | Report | 15503 | 0.031847 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | OH Cable
The crew attended on site and made the site safe by isolating supply to the shed | GALVIN PARK SECONDARY COLLEGE, 101 SHAWS ROAD, WERRIBEE VIC 3030 | 32178756 | Vandalism | [6 empty] | Report received from an REC working for Wyndham City Council that a meter had been stolen and switchboard gutted with live mains exposed inside the brick enclosure. There was no fire, no reported injuries. | Meter board (including fuses) | 2 | 2 | 2 |  | WBE031 | Vandalsim | Damage to network assets | 43142.6944 |  |  | 10688 |  |  | 20181123PWA_01 | Infrastructure (network-based) | -37.8857 | 144.6524 | 1 | Powercor | Report | 13551 | 0.026056 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
On arrival crew carried out repairs | 97-121 MURRAY ROAD, THORNHILL PARK VIC 3335 | 30108502 | Working too close to underground cables | [6 empty] | Following a report of no supply at 121 murray rd rockbank a crew found significant road reconstruction work at incident location. A number of pole substations had their earthing systems interfered with. A number of disconnected underground services had been disturbed. There was no fire and no reported injuries. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN021 | Road forming works | Loss of supply;Damage to network assets | 43170.4271 |  |  | 10689 | Roadway |  | 20181123PWA_02 | Infrastructure (network-based) | -37.7149 | 144.6285 | 1 | Powercor | Report | 13552 | 0.026796 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Dug up
On arrival crew isolated supply and carried out repairs | 435 DAVIS ROAD, MOUNT COTTRELL VIC 3024 | 30306756 | Vandalism;Copper theft | [6 empty] | Customer reported someone had cut service at incident location. Crew found customers underground service cable had been disconnected in service pit and an attempt had been made to remove customers cable using chains and vehicle but cable remained in place with chain connected, they were possibly disturbed in the attempt to remove cable. There was no fire, no reported injuries | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Attempted copper theft & vandalism | Damage to network assets | 43231.5778 |  |  | 10690 | Roadway |  | 20181123PWA_03 | Infrastructure (network-based) | -37.8265 | 144.6547 | 1 | Powercor | Report | 13553 | 0.035235 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
Fault crew disptached. Repaired the conductor G&B. investigation found resident felling adjacent trees outside clearance space, contacted and damaged HV conductor. resident called in "line caught fire now out" mistaking flash over as "fire". site investigation found no sign of fire start. | THE SANCTUARY, 437 MAROONDAH HIGHWAY, MERTON VIC 3715 | 3913866 | Working too close to overhead lines | [6 empty] | E0005264 - report of tree fire following contact with HV conductor | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | No Go Zone (contact) | 26/11/2018 16:47 |  |  | 10697 |  |  | 20181127SPN_01 | Infrastructure (network-based) | -37.0004 | 145.7468 | 1 | AusNet Services Distribution | Report | 17787 | 0.029869 | 22kV AC | Mangalore Airport | 3715 | Merton | Trees
Jemena dispatched Network HV Operator to make safe and Faults crew dispatched to repair HV cable and conduit. | VAUGHAN STREET, ESSENDON FIELDS VIC 3041 | 11586941 | Working too close to underground cables |  |  |  | Not followed |  | 2 | 3rd Party Contractor installing customers conduit hit and damaged HV conduit and HV Cable outer sheath insulation. | Cable | 0 | 0 | 0 |  | AW 01 | Excavator contractor did not identify underground electrical assets | Loss of supply | 27/11/2018 19:10 |  |  | 10699 | Public space |  | 20181128JEM_01 | Infrastructure (network-based) | -37.7238 | 144.8926 | 1 | Jemena | Report | 13927 | 0.038183 | 22kV AC | Essendon Airport | 3041 | Essendon Fields | Dug up
The CitiPower Underground Crew attended the site to make safe and isolate the LV cables in the area. The damaged cables are to be fixed under a fault follow up. | GOSCHS PADDOCK, 112-158 OLYMPIC BOULEVARD, MELBOURNE VIC 3004 | 30180536 | Working too close to underground cables | [6 empty] | A third party, Fulton Hogan, advised the CitiPower Report Room that they had cut through a live underground public lighting cable. When the CitiPower faults crew arrived they found a damaged and exposed lv public lighting cables. There was no fire, no reported injuries or third party property damage | Cable | 2 | 2 | 2 |  | FR008 | Excavator pulled conduit damaging cable | No Go Zone (contact);Damage to network assets | 26/11/2018 2:47 |  |  | 10701 | Public space |  | 20181128PWA_02 | Infrastructure (network-based) | -37.8241 | 144.9875 | 1 | CitiPower | Report | 13709 | 0.038554 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Dug up
On arrival crew isolated supply and carried out repairs | 126 THE PARADE, OCEAN GROVE VIC 3226 | 30058011 | Working too close to overhead lines | [6 empty] | A customer informed a loud bang at the incident location. On arrival, the Powercor crew found that a broken LV conductor sitting on concrete pumping truck. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | DDL011 | Concrete pumper struck LV | Damage to network assets | 43292.5806 |  |  | 10702 | Roadway |  | 20181128PWA_03 | Infrastructure (network-based) | -38.2669 | 144.5296 | 1 | Powercor | Report | 13573 | 0.011559 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Vehicle
Crew replacing stolen underground cable and made site safe. | 555 RESERVOIR ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown person has stolen underground cable | Cable | 2 | 2 | 2 |  |  | Copper theft by unknown personnel | Loss of supply | 43171.516 |  |  | 10718 | Roadway |  | 20181203JEM_03 | Infrastructure (network-based) | -37.5685 | 144.6743 | 1 | Jemena | Report | 13594 | 0.035175 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew isolated supply and carried out repairs | 5 WHITES ROAD, MOUNT DUNEED VIC 3217 | 32073045 | Working too close to underground cables | [6 empty] | Sam from Yarra Valley Excavations called to report that he had dug up an LV cable at the incident location. On arrival the crew found that contractors installing light poles had inadvertently dug up a 3 core 16mm LV UG service cable, which didn't appear on their 'Dial before you dig' plans. There were no injuries, fires or third party damage. | Services cable | 2 | 2 | 2 |  | WPD022 | excavation work | No Go Zone (contact);Damage to network assets | 43354.6292 |  |  | 10724 | Roadway |  | 20181204PWA_06 | Infrastructure (network-based) | -38.2337 | 144.3336 | 1 | Powercor | Report | 13602 | 0.0087523 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Mount Duneed | Dug up
Replaced service cable | 98 SHAFTESBURY PARADE, THORNBURY VIC 3071 | 30184369 |  |  |  | Moisture ingress;Corrosion |  |  | 2 | Customer reports receiving an electric shock when she reached into her bath (full of water) and also when she touched the bath and shower taps. | Service conductor | 0 | 0 | 0 |  | NC013 | Corroded neutral screen | Minor shock | 43170.4583 |  |  | 10725 | Residential |  | 20181204PWA_07 | Infrastructure (customer connection) | -37.7596 | 144.9914 | 1 | CitiPower | Report | 13676 | 0.018355 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | OH Cable
Fault Crew made site safe, repaired damaged conduit and pit, replaced stolen cable and re-instated the supply to public lights and to the NBN cabinet. | HACKETTS ROAD, POINT COOK VIC 3030 | 30304594 | Vandalism;Copper theft | [6 empty] | David Williams, employee from NBN, reported no power supply on their COMMS cabinet located at the corner of Featherbrook drive and Hacketts road, Point cook. On arrival the Crew found that 4 service pits had been interfered with. The lights on the 3 poles were not operating. There was minor damage to a service pit and a conduit. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | WBE034 | copper theft/vandalism | Loss of supply;Damage to network assets | 43384.4292 |  |  | 10726 | Roadway |  | 20181204PWA_08 | Infrastructure (network-based) | -37.9073 | 144.7149 | 1 | Powercor | Report | 13604 | 0.017235 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Crew have repaired the damage, site has been made safe. | COBURNS ROAD, TOOLERN VALE VIC 3337 | 32174296 | Vandalism;Copper theft | [6 empty] | Powercor received reports that thieves have stolen the earthing from the substation pole and ripped the low voltage underground service out of the ground between the pole and customer's pit. A hammer was left on site near the pole. Melton Police have taken it for fingerprinting. There was no fire and no reports of injury. | Services cable | 2 | 2 | 2 |  | MLN014 | Copper theft/vandalism | Damage to network assets | 43445.4167 |  |  | 10727 | Roadway |  | 20181204PWA_09 | Infrastructure (network-based) | -37.6339 | 144.5731 | 1 | Powercor | Report | 13605 | 0.030641 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
Crew re-terminated the U/G Service Neutral Conductor at the existing Krone Fuse Switch located on the Reticulation Pole | 44-46 GEELONG ROAD, PORTARLINGTON VIC 3223 | 30330746 |  |  |  | Corrosion;Neutral fault |  |  | 2 | Person was attempting to unlock the installation Group Meter Panel located in the driveway opposite his Unit, when he received an electric shock as he made simultaneous contact with his hands while standing on the wet ground. | Any other type | 0 | 0 | 0 |  | DDL021 | Corroded U/G Service Neutral Conductor termination | Minor shock | 30/11/2018 7:30 |  |  | 10740 | Residential |  | 20181204PWA_22 | Infrastructure (network-based) | -38.1167 | 144.6421 | 1 | Powercor | Report | 13618 | 0.023694 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Portarlington | Connection
On arrival the crew confirmed a bird flashover and grass fire. One HV fuse was replaced. | 660 LEITCHVILLE-KERANG ROAD, LEITCHVILLE VIC 3567 | 33021808 |  | Bird | [5 empty] | A CFA inspector reported that at an unknown date it appears a bird flashed over on concrete pole substation at the incident location. The bird fell to ground igniting road side grass. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CHA005 | Bird Incident | Grassfire | 43143.5264 | 1 | Small: 10 - 1000 sq.m | 10741 | Roadway |  | 20181205PWA_01 | Infrastructure (network-based) | -35.8884 | 144.2496 | 1 | Powercor | Report | 13620 | 0.0020243 | 22kV AC | Bendigo Airport | 3567 | Leitchville | Animal
On arrival crew isolated supply and carried out repairs | 44 NORTHUMBERLAND ROAD, SUNSHINE NORTH VIC 3020 | 33077940 | Working too close to underground cables | [6 empty] | The site Manager Sam advised Powercor that an excavator had dug up and exposed a live mains cable at Sunshine College. On arrival the fault crew found that the 240mm LV UG cable between the pole and the customer's pillar, had been struck by the excavator and sustained damage to the White & Blue phases, resulting in the White & Blue fuses blown in the Krone box. There were no reported injuries or fire. | Services cable | 2 | 2 | 2 |  | SSE032 | Excavation work | Loss of supply;No Go Zone (contact) | 13/11/2018 12:47 |  |  | 10742 | Public space |  | 20181205PWA_02 | Infrastructure (network-based) | -37.7745 | 144.8412 | 1 | Powercor | Report | 13623 | 0.023197 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Dug up
The customers reported their equipment damaged so LEI was called. The LEI confirmed electrical equipment damage. The crew isolated supply and carried out repairs | 128 PENSHURST-WARRNAMBOOL ROAD, KOROIT VIC 3282 | 33098677 | Working too close to underground cables | [6 empty] | A customer and contractor reported UG dug up at the incident location. Upon arrival, the crew found that the LV UG cable had been damaged by the contractor while they were using bore machine. There was no fire or reported injuries. | Cable | 2 | 2 | 2 |  | KRT013 | Excavation works | No Go Zone (contact);Damage to network assets | 14/11/2018 11:15 |  |  | 10744 | Roadway |  | 20181205PWA_03 | Infrastructure (network-based) | -38.2902 | 142.3528 | 1 | Powercor | Report | 17370 | 0.0020127 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3282 | Koroit | Dug up
Isolated failed public light and replaced | 45 LAFAYETTE STREET, TRARALGON VIC 3844 | LIS2603888 |  |  |  | Defective component |  |  |  | E0004855 - report of street light head fire | Public lighting | 0 | 0 | 0 |  | TGN43 | This is an older public light where the igniter or starter has failed causing a head fire. Failed head has been removed and replaced it with new. | Pole-top fire;Melting or smoking only | 16/11/2018 21:56 | 1 | Negligible: no ground fire | 10747 |  |  | 20181205SPN_03 | Infrastructure (network-based) | -38.1976 | 146.5249 | 1 | AusNet Services Distribution | Report | 13632 | 0.023434 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | AF Other
Fault crew dispatched to investigate. Candling BA Fuse replaced | 1589 EUROA-MANSFIELD ROAD, GOORAM VIC 3666 | LIS3904896 |  |  |  | Candled fuse |  |  |  | E0005715 - reported fuse candling. No evidence of ground fire | Boric acid | 0 | 0 | 0 |  | BN1 | Candling BA fuse on s/stn. | Pole-top fire | 43171.6167 | 1 | Negligible: no ground fire | 10748 |  |  | 20181205SPN_04 | Infrastructure (network-based) | -36.8757 | 145.6133 | 2 | AusNet Services Distribution | Report | 13634 | 0.033094 | 22kV AC | Mangalore Airport | 3666 | Gooram | Fuse
Fault crew dispatched to investigate and make safe. Fuse replaced and supply restored | 59 RANGEVIEW AVENUE, WANGARATTA VIC 3677 | LIS5107251 |  |  |  | Candled fuse |  |  |  | E0005799 - reported candling HV fuse | EDO fuse | 0 | 0 | 0 |  | WN4 | Candled HV EDO Fuse on s/stn pole. No evidence of ground fire | Pole-top fire | 43232.2951 | 1 | Negligible: no ground fire | 10751 |  |  | 20181205SPN_06 | Infrastructure (network-based) | -36.3554 | 146.2961 | 1 | AusNet Services Distribution | Report | 13639 | 0.03045 | 22kV AC | Wangaratta Aero | 3677 | Wangaratta | Fuse
CitiPower crew attended and Isolated cable | 453 ST KILDA ROAD, MELBOURNE VIC 3004 | 10484247 | Working too close to underground cables | [5 empty] | 1 | Communications contractor for a Telco exposed and cut into HV underground cable causing the cable to fault. The person's hands were believed to be exposed to electrical flash and he attended hospital for a precautionary medical check. | Cable | 0 | 0 | 0 |  | FR031 | Interference with Cable in conduit | Minor shock;Loss of supply | 43232.5382 |  |  | 10756 | Construction |  | 20181206PWA_01 | Infrastructure (network-based) | -37.8403 | 144.9772 | 1 | CitiPower | Report | 13647 | 0.00065046 | 11kV AC | Essendon Airport | 3004 | Melbourne | Dug up
On arrival crew isolated supply and carried out repairs. | 9 HOCKINGS ROAD, DINGEE VIC 3571 | 32040819 |  |  |  | Corrosion |  |  |  | Vic Fire Reports small grass fire caused by sparks from pole at incident location. On arrival crew found small ground fire caused by a burn out porcelain fuse box. There was no injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | EHK024 | Overheated connection | Grassfire | 43232.8028 | 1 | Small: 10 - 1000 sq.m | 10759 | Roadway |  | 20181206PWA_02 | Infrastructure (network-based) | -36.4005 | 144.2301 | 1 | Powercor | Report | 13649 | 0.039416 | Low voltage AC (<1kV) | Bendigo Airport | 3571 | Dingee | Connection
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions. | DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806824 |  | Precipitation;Prone to salt deposition |  | Leakage |  |  | 1 | At 0142hrs on 29/11/2018, 22kV feeder MC 09 and circuit breaker reclosed to lockout. At the same time, MGE 32 circuit breaker successfully reclosed and held. During light misty rain, a pole fire occurred at pole No. LIS 1806824 located outside 24 De Havilland Road at the HV isolators (OA4083) which is the normal open point between 22kv feeders MC 06 and MC 09. The HV cross arm broke and a HV conductor was in close proximity to the LV conductors and the faults crew requested that a LEI attend as a HVI was suspected. The LEI tested properties in the vicinity and confirmed that a HVI did not occur. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MC 06 and MC 09 | Pole top tracking during light misty rain. | Pole-top fire | 29/11/2018 1:42 | 1 | Negligible: no ground fire | 10764 | Roadway |  | 20181206UTD_10 | Infrastructure (network-based) | -37.9878 | 145.1008 | 1 | United Energy Distribution | Report | 13654 | 0.0020799 | 22kV AC | Moorabbin Airport | 3195 | Mordialloc | Pole
White phase abc clamp was replaced. Site was evaluated and made safe. Supply was restored at 1725. | 5 DE CARLE STREET, COBURG VIC 3058 |  |  |  |  | Age |  |  | 2 | Aged ABC clamp burnt off resulted in loss of supply. | Conductor (insulated) | 0 | 0 | 0 |  |  | White phase abc clamp was Burnt Off. Due to lack of evidence it could not be confirmed why and how the clamp started burning. | Loss of supply;Melting or smoking only | 43293.6944 |  |  | 10767 | Public space |  | 20181207JEM_01 | Infrastructure (network-based) | -37.7544 | 144.9659 | 0 | Jemena | Report | 13931 | 0.014795 | 22kV AC | Essendon Airport | 3058 | Coburg | AF Other
On arrival crew isolated supply and carried out repairs | COONIMUR-PIANGIL ROAD, PIANGIL VIC 3597 | 32159605 | Crane, excavator or other construction/farming equipment | [6 empty] | ESV reported a tractor hit pole causing wire to come down at incident location. Crew found that a tractor towing orchard spraying equipment had knocked down a wooden SWER pole There was no fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | SHL002 | Tractor and implement struck pole | Loss of supply;Damage to network assets | 30/11/2018 6:56 |  |  | 10780 | Agricultural |  | 20181211PWA_01 | Infrastructure (network-based) | -35.051 | 143.2911 | 1 | Powercor | Report | 13678 | 0.031868 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3597 | Piangil | Vehicle
Overhead service line replaced | 10 BEAMISH STREET, WARRNAMBOOL VIC 3280 | 32195557 |  |  |  | Corrosion |  |  | 2 | Plumber was removing the Water Meter at the property when he received an electric shock as he made simultaneous contact between his hand on the metallic Water Meter and his knees while kneeling on the wet ground. | Service conductor;Neutral screen | 0 | 0 | 0 |  | WBL006 | Corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole. | Minor shock | 21/11/2018 9:00 |  |  | 10781 | Residential |  | 20181211PWA_02 | Infrastructure (network-based) | -38.3669 | 142.4678 | 1 | Powercor | Report | 13679 | 0.036231 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Replaced Service Cable | 6 WARATAH CRESCENT, PORTLAND VIC 3305 | 32127338 |  |  |  | Corrosion |  |  |  | Plumber was repairing a leaking galvanised Water Pipe under the house when he received an electric shock as he made simultaneous contact between his hand on the metallic Water Pipe and his body while lying on the wet ground. | Service conductor;Neutral screen | 0 | 0 | 0 |  | PLD006 | Corroded Neutral Conductor termination at the Pole Top | Minor shock | 22/11/2018 9:00 |  |  | 10783 | Residential |  | 20181211PWA_04 | Infrastructure (network-based) | -38.3638 | 141.5972 | 1 | Powercor | Report | 13681 | 0.028405 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
On arrival crew carried out repairs. | 668 JOEL SOUTH ROAD, JOEL SOUTH VIC 3384 | 30086384 |  |  |  | Fuse failed to eject |  |  |  | Vic Fire reported a small grass fire at the incident location. On arrival the fault crew found that an EDO had "hung Up" dropping hot material to the ground, igniting a grass fire approx. 6m x 25m in area There were no reported injuries. | EDO fuse | 2 | 2 | 2 |  | STL007 | Corrosion | Grassfire | 43416.7708 | 1 | Small: 10 - 1000 sq.m | 10798 | Agricultural |  | 20181213PWA_03 | Infrastructure (network-based) | -37.0724 | 143.0015 | 1 | Powercor | Report | 13702 | 0.014662 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3384 | Joel South | Fuse
On arrival crew isolated supply and carried out repairs LEI attended and checked premises for high voltage injection damage. | 285 DANDENONG ROAD, PRAHRAN VIC 3181 | 30218601 |  | Lightning |  |  |  |  | 1 | The CitiPower Control Room identified a fault on HV feeder BC013. Additionally, customers in Closeburn Ave, Prahran called in with no supply and damaged appliances. On arrival crew found conductor on the ground. The fallen conductor had made contact with the LV circuit below resulting in up to 10 HVI incidents being reported. There was no fire and no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | BC013 | Connection ruptured during storm conditions | HV injection;Loss of supply | 15/12/2018 5:16 |  |  | 10817 | Roadway |  | 20181218PWA_01 | Infrastructure (network-based) | -37.8592 | 145.0041 | 1 | CitiPower | Report | 13740 | 0.040604 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3181 | Prahran | Lightning
On arrival crew isolated supply and carried out repairs. | 394 LARISSA ROAD, NARING VIC 3636 | 30126292 |  | Bird |  |  |  |  | 1 | A pelican made contact with HV overhead conductors at incident location. one phase broke and fell to ground. protection operated as expected. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | NKA001 | Bird Incident | Loss of supply;Damage to network assets | 30/11/2018 4:22 |  |  | 10819 | Agricultural |  | 20181218PWA_03 | Infrastructure (network-based) | -36.0556 | 145.5955 | 1 | Powercor | Report | 13741 | 0.012049 | 22kV AC | Shepparton Airport | 3636 | Naring | Animal
Discussion on site and followup with third party involved. | 974 SISTERS-GARVOC ROAD, THE SISTERS VIC 3265 | 32058495 | Unauthorised access | [5 empty] | 2 | Interference with Powercor asset (In the vicinity of Sparrow 2 LIS number 408332) , asset/s accessed by third party to undertake inspection activities without permission. | Pole (wood) | 2 | 2 | 2 |  | TRG002 | Third party undertaking pole testing without Powercor permission. | Interference - unauthorised access to asset;Other | 18/12/2018 15:59 |  |  | 10823 | Agricultural |  | 20181218PWA_04 | Infrastructure (network-based) | -38.2208 | 142.7728 | 1 | Powercor | Report | 13747 | 0.013067 | 22kV AC | Warrnambool Airport Ndb | 3265 | The Sisters | Other
Further investigation found Voltage tests between independent earth and various points of the electrical installation, including the distribution assets, identified a severely corroded neutral screen of a copper neutral screened O/H service cable as the cause of the high impedance associated with the return path of the neutral current. The corrosion of the service cable-way due to damage to the outer sheath, the cause of which is unknown. Service crew replace the damaged portion of the cable. As a test, an NST was carried out on the installation, by the attending LEI that indicated a Pass result. | 7 VICTORIA STREET, COBURG VIC 3058 |  |  |  |  | Corrosion |  |  | 2 | Plumber and electrician reported sparks on the roof while doing repairs. No worker reported an electric shock. | Service conductor | 0 | 0 | 0 |  | CS3 | A severely corroded neutral screen of a copper neutral screened O/H service cable as the cause of the high impedance associated with the return path of the neutral current. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/12/2018 22:00 |  |  | 10833 | Commercial |  | 20181220JEM_01 | Infrastructure (customer connection) | -37.7433 | 144.9658 | 1 | Jemena | Report | 13762 | 0.010997 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | OH Cable
TThe attended Jemena fault crew tightened the loose split bolt clamp at reticulation pole of the neutral conductor and completed an NST test which indicated a PASS result. The attended LEI conducted final voltage tests between an independent earth to plumbing fixtures where the electric shock occurred, neutral bar at main switchboard and metallic meter box. Result : a steady 0.4 volts from no load to 0.7 volts on load was recorded. An NST test on the installation indicated a PASS result. The property was left ON supply. | 113 VICTORIA STREET, WILLIAMSTOWN VIC 3016 | 12033771 |  |  |  | Age;Mechanical breakdown |  |  | 2 | Michael received an electric shock yesterday at noon when he touched the water tap in the kitchen. Voltage tests between an independent earth and various parts of the electrical installation, including the tap and distribution assets, identified loose split bolt clamp at reticulation pole of the neutral conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and metallic pipes, this increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 7.9 V on the water piping system. | Service conductor | 0 | 0 | 0 |  | NT 15 | loose split bolt clamp at reticulation pole of the neutral conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and metallic pipes, this increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 7.9 V on the water piping system. | Minor shock | 21/12/2018 11:48 |  |  | 10838 | Residential |  | 20181221JEM_01 | Infrastructure (network-based) | -37.8592 | 144.8888 | 1 | Jemena | Report | 13770 | 0.0069491 | Low voltage AC (<1kV) | Laverton Raaf | 3016 | Williamstown | AF Other
Fault crew dispatched to investigate and make safe. Candled fuse replaced with new and supply restored. | 168 ROBBINS ROAD, BORALMA VIC 3682 | LIS 5105160 |  |  |  | Candled fuse |  |  |  | report of candled EDO fuse | EDO fuse | 0 | 0 | 0 |  | WN3 | Suspected damage due to lightning. No evidence of ground fire | Pole-top fire | 20/12/2018 17:15 | 1 | Negligible: no ground fire | 10836 |  |  | 20181221SPN_01 | Infrastructure (network-based) | -36.2304 | 146.42 | 2 | AusNet Services Distribution | Report | 18121 | 0.041071 | 12.7kV AC (SWER) | Wangaratta Aero | 3682 | Boralma | Fuse
Fault crew dispatched | 984 GORMANDALE-STRADBROKE ROAD, WILLUNG VIC 3847 | LIS 2607873 |  |  |  | Fuse failed to eject |  |  | 0 | E0006943 - report of hung up EDO fuse | EDO fuse | 0 | 0 | 0 |  | TGN41 | Fuse hang up only. No candling and no evidence of fire | Hung-up fuse only | 20/12/2018 22:32 |  |  | 10837 |  |  | 20181221SPN_02 | Infrastructure (network-based) | -38.2568 | 146.7934 | 2 | AusNet Services Distribution | Report | 13768 | 0.0033843 | 22kV AC | Morwell (Latrobe Valley Airport) | 3847 | Willung | Fuse
Site was made safe and repair undertaken. | AITKEN BLVD , CRAIGIEBURN VIC 3064 |  | Copper theft | [5 empty] | 2 | Stolen underground cable for street lights | Cable | 2 | 2 | 2 |  |  | An unknown person/s has stolen 5 bays of underground cable for street lights in Aitken Blvd | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/12/2018 23:40 |  |  | 10847 | Roadway |  | 20181227JEM_01 | Infrastructure (network-based) | -37.6289 | 144.9125 | 1 | Jemena | Report | 13780 | 0.041017 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
The 22kV polymeric insulators and LV tee-off cross arm were replaced and an assessment is to be completed in daylight to determine if the pole requires replacement. | 1510 FRANKSTON-FLINDERS ROAD, TYABB VIC 3913 | 1108044 |  | Prone to salt deposition |  | Leakage |  |  |  | Pole fire reported at pole No. LIS 1108044 located in Frankston-Flinders Road, Tyabb near the corner of Delepan Drive. A 22kV polymeric insulator failed that caused tracking to the LV tee-off cross arm with approximately 75mm of timber burnt away. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | HGS 33 | The cause can be attributed to salt borne contaminants as the pole is located in close proximity to Westernport Bay | Pole-top fire | 22/12/2018 2:07 | 1 | Negligible: no ground fire | 10848 | Roadway |  | 20181227UTD_03 | Infrastructure (network-based) | -38.2572 | 145.1894 | 1 | United Energy Distribution | Report | 13781 | 0.025225 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3913 | Tyabb | Pole
On arrival crew checked for damage to assets, none found | 116 VERNEY NORTH ROAD, CONGUPNA VIC 3633 | 33092637 |  | Bird |  |  |  |  | 1 | Customer reported fire at 116 Verney North road, Congupna. Upon arrival the fault crew found that a bird had flashed over substation pole P30 SHTS-NKA #1. The bird fell to ground igniting a grass fire of approximately 10M x 50M in area, CFA attended and extinguished the ground fire. There were no reported injuries, minor fence post damage. | Pole mounted | 2 | 2 | 2 |  | SHN011 | Bird Incident | Loss of supply;Grassfire | 29/12/2018 9:53 | 1 | Small: 10 - 1000 sq.m | 10855 | Roadway |  | 20190102PWA_02 | Infrastructure (network-based) | -36.3126 | 145.4229 | 1 | Powercor | Report | 13792 | 0.023934 | 22kV AC | Shepparton Airport | 3633 | Congupna | Animal
The damaged junction box was removed from the POA and the faults crew repaired the connections. Supply was restored upon completion. | UNIT 2 14 ULUPNA ROAD, ORMOND VIC 3204 |  |  |  |  | Overheated connection |  |  |  | Caller reports fire at the POA. A SECV installed junction box at the POA caught on fire due to a probable loose connection that subsequently damaged the customers fascia board. In addition, there was some smoke damage to the installation but no wiring damage. | Connection box | 0 | 0 | 0 |  |  | A probable loose connection in the SECV installed junction that damaged the customers fascia board was the most likely cause. | Property | 43466.5743 | 1 | Negligible: no ground fire | 10853 | Residential |  | 20190102UTD_01 | Infrastructure (customer connection) | -37.9026 | 145.0434 | 1 | United Energy Distribution | Report | 13786 | 0.0014988 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Ormond | Connection
On arrival crew isolated supply and carried out repairs | 5 BROWN STREET, CALIFORNIA GULLY VIC 3556 | 30025130 | Working too close to underground cables | [6 empty] | A contractor working for Telstra contacted an underground service cable at the incident location. The conduit was fractured. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | EHK031 | Exavator struck underground service | Loss of supply;No Go Zone (contact);Damage to network assets | 43263.6889 |  |  | 10862 |  |  | 20190103PWA_04 | Infrastructure (network-based) | -36.7273 | 144.2493 | 1 | Powercor | Report | 13801 | 0.0033171 | Low voltage AC (<1kV) | Bendigo Airport | 3556 | California Gully | Dug up
Supply isolated and repairs carried out | MOUNT ELIZA ROAD, RIDDELLS CREEK VIC 3431 | 60344388 | Vandalism;Copper theft | [6 empty] | A member of the public reported exposed wires at the bases of three lighting poles. on arrival crew reported there had been an attempt to steal underground service cables. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | GSB012 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43263.2951 |  |  | 10863 | Roadway |  | 20190103PWA_05 | Infrastructure (network-based) | -37.425 | 144.7286 | 1 | Powercor | Report | 13802 | 0.014219 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3431 | Riddells Creek | Other
On arrival crew isolated supply and carried out repairs | OLD CHARLTON-BOORT ROAD, WYCHITELLA VIC 3525 | 32028838 |  | Lightning |  |  |  |  | 1 | During lightning storm lightning struck pole 127 Borung line. The resultant lighting strike fractured the HV crossarm allowing conductor to rest suspended just above ground in a de-energised state. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | CTN001 | Lightning strike | Loss of supply;Damage to network assets | 43355.4167 |  |  | 10865 | Roadway |  | 20190103PWA_07 | Infrastructure (network-based) | -36.2234 | 143.5647 | 1 | Powercor | Report | 13804 | 0.034235 | 22kV AC | Swan Hill Aerodrome | 3525 | Wychitella | Lightning
crew attended and repaired connections | 19 JAMES STREET, PORT FAIRY VIC 3284 | 32196810 |  |  |  | Corrosion |  |  |  | Several patrons at the Caravan Park reported receiving an electric shock at the time of showering as they made simultaneous contact between their hands on the metallic taps and their bare feet while standing on the wet concrete shower base. Additionally, several patrons also reported receiving an electric shock when operating an external tap as they made simultaneous contact between their hands on the metallic tap and their bare feet while standing on the wet ground | Dropper/bridge | 0 | 0 | 0 |  | Krt022 | Corroded Neutral Bridge at the Reticulation Pole and a corroded O/H Service Neutral Conductor termination at the Connection Box located at the Service Pole | Minor shock | 43293.375 |  |  | 10867 | Commercial |  | 20190104PWA_01 | Infrastructure (network-based) | -38.3864 | 142.2341 | 1 | Powercor | Report | 13806 | 0.012462 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Connection
On arrival crew isolated supply and carried out repairs | 10 SCOTSBURN STREET, HAWTHORN VIC 3122 | 30202117 |  |  |  | Overheated connection |  |  |  | VicFire called the CitiPower Report Room to advise of a pole fire at 10 Scotsburn St, Hawthorn. On arrival the CitiPower overhead faults crew found an FOLCB and LV cable to 10 Scotburn St, Hawthorn to have heat damage causing it to fall to the ground. The crew observe charring marks on the ground of approx. 1sqm. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | CL036 | Connection failure - Insufficient remains to determine cause further | Grassfire | 43466.1493 | 1 | Localised: less than 10 sq.m | 10869 | Roadway |  | 20190104PWA_03 | Infrastructure (customer connection) | -37.8323 | 145.0288 | 1 | CitiPower | Report | 13810 | 0.021541 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Connection
corroded Neutral connection replaced by faults truck | 33 GRAMMAR STREET, WENDOUREE VIC 3355 | 32008289 |  |  |  | Corrosion |  |  |  | The customer was having a shower at the time received an electric shock when he simultaneously contacted the metallic water tap with his hands whilst standing in the shower. | Service conductor | 0 | 0 | 0 |  | BAN001 | Corroded service neutral connection at POA | Minor shock | 14/12/2018 12:00 |  |  | 10870 | Residential |  | 20190104PWA_04 | Infrastructure (customer connection) | -37.5345 | 143.8344 | 1 | Powercor | Report | 13809 | 0.017166 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | OH Cable
On arrival crew isolated supply and carried out repairs | COURT OF APPEAL, 455-469 LONSDALE STREET, MELBOURNE VIC 3000 | 30207025 | Working too close to underground cables | [6 empty] | The CitiPower Report Room was advised that a third party had made contact with an underground cable in the laneway behind 459 Lonsdale St, Melbourne. On arrival the CitiPower faults crew found a Plumbing Contractor has made contact with and pierced a Low Voltage cable with a screw driver. There was no fire, no injuries sustained or third party property damage. | Cable | 2 | 2 | 2 |  | LQ024 | Plumber relocating fire service using screw driver penetrated into core of cable. | No Go Zone (contact);Damage to network assets | 29/12/2018 12:09 |  |  | 10871 | Commercial |  | 20190104PWA_05 | Infrastructure (network-based) | -37.8134 | 144.9588 | 1 | CitiPower | Report | 13811 | 0.0010463 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Other
On arrival crew isolated supply and carried out repairs | 190 POLLANDS ROAD, MOYSTON VIC 3377 | 32091855 |  |  |  | Insulator |  |  | 1 | Vic Fire reported conductors down and grass fire. On arrival crew found a SWER conductor had fallen to ground starting a small grass fire, There was no reported injuries | Conductor (bare);Insulators | 2 | 2 | 2 |  | ART033 | An insulator sheared off at the top shed in windy conditions allowing conductor to strike ground | Grassfire | 43556.9076 | 1 | Medium: 1000 sq.m - 10 ha | 10884 | Agricultural |  | 20190107PWA_03 | Infrastructure (network-based) | -37.2532 | 142.7199 | 1 | Powercor | Report | 13827 | 0.011737 | 12.7kV AC (SWER) | Hamilton Airport | 3377 | Moyston | AF Other
The attending Powercor Fault Crew re-terminated the existing Overhead Service Cable at the FMJB | 50 ONEILLS ROAD, MELTON VIC 3337 | 30119408 |  |  |  | Overheated connection |  |  | 2 | Person was in the bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic shower rose and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified that the neutral termination of the aluminum service cables was burnt out in the customer FMJB. | Service conductor | 0 | 0 | 0 |  | MLN014 | Neutral burnt off at terminal in Fused mains junction box | Minor shock | 26/12/2018 8:30 |  |  | 10885 | Residential |  | 20190107PWA_04 | Infrastructure (customer connection) | -37.678 | 144.5777 | 1 | Powercor | Report | 13825 | 0.024757 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
The attending Powercor Fault Crew replaced the Service Cable | 30 ENERGETIC STREET, LONG GULLY VIC 3550 | 33016485 |  |  |  | Corrosion |  |  |  | person was standing in front of the Meter Enclosure checking the Switchboard when she received an electric shock as she made simultaneous contact between her hand on the metal Meter Enclosure and her bare feet while standing on the damp concrete ground. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a Corroded Neutral Screened Conductor of an O/H Neutral Screened Service Cable between the Service Pole and the Customerâ€™s FOLCB | Service conductor | 0 | 0 | 0 |  | BET001 | Corroded Neutral Screened Conductor of an O/H Neutral Screened Service Cable between the Service Pole and the Customerâ€™s FOLCB | Minor shock | 27/12/2018 12:30 |  |  | 10888 | Residential |  | 20190107PWA_06 | Infrastructure (customer connection) | -36.7507 | 144.2545 | 1 | Powercor | Report | 13830 | 0.013896 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Long Gully | OH Cable
LEI and truck dispatched. Initial NST test failed. Voltage on the neutral was 157 volts. Found the mains box had burnt out and also the neutral in the pole box on pole 1305874 had corroded and broke off. REC replaced the mains box. Fault crew connected service directly to the mains. Supply tested safe and restored. | 33 CONSTANTINE AVENUE, ST ANDREWS BEACH VIC 3941 |  |  |  |  | Corrosion |  |  | 1 | Customer was washing clothes in the laundry and felt tingles from the tap. | Service conductor;Aluminium twisted (XLPE);Connection box | 0 | 0 | 0 |  |  | Neutral connection corroded at pole end | Minor shock | 20/12/2018 17:30 |  |  | 10883 | Residential |  | 20190107UTD_01 | Infrastructure (network-based) | -38.4224 | 144.8353 | 1 | United Energy Distribution | Report | 13823 | 0.00052662 | Low voltage AC (<1kV) | Moorabbin Airport | 3941 | St Andrews Beach | Connection
On arrival crew inspected assets for damage. | 39 RIVERSIDE ROAD, DOOEN VIC 3401 | 32091134 |  | Bird | [5 empty] | A crow caused a flashover at a Lightning Arrestor on a gas switch pole and this resulted in a small grass fire of 5mÂ² at the base of the pole. There was no reported injuries or third party property damage. | Any other type;Surge diverter | 2 | 2 | 2 |  | HSM005 | Bird Incident | Grassfire | 43647.7458 | 1 | Localised: less than 10 sq.m | 10902 |  |  | 20190108PWA_04 | Infrastructure (network-based) | -36.6967 | 142.2295 | 1 | Powercor | Report | 13846 | 4.6296e-06 | 22kV AC | Horsham Aerodrome | 3401 | Dooen | Animal
On arrival crew isolated supply and carried out repairs. | 239A HARKNESS ROAD, HARKNESS VIC 3337 | 31024169 | Copper theft | [6 empty] | During routine maintenance, a call was recieved to report the theft of approx. 3m of HV earth from pole from incident location. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN022 | Copper theft | Damage to network assets | 19/12/2018 15:00 |  |  | 10915 | Roadway |  | 20190110PWA_05 | Infrastructure (network-based) | -37.6561 | 144.5368 | 1 | Powercor | Report | 13866 | 0.02322 | Earthing cable | Melbourne Airport | 3337 | Harkness | Other
Fault crew dispatched. Fuse replaced and supply restored | 172 FERNDALE-STRZELECKI ROAD, FERNDALE VIC 3821 | LIS2005124 |  |  |  | Candled fuse |  |  |  | E0007026 - report of candling fuse | EDO fuse | 0 | 0 | 0 |  | LGA24 | Candled EDO fuse. Replaced fuse and restored supply. | Pole-top fire | 17/12/2018 6:34 | 1 | Negligible: no ground fire | 10926 |  |  | 20190111SPN_05 | Infrastructure (network-based) | -38.3141 | 145.9084 | 1 | AusNet Services Distribution | Report | 13884 | 0.014201 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Ferndale | Fuse
Fault crew dispatched. Fuse replaced and supply restored | 27 CAMELOT COURT, WARRAGUL VIC 3820 | LIS2720623 |  | Bird |  | Defective component |  |  |  | E0007156 - Report of candled fuse | Boric acid | 0 | 0 | 0 |  |  | Bird Incident | Pole-top fire | 29/12/2018 21:21 | 1 | Negligible: no ground fire | 10927 |  |  | 20190111SPN_06 | Infrastructure (network-based) | -38.1642 | 145.907 | 1 | AusNet Services Distribution | Report | 13885 | 0.018797 | 22kV AC | Morwell (Latrobe Valley Airport) | 3820 | Warragul | Animal
Site visit confirmed fire was extinguished prior to arrival. Removed the isolators (switch #601495) as they are not required to operate the network and re bridged the HV tee-off. | MURRAY VALLEY HIGHWAY, HUON 3695 | 5214084 |  | Bird |  |  |  | Phase to earth | 2 | Fire at base of pole | Conductor (bare) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 13/01/2019 21:20 | 1 | Small: 10 - 1000 sq.m | 10935 | Roadway |  | 20190114SPN_01 | Infrastructure (network-based) | -36.2588 | 147.0923 | 1 | AusNet Services Distribution | Report | 17766 | 0.0022002 | 22kV AC | Wangaratta Aero | 3695 |  | Animal
On arrival crew isolated supply and carried out repairs. | TAMERESK, 1528 MURRAY VALLEY HIGHWAY, BEVERFORD VIC 3590 | 32160477 |  |  |  | Leakage |  |  | 1 | During a patrol of assets after a feeder operation the remains of a crossarm fire was found at the incident location. there was no ground fire, no reported injuries or third party property damage | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Crossarm fire due to excessive leakage current | Pole-top fire | 43800.466 | 1 | Negligible: no ground fire | 10947 | Roadway |  | 20190115PWA_02 | Infrastructure (network-based) | -35.2285 | 143.4777 | 1 | Powercor | Report | 13921 | 0.011712 | 22kV AC | Swan Hill Aerodrome | 3590 | Beverford | Crossarm
On arrival crew isolated supply and carried out repairs. | 155 GALATEA ROAD, NEWTOWN VIC 3351 | 33002011 |  | Lightning |  | Fuse failed to eject |  |  |  | Customer reported following lightning strike pole caught fire. There was no ground fire, no reported injuries or third party property damage | EDO fuse | 2 | 2 | 2 |  | BAS021 | Lighning strike followed by EDO fuse hangup | Pole-top fire | 30/12/2018 13:30 | 1 | Negligible: no ground fire | 10948 | Forest - native (not park) |  | 20190115PWA_03 | Infrastructure (network-based) | -37.7035 | 143.6432 | 1 | Powercor | Report | 13922 | 0.034892 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3351 | Newtown | Lightning
Fault crew dispatched. Failed FOLCB replaced and supply restored | 42 SUMMERHAYS AVENUE, CAPE WOOLAMAI VIC 3925 | LIS2810560 |  |  |  | Defective component |  |  |  | report of junction box fire on pole | Connection box | 0 | 0 | 0 |  | WGI32 | Pole mounted FOLCB failed and melted. Unable to determine cause of failure and there was no evidence of ground fire | Melting or smoking only | 14/01/2019 13:46 |  |  | 10944 |  |  | 20190115SPN_04 | Infrastructure (customer connection) | -38.5223 | 145.3403 | 2 | AusNet Services Distribution | Report | 18137 | 0.029821 | Low voltage AC (<1kV) | Moorabbin Airport | 3925 | Cape Woolamai | Connection
Crew attended and inspected kiosk lv door, no damage found. Locked door. | 1 DOWNLAND PLACE, DINGLEY VILLAGE VIC 3172 |  | Vandalism | [5 empty] | 2 | A pad mount transformer door had been forced open. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  |  | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43678.625 |  |  | 10945 | Public space |  | 20190115UTD_03 | Infrastructure (network-based) | -37.9746 | 145.1309 | 1 | United Energy Distribution | Report | 15144 | 0.013564 | 22kV AC | Moorabbin Airport | 3172 | Dingley Village | Other
Fault crew and LEI attended. The LEI confirmed a high voltage injection occurred affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 5 LARNE AVENUE, DONVALE VIC 3111 | 7067404 |  | Fallen;Property owner/customer |  |  |  |  | 1 | Private tree from customers property at 48 Larne Avenue fell into HV/LV conductors pushing the HV into the open point at cnr of Larne Avenue and White lodge Court. The HV fell into the red phase LV on the Larne side and fell into the white phase on the White Lodge side. Both sides of the open point sustained HVI damage. | Conductor (bare) | 0 | 0 | 0 |  | NW13 | Vegetation: Trees Incident | HV injection | 43800.5938 |  |  | 10952 | Roadway |  | 20190115UTD_05 | Infrastructure (network-based) | -37.7968 | 145.1939 | 1 | United Energy Distribution | Report | 13935 | 0.017935 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3111 | Donvale | Trees
On arrival crew isolated supply and carried out repairs. | WYE VALLEY CVAN PK, 25 GREAT OCEAN ROAD, WYE RIVER VIC 3234 | 33040040 |  |  |  | Overheated connection |  |  |  | VicFire reported transformer on fire at big 4 holiday park, at incident location. On arrival crew found the centre phase HV dropper had overheated. There was no fire, no reported injuries or third party property damage. | Dropper/bridge | 2 | 2 | 2 |  | CLC007 | Overheated connection | Melting or smoking only | 31/12/2018 12:12 |  |  | 11954 | Commercial |  | 20190116PWA_02 | Infrastructure (network-based) | -38.6348 | 143.8898 | 1 | Powercor | Report | 14938 | 0.0078449 | 22kV AC | Avalon Airport | 3234 | Wye River | Connection
Crew attended and checked condition of assets | 1815 GEELONG ROAD, MOUNT HELEN VIC 3350 | 33000502 |  | Animal | [5 empty] | On 6/1/19 at approx. 01:33 hrs a possum caused a flashover on the cable head structure on Buninyong Pole 89 (LIS 342). The possum fell to the ground and caused a small ground fire covering an area of approx. 3 sq metres. The CFA attended and extinguished the fire. There was no third party damage or injury. | Surge diverter | 0 | 0 | 0 |  | BAS013 | Animal Incident | Grassfire | 43617.0646 | 1 | Localised: less than 10 sq.m | 11955 | Roadway |  | 20190116PWA_03 | Infrastructure (network-based) | -37.6234 | 143.8789 | 1 | Powercor | Report | 14942 | 0.023678 | 22kV AC | Ballarat Aerodrome | 3350 | Mount Helen | Animal
On arrival crew isolated supply and carried out repairs | 73-87 BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30249834 | Working too close to underground cables | [6 empty] | Civil contractor reported underground cable dug up, believed to be LV, On arrival crew found conduit broken but no wires exposed. There was no fire, no reported injuries or third party property damage. Contractor had a permit to work in place. | Services cable | 2 | 2 | 2 |  | SU034 | Excavating for road works contacted cable | No Go Zone (contact);Damage to network assets | 43678.4868 |  |  | 11956 | Roadway |  | 20190116PWA_04 | Infrastructure (network-based) | -37.8148 | 144.8034 | 1 | Powercor | Report | 14941 | 0.019711 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Dug up
Fault crew dispatched to investigate | 490 ANDERSONS INLET ROAD, BENA VIC 3946 | LIS 2008210 |  | Lightning |  | Defective component |  | Phase to earth |  | E0008129 - Pole fire reported and small grass fire in the area. | Pole top | 0 | 0 | 0 |  | LGA23 | The tie on the insulator has failed, possibly due to a lightning strike based on evidence of black charring on the insulator. The conductor has dropped and come in to contact with the pole, burning through the pole causing the top section to fail and fall to ground resulting in a small grass fire. | Grassfire | 16/01/2019 15:11 | 1 | Localised: less than 10 sq.m | 11960 |  |  | 20190117SPN_01 | Infrastructure (network-based) | -38.4535 | 145.739 | 2 | AusNet Services Distribution | Report | 14947 | 0.015472 | 22kV AC | Morwell (Latrobe Valley Airport) | 3946 | Bena | Lightning
CFA attended and extinguished fire Pole replaced under outage | 420 CONNS LANE, YANGERY VIC 3283 | 32195757 |  |  |  | Unknown technical factor |  |  | 1 | Emergency services reported a pole and ground fire . The attending crew found that a pole fire had occurred on pole 1 and a grass fire of some 6 by 20 metres had occurred on the roadside grass. No injuries or direct damage was noted. | Pole (wood) | 0 | 0 | 0 |  | KRT013 | pole fire - to be investigated | Grassfire | 21/01/2019 15:54 | 1 | Small: 10 - 1000 sq.m | 11980 | Roadway |  | 20190122PWA_01 | Infrastructure (network-based) | -38.3143 | 142.4293 | 1 | Powercor | Report | 14985 | 0.027095 | 22kV AC | Warrnambool Airport Ndb | 3283 | Yangery | Pole
Fire was out when Fault crew arrived. Supply was isolated, Krone box and wires replaced and power restored. | 1 LUSCOMBE DRIVE, DIAMOND CREEK VIC 3089 | LIS 926985 |  |  |  | Electrical overload |  |  |  | E0008397 - Krone box fire | Connection box | 0 | 0 | 0 |  | ELM15 | The sheeting on the leads coming out from the supply transformer to the TX ISOLâ€™s Krone box was melted and the spillage of the plastic fell to ground. Possible Overloaded TX / TX leads or loose terminals in the TX ISOL Krone box. | Pole-top fire | 21/01/2019 18:21 | 1 | Small: 10 - 1000 sq.m | 11979 |  |  | 20190122SPN_01 | Infrastructure (network-based) | -37.6691 | 145.1621 | 1 | AusNet Services Distribution | Report | 14983 | 0.002081 | Low voltage AC (<1kV) | Essendon Airport | 3089 | Diamond Creek | Connection
On arrival crew isolated supply and carried out repairs. | 140 PATULLOS ROAD, LARA VIC 3212 | 30076248 | Vandalism;Copper theft | [6 empty] | A passer-by reported vandalised UG pits at the incident location. Upon arrival, Powercor fault crew found that the street light cables had stolen. The UG pits/covers had been damaged. There were approx. 100m of 16mm cables from 7 light poles had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | FNS021 | Copper theft and vandalism | Damage to network assets | 43709.5903 |  |  | 11989 | Roadway |  | 20190123PWA_04 | Infrastructure (network-based) | -38.0212 | 144.3807 | 1 | Powercor | Report | 15000 | 0.037337 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Other
Crew attended and replaced grey service cable | 152 MONTGOMERY STREET, LAKE BOLAC VIC 3351 | 30082376 |  |  |  | Corrosion |  |  | 2 | Customer was showering when she received an electric shock as she made simultaneous contact with her hand on the metal Shower Rose and her bare feet while standing on the wet shower base. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  | ART033 | Corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole | Minor shock | 43678.375 |  |  | 11990 | Roadway |  | 20190123PWA_05 | Infrastructure (network-based) | -37.7152 | 142.8392 | 1 | Powercor | Report | 15001 | 0.0097801 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3351 | Lake Bolac | Connection
On arrival crew isolated supply and carried out repairs. | 184 CANTERBURY ROAD W, LARA VIC 3212 | 30351625 | Vandalism;Copper theft | [6 empty] | Report of cables cut and stolen at incident location. There was no fire no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | FNS021 | Copper theft and vandalism | Damage to network assets | 43709.734 |  |  | 11991 | Roadway |  | 20190123PWA_06 | Infrastructure (network-based) | -38.0321 | 144.3783 | 1 | Powercor | Report | 15002 | 0.013427 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Other
on arrival site made safe replacement pole organised. | 29 WARRENWOOD AVENUE, HOPPERS CROSSING VIC 3029 | 30240443 | Unknown external/community factor |  |  | Corrosion |  |  |  | A resident contacted PAL to advise that a steel URD lighting pole ( LIS 998192), within a walkway beside this house, had fallen to ground and electrical cables within the pole were exposed. Advised that the pole appeared rusted at the base and was now laying in the nature strip beside the pedestrian walkway. There was no fire, no reported injuries or third party property damage. | Pole (steel) | 2 | 2 | 2 |  | WBE013 | P/L pole failed It is unclear whether the pole came to ground solely due to atmospheric conditions, or whether it was assisted to ground by persons unknown. | Damage to network assets | 25/03/2019 12:50 |  |  | 13550 | Public space |  | 20190418PWA_10 | Infrastructure (network-based) | -37.8813 | 144.6957 | 1 | Powercor | Report | 16973 | 0.010287 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Pole
Site was made safe by Jemena Work Party. Faults crew installed new service line and LV crossarm. | 75 FRANCIS STREET, YARRAVILLE VIC 3013 |  |  |  |  | Age |  |  | 2 | TE#179657 - Report from MFB advising wire down on Francis St. Fault crew advised that service to no. 75 Francis Street had burnt off at pole end and come down. Minor burn marks at base of pole. | Service conductor;Neutral screen | 0 | 0 | 0 |  | YVE24 | Neutral screen service failed at pole and fell to ground in a de-energised state. | Loss of supply;Singeing or local charring/blackening only | 20/04/2019 14:22 |  |  | 13556 | Residential |  | 20190420JEM_01 | Infrastructure (customer connection) | -37.8215 | 144.8917 | 1 | Jemena | Report | 16811 | 0.022397 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | OH Cable
Fault crew dispatched and failed/burnt street light replaced. Street light returned to depot | 781 BURWOOD HIGHWAY, FERNTREE GULLY VIC 3156 | LIS1312340 |  |  |  | Defective component |  |  |  | E0018959 - Report of street light head on fire | Public lighting | 0 | 0 | 0 |  | FGY32 | Fault crew dispatched and found street light lantern had failed and burnt out. Cause of failure unkown at this time. Area immediately surrounding the PE cell holder was burnt and PE Cell fragments were found on ground but no evidence of ground fire. Lantern replaced and failed lantern returned to depot. | Pole-top fire | 21/04/2019 19:30 | 1 | Negligible: no ground fire | 13557 | Roadway |  | 20190422SPN_01 | Infrastructure (network-based) | -37.8808 | 145.2718 | 1 | AusNet Services Distribution | Report | 16931 | 0.027716 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Ferntree Gully | AF Other
Remnant pole cable ends were re-instated within their pits. Pit lids were re-instated onto their pit bodies. | 45 ZODIAC WAY, FRASER RISE VIC 3336 | 30322454 | Vandalism;Copper theft | [6 empty] | Ms Natasa Tomic reported exposed underground cabling at LIS 828275, P/L pole near bus stop in Hume Rd. A Powercor crew attended the site and noted pit lids lifted along Hume Rd once again. There was no fire, no reported injuries | Services cable;Services pit | 2 | 2 | 2 |  | SA011 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/03/2019 17:28 |  |  | 13563 | Roadway |  | 20190423PWA_01 | Infrastructure (network-based) | -37.7116 | 144.731 | 1 | Powercor | Report | 17359 | 0.012078 | Low voltage AC (<1kV) | Melbourne Airport | 3336 | Fraser Rise | Other
On arrival crew isolated supply | 16 PRINCES STREET, MILDURA VIC 3500 | 32149824 |  |  |  | Leakage |  |  | 1 | A pole fire reported at the incident location. Upon arrival, that the crew found HV cross arm burnt through. There were no injuries or ground fire. HVI damage was reported. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | MDA033 | Excessive leakage current | Pole-top fire;HV injection | 23/04/2019 14:47 | 1 | Negligible: no ground fire | 13579 |  |  | 20190424PWA_01 | Infrastructure (network-based) | -34.1927 | 142.1498 | 1 | Powercor | Report | 16839 | 0.011111 | 22kV AC | Mildura Airport | 3500 | Mildura | Crossarm
On arrival crew isolated supply and commenced repairs | 3219 SAN MATEO AVENUE, MILDURA VIC 3500 | 32146495 |  |  |  | Leakage |  |  | 1 | A pole fire reported at the incident location. HVI was found . There were no injuries or ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | MBN032 | Excessive leakage current | Pole-top fire;HV injection | 23/04/2019 22:40 | 1 | Negligible: no ground fire | 13581 | Roadway |  | 20190424PWA_03 | Infrastructure (network-based) | -34.2417 | 142.1035 | 1 | Powercor | Report | 16843 | 0.029566 | 22kV AC | Mildura Airport | 3219 | Mildura | Crossarm
Crew attended and disconnected supply at the pole. | 60 GREENPATCH DRIVE, BANGHOLME VIC 3175 |  | Vandalism;Unauthorised work;Crane, excavator or other construction/farming equipment | [5 empty] | 2 | A UE service crew attended site for an Abolishment appointment, and found the site under demolition and the meter had been run over by heavy equipment. | Other meter;Meter board (including fuses) | 2 | 2 | 2 |  |  | The crew spoke to the owner on site who advised his brother was using a bobcat which caused the damage to the meter. | Damage to network assets | 43773.4792 |  |  | 13576 |  |  | 20190424UTD_02 | Infrastructure (network-based) | -38.0422 | 145.1648 | 1 | United Energy Distribution | Report | 17023 | 0.035883 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Bangholme | Vehicle
Crews attended and patrolled the area, however were not able to determine the original cause of the fault. The fire brigade attended and extinguished the fire. A notification has been raised to install HV spreaders on the impacted span. | 24A WESTALL ROAD, SPRINGVALE VIC 3171 | 629253 |  |  |  | Conductor clashing |  |  |  | At 02:58 hrs on 3 April, an incident occurred that caused multiple device reclose operations, and resulted in a small fire (approximately 8sq m) in a grassy pole line easement. The pole line consists of two HV feeders on the same pole with horizontal construction. | Conductor (bare) | 0 | 0 | 0 |  | SV20, SV16 | The original cause of the incident was not determined. The cause of the grass fire was determined to be conductor clashing. | Loss of supply;Grassfire | 43528.1236 | 1 | Localised: less than 10 sq.m | 13578 | Industrial |  | 20190424UTD_04 | Infrastructure (network-based) | -37.9368 | 145.1424 | 1 | United Energy Distribution | Report | 17515 | 0.025029 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Conductor
The attending Jemena Fault Crew were unable to run a new service line, due to the poor condition of the two point connection box at the Customer's POA. Access was also restricted due to the Bull Nose verandah. Supply was disconnected at pole end and service cut away. The installation was left OFF supply. A defect notice was issued to the customer. The customer was also advised to engage a REC to rectify the Point Of Attachment. The customer was advised by the attending LEI to seek medical attention, as she mentioned a mild sensation in her hand. | 276 TYLER STREET, PRESTON VIC 3072 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Mrs Corina Carmelo was showering when she received an electric shock as she made simultaneous contact between her hand on the shower tap and her bare feet while standing on the wet shower base. Voltage tests between an independent earth and the metallic shower taps and water pipe system recorded a reading of 5.2 Volts. A voltage of up to 42.3 Volts was recorded with a increase of load to the installation using an electric Kettle. Further investigation confirmed the a broken Overhead Service Neutral Conductor, between the Reticulation Pole and the Customer's Point of Attachment. TechSafe report is attached in the "Notes & Findings" section. | Service conductor | 0 | 0 | 0 |  | CN07 | The service neutral conductor was broken between the Reticulation Pole and the Customer's Point of Attachment. This caused the return current path to flow through the earthing and metallic water pipe system resulting in an electric shock. | Minor shock | 25/04/2019 10:14 |  |  | 13584 | Residential |  | 20190425JEM_02 | Infrastructure (customer connection) | -37.7302 | 145.0069 | 1 | Jemena | Report | 16846 | 0.0034907 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | OH Cable
Crew isolated supply to make safe | 20 DALRYMPLE ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown person stole underground cable for street lighting | Cable | 2 | 2 | 2 |  | SBY13 | Unknown person stole copper | Damage to network assets | 28/04/2019 9:39 |  |  | 13589 | Roadway |  | 20190428JEM_01 | Infrastructure (network-based) | -37.5446 | 144.6892 | 1 | Jemena | Report | 16853 | 0.032332 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
crew attended and replaced cross-arm | WAKEFIELD, 139 LOWAN TANK ROAD, WALPEUP VIC 3507 | 32147524 | Crane, excavator or other construction/farming equipment |  |  | Leakage |  |  | 2 | Customer called to advise that the UHF antenna of his tractor had clipped low HV whilst he was spraying his crop. the attending crew found the HV cross-arm had burnt and the conductor was sitting at about 2.5m above the ground. | Crossarm (wood) | 0 | 0 | 0 |  | OYN001 | leakage current ignited wooden cross-arm | Pole-top fire;Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/04/2019 12:56 | 1 | Negligible: no ground fire | 13591 | Agricultural |  | 20190429PWA_02 | Infrastructure (network-based) | -35.1213 | 142.0199 | 1 | Powercor | Report | 17603 | 0.020646 | 22kV AC | Mildura Airport | 3507 | Walpeup | Crossarm
Fault crew dispatched. Candled fuse replaced | 87 QUEENS ROAD, SILVAN VIC 3795 | LIS1010930 |  |  |  | Candled fuse |  |  |  | E0019078 - Report of HV fuse Candling. No evidence of ground fire | Boric acid | 0 | 0 | 0 |  | LDL23 | HV BA fuse appears to have hung-up and then candled. No evidence of ground fire | Pole-top fire | 19/04/2019 17:58 | 1 | Negligible: no ground fire | 13597 | Roadway |  | 20190429SPN_03 | Infrastructure (network-based) | -37.8191 | 145.4205 | 1 | AusNet Services Distribution | Report | 16927 | 0.023735 | 22kV AC | Moorabbin Airport | 3795 | Silvan | Fuse
The branch was removed and minor repairs were made to the conductor. | 71 MADIGAN DRIVE, GLEN WAVERLEY VIC 3150 | 612985 |  | Blown branch/vegetation |  |  |  |  | 1 | UE received report from fire authority of a pole fire. On attendance, fault crew found a branch from a private tree had broken in strong winds and fallen onto the HV lines and ignited. | Conductor (bare) | 2 | 2 | 2 |  | MGE23 | Vegetation: Trees Incident | Other vegetation | 29/03/2019 22:04 | 1 | Negligible: no ground fire | 13593 | Roadway |  | 20190429UTD_01 | Infrastructure (network-based) | -37.8909 | 145.1884 | 1 | United Energy Distribution | Report | 17030 | 0.020834 | 22kV AC | Moorabbin Airport | 3150 | Glen Waverley | Trees
Crew attended, isolated and repaired cable | 79 CITY VISTA COURT,PLUMPTON,VIC,3335 | 30117188 | Working too close to underground cables | [5 empty] | 2 | Customer advised that an excavator has dug up an underground cable. Attending crew found a low voltage cable had been severed by an excavator trenching in the nature strip | Cable | 0 | 0 | 0 |  | SA009 | Location of cable unclear | Damage to network assets | 43528.5424 |  |  | 13602 | Roadway |  | 20190430PWA_02 | Infrastructure (network-based) | -37.7149 | 144.7268 | 1 | Powercor | Report | 16950 | 0.017814 | Low voltage AC (<1kV) | Melbourne Airport | 3335 |  | Dug up
isolated and replaced cabling | 124-158 MANOR LAKES BOULEVARD, MANOR LAKES VIC 3024 | 30250327 | Copper theft | [5 empty] | 2 | follow up of other copper theft incidents in the area found cables of lighting scheme to some 10 poles had been stolen | Services cable | 0 | 0 | 0 |  | WBE014 | copper theft | Damage to network assets | 43559.3986 |  |  | 13605 | Roadway |  | 20190501PWA_02 | Infrastructure (network-based) | -37.8769 | 144.5993 | 1 | Powercor | Report | 16948 | 0.032 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Other
Earthing replaced | 9 FOWLERS LANE, MYRNIONG VIC 3341 | 30104833 | Copper theft | [5 empty] | 2 | Asset Inspector reported HV/LV earths at substation have been stolen. | Conductor (bare) | 0 | 0 | 0 |  | BMH003 | interference- Copper theft | Damage to network assets | 43559.5437 |  |  | 13611 | Roadway |  | 20190501PWA_04 | Infrastructure (network-based) | -37.5936 | 144.3089 | 1 | Powercor | Report | 16947 | 0.030122 | Earthing cable | Avalon Airport | 3341 | Myrniong | Other
Jemena underground crew made repairs to vandalised sections of UG cable and restored power to street lights. | 10 WILLIAMS LANE, TAYLORS HILL VIC 3037 |  | Vandalism;Copper theft | [5 empty] | 2 | Unknown persons vandalised underground electricity pits along Calder Park Drive, North of Taylors Hill Boulevard | Cable;Services pit | 0 | 0 | 0 |  | SHM21 | vandalism / attempted copper theft | Damage to network assets | 43501.4778 |  |  | 13624 | Residential |  | 20190502JEM_01 | Infrastructure (network-based) | -37.708 | 144.7557 | 1 | Jemena | Report | 16903 | 0.034557 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Taylors Hill | Other
pole replaced | 9 KING STREET, SWAN HILL VIC 3585 | 32161090 |  |  |  | Leakage |  |  | 1 | Powercor received an alarm indicating that a high voltage automatic circuit recloser had opened. The attending crew found that a pole top fire had occurred which destroyed the top of a pole and dislodged overhead conductors. The crew indicated that the fire may have ignited in the vicinity of the low voltage cross-arm supporting isolators and an LV underground cable. No ground fire. | Conductor (bare);Conductor (insulated);Cable;Any other type | 0 | 0 | 0 |  | SHL004 | Unable to confidently determine, probable leakage current | Pole-top fire;Loss of supply | 43470.2618 | 1 | Negligible: no ground fire | 13625 | Roadway |  | 20190503PWA_01 | Infrastructure (network-based) | -35.3287 | 143.5566 | 1 | Powercor | Report | 16904 | 0.015424 | Low voltage AC (<1kV);22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Pole
Crew replaced approx. 25m of 4c 16mm LV Service Cable (pole to pit) and also replaced approximately 5m of Copper Earths that where cut away and stolen/taken. | 249 PARWAN SOUTH ROAD, PARWAN VIC 3340 | 33109117 | Vandalism;Copper theft | [6 empty] | On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through the 4c 16mm LV Service Cable and Earths on Pole 15 LIS-964762, "PARWANRAIL P15" 25kVA Three-Phase Pole Sub. Approximately 25m of 4c 16mm LV Service Cable (pole to pit was cut away and stolen/taken) and approximately 5m of Copper Earths was also cut away and stolen/taken. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Earth/earthing | 2 | 2 | 2 |  | BMH006 | Copper theft and van | Damage to network assets | 43620.384 |  |  | 13634 | Roadway |  | 20190506PWA_05 | Infrastructure (network-based) | -37.7256 | 144.4682 | 1 | Powercor | Report | 16915 | 0.0063021 | Low voltage AC (<1kV);Earthing cable | Avalon Airport | 3340 | Parwan | Other
On arrival crew isolated supply and carried out reports | 130 MCKENZIES ROAD, CARAMUT VIC 3274 | 32055849 | Crane, excavator or other construction/farming equipment | [6 empty] | Shaun Bailey reported that a tractor driver has hit the stay wire on one of the poles causing the mains wires to break and fall, unsure of exactly which pole, one that runs just on the northern side of McKenzies Road, quite close to the junction of Four Mile Road. Crew found a tractor had damaged a SWER pole and stay wire, with 5 to 6 bays of conductor on the ground, no ground fire, driver taken to hospital for medical review (Not electrically related). There was no fire, no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | TRG002 | Tractor entangled stay wire | Damage to network assets | 43681.6042 |  |  | 13636 | Agricultural |  | 20190506PWA_07 | Infrastructure (network-based) | -38.0049 | 142.5914 | 1 | Powercor | Report | 16917 | 0.0065775 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3274 | Caramut | Vehicle
An upstream ACR operated to clear the fault. When crews arrived at site, the fire authority was in the process of extinguishing the pole fire. Emergency switching was undertaken to isolate the faulty section. The pole and transformer were replaced under access authority conditions. | 2080 BONEO ROAD, FLINDERS VIC 3929 | 1313131 |  | Precipitation;Prone to salt deposition |  | Insulator;Leakage |  |  | 1 | An ACR tripped to lockout indicating a fault had occurred downstream. Subsequently a call was received from fire authority advising of a pole fire. On attendance, crews found top of pole had burnt through and fell. | Pole (wood);Pole mounted | 0 | 0 | 0 |  | DMA23 | The cause has been attributed to the centre phase dressing down insulator tracking in light rain conditions after a long dry spell and caused the pole fire. | Pole-top fire;Loss of supply | 21/04/2019 21:55 | 1 | Negligible: no ground fire | 13629 | Roadway |  | 20190506UTD_02 | Infrastructure (network-based) | -38.4779 | 144.9936 | 1 | United Energy Distribution | Report | 16909 | 0.036193 | 22kV AC | Moorabbin Airport | 3929 | Flinders | Pole
isolated and repaired | 2520 COBDEN-PORT CAMPBELL ROAD, PORT CAMPBELL VIC 3269 | 32056227 |  | Bird |  | Overheated connection |  |  |  | CFA reported pole fire at incident location. On arrival crew found bird nest material in FOLCB had caught fire and melted the box and conductor insulation. Melted plastic fell to the ground but did not start a fire. | Any other type | 0 | 0 | 0 |  | TRG003 | Bird Incident | Pole-top fire | 21/04/2019 5:34 | 1 | Negligible: no ground fire | 13641 | Roadway |  | 20190507PWA_02 | Infrastructure (network-based) | -38.6004 | 143.0012 | 1 | Powercor | Report | 17052 | 0.021344 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Port Campbell | Animal
Supply isolated, crossarm replaced. | 73 SCULTHORPE ROAD, NANGILOC VIC 3494 | 32144798 |  |  |  | Leakage |  |  | 2 | Customer reported broken cross arm at incident location. Upon arrival crew found that a intermediate cross arm burnt through at the kingbolt, the cross arm straps kept the conductors aloft. | Crossarm (wood) | 0 | 0 | 0 |  | RCT013 | excessive leakage current | Pole-top fire | 24/04/2019 20:44 | 1 | Negligible: no ground fire | 13648 | Roadway |  | 20190507PWA_08 | Infrastructure (network-based) | -34.464 | 142.3414 | 1 | Powercor | Report | 16997 | 0.0028426 | 22kV AC | Mildura Airport | 3494 | Nangiloc | Crossarm
The Jemena fault crews replaced the single phase overhead neutral screened copper service cable with a new twisted aluminium cable | 27 GOULBURN STREET, YARRAVILLE VIC 3013 |  |  |  |  | Age |  | Phase to neutral | 2 | Customer received an electric shock while he was having shower when he made simultaneous contact between his hand on the tap whilst standing bare foot in a wet area in contact with the metallic drain. Voltage tests between an independent earth and the taps (point of contact) and various parts of electrical installation, including the distribution assets, identified overhead neutral screened service cable damaged. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 12.3 Volts on the water piping system. TechSafe report is attached in the "Notes & Findings" section. ref TBL# 180315 | Conductor (insulated);Neutral screen | 0 | 0 | 0 |  |  | Damaged neutral screened service cable | Minor shock | 43682.4576 |  |  | 13655 | Residential |  | 20190508JEM_01 | Infrastructure (customer connection) | -37.8151 | 144.8891 | 1 | Jemena | Report | 17046 | 0.040475 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | OH Cable
On arrival crew isolated supply and carried out repairs | 5 KYNOCH STREET, DEER PARK VIC 3023 | 33077529 | Copper theft | [6 empty] | ESCUDO CONTRUCTIONS, Construction site manager called reporting that underground mains from pole to pit have been stolen. On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through the 4c 16mm LV Service Cable on LV Pole LIS-16678-7728 - Approximately 40m of newly installed 4c 16mm LV Service Cable - pole to pit was cut away and stolen/taken. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | SU021 | copper theft | Damage to network assets | 43742.6972 |  |  | 13667 | Residential |  | 20190510PWA_08 | Infrastructure (network-based) | -37.7656 | 144.7719 | 1 | Powercor | Report | 17064 | 0.035465 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Other
Emergency switching was undertaken to isolate the section of the fault. The cross-arm was replaced and conductors repaired under access authority conditions. Checks were also undertaken to confirm no HVI had occurred. | 2801 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302382 |  | Prone to salt deposition |  | Mechanical breakdown;Leakage |  |  | 1 | On 26 April at 9.00 am, feeder protection operated for feeder CB STO23 to open to lockout. Soon after, a call from the fire authority advised of wires down near the corner of Pt Nepean Rd and St Johns Wood Rd. On attendance, fault crews found a cross arm had failed due to internal tracking. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | STO23 | The HV cross-arm was inspected and found to have broken at the road side cross-arm strap. Signs of tracking and internal burning were evident at the break. | Pole-top fire;Loss of supply | 26/04/2019 7:39 | 1 | Negligible: no ground fire | 13665 | Roadway |  | 20190510UTD_02 | Infrastructure (network-based) | -38.3612 | 144.7817 | 1 | United Energy Distribution | Report | 17062 | 0.029416 | 22kV AC | Avalon Airport | 3942 | Blairgowrie | Crossarm
crew removed service | 32 MAY STREET, ALTONA NORTH VIC 3025 | 32170367 | Unauthorised work | [5 empty] | 2 | Crew attending site to abolish meter and service found that the service fuse had been removed and the meter /meter panel was missing. | Smart meter;Connection to meter;Meter board (including fuses) | 0 | 0 | 0 |  | BLT030 | Interference by parties unknown | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/03/2019 13:40 |  |  | 13673 | Residential |  | 20190514PWA_01 | Infrastructure (network-based) | -37.8338 | 144.8569 | 1 | Powercor | Report | 17071 | 0.013853 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Other
crew attended and replaced cross-arm on top circuit | 2351 KULKYNE WAY, IRAAK VIC 3494 | 30096877 |  |  |  | Leakage |  |  | 1 | Vic fire reported a pole fire. The attending crew found that a cross arm had burnt at the king bolt position. | Crossarm (wood) | 0 | 0 | 0 |  | RCT013 | excessive leakage current | Pole-top fire | 43470.4882 | 1 | Negligible: no ground fire | 13675 | Roadway |  | 20190514PWA_03 | Infrastructure (network-based) | -34.4477 | 142.3355 | 1 | Powercor | Report | 17073 | 0.012564 | 22kV AC | Mildura Airport | 3494 | Iraak | Crossarm
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI was dispatched to the site and undertook investigation to determine any damage to customers appliances and equipment. Faults crew also assisted the LEI to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed. | 32 MUNRO AVENUE, ASHBURTON VIC 3147 | 8802981 |  | Blown branch/vegetation |  |  |  |  | 1 | At 2150hrs on 7/05/2019, an 11kV ACR opened to lockout. During high winds, a branch from a council tree outside 28 Munro Ave broke and fell onto the HV conductors in the street. The branch caught fire, and the centre phase conductor fell onto the LV conductors below and resulted in HV injection into the neighbouring properties. | Conductor (bare) | 0 | 0 | 0 |  | EM5 | Vegetation: Trees Incident | HV injection;Loss of supply;Other vegetation | 43651.9097 | 1 | Negligible: no ground fire | 13677 | Roadway |  | 20190514UTD_01 | Infrastructure (network-based) | -37.8659 | 145.0757 | 1 | United Energy Distribution | Report | 17075 | 0.037891 | 11kV AC | Moorabbin Airport | 3147 | Ashburton | Trees
crew attended and restored supply | 265 STEWART ROAD, RED CLIFFS VIC 3496 | 30097852 | Working too close to overhead lines | [5 empty] | 1 | Tipper Truck made contact with HV conductor while unloading. Crew received information from local farmer: truck, Police and Work Safe had left the site prior to crew arrival | Conductor (bare) | 0 | 0 | 0 |  | RCT022 | intereference Tip truck unloading near line | Loss of supply;No Go Zone (contact) | 14/05/2019 15:19 |  |  | 13680 | Roadway |  | 20190516PWA_01 | Infrastructure (network-based) | -34.3164 | 142.2242 | 1 | Powercor | Report | 17082 | 0.025307 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Vehicle
On attendance, the fault crew found an active simpi crimp connection at the POA had failed. The crew replaced the connection and restored supply. No other damage was sustained by the crimp failure. | 169 MCKINNON ROAD, MCKINNON VIC 3204 | 2326708 |  |  |  | Overheated connection |  |  | 1 | Report received of a service wire that caught fire at the POA. | Service conductor;Connector/termination | 0 | 0 | 0 |  |  | It is likely the crimp connection had deteriorated over time and overheated. | Other electricity related | 43620.4896 | 1 | Negligible: no ground fire | 13684 | Residential |  | 20190520UTD_01 | Infrastructure (customer connection) | -37.9109 | 145.0379 | 1 | United Energy Distribution | Report | 17088 | 0.017457 | Low voltage AC (<1kV) | Moorabbin Airport | 3204 | Mckinnon | Connection
line isolated and conductor repaired | 119 COHUNA-MCMILLANS ROAD, COHUNA VIC 3568 | 33019552 |  | Lightning |  |  |  |  | 1 | Emergency services reported wire down and ground fire at the incident location. Upon arrival fault crew found that road side 22kV conductor failed approximately 20M from pole 41 Greens Rd. The downed conductor caused localised burning of grass in the immediate vicinity of where it came to rest, approximately 2.0M in burnt area comprised of small patches. | Conductor (bare) | 0 | 0 | 0 |  | CHA006 | probable previous lightning damage | Grassfire | 18/05/2019 17:30 | 1 | Localised: less than 10 sq.m | 13691 | Roadway |  | 20190521PWA_01 | Infrastructure (network-based) | -35.82 | 144.1938 | 1 | Powercor | Report | 17097 | 0.031786 | 22kV AC | Swan Hill Aerodrome | 3568 | Cohuna | Lightning
The service was disconnected. | 66 MOUNT STREET, HEIDELBERG VIC 3084 |  | Unauthorised access | [5 empty] | 2 | Metering & Service crew attended the site for a service and metering upgrade. The crew arrived they found a new meter panel, switchboard and associated wiring had already been installed and the outgoing load tails from one of the existing 1ph meters had been removed and the outgoing tails from the other existing 1ph meter had been relocated with the active tail directly connected to the old non-auto black main switch which was connected to the load side meter tail of the new installation wiring at the new meter panel with all of this energized and on supply. The REC and LEI were on site. No COES had been issued for the works completed in the above description. A new prescribed COES was issued once the 1ph supply and metering had been removed and the new 3ph alteration works were complete. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/04/2019 8:00 |  |  | 13696 | Residential |  | 20190523JEM_02 | Infrastructure (network-based) | -37.7575 | 145.062 | 1 | Jemena | Report | 17119 | 0.037722 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Heidelberg | Other
The fault crew replaced the connector and restored supply. | 1889 MALVERN ROAD, MALVERN EAST VIC 3145 | 2317286 |  |  |  | Overheated connection |  |  | 2 | UE received report from fire authority of a pole fire outside 1889 Malvern Rd Malvern. On arrival, the fault crew found an LV connection from the OH mains to an underground cable had burnt out. | Connector/termination | 0 | 0 | 0 |  |  | It is likely the connection of the insulation piercing connector with the bare conductor has deteriorated over time resulting in the connector overheating. | Plant/equipment | 13/05/2019 14:18 | 1 | Negligible: no ground fire | 13698 | Roadway |  | 20190523UTD_01 | Infrastructure (network-based) | -37.8681 | 145.0599 | 1 | United Energy Distribution | Report | 17105 | 0.012362 | Low voltage AC (<1kV) | Moorabbin Airport | 3145 | Malvern East | Connection
The attending construction crew were able to identify the problem as a high impedance of the neutral conductor at the junction box on the street pole in which the service line feeding the property was connected to. The attending construction crew replaced the neutral conductor between the junction box and the open wire at the pole. At this stage supply was restored 55 Queen St. The attending LEI then conducted an NST test at the group meter panel of the installation with a pass result recorded with a resistance of 0.11 ohms on the neutral conductor. A test between an independent earth and the neutral bar at the group meter panel now recorded 0V under no load. At this stage supply was restored to all units. Following power being restored further tests between an independent earth and the metallic water pipe system at unit three where the shocks were received now identified 2V under load. An NST test was also carried out at the installations switchboard with a pass result recorded. The installations were deemed safe and left on supply. | UNIT 3 55 QUEEN STREET, COBURG VIC 3058 |  |  |  |  | Neutral fault |  |  | 2 | ref tbl# 181081 - customer reported tingles from kitchen taps. The fault was first noticed when Jacqueline touched the kitchen tap with her bare wet hand while simultaneously making contact with the dry conductive tiles. Jacqueline was wearing socks and no shoes at the time of the incident. The attending LEI conducted voltage tests between an independent earth, the metallic water pipe system connected to earth and the neutral bar at the customers switchboard identified 13.6V under no load and 25.6V under load. The same result was recorded at neutral bar at the group meter panel of the installation. NST tests at the unit switchboard and the group meter panel of the installation both recorded a fail result. At this stage all units at the address were isolated and a Jemena truck crew called to investigate further. TechSafe report is attached in the "Notes & Findings" section. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  |  | Damaged neutral connection at pole end. Fault was found to be due to a high resistance at the T-join feeding the pit in which fed 4 and 6 Terrell Crt, Roxburgh Park. | Minor shock | 27/05/2019 12:41 |  |  | 13714 | Residential |  | 20190527JEM_02 | Infrastructure (network-based) | -37.7494 | 144.9501 | 1 | Jemena | Report | 17131 | 0.018299 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Connection
The crew disconnected and removed the existing unsafe NS overhead service. The REC to install a new POA and FOLCB in the required compliant location and provide a COES when completed. | 77 MELBOURNE ROAD, WILLIAMSTOWN VIC 3016 |  | Unauthorised access | [5 empty] | 2 | Metering & Service crew attended the site for a 1ph overhead supply alteration. When the crews arrived they found an existing 1ph neutral screen overhead service to the property which was connected to the side of the property and touching against the conductive down pipe. The REC had removed the service fuse, disconnected and cut away the customer mains, removed the distributors electricity meter and existing meter panel and had installed a new 1ph FOLCB, new mains and new meter panel and wiring in the existing metering location. | Service conductor | 2 | 2 | 2 |  |  | Unauthorised access to assets. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/02/2019 10:29 |  |  | 13716 | Residential |  | 20190528JEM_02 | Infrastructure (network-based) | -37.86 | 144.895 | 1 | Jemena | Report | 17133 | 0.004485 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Other
Crew attended, pole to be replaced | 58 BARKLY STREET, WARRNAMBOOL VIC 3280 | 32194380 |  |  |  | Leakage |  |  | 2 | CFA Comms reported pole fire. Attending crew found pole top had burnt above HV strain cross arm and would require replacement in daylight. no customers impacted | Pole (wood) | 0 | 0 | 0 |  | WBL008 | Leakage from centre phase insulator | Pole-top fire | 27/05/2019 22:57 | 1 | Negligible: no ground fire | 13718 | Residential |  | 20190528PWA_02 | Infrastructure (network-based) | -38.3865 | 142.4928 | 1 | Powercor | Report | 17361 | 0.025047 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
On arrival supply isolated repairs arranged | 605 DERRIMUT ROAD, TARNEIT VIC 3029 | 30309075 | Copper theft | [6 empty] | Bryce Norton 0418 533 859 advised that underground cables have been stolen to Telstra comms unit. On arrival, the crew found pit pulled out of ground after theft of mains to a Telstra tower. | Services cable | 2 | 2 | 2 |  | TNA013 | Copper theft | Damage to network assets | 16/04/2019 16:43 |  |  | 13726 | Roadway |  | 20190529PWA_02 | Infrastructure (network-based) | -37.8314 | 144.6919 | 1 | Powercor | Report | 17144 | 0.020064 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs. | 734-810 BULMANS ROAD, TOOLERN VALE VIC 3337 | 33076378 | Vandalism;Copper theft | [6 empty] | Reported no supply to the Equestrian Centre premises. Customer indicated cables appeared stolen and that cables at the LV supply pit appeared exposed and alive. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN023 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/04/2019 4:36 |  |  | 13733 | Roadway |  | 20190529PWA_09 | Infrastructure (network-based) | -37.6367 | 144.5544 | 1 | Powercor | Report | 17152 | 0.016505 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
The crew were able to safely abolish the existing overhead supply and electricity meter and complete the new overhead builders temporary supply connection. | 115 THE EYRIE, EAGLEMONT VIC 3084 |  | Unauthorised access | [5 empty] | 2 | Jemena crew attended the site with service order for an abolishment of supply and metering (NMI 6001066941) in conjunction with a new connection for an overhead builders temporary supply (NMI 6001476686). When they arrived they found the existing overhead service, electricity meter and switchboard in an unsafe manner as per the attached photos (in the Notes & Findings section). The builder was on site whilst the crew were on site and he advised that the electrical installation was placed in this condition so they could continue with their demolition and construction works. Responsible party who relocated Jemena assets is unknown. | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43383.8354 |  |  | 13750 | Residential |  | 20190531JEM_02 | Infrastructure (network-based) | -37.7653 | 145.0556 | 1 | Jemena | Report | 17196 | 0.040465 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Eaglemont | Other
The crews disconnected and made safe the service line and completed the abolishment. | 75 BRENDAN ROAD, GREENVALE VIC 3059 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address yesterday for an abolishment of supply and metering. When they arrived they found the overhead service line disconnected and removed from the customer property and coiled and taped against the distribution pole stay or guide wire. The overhead service line was still energised and live. There were no identified parties at the incident site at the time, therefore no other details are available Photos are attached in the Notes and Findings section | Service conductor | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/02/2019 17:03 |  |  | 13759 | Residential |  | 20190531JEM_09 | Infrastructure (network-based) | -37.6308 | 144.8903 | 1 | Jemena | Report | 17179 | 0.039204 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
The SOâ€™s will be returned with a WTV and the REC required to complete all of the items listed in the incident description. The REC Robert (0401535809) has been advised of the above and again given a talking to. | 141 WOODLAND STREET, ESSENDON VIC 3040 |  | Unauthorised access | [5 empty] | 2 | Hi Teams, Zinfra has attended the above site today and found several issues with one being a very significant issue. 1. The REC has disconnected and altered the installation wiring with the metering (yet to be metered ) tails having been removed from the main control circuit breakers to units 1-2-3-4-5 and re-supplied from a circuit breaker on the previously metered and energised public lighting switchboard which has connected and energised the units. The units cannot be metered until the wiring has been reinstated and the appropriate certificate/certificates of electrical safety provided. 2. The unused holes in the meter panel need to be filled. 3. The permanent unit numbers need to be displayed at the entrance to each unit. (Builder has numbers on site fitting 8/2/19). 4. The door to the room containing the main switchboard and metering needs to be suitably labelled. 5. Unit 2 service order requests single phase metering, the meter panel has been wired for three phase. This is the second time this has occurred on this site. On the first occasion the REC was given a talking to about connecting and energising the installation from alternative sources of supply and advised not to do this particularly when there is a request for the Electricity Distributor to attend to meter and connect supply. On the first occasion when we attended with a service order for the PL&P connection our team found the MSB and PL&P services supplied and energised from the BTS pole. Photos are attached in the Notes and Findings section. | Circuit breaker;Smart meter;Switchboard | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43648.7076 |  |  | 13760 | Residential |  | 20190531JEM_10 | Infrastructure (network-based) | -37.7421 | 144.9131 | 1 | Jemena | Report | 17180 | 0.0020926 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Other
Site made safe by disconnecting the service and providing a defect notice. | 30 IDA STREET, NIDDRIE VIC 3042 |  | Unauthorised access | [5 empty] | 2 | Crews attended the 30 and 30A Ida Street Niddrie on 13.2.19 with SOâ€™s for 1ph UG supplies to each of the properties. Please see attached photos of the customerâ€™s mechanically and electrically unprotected UG mains not located UG and located on the surface of the ground in areas where they will be damaged with significant risk to persons on site. EWR and COES also attached REC number 23259 | Cable | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 13/02/2019 17:08 |  |  | 13762 | Residential |  | 20190531JEM_12 | Infrastructure (network-based) | -37.7457 | 144.8884 | 1 | Jemena | Report | 17245 | 0.0098345 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | Other
Site made safe. For this to be connected and metered the REC is required to reinstate the electrical installation to its correct and completed state and have the installation re-inspected and a new prescribed COES issued and then re-raise the connection SO. | 5 ELEMENT STREET, CRAIGIEBURN VIC 3064 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address this morning with a SO for a new 1ph UG supply and metering. Please see attached photos of the electrical installation. When they arrived they found the customer mains cut and the metering enclosure switchboard and support pole laying on the ground. | Switchboard | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/02/2019 8:45 |  |  | 13765 | Residential |  | 20190531JEM_15 | Infrastructure (network-based) | -37.6018 | 144.8915 | 1 | Jemena | Report | 17185 | 0.022216 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
On arrival crew carried out repairs. | 375 BLUE JOHANNA ROAD, JOHANNA VIC 3238 | 33039953 |  |  |  | Overheated connection |  |  |  | Report received of a Pole mounted fuse box fire. Incident found during outage data review. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | CLC006 | Overheated connection | Pole-top fire | 14/12/2018 23:25 | 1 | Negligible: no ground fire | 13744 | Agricultural |  | 20190531PWA_05 | Infrastructure (network-based) | -38.7297 | 143.3769 | 1 | Powercor | Report | 17164 | 0.02809 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3238 | Johanna | Connection
On arrival crew isolated supply and issued defect for customer repairs. | 155 HOPPERS LANE, WERRIBEE SOUTH VIC 3030 | 33107202 | Vandalism;Copper theft | [6 empty] | A customer reported a vandalised installations at the incident location. Upon arrival, the crew found that the customer wiring and fuse board vandalised and two meters had been taken away. The crew made the place safe and defect notice issued. This is a communication tower at the location and the standby generator has been running since the vandalism took place. There was no fire or reported injuries. | Smart meter;Meter board (including fuses) | 2 | 2 | 2 |  | WBE034 | copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43501.3681 |  |  | 13777 |  |  | 20190603PWA_06 | Infrastructure (network-based) | -37.9043 | 144.7019 | 1 | Powercor | Report | 17200 | 0.026834 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Other
On arrival crew isolated supply and carried out repairs | 1141 CHINKAPOOK-MITTYACK ROAD, GERAHMIN VIC 3546 | 32144027 |  | Wind | [5 empty] | Customer reported pole down on Chinkapook-Mittyack Road near intersection Millsteed Road, pole in paddock has been knocked over by a mini tornado, pole is laying flat on ground but wires are still intact and are not actually in touch with the ground, the way the pole has landed they are still off the ground, supply still ok to farm, pole can be see from the road. Crew found pole ended up 30m from where snapped off, definitely storm damage, trees down everywhere, happened a few days ago. No protection operation, no ground fire, no injuries, no property damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | OYN003 | Sever wind storm | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43651.2965 |  |  | 13779 | Agricultural |  | 20190603PWA_08 | Infrastructure (network-based) | -35.1921 | 142.8331 | 1 | Powercor | Report | 17202 | 0.017911 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3546 | Gerahmin | Other
On arrival crew isolated supply and carried out repairs. | DOHERTYS ROAD, TARNEIT VIC 3029 | 30545361 | Copper theft | [6 empty] | Reported recieved of open pit with exposed cables, looks like has been cut and stolen On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through and stolen the 4c 35mm LV Service Cable within the LV Service Pit at the base of PL Lighting Pole LIS-868147-7728. There was no fire or reported injuries | Services cable;Services pit | 2 | 2 | 2 |  | LV002 | copper theft | Damage to network assets | 43774.4757 |  |  | 13784 | Roadway |  | 20190603PWA_13 | Infrastructure (network-based) | -37.8192 | 144.6896 | 1 | Powercor | Report | 17207 | 0.014661 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
An EIO was dispatched to investigate. On testing, the EIO measure 10 volts on the neutral. After investigating for possible causes, it was deemed there is no fault on the network, however the decision was made to upgrade the open wire conductors of the street circuit. After completion of works, the EIO attended and measured 1.5V on the neutral disconnected at the meter, and 2.6V connected and loaded, and NST passed. | 8A FLEMING STREET, MORNINGTON VIC 3931 |  |  |  |  | Out of balance load |  |  | 1 | UE received a report from an electrician that he received a small shock from a meter box. | Meter board (including fuses) | 2 | 2 | 2 |  |  | Cause of voltage rise on the neutral deemed to be imbalance of load and small section conductor on the LV circuit. | Minor shock | 28/02/2019 14:15 |  |  | 13787 | Residential |  | 20190604UTD_01 | Infrastructure (network-based) | -38.2294 | 145.0276 | 1 | United Energy Distribution | Report | 17210 | 0.011847 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Conductor
Site made safe | 46 GARNET STREET, NIDDRIE VIC 3042 |  | Working too close to overhead lines | [5 empty] | 2 | No Go Zone infringement involving third party excavator pulling down live overhead service conductor onto the nature trip | Service conductor;Neutral screen | 0 | 0 | 0 |  | ES21 | No Go Zone infringement | No Go Zone (contact) | 14/05/2019 7:47 |  |  | 13810 | Residential |  | 20190605JEM_01 | Infrastructure (network-based) | -37.7473 | 144.8875 | 1 | Jemena | Report | 17233 | 0.033709 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | Vehicle
Crew attended and made the site safe. Repairs arranged | 220 BOTANICA SPRINGS BOULEVARD, BROOKFIELD VIC 3338 | 30293002 | Vandalism;Copper theft | [6 empty] | Contractor reported U/G pit lid missing also possible theft. On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through and stolen the 4c 16mm LV Service Cable within the LV Service Pits supplying 8 x PL Lighting Poles between Botanica Springs Blvd to Clarkes Rd 8x LV Service Pits and PL Lights have been affected, they have been tampered with and the 4c 16mm LV Service Cables have been cut and removed/stolen. Aprox. 335 meter's of cable has been stolen. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 18/05/2019 12:13 |  |  | 13798 | Roadway |  | 20190605PWA_03 | Infrastructure (network-based) | -37.6991 | 144.5424 | 1 | Powercor | Report | 17221 | 0.004765 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew isolated supply and carried out repairs. | 185 ZEERUST ROAD, ZEERUST VIC 3634 | 33093329 |  |  |  | Overheated connection |  |  |  | CFA reported transformer fire at the incident location. Upon arrival crew found that a LV fuse box had melted and candled due to excessive hea. No ground fire resulted or any other 3 party damage. | Connection box | 2 | 2 | 2 |  | SHN011 | Overheating | Pole-top fire | 19/05/2019 18:17 | 1 | Negligible: no ground fire | 13801 | Roadway |  | 20190605PWA_05 | Infrastructure (network-based) | -36.2764 | 145.4113 | 1 | Powercor | Report | 17224 | 0.0067512 | Low voltage AC (<1kV) | Shepparton Airport | 3634 | Zeerust | Connection
On arrival crew isolated supply and carried out repairs. | CENTRAL CITY CARAVAN PARK, 362 HIGH STREET, GOLDEN SQUARE VIC 3555 | 33014937 | Working too close to overhead lines | [6 empty] | A customer informed that a power line has taken down by an excavator at the incident location. Upon arrival, the Powercor crew found that the cable had been damaged by an excavator. There was no fire, no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | BET008 | Excavation work | Damage to network assets | 23/05/2019 13:53 |  |  | 13814 |  |  | 20190606PWA_02 | Infrastructure (network-based) | -36.7732 | 144.257 | 1 | Powercor | Report | 17238 | 0.0081759 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Golden Square | Vehicle
On arrival crew isolated supply and carried out repairs. | 19 COACH ROAD, WOODEND VIC 3442 | 30319277 | Vandalism;Copper theft | [6 empty] | A Line worker reported that pits were open and cable was missing at the incident location. On arrival the crew found that several underground pits had been opened and several sections of LV UG cable had been stolen, totaling approx. 200m. There were no reported injuries or fire. The incident was reported to police. | Services cable;Services pit | 2 | 2 | 2 |  | WND012 | copper theft | Damage to network assets | 24/05/2019 6:32 |  |  | 13817 | Roadway |  | 20190606PWA_04 | Infrastructure (network-based) | -37.3431 | 144.5846 | 1 | Powercor | Report | 17242 | 0.036719 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Other
Crews isolated the supply to the BTS, so the BTS can be re-installed. | 964 BURKE ROAD, DEEPDENE VIC 3103 | 30355633 | Working too close to overhead lines | [5 empty] | 2 | A representative at a building site called to report that a BTS pole had fallen down and was laying on an excavator. When the crew arrived they found that the excavator was digging away at a bank, and the excavator dislodged the BTS pole, causing it to fall over. There were no reported injuries, and no exposed live wires. | Aluminium twisted (grey);Customer installation | 0 | 0 | 0 |  | L022 | excavating near BTS pole | Loss of supply;No Go Zone (contact) | 31/05/2019 13:04 |  |  | 13821 | Construction |  | 20190606PWA_07 | Infrastructure (network-based) | -37.8078 | 145.0615 | 1 | CitiPower | Report | 17251 | 0.00051736 | Low voltage AC (<1kV) | Essendon Airport | 3103 | Deepdene | Other
crew attended and replaced the service line | 6 SHEFFIELD STREET, BRUNSWICK VIC 3056 | 30156384 |  |  |  | Corrosion |  |  | 2 | person received an electric shock when he simultaneously contacted the Metallic tap with his hand whilst with his feet in simultaneous contact with metallic waste standing in the shower. | Aluminium twisted (grey) | 0 | 0 | 0 |  | WB002 | Corroded service neutral at DB Pole | Minor shock | 16/04/2019 17:30 |  |  | 13825 | Residential |  | 20190606PWA_11 | Infrastructure (customer connection) | -37.7602 | 144.951 | 1 | CitiPower | Report | 17257 | 0.022043 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | OH Cable
Crew attended and repaired service connections | 32 SUTTON STREET, BALWYN NORTH VIC 3104 | 30191576 |  |  |  | Corrosion |  |  | 2 | Person received an electric shock when he simultaneously contacted the metallic tap with his hand and simultaneously touched the metallic frame of the dishwasher with his other hand. | Service conductor | 0 | 0 | 0 |  | L018 | Corroded service neutral at FMJB | Minor shock | 17/04/2019 19:00 |  |  | 13826 |  |  | 20190606PWA_12 | Infrastructure (customer connection) | -37.7954 | 145.0806 | 1 | CitiPower | Report | 17258 | 0.0043623 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Connection
The crew has abolished the overhead service line and removed the potentially unsafe installation. However, the crew were unable to recover the electricity meter. | 30 CASTLEY CRESCENT, BRAYBROOK VIC 3019 |  | Unauthorised access | [5 empty] | 2 | Metering and servicing crews attended the above address today with a SO for an abolishment of supply and metering. When the crew arrived, they found the electricity meter has been disconnected and removed from site. The overhead service line was still connected to the property and connected to supply and the service fuse still inserted in the property Fused Overhead Line Connection Box (FOLCB). There were no parties on site and therefore no details of REC, demolition or building company. Photos are attached in the "Notes and Findings" section | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43561.6813 |  |  | 13829 | Residential |  | 20190607JEM_01 | Infrastructure (network-based) | -37.7829 | 144.8618 | 1 | Jemena | Report | 17261 | 0.041483 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
On arrival crew isolated supply and carried out repairs. | WINIAM ROAD, NHILL VIC 3418 | 32122897 |  |  |  | Leakage |  |  |  | Vic fire reported a pole fire at the incident location. On arrival the crew found minor burning of the wooden pole top. The conductor stayed in position until crews arrived to perform repairs. There were no reported injuries, and no ground fire. | Pole (wood) | 2 | 2 | 2 |  | NHL015 | Excessive leakage current | Pole-top fire | 31/05/2019 6:53 | 1 | Negligible: no ground fire | 13827 | Roadway |  | 20190607PWA_01 | Infrastructure (network-based) | -36.4151 | 141.6602 | 1 | Powercor | Report | 17259 | 0.015738 | 22kV AC | Horsham Aerodrome | 3418 | Nhill | Pole
On arrival crew isolated supply and carried out repairs. CTA organised for check for HVI - Nil reported. | 43-45 GREAVES STREET S, WERRIBEE VIC 3030 | 30102876 | Vehicle | [5 empty] | 1 | Report received that a truck had brought wires down at the incident location causing a power outage. Upon arrival the crew found that a truck has clipped the Optus cable spanning causing the Optus cable to flick up and into the LV open wire ( which in turn flicked up and contacted the HV open wire , resulting in the feeder CB operating and splash marks being sustained to the LV conductor. The Optus cable as well as the HV/LV overhead conductors remained intact however the Optus cable ended up twisted in the LV conductor. A CTA was to be dispatched to site to investigate potential HVI's, There was no ground fire, shock, injury, or reports of third party damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE024 | Vehicle struck communication service | Damage to network assets | 43530.7208 |  |  | 13830 | Roadway |  | 20190607PWA_03 | Infrastructure (network-based) | -37.909 | 144.6564 | 1 | Powercor | Report | 17262 | 0.035703 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | Vehicle
Service disconnected at pole end and removed. Supply isolated due to non compliant installation | 35 DUNNE STREET, KINGSBURY VIC 3083 |  | Unauthorised access | [5 empty] | 2 | Zinfra compliance officer found non compliant installation due to demolition works Service conductor and point of attachment were made unsafe as a result of demolition works There could be issues with earthing and protection, therefore this incident has also been forwarded to complaints@energysafe.vic.gov.au Photos and electrical works request (EWR) are attached in the "Notes and Findings" section REC details are in the "Other information sources" section | Service conductor;Customer installation | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43775.625 |  |  | 13848 | Residential |  | 20190611JEM_01 | Infrastructure (network-based) | -37.715 | 145.0395 | 1 | Jemena | Report | 17282 | 0.023212 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Kingsbury | Other
Crew isolated supply to test and make repairs | 47 CENTREWAY, GLENROY VIC 3046 |  | Working too close to underground cables | [5 empty] | 2 | NBN crew did not maintain limits of approach while performing their works and damaged Jemena underground service cable A No Go Zone permit to work had not been issued for this site/work | Services cable;Copper | 0 | 0 | 0 |  |  | NBN crew did not maintain limits of approach while performing their works and damaged Jemena underground service cable | No Go Zone (contact) | 43775.5083 |  |  | 13850 | Residential |  | 20190611JEM_03 | Infrastructure (network-based) | -37.7032 | 144.9062 | 1 | Jemena | Report | 17284 | 0.025131 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Dug up
On arrival crew isolated supply and carried out repairs. | 45 OSBORNE STREET, OCEAN GROVE VIC 3226 | 30233688 |  |  |  | Unknown technical factor |  |  |  | Crew were dispatched to incident following reports transformer and pole were on fire. The fire brigade were also enroute. Upon arrival, the crew identified a 2 wire neutral screened service to 45 Osborne St had burnt at the pole junction box. The wire fell to the ground causing 1m2 of grass to burn. There was no reported injuries. | Service conductor;Connection box | 2 | 2 | 2 |  | DDL023 | insufficient remains to determine cause | Pole-top fire;Grassfire | 43683.4625 | 1 | Localised: less than 10 sq.m | 13839 | Roadway |  | 20190611PWA_01 | Infrastructure (network-based) | -38.271 | 144.5192 | 1 | Powercor | Report | 17272 | 0.020502 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
On arrival crew made arrangements for repair | 492 QUEENS PARADE, FITZROY NORTH VIC 3068 | 30220507 | Working too close to underground cables | [6 empty] | Contractor for Yarra Trams (DEMCOR ENGINEERING PTY LTD) reported hitting an underground cable and possibly damaging it. On arrival, the crew found an underground cable had been hit and damaged due to customer excavator. There was no ground fire, no third party damaged and no reported injuries. | Cable | 2 | 2 | 2 |  | F035 | Excavator struck cable | No Go Zone (contact);Damage to network assets | 43683.4771 |  |  | 13853 | Roadway |  | 20190612PWA_03 | Infrastructure (network-based) | -37.7851 | 144.9949 | 1 | CitiPower | Report | 17369 | 0.030334 | Supervisory cable;Other | Essendon Airport | 3068 | Fitzroy North | Dug up
Fault Crew re-terminated the existing O/H Service Cable at the Customer's FOLCB | 510 MURRAY STREET, COLAC VIC 3250 | 32063770 |  |  |  | Overheated connection |  |  |  | Person was in the Kitchen when he received an electric shock from the exposed metal of the Oven as he made simultaneous contact with his hand on the Oven whilst standing on the Kitchen floor. | Aluminium twisted (grey);Customer installation | 0 | 0 | 0 |  | CLC002 | Loose Overhead Service Neutral Conductor termination at the Customer's FOLCB | Minor shock | 17/04/2019 11:00 |  |  | 13860 | Residential |  | 20190612PWA_09 | Infrastructure (customer connection) | -38.3363 | 143.564 | 1 | Powercor | Report | 17296 | 0.018595 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | Connection
Fault Crew replaced the service cable | 5 BANK STREET, PORT FAIRY VIC 3284 | 30136317 |  |  |  | Corrosion |  |  | 2 | persons were in the Toilet / Bathroom washing their hands at various times when they reported receiving an electric shock when they made simultaneous contact with their hands between the taps and the basin. | Service conductor | 0 | 0 | 0 |  | KRT022 | Corroded Neutral Screen service Conductor | Minor shock | 22/04/2019 19:00 |  |  | 13862 | Public space |  | 20190612PWA_11 | Infrastructure (customer connection) | -38.3838 | 142.2383 | 1 | Powercor | Report | 17298 | 0.038771 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | OH Cable
service repaired at customers FOLCB | 96 BARKLY STREET, ST KILDA VIC 3182 | 30218635 |  |  |  | Corrosion |  |  | 2 | person received an electric shock when he simultaneously contacted the water tap with his hand and kneeling on a grassed area. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | SK001 | Corroded service neutral at FOLCB | Minor shock | 43651.7083 |  |  | 13864 | Residential |  | 20190612PWA_13 | Infrastructure (network-based) | -37.8635 | 144.982 | 1 | CitiPower | Report | 17300 | 0.039418 | Low voltage AC (<1kV) | Essendon Airport | 3182 | St Kilda | Connection
UE dispatched a fault crew. On attendance, they discovered illegal wiring from the pit to the garage in a trench that had been dug by previous occupant. A hole had been drilled into the service pit where the illegal wiring entered. The fault crew removed the illegal wiring in the pit. | 25 PETUNIA DRIVE, KEYSBOROUGH VIC 3173 |  | Vandalism;Theft;Unauthorised work | [5 empty] | 2 | UE received report from REC Craig of illegal wiring. The property at 25 Petunia Dve Keysborough had previously been disconnected for an illegal bypass behind the meter. The REC advised of exposed wires in the UE service pit. | Services pit | 2 | 2 | 2 |  |  | Cause was the wilful damage by unknown third party to install illegal wiring for a crop house. | Damage to network assets | 24/05/2019 15:45 |  |  | 13869 | Residential |  | 20190612UTD_03 | Infrastructure (network-based) | -38.0014 | 145.1782 | 1 | United Energy Distribution | Report | 17307 | 0.034272 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Other
Crew made site safe and repaired damage. | PLEASANT VIEW, 7332 NHILL-HARROW ROAD, MIGA LAKE VIC 3409 | 32095476 |  |  |  | Candled fuse |  |  |  | Candled EDO fuse (fire). Fire incident found during outage data review . No ground fire | EDO fuse | 2 | 2 | 2 |  | HSM004 | excessive leakage current | Pole-top fire | 43353.5778 | 1 | Negligible: no ground fire | 13873 | Agricultural |  | 20190613PWA_03 | Infrastructure (network-based) | -36.9476 | 141.6249 | 1 | Powercor | Report | 17311 | 0.012282 | 12.7kV AC (SWER) | Horsham Aerodrome | 3409 | Miga Lake | Fuse
Fault Crew replaced the corroded Pole Box at the Reticulation Pole | 1367 BYRNESIDE-KYABRAM ROAD, LANCASTER VIC 3620 | 30250247 |  |  |  | Corrosion |  |  | 2 | person was in the Kitchen standing at the Sink washing dishes when he received an electric shock as she made simultaneous contact with one hand on the metal Tap and his bare feet while standing on the conductive Concrete Floor | Service conductor | 0 | 0 | 0 |  | KYM003 | Corroded O/H Service Neutral Conductor termination at the Pole Box located on the Reticulation Pole. | Minor shock | 43622.75 |  |  | 13876 | Agricultural |  | 20190613PWA_06 | Infrastructure (network-based) | -36.3253 | 145.1318 | 1 | Powercor | Report | 17314 | 0.03777 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Lancaster | Connection
Fault Crew replaced the corroded Pole Box at the Reticulation Pole | 140 SPARKS ROAD, NORLANE VIC 3214 | 30224852 |  |  |  | Corrosion |  |  | 2 | Person was in the Kitchen standing at the sink washing dishes when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and her other hand in contact with the metal sink. | Service conductor | 0 | 0 | 0 |  | CRO013 | Corroded O/H Service Neutral Conductor termination at the Pole Box located on the Reticulation Pole | Minor shock | 43502.6042 |  |  | 13878 | Residential |  | 20190613PWA_08 | Infrastructure (network-based) | -38.092 | 144.3613 | 1 | Powercor | Report | 17316 | 0.017015 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Connection
Crew made safe and performed repairs. | 325 BOOLEY ROAD, GHERINGHAP VIC 3331 | 30323976 |  |  |  | Candled fuse |  |  |  | Candled EDO fuse (fire). Incident found during outage data review. No ground fire. | EDO fuse | 2 | 2 | 2 |  | GL015 | excessive leakage current | Pole-top fire | 13/12/2018 16:45 | 1 | Negligible: no ground fire | 13882 | Roadway |  | 20190613PWA_11 | Infrastructure (network-based) | -38.0943 | 144.2164 | 1 | Powercor | Report | 17321 | 0.033066 | 22kV AC | Avalon Airport | 3331 | Gheringhap | Fuse
On arrival crew isolated supply and carried out repairs. | 25 WOORINEN-GOSCHEN ROAD, WOORINEN SOUTH VIC 3588 | 30259059 |  | Bird | [5 empty] | VIC Fire reported pole fire, possible junction box, brigade en route. Crew found remains of a burnt fuse box. There was no ground fire, no pole fire just light black stain from smoke and spatter. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | SHL004 | Bird Incident | Pole-top fire | 16/06/2019 0:24 | 1 | Negligible: no ground fire | 13895 | Roadway |  | 20190617PWA_01 | Infrastructure (network-based) | -35.2959 | 143.454 | 1 | Powercor | Report | 17338 | 0.021988 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3588 | Woorinen South | Animal
On arrival crew organised repairs. | 30 ROSS WATT ROAD, GISBORNE VIC 3437 | 30338661 | Copper theft | [6 empty] | Adrew McArdle reported pit lid removed & possible copper theft at 30 Ross Watt Road Gisborne, closest to LIS 845163. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | GSB013 | copper theft | Damage to network assets | 14/06/2019 17:22 |  |  | 13896 | Roadway |  | 20190617PWA_02 | Infrastructure (network-based) | -37.4726 | 144.5914 | 1 | Powercor | Report | 17340 | 0.015326 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
Emergency high voltage switching was completed by opening OA8236 RCGS located in Stanhope Street and the large tree branch was removed. Supply was restored after the 250amp LV red phase fuse was replaced at "Thanet-Wattletree" substation. | 53 THANET STREET, MALVERN VIC 3144 | 2313937 |  | Wind;Fallen |  |  |  |  | 2 | Customers in Thanet Street, Malvern advised of an all supply failure and a wire has been brought down by a tree that is on fire. The MFB have been contacted. The incident address provided was 45 Thanet Street. During strong winds, a large tree branch fell over the HV/LV overhead conductors. The street in Malvern has many council plane trees and its suspected the branch was from a council tree. | Conductor (bare) | 0 | 0 | 0 |  | K 6 | Vegetation: Trees Incident | Other vegetation | 20/11/2018 17:34 | 1 | Negligible: no ground fire | 10755 | Residential |  | 20181206UTD_03 | Infrastructure (network-based) | -37.8628 | 145.0359 | 1 | United Energy Distribution | Report | 18400 | 0.039602 | 11kV AC | Moorabbin Airport | 3144 | Malvern | Trees
LV parallels were installed and the faulty krone switch was replaced. A 315amp DIN fuse had operated and supply was restored upon completion. | 122 GOULD STREET, FRANKSTON VIC 3199 | 3309214 |  | Prone to salt deposition |  | Corrosion;Electrical breakdown |  |  | 2 | The CFA reported a pole fire and the lines are also sparking. A pole fire was reported at pole No. LIS 3309214. The LV krone box that supplied the north circuit of "Beach-Gould" substation caught on fire with the cause being a probable loose connection or corrosion due to salt borne pollutants as the pole is located a short distance from Port Phillip Bay. | Connection box | 0 | 0 | 0 |  | FTN 14 | Probable loose connection or corrosion due to salt borne pollutants. | Pole-top fire | 21/11/2018 2:02 | 1 | Negligible: no ground fire | 10757 | Roadway |  | 20181206UTD_04 | Infrastructure (network-based) | -38.1395 | 145.1205 | 1 | United Energy Distribution | Report | 18384 | 0.028603 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Supply Isolated and Connection replaced | 215 FARM ROAD, COCOROC VIC 3030 | 30143067 |  |  |  | Overheated connection |  |  | 1 | Grass fire occurred within the Werribee Treatment Plant near HV Gas Switch. The resultant fault-current ruptured a connection on the incoming underground cable interface and a grass fire was ignited. | Dropper/bridge | 0 | 0 | 0 |  | WBE024 | Fault current due to fault within HV installation | Grassfire | 43263.6799 | 1 | Medium: 1000 sq.m - 10 ha | 10770 | Agricultural |  | 20181210PWA_01 | Infrastructure (customer connection) | -37.928 | 144.6486 | 1 | Powercor | Report | 13662 | 0.022388 | 22kV AC | Laverton Raaf | 3030 | Cocoroc | Connection
On arrival crew isolated supply and carried out repairs | 11 GOODWOOD STREET, RICHMOND VIC 3121 | 30292583 | Working too close to underground cables | [6 empty] | An underground faults crew were called to a fault at the incident address and discovered damage caused by a third party was believed to be the cause of the fault. It was ascertained on site that the damage occurred when an adjacent low voltage underground pit was installed for future 11 Goodwood Sreet. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | NR015 | Attributed to previous works - using under pavement borer | Loss of supply;Damage to network assets | 19/11/2018 12:00 |  |  | 10789 | Roadway |  | 20181211PWA_09 | Infrastructure (network-based) | -37.8196 | 144.9935 | 1 | CitiPower | Report | 13708 | 0.0042766 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Dug up
Crew attended and removed service and meter from premise | 99 MORACK ROAD, VERMONT SOUTH VIC 3133 |  | Working too close to overhead lines;Unauthorised work | [5 empty] | 1 | Builder Ben Kennedy was on site to complete works, and noticed service wire down. Property was to be disconnected for works | Service conductor | 0 | 0 | 0 |  |  | Suspect demolition works | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43171.3958 |  |  | 10788 | Residential |  | 20181211UTD_01 | Infrastructure (network-based) | -37.8477 | 145.1993 | 1 | United Energy Distribution | Report | 13686 | 0.011434 | Low voltage AC (<1kV) | Moorabbin Airport | 3133 | Vermont South | Other
On arrival crew isolated supply and carried out repairs. LEI organised to check for HVI | 59 RIVERVIEW TERRACE, DARTMOOR VIC 3304 | 30089400 |  |  |  | Leakage |  |  |  | Crew attended the incident site and found that a cross-arm fire had burnt through the cross-arm on the footpath side of the pole. The insulator and end of the cross-arm with high voltage conductor attached came to rest on the low voltage cross-arm. Possible high voltage injection to some customers to be confirmed. There were no reported injuries | Crossarm (wood) | 2 | 2 | 2 |  | PLD003 | Excessive leakage current | Pole-top fire | 13/12/2018 2:48 | 1 | Negligible: no ground fire | 10796 | Roadway |  | 20181213PWA_01 | Infrastructure (network-based) | -37.9309 | 141.2761 | 1 | Powercor | Report | 13700 | 0.032609 | 22kV AC | Portland (Cashmore Airport) | 3304 | Dartmoor | Crossarm
On arrival crew isolated supply and carried out repairs. | 1846 BULGANA ROAD, BULGANA VIC 3377 | 32118131 |  | Lightning | [5 empty] | Vic Fire reported a grass fire caused by a fallen SWER conductor at the incident location. On arrival the fault crew found that the pole had previously been struck by lightning, and was split at the top. A grass fire - estimated at 60 hectares by CFA personnel present at the incident location - was ignited by the fallen conductor. The fire was extinguished by the CFA. There was no reported injuries | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | STL007 | Lightning strike | Grassfire | 43416.6715 | 1 | Large: more than 10 ha | 10797 | Agricultural |  | 20181213PWA_02 | Infrastructure (network-based) | -37.1267 | 142.9913 | 1 | Powercor | Report | 13701 | 0.021867 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3377 | Bulgana | Lightning
EDO Fuse replaced with BA | 60 PRINCES WAY, LONGWARRY NORTH VIC 3816 | LIS 2708577 |  |  |  | Candled fuse |  |  |  | HV EDO Fuse Candling Reported | Any other type | 0 | 0 | 0 |  | WGL12 | Candling due to suspected moisture ingress/weathering | Pole-top fire | 13/12/2018 13:27 | 1 | Negligible: no ground fire | 10805 |  |  | 20181214SPN_01 | Infrastructure (network-based) | -38.091 | 145.7791 | 2 | AusNet Services Distribution | Report | 18118 | 0.040697 | 22kV AC | Moorabbin Airport | 3816 | Longwarry North | Fuse
The Linesmen removed the both sections of the burnt in half fuse and the hanging fuse, replaced both 15E BA fuse tubes and restored supply. | BONEGILLA MIGRANT CENTRE, 82 BONEGILLA ROAD, BONEGILLA VIC 3691 | LIS5209671 |  |  |  | Candled fuse |  |  | 1 | Reported candling fuse | Any other type | 0 | 0 | 0 |  | WOTS25 | Suspected lightning strike resulting in candled HV Fuse. On arrival the fault crew found one BA fuse burnt in half (candled) with both the top and bottom sections still in the fuse unit. No evidence ofground fire. | Pole-top fire | 13/12/2018 20:44 | 1 | Negligible: no ground fire | 10807 |  |  | 20181214SPN_03 | Infrastructure (network-based) | -36.1344 | 147.0087 | 2 | AusNet Services Distribution | Report | 18119 | 0.0036782 | 22kV AC | Wangaratta Aero | 3691 | Bonegilla | Lightning
Jemena contractor Zinfra Servicing crew made safe and reported unauthorised access and alteration of Jemena assets. | 21 BARWON AVENUE, RESERVOIR VIC 3073 |  | Unauthorised work;Unauthorised access | [6 empty] | Builder detached meter board and moved it above ceiling timber framework | Switchboard | 0 | 0 | 0 |  |  | Builder decided to temporarily relocate the meter board into the building ceiling, he advised waiting for a Truck Appointment was taking to long and was holding up his works. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43171.4931 |  |  | 10824 | Construction |  | 20181218JEM_01 | Infrastructure (network-based) | -37.7233 | 145.0236 | 1 | Jemena | Report | 13898 | 0.036418 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Site made safe. Crew repaired asset damage and restored supply. | 22 ODONOHUE ROAD, ANGLESEA VIC 3230 | 32071083 |  |  |  | Corrosion |  |  | 1 | Vic Fire reported transformer sparking, starting grass fire near Angahook - Lorne State Park - Fire brigade onsite - REF: 8763 - LIS 29929. Crew found a burnt HV dropper/lead had failed which started a small 5m2 grass fire, CFA attended, no property damage, no injuries. | Dropper/bridge | 0 | 0 | 0 |  | WPD021 | HV dropper/lead had failed due to corrosion | Grassfire | 24/12/2018 11:23 | 1 | Localised: less than 10 sq.m | 10843 | Peri-urban |  | 20181224PWA_01 | Infrastructure (network-based) | -38.4193 | 144.1701 | 1 | Powercor | Report | 15048 | 0.019328 | 22kV AC | Avalon Airport | 3230 | Anglesea | AF Other
Crew isolated supply and undertook repairs | 95 GREEN STREET, BULLA VIC 3428 |  | Copper theft | [5 empty] | 2 | Copper was stolen at the specified location. | Cable | 2 | 2 | 2 |  |  | Unknown person/s stole underground cable for the pole to pit | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/12/2018 2:14 |  |  | 10850 | Roadway |  | 20181228JEM_01 | Infrastructure (network-based) | -37.6322 | 144.8072 | 1 | Jemena | Report | 13783 | 0.0079456 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
Supply was isolated to customers supplied from "Rasmussen-Bamfield" substation and the LV pillar was replaced by a underground faults crew. Supply was restored upon completion after two x 250amp fuses were replaced that had operated at the time of the fault. | 16 BAMFIELD CLOSE, TEMPLESTOWE VIC 3106 |  |  |  |  | Overheated connection |  |  | 1 | Caller reports transformer is on fire on the corner of Bamfield Close and Rusmussen Drive and will call emergency services. A LV pillar melted and subsequently caught fire due to a deteriorated internal connection. The MFB were promptly in attendance and extinguished the fire prior to the crew arriving. The probable cause was a loose connection that overheated causing dry grass inside the pillar to catch on fire with localised burn marks occurring on an adjacent brick wall. | LV Pillar | 0 | 0 | 0 |  |  | The probable cause was a loose connection that overheated causing dry grass inside the pillar to catch on fire. | Plant/equipment | 29/12/2018 12:14 | 1 | Negligible: no ground fire | 10852 | Roadway |  | 20181231UTD_01 | Infrastructure (network-based) | -37.7669 | 145.1358 | 1 | United Energy Distribution | Report | 13785 | 0.036322 | Low voltage AC (<1kV) | Moorabbin Airport | 3106 | Templestowe | Connection
On arrival crew isolated supply and carried out repairs | 783-857 COBURNS ROAD, HARKNESS VIC 3337 | 32174296 | Vandalism;Copper theft | [6 empty] | REC reported vandalized pillar/pit, cables cut and stolen from incident location. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN032 | copper theft and vandalism | Loss of supply;Damage to network assets | 43385.4229 |  |  | 10876 | Roadway |  | 20190104PWA_10 | Infrastructure (network-based) | -37.6339 | 144.5731 | 1 | Powercor | Report | 13816 | 0.0029479 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Harkness | Other
Crew re-terminated the neutral and all 3 active conductors | UNIT 3 20 CUMMING STREET, BRUNSWICK WEST VIC 3055 | 30159126 |  |  |  | Overheated connection |  |  |  | was showering when she received an electric shock as she made simultaneous contact between her hand on the metallic shower rose and her bare feet while standing on the wet shower base. Emma and her husband had also noticed lights dimming on a regular basis. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an incorrect connection method at the IPC connector which connected the service cable to the copper tail from the mains box. | Connector/termination | 0 | 0 | 0 |  | WB011 | Connection failure - Poor neutral connection at the IPC connector which connected the service cable to the tail from the mains box. | Minor shock | 20/12/2018 7:30 |  |  | 10878 | Residential |  | 20190104PWA_12 | Infrastructure (customer connection) | -37.7606 | 144.9423 | 1 | CitiPower | Report | 13818 | 0.018878 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Connection
On arrival crew isolated supply and carried out repairs. | 15 FLACK STREET, BALLAN VIC 3342 | 33074558 | Working too close to underground cables | [6 empty] | A contractor dug up an UG service during road work excavations at the incident location. Upon arrival, the Powercor fault crew found that the cable had been damaged. There were no injuries or fire. | Cable | 2 | 2 | 2 |  | BMH003 | While carrying excavations related to road works Contractor uncovered LV cable | No Go Zone (contact);Damage to network assets | 43446.6097 |  |  | 10880 | Roadway |  | 20190104PWA_14 | Infrastructure (network-based) | -37.5912 | 144.223 | 1 | Powercor | Report | 13820 | 0.0070023 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Dug up
Crew replaced the deteriorated Single Phase O/H Neutral Screened Service Cable | 88 TIMBOON-CURDIEVALE ROAD, TIMBOON VIC 3268 | 32057910 |  |  |  | Corrosion |  |  |  | person was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet whilst standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Screen Conductor of a copper Neutral Screened O/H Service Cable, located approximately 5 metreâ€™s from the Reticulation Pole | Service conductor | 0 | 0 | 0 |  | TRG003 | Corroded Neutral Screen Conductor of a copper Neutral Screened O/H Service Cable | Minor shock | 27/12/2018 9:00 |  |  | 10892 | Residential |  | 20190107PWA_10 | Infrastructure (customer connection) | -38.4911 | 142.9811 | 1 | Powercor | Report | 13834 | 0.015895 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Timboon | OH Cable
Fault crew dispatched to investigate, make safe and carry out repairs | 630 FOSTER-PROMONTORY ROAD, FOSTER VIC 3960 | LIS2017060 and LIS590810 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | E0007312 - Excavator made contact with O/H HV conductors | Conductor (bare) | 0 | 0 | 0 |  | FTR22 | Excavator (owned by the farmer) was being used to install a water pipe through the paddock and under the powerline when it contacted the O/H HV conductor. Excavator driver (was ok) knew it was there but didnâ€™t realise how close he was and made contact with the conductors between poles 2017060 and 590810. ACR tripped and re-closed causing the HV fuses at pole 2017060 to operate. Minor damage observed on the outside conductor which was repaired. Measured heights of conductors at 7.05m off the ground where contact was made. | No Go Zone (contact) | 43647.5743 |  |  | 10909 |  |  | 20190109SPN_02 | Infrastructure (network-based) | -38.7108 | 146.1655 | 1 | AusNet Services Distribution | Report | 13859 | 0.008309 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Foster | Vehicle
Fault crew dispatched to investigate, make safe and repair | 39-45 CYRIL BEECHEY LANE, CRANBOURNE VIC 3977 | LIS509840 |  |  |  | Defective component;Insulator;Leakage |  | Phase to earth |  | E0007571 - pole fire reported | Conductor (bare);Pole (wood);Insulators | 0 | 0 | 0 |  | CRE32 | Suspected 22kV insulator tracking through a pole stay rod resulting in pole top fire and failure of HV Strain structure, No evidence of ground fire. | Pole-top fire | 43709.6257 | 1 | Negligible: no ground fire | 10925 |  |  | 20190111SPN_04 | Infrastructure (network-based) | -38.1178 | 145.2674 | 1 | AusNet Services Distribution | Report | 17806 | 0.0076238 | 22kV AC | Moorabbin Airport | 3977 | Cranbourne | AF Other
Emergency high voltage switching was completed and the repairs were completed under Access Authority conditions prior to supply being restored. | FERNTREE GULLY ROAD, OAKLEIGH VIC 3166 | 2324619 |  | Animal |  |  |  |  | 1 | At 9.58PM on 27/12/2018, 11kV feeder OAK 35 circuit breaker reclosed to lockout. The MFB advised of a pole fire in Dandenong Road at the corner of Park Road, Oakleigh. A possum made contact with the HV conductors on the HV anchor pole (LIS No. 2324619) located in Ferntree Gully Road on the corner of Bowmans Parade that caused the blue phase HV helical termination to break and a HV conductor to fall in close proximity to the blue phase LV conductors below. Molten metal fell onto the dry grass below and a small grass fire to occur at the base of the pole. In addition, a small charred deceased possum was also at the base of the pole with fragments from damaged HV infrastructure scattered in the vicinity. Secondary damage occurred as a result of fault current with an ampact connection failing on pole No. LIS 2329333 located in Dandenong Road at the corner of Park Road. A high voltage injection (HVI) was suspected to customers in the area and a LEI sent to the site to investigate. It was later confirmed that a HVI did not occur. | Conductor (bare);Pole top;Insulators | 0 | 0 | 0 |  | OAK 35 | Animal Incident | Grassfire | 27/12/2018 21:58 | 1 | Localised: less than 10 sq.m | 10920 | Roadway |  | 20190111UTD_01 | Infrastructure (network-based) | -37.8967 | 145.1043 | 1 | United Energy Distribution | Report | 13873 | 0.010749 | 11kV AC | Moorabbin Airport | 3166 | Oakleigh | Animal
On arrival crew isolated supply and carried out repairs. | 3876 MIDLAND HIGHWAY, STANHOPE VIC 3623 | 30142962 | Vehicle | [6 empty] | Vic fire reported a grass fire at the incident location. Upon arrival, Powercor crew found that there was a grass fire that was caused by a fallen service with its junction box across the road. The crew believed the service was pulled down by an unknown high load. There was no reported injuries | Service conductor | 2 | 2 | 2 |  | SHP014 | Service line believed to have been pulled down by high load. | Grassfire | 43770.5215 | 1 | Small: 10 - 1000 sq.m | 10932 | Roadway |  | 20190114PWA_01 | Infrastructure (network-based) | -36.444 | 145.009 | 1 | Powercor | Report | 13893 | 0.012279 | Low voltage AC (<1kV) | Shepparton Airport | 3876 | Stanhope | Vehicle
Crew located lighting pole and disconnected cascade lighting supply | 459 CHURCH STREET, RICHMOND VIC 3121 | 30221895 |  |  |  | Electrical breakdown |  |  |  | Citipower received a report that a person had received an electric shock from a lighting pole. The attending crew found an metal tramway pole in the vicinity was energised through an insulation fault between the public lighting switched supply and the pole. | Public lighting;Pole (steel) | 0 | 0 | 0 |  | R024 | Insulation breakdown - Broken down insulation on joint on active conductor tail for public light (cable from open wire to light fitting) | Minor shock | 13/01/2019 2:00 |  |  | 10936 | Roadway |  | 20190114PWA_03 | Infrastructure (network-based) | -37.8271 | 144.9978 | 1 | CitiPower | Report | 13903 | 0.026311 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Connection
Jemena Servicing crew advised contractor to cease works, isolated supply to underground cables and service pit | 1031-1033 HEIDELBERG ROAD, IVANHOE VIC 3079 |  | Working too close to underground cables | [5 empty] | 2 | NGZ breach incident by contractor excavating works for Construction Developer exposing underground low voltage conduits and service pit | Services pit | 0 | 0 | 0 |  |  | Contractor did not contact network owner to request instructions and/or Permit to Work as per No Go Zone requirements | No Go Zone (no contact) | 43678.4583 |  |  | 10949 | Construction |  | 20190115JEM_02 | Infrastructure (network-based) | -37.7754 | 145.0388 | 1 | Jemena | Report | 15216 | 0.013841 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Dug up
On arrival crew isolated supply and carried out repairs. LEI inspected properties - no damage found. | 29 WILLIAMS ROAD, MAIDEN GULLY VIC 3551 | 30026676 |  |  |  | Overheated connection |  |  | 1 | Customer reported wires down at incident location. On arrival crew found HV conductor at tee pole had ruptured at PG connection There was suspected HV injection however no damage was identified. There was no fire, and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BET001 | HV conductor ruptured at PG clamp | Loss of supply;Damage to network assets | 24/12/2018 19:06 |  |  | 10938 | Roadway |  | 20190115PWA_01 | Infrastructure (network-based) | -36.7151 | 144.224 | 1 | Powercor | Report | 13908 | 0.034606 | 22kV AC | Bendigo Airport | 3551 | Maiden Gully | Conductor
Fault crew and LEI dispatched to investigate. Earth/Neutral repaired and transformer put back in service. Supply restored to customers following LEI tests | 85 ADENEYS ROAD, DEVON MEADOWS VIC 3977 | LIS517226 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0007737 - report of lawn mower hitting and damaging transformer earth/neutral resulting in HVI | Earth/earthing | 0 | 0 | 0 |  |  | Ride on lawn mower on public land has hit pole 517226 and severed the earth/neutral return for the TX. A private contractor on a ride on lawn mower on public land looks to have clipped the side of the timber power pole 517226, in doing so had severed the earth/neutral return for the pole mounted TX resulting in a low voltage injection for 2 dwellings. | HV injection | 43800.8389 |  |  | 10941 |  |  | 20190115SPN_02 | Infrastructure (network-based) | -38.191 | 145.3318 | 2 | AusNet Services Distribution | Report | 13914 | 0.0053889 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3977 | Devon Meadows | Vehicle
Fault crew dispatched to investigate. There was no damage to customerâ€™s tractor or property apart from small grass fire on his land. Conductors repaired and restrung to approx. 6.3m to provide additional ground clearance | 5 HUMPHRIES ROAD, CATANI VIC 3981 | LIS513501 and LIS513508 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 0 | E0007738 - Tractor moving hay bales contacted O/H HV conductors near pole LIS513501. No injuries sustained, small grass fire reported in the vacinity | Conductor (bare) | 0 | 0 | 0 |  | LLG11 | Tractor contacted single phase 22kV O/H conductors between Cam Poles #513501 & # 513508 while moving bales of hay across his paddock. 2 small grass fires resulted (which was put out by the customer) measuring 1.5x1.5m and 1mx1m (6.25m sq total) Upon investigation, the height of the HV conductors where incident occurred was approximately 4.5m. No fuses or recloses occurred when tractor came into contact with HV. There was no damage to customerâ€™s tractor or property other than the small grass fire on his land. Conductors repaired and restrung to approx. 6.3m to provide additional ground clearance | Grassfire | 43800.7653 | 1 | Localised: less than 10 sq.m | 10942 | Agricultural |  | 20190115SPN_03 | Infrastructure (network-based) | -38.1856 | 145.6623 | 2 | AusNet Services Distribution | Report | 17799 | 0.025714 | 22kV AC | Moorabbin Airport | 3981 | Catani | Vehicle
Dispatched fault crew to investigate and make site safe. The fault was isolated and a new TX plus hardware was erected. | 895 OMEO VALLEY ROAD, OMEO VIC 3898 | LIS 1605874 |  | Lightning | [5 empty] | E0008180 - There was evidence of a fire at the base of the pole in an area of approx. 10m. The TX or pole was possibly hit by lightening this caucused a fracture in the tank. In addition, All fittings on the pole had been heat affected and required replacement. No oil was found in the TX tank and none was seen on the ground. Refer to photos take on site. | EDO fuse | 0 | 0 | 0 |  | BDL8 | Most probable cause is lightning strike (as indicated by evidence found on site i.e. black patches on concrete pole and exit marks etc.). | Grassfire | 17/01/2019 10:46 | 1 | Small: 10 - 1000 sq.m | 11964 |  |  | 20190117SPN_03 | Infrastructure (network-based) | -36.9691 | 147.6048 | 2 | AusNet Services Distribution | Report | 14958 | 0.031403 | 22kV AC | Bairnsdale Airport | 3898 | Omeo | Lightning
Site investigation & testing using an independent earth to possible points of contact around the area where Mark reports receiving a shock (pole #38700) did not reveal any fault on pole #38700 (presumed point of contact) that might have explained why Mark received an electric shock. Further testing was carried out at the time of attendance on all 8 steel poles (4 either side of the road) within the block in Clarendon st between Coventry st and york st (in case the incorrect pole had been identified). CTA and crew attended and carried out inspection and testing of reported pole and poles in the same street block and were unable to find anything that would explain the shock that Mark reports to have received. CTA has advised Aileen to ensure the streetsweeper is inspected for any issues that may have resulted in Mark receiving the shock. | 233 CLARENDON STREET, SOUTH MELBOURNE VIC 3205 | 30209913 |  |  |  | Unknown technical factor |  | Phase to earth |  | ALL details pertaining to the sequence of events for this report have come via City of Port Philip OH&S officer Aileen (0466 836 425).Initial accounts suggested Mark reported arcing and flashing associated with receiving a shock. Follow up with Aileen the day after the initial report confirmed that Mark did NOT see and arcing or flashing AND confirm that Mark did NOT make any contact with the pole. Mark also reports seeing water around the base of the pole that he was driving past when he received a shock. Aileen confirmed in follow up that the pole number identified initially was definitely the pole he was driving past when he reports receiving a shock. | Pole (steel) | 2 | 2 | 2 |  | AP006 | No cause found | Minor shock | 14/01/2019 1:24 |  |  | 11969 | Roadway |  | 20190118PWA_04 | Infrastructure (network-based) | -37.8314 | 144.9601 | 1 | CitiPower | Report | 14965 | 0.039616 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | AF Other
On arrival crew isolated supply and carried out repairs. | MOLONEYS ROAD, WALLUP VIC 3401 | 30081906 |  |  |  | Leakage |  |  | 1 | Vicfire reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV intermediate pole which caused the cross arm to break and the conductors to fall to the ground, resulting in a ground fire (Approx. 2000 sqm) on the road reserve. Protection operated. CFA attended. There were no reported shocks or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | HSM001 | Excessive leakage current | Grassfire | 17/01/2019 18:03 | 1 | Medium: 1000 sq.m - 10 ha | 11970 | Public space |  | 20190118PWA_05 | Infrastructure (network-based) | -36.3536 | 142.3518 | 1 | Powercor | Report | 14966 | 0.024443 | 22kV AC | Horsham Aerodrome | 3401 | Wallup | Crossarm
Crew isolated supply and replaced transformer | 302 BORELLA ROAD, MINCHA WEST VIC 3568 | 30027998 |  | Lightning | [5 empty] | Powercor crew were restoring supply when a transformer failed at this address causing a small grass fire. 1m by 3m. Transformer required replacement. There were no injuries due to this incident. | Transformer | 2 | 2 | 2 |  | CHA006 | Lightning damage to Transformer | Grassfire | 18/01/2019 11:25 | 1 | Localised: less than 10 sq.m | 11971 | Agricultural |  | 20190118PWA_06 | Infrastructure (network-based) | -35.8887 | 144.0917 | 1 | Powercor | Report | 14968 | 0.0099734 | 22kV AC | Swan Hill Aerodrome | 3568 | Mincha West | Lightning
A faults crew attended and identified a probable loose connection contributed to a pole mounted FMJB at pole No. LIS 2310837 to catch on fire outside 20 Cusdin Street, Glen iris. The FMJB supplied a two lot development at 22 Cusdin Street. | 20 CUSDIN STREET, GLEN IRIS VIC 3146 | 2310837 |  | Heat |  | Overheated connection |  |  | 2 | Emergency services reports fire at the top of pole number 2310837. | Connection box | 0 | 0 | 0 |  |  | A probable loose connection overheated causing a FMJB to catch on fire at the pole end. | Pole-top fire | 16/01/2019 14:25 | 1 | Negligible: no ground fire | 11966 | Roadway |  | 20190118UTD_01 | Infrastructure (network-based) | -37.8503 | 145.0699 | 0 | United Energy Distribution | Report | 14960 | 0.01627 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Connection
Fault crew dispatched to investigate and make safe. No visible damage and no repairs required. | 14 Glamis st, Greensborough | LIS903905 |  | Unknown environment factor |  | Unknown technical factor |  |  |  | MFB reported an explosion from pole and small fire on ground next to base of sub pole, now extinguished. | Pole top | 0 | 2 | 0 |  | WT5 | MFB reported an explosion from pole and small fire on ground next to base of sub pole. Fire extinguished before fault crew arrived. Investigation conducted and no damage or fault could be identified that could be attributed to the reported fire. Investigation inconclusive and no cause found. | Grassfire | 21/01/2019 5:15 | 1 | Localised: less than 10 sq.m | 11972 | Residential |  | 20190121SPN_01 | Infrastructure (network-based) | -37.7003 | 145.0974 | 2 | AusNet Services Distribution | Report | 14974 | 0.019066 | 22kV AC | Essendon Airport |  |  | Pole
Dispatched inspector to investigate | 10 MATHER STREET, WANGARATTA VIC 3677 |  |  |  |  | Out of balance load |  |  | 2 | E0008297 - Customer reported receiving Electric Shock from tap | Pad mounted equipment/kiosk | 0 | 0 | 0 |  |  | Mr Peter Bullock received a slight electric shock while he was watering the front garden and made simultaneous contact between the front yard tap and the wet ground. Supply arrangement originates from an Iso pole sub, with 22kV, 12.7kV and 230V. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified that the street distribution is highly unbalanced, with Red-175A; White-135A and Blue-87A. This was identified as the cause of the voltage rise on the distribution neutral. | Minor shock | 19/01/2019 9:36 |  |  | 11974 |  |  | 20190121SPN_02 | Infrastructure (network-based) | -36.3778 | 146.3206 | 2 | AusNet Services Distribution | Report | 14973 | 0.01319 | Low voltage AC (<1kV) | Wangaratta Aero | 3677 | Wangaratta | AF Other
The private tree branches were cut clear and the site made safe. | 5 NAUGHTON GROVE, BLACKBURN VIC 3130 |  |  | Precipitation;Alive |  |  |  |  | 2 | Caller reports the tree is on fire near the wires. During wet conditions, a private tree was sagging near the HV conductors due to the heavy rain causing tracking and the tree to smoke. Previously, one branch had burnt through and had fallen to the ground. | Conductor (bare) | 0 | 0 | 0 |  | NW 21 | Vegetation: Trees Incident | Other vegetation | 13/12/2018 12:42 | 1 | Negligible: no ground fire | 11975 | Residential |  | 20190121UTD_01 | Infrastructure (network-based) | -37.8281 | 145.1584 | 1 | United Energy Distribution | Report | 14977 | 0.019427 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Trees
The flashover caused a conductor for a HV surge divertor to become disconnected and it was arranged for a crew to return tomorrow and cut the tail clear in daylight. | 198 EAST BOUNDARY ROAD, BENTLEIGH EAST VIC 3165 |  |  | Animal | [5 empty] | At 10.43PM on 15/12/2018, 11kV feeder OR 24 circuit breaker successfully reclosed and held. The MFB called to advise there is a pole fire outside 198 East Boundary Road, Bentleigh East. The cause was a possum on the HV CHP to "Boundary198-Walker" Indoor substation. The possum caused a flash over and charred the timber pole. | Cable;Surge diverter;Dropper/bridge | 0 | 0 | 0 |  | OR 24 | Animal Incident | Pole-top fire;Damage to network assets | 15/12/2018 22:43 | 1 | Negligible: no ground fire | 11976 | Roadway |  | 20190121UTD_02 | Infrastructure (network-based) | -37.9159 | 145.0604 | 1 | United Energy Distribution | Report | 14978 | 0.0050359 | 11kV AC | Moorabbin Airport | 3165 | Bentleigh East | Animal
Site made safe, low voltage conductor was repaired and a new service was installed to ensure no future clashing at this location. | 13 ROCKBEARE GROVE, IVANHOE VIC 3079 |  |  |  |  | Conductor clashing | Poor workmanship |  | 2 | Blue phase low voltage conductors on the ground due to clashing of mains and service conductors. | Conductor (bare);Service conductor | 0 | 0 | 0 |  |  | Clashing of mains and service conductors due to insufficient clearance resulting in the conductor and service coming into contact. i.e. original service was not installed in the best location. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/01/2019 8:55 |  |  | 11981 | Residential |  | 20190122JEM_01 | Infrastructure (network-based) | -37.7724 | 145.0382 | 1 | Jemena | Report | 15370 | 0.039145 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Conductor
Fault truck isolated the existing service cable to the property and made repairs. | 93A HAROLD STREET, THORNBURY VIC 3071 | 30199624 |  |  |  | Fatigue |  |  | 2 | Plumber received an electric shock when he made simultaneous contact between the metallic gas pipe and the ground whilst lying on his back in the sub floor cavity | Service conductor | 0 | 0 | 0 |  | NC015 | Connection failure - Pole end neutral service conductor had broken away from the connection to the reticulation conductor | Minor shock | 15/01/2019 14:30 |  |  | 11997 | Residential |  | 20190124PWA_02 | Infrastructure (network-based) | -37.7559 | 144.9914 | 1 | CitiPower | Report | 15008 | 0.034877 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Connection
On arrival crew isolated supply and carried out repairs | 2067 WIMMERA HIGHWAY, APSLEY VIC 3319 | 32120393 |  | Animal |  | Rot |  |  | 1 | A wooden termination cross-arm broke on Aspley P 2 202 the incident location causing conductor clashing and a low conductor across the Wimmera Highway. Debris falling to ground is believed to have ignited a grass fire (61,000m2 burnt) which started at this point. This fire was subsequently extinguished by the CFA. A large truck passing under the low conductor has snagged the low conductor causing it to break and fall to the ground. There was no reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | CHM011 | Crossarm failure due to termite damage | Grassfire | 25/01/2019 9:57 | 1 | Medium: 1000 sq.m - 10 ha | 12013 | Roadway |  | 20190125PWA_03 | Infrastructure (network-based) | -36.9699 | 141.0936 | 1 | Powercor | Report | 15687 | 0.011091 | 22kV AC | Horsham Aerodrome | 3319 | Apsley | Crossarm
On arrival crew isolated supply and carried out repairs. | 2 JOY STREET, BALWYN NORTH VIC 3104 |  |  |  |  | Corrosion |  |  |  | CP received a report of supply interruption and fire at the incident location. On arrival the crew found that an IPC connector and blue phase isolator had burnt out. Debris from isolator fell to ground causing a small fire at the base of the pole. There was no reported injuries or third party property damage. | Disconnector/isolator;Connector/termination | 2 | 2 | 2 |  | WD011 | Overheated connection | Grassfire | 24/01/2019 15:01 | 1 | Localised: less than 10 sq.m | 12016 | Roadway |  | 20190125PWA_04 | Infrastructure (network-based) | -37.7835 | 145.0919 | 1 | CitiPower | Report | 15032 | 0.034089 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | Connection
Dispatched fault crew to investigate and make safe. | 21 DINWOODIE DRIVE, NEWBOROUGH VIC 3825 | LIS 2207877 |  |  |  | Candled fuse |  |  |  | E0008722 - Candled PF HV Fuse in the vicinity of small grass fire (1mx0.5m) on nature strip outside address. | Powder filled | 0 | 0 | 0 |  | MOE31 | Candled fuse. Fuse replaced and supply restored | Grassfire | 25/01/2019 15:25 | 1 | Localised: less than 10 sq.m | 12018 | Residential |  | 20190125SPN_05 | Infrastructure (network-based) | -38.1786 | 146.276 | 1 | AusNet Services Distribution | Report | 15035 | 0.020358 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Newborough | Fuse
The electrical inspector investigatesd- active and neutral links were checked for signs of damage,corrosion or poor termination. All connections at the links were reterminated following identification of a loose connection. The installation was left on supply and a defect notice issued due to the condition of the timber meter panel. | 280-350 HEIDELBERG ROAD, FAIRFIELD VIC 3078 |  |  |  |  | Fault on customer installation |  |  | 2 | A female received an electric shock as she made simultaneously contact between her hand and the general mass of earth. | Connection to meter | 2 | 2 | 2 |  |  | The attending LEI measured the voltage with an independent earth and the metallic water pipe, which recorded a voltage of 15.2 volts with the installation under load( kettle and toaster). A NST test was performed at the main switchboard with recorded a FAIL. The main neutral was disconnected from the neutral link at the meter panel and a NST test was repeated. The NST test recorded a PASS. The neutral conductor was reconnected back onto the link and all terminals were tightened and checked. A loose connection at the neutral link caused a current to flow through the M.E.N connection and the metallic water pipes. The increased impedance to flow of the installation return current through the water pipe system was sufficient to cause a voltage rise of 15.2 volts. This was significantly reduced by tightening connections at the customers meter panel/switchboard. | Minor shock | 29/01/2019 8:23 |  |  | 12032 | Other | Canoe club | 20190129JEM_03 | Infrastructure (customer connection) | -37.7845 | 145.0122 | 1 | Jemena | Report | 15055 | 0.0059907 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Fairfield | Connection
Crews attended the site and confirmed there was no visible damage to the conductors, before restoring supply. A Fault followup was raised by the crew to get a gloving crew to do a closer visual inspection of the conductor in the following days, to ensure there was no damage to the conductor. | BENALLA-TOCUMWAL ROAD, YUNDOOL VIC 3727 | 32180794 |  |  |  | Conductor clashing |  |  | 1 | Following a HV outage, a representative from Lawrence Brothers Quarry called to say that they believed they were the cause of the outage. The representative said that they had done a "shallow blast" in the quarry with approx. 3kg of explosives. Several large rocks were ejected from the quarry as a result of the explosion, with at least one rock striking the nearby HV overhead conductors, resulting in clashing of the conductors and a subsequent outage. There was no fire, no reported injuries or other damage reported. | Conductor (bare) | 2 | 2 | 2 |  | NKA001 | Blasting works at adjacent quarry | Loss of supply | 24/01/2019 11:56 |  |  | 12033 | Commercial |  | 20190129PWA_05 | Infrastructure (network-based) | -36.2107 | 145.7738 | 1 | Powercor | Report | 15313 | 0.0043704 | 22kV AC | Shepparton Airport | 3727 | Yundool | Other
Supply isolated and repairs carried out. | 229-231 DOMAIN ROAD, SOUTH YARRA VIC 3141 | 10587730 | Working too close to underground cables | [6 empty] | Contractors installing optic-fibre cable bored into the RTS 153 22kV underground cable at two points damaging the cable adjacent the incident address. The underground cable subsequently faulted tripping the 22kV feeder circuit breaker. Faulted on the 8.11.2018. (Exact date damaged occurred is unknown). During repairs the underground cable was excavated and the damage identified. There was no ground fire or reported injury due to this incident. | Cable | 2 | 2 | 2 |  | RTS153 | Boring machine damage cable | No Go Zone (contact);Damage to network assets | 43323 |  |  | 12037 | Roadway |  | 20190130PWA_01 | Infrastructure (network-based) | -37.8346 | 144.9854 | 1 | CitiPower | Report | 15075 | 0.018841 | 22kV AC | Essendon Airport | 3141 | South Yarra | Dug up
On arrival crew disconnected supply to lighting | 2 SHAFTSBURY BOULEVARD, POINT COOK VIC 3030 | 30141371 | Working too close to underground cables | [6 empty] | PAL received a report of a contractor exposing underground cable at incident location. On arrival the PCA Field Crew have advised, that the Civil Contractor, Civilex undertaking roadworks at the intersection of Dunnings Rd and Shaftsbury Boulevard, Point Cook have excavated and exposed a public lighting cable within the centre median. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | LV010 | contractor excavating for roadwork | Damage to network assets | 15/01/2019 16:00 |  |  | 12040 | Roadway |  | 20190130PWA_02 | Infrastructure (network-based) | -37.8868 | 144.7499 | 1 | Powercor | Report | 15065 | 0.017853 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Dug up
On arrival crew isolated supply and carried out repairs | 308 POGUE ROAD, TOOLAMBA VIC 3614 | 33090668 |  | Lightning |  |  |  |  | 1 | Vic Fire reported a ground fire at a pole base at the incident location. On arrival, the Powercor crew found a conductor down and small ground fire that was caused by lightning. There were no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MNA034 | Lightning strike | Grassfire | 30/01/2019 15:30 | 1 | Small: 10 - 1000 sq.m | 12050 | Roadway |  | 20190131PWA_01 | Infrastructure (network-based) | -36.4718 | 145.334 | 1 | Powercor | Report | 15079 | 0.022334 | 22kV AC | Shepparton Airport | 3614 | Toolamba | Lightning
On arrival crew isolated supply and carried out repairs. | 310 BAYUNGA ROAD, TATURA VIC 3616 | 30129290 |  | Lightning |  |  |  |  | 1 | A passer-by reported a wire down at the incident location. Upon arrival the Powercor crew found that the conductor on the ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MNA021 | Lightning strike - No fire | Loss of supply;Damage to network assets | 30/01/2019 12:07 |  |  | 12051 |  |  | 20190131PWA_02 | Infrastructure (network-based) | -36.4368 | 145.2592 | 1 | Powercor | Report | 15080 | 0.020904 | 22kV AC | Shepparton Airport | 3616 | Tatura | Lightning
Fault crew attended, took photos of site, replaced FOLCB and restored supply | 23 MCDONALD DRIVE, WANDONG VIC 3758 | 928497 |  |  |  | Defective component |  |  |  | E0008870 - FOLCB on pole burnt out causing small grass fire at base of pole. | Connection box | 0 | 0 | 0 |  | KLO14 | FOLCB on pole failed and burnt resulting in a ground fire at the base of the pole. Cause of FOLCB failure unknown. Fault truck attended, replaced FOLCB and restored supply | Grassfire | 29/01/2019 22:57 | 1 | Localised: less than 10 sq.m | 12052 |  |  | 20190131SPN_01 | Infrastructure (network-based) | -37.3641 | 145.0335 | 1 | AusNet Services Distribution | Report | 17784 | 0.034253 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3758 | Wandong | Connection
On arrival crew isolated supply and carried out repairs. | 36 COORONG AVENUE, IRYMPLE VIC 3498 | 30096208 |  | Wind;Alive | [5 empty] | Customers reported wires down at incident location. On arrival crew found a tree stem had broken and brought down two conductors causing a small ground fire. The stem broke approximately 1.2 m above the ground prior to falling toward overhead conductors. | Conductor (bare) | 2 | 2 | 2 |  | RCT021 | Vegetation: Trees Incident | Loss of supply;Grassfire | 30/01/2019 18:57 | 1 | Localised: less than 10 sq.m | 12065 | Public space |  | 20190201PWA_01 | Infrastructure (network-based) | -34.2515 | 142.162 | 1 | Powercor | Report | 15542 | 0.020263 | 22kV AC | Mildura Airport | 3498 | Irymple | Trees
The Powercor fault crew isolated the shopping strip at pole, where the service for the faÃ§ade servicing originates. An REC was required to make repairs to the customers wiring. | 16-18 POPLAR AVENUE, SHEPPARTON VIC 3630 | 32192567 |  |  |  | Overheated connection |  |  |  | Emergency services reported a POA fire at IGA in Poplar Avenue, Shepparton. Upon arrival crew found that POA did fail due to excessive heat & was likely to have commenced burning as there was evidence of soot on the adjacent veranda faÃ§ade. The CFA extinguished the POA fire using chemical retardant prior to the fault crews arrival. There was no reported injuries. | Connection box | 2 | 2 | 2 |  | STN021 | Overheated connection in service box | Property | 43467.7417 | 1 | Negligible: no ground fire | 12082 | Commercial |  | 20190204PWA_02 | Infrastructure (customer connection) | -36.3991 | 145.4118 | 1 | Powercor | Report | 15124 | 0.011412 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Connection
On arrival crew isolated supply and carried out repairs | 48 DAVID STREET, ALTONA VIC 3018 | 32164804 |  |  |  | Unknown technical factor |  |  |  | MFB called to report a pole fire at the incident location. On arrival the crew found that an FOLCB box on the pole had caught fire and was destroyed. There were no reported injuries, ground fire or third party damage. | Connection box | 2 | 2 | 2 |  | AL012 | Insufficient remains to determine cause | Pole-top fire | 29/01/2019 11:19 | 1 | Negligible: no ground fire | 12083 | Roadway |  | 20190204PWA_03 | Infrastructure (network-based) | -37.8655 | 144.8267 | 1 | Powercor | Report | 15366 | 0.017442 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Connection
On arrival crew isolated supply and carried out repairs. | BENDIGO-PYRAMID ROAD, RAYWOOD VIC 3570 | 30151753 |  | Lightning | [5 empty] | Crews were in process of locating a fault on feeder when a ground fire was located at a pole mounted capacitor at the incident location. CFA attended and extinguished the fire. There was no reported injuries or third party property damage. | Insulators | 2 | 2 | 2 |  | EHK024 | Found arc root on the HV conductor clamps which is a possibility that it was a direct hit of lightning strike. | Grassfire | 43526.6875 | 1 | Small: 10 - 1000 sq.m | 12086 | Roadway |  | 20190205PWA_01 | Infrastructure (network-based) | -36.4895 | 144.2302 | 1 | Powercor | Report | 15145 | 0.0050544 | 22kV AC | Bendigo Airport | 3570 | Raywood | AF Other
On arrival crew isolated supply and carried out repairs. | BENDIGO-PYRAMID ROAD, PYRAMID HILL VIC 3575 | 31004471 |  |  |  | Fatigue |  |  |  | Vicfire reported grass fire caused by Network assets at the incident location. Upon arrival crew found that the roadside phase conductor broken. A ground fire ignited at the incident location. | Conductor (bare) | 2 | 2 | 2 |  | CHA006 | vibration-induced frettage corrosion. | Grassfire | 43526.6958 | 1 | Medium: 1000 sq.m - 10 ha | 12089 | Roadway |  | 20190205PWA_02 | Infrastructure (network-based) | -36.0856 | 144.1146 | 1 | Powercor | Report | 15147 | 0.012786 | 22kV AC | Bendigo Airport | 3575 | Pyramid Hill | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. The LEI confirmed that a high voltage injection occurred (BWD 1904) affecting customers supplied from "Powers-Allinga" substation that sustained minor damage to appliances and equipment. A LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | SPRINGVALE ROAD, DONVALE VIC 3111 | 7071454 |  | Wind;Alive |  | Conductor clashing;HV injection |  |  | 1 | During severe thunderstorm conditions, 22kV feeder NW13 circuit breaker successfully reclosed and held. A caller reports that powerlines are sparking in Springvale Road near the corner of Mitcham Road. A faults crew attended and suspected that a HVI had occurred to customers supplied from "Power-Elinga" substation after a tree fell over the HV and LV conductors that caused a HV crossarm to break at 1 pole south of DT1208 in Springvale Road causing conductors to clash. In addition, molten metal fell into the dry grass below and a 2sqm grass started that self extinguished. | Conductor (bare) | 0 | 0 | 0 |  | NW13 | Vegetation: Trees Incident | Grassfire | 30/01/2019 16:58 | 1 | Localised: less than 10 sq.m | 12088 | Roadway |  | 20190205UTD_02 | Infrastructure (network-based) | -37.7747 | 145.1832 | 1 | United Energy Distribution | Report | 15142 | 0.036078 | 22kV AC | Moorabbin Airport | 3111 | Donvale | Trees
On arrival crew isolated supply and carried our repairs | 1 JASON STREET, LONG GULLY VIC 3550 | 33012138 |  | Bird |  |  |  |  | 1 | Vicfire reported a pole fire at the incident address. Upon arrival the Powercor fault crew found that a bird had flashed over on the HV between the centre phase disc string and the fuse unit bracket, damaging the glass disc string which required replacing. The bird fell to ground and ignited 2 small grass fires near the base of the pole. There was no reported injuries or third party property damage. | Conductor (bare);Insulators;Pole (concrete) | 2 | 2 | 2 |  | BET001 | Bird Incident | Grassfire | 43587.7597 | 1 | Localised: less than 10 sq.m | 12093 | Roadway |  | 20190206PWA_02 | Infrastructure (network-based) | -36.7514 | 144.2561 | 1 | Powercor | Report | 15152 | 0.019899 | 22kV AC | Bendigo Airport | 3550 | Long Gully | Animal
On arrival crew isolated supply and carried out repairs. | 236 NEWBRIDGE-BRIDGEWATER ROAD, BRIDGEWATER VIC 3516 | 32039868 |  |  |  | Electrical breakdown |  |  | 1 | Customer reported loud explosion and smoke on their substation pole at the incident location. Upon arrival Powercor fault crew found that a ABB surge diverter had ruptured ( Polymer type MVK20 ). Material ejected from the arcing resulted in a very small burnt area at the base of the pole, less than 0.2m square. The customer doused the ground with a pail of water which extinguished the smoldering material. There was no reported injuries or third party property damage | Surge diverter | 2 | 2 | 2 |  | BET001 | Surge diverter ruptured | Grassfire | 43587.7576 | 1 | Localised: less than 10 sq.m | 12095 | Agricultural |  | 20190206PWA_03 | Infrastructure (network-based) | -36.6602 | 143.9151 | 1 | Powercor | Report | 15156 | 0.034433 | 22kV AC | Bendigo Airport | 3516 | Bridgewater | AF Other
On arrival crew confirmed isolation and arranged repairs | 420 TUXION ROAD, APOLLO BAY VIC 3233 | 32062167 |  |  |  | Leakage |  |  |  | Vic fire reported a pole fire at the incident location. On arrival the crew found that the SWER strain substation pole had burnt off in the area of the transformer, resulting in the top section of the pole including the transformer falling to the ground. A small grass fire resulted and was extinguished by the CFA. A small amount of oil was spilt from the transformer, however no oil entered any drains or waterways. There was no other reported third party damage. | Pole (wood);Pole mounted | 2 | 2 | 2 |  | CLC007 | Excessive leakage current caused pole fire followed by small ground fire | Pole-top fire;Grassfire | 43618.0417 | 1 | Small: 10 - 1000 sq.m | 12096 | Agricultural |  | 20190206PWA_04 | Infrastructure (network-based) | -38.732 | 143.6488 | 1 | Powercor | Report | 15157 | 0.034431 | 12.7kV AC (SWER) | Avalon Airport | 3233 | Apollo Bay | Pole
An LEI attended with a Zinfra fault crew and undertook tests. Initial testing with no load connected had the NST passing and 1.2V present on the customer earthing system and pool water. As the load was increased (>25A) the voltage increased to 5.6V at the same measured points. Further investigation found that the premises was the last installation on the UE LV circuit. Zinfra fault crews transferred the underground cable that supplied the shared pit to the other side of the open point (smaller distance to s/s). The same voltage tests were carried out on the circuit while heavily loaded (>25A), the voltage at the customer earthing system and pool water remained at 1.2V. Final NST and network analyses passed and indicated positive results. | 16 BIRDROCK AVENUE, MOUNT MARTHA VIC 3934 |  |  |  |  | Out of balance load |  |  | 1 | The occupants of the household report that they have been feeling a minor tingle when coming into contact with the ground as they exit the pool. | Conductor (bare);Services cable;No failed asset | 2 | 2 | 0 |  |  | Cause appears to be the imbalance under certain periods of the LV circuit supplying this property. | Minor shock | 15/01/2019 10:22 |  |  | 12091 | Residential |  | 20190206UTD_01 | Infrastructure (network-based) | -38.2493 | 145.0313 | 1 | United Energy Distribution | Report | 15150 | 0.032347 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | AF Other
An LEI attended with a Zinfra faults crew and undertook testing. NST test at the main switchboard and metering failed. The fault crew inspected the supply pole and replaced the neutral bridge. NST test passed. Supply to house isolated and re tested, also service crew isolated surrounding houses one at a time with no change to measured voltage at pool. Fault crew then conducted testing at sub pole Parker-Marriage which showed an inbalance of loading on phases, (R 80A W 180A B 250A). Decision was made to parallel LV and isolate sub, this achieved a drop in voltage at pool to 0.6V. Sub and circuit to be further tested for rebalancing and assessed. | 5A PARKER STREET, BRIGHTON EAST VIC 3187 |  |  |  |  | Out of balance load |  |  | 1 | Owner has reported receiving shocks at pool for extended period of time upto 3yrs. Shock received whilst in contact with pool water and metal drainage cover. | Connector/termination;Dropper/bridge | 2 | 2 | 0 |  |  | Cause appears to be the imbalance under certain periods of the LV circuit supplying this property | Minor shock | 22/01/2019 11:18 |  |  | 12094 | Residential |  | 20190206UTD_02 | Infrastructure (network-based) | -37.9189 | 145.0178 | 1 | United Energy Distribution | Report | 15309 | 0.026561 | Low voltage AC (<1kV) | Moorabbin Airport | 3187 | Brighton East | AF Other
Dispatched fault crew to investigate and make safe. Feeder MWTS 31 FDR had tripped from Morwell Terminal. Crew issued an EAP and completed the repair, this included removal of the fallen tree and repair and re-sagging of the conductors. | 610 JUMBUK ROAD, YINNAR SOUTH VIC 3869 | LIS 2614576 |  | Fallen |  |  |  |  | 1 | E0009546 - Wires down between LIS #2614576 and LIS #2614577. Tree brought down by conductors. Ground fire in vicinity. Crew arrived onsite at pole 2614577 Jumbuck Road Yinnar south. Crew observed CFA onsite 1 phase of the single phase conductors on the ground and the other was pinned by fallen tree, the crew also observed burnt area in vicinity size of burnt area. Refer to attached photos. | Conductor (bare) | 0 | 0 | 0 |  | MWT31 | Vegetation: Trees Incident | Grassfire | 43618.3007 | 1 | Small: 10 - 1000 sq.m | 12110 |  |  | 20190207SPN_03 | Infrastructure (network-based) | -38.3517 | 146.382 | 1 | AusNet Services Distribution | Report | 15482 | 0.0043831 | 22kV AC | Morwell (Latrobe Valley Airport) | 3869 | Yinnar South | Trees
Site assessed and made safe | 660 ELIZABETH DRIVE, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown person stole new street light underground cable. | Cable | 2 | 2 | 2 |  |  | Unknown person has stolen street light conductors | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43710.4347 |  |  | 12123 | Residential |  | 20190209JEM_01 | Infrastructure (network-based) | -37.589 | 144.7066 | 1 | Jemena | Report | 15191 | 0.036 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Site assessed and made safe | 75 WHITES LANE, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Unknown person stole copper underground cable. | Cable | 2 | 2 | 2 |  |  | Unknown person stole the copper underground cable | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43679.3688 |  |  | 12124 |  |  | 20190209JEM_02 | Infrastructure (network-based) | -37.5861 | 144.8908 | 1 | Jemena | Report | 15192 | 0.032006 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
On arrival crew isolated supply and carried out repairs | 255 RESERVOIR ROAD, WAURN PONDS VIC 3216 | 33046494 |  | Animal | [5 empty] | During a fault patrol a crew found a conductor on the ground at the incident location. There was a small ground fire (30sq m). There was no reported injuries or third party property damage. | Conductor (bare);EDO fuse | 2 | 2 | 2 |  | WPD011 | Animal Incident | Grassfire | 43710.9993 | 1 | Small: 10 - 1000 sq.m | 12126 | Roadway |  | 20190211PWA_01 | Infrastructure (network-based) | -38.224 | 144.2502 | 1 | Powercor | Report | 15197 | 0.038163 | 22kV AC | Avalon Airport | 3216 | Waurn Ponds | Conductor
On arrival crew isolated supply and carried out repairs. | OLD PETERBOROUGH ROAD, PETERBOROUGH VIC 3270 | 30251712 |  | Bird | [5 empty] | CFA called regarding a grass fire at the above location involving our assets. The crew attended and found conductor damage due to a bird strike. conductor fell to ground causing a small ground fire. The fire was approximately 50M X 30M. There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBL012 | Bird Incident | Grassfire | 43740.4701 | 1 | Medium: 1000 sq.m - 10 ha | 12130 | Public space |  | 20190211PWA_02 | Infrastructure (network-based) | -38.5681 | 142.8596 | 1 | Powercor | Report | 15200 | 0.0085625 | 22kV AC | Warrnambool Airport Ndb | 3270 | Peterborough | Animal
On arrival crew isolated supply and carried out repairs. | MALLEE HIGHWAY, MANANGATANG VIC 3546 | 32154472 |  |  |  | Leakage |  |  |  | Report received from Vic Fire of wires down and grass fire at incident location. On arrival crew found the end burnt off a crossarm and a small grass fire (20 sq m) There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN003 | Leakage current caused pole fire (burnt off crossarm) | Pole-top fire;Grassfire | 43710.6312 | 1 | Small: 10 - 1000 sq.m | 12132 | Roadway |  | 20190211PWA_03 | Infrastructure (network-based) | -35.056 | 142.8771 | 1 | Powercor | Report | 15203 | 0.041352 | 22kV AC | Swan Hill Aerodrome | 3546 | Manangatang | Crossarm
On arrival crew isolated supply and carried out repairs. | 480A AVALON ROAD, AVALON VIC 3212 | 30242888 | Vandalism;Copper theft | [6 empty] | CFA reported a pole fire at the above location. The crew attended and noticed the HV earth and the LV cable had been cut off at ground level and above head height on the pole. The cutting of the earth had started the pole fire. The fire was contained to the pole with no ground fire. CFA attended. | Services cable;Earth/earthing | 2 | 2 | 2 |  | FNS032 | Vandalism and copper theft | Pole-top fire;Damage to network assets | 43710.7889 | 1 | Negligible: no ground fire | 12141 | Roadway |  | 20190212PWA_01 | Infrastructure (network-based) | -38.0839 | 144.4224 | 1 | Powercor | Report | 15217 | 0.014416 | Low voltage AC (<1kV);Earthing cable | Avalon Airport | 3212 | Avalon | Other
On arrival crew arranged isolation and carried out repairs. | PATCHEWOLLOCK-SEA LAKE ROAD, NYARRIN VIC 3533 | 30549570 |  |  |  | Leakage |  |  |  | Following a line outage patrol found a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage | Pole (wood) | 2 | 2 | 2 |  | OYN005 | Excessive leakage current | Pole-top fire | 43350.2444 | 1 | Negligible: no ground fire | 12144 |  |  | 20190212PWA_02 | Infrastructure (network-based) | -35.3909 | 142.6841 | 1 | Powercor | Report | 15221 | 0.033514 | 22kV AC | Swan Hill Aerodrome | 3533 | Nyarrin | Pole
Fault crew dispatched to investigate. No evidence of damage to DB assets | 46 INGRAMS ROAD, RESEARCH VIC 3095 | LIS919354 |  | Animal |  |  |  | Phase to earth |  | E0009283 - report of small fire at base of pole caused by possum contacting O/H HV assets | Conductor (bare) | 0 | 0 | 0 |  | ELM13 | Animal Incident | Grassfire | 43526.2931 | 1 | Localised: less than 10 sq.m | 12146 |  |  | 20190212SPN_03 | Infrastructure (network-based) | -37.6994 | 145.1817 | 2 | AusNet Services Distribution | Report | 15536 | 0.014197 | 22kV AC | Essendon Airport | 3095 | Research | Animal
Fault crew dispatched | 10 WILMA GROVE, ST ANDREWS VIC 3761 | LIS520541 |  |  |  | Candled fuse |  |  |  | E0009287 - small grass fire reported | Boric acid | 0 | 0 | 0 |  | DRN23 | candling HV fuse resulting in small ground fire | Grassfire | 43526.7806 | 1 | Localised: less than 10 sq.m | 12147 | Public space |  | 20190212SPN_04 | Infrastructure (network-based) | -37.6023 | 145.283 | 2 | AusNet Services Distribution | Report | 15226 | 0.028382 | 22kV AC | Wallan (Kilmore Gap) | 3761 | St Andrews | Fuse
The attending Powercor Fault Crew broke and remade all connections at the O/H Reticulation Pole and checked the connections in the FOLCB on the Reticulation Pole and completed and NST Test which confirmed a Pass result. | 14 MORONA AVENUE, NORLANE VIC 3214 | 30067861 |  |  |  | Corrosion |  |  |  | Person was in the rear garden operating the metal Tap when she received an electric shock as she made simultaneous contact between her hand on the metallic tap and her bare feet while standing on the wet concrete path. | Services cable | 0 | 0 | 0 |  | CRO022 | Connection malfunction - Corroded U/G Service Neutral Conductor termination at the Reticulation Pole. | Minor shock | 28/01/2019 10:00 |  |  | 12151 | Residential |  | 20190213PWA_03 | Infrastructure (network-based) | -38.0952 | 144.3516 | 1 | Powercor | Report | 15230 | 0.033304 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Connection
Service line replaced | 38 DAVID STREET, ALTONA VIC 3018 | 30104103 |  |  |  | Corrosion |  |  |  | Person received an electric shock when he simultaneously contacted the metallic tap with one hand and with his feet standing on the lawn . A voltage test between the tap and lawn area revealed the service neutral conductor was damaged | Service conductor;Neutral screen | 0 | 0 | 0 |  | AL012 | Corroded service neutral at POA | Minor shock | 29/01/2019 16:30 |  |  | 12153 | Residential |  | 20190213PWA_04 | Infrastructure (customer connection) | -37.8663 | 144.8266 | 1 | Powercor | Report | 15233 | 0.019626 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | OH Cable
HV fuse replaced | 1589 EUROA-MANSFIELD ROAD, GOORAM VIC 3666 | Pole 3904896 |  |  |  | Candled fuse |  |  |  | Candling Fuse | Boric acid | 0 | 0 | 0 |  | BN1 | Candling HV fuse | Pole-top fire | 43801.7688 | 1 | Negligible: no ground fire | 12152 |  |  | 20190213SPN_01 | Infrastructure (network-based) | -36.8757 | 145.6133 | 1 | AusNet Services Distribution | Report | 17767 | 0.016146 | 22kV AC | Mangalore Airport | 3666 | Gooram | Fuse
The tree clearing crew ("Ryder Energy" working on behalf of "Active Tree Services") remained on site to ensure the site was safe and not disturbed. AusNet fault crew dispatched to repair. Tree clearing crew stood down immediately and taken to a Medical Centre for Drug and Alcohol Testing, results were negative. They will remain stood down from work pending the incident investigation by the contractor. Crew advised to contact their Supervisor if they are not confident or require advice on different cutting methodologies to ensure all Safety Practices are adhered to at all times. | 33 STATION STREET, WALLAN VIC 3756 | LIS912429 and LIS912430 | Working too close to overhead lines |  |  |  | Not followed;Ineffective planning/procedures/processes |  |  | E0009357 - Tree clearer cut LV service while cutting trees | Service conductor | 0 | 0 | 0 |  | KLO14 | Vegetation: Trees Incident | No Go Zone (contact) | 43557.4757 |  |  | 12156 |  |  | 20190213SPN_02 | Infrastructure (network-based) | -37.4153 | 145.0048 | 1 | AusNet Services Distribution | Report | 15237 | 0.016885 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3756 | Wallan | Other
crew attended and isolated supply Werribee police informed | 160 MANOR LAKES BOULEVARD, MANOR LAKES VIC 3024 | 30250321 | Copper theft | [5 empty] | 2 | A civil contractor reported a cable theft at the incident location. Upon arrival, the Powercor crew found that the 300m metres of 16mm 4C cable missing from public lighting | Cable;Copper | 0 | 0 | 0 |  | WBE014 | interference - copper theft | Damage to network assets | 43500.4792 |  |  | 13600 | Residential |  | 20190430PWA_01 | Infrastructure (network-based) | -37.8752 | 144.5975 | 1 | Powercor | Report | 16949 | 0.00080324 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Other
Crew removed service cable and advised customer to provide new BTS pole | 185 ROSSLYN STREET, WEST MELBOURNE VIC 3003 | 84030282 | Vehicle | [6 empty] | MFB and Police reported wire down and resting on the truck at the above incident location. On arrival, the crew found a Low Voltage (LV) overhead service cable had been pulled down by the truck and fallen onto the roof of the truck. The LV service overhead cable was a temporary building service cable supplying the construction site | Private overhead electric line (POEL);Service conductor | 0 | 0 | 0 |  | VM026 | civil works near BTS pole compromised footings resulting in lowering of service cable over roadway | Damage to network assets | 43559.2458 |  |  | 13609 | Construction |  | 20190501PWA_03 | Infrastructure (network-based) | -37.8096 | 144.9485 | 1 | CitiPower | Report | 16957 | 0.0064884 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Vehicle
Faulted area isolated and cross-arm replaced. | 121 OGILVIE AVENUE, ECHUCA VIC 3564 | 30121458 |  |  |  | Leakage |  |  | 1 | Emergency services report pole fire O/S 121 OGILVIE AVENUE ECHUCA Powercor crew attended site to find the lowest high voltage cross-arm had burnt thru on the king bolt, conductors fell onto low voltage circuit below | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | ECA001 | leakage current | Pole-top fire | 43470.3819 | 1 | Negligible: no ground fire | 13614 | Roadway |  | 20190501PWA_05 | Infrastructure (network-based) | -36.1406 | 144.7598 | 1 | Powercor | Report | 16932 | 0.010855 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3564 | Echuca | Crossarm
LEI dispatched to investigate. Testing confirmed the damage to insulation on the service cable. Damaged service cable removed and replaced with new. Supply restored | 9 Frieda Ct Ferntree Gully VIC 3156 | LIS1301700 |  |  |  | Defective component;Mechanical breakdown |  | Phase to earth |  | Resident reported receiving electric shock while on an aluminium ladder removing guttering. | Service conductor;Customer installation | 0 | 0 | 0 |  | FGY22 | Customer was on aluminium ladder beginning to remove guttering when he received a shock. Service cable to house was tight as a result of movement on the power pole resulting in the service cable holding device(dog bone) failing allowing the metal shaft to wear through cable livening up the riser bracket and abutting gutter. | Minor shock | 28/04/2019 15:30 |  |  | 13613 | Residential |  | 20190501SPN_02 | Infrastructure (customer connection) | -37.8933 | 145.2819 | 2 | AusNet Services Distribution | Report | 16885 | 0.0022917 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 |  | Pole
Isolated supply to substation from the HV at front of property. Police were notified. | 820-848 PRINCES HIGHWAY, SPRINGVALE VIC 3171 |  | Vandalism;Copper theft | [5 empty] | 2 | On attendance to site for a final read and disconnection, the crew found the fence around the ground type substation Trico-Princes had been cut and the LV isolators had been opened by unknown persons. It was also discovered that these persons had broken into factory to steal copper from switchroom. | Disconnector/isolator;Outdoor;No failed asset;Customer installation | 2 | 2 | 2 |  |  | Unknown persons gained unauthorised access into the substation enclosure to isolate supply to the vacant building for the purpose of copper theft from the building. | Loss of supply;Damage to network assets | 43681.5833 |  |  | 13606 | Commercial |  | 20190501UTD_01 | Infrastructure (network-based) | -37.9367 | 145.1627 | 1 | United Energy Distribution | Report | 17026 | 0.018495 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3171 | Springvale | Other
UE fault crew attended and replaced the 2 core overhead service. | 17 KIRKWOOD AVENUE, SEAFORD VIC 3198 | 3316984 | Working too close to overhead lines | [5 empty] | 1 | Report received that an excavator on a property being renovated has hit and damaged the aerial service line within the property. | Service conductor | 0 | 0 | 0 |  |  | An excavator undertaking excavation works within the property has hit the OH service line. | Loss of supply;Damage to network assets | 14/04/2019 16:20 |  |  | 13608 | Residential |  | 20190501UTD_03 | Infrastructure (network-based) | -38.1181 | 145.1318 | 1 | United Energy Distribution | Report | 17022 | 0.028144 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Vehicle
Made safe, no damage to customers, slight burn marks on conductors, no broken strands. | 1-3 CURTIS STREET, STAWELL VIC 3380 | 33052659 | Blown detritus | Wind |  |  |  |  | 1 | Vic Fire report of explosion possibly caused by trampoline hitting powerlines. Crew found trampoline had made contact with powerlines | Conductor (bare) | 0 | 0 | 0 |  | STL004 | airborne trampoline | Loss of supply | 43742.4951 |  |  | 13623 | Roadway |  | 20190502PWA_02 | Infrastructure (network-based) | -37.0592 | 142.7671 | 1 | Powercor | Report | 16902 | 0.039928 | 22kV AC | Horsham Aerodrome | 3380 | Stawell | Other
The substation has been isolated as it is to be demolished | 1645 BOUNDARY ROAD, MOUNT COTTRELL VIC 3024 | 31031711 | Copper theft | [6 empty] | A customer reported a copper theft at the incident location. The attended crew observed 4m of HV earthing cable from pole sub has been stolen together with the customer service cable. The property is vacant and it is to be demolished so the Sub isolated. | Services cable;Customer installation | 0 | 0 | 0 |  | TNA023 | copper theft | Damage to network assets | 43803.4292 |  |  | 13626 | Residential |  | 20190503PWA_02 | Infrastructure (network-based) | -37.7984 | 144.625 | 1 | Powercor | Report | 17357 | 0.00092477 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival isolation points confirmed and repairs initiated | MOUNT MACEDON ROAD, GISBORNE VIC 3437 | 33026018 | Vandalism;Copper theft | [6 empty] | Gisborne Police reported cable has been ripped out and stolen at pole Mt Macdeon Sanders Tie P6 intersection of Calder Freeway and Mt Macedon Road New Gisborne. Police caught thieves stealing copper from substation supplying bridge heating which wasn't connected as had previously been stolen/vandalized and cabinet damaged, substation still on supply for road lighting which wasn't affected. There was no fire or reported injuries | Services cable | 2 | 2 | 2 |  | GSB011 | Copper theft and vandalism | Damage to network assets | 43620.4535 |  |  | 13635 | Roadway |  | 20190506PWA_06 | Infrastructure (network-based) | -37.4566 | 144.5794 | 1 | Powercor | Report | 16916 | 0.017001 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
pole replaced | 695 IRYMPLE AVENUE, IRYMPLE VIC 3498 | 30558650 |  |  |  | Leakage |  |  | 1 | Vic Fire reported a pole fire at the incident location. Upon arrival, the crew found that the pole top burnt through and fell onto LV | Pole (wood) | 0 | 0 | 0 |  | RCT011 | excessive leakage current | Pole-top fire | 23/04/2019 12:13 | 1 | Negligible: no ground fire | 13640 | Roadway |  | 20190507PWA_01 | Infrastructure (network-based) | -34.2319 | 142.1848 | 1 | Powercor | Report | 16963 | 0.0065868 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3498 | Irymple | Pole
crew attended isolated supply and replaced cross-arm | 3420 DEAKIN AVENUE, MILDURA VIC 3500 | 30098768 |  |  |  | Leakage |  |  | 1 | Vic Fire reported a pole fire at the incident location, attending crew found HV cross-ram had burnt | Crossarm (wood) | 0 | 0 | 0 |  | MBN032 | leakage current ignited wooden cross-arm | Pole-top fire | 23/04/2019 15:37 | 1 | Negligible: no ground fire | 13647 | Residential |  | 20190507PWA_07 | Infrastructure (network-based) | -34.251 | 142.0831 | 1 | Powercor | Report | 16995 | 0.033785 | 22kV AC | Mildura Airport | 3420 | Mildura | Crossarm
Injured Downer field crew employee was taken to hospital via ambulance. ESV advised . Security Manager advised and organised Police to attend. Investigation carried out, incident report attached detailing findings. Safety Gram SG2019017 has been issued advising Modiewark style proximity testers are designed to operate on one single conductor at a time and must not be used to test multi-phase overhead, or underground bundled cables at any time. Safety gram provides advice on how to perform a successful de-energised test using a Modiewark style/or approved tester on bundled cable which requires the cores being separated prior to test. | 12 CARPATHIAN DRIVE, CLYDE NORTH VIC 3978 | LIS2601782514; LIS2601782516 |  |  |  |  | Not followed;Lack of training |  |  | E0019302 - MEC worker (contractor) has received flash burns while testing a section of cut underground cable at an LV pit. Identified that copper theft had occurred at a nearby street light and 2 seperate Modiwarks used to test whether the LV Cable was alive after attempted theft. The work party initially tested the underground pit with a Modiewark proximity detector (set to 240V). The test did not show any voltage from the section of cut 35mm 4 core (live) cable. A secondary test was attempted with a hand held voltmeter on the end of exposed cores, and a flashover occurred. | Services pit | 0 | 0 | 0 |  | CLN13 | The investigation has found the radiated electromagnetic fields from closely bunched multi-phase conductor eliminate the potential to gain a live reading with a Modiewark style tester and bundled cables arerequired to be separated before testing with a modiwark. Safety Gram SG2019017 has been issued advising Modiewark style proximity testers are designed to operate on one single conductor at a time and must not be used to test multi-phase overhead, or underground bundled cables at any time. Safety gram provides advice on how to perform a successful de-energised test using a Modiewark style/or approved tester on bundled cable. A Downer linesman crew (2 person) were issued a fault for a suspected stolen LV service cable located in a service pit. The task required the work crew to isolate and make the cable safe prior to it being reissued for rectification. One member of the faults crew arrived onsite and found that a section of LV service cable had been cut at two pits feeding street lights poles. The lineworker performed a voltage check by waving a Modiewark set to 240V in the pit on the cut 4-core cable, which provided no reading. The second member of the crew arrived onsite and a discussion was had on the works required. The work crew inspected the pit and found there to be no visible signs of an arc flash, which made the crew believe the cable was de-energised. The crew decided that prior to investigating the source of supply, they would test the cable using an approved test method (Modiewark is an indicator test not confirmatory test) to establish the status of the cable if it was alive or dead. The injured person (IP) set up his rubber insulated mat, put on all his required PPE for LV works (LV insulated gloves/outers, hard hat and safety glasses) and laid out his testing devices (earth reel and voltmeter). While kneeling on the rubber mat and leaning into the pit he extended his right hand with his test probe of the voltmeter to check voltage on the exposed ends of the cut 4-core cable, he received a positive test for the cable being alive and pulled back out of the pit. In the process of pulling the testing probe out of the pit, the probe has made contact either between the active and neutral or two actives resulting in an arc flash which caused burns to the worker's face, and right forearm. | Medical attention (first aid/doctor/hospital) | 43621.5833 |  |  | 13645 |  |  | 20190507SPN_02 | Infrastructure (network-based) | -38.0975 | 145.3357 | 1 | AusNet Services Distribution | Report | 17256 | 0.0038183 | Low voltage AC (<1kV) | Moorabbin Airport | 3978 | Clyde North | Other
line isolated and cross arm replaced | 29 RICHARDS ROAD, CASTLEMAINE VIC 3450 | 32045602 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. Upon arrival, the fault crew found 66kV cross arm ignited. | Crossarm (wood) | 0 | 0 | 0 |  | BETS-CMN | leakage current | Pole-top fire | 26/04/2019 9:02 | 1 | Negligible: no ground fire | 13650 | Roadway |  | 20190508PWA_02 | Infrastructure (network-based) | -37.0595 | 144.2085 | 0 | Powercor | Report | 17013 | 0.018726 | 66kV AC | Bendigo Airport | 3450 | Castlemaine | Crossarm
The customer was instructed to keep all people and livestock away from the live conductor until the Powercor crew could attend. Pole replaced | 2694 ROSEBERY-RAINBOW ROAD, RAINBOW VIC 3424 | 32093204 | Vehicle | [5 empty] | 2 | A customer called Powercor to report that a front end loader had taken out a pole in the paddock at the incident location. On arrival the crew found that a large front end loader was carting large square bales of hay in from the paddock when the loader struck a SWER intermediate pole front on. The pole was knocked to the ground, however the conductor remained approx. 3 metres above the ground alive, the loader came to rest well clear of the line. The customer was instructed to keep all people and livestock away from the live conductor until the Powercor crew could attend | Pole (wood) | 0 | 0 | 0 |  | NHL015 | vehicle ( tractor) collided with pole | Loss of supply | 16/04/2019 15:06 |  |  | 13653 | Agricultural |  | 20190508PWA_05 | Infrastructure (network-based) | -35.8505 | 142.1222 | 1 | Powercor | Report | 17020 | 0.010431 | 12.7kV AC (SWER) | Horsham Aerodrome | 3424 | Rainbow | Vehicle
Fault crew and LEI dispatched. Damaged service cable replaced with new. All tests carried out and passed | 4 GLENFERN AVENUE, UPWEY VIC 3158 | LIS1303709 | Vehicle |  |  |  |  | Phase to earth |  | E0019326 - Customer reported receiving tingles from laundry tap | Service conductor | 0 | 0 | 0 |  | FGY13 | New home owner Stephen Hodge received a tingle when he touched the cold tap at the laundry sink. Laundry taps found bonded to the installations earthing system. Neutral Conductor on the overhead service cable was broken and appears to have been broken by a vehicle, most likely by the removalist truck backing up the driveway. The vehicle driver appears to have known they hit and damaged the service as the broken Neutral was found twisted back up onto the service to prevent it from dangling down. AusNet were not contacted until the new home owner received a shock. | Minor shock | 43651.3701 |  |  | 13656 | Residential |  | 20190509SPN_01 | Infrastructure (customer connection) | -37.9173 | 145.3334 | 1 | AusNet Services Distribution | Report | 17050 | 0.0087905 | Low voltage AC (<1kV) | Moorabbin Airport | 3158 | Upwey | OH Cable
Crew isolated and contacted CFA to extinguish pole fire | 901 CARINA SOUTH ROAD, CARINA VIC 3512 | 32154757 |  |  |  | Leakage |  |  | 1 | Customer reported pole fire in paddock. On arrival crew found pole was burning on the inside and on the tee-off cross arm | Crossarm (wood) | 0 | 0 | 0 |  | OYN001 | excessive leakage current | Grassfire | 43651.5618 | 1 | Negligible: no ground fire | 13662 | Agricultural |  | 20190510PWA_05 | Infrastructure (network-based) | -35.3373 | 141.108 | 1 | Powercor | Report | 17059 | 0.018997 | 22kV AC | Mildura Airport | 3512 | Carina | Pole
crew attended and replaced pole | HARDS LANE, WERRIMULL VIC 3496 | 30283808 |  |  |  | Leakage |  |  | 1 | Vicfire reported a pole fire in Hards lane, the attending crew found the top of the pole had burnt and signs of burning on the ground. | Pole (wood) | 0 | 0 | 0 |  | MBN031 | excessive leakage | Grassfire | 43501.2701 | 1 | Localised: less than 10 sq.m | 13666 | Agricultural |  | 20190510PWA_07 | Infrastructure (network-based) | -34.2846 | 141.6612 | 1 | Powercor | Report | 17063 | 0.023177 | 12.7kV AC (SWER) | Mildura Airport | 3496 | Werrimull | Pole
On attendance by the fault crew, the fire authority had extinguished the fire. The fault crew replaced the FOLCB and restored supply to the premise. | 23-25 SOUTH GIPPSLAND HIGHWAY, DANDENONG SOUTH VIC 3175 | 8813163 |  |  |  | Overheated connection |  |  | 1 | UE received report from fire authority of a pole fire outside the Metro Petrol station in Dandenong Sth. On arrival, the crew found a pole mounted Fused Overhead Line Connection Box was in a melted condition. | Connection box | 0 | 0 | 0 |  |  | It is likely that a loose connection within the FOLCB resulted in overheating within the box. | Loss of supply;Plant/equipment | 24/04/2019 8:00 | 1 | Negligible: no ground fire | 13663 | Roadway |  | 20190510UTD_01 | Infrastructure (network-based) | -38.0028 | 145.2269 | 1 | United Energy Distribution | Report | 17060 | 0.0046887 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Connection
Fault crew attended and replaced the damaged aerial service line. | 535 STATION STREET, CARRUM VIC 3197 | 3304916 | Working too close to overhead lines | [5 empty] | 1 | UE received report of an aerial service line hit by an excavator as part of a construction works by the Southern Program Alliance. A Permit to Work was on issue for No Go Zone requirements, however the service appears to be outside the conditions of the permit. | Service conductor | 0 | 0 | 0 |  |  | A No Go Zone permit was on issue. Then aerial service line that was damaged app[ears to be located outside of the permit zone. | Loss of supply;No Go Zone (contact);Damage to network assets | 17/04/2019 17:30 |  |  | 13670 | Roadway |  | 20190513UTD_01 | Infrastructure (network-based) | -38.0785 | 145.1239 | 1 | United Energy Distribution | Report | 17068 | 0.041219 | Low voltage AC (<1kV) | Moorabbin Airport | 3197 | Carrum | Vehicle
Crew confirmed site was safe, proceeded to complete appointment and report interference with CP/PAL assets | 6 FAIRFAX CIRCUIT, ALBANVALE VIC 3021 | 30103976 | Caused by REC/contractor | [5 empty] | 2 | meter and servicing crew attended site and found that the fuse and meters had been removed. | Connection to meter;Meter board (including fuses) | 0 | 0 | 0 |  | SU022 | Interference works preceding appointment | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43529.375 |  |  | 13674 | Residential |  | 20190514PWA_02 | Infrastructure (network-based) | -37.7501 | 144.7622 | 1 | Powercor | Report | 17072 | 0.0058044 | Low voltage AC (<1kV) | Laverton Raaf | 3021 | Albanvale | Other
leads replaced | 371 CHANNEL ROAD, MERBEIN VIC 3505 | 30155030 |  |  |  | Electrical breakdown |  |  | 1 | Vic Fire reported power line sparking and arcing. Attending crew found HV insulated leads to transformer had ruptured. | Conductor (covered uninsulated) | 0 | 0 | 0 |  | MBN031 | insulation ruptured | Loss of supply;Singeing or local charring/blackening only | 43713.8667 |  |  | 13676 | Agricultural |  | 20190514PWA_04 | Infrastructure (network-based) | -34.1757 | 142.0438 | 1 | Powercor | Report | 17394 | 0.0070949 | 22kV AC | Mildura Airport | 3505 | Merbein | Conductor
Section made safe and repairs undertaken | 65 BUCKLAND WAY, SUNBURY VIC 3429 | 10150313 | Copper theft | [5 empty] | 2 | Copper theft of LV UG cable roughly 30m in length | Cable | 0 | 0 | 0 |  | SHM11 | Copper theft | Loss of supply | 18/05/2019 6:49 |  |  | 13682 |  |  | 20190518JEM_01 | Infrastructure (network-based) | -37.6064 | 144.7235 | 1 | Jemena | Report | 17086 | 0.018994 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Fault crew dispatched to make safe and carry out repairs. Overhead line isolated and broken steel conductors repaired | 1425 BALLARTO ROAD, CLYDE VIC 3978 | LIS519134 | Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0020138 - report of an excavator hitting and bringing down overhead HV conductors | Conductor (bare) | 0 | 0 | 0 |  | CLN22 | Fault crew advised that an excavator has hit and brought down overhead HV conductors, resulting in 2 blown fuses and damaged steel conductor. The excavator operator was aware of the O/H conductors but forgot the boom was up whilst tracking and made contact with the conductors. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 17/05/2019 7:45 |  |  | 13693 |  |  | 20190521SPN_04 | Infrastructure (network-based) | -38.1324 | 145.3167 | 1 | AusNet Services Distribution | Report | 17100 | 0.035922 | 22kV AC | Moorabbin Airport | 3978 | Clyde | Vehicle
Crew removed service line and meter to make property safe | 7 HIGHLAND STREET, KINGSBURY VIC 3083 |  | Unauthorised access | [5 empty] | 2 | Demolition company have demolished most of house and removed service fuse at point of attachment Details of the demolition company are unavailable as the house has already been demolished | Customer installation | 0 | 0 | 0 |  |  | Demolition company have made property unsafe by knocking it down prior to having property disconnected from supply | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/05/2019 14:39 |  |  | 13694 | Residential |  | 20190522JEM_01 | Infrastructure (network-based) | -37.7177 | 145.0398 | 1 | Jemena | Report | 17101 | 0.039093 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Kingsbury | Other
Metering manager attended site to ensure the site was safe. Zinfra Compliance Officer visited site on 7 May 2019 and established that 006 meter 0366812 is still on site and is connected and functioning correctly. There are no controlled loads on site, these having been disconnected and no longer in use. | 7 POWLETT STREET, SUNBURY VIC 3429 |  | Unauthorised access | [5 empty] | 2 | Metering & Service (M&S) crew attended site for a meter consolidation for Solar purposes. The crew advised the customer/home owner that an REC is required on site when they attend for meter consolidations so the REC can complete the wiring disconnections/alterations/changes to the customer wiring and metering arrangements. The customer/home owner called the Solar REC and placed him on speaker with herself and the M&S crew to which the M&S crew explained the requirement for him to be on site to complete the wiring works for them to be able to complete the metering consolidation. The REC advised the crew that he would not be attending site and was directing the crew to complete the customer wiring works and to remove the electricity meter and complete the metering consolidation themselves without his involvement as he would not be attending site. When the crew advised the REC that they cannot alter/change the customer wiring and configurations the REC advised the crew that if they didnâ€™t complete it he would attend site the following day and personally remove the wiring and meter himself and drop it off to Collins St (Jemena Office). The crew strongly advised the REC that he cannot do this as it is an offense and there is consequences for this. The customer wiring behind the meter panel has been disconnected. Meter 0262582 is no longer on site and was dropped off at Jemena Collins St on 15.3.19 The REC appears to be in breach of Regulation 45A of the Electricity Safety Act and did not complete and provide a certificate of electrical safety for the disconnection and alteration of the customer wiring at the metering location. The REC appears to be in Breach of Regulation 320(b) & (d) of the Electricity Safety (Installations) Regulations by interfering with a seal and metering equipment. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/03/2019 10:00 |  |  | 13695 | Residential |  | 20190523JEM_01 | Infrastructure (network-based) | -37.5815 | 144.7421 | 1 | Jemena | Report | 17120 | 0.0087211 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
The REC installed a suitably installed permanent mechanical barrier and protection bollard to project and restrict the area in front of the metering equipment and below the FOLCB and removing the construction scaffold below the distributors service line location. The crews remained on site until the issuel had been rectified. | 68 SOUTH STREET, ASCOT VALE VIC 3032 |  | Unauthorised access | [5 empty] | 2 | Service & Metering crew attended the site for a service and metering upgrade. When the crew arrived they found the overhead service in a bad condition (see photos attached in section 7) with a piece of PVC conduit placed over the overhead service cable which was placing pressure and sag on the service cable with the service cable draped over the new conductive metal guttering and the crimped cable moulded/mudded into the new/repaired roof structure with no sign of or access to the FOLCB and SPD fuses. It appears the property has conducted a major renovation and upgrade in and around the live overhead service and created an unsafe situation. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/04/2019 11:00 |  |  | 13697 | Residential |  | 20190523JEM_03 | Infrastructure (network-based) | -37.7777 | 144.9251 | 1 | Jemena | Report | 17118 | 0.0006169 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Other
Service crew reattached service to No 9 to the catenary wire. | 7 STOOKE STREET, YARRAVILLE VIC 3013 |  | Unauthorised access | [5 empty] | 2 | While the Metering & Service crew attended a site for a new Builder Temporary Supply (BTS) at 7 STOOKE STREET, YARRAVILLE VIC 3013, they noticed that the builder had raised the service going to No 9. | Neutral screen | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/03/2019 19:58 |  |  | 13704 | Residential |  | 20190523JEM_08 | Infrastructure (network-based) | -37.8149 | 144.8649 | 1 | Jemena | Report | 17114 | 0.025822 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Other
The fault crew replaced the FOLCB and restored supply to the premise. | 31 MUNRO STREET, BLAIRGOWRIE VIC 3942 | 1304717 |  |  |  | Overheated connection |  |  | 2 | UE received a report from fire authority of a pole fire outside 31 Munro St Blairgowrie. On arrival, the crew found a pole mounted Fused Overhead Line Connection Box was in a melted condition. | Connection box | 0 | 0 | 0 |  |  | It is likely that a loose connection within the FOLCB resulted in overheating within the box. | Plant/equipment | 17/05/2019 20:40 | 1 | Negligible: no ground fire | 13699 | Roadway |  | 20190523UTD_02 | Infrastructure (network-based) | -38.3754 | 144.7742 | 1 | United Energy Distribution | Report | 17106 | 0.020468 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Connection
Crew made safe and repaired broken connections. Techsafe inspector investigated possible high voltage injection. The attending LEI carried out a further damage assessment at all affected properties on the circuit. An inspection was carried out of all meters, customer fuse boxes and accessible switchboards. No signs of evident damage was recorded. Following the damage assessment the attending LEI deemed the circuit as safe to restore following the Jemena construction crew completing their works. | 1 WILLIS STREET, YARRAVILLE VIC 3013 | 11450463 |  | Blown branch/vegetation |  |  |  |  | 1 | Tree across HV overhead lines at WILLIS-SCHILD substation, causing red phase bridge to fail at HV isolators 11136 Stephen St North Schild Red phase HV conductor connection failed at Stephen corner Shild, causing HV conductor to fall to ground Upon arriving the attending LEI carried out a damage assessment at the point in which the fault had occurred. There were no apparent splash marks present on the LV conductors at the corner of Somerville Rd and Stephenson St where the HV conductors had dropped. TechSafe report is attached in the "Notes & Findings" section | Conductor (bare);Disconnector/isolator;Dropper/bridge | 0 | 0 | 0 |  | FE05 | Vegetation: Trees Incident | Loss of supply;Less than $50k damage;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/05/2019 21:09 |  |  | 13710 | Residential |  | 20190527JEM_01 | Infrastructure (network-based) | -37.8162 | 144.892 | 1 | Jemena | Report | 17288 | 0.032869 | 22kV AC | Essendon Airport | 3013 | Yarraville | Trees
worksite earth and short circuit applied | ADAMSON RISE, NARRAWONG VIC 3285 | 30142078 |  |  |  | Induction | Inappropriate tools/plant/equipment |  | 2 | Line-worker received slight electric shock from 66kV conductor whilst making bridge connection under outage conditions in 2015 | Conductor (bare) | 0 | 0 | 0 |  | KRT-PLD No 1 | induction from lines crossing other parts of outage area. | Minor shock | 42167.5833 |  |  | 13708 |  |  | 20190527PWA_01 | Infrastructure (network-based) | -38.2475 | 141.7365 | 1 | Powercor | Report | 17125 | 0.0090706 | 66kV AC | Portland (Cashmore Airport) | 3285 | Narrawong | Conductor
The crew's supervisor reported the unsafe situation (service and exposed accessible terminals of the FOLCB were live) to ESV emergency line (Ref: 11440320 â€“ Spoke to Megan). Simon Oâ€™Leary from ESV called Frank and advised ESV arenâ€™t attending and to just take photos of unsafe electrical situation, disconnect the supply and report through the reporting channels. Crew disconnected and abolished the service and electricity meter. | 5 CARR STREET, COBURG NORTH VIC 3058 |  | Unauthorised access | [5 empty] | 2 | Metering & Service crews attended the site for an abolishment of a supply and electricity meter. When the crew arrive they found the overhead service cable, POA, FOLCB and a section of the dwelling fascia relocated to the property boundary fence. | Aluminium twisted (XLPE) | 2 | 2 | 2 |  |  | Unknown persons relocate service. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/03/2019 11:38 |  |  | 13715 | Residential |  | 20190528JEM_01 | Infrastructure (network-based) | -37.7309 | 144.9701 | 1 | Jemena | Report | 17132 | 0.020042 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg North | Other
On arrival crew isolated supply and carried out repairs | 190 HALLYBURTONS ROAD, COBDEN VIC 3266 | 31009270 | Working too close to overhead lines | [5 empty] | 1 | A Powercor contactor attended HV outage at the incident location found that a HV line had been contacted by a third party vehicle, which in turn damaged the steel conductor. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG003 | Excavator contacted overhead conductors | No Go Zone (contact);Damage to network assets | 27/05/2019 10:47 |  |  | 13720 | Roadway |  | 20190528PWA_03 | Infrastructure (network-based) | -38.3174 | 143.0503 | 1 | Powercor | Report | 17137 | 0.027306 | 22kV AC | Warrnambool Airport Ndb | 3266 | Cobden | Vehicle
supply isolated. in communication with air Services Australia regarding future of this site | AIR NAVIGATION FACILITY, 489 BOGGY GATE ROAD, CLARKEFIELD VIC 3430 |  | Copper theft | [5 empty] | 2 | powercor metering detected a meter that was no longer communicating. On arrival the crew identified that the copper underground service cable to this site had been stolen. | Services cable | 0 | 0 | 0 |  |  | copper theft | Damage to network assets | 23/05/2019 16:16 |  |  | 13725 | Other | critical infrastructure- air services Australia locating beacon | 20190529PWA_01 | Infrastructure (network-based) | -37.4619 | 144.7984 | 1 | Powercor | Report | 17147 | 0.031182 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3430 | Clarkefield | Other
On arrival crew carried out repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298010 | Vandalism;Copper theft | [6 empty] | Lineworker, reported that while travelling along Bulmans Rd Melton West, he became aware that copper thieves had exposed underground cable which was still alive. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN022 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 18/04/2019 18:09 |  |  | 13727 | Roadway |  | 20190529PWA_03 | Infrastructure (network-based) | -37.6871 | 144.5494 | 1 | Powercor | Report | 17145 | 0.02925 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Powercor Powercor Fault crew made the site safe and made temporary arrangements to restore 3 phase LV supply to the Sri Durga Centre. Powercor underground crew followed to replace the 3 phase pole to pit cable. | 676-700 NEALE ROAD, DEANSIDE VIC 3336 | 30106105 | Vandalism;Copper theft | [6 empty] | Sri Durga Culture & Educational Centre reported part loss of supply. A Powercor Fault crew attended the site and noted attempted cable theft and other damage to Powercor LV assets . There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft & vandalism | Damage to network assets | 22/04/2019 7:51 |  |  | 13732 | Roadway |  | 20190529PWA_08 | Infrastructure (network-based) | -37.7405 | 144.6964 | 1 | Powercor | Report | 17151 | 0.03323 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Other
A CPO has removed the service fuse and issued a Level 1 defect on site. A Faults truck attended and disconnected the illegal overhead service connection to the builders temporary supply pole. | 30 CHIRNSIDE STREET, KINGSVILLE VIC 3012 |  | Unauthorised access | [5 empty] | 2 | Jemena Network Connections have raised a concern to Jemena Compliance regarding an overhad service and residential meter currently connected to a builders temporary supply (BTS) pole at the address. Photos are attached in the Notes and FIndings section. A CPO has attended to investigate and found another unauthorised and illegal overhead service connection and meter connected to a BTS pole that has been relocated from an old residential dwelling by non-authorised personal and no CES issued. Network Connections advise the overhead service and meter is registered to a residential dwelling at this address and there is no record of an abolishment or a new connection for a BTS. The CPO advises the seals on the meter plus the neutral link and meter panel have not been crimped with an approved sealing tool. The pole has been serviced with an old 16mm black twisted service cable and not 25mm. Meter number: 0348351 Defect number: J08207 Meter read: (03) 00129.5KW No details of REC or builder are available | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/10/2018 13:04 |  |  | 13751 | Residential |  | 20190531JEM_03 | Infrastructure (network-based) | -37.8058 | 144.8829 | 1 | Jemena | Report | 17198 | 0.0098206 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Kingsville | Other
Compliance were advised that the existing installation should be reported to ESV emergency on call due to the serious unsafe nature of the installation. I attended site to meet the crew at their request. Whilst turning into the site street, John Vasilopoulos was was in an adjacent street and I stopped to ask if he could attend with me which he did. The crew were able to safely disconnect the overhead service and make the installation safe. At the completion of the TA the REC and LEI had not yet completed their new installation and no prescribed CES had been issued so the crews were unable to complete the new connection. Customer: Andrew Sicari REC: David Wilkshire 27824 (Mob: 0403724797). Details are in the Other information sources section. A Grade: Andrew Griffiths A52776 | 65 TADSTAN DRIVE, TULLAMARINE VIC 3043 |  | Unauthorised access | [5 empty] | 2 | Crews attended the above address for a 9.30am Truck Appointment for a 1ph to 1ph mains upgrade. When they arrived they found the existing 1ph neutral screen overhead service supplying the property straight through the roof tiles and ceiling space and into the front room of a newly constructed house extension and the point of attachment and FOLCB supported on timber supports as per the attached photos in Notes and Findings section. The sevice fuse had been removed with the live pins of the FOLCB accessible and in arms reach and the existing 1ph meter and meter panel removed and laying on the ground. Electrical Works Request (EWR) also attached in Notes & Findings section. | Service conductor;Neutral screen;Connection box | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/10/2018 12:26 |  |  | 13753 | Residential |  | 20190531JEM_04 | Infrastructure (network-based) | -37.6952 | 144.8792 | 1 | Jemena | Report | 17173 | 0.03959 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Other
The customer was off supply and has been advised to contact Jemena Network Connection to arrange an After Hours appointment for a crew to return to complete the connection. No CES was issued and available on site and will need to be provided when the crew return. | 20 LAWSON STREET, SUNBURY VIC 3429 |  | Unauthorised access | [5 empty] | 2 | The metering & Service crew attended the site for a 1ph mains supply upgrade. When the crew arrived they found the REC had removed the service fuse from the FOLCB, cut away his consumers mains, removed the distributors electricity meter which was laying on the ground and was in the process of installing his new meter panel and new consumers mains wiring. The crew also found that the existing 1ph neutral screen overhead service supplying the property was connected to an old small SEC junction box on the distributors pole which also had the neutral screen service supplying the customer at number 22 connected. The RECâ€™s new POA and FOLCB location also did not comply and requires a raiser bracket to be installed to increase the service height. We confirmed the customer at number 22 is a non-life support customer and to make the installation safe at number 20 the crews were able to disconnect the small SEC junction box and disconnect the old neutral screen service to number 20. Photos are attached in the Notes and Findings section REC details are not available. | Service conductor;Neutral screen;Smart meter;Connection box | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/02/2019 10:43 |  |  | 13763 | Residential |  | 20190531JEM_13 | Infrastructure (network-based) | -37.5833 | 144.7144 | 1 | Jemena | Report | 17246 | 0.013613 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Supply was not connected Site made safe | 43 MAY STREET, PRESTON VIC 3072 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address today with a SO for a new 1ph UG supply and metering. When they attended they found the metering switchboard enclosure had 2 fully exposed opening holes at the top of the enclosure that allows direct access to live parts and full exposure to the ingress of water. The min safety IP rating was not maintained and the electrical installation was unsafe to connect to supply. EWR, CES and photos are attached in Notes and Findings section | Switchboard | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/02/2019 15:54 |  |  | 13768 | Residential |  | 20190531JEM_18 | Infrastructure (network-based) | -37.733 | 144.9961 | 1 | Jemena | Report | 17188 | 0.032514 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
On arrival crew isolated supply and carried out repairs | 5 MACADAM STREET W, DAYLESFORD VIC 3460 | 31001630 |  |  |  | Overheated connection |  |  |  | CFA reported reported a fire on a pole at the incident location. On arrival, the crew found that a connection in a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. There was no ground fire. There were no reported injuries or third party property damages. | Connection box | 2 | 2 | 2 |  | BAN011 | Overheated connection | Pole-top fire | 21/05/2019 19:01 | 1 | Negligible: no ground fire | 13741 | Roadway |  | 20190531PWA_02 | Infrastructure (network-based) | -37.3521 | 144.1423 | 1 | Powercor | Report | 17161 | 0.036697 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3460 | Daylesford | Connection
On arrival crew carried out repairs. | 49 SALTMARSH CRESCENT, POINT COOK VIC 3030 | 30338164 | Copper theft | [6 empty] | A passer by, Cameron (PH 0413767237) reported that some pits have been vandalized, the cables cut and IPCs hanging out - possible hazard. Cameron was unable to supply an exact location, but advised it's several pits and the street is not very long, near Hacketts rd. in Point cook. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WBE034 | Copper theft | Damage to network assets | 27/04/2019 12:38 |  |  | 13743 | Roadway |  | 20190531PWA_04 | Infrastructure (network-based) | -37.9063 | 144.7162 | 1 | Powercor | Report | 17163 | 0.030955 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew carried out repairs | 5750 GREAT OCEAN ROAD, PETTICOAT CREEK VIC 3233 | 32062627 |  |  |  | Leakage |  |  |  | Report from customer of pole fire . Possibly lighning strike but not confirmed. 22kv crossarm burnt of at one end. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CLC001 | Excessive leakage current | Pole-top fire | 23/01/2019 9:03 | 1 | Negligible: no ground fire | 13748 | Roadway |  | 20190531PWA_07 | Infrastructure (network-based) | -38.716 | 143.7297 | 1 | Powercor | Report | 17168 | 0.018086 | 22kV AC | Avalon Airport | 3233 | Petticoat Creek | Crossarm
On arrival crew isolated supply and carried out repairs. | STATION ROAD, GISBORNE VIC 3437 | 30338649 | Vandalism;Copper theft | [6 empty] | Report from employee of pits opened on side of Calder Fwy on-ramp. On arrival crew found pit lids removed and copper cut. Approximately 135m of 16mm copper had been removed between pole LIS 845137 and LIS 8451414. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | GSB013 | copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43501.7188 |  |  | 13776 | Roadway |  | 20190603PWA_05 | Infrastructure (network-based) | -37.4727 | 144.5941 | 1 | Powercor | Report | 17199 | 0.0071597 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
On arrival crew isolated supply and carried out repairs. | TARNEIT SKIES, UNIT 121 250 THAMES BOULEVARD, TARNEIT VIC 3029 | 30243805 | Vandalism;Copper theft | [6 empty] | Report recieved of open pit with exposed cables, looks like have been cut and stolen. Pit located on the base of pole LIS 725434 . Reported by Kane B 0407 829 581 On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through and stolen the 4c 16mm LV Service Cable within the LV Service Pit at the base of PL Lighting Pole LIS-725434-7728 ( LV supply pit was found to be ALIVE) - There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WBE012 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43804.3333 |  |  | 13783 | Roadway |  | 20190603PWA_12 | Infrastructure (network-based) | -37.8603 | 144.66 | 1 | Powercor | Report | 17206 | 0.0054086 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Powercor linesman repaired the service at FMJB | 5 BLACKWOOD DRIVE, MELTON SOUTH VIC 3338 | 32175423 |  |  |  | Corrosion |  |  | 2 | Person received an electric shock when he simultaneously contacted the water tap with his hand and standing on a grassed area bare foot. | Aluminium twisted (grey) | 0 | 0 | 0 |  | MLN011 | Corroded service neutral at FMJB | Minor shock | 16/04/2019 13:00 |  |  | 13785 | Residential |  | 20190603PWA_14 | Infrastructure (customer connection) | -37.693 | 144.5758 | 1 | Powercor | Report | 17208 | 0.024409 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | OH Cable
The crew made the site safe and a fault-follow up has been raised to replace the stolen low voltage cable. | 102-120 MODAL PLACE, ALTONA VIC 3018 | 30553974 | Vandalism;Copper theft | [6 empty] | PS MARINE PTY LTD, Ailsha 0447608710 advises no power to premises. Crew attended to find that some one had stolen cabling between pole LIS 877004 and LIS 989311 note pits at base of each pole. At pole LIS 877004 live low voltage cable hanging form pole creating a public safety issue. About 250 meters of low voltage cable was stolen. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | LVN022 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/05/2019 15:30 |  |  | 13786 | Roadway |  | 20190604PWA_01 | Infrastructure (network-based) | -37.8552 | 144.796 | 1 | Powercor | Report | 17209 | 0.034903 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
On arrival crew isolated supply and arranged repairs. | MATHERS ROAD, YALCA VIC 3637 | 33084505 | Crane, excavator or other construction/farming equipment | [6 empty] | Report of Tractor making contact with pole. Crew found pole had been damaged requiring replacement, no injuries, no property damage, no vehicle damage, no ground fire. | Pole (concrete) | 2 | 2 | 2 |  | NKA006 | Tractor carrying out agricultural works struck pole. | Damage to network assets | 13/05/2019 17:24 |  |  | 13788 | Agricultural |  | 20190604PWA_02 | Infrastructure (network-based) | -35.9587 | 145.2732 | 1 | Powercor | Report | 17211 | 0.017417 | 22kV AC | Shepparton Airport | 3637 | Yalca | Vehicle
Supply currently not connected to building. No PTw's on issue | 323 VICTORIA ROAD, THORNBURY VIC 3071 | 30197194 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | CitiPower had provided an offer to relocate overhead power lines to allow construction of a new building. Upon review it was found that this offer had lapsed and construction of the building was well advanced. The building does not meet statutory clearances. | Conductor (bare) | 0 | 0 | 0 |  | FF084 | Building in vicinity of overhead lines | No Go Zone (no contact) | 20/05/2019 10:00 |  |  | 13799 | Construction |  | 20190605PWA_04 | Infrastructure (network-based) | -37.7593 | 145.0131 | 1 | CitiPower | Report | 17222 | 0.04086 | Low voltage AC (<1kV);6.6kV AC | Essendon Airport | 3071 | Thornbury | Other
Supply isolated and repairs undertaken. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298008 | Vandalism;Copper theft | [6 empty] | Emergency Services report at the intersection of High St and Bulmans Road, near the bridge, pit lid removed and cables exposed, possible copper theft. Crew found 300m of public lighting underground cable missing from LIS 784377 and LIS 784382, thieves had been on site for some time stripping the insulation. Copper theft at this site is a regular occurrence. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN022 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 20/05/2019 13:42 |  |  | 13803 | Roadway |  | 20190605PWA_06 | Infrastructure (network-based) | -37.688 | 144.5492 | 1 | Powercor | Report | 17226 | 0.026066 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and carried out repairs. | 87 SCHREENANS ROAD, BONSHAW VIC 3352 | 33003184 |  | Bird | [5 empty] | The Customer reported the pole in front of his property at the incident location was smoking at the base and smelled as though something was burning underground, but he had no supply issues and was unsure of the cause. The crew said that when they first arrived and isolated the HV fuse, they removed a birds nest from the LV bushings of the transformer not believing it to be the cause, however when they later checked the nest, they found a piece of fencing wire embedded in the nest. The crew believe that the fencing wire may have shorted a live transformer bushing to the concrete pole, thereby livening the pole to 240V and causing steam to rise around the pole. There were no other potential causes found, and all undergrounds and earths were tested and returned to supply. There was no fire and no reported injuries. | Pole mounted;Pole (concrete) | 2 | 2 | 2 |  | BAS021 | Bird Incident | Melting or smoking only | 28/05/2019 11:24 |  |  | 13818 | Roadway |  | 20190606PWA_05 | Infrastructure (network-based) | -37.6042 | 143.8106 | 1 | Powercor | Report | 17247 | 0.035488 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Bonshaw | Animal
Powercor Fault crews are to attend and install cover guards over the service as an interim measure until a solution is found. Work is to cease on the scaffold until a solution is found. | 956 BURKE ROAD, DEEPDENE VIC 3103 | 30167815 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | A customer reported that the overhead service to the neighboring property was about 10cm from making contact with some scaffolding. When the crew attended they found that the service was also being propped up with a piece of timber. The company undertaking the construction was reported as Chrystal Homes Pty Ltd. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  | L022 | building too close and interference | No Go Zone (no contact);No Go Zone (contact) | 30/05/2019 12:23 |  |  | 13820 | Construction |  | 20190606PWA_06 | Infrastructure (network-based) | -37.8096 | 145.0609 | 1 | CitiPower | Report | 17250 | 0.030515 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Deepdene | Other
On arrival crew isolated supply and arranged repairs. | 276 FERRIS ROAD, STRATHTULLOH VIC 3338 | 30305881 | Vandalism;Copper theft | [6 empty] | Report received of copper theft from P/L pole to pit at LIS-811757 in Ferris Rd Melton South, with live cables on the ground. Upon arrival the crew found the thieves had pulled out, cut and left around 4m of the 16mm 4/c service at the service pit adjacent to LIS-811757. The thieves also stole 50m of P/L cable between LIS-811757 and LIS-811758. No shock, injury or third party property damage to report. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/05/2019 1:26 |  |  | 13828 | Roadway |  | 20190607PWA_02 | Infrastructure (network-based) | -37.7171 | 144.5998 | 1 | Powercor | Report | 17260 | 0.025358 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Strathtulloh | Other
On arrival crew isolated supply and carried out repairs. | 22 COOPER AVENUE, ALTONA NORTH VIC 3025 | 32164659 |  |  |  | Corrosion |  |  | 1 | MFB reported a transformer was on fire. Upon arrival the fault crew found a melted red phase LV bushing a 300kVA pole sub. The fire self extinguished according to the MFB. The fire was contained to the area immediately surrounding the LV bushing and transformer tank on the pole itself. There was no ground fire to report. No reports of shock, injury or third party damage. | Pole mounted;Connector/termination | 2 | 2 | 2 |  | AL002 | Moisture ingress at connection | Pole-top fire | 43530.7785 | 1 | Negligible: no ground fire | 13831 | Roadway |  | 20190607PWA_04 | Infrastructure (network-based) | -37.84 | 144.8439 | 1 | Powercor | Report | 17263 | 0.010538 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Connection
Isolated and made safe. Replaced damaged Jemena assets (transformer) | 145 GREEN STREET, BULLA VIC 3428 |  | Theft | [5 empty] | 2 | Alleged attempted copper theft of customer LV underground service cable caused damage to Jemena Transformer Wildwood Rd P15E5, when service cable was forcibly pulled out of ground. Some earthing taken off Jemena pole as well. | Services cable;Pole mounted;Earth/earthing | 2 | 2 | 2 |  | COO11 | Attempted copper theft | Loss of supply;Damage to network assets | 43744.2382 |  |  | 13838 | Residential |  | 20190610JEM_01 | Infrastructure (network-based) | -37.6267 | 144.8112 | 1 | Jemena | Report | 17270 | 0.0073009 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
On arrival crew carried out repairs | 930 MT DUNEED ROAD, FRESHWATER CREEK VIC 3217 | 32079902 | Working too close to underground cables | [6 empty] | An REC called to report that a customer had dug up the transformer earth with trenching equipment. On arrival the crew found the Low Voltage earth on the substation had been cut with a trenching machine. There was no fire, no supply issues, and no shocks were received. | Earth/earthing | 2 | 2 | 2 |  | WPD014 | Trencher struck earthing cable | No Go Zone (contact);Damage to network assets | 43591.3826 |  |  | 13840 | Roadway |  | 20190611PWA_02 | Infrastructure (network-based) | -38.2344 | 144.2292 | 1 | Powercor | Report | 17273 | 0.029196 | Earthing cable | Avalon Airport | 3217 | Freshwater Creek | Dug up
Fault crew and LEI dispatched to investigate Voltage tests between an independent earth and various points of the electrical installation, including distribution assets. Fault crew isolated and replaced the service cable. Following repair, NST and all VESI tests carried out and passed. | 53 RANKIN ROAD, BORONIA VIC 3155 | LIS1219151 |  |  |  | Corrosion;Mechanical breakdown |  | Phase to earth |  | E0021107 - customer reported receiving electric shock from kitchen sink | Service conductor | 0 | 0 | 0 |  | BRA14 | Vegetation: Trees Incident | Minor shock | 43744.2188 |  |  | 13842 | Residential |  | 20190611SPN_02 | Infrastructure (network-based) | -37.867 | 145.2722 | 2 | AusNet Services Distribution | Report | 17275 | 0.033228 | Low voltage AC (<1kV) | Moorabbin Airport | 3155 | Boronia | Trees
The Powercor crew made the site safe, disconnected supply to the 3 service pits and left a defect notice in the meter box at the 4 affected properties. | 25 LANCASHIRE DRIVE, WERRIBEE VIC 3030 | 60380415 | Copper theft | [6 empty] | A Powercor employee reported to control room that 3 service pits have been interfered with and the consumer mains cables have been damaged at a new residential development on Lancashire drive, Werribee. | Services cable;Services pit | 2 | 2 | 2 |  | WBE031 | Attempted copper theft | Damage to network assets | 43622.709 |  |  | 13851 | Roadway |  | 20190612PWA_01 | Infrastructure (network-based) | -37.9126 | 144.6071 | 1 | Powercor | Report | 17285 | 0.0039178 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
On arrival crew isolated supply and carried out repairs. | 662 OLD CALDER HIGHWAY, KEILOR VIC 3036 | 33073634 |  |  |  | Unknown technical factor |  |  |  | MFB and a customer reported conductors and a transformer on fire. Pole located outside a row of townhouses near intersection of Flora street and Calder Highway. They advised it was a small fire and still currently on supply. CFA have been called. On arrival the Powercor crew found that the connections in a krone box had overheated and the box melted. The small fire extinguished by itself. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | SA002 | Insufficient remains to determine a cause | Pole-top fire | 43683.7382 | 1 | Negligible: no ground fire | 13852 | Roadway |  | 20190612PWA_02 | Infrastructure (network-based) | -37.7207 | 144.8383 | 1 | Powercor | Report | 17286 | 0.021606 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Connection
Service replaced | 2 DOOLAN STREET, WERRIBEE VIC 3030 | 30103252 |  |  |  | Corrosion |  |  | 2 | Person received an electric shock when he simultaneously contacted the metallic tap with his hand and the metallic waste shower base with his foot. | Neutral screen | 0 | 0 | 0 |  | WBE024 | Corroded service neutral at Fused mains junction box | Minor shock | 17/04/2019 14:00 |  |  | 13854 | Residential |  | 20190612PWA_04 | Infrastructure (customer connection) | -37.9116 | 144.6548 | 1 | Powercor | Report | 17289 | 0.015987 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | OH Cable
On arrival crew made arrangement for repairs | 13 BOGONG LOOP, TARNEIT VIC 3029 | 30547816 | Copper theft | [6 empty] | ul, a carpenter working near the location of the incident, reported to Powercor control room that vandals have cut cables from back of the meter at #13 BOGONG LOOP,TARNEIT, and looks like other houses in street have been affected as well. On arrival The Powercor crew found that on 4 properties, the consumer mains have been cut and stolen. Cables were cut at the meter boxes and inside the pits. The crew advised that the 4 houses are vacant, located at a new residential development. The properties affected are: LOT-1510, - BOGONG LOOP,TARNEIT LOT-1511, - BOGONG LOOP,TARNEIT LOT-1512, - BOGONG LOOP,TARNEIT LOT-1519, - BOGONG LOOP,TARNEIT There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WBE032 | copper theft | Damage to network assets | 43744.3688 |  |  | 13861 | Roadway |  | 20190612PWA_10 | Infrastructure (network-based) | -37.8431 | 144.6459 | 1 | Powercor | Report | 17297 | 0.035139 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
fault crew replaced service termination clamp | 25 BAYVIEW STREET, PRAHRAN VIC 3181 | 30169731 |  |  |  | Electrical breakdown |  |  | 2 | Person (roof plumber) received an electric shock when he simultaneously contacted the steel roof with his hand and the aluminium ladder with the other hand A voltage test between the ladder and the conductive steel roof resulted with 50 Volts. Tests to the various other parts of the installation found no faults. | Service conductor;Aluminium twisted (XLPE) | 0 | 0 | 0 |  | BC013 | service clamp at point of attachment created hole in service insulation and tracking to bracket | Minor shock | 43743.6667 |  |  | 13863 | Residential |  | 20190612PWA_12 | Infrastructure (network-based) | -37.852 | 145.0038 | 1 | CitiPower | Report | 17299 | 0.021655 | Low voltage AC (<1kV) | Moorabbin Airport | 3181 | Prahran | AF Other
Crew made site safe and replaced service. | 20 CHURCH STREET, KEILOR VIC 3036 | 31023832 |  | Within clearances | [5 empty] | Tree fire due to tree rubbing on service line. Incident found in during outage data review. 1 sqm ground fire | Service conductor | 2 | 2 | 2 |  | SA002 | Vegetation: Trees Incident | Grassfire | 43355.0493 | 1 | Localised: less than 10 sq.m | 13875 | Roadway |  | 20190613PWA_05 | Infrastructure (network-based) | -37.7219 | 144.8344 | 1 | Powercor | Report | 17313 | 0.031253 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Trees
Fault Crew replaced the corroded Pole Box on the SWER Pole | 53 SIDDLES ROAD, REDESDALE VIC 3444 | 30031525 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom standing in the Shower when she received an electric shock as she made simultaneous contact with one hand on the metal Tap and her bare feet while standing on the conductive shower base. | Connector/termination | 0 | 0 | 0 |  | BET005 | Corroded U/G Neutral Conductor termination at the Pole Box located on the SWER Pole | Minor shock | 28/05/2019 19:00 |  |  | 13881 | Agricultural |  | 20190613PWA_10 | Infrastructure (network-based) | -37.0559 | 144.5174 | 1 | Powercor | Report | 17320 | 0.037641 | Low voltage AC (<1kV) | Bendigo Airport | 3444 | Redesdale | Connection
Crew made site safe and performed repairs. | BRINSMEADE, 111A QUICKS ROAD, BRIM VIC 3391 | 32090705 |  |  |  | Candled fuse |  |  |  | Candled HV EDO Fuse (Fire) Fire incident was found during outage data review. No ground fire | EDO fuse | 2 | 2 | 2 |  | HSM003 | Excessive leakage current | Pole-top fire | 17/12/2018 0:34 | 1 | Negligible: no ground fire | 13885 | Agricultural |  | 20190613PWA_13 | Infrastructure (network-based) | -36.0715 | 142.341 | 1 | Powercor | Report | 17324 | 0.0076412 | 12.7kV AC (SWER) | Horsham Aerodrome | 3391 | Brim | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. A LEI was dispatched to the site and undertook investigation to determine any damage to customers appliances and equipment. Faults crew also assisted the LEI to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed. | 383 BAYVIEW ROAD, ROSEBUD VIC 3939 | 1310931 | Vehicle | [5 empty] | 1 | At 0906hrs on 1/06/2019, a 22kV CB opened to lockout. Subsequently UE received a report of a pole down near the corner of Bayview and Jetty Rd Rosebud due to a multiple vehicle accident. As a consequence of the pole being hit, HV conductors contacted the LV conductors below and resulted in HV injection into the neighbouring properties. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | RBD12 | Two vehicles were involved in a collision that resulted in the UE pole being hit and falling. | HV injection;Loss of supply;Damage to network assets | 43471.3792 |  |  | 13884 | Roadway |  | 20190613UTD_01 | Infrastructure (network-based) | -38.3737 | 144.909 | 1 | United Energy Distribution | Report | 17323 | 0.0066725 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3939 | Rosebud | Vehicle
UE dispatched a fault crew in conjunction with an EIO to investigate. The EIO tested the Active Service Link Cable between the Ceramic Fuse Mains Box and the Consumer Mains Junction Box and detected 220 volts between the Cotton Wrap Insulation and an Independent Earth. The faults crew replaced the Link Cable, and performed NST at the meter which passed. Supply to the property was left on. | 4 MOONAH COURT, DOVETON VIC 3177 |  | Unauthorised work |  |  |  |  | Phase to earth | 2 | UE received report of a person receiving a shock when installing bird deterrent spikes on the house POS while standing on an aluminium ladder. | Connection box;No failed asset;Customer installation | 2 | 2 | 2 |  |  | The cause was the worker was working from an aluminium ladder around live wires without appropriate personal protective clothing. | Minor shock | 43622.5153 |  |  | 13890 | Residential |  | 20190613UTD_04 | Infrastructure (network-based) | -37.9905 | 145.2462 | 1 | United Energy Distribution | Report | 17329 | 0.027774 | Low voltage AC (<1kV) | Moorabbin Airport | 3177 | Doveton | Other
UE dispatched a fault crew. On attendance, the crew found a 3 phase FOLCB at the pole end had burnt out and caused burning to the LV cross-arm. The box was replaced and supply restored. NST was performed with confirmed pass result. | 30 COORAMINTA ROAD, RYE VIC 3941 | 1305535 |  |  |  | Overheated connection |  |  | 2 | UE received a report from the fire authority of a pole sparking. | Crossarm (wood);Connection box | 0 | 0 | 0 |  |  | The cause was overheated connection in the connection box, likely due to a loose connection. | Plant/equipment | 43652.3333 | 1 | Negligible: no ground fire | 13897 | Roadway |  | 20190617UTD_01 | Infrastructure (network-based) | -38.395 | 144.8034 | 1 | United Energy Distribution | Report | 17341 | 0.0024977 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Connection
The NGZ assessor did not issue a permit. The assessor made it safe by installing two tiger covers. | 13 ROCKBEARE GROVE, IVANHOE VIC 3079 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Jemena No Go Zone assessor found scaffolding has been built around the service line without a shutdown or a No Go Zone permit to work. Details of the person who requested a No Go Zone assessment are entered into the "Other information sources" section Photos and a copy of the No Go Zone inspection report are included in the "Notes & Findings" section | Conductor (insulated) | 2 | 2 | 2 |  |  | Person erected scaffolding too close to overhead lines | No Go Zone (no contact) | 18/06/2019 13:35 |  |  | 13905 | Construction |  | 20190618JEM_01 | Infrastructure (customer connection) | -37.7725 | 145.0384 | 1 | Jemena | Report | 17531 | 0.0029988 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Other
Powercor Fault Crew replaced the existing O/H Twisted Service Cable | 236 ECHUCA ROAD, MOOROOPNA VIC 3629 | 32189987 |  |  |  | Corrosion;Overheated connection |  |  | 2 | Customer was in the Bathroom Showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet whilst standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | SHTS-MNA | Corroded and loose O/H Service Neutral Conductor termination at the Split Bolt Clamp located at the Reticulation Pole. | Minor shock | 43678.8333 |  |  | 11992 | Residential |  | 20190123PWA_07 | Infrastructure (network-based) | -36.3734 | 145.3468 | 1 | Powercor | Report | 15003 | 0.030087 | Low voltage AC (<1kV) | Shepparton Airport | 3629 | Mooroopna | Connection
On arrival crew isolated supply and carried out repairs. The customer was issued a defect to repair stolen customer mains cables. | 32 LONG FOREST ROAD, LONG FOREST VIC 3340 | 33076588 | Vandalism;Copper theft | [6 empty] | An optus worker reported vandalism to pit and pillar at corner of Long forest road and Bacchus marsh rd. Wires are exposed, no shock. No supply to optus/telstra assets. On arrival crew observed that LV earths had been cut form the substation. There was no fire, no reported injuries. | Earth/earthing | 2 | 2 | 2 |  | BMH006 | Copper theft and vandalism | Damage to network assets | 43800.5639 |  |  | 11999 | Roadway |  | 20190124PWA_04 | Infrastructure (network-based) | -37.6795 | 144.5043 | 1 | Powercor | Report | 15010 | 0.036822 | Earthing cable | Laverton Raaf | 3340 | Long Forest | Other
Fault Crew replaced the corroded O/H Neutral Bridge Conductor at the Reticulation Pole | 76 BENT STREET, MACEDON VIC 3440 | 32050690 |  |  |  | Corrosion |  |  |  | Customer was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metallic Shower Tap and his bare feet whilst standing on the wet shower base. | Conductor (bare) | 0 | 0 | 0 |  | GSB014 | Connection failure- Corroded O/H Neutral Bridge Connection at the Reticulation Pole | Minor shock | 43800.375 |  |  | 12000 | Residential |  | 20190124PWA_05 | Infrastructure (customer connection) | -37.4175 | 144.5706 | 1 | Powercor | Report | 15011 | 0.028353 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Connection
Emergency high voltage switching was completed with the HV spur switched out and the tree branch was safely removed. Supply was restored following the short outage. | 8 LUXTON DRIVE, SOMERS VIC 3927 | 1107139 |  | Blown branch/vegetation |  |  |  |  | 2 | An Asset Inspector contacted the United Energy Resource Co-coordinators and advised that a broken gum tree branch is resting on the HV overhead conductors at "Luxton 1-Sandy Point" substation with flames witnessed. | Conductor (bare) | 0 | 0 | 0 |  | HGS 23 | Vegetation: Trees Incident | Other vegetation | 24/01/2019 8:30 | 1 | Negligible: no ground fire | 11995 | Roadway |  | 20190124UTD_01 | Infrastructure (network-based) | -38.3777 | 145.1403 | 1 | United Energy Distribution | Report | 18393 | 0.029356 | 22kV AC | Moorabbin Airport | 3927 | Somers | Trees
Section of cable was isolated and made safe | 12 PUCKLE STREET, MOONEE PONDS VIC 3039 |  | Working too close to underground cables | [5 empty] | 2 | GND Civil were installing conduits utilising a boring equipment. GDN had the required DBYG plans and setup boring machine, however during the activity the drill head struck rock and inadvertently changed the direction of the drill head causing it to veer off course as a result the drill head struck the low voltage cable. The pot holing that GND Civil group undertook, identified the cables to be installed at the correct depth of 800mm and they believed an appropriate drill depth of 1600mm needed to be set in order to avoid the known assets. (tbl# 175383) | Cable | 0 | 0 | 0 |  |  | GND Civils - drill head struck rock and inadvertently changed the direction of the drill head causing it to veer off course as a result the drill head struck the low voltage cable. | No Go Zone (contact) | 25/01/2019 11:49 |  |  | 12015 | Commercial |  | 20190125JEM_01 | Infrastructure (network-based) | -37.7669 | 144.9242 | 1 | Jemena | Report | 15030 | 0.014196 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Dug up
Crews attended the site to make safe and repair conductors. Council tree has now been cut. | 34 ANDREWS AVENUE, RESERVOIR VIC 3073 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Live low voltage conductors (white and blue phase) were brought down to the ground due to large tree branch breaking off. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Loss of supply;Less than $50k damage | 25/01/2019 9:06 |  |  | 12017 |  |  | 20190125JEM_02 | Infrastructure (network-based) | -37.7299 | 145.0333 | 1 | Jemena | Report | 15033 | 0.04017 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Trees
Crews pulled fuses in pit to be made safe. | 1905 MICKLEHAM ROAD, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stolen copper service cable and pit connectors. | Services cable | 0 | 0 | 0 |  |  | Unknown person(s) stole copper service cable and pit connectors. | Damage to network assets | 25/01/2019 14:05 |  |  | 12020 | Roadway |  | 20190125JEM_03 | Infrastructure (network-based) | -37.5616 | 144.8763 | 1 | Jemena | Report | 15038 | 0.0099167 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
Fault crew dispatched to investigate and make safe. Crew opened Transformer fuses and replaced damaged fuse. | 40 MORTIMER ROAD, TYNONG NORTH VIC 3813 | LIS 524311 |  |  |  | Candled fuse |  |  | 0 | E0008495 - Crew arrived on site to find a burnt and smoking EDO fuse which had not blown. | EDO fuse | 0 | 0 | 0 |  | PHM33 | crew arrived on site to find a candled EDO fuse. Fuse was replaced and supply restored | Pole-top fire | 16/01/2019 22:05 | 1 | Negligible: no ground fire | 12005 |  |  | 20190125SPN_01 | Infrastructure (network-based) | -38.0269 | 145.6044 | 1 | AusNet Services Distribution | Report | 15018 | 0.031065 | 22kV AC | Moorabbin Airport | 3813 | Tynong North | Fuse
Fault crew dispatched. Failed LV IPC replaced and supply restored. | 30 FARADAY ROAD, CROYDON SOUTH VIC 3136 | LIS1209220 |  |  |  | Defective component |  |  |  | E0008624 - Report of sparks from pole. | Connector/termination | 0 | 0 | 0 |  | CYN11 | LV IPC connector on red phase of LV ABC street circuit found to have failed and burnt. No evidence of ground fire. Cause of failure unknown but appears to be defective component. | Melting or smoking only | 24/01/2019 21:00 |  |  | 12007 | Roadway |  | 20190125SPN_02 | Infrastructure (network-based) | -37.8162 | 145.2751 | 1 | AusNet Services Distribution | Report | 15024 | 0.019416 | Low voltage AC (<1kV) | Moorabbin Airport | 3136 | Croydon South | Connection
LEI and Fault crew dispatched to investigate and carry out repairs. All repairs and tests completed/passed and supply restored. | 52A DIXON COURT, BORONIA VIC 3155 | LIS 1211848 |  | Bird |  | HV injection |  | Phase to earth | 1 | E0008666 - reported HV Injection as a result of brid coming into O/H conductors on pole. | Service conductor | 0 | 0 | 0 |  | BRA14 | Bird Incident | HV injection | 24/01/2019 8:44 |  |  | 12014 | Residential |  | 20190125SPN_04 | Infrastructure (network-based) | -37.8626 | 145.263 | 2 | AusNet Services Distribution | Report | 15315 | 0.022613 | 22kV AC | Moorabbin Airport | 3155 | Boronia | Animal
A faults crew attended and identified a probable loose connection contributed to a pole mounted three phase FMJB at pole No. LIS 3308696 to catch on fire outside 72 Dandenong Road W Frankston. The FMJB supplied a small group of shops. | 78 DANDENONG ROAD W, FRANKSTON VIC 3199 | 3308696 |  | Heat |  | Overheated connection |  |  | 2 | The CFA called to advise that a pole is on fire outside 72 Dandenong Road, Frankston and there is arcing and sparking. | Connection box | 0 | 0 | 0 |  | FTN14 | A probable loose connection overheated causing a FMJB to catch on fire at the pole end. | Pole-top fire | 24/01/2019 11:11 | 1 | Negligible: no ground fire | 12006 | Roadway |  | 20190125UTD_01 | Infrastructure (network-based) | -38.1356 | 145.1291 | 1 | United Energy Distribution | Report | 18401 | 0.041094 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Emergency services put out the grass fire. Jemena crews isolated the site and made safe for termination repairs. | 60 EMU ROAD, MAIDSTONE VIC 3012 | A151624 |  | Wind |  | Moisture ingress;Age |  |  | 1 | High voltage cable termination on cable head pole no. A151624 failed and caused molten insulation to be blown away to an area which was overgrown and very dry, which resulted in a grass fire less than 10 square metres. A photograph is attached in the "Notes & Findings" section | Connector/termination | 0 | 0 | 0 |  | BY14 | The high voltage cable termination had melted and burnt out. The cause of termination burnt out was due to ingress of moisture resulting in the deterioration of the paper insulation. With time, paper can become brittle and absorb moisture which reduces its dielectric strength giving way to partial discharges. Degradation of paper also occurs from heating of the copper conductor, especially during times of peak demand as more current is pushed through the conductors. These partial discharges break down and weaken the paper insulation ultimately resulting in flash over. Given the windy conditions, coupled with overgrown and very dry conditions in the area, the molten insulation had blown away off the termination and started a grass fire. | Grassfire | 25/01/2019 17:03 | 1 | Localised: less than 10 sq.m | 12021 | Industrial |  | 20190126JEM_01 | Infrastructure (customer connection) | -37.7795 | 144.8785 | 1 | Jemena | Report | 17752 | 0.0009456 | 22kV AC | Essendon Airport | 3012 | Maidstone | Connection
On arrival crew isolated supply and carried out repairs. | DOHERTYS ROAD, TARNEIT VIC 3029 | 32178565 | Vandalism;Copper theft | [6 empty] | A Powercor employee reported that UG cables had been stolen that feed the street lights at the incident location. On arrival the crew found that the load side of the cables had been cut, but the thieves may have been disturbed and the cables had not been stolen. No theft, no fire and no injuries reported. | Services cable | 2 | 2 | 2 |  | TNA023 | attempted copper theft and vandalism | Damage to network assets | 17/01/2019 10:24 |  |  | 12043 |  |  | 20190130PWA_03 | Infrastructure (network-based) | -37.8196 | 144.693 | 1 | Powercor | Report | 15071 | 0.0088252 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs. | 310 ASHBOURNE ROAD, WOODEND VIC 3442 | 31006676 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [6 empty] | An excavator being used to install pipes at this location has contacted and damaged an overhead three core service, which is now at head height. Low voltage fuse blew isolating damaged equipment from the network. No injuries and no fire associated with this incident. | Service conductor | 2 | 2 | 2 |  | WND021 | Excavator installing pipes struck service | Loss of supply;Damage to network assets | 18/01/2019 9:50 |  |  | 12045 | Agricultural |  | 20190130PWA_04 | Infrastructure (network-based) | -37.3775 | 144.5031 | 1 | Powercor | Report | 15073 | 0.034657 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Vehicle
Dispatched fault crew to investigate and make safe. 20m of damaged conductor replaced, O/H SWER re-strung and supply restored | 20 GRANITE LANE, TYNONG VIC 3813 | 510558 | Crane, excavator or other construction/farming equipment |  |  | Fatigue |  |  |  | E0008751 - Report of O/H SWER conductors on the ground following possible contact by excavator. No evidence of fire | Conductor (bare) | 0 | 0 | 0 |  | PHM33 | 3/2.75 steel SWER conductor has failed at a or near to a PG clamp possibly as a result of contact by an excavator (unable to confirm). Conductor appears to have suffered cable fatigue as this is a long 420m span. Damaged section of conductor (approx. 20m) was repaired/replaced, conductor restrung and supply restored. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/01/2019 11:52 |  |  | 12036 | Agricultural |  | 20190130SPN_01 | Infrastructure (network-based) | -38.0724 | 145.629 | 2 | AusNet Services Distribution | Report | 15061 | 0.010731 | 12.7kV AC (SWER) | Moorabbin Airport | 3813 | Tynong | Vehicle
Dispatched crew to investigate and make safe. Damaged ACR replaced, no other damage to assets | 214 CAMBRIDGE ROAD, KILSYTH VIC 3137 | LIS1001084 |  | Animal |  |  |  | Phase to earth |  | E0008754 - MFB reported fire outside 214 Cambridge rd, Kilsyth. Crew found Possum had got on top of ACR LD070. scorched earth at base of ACR. | ACR/OCR | 0 | 0 | 0 |  | CYN33 | Animal Incident | Grassfire | 26/01/2019 22:35 | 1 | Localised: less than 10 sq.m | 12038 | Residential |  | 20190130SPN_02 | Infrastructure (network-based) | -37.8006 | 145.3293 | 1 | AusNet Services Distribution | Report | 15367 | 0.022885 | 22kV AC | Moorabbin Airport | 3137 | Kilsyth | Animal
Emergency high voltage switching was completed to minimise the number of customers affected. The LV conductors were isolated to prevent backfeed during the HV switching and there was a short delay in isolating the HV conductors as a load transfer was required to an AusNet Services feeder. The red and blue phase LV fuses operated at "Donelly-Moore" substation along with the west circuit red phase LV fuse at "Frawley-Charles" substation. The rectification work was completed under Access Authority conditions and when this was completed with supply restored, the LEI inspected properties supplied from ""Frawley-Charles" substation following the LV fuse replacements and confirmed that a HVI did not occur. | 41 FRAWLEY ROAD, HALLAM VIC 3803 | 616529 | Vehicle |  |  | Conductor clashing |  |  | 1 | At 3.39AM on 27/01/2019, 22kV feeder DN22 circuit breaker reclosed to lockout. Emergency services advised there is a wire down over the roadway and a grass fire nearby. A truck struck and broke a HV/LV timber pole (LIS No. 0616529) located near 41 Frawley Road that caused HV and LV conductors to clash and fall to the ground. A high voltage injection was suspected and a LEI was called to investigate. Subsequent damage occurred due to probable fault current that caused connections to fail at multiple locations and conductors to fall to the ground. Molten metal fell into the dry grass below and caused 3 small fires that were estimated to be 2-3sqm in size at the following locations outside: 1. 41 Frawley Road 2. 66 Frawley Road 3. corner of Frawley Road and Charles Street. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | DN22 | A truck struck and broke a HV/LV timber pole that caused conductors to clash and fall to the ground. | Grassfire | 27/01/2019 3:39 | 1 | Localised: less than 10 sq.m | 12035 | Roadway |  | 20190130UTD_01 | Infrastructure (network-based) | -37.9984 | 145.256 | 1 | United Energy Distribution | Report | 15058 | 0.002272 | 22kV AC | Moorabbin Airport | 3803 | Hallam | Vehicle
On arrival crew isolated supply and carried out repairs. | 51 STRATHALBYN STREET, KEW EAST VIC 3102 | 30178527 |  |  |  | Corrosion |  |  |  | MFB reported arching, sparking and wires on the ground. On arrival, the crew found an Low Voltage (LV) overhead conductor had broken fallen onto the ground due to a Insulation Piercing Connector (IPC) overheating. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | Q014 | overheated IPC connector | Loss of supply;Damage to network assets | 22/01/2019 18:15 |  |  | 12072 | Roadway |  | 20190201PWA_06 | Infrastructure (network-based) | -37.7959 | 145.0514 | 1 | CitiPower | Report | 15108 | 0.015931 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | Connection
Emergency high voltage switching was completed by opening RWT 24 circuit breaker and the HV spur fusing at BH2047 located in Creek Road. In addition, the LV overhead conductors were isolated at "Brunswick-Creek" pole type substation. The burnt branch was promptly removed under Access Authority conditions and the feeder restored. The blue phase HV powder filled fuse at the spur fusing was replaced and supply restored. | CREEK ROAD, MITCHAM VIC 3132 |  |  | Blown branch/vegetation | [5 empty] | Customers supplied ex the HV spur fusing at BH2047 located in Creek Road advised of a loss of their electricity supply. A caller mentioned a branch has fallen onto the powerlines and is smoking. The CFA are in attendance. | Conductor (bare) | 0 | 0 | 0 |  | RWT 12 | Vegetation: Trees Incident | Other vegetation | 30/01/2019 17:05 | 1 | Negligible: no ground fire | 12067 | Roadway |  | 20190201UTD_01 | Infrastructure (network-based) | -37.8186 | 145.1962 | 1 | United Energy Distribution | Report | 15103 | 0.0086632 | 22kV AC | Moorabbin Airport | 3132 | Mitcham | Trees
New p bracket and insulator fitted and conductor re fitted to insulator. | 100 CAMPASPE ROAD, WILLOWMAVIN VIC 3764 | LIS 4702628 |  |  |  | Insulator;Mechanical breakdown |  |  | 1 | E0009278 - HV conductor down due to breakage of HV pin type insulator causing grass fire and the death of 3 cows. Approximately 135m x 135m area burnt. | Conductor (bare);Insulators | 0 | 0 | 0 |  | KMS11 | insulator make DIA (Dalton Insulators Australia) manufacture year 1980 broke due to crack around the conductor groove. The crack was caused by cement growth. | Grassfire;Fatality of livestock, pet or companion animal | 43498.9535 | 1 | Medium: 1000 sq.m - 10 ha | 12075 | Agricultural |  | 20190204SPN_01 | Infrastructure (network-based) | -37.2512 | 144.9184 | 1 | AusNet Services Distribution | Report | 17901 | 0.0015035 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3764 | Willowmavin | AF Other
Fault crew dispatched to investigate and make safe. Fuse was replaced. | 225 CORNWALLS ROAD, FISH CREEK VIC 3959 | LIS2023994 |  |  |  | Candled fuse |  |  |  | HV ELF fuse candling. No evidence of ground fire | Any other type | 0 | 0 | 0 |  | FTR21 | Customer contacted AusNet advising they had fluctuating volts, fault crew was dispatched and, upon arrival, found a candling ELF fuse tube. Fuse replaced and supply restored. No evidence of ground fire | Pole-top fire | 43467.7931 | 1 | Negligible: no ground fire | 12076 | Agricultural |  | 20190204SPN_02 | Infrastructure (network-based) | -38.699 | 146.0462 | 2 | AusNet Services Distribution | Report | 17763 | 0.019749 | 22kV AC | Morwell (Latrobe Valley Airport) | 3959 | Fish Creek | Fuse
CS2 Feeder CB unsuccessfully reclosed. When crew arrived on site, there was debris from HV insulator on the ground. Crew isolated area to make safe and restored surrounding area, HV isolator was replaced, conductor repaired and insulator debris removed (refer to SAP not. 10289157). | 205 MUNRO STREET, COBURG VIC 3058 |  |  | Lightning | [5 empty] | Lightning struck high voltage insulator at pole A048458. The lightning shattered the insulator and burnt through the conductor, bringing down 2 bays of centre phase high voltage conductor between poles A048459 and A048629 (refer to TE #176107). No photos available. | Conductor (bare) | 0 | 0 | 0 |  |  | Lightning struck high voltage insulator at pole A048458 | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43618.8035 |  |  | 12098 | Residential |  | 20190207JEM_01 | Infrastructure (network-based) | -37.7432 | 144.9479 | 1 | Jemena | Report | 15159 | 0.027247 | 22kV AC | Essendon Airport | 3058 | Coburg | Lightning
Area made safe, and service removed. | 130 BONDS LANE, GREENVALE VIC 3059 |  |  |  |  | Mechanical breakdown |  |  |  | Live service on ground at base of pole near lot 344, Bonds Lane, Greenvale (Located opposite 130 Bonds Lane, Greenvale). Area is currently under development â€“ there are no houses at this location. | Service conductor | 0 | 0 | 0 |  |  | Catenary wire failed due to mechanical degradation causing service to fall to ground. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43648.3313 |  |  | 12101 | Residential |  | 20190207JEM_02 | Infrastructure (network-based) | -37.6371 | 144.8757 | 1 | Jemena | Report | 15162 | 0.025834 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | AF Other
Made safe | 215 GORDON STREET, FOOTSCRAY VIC 3011 |  | Copper theft | [5 empty] | 2 | Zinfra technical reported that cable from pole to pit was stolen. | Cable | 0 | 0 | 0 |  |  | Unknown persons stole underground cable. | Loss of supply;Damage to network assets | 43618.6639 |  |  | 12107 | Residential |  | 20190207JEM_04 | Infrastructure (network-based) | -37.7996 | 144.8882 | 1 | Jemena | Report | 15168 | 0.029352 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Other
On arrival crew isolated supply and carried out repairs. | 51 WILLIAMS ROAD, SHEPPARTON VIC 3630 | 33089513 | Vehicle | [6 empty] | Vic Fire reported a truck has brought down power lines over foot path at the incident location. Upon arrival, the Powercor crew found that a LV conductor and several other services on the pole had been damaged. There were no injuries or fire. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | STN024 | Truck brought down service and LV conductor | Loss of supply;Damage to network assets | 23/01/2019 10:32 |  |  | 12100 | Roadway |  | 20190207PWA_01 | Infrastructure (network-based) | -36.3808 | 145.4187 | 1 | Powercor | Report | 15161 | 0.019977 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Vehicle
On arrival crew carried out repairs | GREEN HILL ROAD, EYNESBURY VIC 3338 | 30105815 | Vandalism;Copper theft | [6 empty] | Contractor for PAL found earthing and underground lighting cable stolen at incident location. There was no fire, no reported injuries and no third party property damage. It is also reported that the cable which had previously been stolen, was re-installed on Saturday 19th Jan, and found missing again 24/1/19 | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN011 | Vandalism and copper theft | Damage to network assets | 24/01/2019 8:42 |  |  | 12105 | Roadway |  | 20190207PWA_04 | Infrastructure (network-based) | -37.4507 | 144.5512 | 1 | Powercor | Report | 15166 | 0.040054 | Low voltage AC (<1kV);Earthing cable | Melbourne Airport | 3338 | Eynesbury | Other
On arrival crew isolated supply and carried out repairs. REC attended to repair a number of customer points of attachments. | 145 KILBY ROAD, KEW EAST VIC 3102 | 30178584 |  | Fallen | [5 empty] | Vic fire reported wire down across roadway at incident location. On arrival crew reported a tree has fallen across LV conductors, resulting in conductors falling to ground, the resultant loading caused an adjacent LV pole to fracture and fall to the ground. There was no fire, no reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | Q014 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 25/01/2019 14:34 |  |  | 12111 | Roadway |  | 20190207PWA_06 | Infrastructure (network-based) | -37.7927 | 145.057 | 1 | CitiPower | Report | 15173 | 0.027631 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | Trees
Fault crew and LEI dispatched to investigate | 134 WARBURTON HIGHWAY, LILYDALE VIC 3140 | LIS1001883 |  |  |  | Defective component |  | Phase to neutral | 0 | E0008748 - Plumber reported electric shock while working at customer property | Connection box | 0 | 0 | 0 |  | LDL23 | Plumber was installing new water pipes under the house and felt a tingle when he made contact to the old gal water pipe and felt a â€œtingleâ€. Gal pipe is still connected to the installations M.E.N. earthing system even though the pipe is not in use.The home has a recent earth stake now. Home has a recent switchboard upgrade with RCDs etc but no RCDs tripped. The installation was using a high load of over 30 Amps and the Neutral connection on the pole may have been intermittent resulting in current to be present in the installations earthing system. Fault crew repaired/re-terminated connections on pole and FOLCB and supply restored. | Minor shock | 26/01/2019 6:29 |  |  | 12112 | Residential |  | 20190207SPN_04 | Infrastructure (network-based) | -37.7608 | 145.3967 | 2 | AusNet Services Distribution | Report | 15175 | 0.014924 | Low voltage AC (<1kV) | Moorabbin Airport | 3140 | Lilydale | AF Other
Crews attended and made the site safe. A woman was still in the car, and was assisted by the crew to exit the car safely. The incident was called through to ESV, with Reference no. 11243561 obtained. UE fault crews attended with an LEI and undertook inspection for damage at neighbouring premises. The LEI confirmed that a high voltage injection occurred affecting customers supplied from "Packham Springfield" substation. Procedures as indicated in the work instruction for HV injections have been followed. | 520 MIDDLEBOROUGH ROAD, BLACKBURN NORTH VIC 3130 | 7031328 |  |  |  | Rot | Followed but inappropriate |  |  | At 12:18pm a wood pole failed and fell onto the roadway in Middleborough Rd opposite Packham St, Box Hill North. The feeder protection operated and de-energised the lines. Soon after, a passing vehicle contacted the fallen conductors. It was also confirmed that HVI had occurred to neighbouring residences. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | DC7 | The pole has failed at the base. Refer to attached pole failure report. While the pole base does have signs of rot (included in "Technical" causal factor), testing showed enough sound wood for the pole to be classified as serviceable. However, the root cause has been identified as a fracture resulting from the act of straightening the pole. | HV injection;Significant disruption to the community | 43618.5125 |  |  | 12099 | Roadway |  | 20190207UTD_01 | Infrastructure (network-based) | -37.8082 | 145.1408 | 1 | United Energy Distribution | Report | 15539 | 0.012583 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3130 | Blackburn North | Pole
A fault crew attended and lowered the EWP with ambulance services in attendance. The area was cordoned off and Emergency Services, ESV and Worksafe representatives were in attendance investigating the cause of the incident. | 9 LATROBE STREET, HUGHESDALE VIC 3166 |  |  | Within clearances |  |  |  | Phase to phase | 2 | At 12.07PM, emergency services contacted the United Energy faults and emergencies call centre advising that a â€œtree lopper is stuck in tree â€“ unsure if injured or notâ€. The tree cutter was working in a Elevating Work Platform (EWP) outside 9 Latrobe Street, Hughesdale and has made contact with the white and blue phase LV conductors. There was no loss of supply to customers supplied from "Barkly-Warrigal" substation. ESV were contacted by the MFB with reference number 11248929 provided. The tree cutter was working for Active Tree Services on behalf of the City of Monash. The tree cutter was not working for United Energy or its contractors. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Electrocution | 43648.5049 |  |  | 12113 | Roadway |  | 20190207UTD_02 | Infrastructure (network-based) | -37.9018 | 145.0851 | 1 | United Energy Distribution | Report | 15487 | 0.011523 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Hughesdale | Other
A UE fault crew attended and called for an LEI to attend and investigate. The LEI found that the 3 phase, 4 pole RCD protecting all power circuits had sustained damage. Fault crew isolated property and LEI issued customer with defect notice for an REC to return to repair damage. | 22 NIRVANA AVENUE, MALVERN EAST VIC 3145 |  |  | Lightning |  |  |  |  | 2 | Lightning struck onto or close to house and caused MSB damage at property. White phase service fuse to the property had blown. | Customer installation | 2 | 2 | 2 |  |  | Lightning seems to have struck on or near the premise affected. | Loss of supply | 30/01/2019 17:15 |  |  | 12115 | Residential |  | 20190207UTD_03 | Infrastructure (network-based) | -37.8824 | 145.0641 | 1 | United Energy Distribution | Report | 15180 | 0.037336 | Low voltage AC (<1kV) | Moorabbin Airport | 3145 | Malvern East | Lightning
On arrival crew isolated supply and carried out repairs. REC on site LEI inspecting premises | 27 DEEPDENE ROAD, DEEPDENE VIC 3103 | 30349038 |  | Blown branch/vegetation | [5 empty] | The CitiPower Report Room was contact by two customer advising of switchboard damage during a storm. On arrival the crew found a council tree between between the HV and LV in Deepene Rd Balwyn South. There was point of attachment damage to No.27 Deepdene Rd. No. 50 Deepdene rd had suspected switchboard damage and appliance damage. There was no fire and no reported injuries. | Conductor (bare);Service conductor | 2 | 2 | 2 |  | L002 | Vegetation: Trees Incident | HV injection;Loss of supply;Damage to network assets | 43618.9208 |  |  | 12118 | Roadway |  | 20190208PWA_02 | Infrastructure (network-based) | -37.8144 | 145.0618 | 1 | CitiPower | Report | 15183 | 0.034975 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3103 | Deepdene | Trees
On arrival crew carried out repairs. | 2613 PYRENEES HIGHWAY, MOOLORT VIC 3465 | 30017086 |  |  |  | Leakage |  |  |  | Vicfire reported pole fire at the incident location. Upon arrival crew found that a pole fire had occurred on a 66/22/LV pole, Carisbrook 144A. Pole fire occurred at position #3 crossarm kingbolt, but involved the LV crossarm also at the kingbolt position. All conductors remained aloft. No ground fire, 3rd party damage or injury transpired. | Pole (wood) | 2 | 2 | 2 |  | MRO007 | Excessive leakage current | Pole-top fire | 43618.8958 | 1 | Negligible: no ground fire | 12119 | Roadway |  | 20190208PWA_03 | Infrastructure (network-based) | -37.0844 | 143.9459 | 1 | Powercor | Report | 15184 | 0.016821 | 22kV AC | Ballarat Aerodrome | 3465 | Moolort | Crossarm
Crews attended and repaired conductors. Driver of excavator not on site. | 57 ALBERT AVENUE, SPRINGVALE VIC 3171 | 612359 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | LV mains conductors were brought hit and damaged by an excavator undertaking demolition works at 57 Albert Ave Springvale. | Conductor (bare) | 0 | 0 | 0 |  |  | Demolition contractor contacted bare LV mains in street. No other details obtained. | No Go Zone (contact) | 22/01/2019 9:20 |  |  | 12120 | Roadway |  | 20190208UTD_01 | Infrastructure (network-based) | -37.9544 | 145.1455 | 1 | United Energy Distribution | Report | 15185 | 0.031255 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Vehicle
Section isolated and repairs initiated by Jemena | 67 MOUNTAIN VIEW PARADE, ROSANNA VIC 3084 |  |  | Animal |  | Conductor clashing |  | Phase to phase | 1 | A possum caused a flashover (bridged out across HV fused isolators) at Darvall-Waiora distribution substation. This caused clashing and the high voltage bridges to fail resulting in live high voltage conductors to fall to the ground. | Conductor (bare) | 0 | 0 | 0 |  | NH 5 22KV Fdr | Animal Incident | Loss of supply;Damage to network assets | 43771.1347 |  |  | 12128 | Residential |  | 20190211JEM_01 | Infrastructure (network-based) | -37.7406 | 145.0599 | 1 | Jemena | Report | 15196 | 0.014374 | 22kV AC | Essendon Airport | 3084 | Rosanna | Animal
Replaced EDO tube and restored supply. | 1 KEARNEY LANE, TEMPLESTOWE VIC 3106 | LIS1207946 |  | Lightning |  | Candled fuse |  |  | 1 | E0009935 - Fuse candling reported | EDO fuse | 0 | 0 | 0 |  | ELM 34 | Candled EDO fuse and no evidence of ground fire. Suspect fault occurred during previous lightning storm. Replaced EDO tube and restored supply. | Pole-top fire | 43740.3201 | 1 | Negligible: no ground fire | 12137 |  |  | 20190211SPN_02 | Infrastructure (network-based) | -37.7367 | 145.1723 | 1 | AusNet Services Distribution | Report | 18282 | 0.039145 | 22kV AC | Moorabbin Airport | 3106 | Templestowe | Fuse
Fault crew dispactched and Fused mains box replaced | 11 TRELAWNY AVENUE, SANDY POINT VIC 3959 | LIS2021646 |  |  |  | Defective component |  |  |  | E0009927 - Vic Fire reported pole fire. Fused Mains Box failed resulting in pole fire. No evidence of ground fire | Connection box | 0 | 0 | 0 |  | FTR21 | Pole mounted Fused Mains Box has failed and melted resulting in pole fire. Cause of failure unknown. No evidence of ground fire | Pole-top fire | 43710.7139 | 1 | Negligible: no ground fire | 12138 |  |  | 20190211SPN_03 | Infrastructure (network-based) | -38.8322 | 146.1326 | 2 | AusNet Services Distribution | Report | 15212 | 0.0069722 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3959 | Sandy Point | Fuse
Fault crew dispatched. candled EDO fuse removed and replaced with new | 8A MAURICE ROAD, GRUYERE VIC 3770 | LIS1002281 |  | Bird |  | Candled fuse |  |  |  | E0009921 - report of EDO HV fuse candling. No evidence of ground fire | EDO fuse | 0 | 0 | 0 |  | LDL23 | Bird Incident | Pole-top fire | 43679.8118 | 1 | Negligible: no ground fire | 12140 |  |  | 20190211SPN_04 | Infrastructure (network-based) | -37.7585 | 145.4304 | 1 | AusNet Services Distribution | Report | 17808 | 0.018814 | 22kV AC | Moorabbin Airport | 3770 | Gruyere | Animal
Emergency high voltage switching was completed to minimise the number of customers affected and the repairs were completed under Access Authority conditions prior to supply being restored. The LEI confirmed that a high voltage injection occurred affecting customers supplied from "McCelland Telecom" substation. The LEI investigated the amount of damage that occurred to customers appliances and equipment and the faults crew also assisted the LEI's to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | 240 MCCLELLAND DRIVE, LANGWARRIN VIC 3910 | 3319579 |  | Blown branch/vegetation |  |  |  |  | 1 | During storm event, reports received of wires down in McClelland Dve/Centenary Park Dve Langwarrin. Customers supplied from Pole substation McCelland Telecom experienced HVI. | Conductor (bare);Transformer | 0 | 1 | 0 |  | LWN21 | Vegetation: Trees Incident | HV injection | 30/01/2019 17:35 |  |  | 12125 | Roadway |  | 20190211UTD_01 | Infrastructure (network-based) | -38.135 | 145.178 | 1 | United Energy Distribution | Report | 15193 | 0.023603 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3910 | Langwarrin | Trees
A faults crew attended and patrolled the feeder. A small 9sqm grass fire had started at the base of pole number 3310277 that was extinguished by the CFA. | 250 ROBINSONS ROAD, LANGWARRIN SOUTH VIC 3911 | 3310277 |  | Heat |  | Leakage |  |  | 1 | At 1.27AM on 01/02/2019, protection alarms were received from 66kV feeder TBTS-FTS as it successfully reclosed. A short time afterwards, the CFA advised of a grass fire at the base of pole number LIS 3310277 in Robinsons Road, Langwarrin near the corner of Warrandyte Road. | Insulators;Pole (concrete) | 0 | 0 | 0 |  | TBTS-FTS | Due to unknown circumstances, tracking from the 66kV conductors traveled down the concrete pole and caused the small fire to start at the base. It was suspected that salt borne contaminants attributed to the event and the insulators were cleared prior to supply being restored. | Grassfire | 43467.0604 | 1 | Localised: less than 10 sq.m | 12129 | Roadway |  | 20190211UTD_03 | Infrastructure (network-based) | -38.1776 | 145.1656 | 1 | United Energy Distribution | Report | 18383 | 0.034082 | 66kV AC | Moorabbin Airport | 3911 | Langwarrin South | Conductor
Fault crew dispatched. Cable and surge diverters replaced and supply restored. | 990 KOO WEE RUP ROAD, PAKENHAM VIC 3810 | LIS515966 |  |  |  | Defective component;Electrical breakdown |  |  |  | E0009793 - Grass fire reported adjacent to pole LIS515966 | Cable | 0 | 0 | 0 |  | PHM22 | HV cable on Blue phase of cable head pole has failed and burnt resulting in a ground fire. The insulation on the blue phase dropper appears to have degraded resulting in failure and subsequent fire. | Grassfire | 43648.65 | 1 | Medium: 1000 sq.m - 10 ha | 12158 | Agricultural |  | 20190213SPN_04 | Infrastructure (network-based) | -38.1102 | 145.4866 | 2 | AusNet Services Distribution | Report | 15241 | 0.0013576 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | AF Other
Fault crew dispatched. Surge Diverter replaced and damaged cablehead repaired. | 165 ROBINSON RD, NARRE WARREN NORTH VIC 3804 | LIS519932 |  |  |  | Defective component |  |  |  | E0009795 - Surge Diverter on cablehead pole has failed resulting in small ground fire approx. 1m sq. | Cable;Surge diverter | 0 | 0 | 0 |  | LYD14 | Surge Diverter on Blue phase of cablehead pole appears to have failed resulting in small ground fire approx. 1m sq. | Grassfire | 43648.8806 | 1 | Localised: less than 10 sq.m | 12159 | Roadway |  | 20190213SPN_05 | Infrastructure (network-based) | -37.9827 | 145.3192 | 2 | AusNet Services Distribution | Report | 17794 | 0.0067106 | 22kV AC | Moorabbin Airport | 3804 | Narre Warren North | AF Other
Fault truck dispatched to investigate. No damage to distribution assets and no repairs required | 3 SURREY ROAD W, CROYDON VIC 3136 | LIS1215701 | Vehicle | [6 empty] | report of grass fire following truck contacting O/H communications cable causing them to contact O/H HV conductors. | Conductor (bare) | 0 | 0 | 0 |  | CPK21 | Truck believed to have contacted O/H communications cable causing them to contact O/H HV conductors. Investigator found no damage to Distribution assets | Grassfire;No Go Zone (contact) | 43801.4653 | 1 | Localised: less than 10 sq.m | 12161 |  |  | 20190213SPN_06 | Infrastructure (network-based) | -37.7893 | 145.2834 | 2 | AusNet Services Distribution | Report | 18122 | 0.014617 | 22kV AC | Moorabbin Airport | 3136 | Croydon | Vehicle
The attending Powercor Fault Crew replaced the existing O/H Service Cable from the Pole to New FOLCB installed by REC under Fault conditions | 12 WARREN STREET, STAWELL VIC 3380 | 30084671 |  |  |  | Corrosion;Fault on customer installation |  |  |  | Person was in the rear yard operating the External Garden Tap when he received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the conductive wet ground. | Service conductor;Customer installation | 0 | 0 | 0 |  | STL005 | Corroded O/H Service Neutral Conductor termination at the Mains Connection Box located at the Customerâ€™s POA. | Minor shock | 30/01/2019 19:30 |  |  | 12170 | Residential |  | 20190214PWA_06 | Infrastructure (customer connection) | -37.0658 | 142.7762 | 1 | Powercor | Report | 15255 | 0.029302 | Low voltage AC (<1kV) | Horsham Aerodrome | 3380 | Stawell | Connection
The attending Powercor Fault Crew re-terminated all O/H Service Cable connections directly to the O/H Reticulation Conductors | 18 BUCKLEYS ROAD, POINT LONSDALE VIC 3225 | 30068478 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom showering when she received an electric shock as she made simultaneous contact with her hand on the metal tap and her bare feet whilst standing on the conductive wet shower base. | Service conductor | 0 | 0 | 0 |  | DDL012 | Corroded O/H Service Neutral Conductor termination at the Pole Top Junction Box located on the Reticulation Pole. | Minor shock | 26/01/2019 7:30 |  |  | 12173 | Residential |  | 20190214PWA_08 | Infrastructure (network-based) | -38.2856 | 144.61 | 1 | Powercor | Report | 15258 | 0.0068414 | Low voltage AC (<1kV) | Avalon Airport | 3225 | Point Lonsdale | Connection
Crew replaced melted service connector in service pit | 40 CUNNINGHAMS ROAD, WERRIBEE SOUTH VIC 3030 | 60268604 |  |  |  | Electrical breakdown |  |  | 2 | dog was standing on a pit when he made simultaneous contact between his leg on the pit and the wet ground long side the pit and seemed to receive a shock (sprinklers going on the front lawn ) Voltage tests between an independent earth and various points near the pit found voltage of 235 volts. | Services pit | 0 | 0 | 0 |  | WBE034 | Damaged u/g public lighting service cable in pit | Minor shock | 43618.75 |  |  | 12174 | Residential |  | 20190214PWA_09 | Infrastructure (network-based) | -37.9317 | 144.7288 | 1 | Powercor | Report | 15259 | 0.0074375 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Connection
A faults truck attended after the MFB had extinguished the 10m x 5m grass fire caused by fallen molten metal falling into the dry grass below. Appeared that an un-identified truck contacted the Optus communication cable between pole numbers 0618315 and 0629124 causing the Optus cable to flick up and make brief contact with a HV conductor. Optus were contacted as the steel strand that holds the communication cable to the catenary has unraveled and they are required to attend promptly. | PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 618315 | Vehicle |  |  | Conductor clashing |  |  | 2 | At 1.20PM, SVW zone substation identified a Master Earth Fault (MEF) and a short time afterwards, the MFB were on site (1.37PM) outside the Springvale Cemetery near Main Drive where they advised that a sparking powerline has started a grass fire. No customers were affected. A unknown vehicle has contacted the Optus communication cable located outside the Springvale Cemetery near pole number LIS 0618315. | Conductor (bare) | 0 | 0 | 0 |  | SVW 55 | An unknown over height vehicle has contacted an Optus communication cable that caused it to flick up briefly into a HV conductor. | Grassfire | 43648.5674 | 1 | Small: 10 - 1000 sq.m | 12175 | Roadway |  | 20190214UTD_03 | Infrastructure (network-based) | -37.9499 | 145.175 | 1 | United Energy Distribution | Report | 18394 | 0.0048542 | 22kV AC | Moorabbin Airport | 3171 | Springvale | Vehicle
"Monaco- Ti Tree" substation was isolated HV/LV after placing customers supplied from it under LV parallel from adjacent substations. The burnt off lead and krone box were replaced under Access Authority conditions before supply was restored. | MONACO STREET, PARKDALE VIC 3195 | 9864653 |  | Heat |  | Overheated connection |  |  | 2 | Customers supplied from "Monaco-Ti Tree" substation advised of a loss of their electricity supply. The MFB advised of a transformer fire at pole number LIS 9864653 and are now leaving the site. A faults crew attended and identified the red phase LV lead was burnt out between the LV transformer and the krone switch due to probable overload as it was very warm at the time of the fault. | Connector/termination;Dropper/bridge | 0 | 0 | 0 |  | M 35 | Probable overload during hot weather. | Pole-top fire;Loss of supply | 43648.7236 | 1 | Negligible: no ground fire | 12176 | Roadway |  | 20190214UTD_04 | Infrastructure (network-based) | -37.9965 | 145.0738 | 1 | United Energy Distribution | Report | 15261 | 0.034413 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Parkdale | AF Other
Zinfra personnel, representing UE, visited the site on at least two occasions and spoke to the builder / developer, whose attitude towards safety of electricity network assets was low. Zinfra also contacted WorkSafe officer Allan McGuiness. Please refer to attached report and photos from Zinfra. | 210-218 BOUNDARY ROAD, BRAESIDE VIC 3195 | 9816622 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | A faults crew noticed some hand rail fall arrest that had been erected on a building at 210 to 218 Boundary Rd Braeside very close to the HV surge diverters mounted on a pole type sub. Further investigation revealed the builder/developer has undertaken works within the No Go Zone without obtaining a No Go Zone permit. Further, it has been determined that the structure built may be in contravention of Regulation 313 of the Electricity Safety (Installations) Regulations 2009 with a distance measured from the building to the live surge diverters on the pole substation structure of 2050mm. | Pole mounted;No failed asset | 2 | 2 | 2 |  |  | Apparent disregard or lack of knowledge of electricity safety regulations and rules (No Go Zone) by the builder / developer | No Go Zone (no contact) | 13/02/2019 16:07 |  |  | 12178 | Construction |  | 20190214UTD_05 | Infrastructure (network-based) | -37.9939 | 145.1071 | 2 | United Energy Distribution | Report | 15433 | 0.033094 | 22kV AC | Moorabbin Airport | 3195 | Braeside | Other
On arrival crew isolated supply and carried out repairs. | BURN BRAE, 151 MYERS ROAD, DEAN VIC 3363 | 32008548 |  |  |  | Leakage |  |  |  | Property owner advised pole on fire at incident address. Crew attended to find pole top and conductors on ground. Pole burnt through at the cross-arm strap bolt. No ground fire and no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | BAN008 | Excessive leakage current | Pole-top fire | 15/02/2019 10:30 | 1 | Negligible: no ground fire | 12180 | Agricultural |  | 20190215PWA_01 | Infrastructure (network-based) | -37.4503 | 144.016 | 1 | Powercor | Report | 15265 | 0.01453 | 22kV AC | Ballarat Aerodrome | 3363 | Dean | Pole
Fault crew dispatched. Fuse replaced. | 379 DIFFEY ROAD, EVERTON VIC 3678 | pole 4508817 |  |  |  | Candled fuse |  |  |  | E0010821 - Blown HV EDO fuse stuck up and burnt in half on pole 4508817. Single phase 10kVA substation "CHAMBERLAIN 14". Feeder WN5. No Ground fire sighted. | EDO fuse | 0 | 0 | 0 |  | WN5 | Candled HV fuse | Pole-top fire | 18/02/2019 1:42 | 1 | Negligible: no ground fire | 12184 |  |  | 20190218SPN_02 | Infrastructure (network-based) | -36.4219 | 146.5812 | 1 | AusNet Services Distribution | Report | 15272 | 0.031995 | 22kV AC | Wangaratta Aero | 3678 | Everton | Fuse
Fault crew dispatched and conductor repaired | 411 CHILDERS-THORPDALE ROAD, THORPDALE VIC 3835 | LIS2207436 |  |  |  | Corrosion |  |  |  | E0010807 - Conductor down and subsequent ground fire reported | Conductor (bare) | 0 | 0 | 0 |  | MOE22 | Rusted 3/12 Steel conductor broke mid span at the steel sleeve between poles LIS2207435 and LIS2207436 resulting in a small ground fire. Only one conductor of the 3phase circuit broke. One dead cow found in the vacinity of the wood pole. | Grassfire | 17/02/2019 10:55 | 1 | Localised: less than 10 sq.m | 12185 |  |  | 20190218SPN_03 | Infrastructure (network-based) | -38.2963 | 146.134 | 1 | AusNet Services Distribution | Report | 15274 | 0.036135 | 22kV AC | Morwell (Latrobe Valley Airport) | 3835 | Thorpdale | Conductor
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was repaired under Access Authority conditions. A LEI confirmed a HVI occurred (KEY 1901) affecting customers who reside in the vicinity that sustained minor damage to appliances and equipment. Procedures as indicated in the work instruction for HV injections has been followed and letters and claim forms have been distributed to the affected customers within the area. | HAMMOND ROAD, DANDENONG VIC 3175 | 623109 | Vehicle |  |  | Conductor clashing;HV injection |  |  | 1 | At 11.53AM on 11/02/2019, 22kV feeder DVY 31 circuit breaker reclosed to lockout. Callers to the United Energy faults and emergencies call centre advised that a truck has pulled down power lines and caused a fire. A high load (as indicated by Victoria Police) has struck a LV slack span at the HV/LV tee-off from Hammond Road into Superior Drive. This caused the red phase LV conductor to break and to fall to the ground and the blue phase LV conductor was very tight when the crossarm twisted causing it to make contact with the HV conductors. A HVI was suspected to customers supplied from "Grantio-Hammond" substation and a LEI was dispatched to investigate. In addition, a 30sqm grass fire started as a result of molten metal dropping to the ground that was extinguished by the CFA. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | DVY 31 | A high load contacted the LV overhead conductors at the corner of Hammond Road and Superior Drive causing a HVI and a grass fire. | HV injection;Grassfire | 43771.4951 | 1 | Localised: less than 10 sq.m | 12187 | Roadway |  | 20190218UTD_01 | Infrastructure (network-based) | -38.033 | 145.202 | 1 | United Energy Distribution | Report | 15488 | 0.014531 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3175 | Dandenong | Vehicle
On arrival crew isolated supply and carried out repairs. | 222 CLARKES ROAD, BROOKFIELD VIC 3338 | 30293002 | Vandalism;Copper theft | [6 empty] | Report received that multiple pit covers removed and wires pulled out from pits and exposed on Brooklyn Rd west of Clarkes Rd and between Clarkes Rd and Botanica Springs Blvd. Upon arrival the fault crew found approximately 180 metres of public lighting service cable had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft | Damage to network assets | 28/01/2019 16:31 |  |  | 12192 | Roadway |  | 20190219PWA_02 | Infrastructure (network-based) | -37.6996 | 144.5461 | 1 | Powercor | Report | 15282 | 0.027457 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew carried out repairs | 35 YERRIN STREET, BALWYN VIC 3103 | 30175542 | Vandalism;Copper theft | [6 empty] | A passerby advised CitiPower that the pole to pit copper had been stolen, and the underground cable was exposed at the incident location. On arrival the crew found that an unknown person/s had removed a 4 core UG cable with force, resulting in damage to the cover guards and conduit on the pole. There were no reported injuries or fire. | Services cable | 2 | 2 | 2 |  | WD013 | Copper theft | Damage to network assets | 29/01/2019 7:33 |  |  | 12194 | Roadway |  | 20190219PWA_03 | Infrastructure (network-based) | -37.8095 | 145.0847 | 1 | CitiPower | Report | 15284 | 0.01809 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Other
The attending Powercor Fault Crew disconnected and removed the existing Meter and O/H Neutral Screened Service Cable following instructions from the REC / Builder to abolish the electricity supply to the property pending completion of extensive building renovation works. | 202 FOREST STREET, BENDIGO VIC 3550 | 30027049 |  |  |  | Neutral fault;Mechanical breakdown |  |  |  | Electrician was laying on his back under the house clipping new cables when his arm came in contact with an existing Bare Earthing Conductor when he received an electric shock. A subsequent test by the Electrician proved the earthing conductor to be live. The Electrician removed the Service Fuse at the POA and disconnected the Main Neutral Conductor at the Neutral Bar in the Main Switchboard to make safe. | Service conductor | 0 | 0 | 0 |  | BET008 | Service cable damaged in span- neutral discontinuous | Minor shock | 18/02/2019 14:00 |  |  | 12200 | Residential |  | 20190220PWA_04 | Infrastructure (customer connection) | -36.7517 | 144.2693 | 1 | Powercor | Report | 15297 | 0.034098 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | OH Cable
On arrival crew isolated supply | 412 WHITEHORSE ROAD, SURREY HILLS VIC 3127 | 30234181 | Working too close to underground cables | [6 empty] | Nick (Ph. 0425 773 695) advised an UG cable hit with excavator at the incident location. Upon arrival, CitiPower crews found that the live UG cable had been damaged by an excavator. The building was being demolished while this cable was damaged. The damaged location is within this private property. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | RD005 | Excavator struck service | No Go Zone (contact) | 31/01/2019 11:00 |  |  | 12201 | Residential |  | 20190220PWA_05 | Infrastructure (network-based) | -37.8139 | 145.0888 | 1 | CitiPower | Report | 15298 | 0.021681 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | Dug up
Fault crew dispatched and fuse replaced | 136 MOXHAMS ROAD, MONBULK VIC 3793 | LIS1322918 |  |  |  | Candled fuse |  |  |  | E0011130 - candling fuse reported | Any other type | 0 | 0 | 0 |  | BGE24 | Candling HV fuse. Fuse replaced and supply restored | Pole-top fire | 18/02/2019 12:40 | 1 | Negligible: no ground fire | 12202 |  |  | 20190220SPN_01 | Infrastructure (network-based) | -37.8854 | 145.4119 | 2 | AusNet Services Distribution | Report | 17918 | 0.017519 | 22kV AC | Moorabbin Airport | 3793 | Monbulk | Fuse
low voltage circuit was isolated and earthed to allow for repair. Conductors repaired and spreader installed between span A049154 and A049155. | 6 ROYAL PARADE, PASCOE VALE SOUTH VIC 3044 | A049154 |  | Wind |  | Conductor clashing |  |  |  | Jemena work party advised Red Phase LV conductor and neutral conductor down (live). (Refer to TE# 176896, 176903) | Conductor (bare) | 0 | 0 | 0 |  |  | Conductor clashed mid span. Conductor size was relatively thin (7/.064) and strong winds at time of incident caused conductor clash. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/02/2019 6:16 |  |  | 12213 | Residential |  | 20190225JEM_01 | Infrastructure (network-based) | -37.746 | 144.9458 | 1 | Jemena | Report | 15318 | 0.037135 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale South | Conductor
Voltage tests revealed a high impedance in the return neutral due to an open circuit between the open wire and the neutral screen service junction box. On arrival, the attending LEI conducted voltage tests and a neutral impedance test on the incoming neutral at the switchboard and recorded 8.4ohms resistance. The attending linesmen visually found the broken neutral connection and re terminated it at the junction box then conducted an NST test at the FOLCB which passed. The attending LEI conducted an NST test at the customer switchboard which passed. The LEI conducted voltage tests at the front tap and customer switchboard and recorded 0.5v. An impedance test on the incoming neutral recorded 0.2 ohms. | 55 MITCHELL STREET, MARIBYRNONG VIC 3032 |  |  |  |  | Neutral fault |  |  |  | Electrician advised customer reported to have received shocks from their Air Con and Kettle. Ref TBL# 176992. | Neutral screen | 0 | 0 | 0 |  |  | Broken neutral connection on neutral screen service between the junction box at pole end and the open wire service. | Minor shock | 26/02/2019 16:51 |  |  | 12233 | Residential |  | 20190226JEM_03 | Infrastructure (network-based) | -37.7834 | 144.8856 | 1 | Jemena | Report | 15341 | 0.021394 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Maribyrnong | Connection
On arrival crew isolated supply and carried out repairs. | 11 STUART STREET, BEAUFORT VIC 3373 | 33005424 |  |  |  | Candled fuse |  |  |  | Following report from supply interruption crew found an EDO fuse fuse had candled before falling to the ground. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | BAS011 | Edo fuse hung up | Pole-top fire | 17/02/2019 4:06 | 1 | Negligible: no ground fire | 12225 | Roadway |  | 20190226PWA_05 | Infrastructure (network-based) | -37.4321 | 143.3785 | 1 | Powercor | Report | 15330 | 0.010251 | 22kV AC | Ballarat Aerodrome | 3373 | Beaufort | Fuse
Fault crew dispatched to investigate. No evidence of any damage to DB assets | 60 CARBEEN DRIVE, BUNDOORA VIC 3083 | LIS905808 |  | Bird |  |  |  | Phase to earth | 1 | Ground fire (approx 13 x 2 metres) reported at base of pole following bird contacting O/H HV assets on pole. No evidence of any damage to DB assets | Conductor (bare);Pole top;Pole (concrete) | 0 | 0 | 0 |  | WT6 | Bird Incident | Grassfire | 24/02/2019 18:09 | 1 | Small: 10 - 1000 sq.m | 12229 |  |  | 20190226SPN_01 | Infrastructure (network-based) | -37.6818 | 145.0586 | 1 | AusNet Services Distribution | Report | 17774 | 0.021341 | 22kV AC | Essendon Airport | 3083 | Bundoora | Animal
Fault crew dispatched. Tree removed from the line and supply restored | 220 TWO MILE ROAD, HERNES OAK VIC 3825 | LIS2206528 and LIS2206529 |  | Fallen | [5 empty] | E0011790 - MFB reported tree fire following tree contacting O/H conductors | Conductor (bare) | 2 | 2 | 2 |  | MOE31 | Vegetation: Trees Incident | Other vegetation | 25/02/2019 19:29 | 1 | Small: 10 - 1000 sq.m | 12230 |  |  | 20190226SPN_02 | Infrastructure (network-based) | -38.211 | 146.278 | 1 | AusNet Services Distribution | Report | 17805 | 0.031385 | 22kV AC;66kV AC | Morwell (Latrobe Valley Airport) | 3825 | Hernes Oak | Trees
On arrival crew isolated supply. Due to damage to POA supply left off until REC had repaired damage. | 8 CELLANA COURT, PORTLAND VIC 3305 | 30093294 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer called to say they had brought down a service wire with an excavator at the incident location. On arrival the crew found that a worker from Portland Precision Engineering at 7 Cellana Crt, had gone over the road to 8 Cellana Crt to borrow an excavator. When the worker was driving out of the driveway, he had boom raised, and it contacted the overhead 3 phase LV service cable. The operator remained in the excavator until the crew arrived. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | PLD006 | Excavator while traversing driveway became entangled in service line | Damage to network assets | 14/02/2019 16:44 |  |  | 12245 | Commercial |  | 20190228PWA_01 | Infrastructure (network-based) | -38.3648 | 141.623 | 1 | Powercor | Report | 15357 | 0.036648 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
On arrival crew isolated supply and carried out repairs. | 2768 KULKYNE WAY, NANGILOC VIC 3494 | 32149834 |  |  |  | Overheated connection |  |  |  | CFA called reporting grass fire at incident location. On arrival crew found fire of approx. 1000 m2 and part of the burnt area was under our pole. Insulation between D clamp and isolator had melted on LV cables, fallen debris ignited grass below. CFA and State Forest Management crews in attendance. There were no injuries or third party property damage. | Conductor (insulated) | 2 | 2 | 2 |  | RCT013 | Overheated connection between LV islolator and D clamp | Grassfire | 27/02/2019 18:13 | 1 | Small: 10 - 1000 sq.m | 12246 | Forest - native (not park) |  | 20190228PWA_02 | Infrastructure (network-based) | -34.485 | 142.3634 | 1 | Powercor | Report | 15358 | 0.039846 | Low voltage AC (<1kV) | Mildura Airport | 3494 | Nangiloc | Connection
On arrival crew isolated supply and carried out repairs | 42 ARNOLDS AND SMITHS ROAD, WOMBELANO VIC 3409 | 32095549 | Crane, excavator or other construction/farming equipment | [6 empty] | Customer - Ms Pamela Burbrer - reported the conductor down at the incident location - reported it as "Excavator has hit service, lowering the wire, no injuries. Overhead service line Attached at both ends. On arrival the fault crew found SWER conductor had been dislodged from P.67 & P.68 of MIGA Spur line, and was still alive. The conductor measured 4.5m above ground where it crossed Arnolds and Smiths Road, and was suspended 100mm above stubble in paddock between P.67 & P.68 MIGA Spur Line. There were no injuries to the excavator operator, no ground fire and no other damage. | Conductor (bare) | 2 | 2 | 2 |  | HSM004 | Excavator travelling across paddock struck SWER conductor | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/02/2019 17:50 |  |  | 12248 | Agricultural |  | 20190228PWA_04 | Infrastructure (network-based) | -36.9624 | 141.6273 | 1 | Powercor | Report | 15363 | 0.029262 | 12.7kV AC (SWER) | Horsham Aerodrome | 3409 | Wombelano | Vehicle
Crew attended and replaced mains box and aerial services | 13 REDFEARN COURT, CORIO VIC 3214 | 30071844 |  | Heat |  | Electrical overload;Overheated connection |  |  | 2 | customer reported no supply and pole on fire. Attending crew found fused mains box on pole had overheated, burnt service cables and charred pole. | Cable | 0 | 0 | 0 |  | CRO013 | overheated connection | Pole-top fire;Loss of supply | 43527.1243 | 1 | Negligible: no ground fire | 12252 | Residential |  | 20190304PWA_01 | Infrastructure (customer connection) | -38.0819 | 144.3411 | 1 | Powercor | Report | 15374 | 0.0132 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
On arrival crew isolated supply and carried out repairs | 4235 LALBERT-KERANG ROAD, LALBERT VIC 3542 | 30019603 | Blown detritus | Wind | [5 empty] | Report of wire has blown into conductors started fire at incident location. Crew found that a Willy Willy had blown some old tangled fencing wire onto the SWER overhead conductor. There was a ground fire of approx. 8000 sq m, there was no reported injuries, no asset damage. | Conductor (bare) | 2 | 2 | 2 |  | SHL001 | fence wire blown onto line by wirly wind | Grassfire | 28/02/2019 14:41 | 1 | Medium: 1000 sq.m - 10 ha | 12253 | Agricultural |  | 20190304PWA_02 | Infrastructure (network-based) | -35.6769 | 143.4027 | 1 | Powercor | Report | 17602 | 0.031666 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3542 | Lalbert | Other
On arrival crew isolated supply and carried out repairs. | 765 DHURRINGILE ROAD, TOOLAMBA WEST VIC 3614 | 33097279 |  | Fallen | [5 empty] | Reports received of small grass fire. On arrival crew found a limb had fallen through conductors between poles 9 & 10 at incident location. Disturbance to Conductors caused a small grass fire between poles 6 & 7. There were no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MNA021 | Vegetation: Trees Incident | Grassfire | 43468.8458 | 1 | Medium: 1000 sq.m - 10 ha | 12255 |  |  | 20190304PWA_03 | Infrastructure (network-based) | -36.4816 | 145.2413 | 1 | Powercor | Report | 15377 | 0.021172 | 22kV AC | Shepparton Airport | 3614 | Toolamba West | Trees
Fault crew dispatched, candled EDO fuse replaced and supply restored | 205 LINDNERS ROAD, JEERALANG JUNCTION VIC 3840 | LIS2616504 |  |  |  | Candled fuse |  |  |  | E0012584 - report of candling fuse | EDO fuse | 0 | 0 | 0 |  | MWT31 | Candled HV EDO fuse only and no evidence of ground fire | Pole-top fire | 43499.3396 | 1 | Negligible: no ground fire | 12264 |  |  | 20190304SPN_07 | Infrastructure (network-based) | -38.3521 | 146.4376 | 2 | AusNet Services Distribution | Report | 17796 | 0.01948 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Jeeralang Junction | Fuse
Fault crew dispatched to investigate and carry out repairs. Repair works for fallen ABC mains required converting LV ABC AT1 to (N) LV ABC Strain. | 29 RIVER AVENUE, PLENTY VIC 3090 | LIS923074 |  |  |  | Electrical overload |  |  |  | E0012617 - report of pole fire | Conductor (ABC) | 0 | 0 | 0 |  | ELM15 | An ABC mains connection clamp failed due to high electrical demand causing ABC XLPE insulation to melt and drip on ground. The ABC overhead mains also broke and fell on ground. ABC repaired and supply restored | Pole-top fire | 43527.7708 | 1 | Localised: less than 10 sq.m | 12268 |  |  | 20190304SPN_08 | Infrastructure (network-based) | -37.6665 | 145.1213 | 2 | AusNet Services Distribution | Report | 18284 | 0.017648 | Low voltage AC (<1kV) | Essendon Airport | 3090 | Plenty | Connection
The faults crew isolated teh transformer HV and LV and proceeded to replace the burnt red phase transformer isolator conductor from the transformer to the reticulation along with the neutral conductor under Access Authority conditions. They also replaced a single phase grey twisted service that supplied 25 Delbeattie Drive with a XLPE service and supply was restored to the customers upon completion. . | 34 DALBEATTIE DRIVE, CLARINDA VIC 3169 |  |  | Heat |  | Electrical breakdown |  |  | 2 | Caller reports the transformer directly outside the property has caught fire. The electricity supply to the house is okay and they have contacted emergency services. The faults crew found the transformer wasn't on fire upon arrival, but identified the neutral and red phase transformer isolator conductors had been rubbing together for a long period of time at "Dalbeattie-Tatiara" pole type substation. | Conductor (insulated);Pole mounted | 0 | 0 | 0 |  | CDA 22 | The neutral and red phase transformer isolator conductors had been rubbing together for a long period of time at "Dalbeattie-Tatiara" substation. | Pole-top fire | 28/02/2019 18:02 | 1 | Negligible: no ground fire | 12263 | Roadway |  | 20190304UTD_01 | Infrastructure (network-based) | -37.9365 | 145.0995 | 1 | United Energy Distribution | Report | 15390 | 0.025414 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clarinda | Conductor
A fault crew and an EIO were dispatched to site to investigate. The fault crew disconnected supply at the pole end. The EIO attended the next day as there was no access to site on the day the incident was reported. To enable investigation to occur, the supply was reconnected at the pole. On reconnection, the crew noticed arcing marks on the neutral conductor at the pole. All testing passed and supply was left on. | 701 MELBOURNE ROAD, SORRENTO VIC 3943 | 1306520 |  |  |  | Neutral fault |  | Phase to earth | 1 | UE received a report of tingles/shocks being experienced from pipes on a property under renovation. | Connector/termination | 0 | 0 | 0 |  |  | The supply was disconnected prior to investigation. On reconnection, it was noticed that the neutral conductor had arcing marks. It is likely that the incident was caused by a loose neutral connection of the service wire at the pole end. | Minor shock | 43805.7014 |  |  | 13898 | Residential |  | 20190617UTD_02 | Infrastructure (network-based) | -38.3508 | 144.746 | 1 | United Energy Distribution | Report | 17343 | 0.028277 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Connection
made safe and replaced isolator. caused by burnt out transformer lv isolators. No signs of ground fire. | 118 GEHREYS LANE, KILMORE VIC 3764 | lis 4716905 |  |  |  | Defective component |  |  | 2 | Pole fire - caused by burnt out transformer lv isolators. | Disconnector/isolator | 0 | 0 | 0 |  | KMS12 | defective transformer lv isolator | Pole-top fire | 18/06/2019 17:40 | 1 | Negligible: no ground fire | 13908 |  |  | 20190619SPN_01 | Infrastructure (network-based) | -37.3232 | 144.9422 | 2 | AusNet Services Distribution | Report | 18322 | 0.030986 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3764 | Kilmore | Connection
The REC is going to re-instate his existing consumer mains into the metering position and have his LEI return to provide a new COES. The REC is going to call Network Connections to arrange an After Hours appointment for the M&S crew to return to test and reconnect the customer under the existing overhead supply and customer mains arrangement. The M&S crew have carded and notified the other customers to re-attend Tuesday 25 June 2019 to complete the neutral screen service upgrades and also complete the customer mains upgrade Truck Appointment | 119 CUMBERLAND ROAD, PASCOE VALE VIC 3044 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address today for an 11.00am Truck Appointment for a customer initiated 1phase overhead supply, consumer mains, meter panel, switchboard, earthing upgrade/rewire When the M&S crew arrived they found the REC had removed the service fuse, disconnected and cut away the existing consumer mains, removed the existing meter panel and distributors electricity meter and customer switchboard and has installed a new FOLCB, consumer mains, meter panel and switchboard in the original metering/switchboard location and the installation signed off with a prescribed COES on site. Unfortunately the customer overhead supply was connected to a small SEC junction box that was also supplying 2 other customers and was being serviced from a 3phase neutral screen road crossing. Photos and COES are attached in the "Notes & Findings" section | Smart meter;Connection box | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/06/2019 11:00 |  |  | 13915 |  |  | 20190624JEM_01 | Infrastructure (customer connection) | -37.7282 | 144.9388 | 1 | Jemena | Report | 17389 | 0.016968 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
Supply isolated and repairs made Crew replaced transformer LV isolators, 2 x krone switches and transformer LV leads. | 129 RENNIE STREET, COBURG VIC 3058 | A073199 |  |  |  | Overheated connection |  |  | 2 | Asset failures resulting in asset fire (no grass/vegetation fire) MUCHELL-RENNIE substation krone isolator switch melted and has damaged wiring from transformer to isolator and fused krone box Photos are attached in the "Notes & Findings" section | Any other type | 0 | 0 | 0 |  | CS09 | Krone isolator had a hot connection, which melted plastic and burnt transformer LV dropper from transformer to switch | Other electricity related | 25/06/2019 19:13 | 1 | Negligible: no ground fire | 13919 | Residential |  | 20190625JEM_01 | Infrastructure (network-based) | -37.7516 | 144.9785 | 1 | Jemena | Report | 17742 | 0.024267 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Connection
Fault crew dispatched to investigate. Damaged service cable in pit repaired and new IPCs installed. All tests carried out and passed following repairs and supply restored. | 144 MAROONDAH HIGHWAY, RINGWOOD VIC 3134 | LIS5825894 |  |  |  | Fault on customer installation;Not built/maintained to design |  | Phase to earth |  | E0021906 - customer reported his dog received an electric shock while walking over an electrical service pit | Services cable;Services pit | 0 | 0 | 0 |  | RWT14 | Member of the public reported their dog received an electric shock whilst walking over the electrical service pit. Blue phase conductor of service cable supplying shop found to be damaged in the pit with a 'nick' in the insulation. Fault crew removed the damaged section of service cable and re-terminated the cable using IPCs. | Shock to livestock, pet or companion animal | 26/06/2019 18:26 |  |  | 13928 | Commercial |  | 20190627SPN_02 | Infrastructure (network-based) | -37.8139 | 145.2332 | 1 | AusNet Services Distribution | Report | 17405 | 0.016252 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Ringwood | UG Cable
Fault crew dispatched and corroded neutral connection repaired. | 24 LEE PARADE, LEONGATHA VIC 3953 | LIS2003300 |  |  |  | Corrosion |  |  |  | E0021899 - Customer was showering when they felt a tingle on the palm of their hand and fingers. They experienced further tingles when they touched the tap to turn it off. | Connector/termination | 0 | 0 | 0 |  | LGA22 | Fault crew attended and found a corroded neutral connection. All tests carried out and passed following repairs and supply restored | Minor shock | 26/06/2019 16:18 |  |  | 13932 | Residential |  | 20190628SPN_02 | Infrastructure (customer connection) | -38.4819 | 145.9537 | 1 | AusNet Services Distribution | Report | 17409 | 0.015065 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha | Connection
Isolated section and made safe, issued work authority to make repairs | 48 RUTHERFORD ROAD, VIEWBANK VIC 3084 | A120357 |  |  |  | Overheated connection |  |  | 1 | Live high voltage overhead bare conductor fell on ground due to failed ampact connector. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | nh0-008 | The primary cause is an ampact connector failure, which is not a standard connector for copper to copper connection as opposed to split bolt connector. The heat generated by high resistance ampact put heat / strain on insulator causing insulator to fail. Pole A120357. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43472.4056 |  |  | 13942 | Residential |  | 20190701JEM_02 | Infrastructure (network-based) | -37.7415 | 145.09 | 1 | Jemena | Report | 17420 | 0.040751 | 22kV AC | Essendon Airport | 3084 | Viewbank | Connection
Crew re-terminated the existing O/H Service Cable at the new FOLCB | 165 MCCALLUM STREET, SWAN HILL VIC 3585 | 32158622 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom showering when she believes she experienced a minor electric shock as she made simultaneous contact with her hand on the metallic taps and her bare feet whilst standing on the metallic waste outlet in the shower base. | Customer installation | 0 | 0 | 0 |  | SHL008 | Corroded O/H Service Neutral Conductor termination in the Customers FOLCB located at the POA. | Minor shock | 43775.4167 |  |  | 13938 | Roadway |  | 20190701PWA_03 | Infrastructure (customer connection) | -35.341 | 143.5457 | 1 | Powercor | Report | 17415 | 0.036259 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
On arrival crew isolated supply and carried our repairs | BADMAN, 7640 MALLEE HIGHWAY, PANITYA VIC 3512 | 31021260 |  |  |  | Leakage |  |  |  | Customer reported low conductors and pole fire. On arrival crew found crossarm burnt in half. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 21/04/2019 12:39 | 1 | Negligible: no ground fire | 13941 | Agricultural |  | 20190701PWA_05 | Infrastructure (network-based) | -35.2325 | 141.0208 | 1 | Powercor | Report | 17419 | 0.020956 | 22kV AC | Mildura Airport | 3512 | Panitya | Crossarm
Supply isolated repairs carried out | 3171 ONTARIO AVENUE, MILDURA VIC 3500 | 30099184 |  |  |  | Leakage |  |  |  | Report received of a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MBN032 | Excessive leakage current | Pole-top fire | 26/04/2019 16:18 | 1 | Negligible: no ground fire | 13949 | Roadway |  | 20190702PWA_04 | Infrastructure (network-based) | -34.2258 | 142.0934 | 1 | Powercor | Report | 17430 | 0.035372 | 22kV AC | Mildura Airport | 3171 | Mildura | Crossarm
Single bay of O/H HV conductor was isolated and repaired (sleeved) and supply restored. | 8 MIMOSA AVENUE, EMERALD VIC 3782 | LIS400429 |  | Alive | [5 empty] | E0022172 - Tree has fallen onto and brought down O/H HV conductors between poles LIS400428 and LIS400429 | Conductor (bare) | 0 | 0 | 0 |  | BGE22 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43472.7035 |  |  | 13953 |  |  | 20190702SPN_01 | Infrastructure (network-based) | -37.9343 | 145.47 | 1 | AusNet Services Distribution | Report | 17434 | 0.039905 | 22kV AC | Moorabbin Airport | 3782 | Emerald | Trees
Switching to isolate the impacted pole was undertaken and the damaged fuse unit was replaced under access authority conditions. | 46 SANDY POINT ROAD, SOMERS VIC 3927 | 1108920 |  |  |  | Candled fuse |  |  | 1 | ACR MT7712 operated by reclosing for a downstream fault. The subsequent patrol by a faults crew found fuse switch unit MT0513 with a damaged centre phase Boric Acid fuse unit and the red phase fuse had operated. The damaged centre phase fuse had candled. | Boric acid | 0 | 0 | 0 |  | HGS21 | Animal Incident | Hung-up fuse only;Plant/equipment | 43622.6951 | 1 | Negligible: no ground fire | 13951 | Roadway |  | 20190702UTD_02 | Infrastructure (network-based) | -38.3829 | 145.1708 | 1 | United Energy Distribution | Report | 18141 | 0.014991 | 22kV AC | Moorabbin Airport | 3927 | Somers | Fuse
On arrival crew isolated supply and carried out repairs. | 1180-1196 GISBORNE-MELTON ROAD, TOOLERN VALE VIC 3337 | 30322439 | Copper theft | [6 empty] | Following a report of a public light not working a fault crew found that approximately 200mtrs of underground cable had been stolen from the incident location. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN012 | Copper theft | Damage to network assets | 25/06/2019 0:49 |  |  | 13958 |  |  | 20190703PWA_03 | Infrastructure (network-based) | -37.6092 | 144.5907 | 1 | Powercor | Report | 17449 | 0.0070266 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
Fault crew dispatched and candled HV Fuse replaced | 6 BACK CREEK ROAD, YACKANDANDAH VIC 3749 | LIS5218276 |  |  |  | Candled fuse |  |  |  | E0021950 - report of candled BV HV fuse | Boric acid | 0 | 0 | 0 |  | WOTS11 | Candled Boric Acid HV fuse | Pole-top fire | 27/06/2019 9:45 | 1 | Negligible: no ground fire | 13963 |  |  | 20190704SPN_01 | Infrastructure (network-based) | -36.3187 | 146.8416 | 1 | AusNet Services Distribution | Report | 17455 | 0.0081771 | 22kV AC | Wangaratta Aero | 3749 | Yackandandah | Fuse
Fault crew attended and isolated the LV circuit, and replaced the pillar. Supply was restored on completion. | 8 FARRER COURT, DONCASTER EAST VIC 3109 | 7063437 |  |  |  | Overheated connection |  |  | 2 | UE received a report from a customer that a pillar in front of their property was on fire. | LV Pillar | 0 | 0 | 0 |  |  | It is likely that an underground cable connection overheated and failed in the LV pillar. | Plant/equipment | 22/06/2019 21:43 | 1 | Negligible: no ground fire | 13961 | Roadway |  | 20190704UTD_02 | Infrastructure (network-based) | -37.7741 | 145.148 | 1 | United Energy Distribution | Report | 17452 | 0.020409 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Connection
crew attended and isolated supply. repairs deferred to daylight | OLD COACH ROAD, BEECH FOREST VIC 3237 | 32065417 | Working too close to overhead lines | [5 empty] | 1 | Tree clearers report wires down at pole 370 Gellibrand . tree clearers safe. Attending crew found pine tree contacted line during harvesting operations had brought down 4 spans of HV conductor. | Conductor (bare) | 0 | 0 | 0 |  | CLC006 | apparent plantation harvesting | No Go Zone (contact);Damage to network assets | 43562.6451 |  |  | 13966 | Forest - plantation |  | 20190705PWA_01 | Infrastructure (network-based) | -38.6578 | 143.5818 | 1 | Powercor | Report | 17459 | 0.019391 | 22kV AC | Avalon Airport | 3237 | Beech Forest | Trees
fault crew replaced the corroded neutral bridge conductor at the pole | 9 THE BROADWAY, ALTONA NORTH VIC 3025 | 30109895 |  |  |  | Corrosion |  |  | 2 | Robert placed his hand into the outdoor spa to test the water temperature and received an electric shock when he made simultaneous contact between the water in the spa with his hand and the general mass of earth with his feet. | Dropper/bridge | 0 | 0 | 0 |  | BLT030 | Corroded Neutral Bridge at pole | Minor shock | 25/05/2019 18:00 |  |  | 13972 | Residential |  | 20190705PWA_05 | Infrastructure (network-based) | -37.8351 | 144.8625 | 1 | Powercor | Report | 17465 | 0.020807 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Connection
Section was left isolated pending investigation Investigation was subsequently conducted by Jemena Works Practices. | 345 OAKLANDS ROAD, OAKLANDS JUNCTION VIC 3063 | 11463522 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | While out to repair a wire down in the area, work crew spotted a set of HV fuses on Oaklands Road that had operated. On further investigation, he found an excavator on the block of land at 345 Oaklands Road, Oaklands Junction, which had contacted the HV overhead line running to the 25kVA pole-mounted substation on the property (OAKLANDS RD-P41E2) There was no owner's name on the excavator. Although there was no damage to HV overhead assets, but there were visible burn marks on the HV overhead line. It is unknown when the excavator contacted the HV overhead line, as there were no customer calls or AMI meter activity, as the AMI meters registered to the address were deactivated in 2014. The crew measured the HV overhead height at 5.9 metres. Photos are attached in the "Notes & Findings" section. There is no additional information of the responsible third party. | Conductor (bare) | 0 | 0 | 0 |  | COO11 | Excavator contacted high voltage overhead line | No Go Zone (contact) | 43684.7049 |  |  | 13987 | Roadway |  | 20190708JEM_02 | Infrastructure (network-based) | -37.6034 | 144.8408 | 1 | Jemena | Report | 17486 | 0.014932 | 22kV AC | Melbourne Airport | 3063 | Oaklands Junction | Vehicle
Fault Crew replaced the existing corroded O/H Neutral Screened Service Cable | 48 ASHBOURNE STREET, HERNE HILL VIC 3218 | 30074904 |  |  |  | Corrosion |  |  | 2 | person as in the Kitchen and received an electric shock when she made simultaneous contact with her hands on both metal taps whilst standing on the conductive floor. | Service conductor | 0 | 0 | 0 |  | GL014 | Corroded Neutral Screened Conductor of an O/H Neutral Screened Service Cable. | Minor shock | 25/06/2019 17:00 |  |  | 13986 | Residential |  | 20190708PWA_02 | Infrastructure (customer connection) | -38.133 | 144.3234 | 1 | Powercor | Report | 17484 | 0.03231 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Herne Hill | OH Cable
Fault crew dispatched to investigate and make safe. Damage was located at pole 5108319. A birds nest was found burnt on top of the gas switch at 5108319, and the surge arrestors on the gas switch were also found to be damaged and blackened. Debris were cleared from from the gas switch and surge arrestors were replaced. | 1 WARATAH DRIVE, WANGARATTA VIC 3677 | LIS5119925 |  | Lightning | [5 empty] | Report of pole fire: burnt bird nest on top of the Gas Switch caused by lightning. Surge arrestors were also damaged. Refer to photos. | Surge diverter | 0 | 0 | 0 |  | WN2 | Caused by lightning | Pole-top fire | 43653.8174 | 1 | Negligible: no ground fire | 13975 |  |  | 20190708SPN_01 | Infrastructure (network-based) | -36.3383 | 146.3038 | 2 | AusNet Services Distribution | Report | 18882 | 0.032438 | 22kV AC | Wangaratta Aero | 3677 | Wangaratta | Pole
Fault crew dispatched and candled BA HV fuse replaced | 335 HODGES ESTATE ROAD, ELLASWOOD VIC 3875 | LIS1605515 |  |  |  | Candled fuse |  |  |  | Candled fuse reported | Boric acid | 0 | 0 | 0 |  | BDL44 | Boric Acid HV fuse candled. No evidence of ground fire | Pole-top fire | 30/06/2019 13:59 | 1 | Negligible: no ground fire | 13981 |  |  | 20190708SPN_07 | Infrastructure (network-based) | -37.7884 | 147.5687 | 1 | AusNet Services Distribution | Report | 17856 | 0.0076169 | 22kV AC | Bairnsdale Airport | 3875 | Ellaswood | Fuse
On arrival crew carried out repairs | PT ADDIS FLOWER FARM, 180 POINT ADDIS ROAD, BELLS BEACH VIC 3228 | 30063422 | Working too close to underground cables | [6 empty] | A contractor dug up HV earthing at the incident location. Upon arrival, a Powercor crew found that the earthing had been damaged by the contactor's excavator. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | WPD021 | Excavation works by contractor using excavator | Damage to network assets | 28/06/2019 14:00 |  |  | 13998 | Roadway |  | 20190715PWA_01 | Infrastructure (network-based) | -38.3868 | 144.2463 | 1 | Powercor | Report | 17499 | 0.035532 | Earthing cable | Avalon Airport | 3228 | Bells Beach | Dug up
On arrival crew confirmed isolation | 27 KYLE ROAD, ALTONA NORTH VIC 3025 | 30254605 | Vandalism;Copper theft | [6 empty] | Site supervisor Jason (ph 0403144268) calling to report that copper theft on pole number 735916, looks like they have swung the fuses off the pole and stolen all the cable from transformer to the sub and also stolen equipment in the substation. fence appears to have been cut. access okay. There was no fire, no reported injuries. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | BLT017 | Copper theft | Damage to network assets | 43472.4306 |  |  | 14000 | Industrial |  | 20190715PWA_03 | Infrastructure (network-based) | -37.8297 | 144.8569 | 1 | Powercor | Report | 17501 | 0.00042593 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3025 | Altona North | Other
Crew advised all 3 service fuses at pole end had operated. Confirmed site safe and underground crew to conduct repairs. | 7A BORRIE STREET, RESERVOIR VIC 3073 |  | Working too close to underground cables | [5 empty] | 2 | Construction of new units at 57 Miranda Rd Reservoir required new storm water pipe to be installed in easement at 9 Borrie St Reservoir. While conducting underground boring the underground service cable was damaged (see attched photos). Note: Construction crew and boring machine operator not on site when Jemena faults crew arrived. | Cable | 0 | 0 | 0 |  |  | Third party damage due to works underway in the nature strip. Crew advised that borer had made contact with LV underground cable from pole to pit. | No Go Zone (contact) | 16/07/2019 16:52 |  |  | 14010 | Residential |  | 20190716JEM_04 | Infrastructure (network-based) | -37.7075 | 145.0198 | 1 | Jemena | Report | 17518 | 0.016192 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Dug up
Fault crew and LEI dispatched to investigate. Supply isolated and properties inspected for damage. Damaged meters replaced and supply retored following tests being carried out and passed. | 314-316 YARRA ROAD, WONGA PARK VIC 3115 | LIS1203569 |  | Blown branch/vegetation |  | Conductor clashing |  |  | 2 | Tree branch has blown onto HV and LV conductors resulting in HVI | Conductor (bare) | 0 | 0 | 0 |  | CPK11 | Vegetation: Trees Incident | HV injection | 13/07/2019 13:15 |  |  | 14019 | Residential |  | 20190717SPN_02 | Infrastructure (network-based) | -37.7556 | 145.2727 | 1 | AusNet Services Distribution | Report | 17535 | 0.039126 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3115 | Wonga Park | Trees
On arrival crew carried our repairs | 41-53 ABEY ROAD, COBBLEBANK VIC 3338 | 30336498 | Copper theft | [6 empty] | Customer approached the crew, while they were on another job and advised that pit lids removed & cables exposed . On arrival, the crew found LV underground cables from LIS 842955 to 842966 and also between LIS 842973 to 842968 were stolen. There was no fire. no reported injuries or third party property damage | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43623.8333 |  |  | 14025 | Roadway |  | 20190719PWA_03 | Infrastructure (network-based) | -37.7058 | 144.5962 | 1 | Powercor | Report | 17544 | 0.024706 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
On arrival crew isolated supply and carried out repairs. | 3 LOWE STREET, OCEAN GROVE VIC 3226 | 33043236 |  | Bird |  |  |  |  | 1 | A customer saw sparks coming from pole with streetlight on it, first pole in Lowe St. Power went off momentarily... A crew was dispatched to investigate. On arrival the crew identified a live HV conductor laying on the ground between P1 (LIS-7141) and P2 (LIS-787357), causing burns to the green grass. The crew found a deceased bird believed to be the likely cause. It was suspected that the bird had bridged over two HV phases, causing 1 phase helical termination to fail and conductor to fall to ground. There were no reported injuries or third party property damage. The fire brigade and police had the road blocked to keep the public away from the danger. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | DDL011 | Bird Incident | Grassfire | 19/07/2019 17:48 | 1 | Medium: 1000 sq.m - 10 ha | 14029 | Roadway |  | 20190722PWA_02 | Infrastructure (network-based) | -38.2594 | 144.5349 | 1 | Powercor | Report | 17658 | 0.010817 | 22kV AC | Avalon Airport | 3226 | Ocean Grove | Animal
On arrival crew isolated supply and made site safe. | 120 GRUBB ROAD, OCEAN GROVE VIC 3226 | 31011411 | Working too close to underground cables | [6 empty] | A contractor reported a low voltage cable had been dug up on a development site to a Powercor employee. Upon arrival, a crew found that the UG service had been damaged by an excavator. The cable was left energized and exposed behind barricading. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | DDL011 | land scrapping for new estate | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43776.5833 |  |  | 14036 | Roadway |  | 20190722PWA_05 | Infrastructure (customer connection) | -38.2455 | 144.5379 | 1 | Powercor | Report | 17557 | 0.0013391 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Dug up
EAP issued and repairs carried out. Approximately 3 metres of 3/2.75 steel conductor replaced. New Steel D loop fitted where Cu/Al was installed and fuse dropper reattached. Other connections check ok and supply was restored | 2 WILLOWMAVIN ROAD, KILMORE VIC 3764 | LIS 47125143; FLOC: DL-BK007-0047125143 |  |  |  | Fatigue |  | Phase to earth | 0 | E0023172 - HV conductor to ground. Crew reported that fuse blown at SE253 and live HV conductors on ground west of LIS47125143. | Conductor (bare) | 0 | 0 | 0 |  | SE 253 | Steel conductor failed underneath Cu/Al universal clamp. The HV conductor broke clear on the load side of fuse pole 47125143 and fell to the ground. This type of connection is no longer standard practice. | Loss of supply | 43776.9319 |  |  | 14033 |  |  | 20190722SPN_02 | Infrastructure (network-based) | -37.2812 | 144.9495 | 1 | AusNet Services Distribution | Report | 17572 | 0.0010671 | 22kV AC | Wallan (Kilmore Gap) | 3764 | Kilmore | Conductor
On arrival crew isolated supply and carried out repairs | 702 FOOTSCRAY ROAD, WEST MELBOURNE VIC 3003 | 30543422 | Working too close to underground cables | [6 empty] | Customer contractor reported they have dug up and damaged the conduit and underground cable at the above incident. Upon crew arrival, they found that a white conduit was damaged and a cable exposed. There was no reported shock or injuries. | Cable | 2 | 2 | 2 |  | DA026 | contractor carrying out excavation works | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/07/2019 11:17 |  |  | 14044 | Roadway |  | 20190723PWA_02 | Infrastructure (network-based) | -37.807 | 144.9095 | 1 | CitiPower | Report | 17566 | 0.020803 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Dug up
Fault crews attended and undertook emergency switching to isolate the faulty section. Police were on site with the SES and they cleared the tree off the lines. The fault crews repaired the lines as well as replacing a damaged LV cross-arm, and issued defect notices to the neighbouring customers who sustained damage to their POS when the tree fell on the lines. | 15 SANDGATE AVENUE, FRANKSTON VIC 3199 | 3314579 |  | Wind;Fallen |  |  |  |  | 0 | UE received reports of a tree falling over power lines with lines hanging low. On attendance, fault crews found live LV conductors on the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43745.8806 |  |  | 14041 | Roadway |  | 20190723UTD_02 | Infrastructure (network-based) | -38.1631 | 145.142 | 1 | United Energy Distribution | Report | 17563 | 0.033296 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Trees
UE dispatched a faults crew. On attendance, the crew isolated the cable at the pole, and an underground crew undertook repairs to the cable. | 19 FREDERICK STREET, DONCASTER VIC 3108 |  | Working too close to underground cables | [5 empty] | 2 | UE received a report of an underground cable being dug up by a water company. A third party plumbing contractor undertaking excavation works in the footpath had dug up a underground pole to pit LV cable. | Cable | 0 | 0 | 0 |  |  | A third party plumbing contractor undertaking excavation works in the footpath dug up the underground cable. There was no No Go Zone request associated with the excavation works. | Damage to network assets | 19/06/2019 11:00 |  |  | 14051 | Roadway |  | 20190724UTD_05 | Infrastructure (network-based) | -37.7895 | 145.1263 | 1 | United Energy Distribution | Report | 17575 | 0.012234 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | Dug up
Fault Crew replaced the existing Service Connection Box on the building facade and reterminated the existing Service Cables | 129 MAIN STREET, STAWELL VIC 3380 | 30223477 |  |  |  | Corrosion |  |  | 2 | Plumber engaged by GWM Water was replacing a Water Meter Isolation Tap at the property when he received an electric shock as he made simultaneous contact between his hand on the metallic Water Meter and his knees while kneeling on the ground. | Connector/termination | 0 | 0 | 0 |  | STL005 | Corroded Service Neutral Conductor termination of a 4 Core Flat Rubber Shop Veranda Service Cable | Minor shock | 43806.5833 |  |  | 14076 | Roadway |  | 20190730PWA_02 | Infrastructure (customer connection) | -37.0557 | 142.7816 | 1 | Powercor | Report | 17616 | 0.035867 | Low voltage AC (<1kV) | Horsham Aerodrome | 3380 | Stawell | Connection
On arrival crew isolated supply and carried out repairs. An LEI inspected premises for HVI. | 59 KEAM STREET, MILDURA VIC 3500 | 32147403 |  | Bird |  |  |  |  | 1 | Vicfire reported wires down at the incident location. On arrival the crew found that a HV conductor had fallen onto the white and blue phase of the open wire LV conductors below and then to the ground. There was evidence of the start of a birds nest on the cross-arm of the pole where the cable parted from, and the crew stated that they suspected a bird carrying a piece of wire may have been the cause. There was various damage caused to customer's premises by the HVI into the LV street mains. There were no reported injuries, and no reported fires. | Conductor (bare) | 2 | 2 | 2 |  | MDA022 | Bird Incident | HV injection;Loss of supply | 31/07/2019 8:38 |  |  | 14083 | Roadway |  | 20190801PWA_02 | Infrastructure (network-based) | -34.1997 | 142.1552 | 1 | Powercor | Report | 17626 | 0.0093854 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3500 | Mildura | Animal
Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a severely corroded neutral conductor supplying the neighbourâ€™s installation at the reticulation service pole junction box, the cover was missing. | 10 JOHN STREET, SEDDON VIC 3011 |  |  |  |  | Corrosion |  |  | 2 | Customer was repairing his metallic rear fence when he received an electric shock by making simultaneous contact with the metallic fence and the neighbourâ€™s garage gutter at 5 Margaret St. | Neutral screen;Service cable (insulated) | 2 | 2 | 2 |  |  | Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a severely corroded neutral conductor supplying the neighbourâ€™s installation at the reticulation service pole junction box, the cover was missing. This condition caused current to flow through the installation MEN connection, main earthing conductor and earthing system. This increased impedance to the flow of the installation return current through the general mass of earth and the earthing system was sufficient to cause a voltage rise of 45volts on the earthing system and metallic fixtures including the guttering which was in contact with the earthing system. | Minor shock | 43624.7083 |  |  | 14089 | Residential |  | 20190807JEM_01 | Infrastructure (customer connection) | -37.8034 | 144.8887 | 1 | Jemena | Report | 17633 | 0.011925 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Seddon | OH Cable
Fault crew attended and replaced the stolen LV earth at the sub pole | 1625 STUMPY GULLY ROAD, MOOROODUC VIC 3933 | 1103763 | Copper theft | [5 empty] | 2 | An asset inspector reported that an earth at a pole substation had been cut and stolen. | Earth/earthing | 2 | 2 | 2 |  | MTN22 | Cause was copper theft by unknown persons. | Damage to network assets | 25/07/2019 8:40 |  |  | 14093 | Roadway |  | 20190808UTD_01 | Infrastructure (network-based) | -38.227 | 145.1343 | 1 | United Energy Distribution | Report | 17638 | 0.0068356 | Earthing cable | Moorabbin Airport | 3933 | Moorooduc | Other
Pole replaced | 292 - 296 Princes Highway Corio 3214 | 30268929 |  |  |  | Leakage |  |  |  | Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | FNS021 | Excessive leakage current | Pole-top fire | 43745.9042 | 1 | Negligible: no ground fire | 14098 | Roadway |  | 20190809PWA_01 | Infrastructure (network-based) | -38.0765 | 144.3692 | 1 | Powercor | Report | 17643 | 0.025097 | 22kV AC | Avalon Airport | 3214 |  | Pole
Fault crew dispatched and candled Fuse was replaced. Supply restored | 100 PATERNOSTER ROAD, COCKATOO VIC 3781 | LIS400246 |  |  |  | Candled fuse |  |  | 2 | reported HV fuse candling | Boric acid | 0 | 0 | 0 |  | BGE12 | Candled Boric Acid HV fuse | Pole-top fire | 43715.0625 | 1 | Negligible: no ground fire | 14101 | Agricultural |  | 20190809SPN_02 | Infrastructure (network-based) | -37.9489 | 145.4818 | 2 | AusNet Services Distribution | Report | 17646 | 0.0040185 | 22kV AC | Moorabbin Airport | 3781 | Cockatoo | Fuse
Fault crew dispatched. Candled fuse replaced with new and supply restored | 89 FAIRY DELL ROAD, MONBULK VIC 3793 | LIS1304731 |  |  |  | Candled fuse |  |  |  | Fuse candling reported | Boric acid | 0 | 0 | 0 |  | BGE24 | Candled BA HV fuse. No evidence of ground fire | Pole-top fire | 23/07/2019 10:02 | 0 | Negligible: no ground fire | 14104 | Roadway |  | 20190809SPN_04 | Infrastructure (network-based) | -37.8943 | 145.4168 | 2 | AusNet Services Distribution | Report | 17701 | 0.013233 | 22kV AC | Moorabbin Airport | 3793 | Monbulk | Fuse
SIte made safe repairs organised | 489 Boggy Gate rd Clarkefield 3439 | 32048331 | Vandalism;Copper theft | [6 empty] | Report regarding AIRSERVICES AUSTRALIA Site visit found meter vandalism, stolen and exposed cables at meter position, meter fallen on ground not sure if site if live or off supply, Crew required to attend and make site safe. Crew found underground cable has been stolen from pole to pit, previous thefts from same site, small pry bar and bottle of dish washing liquid left on site. There was no fire, no reported injuries. | Services cable;Meter board (including fuses) | 2 | 2 | 2 |  | GSB012 | copper theft and vandalism | Damage to network assets | 43593.5694 |  |  | 14118 | Commercial |  | 20190812PWA_02 | Infrastructure (network-based) | -37.4607 | 144.9177 | 1 | Powercor | Report | 17666 | 0.02252 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3439 |  | Other
Repairs organised | Saintly Dr, Truganina VIC 3029, Australia | 30356141 | Vandalism;Copper theft | [6 empty] | Project Manager reports thefts at multiple sites / pits on yet to be tied in Axiom estates. Advice recieved that count of 56 pits all up between the two proposed estates. Theft is significant. Thefts from low voltage pits in the following streets / drives. Peterpaul Way, Doreimus Drive, Schembri Drive, Saintly Drive and Pauljoseph Way. there was no fire, no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LVN024 | Copper theft and vandalism | Damage to network assets | 29/07/2019 10:00 |  |  | 14120 | Roadway |  | 20190812PWA_04 | Infrastructure (network-based) | -37.8029 | 144.7479 | 1 | Powercor | Report | 17668 | 0.019426 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Due to vandalism by an unknown person the meter terminal covers had been removed and cables cut, resulting in live copper conductors being left exposed. The attending LEI found it difficult to perform their duties while attending site due to the resident acting strangely. The resident was also repeatedly touching the metal meter box following being instructed to keep clear from it due to the potential dangers. At this stage, due to the circumstances supply to the installation was disconnected by the attending LEI by pulling the installations service fuse at the POA and a service truck was called to assist. Upon the service truck arriving to sight and following further investigation, the installation was deemed to be unsafe. The attending LEI instructed the service crew to remove the overhead supply to the installation and abolish the meter which had been tampered with. A defect letter was issued and the installation left off supply. | 9 BELLBRAE COURT, MEADOW HEIGHTS VIC 3048 |  | Vandalism | [5 empty] | 2 | The electric shock was received when the customer came in contact with exposed live meter terminals at the installations meter box. | Meter board (including fuses) | 2 | 2 | 2 |  | COO13 | Due to vandalism by an unknown person the meter terminal covers had been removed and cables cut, resulting in live copper conductors being left exposed. | Minor shock | 13/08/2019 21:24 |  |  | 14141 | Residential |  | 20190813JEM_01 | Infrastructure (customer connection) | -37.6571 | 144.917 | 1 | Jemena | Report | 17690 | 0.010362 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Meadow Heights | Other
Cable has been repaired, drain patched and conduit relocated. | 189 Barkers Rd, Kew VIC 3101, Australia | 30178372 |  |  |  |  | Ineffective planning/procedures/processes |  |  | Crew attended to discover that Boroondara Council had a blocked storm water drain, they tried to flush the drain which was unsuccessful. They then sent the root cutter up which could not get past the obstruction. On sending the camera up the drain they have discovered a CitiPower conduit and service cable have been installed through the drain. The cable and conduit were damaged by the Root Cutter attempting to clear the drain. The pole to pit was installed on the 05.02.2018 and activated about two weeks ago. No injury or fire resulted from this incident. | Services cable | 2 | 2 | 2 |  | Q010 | Electrical conduit installed in same position as drainage piping | Damage to network assets | 31/07/2019 16:00 |  |  | 14124 | Roadway |  | 20190813PWA_03 | Infrastructure (network-based) | -37.8144 | 145.0347 | 1 | CitiPower | Report | 17952 | 0.010414 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Other
Underground cable and kiosk isolated repairs made. | 8 STRUAN STREET, TOORAK VIC 3142 | 41105363 | Working too close to underground cables | [5 empty] | 1 | Following Feeder trip to Lockout, Crew attended and excavated underground cable, damage is consistent with having been contacted by a boring machine ( two conduits broken and cable failed). NBN contractors observed working in area. There was no fire, no reported injuries or third party property damage. | Cable | 0 | 0 | 0 |  | TK010 | Contractor carrying out directional boring | Loss of supply;Damage to network assets | 23/07/2019 14:40 |  |  | 14126 |  |  | 20190813PWA_05 | Infrastructure (network-based) | -37.8363 | 145.0133 | 1 | CitiPower | Report | 17674 | 0.015262 | 11kV AC | Essendon Airport | 3142 | Toorak | Dug up
crew replaced the corroded connector | 304 DANDENONG ROAD, ST KILDA EAST VIC 3183 | 30219180 |  |  |  | Corrosion |  |  | 2 | person received an electric shock when he simultaneously contacted the Metallic taps with his hand and the baths metallic waste with his foot | Aluminium twisted (grey) | 0 | 0 | 0 |  | BC013 | Corroded Neutral connector at pole | Minor shock | 24/07/2019 11:00 |  |  | 14135 | Residential |  | 20190813PWA_13 | Infrastructure (customer connection) | -37.8597 | 145.0047 | 1 | CitiPower | Report | 17683 | 0.034169 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | St Kilda East | Connection
Fault crews attended. They were advised by the fire authority that the pole top (capacitor) was on fire, but was not witnessed by the crew. The crew undertook emergency switching, and the pole top capacitor unit was emoved from service. | 221-231 HAMMOND ROAD, DANDENONG SOUTH VIC 3175 | 8830311 |  |  |  | Electrical breakdown |  |  | 1 | UE received a report from the fire authority of a sparking pole in Hammond Rd Dandenong Sth. On attendance, crew found a pole mounted capacitor had failed. | Pole mounted capacitor;Other | 0 | 1 | 0 |  | DSH23 | An internal electrical failure of the capacitor unit was the cause of this incident. | Plant/equipment | 43776.3979 | 1 | Negligible: no ground fire | 14131 | Roadway |  | 20190813UTD_01 | Infrastructure (network-based) | -38.0089 | 145.2068 | 1 | United Energy Distribution | Report | 17679 | 0.021557 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | AF Other
On arrival crew isolated supply and carried out repairs. | 2549 C164, Port Campbell VIC 3269, Australia | 32056249 |  |  |  | Overheated connection |  |  |  | A passer-by reported a pole on fire at the incident location. Upon arrival a Powercor crew found a melted fuse box on the pole. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | TRG003 | Moisture ingress | Pole-top fire | 43685.3285 | 1 | Negligible: no ground fire | 14146 | Roadway |  | 20190814PWA_02 | Infrastructure (network-based) | -38.602 | 143.0009 | 1 | Powercor | Report | 17695 | 0.014907 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3269 | Port Campbell | Connection
Site made safe, no repairs required | Footscray Rd, West Melbourne VIC 3003, Australia | 33111293 | Copper theft | [6 empty] | A crew attended the above indoor substation at the incident location and found that the LV bus bars had been stolen These were not energised three phase bus bars about 4m long. This section was not connected to the alive section of the substation. There was no fire, no reported injuries. | Indoor | 2 | 2 | 2 |  | DA026 | copper theft | Damage to network assets | 43685.3764 |  |  | 14149 |  |  | 20190814PWA_04 | Infrastructure (network-based) | -37.8075 | 144.9193 | 1 | CitiPower | Report | 17700 | 0.0029988 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
UE dispatched a fault crew and an EIO to investigate. The EIO undertook testing, with the NST failing and volts measured on the taps and neutral of 2.9V. The faults crew identified a connection issue in the connection box on the pole. The box and service cable were replaced, and subsequent testing passed with voltage measured of 0.2V. | 39 GOULD STREET, FRANKSTON VIC 3199 | 3309119 |  |  |  | Corrosion |  | Phase to phase | 1 | The UE network analytics identified abnormal voltage at this premise. On attendance by an EIO, the customer also advised that they experienced tingles from the taps in the shower. | Connection box;Service cable (insulated) | 0 | 0 | 0 |  |  | Cause was identified as a connection issue with the pole mounted connection box. | Minor shock | 43532.509 |  |  | 14144 | Residential |  | 20190814UTD_02 | Infrastructure (network-based) | -38.1325 | 145.1229 | 1 | United Energy Distribution | Report | 17693 | 0.02613 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
On arrival crew isolated supply and carried out repairs. | 640 Sandilong Ave, Irymple VIC 3498, Australia | 30095461 |  |  |  | Leakage |  |  |  | Report received of a pole fire at the incident location. On arrival crew found a crossarm had burnt in half. There was no HVI There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MDA023 | Excessive leakage current | Pole-top fire | 43777.3333 | 1 | Negligible: no ground fire | 14154 | Roadway |  | 20190815PWA_04 | Infrastructure (network-based) | -34.2219 | 142.1677 | 1 | Powercor | Report | 17710 | 0.0086157 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
On arrival crew isolated supply and carried out repairs | 133 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631 | 30128968 |  |  |  | Electrical overload;Overheated connection |  |  |  | Report received of a house fire at incident location. On arrival crew found fire extinguished and observed that the meter board had sustained fire damage. Crew was advised that customers gas heating had failed and they were running 4 x electric heaters in the house. There was no ground fire, no reported injuries. | Meter board (including fuses) | 2 | 2 | 2 |  | SHN024 | Customer induced overload | Meter board | 13/08/2019 20:29 | 1 | Negligible: no ground fire | 14159 | Residential |  | 20190816PWA_03 | Infrastructure (customer connection) | -36.3533 | 145.4314 | 1 | Powercor | Report | 17716 | 0.032439 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Grahamvale | Installation
Metering and Servicing crew disconnected the overhead service and made safe the installation The REC will be calling Network Connection to arrange an After Hours return visit to reconnect the customer to supply A new prescribed COES is required | 71 Leamington St, Reservoir VIC 3073, Australia | A065714 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crew attended this location (SO: 100101174854 NMI: 6001099479) for a single 9.30am Truck Appointment for a 1ph-1ph mains supply upgrade. When the crew arrived they found the REC had removed the service fuse, removed the existing customer mains, removed the distributors electricity meter and old metering panel and had removed the existing customer FOLCB which was still connected to our live overhead service and was just hanging at the point of attachment fascia location. The REC did not complete works within the allocated truck appointment time and the LEI did not sign and issue a prescribed COES. REC details are in the "Other information sources" section Photos are in the "Notes & Findings" section | Meter board (including fuses);Smart meter | 0 | 0 | 0 |  | CN11 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43473.3958 |  |  | 14177 | Residential |  | 20190820JEM_01 | Infrastructure (network-based) | -37.7123 | 144.9965 | 1 | Jemena | Report | 18443 | 0.02348 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Site made safe | 21 SUNSET BOULEVARD, JACANA VIC 3047 | A128848 | Unauthorised access | [5 empty] | 2 | Metering and Servicing crew crews attended the incident location with a SO for an abolishment of service line and metering in conjunction with a new connection of an overhead Builder's Temporary Supply (BTS) pole When the crew arrived the site was a demolished and vacant site with no existing service line and meter. REC details are in the "Other Information Sources" section (REC number 20142) LEI details are in the "Other Information Sources" section (Licence number 980517) EWR and COES are in the "Notes & Findings" section Photos are in the "Notes & Findings" section | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | BMS23 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/07/2019 13:57 |  |  | 14181 | Residential |  | 20190820JEM_03 | Infrastructure (network-based) | -37.6907 | 144.9133 | 1 | Jemena | Report | 18458 | 0.038464 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Jacana | Other
Crew replaced the cables and made safe. | 1 Galibier Parade, Plumpton VIC 3335, Australia | 30322080 | Copper theft | [6 empty] | A passerby has reported there are cables hanging out of pit near the incident location. Pit seems to feed 4-5 streetlights. He is unsure if it has been vandalised. Upon arrival the crew found service cables from 10 Street light poles cut and all pits open, live wires exposed and hanging out of pit. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | SA011 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/08/2019 17:42 |  |  | 14180 |  |  | 20190820PWA_03 | Infrastructure (network-based) | -37.7111 | 144.7222 | 1 | Powercor | Report | 17739 | 0.010454 | Low voltage AC (<1kV) | Melbourne Airport | 3335 | Plumpton | Other
Fault Crew checked the condition of all conductors and disconnected and remade all terminations between the distribution system and the Point of Attachment (POA) of the installation. The Customerâ€™s REC also checked all neutral connections on the 250 metre Private Overhead Electric Line. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact confirmed 4.0 Volts under normal load conditions. The Customer was advised to arrange the services of an REC to bond the metallic waste water system to the installation earthing system by an equipotential earthing bonding conductor to eliminate any risk of a potential difference between conductive building mediums. The Customer was also advised to consider upgrading the electrical supply system to the property. | 27 LOWAN AVENUE, RED CLIFFS VIC 3496 | 33063426 |  |  |  | Unidentified customer fault |  |  | 2 | Person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower tap and her bare feet while standing on the wet tiled shower base, which was set into a concrete floor. | Private overhead electric line (POEL) | 0 | 0 | 0 |  | RCT023 | Voltage Drop (4v) due to an extensive 250 metre Single Phase Private Overhead Electric Line (POEL). | Minor shock | 43473.7917 |  |  | 14183 | Agricultural |  | 20190820PWA_05 | Infrastructure (customer connection) | -34.3198 | 142.162 | 1 | Powercor | Report | 17746 | 0.012799 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | Installation
Crews isolated supply and carried out repairs LEI attended site following restoration of supply to check for HVI. No damage was found to customers installations. | 42 White Rd, Bullengarook VIC 3437, Australia | 33025072 |  | Fallen | [5 empty] | Following calls of supply interruption, crews found a tree has fallen through conductors at incident location between poles 2 and 3. There was suspected to be a HVI as HV conductors contacted a subsiduary LV circuit. There was no fire, no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | GSB011 | Vegetation: Trees Incident | Damage to network assets | 18/08/2019 20:28 |  |  | 14191 | Agricultural |  | 20190821PWA_01 | Infrastructure (network-based) | -37.4889 | 144.5194 | 1 | Powercor | Report | 17818 | 0.023366 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3437 | Bullengarook | Trees
On arrival crew isolated supply and carried out repairs. | UNIT 1 11 LESLIE STREET, ST ALBANS VIC 3021 | 30247361 |  |  |  | Unknown technical factor |  |  |  | Emergency Services reported fire at POA at the incident location. On arrival the crew found that the FOLCB at the POA was completely melted, dropping hot debris to the ground, which started a small grass fire in the front of the property of less than 0.5 meter square. There were no reported injuries. | Connection box | 2 | 2 | 2 |  | SA012 | Insufficient remains to determine cause | Grassfire | 20/08/2019 23:50 | 1 | Localised: less than 10 sq.m | 14195 | Residential |  | 20190821PWA_02 | Infrastructure (customer connection) | -37.7369 | 144.8095 | 1 | Powercor | Report | 17821 | 0.036609 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Connection
Control room was informed that a car hit the pole and that emergency services blocked off the area. Fault crew dispatched and found pole broken and laying on ground. The line was immediately de-energised remotely. Isolations of the affected area were made and supply restored to the unaffected area. | 43 RESERVE ROAD, WONGA PARK VIC 3115 | LIS1203689 | Vehicle | [6 empty] | Customer reported car colliding with pole. Car and occupant were not on site at time. | Pole (concrete) | 0 | 0 | 0 |  | RWN31 | Car collided with concrete pole. Car and occupant were not on site at time. | Damage to network assets | 43715.0625 |  |  | 14186 | Roadway |  | 20190821SPN_02 | Infrastructure (network-based) | -37.7276 | 145.284 | 1 | AusNet Services Distribution | Report | 17811 | 0.002735 | 22kV AC | Moorabbin Airport | 3115 | Wonga Park | Vehicle
Fault crew dispatched and contacted control room to advise of Conductors down and checked with onsite emergency staff to confirm Pilot was ok and it was also safe to repair the fallen conductors. Line isolated, conductors repaired mid span and restrung. Supply restored. | 45 REGAN ROAD, TRARALGON VIC 3844 | LIS2607088 & LIS2607087 | Manned aircraft | [6 empty] | Plane contacted and brought down 22kV conductors between poles LIS2607088 and LIS2607087 | Conductor (bare) | 0 | 0 | 0 |  | TGN11 | Plane contacted and brought down 22kV conductors between poles LIS2607088 and LIS2607087. Fault Crew dispatched to a feeder fault which reported a plane into 22kV conductors in Reagan Road Traralgon. On arrival, the fault crew observed 3 phase 22kV conductors on the ground betweenpoles LIS2607088 and LIS2607087 and an air craft down in paddock on the eastside of the fallen power lines approximately 200 metres away. Fault crew Contacted control room to advise of conductors down and checked with onsite emergency staff to confirm Pilot was ok and it was also safe to repair the fallen conductors. Line isolated, conductors repaired mid span and restrung (7.8 metres from ground level following repairs). Supply restored. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/08/2019 10:14 |  |  | 14190 | Agricultural |  | 20190821SPN_04 | Infrastructure (network-based) | -38.2023 | 146.4952 | 1 | AusNet Services Distribution | Report | 17815 | 0.0096331 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Vehicle
UE fault crews attended, and undertook emergency switching to isolate the faulty section of line. An EIO was also dispatched to investigate for possible HVI, and confirmed there was no damage to customer installations. The pole was replaced under access authority conditions and supply restored. | 22 HARLEIAN STREET, BLAIRGOWRIE VIC 3942 | 1304484 |  | Prone to salt deposition |  | Leakage |  |  | 1 | UE received calls for loss of supply in Blairgowrie. On attendance, faults crews found a pole fire had occurred and the pole had snapped with wires down, and the HV fuse had operated upstream of the fault location. | Pole top | 0 | 0 | 0 |  | STO14 | In windy and drizzly conditions, tracking had occurred from the HV conductor to the cross-arm coach screw, resulting in the pole fire. | Pole-top fire;Loss of supply | 43716.3722 | 1 | Negligible: no ground fire | 14193 | Roadway |  | 20190821UTD_03 | Infrastructure (network-based) | -38.3692 | 144.7773 | 1 | United Energy Distribution | Report | 17819 | 0.039488 | 22kV AC | Avalon Airport | 3942 | Blairgowrie | Pole
The UE network analytics system issued a remote disconnect to premises supplied from Hazel Railway substation. UE also dispatched a fault crew and an EIO to investigate for any overvoltage damage to premises. The fault crew isolated both LV circuits and repaired the high resistance neutral connection and isolated all damaged street lights. LEI's isolated all customers on the effected circuits. The procedure as indicated in the work instruction for HV injections has been followed for restoring supply to affected customers. | 1 HAZEL STREET, SEAFORD VIC 3198 | 3305558 |  |  |  | Neutral fault |  |  | 1 | The UE network analytics system identified voltage issues consistent with a neutral failure at substation Hazel Railway in Seaford. Soon after, UE received call from a customer advising of sparks coming from the mains box. | Pole mounted;Connector/termination | 0 | 0 | 0 |  | FTN12 | The cause of the overvoltage was a failed connection on the transformer neutral bushing. | HV injection | 18/08/2019 16:05 |  |  | 14204 | Roadway |  | 20190822UTD_05 | Infrastructure (network-based) | -38.1052 | 145.129 | 1 | United Energy Distribution | Report | 17830 | 0.027343 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
On arrival crew isolated supply and carried out repairs | 32 Nicholson St, South Yarra VIC 3141, Australia | 30216014 |  | Blown branch/vegetation | [5 empty] | Resident (Lee Gaywood) reported main wire on the ground and part on the tree at the above incident location Was small fire in tree, now just smoldering There was no ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BC024 | Vegetation: Trees Incident | Other vegetation | 22/08/2019 21:14 | 1 | Negligible: no ground fire | 14219 | Roadway |  | 20190827PWA_02 | Infrastructure (network-based) | -37.8427 | 144.9878 | 1 | CitiPower | Report | 17851 | 0.027222 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Trees
On arrival crew isolated supply and replaced fuses | Bourke Rd, Katamatite VIC 3649, Australia | 32185775 |  |  |  | Candled fuse |  |  |  | Passer by reported sparking and hot debris being emitted from pole top at incident location. Upon arrival crew found that a Boric Acid fuse tube had candled and burnt through. No resultant ground fire | Boric acid | 2 | 2 | 2 |  | NKA001 | Moisture ingress | Pole-top fire | 31/08/2019 0:11 | 1 | Negligible: no ground fire | 14244 | Roadway |  | 20190903PWA_03 | Infrastructure (network-based) | -36.0553 | 145.6977 | 1 | Powercor | Report | 17889 | 0.028118 | 22kV AC | Shepparton Airport | 3649 | Katamatite | Fuse
Fault crew and LEI dispatched to investigate. O/H lines isolated and tree removed. Conductors repaired and customer meters replaced. Supply restored | 22-24 MARLBOROUGH ROAD, HEATHMONT VIC 3135 | LIS1212397 |  | Fallen | [5 empty] | Report of HVI following council owned tree contacting OH conductors | Conductor (bare) | 0 | 0 | 0 |  | RWT31 | Vegetation: Trees Incident | HV injection | 29/08/2019 16:00 |  |  | 14240 | Roadway |  | 20190903SPN_02 | Infrastructure (network-based) | -37.8349 | 145.2302 | 1 | AusNet Services Distribution | Report | 17924 | 0.035345 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3135 | Heathmont | Trees
On arrival the crew found a deteriorated neutral connection at the susbstation. A number of premises were isolated and a LEI attended to carry out premises checks | 10 RUSSELL STREET, QUARRY HILL VIC 3550 | 31008832 | [7 empty] | Customers reported supply issues at the incident location. There was reports of damaged equipment and customers switchboards. There was no fire or reported injuries | Pole mounted;Connector/termination | 2 | 2 | 2 |  | BGO022 | To be determined | Melting or smoking only | 43564.4104 |  |  | 14249 | Roadway |  | 20190905PWA_01 | Infrastructure (network-based) | -36.77 | 144.2777 | 1 | Powercor | Notification | 17895 | 0.02826 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Quarry Hill | Connection
The CFA attended & extinguished the ground fire, police also in attendance. Crew isolated supply and carried out repairs. | Leitchville-Kerang Rd, Horfield VIC 3567, Australia | 33021753 |  | Bird | [5 empty] | Customer reported wires down and fire at incident location. Upon arrival the fault crew found that a swan had hit conductors nearest pole 17 of the Leitchville line, bringing 2 of the 3 conductors down. A ground fire was initiated due to downed conductors, approximately 3M x 10M of road verge was burnt. There was no injuries or third party property damage | Conductor (bare) | 2 | 2 | 2 |  | CH005 | Bird Incident | Grassfire | 43594.2722 | 1 | Small: 10 - 1000 sq.m | 14252 | Roadway |  | 20190906PWA_02 | Infrastructure (network-based) | -35.8856 | 144.2399 | 1 | Powercor | Report | 17923 | 0.01927 | 22kV AC | Bendigo Airport | 3567 | Horfield | Animal
Low voltage supply to the affected pits has been isolated, made safe. FFU to replace damaged / stolen cable. | 2 Troups Rd N, Rockbank VIC 3335, Australia | 30545804 | Copper theft | [6 empty] | Passer by Jarrod 0447257149 advised there are a number of pits which are opened and cables exposed at the corner of Troups Road North & Western Freeway, Rockbank / Mt Cottrell - no sparking/arcing. Crew arrived to find four pit lids with covers removed some with cable exposed, further investigation revealed that four pits had been interfered with. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43505.5903 |  |  | 14258 | Roadway |  | 20190909PWA_02 | Infrastructure (network-based) | -37.7352 | 144.6708 | 1 | Powercor | Report | 17930 | 0.019461 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply and carried out repairs. | 291 BREAMLEA ROAD, CONNEWARRE VIC 3227 | 33045904 |  | Bird | [5 empty] | A swan contacted the HV conductors at the incident location, causing one of the HV conductors to fall to the ground alive via back-feed. This situation resulted in several small grassfires, totaling less than 1m2 in total. The CFA attended, however the grassfires self extinguished once the supply was isolated. There were no reported injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | WPD024 | Bird Incident | Grassfire | 14/09/2019 6:07 | 1 | Localised: less than 10 sq.m | 14274 | Roadway |  | 20190916PWA_01 | Infrastructure (network-based) | -38.2828 | 144.4012 | 1 | Powercor | Report | 17953 | 0.010248 | 22kV AC | Avalon Airport | 3227 | Connewarre | Animal
Om arrival supply isolated and repairs arranged | 1180 EXFORD ROAD, EYNESBURY VIC 3338 | 30257154 | Copper theft | [6 empty] | Crew responding to public lights faults have found copper cable has been stolen. Approximately 200 meters of cable has been stolen. Sites made safe and pits closed. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN011 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43625 |  |  | 14276 | Roadway |  | 20190916PWA_02 | Infrastructure (network-based) | -37.7465 | 144.5676 | 1 | Powercor | Report | 17955 | 0.025963 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Eynesbury | Other
UE dispatched an EIO and a faults crew to investigate. On attendance, an REC was on site replacing the FOLCB in which there had been a burnt out neutral connection. On completion of the work, the attending EIO undertook appropriate tests which passed. | 13 MARSHALL STREET, NOBLE PARK VIC 3174 | 209719 |  |  |  | Unidentified customer fault |  | Phase to earth | 2 | The UE network analytics identified abnormal voltages at this address. On attendance, an REC, who was on site to replace the FOLCB, advised that the customer had reported receiving tingles from the taps in the bathroom. | POA connection (customer side) | 2 | 2 | 2 |  |  | As advised by the REC on site, the cause was a burnt out customer neutral connection in the customer's FOLCB. | Minor shock | 26/08/2019 14:50 |  |  | 14275 | Residential |  | 20190916UTD_01 | Infrastructure (customer connection) | -37.966 | 145.1906 | 1 | United Energy Distribution | Report | 17954 | 0.021219 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Installation
Fault crew and LEI dispatched to investigate. Loose neutral connection repaired at Customer POA (AusNet side) | 105 REEVE STREET, SALE VIC 3850 | 2502236 |  |  |  | Age;Defective component;Not built/maintained to design |  |  |  | Customer reported feeling tingle from shower tap. | POA connection (network side) | 0 | 0 | 0 |  | SLE14 | LEI measured a voltage on earth system and identified a loose supply neutral connection in fused mains box. Loose connection repaired in fused mains box at customer POA. | Minor shock | 43533.7688 |  |  | 14281 | Residential |  | 20190917SPN_02 | Infrastructure (customer connection) | -38.1031 | 147.0606 | 1 | AusNet Services Distribution | Report | 17961 | 0.032309 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | Connection
Fault crew dispatched. Candled HV fuse removed and replaced with new | 29 BEGG STREET, LEONGATHA VIC 3953 | LIS2003532 |  |  |  | Candled fuse |  |  |  | Report of fuse candling | Boric acid | 0 | 0 | 0 |  | LGA23 | Candled 6k BA HV Fuse | Pole-top fire | 43564.3611 | 1 | Negligible: no ground fire | 14283 |  |  | 20190917SPN_03 | Infrastructure (network-based) | -38.4779 | 145.9275 | 2 | AusNet Services Distribution | Report | 17963 | 0.038304 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Leongatha | Fuse
On arrival crew isolated supply. Defect notice issued. | 407 WARRENHEIP STREET, BUNINYONG VIC 3357 | 32002470 | Working too close to underground cables | [6 empty] | REC called to advise demolishers on site , (abolishment not done ) excavator has clipped u/g mains -no one hurt -he has advised them to cease work , please attend and make safe. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | BAS022 | Demolition work - no abolishment of supply | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43747.4736 |  |  | 14297 | Residential |  | 20190918PWA_04 | Infrastructure (customer connection) | -37.6487 | 143.8846 | 1 | Powercor | Report | 17978 | 0.029755 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3357 | Buninyong | Dug up
The attending Powercor Fault Crew replaced the O/H Neutral Bridge Conductor on the LV Street Mains | 19 FASHAM STREET, UNDERBOOL VIC 3509 | 32154225 |  |  |  | Fatigue;Mechanical breakdown |  |  |  | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metallic Shower Tap and his bare feet whilst standing on the wet shower base. | Conductor (bare) | 0 | 0 | 0 |  | OYN001 | Connection failure -O/H Neutral Bridge Connection on the LV Street Mains at the corner of Fasham and Westh Streets . | Minor shock | 43587.5 |  |  | 12164 | Roadway |  | 20190214PWA_01 | Infrastructure (network-based) | -35.1721 | 141.8058 | 1 | Powercor | Report | 15249 | 0.0035463 | Low voltage AC (<1kV) | Mildura Airport | 3509 | Underbool | Connection
Replaced neutral connection and cable to LV aerial bundled cable | 14 LYREBIRD COURT, WERRIBEE VIC 3030 | 30103727 |  |  |  | Corrosion |  |  | 1 | Report of shocks when having a shower and simultaneously made contact with the metallic plumbing features and the wet shower base. This case was originally detected from neutral integrity remote detection, although upon Powercor making contact with the resident he reported getting tingles from the shower and dimming/flickering lights at the property. | Connector/termination | 0 | 0 | 0 |  | WBE021 | high impedance neutral connection on pole - corroded | Minor shock | 43587.7708 |  |  | 12166 | Roadway |  | 20190214PWA_03 | Infrastructure (network-based) | -37.8803 | 144.6743 | 1 | Powercor | Report | 15251 | 0.038363 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
Tightened Loose connection in Fuse mains box | 30 BRUCE STREET S, ALTONA MEADOWS VIC 3028 | 30107087 |  |  |  | Neutral fault |  |  |  | Person received an electric shock when he contacted the metallic garden tap with his hand whilst making simultaneous contact with the general mass of earth with his bare feet | Service conductor | 0 | 0 | 0 |  | LV006 | Loose neutral on line side in fuse mains box | Minor shock | 43648.4167 |  |  | 12177 | Residential |  | 20190214PWA_10 | Infrastructure (customer connection) | -37.8691 | 144.7664 | 1 | Powercor | Report | 15262 | 4.0509e-05 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Connection
Crew refitted distribution cable in street | 1 BERENICE TERRACE, TOORAK VIC 3142 | 30215534 |  |  |  | Neutral fault |  |  |  | Person was turning on back yard tap when he received an electric shock. he made simultaneous contact between the metallic tap with one hand and the general mass of earth with his feet. Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a high impedance neutral conductor within the distribution service cable in the street. | Conductor (bare) | 0 | 0 | 0 |  | TK001 | Connection malfunction - high impedance distribution cable in street | Minor shock | 43771.8125 |  |  | 12188 | Residential |  | 20190218PWA_03 | Infrastructure (network-based) | -37.834 | 145.0088 | 1 | CitiPower | Report | 15277 | 0.019851 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Connection
Fault crew dispatched. MFB attended site and put out fire prior to fault crew attending. | 1 CANTALA CRESCENT, RINGWOOD NORTH VIC 3134 | LIS1210191 |  | Animal |  |  |  | Phase to earth |  | E0011010 - small ground fire reported following possum contacting O/H HV conductors | Conductor (bare) | 0 | 0 | 0 |  | RWN24 | Animal Incident | Grassfire | 18/02/2019 17:20 | 1 | Localised: less than 10 sq.m | 12191 |  |  | 20190219SPN_01 | Infrastructure (network-based) | -37.7991 | 145.216 | 2 | AusNet Services Distribution | Report | 15281 | 0.031294 | 22kV AC | Moorabbin Airport | 3134 | Ringwood North | Animal
Fault crew dispatched. Candled fuse replaced | 17 STOCKDALE ROAD, STRATFORD VIC 3862 | LIS 2511984 |  |  |  | Candled fuse |  |  |  | E0011088 - report of candling fuse | Boric acid | 0 | 0 | 0 |  | MFA21 | Crew arrived onsite found 6k BA fuse had candled. No other damage and no evidence of fallen material at base of pole. Fuse replaced and supply restored | Pole-top fire | 19/02/2019 13:51 | 1 | Negligible: no ground fire | 12195 |  |  | 20190219SPN_03 | Infrastructure (network-based) | -37.9327 | 147.0969 | 2 | AusNet Services Distribution | Report | 15287 | 0.013645 | 22kV AC | Bairnsdale Airport | 3862 | Stratford | Fuse
Crew isolated supply. pole replaced, earthing repaired. | 6502 HENTY HIGHWAY, GLENISLA VIC 3314 | 30553863 |  |  |  | Corrosion |  |  |  | Customer reported Power pole smoking heavily at bottom of pole and burnt at top of pole. On arrival crew found SWER earthing was damaged. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Earth/earthing | 2 | 2 | 2 |  | HSM002 | attributed to high resistance earthing | Pole-top fire | 13/11/2018 8:52 | 1 | Negligible: no ground fire | 12199 | Agricultural |  | 20190220PWA_03 | Infrastructure (network-based) | -37.2352 | 142.2048 | 1 | Powercor | Report | 15296 | 0.0057326 | Earthing cable | Hamilton Airport | 3314 | Glenisla | AF Other
The ACE Energy crew replaced the burnt lantern and the spigot type public lighting bracket re-wired. | NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 8819481 |  |  |  | Overheated connection |  |  | 2 | A light patrol by ACE Energy identified a 150 watt high pressure sodium lantern had been on fire at pole number LIS 8819481 located outside 521 Nepean Highway, Frankston. | Public lighting | 0 | 0 | 0 |  | FSH31 | The cause was a probable loose connection that overheated. | Pole-top fire | 15/02/2019 12:35 | 1 | Negligible: no ground fire | 12196 | Roadway |  | 20190220UTD_01 | Infrastructure (network-based) | -38.1495 | 145.1151 | 1 | United Energy Distribution | Report | 18403 | 0.028409 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
On arrival crew isolated supply. Arrangements made for pole replacement | 61 ELIZABETH STREET, MELBOURNE VIC 3000 | 30202593 | Vehicle | [6 empty] | Victoria Police contacted the CitiPower Report Room to advise a truck has hit a public lighting pole outside No.61 Elizabeth St. On attendance the CitiPower crew found a steel public lighting pole had snapped at the base and was sitting on top of an unattended parked car. The truck in question was not present. Live cables were exposed at the bottom of the pole. There was no fire, no reported injuries. | Pole (steel) | 2 | 2 | 2 |  | LQ034 | Truck collided with lighting pole | Damage to network assets | 43467.1201 |  |  | 12206 | Roadway |  | 20190221PWA_02 | Infrastructure (network-based) | -37.8167 | 144.9641 | 1 | CitiPower | Report | 15304 | 0.032347 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Vehicle
On arrival crew carried out repairs. | AVENUE OF HONOUR, WOODEND VIC 3442 | 30354464 | Vandalism;Copper theft | [6 empty] | A passer-by reported an exposed cable at the incident location. Upon arrival, The Powercor crews found that the UG cable approx. 100m from the pole to pit had been stolen. There was no fire, no reported injuries. | Services pit | 2 | 2 | 2 |  | WND023 | Vandalism and copper theft | Damage to network assets | 43587.6424 |  |  | 12209 |  |  | 20190221PWA_05 | Infrastructure (network-based) | -37.3461 | 144.5348 | 1 | Powercor | Report | 15308 | 0.026039 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Other
Street light isolated | 504 MELBOURNE ROAD, NEWPORT VIC 3015 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stole street light underground cable | Cable | 2 | 2 | 2 |  |  | Person stole underground cable | Loss of supply;Damage to network assets | 22/02/2019 11:49 |  |  | 12210 | Roadway |  | 20190222JEM_01 | Infrastructure (network-based) | -37.8376 | 144.8827 | 1 | Jemena | Report | 15312 | 0.022622 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Other
fault truck replaced the service cable to the property | 3 STUART COURT, BALWYN NORTH VIC 3104 | 30185540 |  |  |  | Corrosion |  |  |  | person received an electric shock when she made simultaneous contact between the metallic shower taps with her hands and the metal shower waste with her feet. | Service conductor | 0 | 0 | 0 |  | WD032 | Corroded service cable | Minor shock | 24/02/2019 17:30 |  |  | 12218 | Residential |  | 20190225PWA_05 | Infrastructure (customer connection) | -37.7943 | 145.1031 | 1 | CitiPower | Report | 15535 | 0.033315 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | OH Cable
Voltage tests between independent earth and various points of the electrical installation, including the distribution assets were carried out. The attending fault crew re terminated the neutral connection on the pole. The installation was tested by the attending EIO and zero volts was recorded on the installation neutral bar in the main S/B, the water pipe system and between the points where the person received the shock. | 8 GEELONG ROAD, FOOTSCRAY VIC 3011 |  |  |  |  | Neutral fault |  |  | 2 | Child care worker Stephanie Ashman was using the outdoor tap in the childrenâ€™s play area when she received an electric shock when he made simultaneous contact with both the water pipe system and the general mass of earth. | Neutral screen | 2 | 2 | 2 |  |  | Voltage tests between independent earth and various points of the electrical installation, including the distribution assets, identified a poor neutral connection on the pole as the cause of the high impedance associated with return path of the neutral current. This condition caused current to flow through the installation M.E.N connection, main earthing conductor, water pipe earth bond conductor and the water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a current flow through the water piping system. | Minor shock | 26/02/2019 12:08 |  |  | 12227 | Commercial |  | 20190226JEM_02 | Infrastructure (network-based) | -37.7948 | 144.8993 | 1 | Jemena | Report | 15332 | 0.014659 | Extra low voltage AC (<50V) | Essendon Airport | 3011 | Footscray | Connection
Replaced the faulty IPC and re-attached LV conductor tie to get the customers back on supply. | 557 INKERMAN ROAD, CAULFIELD NORTH VIC 3161 | 30261573 |  |  |  | Corrosion |  |  |  | A passer-by reported ground fire on the ground at the above incident location. On arrival, the crew found an Low Voltage (LV) overhead conductor tie had broken due to faulty Insulation Piercing Connector (IPC) overheating and melted the LV tie conductor. The melted plastic IPC fell onto the ground and caused ground fire of approximately 20sqm. There was no third party damaged and no reported injuries. | Connector/termination | 2 | 2 | 2 |  | EL011 | Overheated connection | Grassfire | 25/02/2019 17:52 | 1 | Small: 10 - 1000 sq.m | 12223 | Roadway |  | 20190226PWA_03 | Infrastructure (network-based) | -37.8681 | 145.013 | 1 | CitiPower | Report | 15328 | 0.017707 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Connection
On arrival crew isolated supply and carried out repairs. | 21 KURUNJANG DRIVE, KURUNJANG VIC 3337 | 31025469 |  |  |  | Corrosion |  |  |  | MFB Comms reported burnt wire, started a grass fire. brigade onsite On arrival the PCA Faults Crew have advised that a burnt out Blue Phase LV Isolator, Cu to Al D-Loop connection has overheated and caused sparks to fall onto the grassed area below. The resultant hot sparks above had fallen onto the ground/grassed nature strip below causing a small grass fire near the base of the pole (1m x5m). There was no reported injury or shocks as a result of this incident. | Connector/termination | 2 | 2 | 2 |  | MLN012 | Overheated connection at D loop | Grassfire | 25/02/2019 18:49 | 1 | Localised: less than 10 sq.m | 12224 | Roadway |  | 20190226PWA_04 | Infrastructure (network-based) | -37.6728 | 144.5875 | 1 | Powercor | Report | 15329 | 0.016296 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Connection
Fault crew dispatched to investigate. Repairs completed and supply restored | 1 SPRING STREET, THOMASTOWN VIC 3074 | LIS908031 |  |  |  | Defective component |  |  |  | E0011792 - MFB reported pole fire. Fault crew dispatched and found burnt junction box | Connection box | 0 | 0 | 0 |  | TT9 | Single phase pole type junction box failed causing hot molten plastic and aluminium to fall to ground igniting a 1.5 x 1 meter grass fire. | Pole-top fire | 25/02/2019 20:10 | 1 | Localised: less than 10 sq.m | 12231 |  |  | 20190226SPN_03 | Infrastructure (network-based) | -37.6828 | 145.0126 | 2 | AusNet Services Distribution | Report | 15339 | 0.036549 | Low voltage AC (<1kV) | Essendon Airport | 3074 | Thomastown | Connection
"Labuan-Hughes" substation was placed under LV parallel to restore supply to customers in the vicinity and the electrical infrastructure was repaired under Access Authority conditions. | 2 LABUAN STREET, SORRENTO VIC 3943 | 1306285 |  |  |  | Moisture ingress |  |  | 1 | Caller reports there is a fire at the top of the transformer pole located on the corner of Hew and Labuan Streets. They have contacted the fire authority who have just arrived on site to put out a small grass fire. The centre phase XLPE dropper from the fuse units was burnt out at the end of the Raychem sheds near the start of the earth braid and molten metal had dropped into the dry grass with a 4sqm fire starting that was extinguished by the CFA. The centre phase 15amp boric acid fuse had operated and was hanging when the faults crew initially attended. | Boric acid;Dropper/bridge | 0 | 0 | 0 |  | STO 13 | The most likely cause was a failed connection at the Rehchem termination although the close proximity to Bass Strait may have also contributed. | Grassfire | 25/02/2019 17:09 | 1 | Localised: less than 10 sq.m | 12226 | Roadway |  | 20190226UTD_02 | Infrastructure (network-based) | -38.3561 | 144.7587 | 1 | United Energy Distribution | Report | 15331 | 0.024748 | 22kV AC | Avalon Airport | 3943 | Sorrento | Connection
LEI and fault truck dispatched to investigate the incident. NST passed. Volts on the neutral with load was 2.8 volts. The fault truck cleaned the connections and re-greased the terminals at the FOLCB. Fault crew also checked the connections at the pole. A dead possum was removed from the white phase which was the same phase as No 12 Kenny St was connected to. After reconnection the neutral volts remained steady at 1.3 volts with and without load. | 12 KENNY STREET, CRIB POINT VIC 3919 | 1111247 |  | Animal |  | Fault on customer installation |  |  | 1 | UE received report from customer that ongoing issue of tingles from shower head in ensuite only , and flickering lights as well | Connection box;Customer installation | 2 | 2 | 2 |  |  | Animal Incident | Minor shock | 22/02/2019 10:30 |  |  | 12228 | Residential |  | 20190226UTD_03 | Infrastructure (network-based) | -38.3477 | 145.1884 | 1 | United Energy Distribution | Report | 15333 | 0.021022 | Low voltage AC (<1kV) | Moorabbin Airport | 3919 | Crib Point | Animal
On arrival crew isolated supply and carried out repairs. | 21 ALFRED CRESCENT, LOCKINGTON VIC 3563 | 33085689 |  |  |  | Fuse failed to eject |  |  |  | Vic Fire reported a pole fire and smoke coming from just above the transformer at the incident location. Upon arrival the crew found the centre phase fuse hung up asa result of a bird flashover. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | SHP012 | Bird Incident | Pole-top fire;Loss of supply | 25/02/2019 10:57 | 1 | Negligible: no ground fire | 12244 |  |  | 20190227PWA_04 | Infrastructure (network-based) | -36.2741 | 144.5386 | 1 | Powercor | Report | 15356 | 0.038543 | 22kV AC | Bendigo Airport | 3563 | Lockington | Animal
Fault crew dispatched, candled fuse replaced and supply restored | 1 NEAGLE STREET, YARRAGON VIC 3823 | 2202558 |  |  |  | Candled fuse |  |  |  | E0011955 - Report of candled fuse | EDO fuse | 0 | 0 | 0 |  | MOE22 | Candled EDO fuse. No damage to pole and no evidence of ground fire | Pole-top fire | 27/02/2019 9:55 | 1 | Negligible: no ground fire | 12241 | Roadway |  | 20190227SPN_02 | Infrastructure (network-based) | -38.2024 | 146.0678 | 2 | AusNet Services Distribution | Report | 18283 | 0.010046 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon | Fuse
The broken HV powder filled fuse was replaced and supply restored. | 6 BUSHY COURT, SOMERVILLE VIC 3912 | 1109065 |  |  |  | Moisture ingress |  |  | 0 | Caller contacted the United Energy faults and emergencies call centre advising the pole is sparking and the grass underneath has caught on fire. They have also lost their electricity supply. A HV powder filled fuse exploded at the single phase "Bushy-Drovers" pole type substation following moisture ingress that caused a 10sqm grass fire following hot porcelain and molten metal being spread over a large area around the pole. | Powder filled | 0 | 0 | 0 |  | HGS 33 | Moisture ingress was deemed the most likely cause for the HV fuse to malfunction. | Grassfire | 43468.4368 | 1 | Localised: less than 10 sq.m | 12266 | Roadway |  | 20190304UTD_03 | Infrastructure (network-based) | -38.232 | 145.191 | 1 | United Energy Distribution | Report | 18385 | 0.020931 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Fuse
Emergency high voltage switching was completed to minimise the number of customers affected and the electrical infrastructure was replaced under Access Authority conditions prior to supply being restored. The LEI investigated homes in the vicinity for signs of a HVI and later confirmed that a HVI did not occur. | 1491 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1301093 and 1301094 |  | Prone to salt deposition |  | Fatigue |  |  | 1 | At 8.41AM on 02/03/2019, 22kV feeder RBD 22 circuit breaker successfully reclosed and held. Emergency high voltage switching was completed after broken HV and LV crossarms were identified in Point Nepean Road, Rosebud at pole number LIS 1301093 and 1301094. A LEI was requested to attend and investigate the possibility of a high voltage injection to customers supplied from the north circuit of "Boneo-Nepean" substation as the HV and LV conductors may have clashed that caused a small 1sqm grass fire to occur on the grass nature strip. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | RBD 22 | The cause of the HV off-set crossarm failure was attributed to deterioration of the timber HV crossarms with heavy insulators attached located close to the Port Phillip Bay foreshore. | Loss of supply;Grassfire | 43499.3618 | 1 | Localised: less than 10 sq.m | 12267 | Roadway |  | 20190304UTD_04 | Infrastructure (network-based) | -38.3607 | 144.8871 | 1 | United Energy Distribution | Report | 18402 | 0.002603 | 22kV AC | Moorabbin Airport | 3939 | Rosebud | Crossarm
On arrival crew confirmed isolation and arranged repairs | 335 BENWERRIN-MT SABINE ROAD, BENWERRIN VIC 3235 | 33045906 |  |  |  | Electrical breakdown |  |  |  | CFA reported a fire at the incident location. Upon arrival, the Powercor crew found that a lightning arrestor on sub pole, CLC - LRN 217, had been damaged. There was a ground fire, no reported injuries. | Surge diverter | 2 | 2 | 2 |  | CLC005 | Internal fault in silicon carbide surge arrester | Grassfire | 43588.2931 | 1 | Medium: 1000 sq.m - 10 ha | 12279 | National/state park |  | 20190305PWA_05 | Infrastructure (network-based) | -38.4948 | 143.8884 | 1 | Powercor | Report | 16735 | 0.0054063 | 22kV AC | Avalon Airport | 3235 | Benwerrin | AF Other
The United Energy Network Control Centre completed emergency high voltage switching to minimise the amount of customers affected and remotely opened the MGE 34 circuit breaker to enable the onsite First Responder to remove the 3m branch off the conductors with a telescopic stick. | COLUMBIA PARK PRE SCHOOL, 26-28 COLUMBIA DRIVE, WHEELERS HILL VIC 3150 |  |  | Blown branch/vegetation |  |  |  |  | 2 | Caller reports that a 3m branch is resting on the overhead lines causing a fire. It was found that a tree branch from a private gum tree located in 26-28 Columbia Drive, Wheelers Hill fell over the 22kV overhead conductors and started to burn. | Conductor (bare) | 0 | 0 | 0 |  | MGE 34 | Vegetation: Trees Incident | Other vegetation | 18/02/2019 7:13 | 1 | Negligible: no ground fire | 12280 | Roadway |  | 20190305UTD_01 | Infrastructure (network-based) | -37.9139 | 145.1848 | 1 | United Energy Distribution | Report | 15412 | 0.037742 | 22kV AC | Moorabbin Airport | 3150 | Wheelers Hill | Trees
The failed connection was replaced and supply restored to customers supplied from "Milroy-North" substation. | 240 NORTH ROAD, BRIGHTON EAST VIC 3187 | 2305826 |  | Heat |  | Overheated connection |  |  | 2 | Per MFB - transformer has exploded at pole 2305826 and customers supplied from "Milroy-North" substation advised they have lost their electricity supply. A 150mm copper to 19/3.25 aluminium LVABC IPC connection failed at pole No. LIS 2305826 located outside 240 North Road, Brighton East. Molten metal embers fell into a dry council paperbark tree that caused a small branch fire and was extinguished by the MFB. | Conductor (ABC);Connector/termination | 0 | 0 | 0 |  |  | The cause of the failed connection was overload that caused the connection to overheat and fail. | Other vegetation | 43499.7056 | 1 | Negligible: no ground fire | 12281 | Roadway |  | 20190305UTD_02 | Infrastructure (network-based) | -37.9009 | 145.0128 | 1 | United Energy Distribution | Report | 15414 | 0.024395 | Low voltage AC (<1kV) | Moorabbin Airport | 3187 | Brighton East | Connection
Supply isolated repairs iniated | WERRIBEE COLLEGE, 860 DERRIMUT ROAD, TARNEIT VIC 3029 | 32177845 | Vandalism;Copper theft | [6 empty] | Copper theft in various locations. No fire and no injuries reported. Police notified. Lee who is a contractor in the area and works here often advised that vandals have attended the roadwork site at two location, first being b/w Dohertys and Boundary Rd (On Derrimut Rd) and the second being (if heading from Melbourne side) just before the intersection of Derrimut/Dohertys Rd's where crews have previously had to attend - and have removed pit lit around the streetlight poles and have removed/cut cabling. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Vandalism & copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/02/2019 15:28 |  |  | 12286 | Roadway |  | 20190306PWA_02 | Infrastructure (network-based) | -37.8095 | 144.6951 | 1 | Powercor | Report | 15419 | 0.016034 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs | 1 ALBERT STREET, WARRNAMBOOL VIC 3280 | 33101864 | Vehicle | [6 empty] | A truck belonging to Midfield Meats contacted an overhead service cable at the incident location, and brought it to the ground. The truck had left the scene so no height of vehicle available. There was no fire, no reported injuries or third party property damage. | Service conductor | 2 | 2 | 2 |  | WBL004 | Truck pulled down service line | Loss of supply;Damage to network assets | 16/02/2019 11:40 |  |  | 12288 | Roadway |  | 20190306PWA_03 | Infrastructure (network-based) | -38.3738 | 142.4614 | 1 | Powercor | Report | 15421 | 0.014407 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Vehicle
On arrival crew isolated supply. Vicroads to arrange repairs | MOUNT MACEDON ROAD, GISBORNE VIC 3437 | 33026018 | Vandalism;Copper theft | [6 empty] | Report received of theft of customer service cable for bridge heating and lighting. Police were in attendance. There was no fire, no reported injuries. | Customer installation | 2 | 2 | 2 |  | GSB013 | Vandalism and theft of customers equipment | Loss of supply | 16/02/2019 13:50 |  |  | 12290 | Roadway |  | 20190306PWA_04 | Infrastructure (network-based) | -37.4566 | 144.5794 | 1 | Powercor | Report | 15423 | 0.029679 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
Crew attended to replace cross-arm, LEI assessing installation damage | 88 APHRASIA STREET, NEWTOWN VIC 3220 | 30074160 |  |  |  | Leakage |  |  | 1 | Emergency services report that cross-arm had burnt and insulator had fallen into conductors below. Attending crew found that a cross arm fire had occurred and high voltage injection damage was apparent | Crossarm (wood) | 0 | 0 | 0 |  | GL022 | Leakage Current | Pole-top fire;HV injection;Loss of supply | 43619.0354 | 1 | Negligible: no ground fire | 12292 | Residential |  | 20190306PWA_05 | Infrastructure (network-based) | -38.15 | 144.3369 | 1 | Powercor | Report | 15426 | 0.0034676 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3220 | Newtown | Crossarm
On arrival crew isolated supply and arranged repairs. | 7600 MURRAY VALLEY HIGHWAY, TONGALA VIC 3621 | 60198472 | Working too close to underground cables | [6 empty] | Jeremy from Mawson Constructions called, have dug up and exposed an electricity pit at incident location. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | KYM006 | Excavator contacted underground assets during roadworks | No Go Zone (contact);Damage to network assets | 20/02/2019 13:03 |  |  | 12299 | Roadway |  | 20190307PWA_04 | Infrastructure (network-based) | -36.199 | 144.9439 | 1 | Powercor | Report | 15434 | 0.030234 | Low voltage AC (<1kV) | Shepparton Airport | 3621 | Tongala | Dug up
Fault crew dispatched. Spur line was isolated for repair work. | PEPPER TREE COTTAGE, 917 TARCOMBE ROAD, AVENEL VIC 3664 | LIS4708180 |  | Lightning | [5 empty] | E0013339 - report of pole fire. Pole caught fire at ground level from active bushfire being attended by CFA crew. Fire was ignited from lightning strike to the ground. Fire had been active for several days. | No failed asset | 0 | 0 | 0 |  |  | Fire was ignited from lightning strike to the ground. Electricity assets were not involved in fire start. The pole was impacted by the grass fire. Fire had been active for several days. CFA was at scene fighting fire. | Pole-top fire | 43619.6854 | 0 | Small: 10 - 1000 sq.m | 12310 |  |  | 20190308SPN_04 | Infrastructure (network-based) | -36.9493 | 145.307 | 1 | AusNet Services Distribution | Report | 15449 | 0.022829 | 12.7kV AC (SWER) | Mangalore Airport | 3664 | Avenel | Lightning
Fault crew dispatched. Fuses replaced and supply restored | 125 MULCAHY ROAD, PAKENHAM VIC 3810 | LIS501074 & LIS501073 | Crane, excavator or other construction/farming equipment |  |  | Candled fuse |  |  |  | E0013571 - report of excavator making contact with 22kV Conductors resulting in 2 fuses operating and 1 fuse candled | Conductor (bare);Any other type | 0 | 0 | 0 |  | OFR23 | Excavator made contact with 22kV Conductors between LIS501074 & LIS501073 which caused 2 fuses to operate and 1 fuse to candle. No further damage was found and no injuries sustained. Fuses were replace and supply to customers restored | Pole-top fire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43649.6771 | 1 | Negligible: no ground fire | 12311 |  |  | 20190308SPN_05 | Infrastructure (network-based) | -38.0563 | 145.4668 | 1 | AusNet Services Distribution | Report | 17804 | 0.0020903 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | Vehicle
Fault crew dispatched, fuse replaced and supply restored. | 405 RIFLE BUTTS ROAD, MANSFIELD VIC 3722 | LIS 3919053 |  |  |  | Candled fuse |  |  |  | E0013788 - BA fuse candling | Boric acid | 0 | 0 | 0 |  | MSD1 | 6K BA fuse candling only and no evidence of ground fire | Pole-top fire | 43741.2083 | 1 | Negligible: no ground fire | 12312 |  |  | 20190311SPN_01 | Infrastructure (network-based) | -37.1053 | 146.1212 | 1 | AusNet Services Distribution | Report | 17800 | 0.011559 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Fuse
On arrival crew removed wire | 377 GLENELG HIGHWAY, HAMILTON VIC 3300 | 32139027 |  | Bird | [5 empty] | CFA reported a transformer had started a grass fire at the incident location. On arrival the crew found an area 20x12m had been burnt. Wire was found on the transformer possibly from a bird attempting to build a nest. There were no reported injuries. | Pole mounted | 2 | 2 | 2 |  | HTN006 | fencing wire entangled on substation. | Grassfire | 43680.7847 | 1 | Small: 10 - 1000 sq.m | 12316 | Agricultural |  | 20190312PWA_03 | Infrastructure (network-based) | -37.7262 | 141.9888 | 1 | Powercor | Report | 15458 | 0.015691 | 22kV AC | Hamilton Airport | 3300 | Hamilton | Other
On arrival crew isolated supply and carried out repairs | TAYLORS ROAD, TELOPEA DOWNS VIC 3420 | 32121232 |  |  |  | Leakage |  |  | 1 | Crew reported a fire at the incident location. Following a patrol the crew found that a pole fire had occurred on a 12.7kV pole, resulting in a ground fire (approx. 50 sqm) on private property. There were no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Grassfire | 43741.2792 | 1 | Small: 10 - 1000 sq.m | 12317 | Agricultural |  | 20190312PWA_04 | Infrastructure (network-based) | -36.0428 | 141.0319 | 1 | Powercor | Report | 15459 | 0.015192 | 12.7kV AC (SWER) | Horsham Aerodrome | 3420 | Telopea Downs | Pole
Crew replaced the service cable to the property | 12 DALEY STREET, SUNSHINE WEST VIC 3020 | 32164546 |  |  |  | Corrosion |  |  |  | Person received an electric shock when he made simultaneous contact between the metallic shower taps with his hands and the metal shower waste with his feet. | Service conductor | 0 | 0 | 0 |  | SU035 | Corroded connection of Neutral service tails at pole end. | Minor shock | 21/02/2019 7:00 |  |  | 12323 | Residential |  | 20190312PWA_05 | Infrastructure (network-based) | -37.7848 | 144.8073 | 1 | Powercor | Report | 15468 | 0.001103 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Sunshine West | Connection
LEI attended and found 2 faults. existing overhead service replaced, (residual voltage reduced) advised the Customer to avoid using the external metal Tap until an REC could be arranged to install an Equipotential Earth Bonding Conductor to the metal Tap and any other extraneous metal parts to eliminate any further risk of a potential difference between conductive building mediums and earth. | 12 ALLITT AVENUE, BELMONT VIC 3216 | 32070612 |  |  |  | Corrosion;Induction |  |  |  | Person was outside operating an external Tap when he received an electric shock as he made simultaneous contact with his hand on the metal Tap whilst standing on the saturated earth. | Service conductor;Customer installation | 0 | 0 | 0 |  | GCY023 | 2 causes Corroded O/H Service Neutral Conductor termination at the Customer's POA. Induced voltage in the metal Tap caused by an installation Final Sub-circuit in close proximity to the Tap which was supplied by PVC pipe and isolated from the Main Earthing system. | Minor shock | 23/02/2019 8:00 |  |  | 12328 | Residential |  | 20190314PWA_02 | Infrastructure (customer connection) | -38.1808 | 144.3346 | 1 | Powercor | Report | 15479 | 0.020289 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
crew attended and replaced service cable | 21 BALLATER AVENUE, NEWTOWN VIC 3220 | 33045852 |  |  |  | Corrosion |  |  | 2 | Person was in the front yard operating a Garden Tap when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet whilst standing on the wet concrete path. | Service conductor | 0 | 0 | 0 |  | GL021 | Corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable. | Minor shock | 28/02/2019 10:00 |  |  | 12331 | Residential |  | 20190314PWA_05 | Infrastructure (customer connection) | -38.1553 | 144.3239 | 1 | Powercor | Report | 15484 | 0.014069 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | OH Cable
Fault crew dispatched, fuse replaced and supply restored. No evidence of ground fire | 36 MEADOWVIEW LANE, EMERALD VIC 3782 | LIS 418996 |  |  |  | Candled fuse |  |  |  | E0013830 - Candled 6K BA fuse reported | Boric acid | 0 | 0 | 0 |  | BGE22 | Candled 6K BA fuse. No evidence of ground fire, Fault Truck Replaced fuse and restored supply. | Pole-top fire | 43772.4604 | 1 | Negligible: no ground fire | 12335 |  |  | 20190318SPN_01 | Infrastructure (network-based) | -37.9158 | 145.4421 | 2 | AusNet Services Distribution | Report | 15498 | 0.0088056 | 22kV AC | Moorabbin Airport | 3782 | Emerald | Fuse
CFA Extinguished Fires. Crew replaced L11 arm via LIVE LV methods. | 18 MAUD STREET, BENALLA VIC 3672 | span between poles 3902405 & 3901955. |  | Fallen;Council | [5 empty] | E0015015 - A Benalla Council tree branch fell across open wire LV conductors causing the branch to catch fire and fall to the ground . Four ground fires observed in reserve land across from #18 Maud Street: Three were approx. 1m sq. and the larger one around the tree branch was approx. 5m sq. The force of the branch falling on the LV open wire caused the L11 crosss arm on pole 3902402 to snap resulting in red phase conductor dropping onto an insulated service across the Road from # 27 Maud Street . No supply lost to customer. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | BN004 | Vegetation: Trees Incident | Grassfire | 15/03/2019 20:00 | 1 | Localised: less than 10 sq.m | 12337 | Public space |  | 20190318SPN_03 | Infrastructure (network-based) | -36.5579 | 145.979 | 1 | AusNet Services Distribution | Report | 15614 | 0.0060243 | Low voltage AC (<1kV) | Wangaratta Aero | 3672 | Benalla | Trees
Excavator operator ceased work and advised to be assessed in case of medical issues associated with electrical shock.All work in vicinity of electrical assets at road works site were directed to cease until contractors onsite until they can prove they have systems in place not to come into contact of Live Electrical assets. No Go Zone representative has Met with the main Contractor and reviewed their systems to mitigate any future breaches of the NO Go Zone rules, review Safe operating procedures,SWMS etc and educated all onsite the need for dedicated spotters whilst in the No Go Zone area. Work safe have closed out their requirements. Contractor has resubmitted new applications for suppressions for the underground HV cables and will issue Permit to works to cover the rest of the work area. | 2 CHILDS ROAD, EPPING VIC 3076 | LIS905513 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0014861 - third party excavator contacted O/H HV conductors whilst being operated within the No Go Zone with out a Spotter. There were no injuries reported | Conductor (bare) | 0 | 0 | 0 |  | SMG31 | Excavator came into contact with overhead 22 kV Bare Conductors whilst being operated within the No Go Zone with out a Spotter. No permit had been request to operate Excavator within 3 m of Overhead Line | No Go Zone (contact) | 15/03/2019 9:47 |  |  | 12342 |  |  | 20190319SPN_03 | Infrastructure (network-based) | -37.6598 | 145.0216 | 1 | AusNet Services Distribution | Report | 15510 | 0.033023 | 22kV AC | Essendon Airport | 3076 | Epping | Vehicle
Fault crew dispatched. Area isolated and made safe. Metro Trains isolated electrical overhead train network and overhead line was repaired. Council has cleared tree | 1 OAKWOOD LANE, TECOMA VIC 3160 | 1308019 - 1308021 |  | Blown branch/vegetation | [5 empty] | E0014998 - report of HV and LV conductors down following tree contact | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/03/2019 19:19 |  |  | 12344 |  |  | 20190319SPN_04 | Infrastructure (network-based) | -37.9091 | 145.3457 | 2 | AusNet Services Distribution | Report | 15513 | 0.018515 | 22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
On arrival crew isolated supply and carried out repairs. | 200 MYERS STREET, GEELONG VIC 3220 | 17171688 |  |  |  | Leakage |  |  |  | Following a report of a pole fire on arrival the crew found the top crossarm burnt off on outer phase. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | GCY024 | Excessive leakage current, top crossarm burnt off at outer phase | Pole-top fire | 20/03/2019 0:25 | 1 | Negligible: no ground fire | 12350 | Roadway |  | 20190320PWA_01 | Infrastructure (network-based) | -38.1537 | 144.3661 | 1 | Powercor | Report | 15520 | 0.029471 | 22kV AC | Avalon Airport | 3220 | Geelong | Crossarm
On arrival crew isolated supply and carried out repairs. | 36 LUSH COURT, ALTONA MEADOWS VIC 3028 | 60473201 | Vandalism;Copper theft | [6 empty] | Report of cables from pit to pole have been stolen. Pit located at base of pole LIS # 962096. Halfway between Lush court & Central av. Upon arrival the PCA Field Crew have advised, that an unknown person has removed/stolen the recently installed Service Cable running from FOLCB at LV Pole LIS-212120 across the road to a recently installed LV Service Pit at No. 36 Tomkin Court, Altona Meadows. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | LV003 | Vandalism & copper theft | Damage to network assets | 27/02/2019 13:52 |  |  | 12365 |  |  | 20190321PWA_02 | Infrastructure (network-based) | -37.8712 | 144.7707 | 1 | Powercor | Report | 15547 | 0.039569 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Other
On arrival crew isolated supply and carried out repairs. | STATION ROAD, GISBORNE VIC 3437 | 60195578 | Copper theft | [6 empty] | Report of exposed wiring, appears someone has cut street light pole wiring, suspect theft at incident location. Crew found exposed pits and wiring with approximately 200m of 4x16mm copper cable taken. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | GSB013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43468.7326 |  |  | 12366 | Roadway |  | 20190321PWA_03 | Infrastructure (network-based) | -37.4727 | 144.5941 | 1 | Powercor | Report | 15548 | 0.018439 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
On arrival crew isolated supply. defect notice issued for POA repairs | 93 CROMER AVENUE, SUNSHINE NORTH VIC 3020 | 32177791 | Working too close to overhead lines | [6 empty] | Sunshine Motor Repairs and Tyres, Dilli 0433523675 reports a digger working next door at 93 Cromer Avenue, Sunshine North has broken the main wire is lying on ground, no supply. On arrival the fault crew found the excavator pulled down service line 91 Cromer Ave, while working in the yard at 93 Cromer Ave . The operator of the equipment had left the site. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | SSE032 | Excavator operating near service line | No Go Zone (contact);Damage to network assets | 43499.4493 |  |  | 12367 | Commercial |  | 20190321PWA_04 | Infrastructure (network-based) | -37.7515 | 144.8344 | 1 | Powercor | Report | 15550 | 0.035051 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Vehicle
on arrival crew isolated supply and carried out repairs | 41-53 ABEY ROAD, COBBLEBANK VIC 3338 | 60347046 | Copper theft | [6 empty] | A passer-by reported a vandalised electrical pit at the incident location. Upon arrival, the crew found that there were missing LV service cables in two pits, the total length of the cable is ~110 meters. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | copper theft | Damage to network assets | 43527.3993 |  |  | 12369 | Roadway |  | 20190321PWA_05 | Infrastructure (network-based) | -37.7056 | 144.5964 | 1 | Powercor | Report | 15554 | 0.0072917 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
A patrol of the line was undertaken and a section of twin sulfur conductor was found on the ground at pole 195 that is situated in Lodrigans Lane. The CEOT was notified of the conductor on the ground and SCWF were requested to have the TGTS-SCWF 66kV Line isolated and earthed. Repairs were completed as follows: Pole 194 â€“ Damaged insulator replaced Pole 195 & 196 â€“ Damaged insulators replaced, and patch rods (helical splices) installed on the damaged conductors. The repairs were completed at approximately 20:45 hours on Thursday March 21, 2019. CEOT were notified and the TGTS-SCWF 66kV Line was re-energised at approximately 06:00 hours on Friday March 22, 2019. The delay in restoring the line was due to staff from the SCWF not being available until 05:30 hours on the Friday morning. | 589 LONDRIGANS LANE, KOLORA VIC 3265 | SPAN POLE: 195-196 | Vandalism |  |  |  |  | Phase to earth | 1 | E0016104 - TGTS - SCWF 66kV Line Trip - On Wednesday March 20, 2019 at approximately 22:56 hours AEDT a fault occurred on the TGTS-SCWF 66kV Line. A first responder was dispatched to TGTS, and SCWF were advised . Phase conductor twinn Sulphur found on the ground at pole 195. | Conductor (bare) | 0 | 0 | 0 |  | 66kV TGTS - SCWF | "The evidence suggests that the insulator damage and subsequent failure was due to impact by external object" see attached investigation report | Loss of supply | 20/03/2019 22:56 |  |  | 12370 |  |  | 20190321SPN_02 | Infrastructure (network-based) | -38.1778 | 142.8625 | 1 | AusNet Services Transmission | Report | 17158 | 0.037722 | 66kV AC | Warrnambool Airport Ndb | 3265 | Kolora | Other
On arrival crew isolated supply and carried out repairs. | 2 BRAEBURN PLACE, WERRIBEE VIC 3030 | 60360780 | Vandalism | [6 empty] | Reed Wills 0439 382 024 reported possible attempted copper theft on LV mains. Pit was open on arrival with 3 circuits of LV U/Ground copper cable on footpath. Upon testing it was found that one circuit was still â€˜Liveâ€™ whilst the other two sections were de-energised. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | WBE023 | Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43527.4278 |  |  | 12374 | Roadway |  | 20190322PWA_02 | Infrastructure (network-based) | -37.9224 | 144.6333 | 1 | Powercor | Report | 15562 | 0.028167 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
On arrival crew isolated supply and carried out repairs. | UNIT 1 371 PUNT ROAD, CREMORNE VIC 3121 | 30200308 | Working too close to underground cables | [6 empty] | At the incident location â€˜Fulton Hoganâ€™ working on streamline programme advised that they were digging up the footpath hit a UG cable. He advised that the street light on pole #83318 went off but has come back on. Omar 0429107052 site engineer from Fulton Hogan said to the crew â€œthey were digging out the curb in center medium strip and the teeth on the bucket must have caught on the concrete slab and pulled on the neutral screen conductor feeding lighting center mediumâ€. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | R031 | During excavation works contact made with public lighting cable. | No Go Zone (contact);Damage to network assets | 43558.9986 |  |  | 12375 | Roadway |  | 20190322PWA_03 | Infrastructure (network-based) | -37.8248 | 144.9888 | 1 | CitiPower | Report | 15563 | 0.010343 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Cremorne | Dug up
Fault crew dispatched. S/stn isolated and site made safe. Damaged dropper leads replaced with new and installed as per standard | 208 LIVERPOOL ROAD, KILSYTH SOUTH VIC 3137 | LIS1208747 |  |  |  | Electrical breakdown;Not built/maintained to design | Poor workmanship |  |  | E0015870 - report of pole fire on s/stn pole from damaged HV leads. No evidence of ground fire | Transformer;Dropper/bridge | 0 | 1 | 0 |  | CYN22 | HV leads have been installed with an incorrect bending radius & reduced clearance at the TX end of the installation resulting in insulation break down and cable failure. | Pole-top fire | 18/03/2019 16:39 | 1 | Negligible: no ground fire | 12379 |  |  | 20190322SPN_02 | Infrastructure (network-based) | -37.8209 | 145.3169 | 1 | AusNet Services Distribution | Report | 15569 | 0.032865 | 22kV AC | Moorabbin Airport | 3137 | Kilsyth South | AF Other
Emergency high voltage switching was completed to isolate the faulted area, and the electrical infrastructure was repaired under Access Authority conditions. An LEI investigated the amount of damage that occurred to customers appliances and equipment. Procedures as indicated in the work instruction for HV injections has been followed. | 22-24 BLACKBURN ROAD, BLACKBURN VIC 3130 |  |  | Blown branch/vegetation |  | Mechanical breakdown |  |  | 1 | During windy weather, bark from a nearby tree fell across HV conductors. The feeder protection operated to clear the fault, but on reclose a connector failed resulting in HV conductor dropping onto LV conductor and causing HVI. | Conductor (bare) | 0 | 0 | 0 |  | NW21 | The initial cause was bark blown onto the HV conductors, however the failure of a connector was the cause of the HV conductor falling onto the LV conductor below. | HV injection | 22/03/2019 19:30 |  |  | 12408 | Roadway |  | 20190327UTD_01 | Infrastructure (network-based) | -37.8214 | 145.1523 | 1 | United Energy Distribution | Report | 17039 | 0.013008 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3130 | Blackburn | Connection
An LEI attended the site and undertook tests. Initial testing with no load connected had the NST passing and 3V present on the customer earthing system and 1 V at pool water. As the load was increased (>25A) the voltage did not increase at the same measured points. Further investigation found that the premises was the last installation on the UE LV circuit that was of considerable length. The same voltage tests were carried out on the circuit while heavily loaded (>25A), the voltage at the customer earthing system and pool water remained consistent. Final NST and network analyses passed and indicated positive results. The customer was left on supply. | 18 BIRDROCK AVENUE, MOUNT MARTHA VIC 3934 |  |  |  |  | Out of balance load |  |  | 2 | UE received report from customer that they have been feeling very slight tingles when coming into contact with the ground as they exit their pool. | Conductor (bare);Services cable;No failed asset | 2 | 2 | 2 |  |  | Cause appears to be the imbalance under certain periods of the LV circuit supplying this property. | Minor shock | 26/03/2019 16:27 |  |  | 12409 | Residential |  | 20190327UTD_02 | Infrastructure (network-based) | -38.2493 | 145.0315 | 1 | United Energy Distribution | Report | 15619 | 0.031198 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | AF Other
Site made safe, MFB and police attended site as well. Isolated and repairs made under access permit. Licensed electrical inspector ruled out high voltage injection. | 1 SHIRRA PLACE, ATTWOOD VIC 3049 |  |  | Property owner/customer |  |  |  |  | 1 | LBRA tree branch made contact with HV overhead conductor caused the HV to break and drop through LV and to the ground. This resulted in a small grassfire in the backyard of property 1 Shirra Place. The tree in question is a private tree is in the backyard of 1 Shirra Place. Photos and report from licensed electrical inspector (which rules out high voltage injection) are attached in the "Notes & Findings" section | Conductor (bare);Aluminium | 0 | 0 | 0 |  | BD07 | Vegetation: Trees Incident | Loss of supply;Grassfire | 29/03/2019 15:53 | 1 | Localised: less than 10 sq.m | 12422 | Residential |  | 20190330JEM_01 | Infrastructure (network-based) | -37.6739 | 144.8986 | 1 | Jemena | Report | 15638 | 0.0036169 | 22kV AC | Essendon Airport | 3049 | Attwood | Trees
Crew isolated supply to customer switchboard for the sprinklers 1/4/19 Zinfra Fault Crew and LEI carried out tests on the cabinet and measured 8.66 Volts from the metal frame of the Control Cabinet to an independent earth. A NST test was carried out at the FOLCB which confirmed a polarity fault. Zinfra then visually check the incoming cable at the top of pole A028208, at the junction box and noted that the neutral screen on the cable was corroded away, Zinfra repaired the connection and carried out another NST test, which passed. The RCD was tested at 30 mA and functioned correctly. A final NST was completed by the LEI which confirmed a Pass result. The installation was left on supply. | 34 NOLAN AVENUE, BROOKLYN VIC 3012 |  |  |  |  | Corrosion;Neutral fault |  |  | 2 | Whilst carrying out maintenance after solenoids for the sprinkler system had failed and when he touch the steel control box, the REC received a slight electric shock from the frame of the metal cabinet. A call had been made to report the shock and staff attended the site. Licensed electrical inspector attended site to investigate, report attached in the "Notes & Findings" section | Neutral screen | 2 | 2 | 2 |  |  | Neutral screen had disintegrated on the overhead service cable from pole no. A028208 | Minor shock | 43469.4014 |  |  | 12424 | Public space |  | 20190401JEM_01 | Infrastructure (customer connection) | -37.8223 | 144.8456 | 1 | Jemena | Report | 17047 | 0.017635 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Connection
CFA attended site and extinguished grass fire in the nature strip. Scorching on dropper leads but no damage to DB assets | 17 PARK STREET, EPPING VIC 3076 | LIS5645332 |  | Bird |  |  |  | Phase to earth |  | E0017237 - Report of ground fire following bird contacting O/H HV assets | Conductor (bare);Crossarm (steel);Pole (concrete) | 0 | 0 | 0 |  |  | Bird Incident | Grassfire | 27/03/2019 9:40 | 1 | Localised: less than 10 sq.m | 12426 |  |  | 20190401SPN_01 | Infrastructure (network-based) | -37.6409 | 145.0289 | 2 | AusNet Services Distribution | Report | 15642 | 0.037111 | 22kV AC | Essendon Airport | 3076 | Epping | Animal
LEI dispatched. Customer reported an electric shock while switching off a single gang switch located below the fridge doors that operate the chip fryer unit.(Chip Dump Master). All VESI test performed and passed. Voltage tests between an independent earth and various points of the electrical installation did not reveal any defective conditions or equipment. REC advised to replace single gang switch with new IP65 rated switch due to location. | 4379 ANZAC PARADE, WODONGA VIC 3690 | BUNNINGS-ANZAC kiosk |  |  |  | Fault on customer installation |  |  |  | E0018386 - Electric Shock reported by KFC employee when turning off the "Chip Dump Master Switch" on the fridge. | Customer installation;Customer appliance | 0 | 0 | 0 |  | WOTS12 | No fault identified that would account for electric shock. All VESI test performed and passed. Voltage tests between an independent earth and various points of the electrical installation did not reveal any defective conditions or equipment. REC advised to replace single gang switch with new IP65 rated switch due to location. | Minor shock | 30/03/2019 10:15 |  |  | 12428 | Commercial |  | 20190401SPN_02 | Infrastructure (network-based) | -36.1361 | 146.9066 | 2 | AusNet Services Distribution | Report | 16920 | 0.022619 | Low voltage AC (<1kV) | Wangaratta Aero | 3690 | Wodonga | AF Other
On arrival crew isloated supply and carried out repairs | 79 FINLAY ROAD, TONGALA VIC 3621 | 33091308 |  |  |  | Overheated connection |  |  |  | A PAL crew returning from another fault found CFA in attendance at a small grass fire at the incident location. On arrival crew found a HV isolator appears to have flashed. There were no reported injuries or third party property damage. | Disconnector/isolator | 2 | 2 | 2 |  | KYM004 | HV isolator overheated | Grassfire | 30/03/2019 18:24 | 1 | Small: 10 - 1000 sq.m | 12436 | Roadway |  | 20190402PWA_05 | Infrastructure (network-based) | -36.2547 | 144.9987 | 1 | Powercor | Report | 15657 | 0.040236 | 22kV AC | Shepparton Airport | 3621 | Tongala | Connection
On arrival crew isolated supply and carried out repairs | 174 GUNAMALARY ROAD, COWANGIE VIC 3506 | 32151897 |  |  |  | Leakage |  |  |  | CFA reported pole fire on Gunamalary Rd. On arrival crew found that a HV cross arm had burnt through at the kingbolt. The centre phase insulator was on the ground. A Ground fire had occurred, there were no reported injuries or third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire;Grassfire | 31/03/2019 13:36 | 1 | Small: 10 - 1000 sq.m | 12437 | Agricultural |  | 20190402PWA_06 | Infrastructure (network-based) | -35.3126 | 141.3017 | 1 | Powercor | Report | 15658 | 0.030227 | 22kV AC | Mildura Airport | 3506 | Cowangie | Crossarm
crew attended and removed service from fallen pole | MILL STREET, HORSHAM VIC 3400 | 30078522 |  |  |  | Rot |  |  | 2 | A fault crew responded to a report of a fallen pole and found that a private pole had failed and fallen onto the road. | Aluminium twisted (XLPE);Customer installation | 0 | 0 | 0 |  | HSM010 | Deteriorated pole | Loss of supply | 43802.4729 |  |  | 12440 | Commercial |  | 20190403PWA_01 | Infrastructure (network-based) | -36.7068 | 142.1986 | 1 | Powercor | Report | 16994 | 0.034855 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Pole
On arrival crew isolated supply and carried out repairs | 123 CROWS ROAD, WOODEND NORTH VIC 3442 | 30143989 | Vandalism;Copper theft | [6 empty] | Report received that Low voltage service cabling between pole LIS 938528 in Crows road to 182 Crows Road stolen (about 130meters removed). There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WND011 | Copper theft | Damage to network assets | 43558.5 |  |  | 12442 | Roadway |  | 20190403PWA_02 | Infrastructure (network-based) | -37.3255 | 144.4987 | 1 | Powercor | Report | 15665 | 0.030177 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend North | Other
confirmed all people clear of the line & no damaged. Supply restored. No repairs required | BONVALE, 32 SMITH STREET, OXLEY VIC 3678 | LIS5111486 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0018432 - Tip truck came in contact with HV wires while working on road | Conductor (bare) | 0 | 0 | 0 |  | WN5 | Wangaratta City Council tip truck was working on the Oxley Meadow Creek Rd when it came into contact with the overhead 22KV conductors while re-sealing the road. No damage was sustained to the driver, truck or conductor. WN5 feeder CB operated and isolated supply to the area No fire starts | No Go Zone (contact) | 43528.5528 |  |  | 12449 |  |  | 20190403SPN_05 | Infrastructure (network-based) | -36.4492 | 146.3842 | 2 | AusNet Services Distribution | Report | 16934 | 0.0014977 | 22kV AC | Wangaratta Aero | 3678 | Oxley | Vehicle
The attending Powercor Fault Crew replaced the existing O/H Service Cable from the Reticulation Pole to Customerâ€™s FOLCB | 69 MACKENZIE STREET, BENDIGO VIC 3550 | 32053307 |  |  |  | Neutral fault;Mechanical vibration |  |  | 2 | Person was in the Bathroom operating a metal Tap when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on a timber floor. | Service conductor | 0 | 0 | 0 |  | BET006 | Loose O/H Service Neutral Conductor termination at the Pole Top Connection Box | Minor shock | 23/02/2019 11:00 |  |  | 12453 | Residential |  | 20190404PWA_03 | Infrastructure (network-based) | -36.7602 | 144.2728 | 1 | Powercor | Report | 15680 | 0.016045 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | Connection
Fault Crew reterminated the existing O/H Service Cable in the Pole Type Connection Box located on the Reticulation Pole | 44 MERRIVALE DRIVE, WARRNAMBOOL VIC 3280 | 30137699 |  |  |  | Corrosion |  |  | 2 | person was in the Kitchen washing his hands at the Sink when he received an electric shock as he made simultaneous contact with his hand on the Metal Tap and his bare stomach in contact with the metallic Kitchen Sink. | Service conductor | 0 | 0 | 0 |  | WBL004 | Corroded O/H Service Neutral Conductor termination at the Pole | Minor shock | 21/02/2019 7:00 |  |  | 12454 |  |  | 20190404PWA_04 | Infrastructure (network-based) | -38.3825 | 142.4654 | 1 | Powercor | Report | 15681 | 0.027979 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Fault Crew replaced the existing O/H Neutral Screened Four Wire Service Cable | 120 WEBSTER STREET, LAKE WENDOUREE VIC 3350 | 32006986 |  |  |  | Corrosion |  |  | 2 | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Tap and his bare feet whilst standing on the wet shower base and waste water outlet. | Service conductor;Neutral screen | 0 | 0 | 0 |  | BAN005 | Corroded O/H Neutral Screen Conductor | Minor shock | 28/02/2019 9:20 |  |  | 12455 | Residential |  | 20190404PWA_05 | Infrastructure (customer connection) | -37.5561 | 143.8461 | 1 | Powercor | Report | 15682 | 0.041351 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Lake Wendouree | OH Cable
Fault crew attended and disconnected supply prior to LEI attending. The Tenant in the property was unable to provide any information regarding the person or the nature of the incident as they were not home at the time the incident occurred. | 4 LEAWARRA CRESCENT, DELACOMBE VIC 3356 | 32006986 |  |  |  | Corrosion |  |  | 2 | Person reportedly received an electric shock from the metal Tap in the front yard. | Services cable | 0 | 0 | 0 |  | BAS021 | crew found some corrosion in connection | Minor shock | 14/02/2019 0:00 |  |  | 12456 |  |  | 20190404PWA_06 | Infrastructure (customer connection) | -37.5561 | 143.8461 | 1 | Powercor | Report | 15683 | 0.0097384 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3356 | Delacombe | Connection
REC replaced Customers Fused Overhead Line Connection Box and powercor crew replaced the O/H Service Cable | 305 EDGAR STREET, PORTLAND VIC 3305 | 32124775 |  |  |  | Corrosion |  |  | 2 | Customer was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Taps and his bare feet whilst standing on the wet shower base and waste water outlet. | Service conductor;Customer installation | 0 | 0 | 0 |  | PLD006 | corroded FOLCB terminal and incoming service cable | Minor shock | 43468.375 |  |  | 12462 | Residential |  | 20190405PWA_01 | Infrastructure (customer connection) | -38.3628 | 141.5925 | 1 | Powercor | Report | 15690 | 0.010749 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Connection
Attending crew repaired connection at the pole box | 133 HEATH STREET, PORT MELBOURNE VIC 3207 | 30201775 |  |  |  | Corrosion |  |  | 2 | Person received an electric shock when he simultaneously contacted the effectively earthed appliance(s) with his hands and standing on concrete floor bare foot | Service conductor | 0 | 0 | 0 |  | MG001 | Corroded connection at pole connection box | Minor shock | 28/02/2019 20:00 |  |  | 12465 | Residential |  | 20190405PWA_04 | Infrastructure (network-based) | -37.8338 | 144.9457 | 1 | CitiPower | Report | 15693 | 0.034262 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Connection
The fault crew questioned the people on site however they did not know who the crane company was as they were workers and English was not their first language. The crew on site checked the conductors and found no signs of any damage and said although they didn't check the height of the conductors, there was more than the required clearance. The crew checked that everything was safe, then replaced the blown fuses. Action raised to have Customer consultant attend the site and discuss No Go Zone with customer | 4385 SOUTH GIPPSLAND HIGHWAY, CALDERMEADE VIC 3984 | LIS524359 and LIS524358 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0018488 - customers reported an outage after advising a silo was being moved and came into contact with O/H HV. | Conductor (bare) | 0 | 0 | 0 |  | LLG11 | Third party was moving a silo on site when it came into contact with O/H HV. customers reported an outage after advising a silo was being moved, came into contact with the HV on the customer's property. Fault crew confirmed no damage to conductor and that the upstream fuses were blown. Investigation has identified that it was most likely a mobile crane which contacted the conductors | No Go Zone (contact) | 43559.5375 |  |  | 12467 |  |  | 20190405SPN_02 | Infrastructure (network-based) | -38.2416 | 145.5286 | 1 | AusNet Services Distribution | Report | 15696 | 0.017324 | 22kV AC | Moorabbin Airport | 3984 | Caldermeade | Vehicle
MMFB attended site to extinguish fire Jemena work crew arrived on site, isolated asset and made safe | 34 YORK AVENUE, IVANHOE EAST VIC 3079 | A016819 |  |  |  | Electrical breakdown |  |  | 2 | Small vegetation fire (tree on property) due to molten metal falling from LV fused switch which failed outside 34 York Avenue, Ivanhoe East No photo is available for this incident | Any other type | 0 | 0 | 0 |  | HB14 | LV fused switch failure due to electrical deterioration and failure to carry load | Other vegetation | 43742.1764 | 1 | Negligible: no ground fire | 12488 | Residential |  | 20190410JEM_01 | Infrastructure (network-based) | -37.7705 | 145.0552 | 1 | Jemena | Report | 17748 | 0.016973 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe East | Connection
Crews isolated the site, and issued a defect notice for the customer to perform repairs. | 45 BUNNETT STREET, SUNSHINE NORTH VIC 3020 | 30118061 | Unauthorised access;Copper theft | [6 empty] | A customer called to report that fuses on the substation had been opened by burglars on the weekend, and that they had cut a cable and exposed cables. On arrival the crew found that the 22kV HV fuses on the substation had been opened by an unknown person, and they had cut and attempted to steal some of the customers underground LV mains between the substation and the building. The crew said that they believe the thieves had been disturbed and had not completed stealing the cables. There were no reported injuries or fires. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | SSE032 | Atempted copper theft | Damage to network assets | 43802.3597 |  |  | 13490 | Industrial |  | 20190410PWA_02 | Infrastructure (network-based) | -37.7624 | 144.8404 | 1 | Powercor | Report | 16739 | 0.008559 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Other
On arrival crew isolated supply and carried out repairs. | 1259-1265 PLUMPTON ROAD, FRASER RISE VIC 3336 | 32170474 | Copper theft | [6 empty] | Customer called to report damage to fuse box on pole and loss of power. Upon arrival the fault crew found that the LV underground service cable between the pit 3m away and pole LIS-111853 had been removed from the conduit. In doing so, possibly by driving a vehicle away while the underground service was still connected, the thieves have damaged one of the other FOLCB's (there are 3x LV undergrounds serviced from this pole), which in turn has caused a loss of supply to the other property connected from the same pole. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 13/03/2019 18:55 |  |  | 13491 | Roadway |  | 20190410PWA_03 | Infrastructure (network-based) | -37.7094 | 144.6936 | 1 | Powercor | Report | 16729 | 0.026802 | Low voltage AC (<1kV) | Melbourne Airport | 3336 | Fraser Rise | Other
Crew confirmed isolation repairs arranged | 19 STATION ROAD, GISBORNE VIC 3437 | 30338658 | Vandalism;Copper theft | [6 empty] | Powercor employee reported copper theft from PL circuit on the Calder HWY outbound onramp at Gisborne. Upon arrival the fault crew found that thieves had returned since the 10th of March and stolen the remainder of the 4 core 16mm copper public lighting cable supplying the lighting on that segment of the on ramp. Approximately 100m of LV PL cable was stolen, now needing to be replaced between 4 service pits. No injury or shock reported, additional theft reported to Gisborne police. | Services cable | 2 | 2 | 2 |  | GSB013 | Copper theft | Damage to network assets | 13/03/2019 0:00 |  |  | 13492 | Roadway |  | 20190410PWA_04 | Infrastructure (network-based) | -37.4737 | 144.5927 | 1 | Powercor | Report | 16730 | 0.035483 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
On arrival crew isolated supply and replaced service line. | 310 DANKS STREET, MIDDLE PARK VIC 3206 | 30213586 |  |  |  | Mechanical breakdown |  |  |  | Inspectors doing routine testing on steel poles found LIS #37047 live at 240v. Fault crew arrived on site found that the service line going to 310 Danks St Middle Park has rubbed against a lighting bracket stay wire . There was no fire, no reported injuries or shocks. | Pole (steel) | 2 | 2 | 2 |  | AP008 | Service line rubbed through by steel lighting bracket stay | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43712.8472 |  |  | 13493 | Roadway |  | 20190410PWA_05 | Infrastructure (network-based) | -37.8507 | 144.9578 | 1 | CitiPower | Report | 16732 | 0.011818 | Low voltage AC (<1kV) | Essendon Airport | 3206 | Middle Park | AF Other
Fault crew dispatched. Candled Boric Acid HV fuse replaced. | 540 MT BEENAK ROAD, THREE BRIDGES VIC 3797 | LIS2601656341 |  |  |  | Candled fuse |  |  |  | E0021377 - report of candled BA HV Fuse | Boric acid | 0 | 0 | 0 |  | WYK23 | Candled BA HV Fuse. No evidence of ground fire | Pole-top fire | 13/06/2019 11:42 | 1 | Negligible: no ground fire | 13903 |  |  | 20190618SPN_01 | Infrastructure (network-based) | -37.8611 | 145.6391 | 2 | AusNet Services Distribution | Report | 17791 | 0.013416 | 22kV AC | Moorabbin Airport | 3797 | Three Bridges | Fuse
Advised builder James Cicero to cease work and create a No Access area within 3000 mm of LV overhead . | 26 SALISBURY STREET, WERRIBEE VIC 3030 | 31024819 | Building too close or within the No Go Zone | [5 empty] | 2 | Building erected in breach of installations regulations (r313) from LV bare overhead conductors. Structure is under construction and has clearance of 2700 mm below and 1000mm alongside LV Overhead | Conductor (bare) | 0 | 0 | 0 |  | WBE034 | Building under construction near overhead lines. | No Go Zone (no contact) | 20/06/2019 9:00 |  |  | 13912 | Construction |  | 20190624PWA_03 | Infrastructure (network-based) | -37.9023 | 144.6647 | 1 | Powercor | Report | 17386 | 0.010899 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
Attending Powercor fault crew re-terminated exposed end. Repairs were effected to the rest of the lighting circuit, and lighting was restored to the remainder of the circuit. | 107-115 ABEY ROAD, COBBLEBANK VIC 3338 | 30336495 | Vandalism;Copper theft | [6 empty] | Passing Powercor fault crew noticed absence of area lighting in Abey Rd west of Bundy Drive. Attending Powercor fault crew noted approx. 150 route metres of underground lighting cable cut and stolen between poles LIS 842964, 842965 & 842966. Live end had been left exposed. Interference to, and theft of underground cable has occurred previously at this location. There were no shocks, injuries or ground fire. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 19/06/2019 19:50 |  |  | 13914 | Roadway |  | 20190624PWA_05 | Infrastructure (network-based) | -37.7053 | 144.5939 | 1 | Powercor | Report | 17388 | 0.04114 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
On arrival crew isolated supply and carried out repairs | 135-165 ABEY ROAD, COBBLEBANK VIC 3338 | 31034745 | Vandalism;Copper theft | [6 empty] | Passer by reported Copper theft in various locations along abey rd. Also refer to 20190624PWA_05 same general location. No fire and no injuries reported. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 20/06/2019 11:25 |  |  | 13918 |  |  | 20190625PWA_03 | Infrastructure (network-based) | -37.7045 | 144.5871 | 1 | Powercor | Report | 17392 | 0.03009 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
cables excavated and repairs made | 260 CECIL STREET, SOUTH MELBOURNE VIC 3205 | 30170864 |  |  |  | Not built/maintained to design |  |  | 1 | High voltage cable failed, it was subsequently found that during the installation of a LV cable, the boring tip has made contact with the cable resulting in damage to the insulation. The insulation deteriorated and then failed on 16th June 2019. | Cable | 0 | 0 | 0 |  | AP006 | works undertaken close to HV cable, | Loss of supply | 17/06/2019 14:00 |  |  | 13926 | Roadway |  | 20190627PWA_04 | Infrastructure (network-based) | -37.8361 | 144.9589 | 1 | CitiPower | Report | 17417 | 0.039001 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3205 | South Melbourne | Dug up
fault crew attended and made safe, underground crew attended and capped cable. | 10 ST JAMES PLACE, TOORAK VIC 3142 | 30218002 | Unauthorised access | [5 empty] | 2 | Fault crew attended site after demolition company partially removed supply cables. | Services cable | 0 | 0 | 0 |  | TK005 | interference with assets during building demolition | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/06/2019 13:22 |  |  | 13927 | Roadway |  | 20190627PWA_05 | Infrastructure (customer connection) | -37.8479 | 145.0202 | 1 | CitiPower | Report | 17404 | 0.030978 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Other
Fault crew and LEI dispatched. Fault crew identified the star picket had damaged the U/G cable supplying 184 and 190 Mt Lookout Rd, causing it to become live resulting in the customer receiving an electric shock. Cable was isolated and repaired. Tests carried out and passed and supply restored. | 196 MOUNT LOOKOUT ROAD, MOUNT TAYLOR VIC 3875 | LIS1605565 | Working too close to underground cables |  |  |  |  | Phase to earth |  | E0021757 - customer reported receiving electric shock whilst removing existing star picket from his property | Cable | 0 | 0 | 0 |  | BDL44 | Matt recently purchased the property and was removing previously installed star pickets. He had dug around the star picket and cut the base with an angle grinder, when he went to break it off he received a severe shock. Fault crew and LEI dispatched to investigate and found the star picket had damaged the U/G cable causing it to become live. | Minor shock | 24/06/2019 13:52 |  |  | 13925 |  |  | 20190627SPN_01 | Infrastructure (network-based) | -37.7701 | 147.5825 | 1 | AusNet Services Distribution | Report | 17402 | 0.040946 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Mount Taylor | Other
LEI and fault crew dispatched. REC ran an independant earth and measured 10V AC. REC attended and repaired MEN and earth to meterboard. All tests carried out and passed following repairs. Follow up visit organised to rebalance street circuits. | 35 BYRNE STREET, LEONGATHA VIC 3953 | LIS2003181 |  |  |  | Out of balance load;Fault on customer installation |  | Phase to earth |  | E0021856 - REC reported receiving 'tingles' from ground next to HWS | Meter board (including fuses);Customer installation | 0 | 0 | 0 |  | LGA22 | REC was attending to a HWS not operating correctly and knelt down on the grass to remove the cover when he felt a tingle. Found no earth on metal meterboard. REC attended and repaired MEN and earth to meterboard. All tests carried out and passed following repairs. Further tests carried out which identified street circuits out of balance which may have contributed to the electric shock. Follow up visit organised to rebalance street circuits. | Minor shock | 26/06/2019 9:18 |  |  | 13931 |  |  | 20190628SPN_01 | Infrastructure (network-based) | -38.4877 | 145.9464 | 1 | AusNet Services Distribution | Report | 17408 | 0.018802 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha | Installation
â€¢ The Vegetation Crew notified their Supervisors of the Incident. â€¢ Zinfra Management notified Jemena Network Operations and Control of the incident and requested a fault crew to attend. â€¢ Zinfra Management secured the site and made contact with the impacted customer. â€¢ Zinfra Fault Response crew attended and rectified the fault. â€¢ Zinfra commenced an investigation. | 90 GLASS STREET, ESSENDON VIC 3040 | [5 empty] | Poor workmanship |  | 2 | During planned vegetation clearing works, a sub-contracted vegetation worker made inadvertent contact to the adjacent customerâ€™s neutral screen service causing damage to the adjacent service. Planned Zinfra vegetation works were conducted in the front yard of 90 Glass St, Essendon with the focus of clearing vegetation from a cross over service supplying 88 Glass St. The sub-subcontracted vegetation crew to Zinfra (Active Tree Services â€“ Underline Tree Clearing), had completed their site risk assessment and proceeded to undertake vegetation clearing activities with both battery powered and hand powered pole saws. The vegetation crew were clearing overhanging branches of an overhanging Ash tree when the Pole Saw Operator (Using a battery powered pole saw) made contact with the adjacent neutral screen service (Image 1). The Pole Saw Operator understands the clearance requirements for cutting, however, with a momentary lapse of concentration, he has overlooked the need to maintain effective control of the running chainsaw post cut. The subsequent movement of the pole saw made contact with the neutral screen service (Image 2). The resultant impact damaged the outer insulation, neutral screens (30%) and made contact with the exposed active conductor within. | Neutral screen | 0 | 0 | 0 |  |  | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43472.3646 |  |  | 13940 | Residential |  | 20190701JEM_01 | Infrastructure (network-based) | -37.7461 | 144.9143 | 1 | Jemena | Report | 17621 | 0.013988 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Other
On arrival crew isolated supply and carried out repairs | 110 CARINA NORTH ROAD, CARINA VIC 3512 | 32153602 |  |  |  | Leakage |  |  |  | Following report from customer a pole fire was found at the incident location. On arrival crew found end burnt of crossarm and conductor hanging low across paddock. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 43528.5486 | 1 | Negligible: no ground fire | 13939 | Agricultural |  | 20190701PWA_04 | Infrastructure (network-based) | -35.2547 | 141.1078 | 1 | Powercor | Report | 17416 | 0.036332 | 22kV AC | Mildura Airport | 3512 | Carina | Crossarm
On arrival crew isolated supply, crossarm replaced | BLAKE ROAD, IRAAK VIC 3494 | 30098951 |  |  |  | Leakage |  |  |  | Customer reports pole fire at incident location. On arrival crew found termination crossarm burnt There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT014 | Excessive leakage current | Pole-top fire | 23/04/2019 11:39 | 1 | Negligible: no ground fire | 13943 | Agricultural |  | 20190701PWA_06 | Infrastructure (network-based) | -34.4274 | 142.3492 | 1 | Powercor | Report | 17421 | 0.031574 | 22kV AC | Mildura Airport | 3494 | Iraak | Crossarm
A faults truck attended and replaced the blue phase HV powder filled fuse at pole No. LIS 0629670 that restored supply to the customers supplied from the pole type substation. | 29 ROSEBANK AVENUE, CLAYTON SOUTH VIC 3169 | 629670 |  |  |  | Candled fuse |  |  |  | UE received a report of sparks coming from the top of a pole. On attendance, the fault crew found the Blue phase Powder Filled Fuse had candled. | Powder filled | 0 | 0 | 0 |  | SV33 | The cause of the fuse candling is unknown. | Plant/equipment | 43622.3889 | 1 | Negligible: no ground fire | 13960 |  |  | 20190704UTD_01 | Infrastructure (network-based) | -37.9392 | 145.1311 | 1 | United Energy Distribution | Report | 17516 | 0.0040683 | 22kV AC | Moorabbin Airport | 3169 | Clayton South | Fuse
Emergency switching was performed to isolate the faulty asset and restore supply to customers. Repairs of the HV UG cable termination and the LV UG cable termination on the pole were instigated under access authority conditions. | 94-106 PATTERSON ROAD, BENTLEIGH VIC 3204 | 1803554 |  |  |  | Moisture ingress |  |  | 1 | At 6:05pm on Saturday 22 June, feeder CB MR14 reclosed and opened to lockout. Soon after, UE received a report from the fire authority of "powerlines on fire". On attendance, fault crew found a Cabus box HV underground cable pole top termination had failed. Damage was also sustained to the LV UG cable termination on the same pole. | Cable;Connector/termination | 1 | 0 | 0 |  | MR14 | The cause of the Cabus box failure is unknown, however a common cause is moisture ingress over time. | Loss of supply;Plant/equipment | 22/06/2019 18:05 | 1 | Negligible: no ground fire | 13962 | Roadway |  | 20190704UTD_03 | Infrastructure (network-based) | -37.9257 | 145.0349 | 1 | United Energy Distribution | Report | 17453 | 0.0067627 | 22kV AC | Moorabbin Airport | 3204 | Bentleigh | Connection
Replaced 3 phase fuse mains box at pole end. | UNIT 5 6 AUSTIN STREET, FAIRFIELD VIC 3078 |  |  |  |  | Corrosion |  |  | 2 | Customer was washing up prior to going to bed at 21:00 on 28/6/19, when she turned on the hot tap she received a tingling sensation from it. The truck checked the FOLCB on the Reticulation Pole A012251 and found the neutral conductor and neutral bar corroded and burnt. The FOLCB on the Reticulation Pole was replaced by the Fault Crew and VESI testing carried out. LEI also requested Jemena carry out current measurements to see if the mains have been overloaded as the cable at the FOLCB was showing signs of heat deterioration. The Installation was left ON Supply. | Connection box | 0 | 0 | 0 |  |  | Failed 3 phase fuse mains box at pole. | Minor shock | 28/06/2019 21:00 |  |  | 13968 | Residential |  | 20190705JEM_01 | Infrastructure (network-based) | -37.7838 | 145.0195 | 1 | Jemena | Report | 17461 | 0.025507 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Fairfield | Fuse
UE dispatched fault crews. The crews found that a council tree had fallen onto a HV tee line. An upstream line fuse operated as a result of the fault. A small patch of grass of 1 sq metre had burnt. An EIO was also dispatched to investigate for HVI, and confirmed there was no HVI. The fault crews undertook emergency switching to isolate the faulty section, and instigated repairs to the line. | 1003 FRANKSTON-FLINDERS ROAD, SOMERVILLE VIC 3912 | 1109629 |  | Fallen | [5 empty] | UE received a report from the fire authority of wires down and a grass fire. | Conductor (bare) | 0 | 0 | 0 |  | HGS22 | Vegetation: Trees Incident | Grassfire | 43472.4868 | 1 | Localised: less than 10 sq.m | 13970 | Roadway |  | 20190705UTD_01 | Infrastructure (network-based) | -38.2188 | 145.1724 | 1 | United Energy Distribution | Report | 17463 | 0.0049954 | 22kV AC | Moorabbin Airport | 3912 | Somerville | Trees
Fault crew dispatched and removed the Tree from the line and re strung the HV and LV conductors. LEI Completed installation checks on the customers directly impacted impacted by the tree and all tests passed. Some customer appliance damage identified by HVI | 75 DAPHNE DRIVE, MOE SOUTH VIC 3825 | LIS2208584 |  | Blown branch/vegetation | [5 empty] | E0022093 - HVI reported | Conductor (bare) | 0 | 0 | 0 |  | MOE31 | Vegetation: Trees Incident | HV injection | 29/06/2019 18:30 |  |  | 13980 |  |  | 20190708SPN_06 | Infrastructure (network-based) | -38.2155 | 146.2491 | 2 | AusNet Services Distribution | Report | 17478 | 0.041345 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Moe South | Trees
Site was visited by crew, photos taken and Enabalon report completed. | 18 HEDWIG DRIVE, MOOROOLBARK VIC 3138 | LIS1013440 | Vehicle | [5 empty] | 2 | Car caught fire next to pole. Scorched pole approx. 3m up on one side, and burnt out a tree and caused significant damage to the road base. No significant damage to the Pole or other AusNet Services assets. Refer to the attached site photos. | Pole (wood) | 0 | 0 | 0 |  | CPK13 | Caused by third party vehicle fire. | Grassfire | 43715.1625 | 0 | Localised: less than 10 sq.m | 13988 |  |  | 20190710SPN_01 | Infrastructure (network-based) | -37.7683 | 145.3092 | 2 | AusNet Services Distribution | Report | 17488 | 0.0023947 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | Pole
Crew replaced the neutral bridge at the Service Pole | 51 ROSS STREET, PORT MELBOURNE VIC 3207 | 30204145 |  |  |  | Corrosion |  |  | 2 | Person was in the kitchen using the kitchen sink tap when he received an electric shock as he made simultaneous contact between her hand on the metal taps and her other hand touching the kitchen sink . | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | PM008 | Corroded O/H Neutral Conductor bridge at the Pole located on the Reticulation Service Pole. | Minor shock | 25/06/2019 21:00 |  |  | 13996 | Residential |  | 20190712PWA_01 | Infrastructure (network-based) | -37.8363 | 144.9361 | 1 | CitiPower | Report | 17497 | 0.034186 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Connection
Crew attended and made the site safe | 148-200 ABEY ROAD, COBBLEBANK VIC 3338 | 30336492 | Copper theft | [6 empty] | Employee states that driving down Abey Rd, Cobblebank & saw 2 pits that have had lid removed & there were wires exposed. Suspects copper thieves On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen the 4c 16mm LV Service Cable within the LV Service Pits supplying the recently PL Lighting Poles from outside 80-90 Abey Road heading west to 148-200, Cobblebank, 3338 (Melton South) Approximately 1,120m of 4c 16mm LV Service Cable has been cut away and stolen from the LV Service Pit at PL Lighting Pole There was no fire, no reported injuries or third party poperty damage. | Services cable | 2 | 2 | 2 |  | MLN011 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/06/2019 15:22 |  |  | 13999 | Roadway |  | 20190715PWA_02 | Infrastructure (network-based) | -37.705 | 144.5914 | 1 | Powercor | Report | 17500 | 0.028285 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
Supply checked, NST passed 1-2.9 volts detected | 2 MOSS STREET, EDENHOPE VIC 3318 | 32099516 |  |  |  | Out of balance load |  |  | 2 | Edenhope/ Apsley Netball Club Team Members were showering in the Change Room when several Team Members felt they received a minor electric shock as they made simultaneous contact between their hands on the metal Shower Rose and their bare feet while standing on the wet shower base. | Conductor (bare) | 0 | 0 | 0 |  | CHM001 | Voltage tests between an independent earth and various parts of the electrical installation identified a Load Imbalance in the Clubrooms and a potential Load Imbalance on the LV Street Circuit and the Sub-station. | Minor shock | 21/06/2019 14:00 |  |  | 14001 | Public space |  | 20190715PWA_04 | Infrastructure (network-based) | -37.0378 | 141.2834 | 1 | Powercor | Report | 17502 | 0.0035579 | Low voltage AC (<1kV) | Horsham Aerodrome | 3318 | Edenhope | AF Other
No action taken as the assets were removed by unknown persons. | 2 DUDLEY STREET, FOOTSCRAY VIC 3011 |  | Theft;Unauthorised work | [5 empty] | 2 | Metering & Service crew attended the site for abolishment of supply and metering in conjunction with a new connection for an overhead BTS. When the crew arrived they found a demolished and vacant site ready and prepared for construction with no electricity service line or meter on site. | Service conductor;Smart meter | 2 | 2 | 2 |  |  | Unknown person removed overhead service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43562.1819 |  |  | 14008 | Residential |  | 20190716JEM_02 | Infrastructure (customer connection) | -37.7939 | 144.8832 | 2 | Jemena | Report | 17509 | 0.023551 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Other
Upon arrival the attending L.E.I. conducted voltage tests between an independent earth to various parts of the electrical installation, including the tap in which the shocks were received, recording a voltage of 34.2 volts under load. At this this stage a damaged/high impedance neutral conductor was identified at the neutral screened service cable feeding the installation and attended Jemena construction crew was replaced the service. This high impedance neutral conductor resulted in current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond and metallic water pipe. | 11 JUKES ROAD, FAWKNER VIC 3060 |  |  |  |  | Age;Corrosion;Neutral fault |  |  | 2 | The electric shock was first noticed when the customer was turning on the metallic water tap at the rear of the house and simultaneously made contact between his bare hand and the ground in which he was standing. | Service conductor;Neutral screen | 2 | 2 | 2 |  |  | A damaged/high impedance neutral conductor . | Minor shock | 43531.7083 |  |  | 14017 | Residential |  | 20190717JEM_04 | Infrastructure (customer connection) | -37.7033 | 144.9777 | 1 | Jemena | Report | 17528 | 0.033567 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | OH Cable
On arrival crew inspected assets and restored supply | 77-95 MURRAY ROAD, THORNHILL PARK VIC 3335 | 30108506 | Working too close to overhead lines | [6 empty] | Following a fault call crew found that a Concrete Pumping Truck had contacted the HV line mid span causing HV PF fuse to operate. Pumper left scene before operator and company details could be obtained. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | MLN021 | Concrete pumper contacted conductors | No Go Zone (contact) | 15/07/2019 8:06 |  |  | 14013 | Roadway |  | 20190717PWA_02 | Infrastructure (network-based) | -37.7158 | 144.6307 | 1 | Powercor | Report | 17524 | 0.037813 | 22kV AC | Laverton Raaf | 3335 | Thornhill Park | Vehicle
On arrival supply isolated and repairs completed | 530-568 COBURNS ROAD, KURUNJANG VIC 3337 | 30344877 | Vandalism;Copper theft | [6 empty] | Ben Houtten ph 0438006394 - reported a pit located at 544 Coburns Rd, Kurunjang has been tampered with, appears to be copper theft, and wires exposed and hanging out of pit, could be live, also the next pit along has been opened up (northbound). There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN014 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43623.4688 |  |  | 14027 | Roadway |  | 20190719PWA_04 | Infrastructure (network-based) | -37.6525 | 144.5743 | 1 | Powercor | Report | 17546 | 0.02561 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Other
On arrival crew isolated supply and carried out repairs. | C GREEN BALLARAT DELIVERY CO PTY LTD, 31 OLD MIDLAND HIGHWAY, MOUNT ROWAN VIC 3352 | 30013024 | Working too close to underground cables | [6 empty] | A customer reported an outage at the incident location. Upon arrival a Powercor crew found that an UG LV cable had been dug up by a contractor. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BAN009 | Excavator struck LV cable | Damage to network assets | 43684.4167 |  |  | 14034 |  |  | 20190722PWA_04 | Infrastructure (network-based) | -37.5157 | 143.8478 | 1 | Powercor | Report | 17554 | 0.014446 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Dug up
Fault crew dispatched. O/H conductors repaired and supply restored | 29 WARRINGAH DRIVE, CHUM CREEK VIC 3777 | LIS1411390 |  | Fallen |  |  |  |  | 2 | Report of O/H HV conductors on ground | Conductor (bare) | 0 | 0 | 0 |  | LDL23 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/07/2019 12:07 |  |  | 14032 | Roadway |  | 20190722SPN_01 | Infrastructure (network-based) | -37.6241 | 145.5091 | 1 | AusNet Services Distribution | Report | 17552 | 0.027946 | 22kV AC | Moorabbin Airport | 3777 | Chum Creek | Trees
Fire brigade extinguished fire. Fault crew dispatched and street light isolated in pit. Failed street light replaced with new | 743 BORONIA ROAD, WANTIRNA VIC 3152 | LIS5625514 |  |  |  | Defective component |  |  |  | Report of street light fire | Public lighting | 0 | 0 | 0 |  | BRA11 | Investigation concluded that the igniter appears to have failed resulting in the street light catching fire. No evidence of ground fire | Pole-top fire | 19/07/2019 8:38 | 1 | Negligible: no ground fire | 14035 | Roadway |  | 20190722SPN_03 | Infrastructure (network-based) | -37.8469 | 145.2219 | 1 | AusNet Services Distribution | Report | 17556 | 0.013167 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | AF Other
UE dispatched a fault crew and an EIO to investigate. The fault crew undertook emergency switching to isolate the transformer and the LV circuits. The EIO inspected over 200 premises for any damage, and found one premise with minor property damage. The fault crew replaced the transformer and restored supply to premises as they were cleared by the EIO. | 39 BOWMORE ROAD, NOBLE PARK VIC 3174 | 633382 |  |  |  | Neutral fault;Overheated connection |  |  | 1 | Network Analytics identified high volts on premises supplied from Jenkins Bowmore distribution substation. On attendance, faults crews found a burnt out neutral connection at the transformer causing an overvoltage to premises supplied from that substation. | Pole mounted | 0 | 1 | 0 |  |  | It is believed that the overvoltage incident was caused by the broken neutral at the transformer. Evidence shows the broken neutral resulted from thermal damage that was most likely caused by high resistance connection. | Less than $50k damage;Melting or smoking only | 43592.8493 |  |  | 14040 | Residential |  | 20190723UTD_01 | Infrastructure (network-based) | -37.9578 | 145.1767 | 1 | United Energy Distribution | Report | 17571 | 0.016581 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Connection
On arrival crew isolated supply and carried out repairs | 2375 SPRINGFIELD ROAD, CHILLINGOLLAH VIC 3585 | 32155903 |  |  |  | Leakage |  |  |  | A customer reported a wire hanging low in the mid air and smoke coming from the pole at the incident location. The attended crew found that the angle cross arm burnt through on the pole. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | SHL001 | Excessive leakage current | Pole-top fire | 16/07/2019 15:24 | 1 | Negligible: no ground fire | 14049 | Roadway |  | 20190724PWA_02 | Infrastructure (network-based) | -35.262 | 143.0506 | 1 | Powercor | Report | 17573 | 0.020359 | 22kV AC | Swan Hill Aerodrome | 3585 | Chillingollah | Pole
On arrival crew isolated supply and carried out repairs | 72A BEACONSFIELD PARADE, ALBERT PARK VIC 3206 | 30206472 | Working too close to underground cables | [6 empty] | Call received reporting an excavator had damaged a cable at incident location. On arrival a crew found a contractor had damaged a low voltage public lighting TPS cable. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | AP015 | Contractor using excavator struck cable | No Go Zone (contact);Damage to network assets | 17/07/2019 10:01 |  |  | 14056 | Roadway |  | 20190724PWA_07 | Infrastructure (network-based) | -37.8469 | 144.9469 | 1 | CitiPower | Report | 17581 | 0.0023519 | Low voltage AC (<1kV) | Essendon Airport | 3206 | Albert Park | Dug up
Immediate Actions on â€¢ The NGZ team member on site cancelled the Jemena PTW, as the clearances to overhead power lines had not been maintained. â€¢ Work Safe Inspector placed a prohibition notice on any productive construction work associated with the area facing High Street and any rectification works to remedy the contravention. Remedial Actions â€¢ Builder to review Safe Work Systems and SWMS and communicate/demonstrate to Work Safe the systems that will be in place to ensure NGZ clearance are maintained during future construction works and the site is compliant with the NGZ clearances. â€¢ Scaffolding at ground level to have hoarding up to the gantry roof to prevent unauthorised access to the first level construction area by climbing the scaffolding. â€¢ In conjunction with Work Safe and Zinfra NGZ team dismantle or put in place an appropriate engineering controls to ensure the scaffolding is compliant with the NGZ clearances . â€¢ Return the vertical scaffolding standards at the perimeter of the gantry roof back to the building construction building line and erect hording to prevent access to NGZ areas of the gantry roof. â€¢ The prohibition notice can be rescinded and a new PTW issued by the Zinfra NGZ when the following occurs. o The Builder has reviewed all related SWMS and can demonstrate that Safe Systems of Work are in place to prevent further NGZ breaches and o Work Safe and Zinfra are satisfied that the site is compliant with the NGZ requirements. | 708 HIGH STREET, RESERVOIR VIC 3073 | 16423583 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Jemena were advised by a Zinfra No Go Zone (NGZ) Officer of a NGZ breach of clearances to overhead power lines (Insulated Arial Bundled Conductors ABC) at 708 High Street Reservoir on 26 July 2019. The building company ABEE Holdings Pty Ltd is responsible for all works at this siteâ€“ Registered Builder Mehmet Kurucan. A Permit To Work (PTW -21270 see attachment 1) was issued by the Zinfra NGZ team on the on the 2 May 2019 and there is a requirement is for the permit to remain on site and be available at all times however the builder on request could not locate his PTW copy. The NGZ team member who issued the initial permit advised he was not made aware of the future construction works that took place in proximity to the overhead power lines at the time the permit was issued. Jemena advised Work Safe of the breach on 26 July and a meeting was held at the site on 29th July with Work Safe Inspector Andrew Henrys, three members of the Zinfra NGZ team and a Jemena Work Practices team member. The site meeting confirmed the construction work breached the Work Safe / ESV NGZ and Jemena clearances, it was also identified: o The Gantry roof area was being used as the work platform and the perimeter vertical scaffolding standards were installed at the edge of the gantry and not confined to the construction area. o This allowed construction workers to access the gantry roof area within the NGZ area, out to the perimeter of the gantry and no hoarding was in place. o The Scaffolding at ground level supporting the pedestrian gantry did not have any hoarding to stop unauthorised persons accessing the construction area and overhead power lines. | Conductor (ABC);Conductor (bare) | 0 | 0 | 0 |  | CN7 | Scaffolding was built too close to live conductors. | No Go Zone (no contact) | 26/07/2019 12:43 |  |  | 14065 | Commercial |  | 20190726JEM_01 | Infrastructure (network-based) | -37.7279 | 145.006 | 1 | Jemena | Report | 17591 | 0.0036285 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3073 | Reservoir | Other
Supply isolated at pit and repairs completed. | 291A MAUDE STREET, SHEPPARTON VIC 3630 | 30326427 | Working too close to underground cables | [6 empty] | Contractor called, believed to be customer mains dug up/cut into. Everyone okay, Uncertain if supply is still on. Crew arrived to find contractor had damaged a low voltage underground cable when cutting into a conduit believed to be empty. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | STN014 | Contractor cut conduit believing it was unused | No Go Zone (contact) | 19/07/2019 13:00 |  |  | 14073 | Roadway |  | 20190729PWA_05 | Infrastructure (customer connection) | -36.3839 | 145.4002 | 1 | Powercor | Report | 17601 | 0.0067963 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Dug up
Crew isolated the service, site made safe. | 206 BLACK FOREST ROAD, WYNDHAM VALE VIC 3024 | 30119992 | Copper theft | [6 empty] | Report received of possible copper theft Person was climbing pole last night cut cable running up the pole removed channel. Power cable been cut, exposed cables at the base of pole and near bus stop and child care center. Pole in front of house power is ok. Crew arrived to find service cable to an abandoned sewer pump had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE031 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/07/2019 10:00 |  |  | 14074 | Roadway |  | 20190729PWA_06 | Infrastructure (network-based) | -37.9 | 144.6143 | 1 | Powercor | Report | 17610 | 0.0063472 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
On arrival crew isolated supply and carried out repairs. | MATHESONS, 308 DENNEYS ROAD, WYCHEPROOF VIC 3527 | 32027183 |  |  |  | Leakage |  |  |  | Report received of HV crossarm burnt off. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CTN001 | Excessive leakage current | Pole-top fire | 43467.3701 | 1 | Negligible: no ground fire | 14079 |  |  | 20190730PWA_05 | Infrastructure (network-based) | -36.0505 | 143.1709 | 1 | Powercor | Report | 17619 | 0.0032211 | 22kV AC | Swan Hill Aerodrome | 3527 | Wycheproof | Crossarm
Workers advised to move a safe distance away from conductors as per new permit to work (photo attached). | 409 SOMERVILLE ROAD, WEST FOOTSCRAY VIC 3012 | A011067 | Working too close to overhead lines | [5 empty] | 2 | Crane working to close to HV conductors. Crane was for civil works for water main upgrade (PTW - J036508). PTW did not cover crane working too close to HV). | Conductor (bare) | 2 | 2 | 2 |  | TH11 | Crane working to close to HV conductors | No Go Zone (no contact) | 31/07/2019 13:00 |  |  | 14081 | Roadway |  | 20190731JEM_01 | Infrastructure (network-based) | -37.8105 | 144.8612 | 1 | Jemena | Report | 17623 | 0.032941 | 22kV AC | Essendon Airport | 3012 | West Footscray | Vehicle
Attending Powercor fault crew installed new LV pit and re-installed and re-terminated LV cables | 200-208 PAYNES ROAD, THORNHILL PARK VIC 3335 | 32169125 | Working too close to underground cables | [6 empty] | A report was received from a customer of no supply. Attending Powercor fault crew noted estate civil excavation works, damaged LV pit and damaged and exposed live LV cables. The site was left unattended without notices/barriers. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Excavation works by civil contractor | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/07/2019 21:25 |  |  | 14082 | Public space |  | 20190801PWA_01 | Infrastructure (network-based) | -37.7206 | 144.6361 | 1 | Powercor | Report | 17624 | 0.032212 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Dug up
On arrival crew isolated supply and carried out repairs. | 668 DIGGERS ROAD, WERRIBEE SOUTH VIC 3030 | 32171115 |  |  |  | Unknown technical factor |  |  |  | MFB and local resident reported pole fire in Diggers Rd. that had now extinguished. Attending Powercor fault crew noted a burnt FOLCB . There were no shocks, injuries or ground fire. | Connection box | 2 | 2 | 2 |  | WBE034 | Insufficient remains to determine cause. | Pole-top fire | 31/07/2019 18:00 | 1 | Negligible: no ground fire | 14084 | Roadway |  | 20190801PWA_03 | Infrastructure (network-based) | -37.9688 | 144.6851 | 1 | Powercor | Report | 17627 | 0.021503 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Connection
The crew isolated the service cable at the pole end, and instructed the customer to remove his scaffold and get his REC to check his POA before supply could be restored. They also told the customer he would need to seek No Go Zone approval before continuing with any work. | 144 THORNHILL ROAD, HIGHTON VIC 3216 | 32086799 | Building too close or within the No Go Zone;Working too close to overhead lines | [6 empty] | A customer called in to say that he had cut through his supply line. On arrival the crew found that the customer had erected a scaffold under the service cable on the front of his two story house. The customer told the crew that he had been using a saw when the saw kicked back and hit the dropper loop of the service cable at the POA, causing a flash. The customer stated that he had not received any shocks or injuries. There was no reported fire. | Service conductor | 2 | 2 | 2 |  | WPD033 | Customer carrying out house repairs cut service line | Loss of supply;No Go Zone (contact);Damage to network assets | 43473.4014 |  |  | 14085 |  |  | 20190802PWA_01 | Infrastructure (customer connection) | -38.1821 | 144.311 | 1 | Powercor | Report | 17635 | 0.0088345 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Other
Repairs completed supply restored | 90-98 COODE ROAD, WEST MELBOURNE VIC 3003 | CP0002318 | Copper theft | [6 empty] | An outage occurred in the early hours of the morning at the incident location. When the crews arrived at the incident location, they found that the door of the substation had been forced open and a low voltage circuit breaker had been opened, they also found bus bars had been stolen. There were no reported injuries or other damage. | Indoor | 2 | 2 | 2 |  | DA004 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/07/2019 6:52 |  |  | 14087 | Industrial |  | 20190802PWA_03 | Infrastructure (network-based) | -37.8104 | 144.9223 | 1 | Powercor | Report | 17631 | 0.010777 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
â€¢ The W & B LV fuses blown on tee to the Aged Care facility. â€¢ Infinity contacted Jemena who sent faults crew to investigate. â€¢ No visible damage detected and fuses replaced. â€¢ Infinity instructed to cease work and immediately obtain Jemena PTW. | 7 TRACEY STREET, RESERVOIR VIC 3073 | A010677 | Working too close to overhead lines | [5 empty] | 1 | At approximately 10am while excavating a trench across the driveway which ended beneath the LV open wire conductors between the network pole tee in the street and the first private pole on the private land, the Excavator struck the LV overhead conductors close to pole A010677. | Conductor (bare) | 0 | 0 | 0 |  | LV | Excavator struck the LV overhead conductors close to pole A010677. | No Go Zone (contact) | 43532.4167 |  |  | 14088 | Residential |  | 20190803JEM_01 | Infrastructure (network-based) | -37.7047 | 144.9962 | 1 | Jemena | Report | 17632 | 0.004831 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Vehicle
Zinfra personnel instructed the builder on 5/08/19 to cease work and obtain a PTW. Zinfra NGZ Assessor is investigating possible solutions. Note: 6/08/19 at approximately 10am, WP Specialist attended site and encountered the Zinfra No Go Assessors who had already instructed the Site Manager Lou to cease work and would prepare an assessment and PTW within 1 day. | 100 DERBY STREET, PASCOE VALE VIC 3044 | A035181 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | NGZ breach: concrete tilt slabs have been installed approximately 2.1m from the high voltage conductors and are higher. There is no PTW record for this site | Conductor (bare) | 2 | 2 | 2 |  | CN5 | Concrete tilt slabs have been installed approximately 2.1m from the high voltage conductors | No Go Zone (no contact) | 43593.5417 |  |  | 14092 | Residential |  | 20190808JEM_02 | Infrastructure (network-based) | -37.7274 | 144.9472 | 1 | Jemena | Report | 17637 | 0.039782 | 22kV AC | Essendon Airport | 3044 | Pascoe Vale | Other
A UE fault crew attended and replaced the 5A EDO fuse. | 96 COOLART ROAD, TUERONG VIC 3915 | 1110660 |  |  |  | Fuse failed to eject |  |  | 0 | UE received a report from a customer of flame from fuses near transformer on pole | EDO fuse | 0 | 0 | 0 |  | HGS22 | The original cause for the fuse element to operate was not found. The hang up was likely due to a build up of dirt over time resulting in the EDO barrel latch not releasing on operation of the element. | Plant/equipment | 29/07/2019 19:30 | 1 | Negligible: no ground fire | 14094 | Agricultural |  | 20190808UTD_02 | Infrastructure (network-based) | -38.314 | 145.1388 | 1 | United Energy Distribution | Report | 17639 | 0.013294 | 22kV AC | Moorabbin Airport | 3915 | Tuerong | Fuse
Fault crew attended and disconnected the service cable, pending repairs. | 9-11 ELLINGWORTH PARADE, BOX HILL VIC 3128 |  | Working too close to underground cables | [5 empty] | 2 | UE received a report of builders on a demolition site have hit an UG cable. On attendance, it was discovered that an excavator for the site had hit and damaged a 50mm sq UG service cable. | Services cable | 0 | 0 | 0 |  |  | Cause was excavation works by the building site in the roadway area. There was no No Go Zone request for the civil works at this location. | Damage to network assets | 25/07/2019 10:25 |  |  | 14096 | Roadway |  | 20190808UTD_04 | Infrastructure (network-based) | -37.8205 | 145.1246 | 1 | United Energy Distribution | Report | 17641 | 0.029308 | Low voltage AC (<1kV) | Moorabbin Airport | 3128 | Box Hill | Dug up
31002530 | 1983 BORUNG HIGHWAY, JEFFCOTT VIC 3480 | 31002530 |  |  |  | Leakage |  |  |  | During pole inspection pole fire damage to crossarm found There was no ground fire, no reported injuries or third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | CTN006 | Excessive leakage current | Pole-top fire | 43776.5417 | 1 | Negligible: no ground fire | 14099 | Roadway |  | 20190809PWA_02 | Infrastructure (network-based) | -36.272 | 143.1372 | 1 | Powercor | Report | 17644 | 0.03892 | 22kV AC | Swan Hill Aerodrome | 3480 | Jeffcott | Crossarm
Fire brigade extinguished fire. Fault crew dispatched. No damage to conductor or assets | 2 ANDERSON STREET, LILYDALE VIC 3140 | LIS1008057 |  | Blown branch/vegetation | [5 empty] | Fire brigade Report tree fell and caught fire when it contacted O/H conductors. | Conductor (bare) | 0 | 0 | 0 |  | LDL12 | Vegetation: Trees Incident | Other vegetation | 43776.1424 | 1 | Negligible: no ground fire | 14103 | Residential |  | 20190809SPN_03 | Infrastructure (network-based) | -37.7612 | 145.3544 | 2 | AusNet Services Distribution | Report | 17697 | 0.024425 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Trees
THE LEI confirmed the reverse polarity connection at the customers FOLCB where unknown persons have installed a new FMJB. The existing consumers 6mm neutral screen conductor had been removed and replaced with new 16mm SDI conductors terminated into the new FMJB. The live single phase grey twisted service had been disconnected and reconnected into the new FMJB. There was remnants of the old porcelain fuse and wiring nearby and the facade had been repaired following the replacement of the consumers FMJB. The single phase meter and overhead service were removed and a defect issued left on site for non-compliant wiring. | 33 JINDABYNE AVENUE, CHADSTONE VIC 3148 |  | Unauthorised work |  |  | Reverse polarity | Unauthorised REC work |  | 2 | The United Energy AMI Analytics team received meter communications alarms. The remote meter safety disconnect failed and a faults crew was dispatched to investigate. The faults crew attended and identified a reverse polarity within the consumers FMJB at the POA with transposed wiring. It appears that unknown third party persons have replaced the consumers FMJB with no consultation with UE and inadvertently created a reverse polarity. The crew contacted the United Energy Resource Coordinator and requested that a LEI attend. No electric shocks had been received as the occupancy was vacant since 15/07/2019 following the previous occupier leaving. | POA connection (customer side);Service cable (insulated) | 0 | 0 | 0 |  | OAK 21 | Unknown third party persons have replaced the consumers FMJB with no consultation with UE and inadvertently created a reverse polarity. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/07/2019 14:00 |  |  | 14107 | Residential |  | 20190809UTD_01 | Infrastructure (customer connection) | -37.8761 | 145.103 | 1 | United Energy Distribution | Report | 17653 | 0.033078 | Low voltage AC (<1kV) | Moorabbin Airport | 3148 | Chadstone | Other
Danger "Alive" signs have been placed on the substation door to warn of live equipment inside. Padlocks damaged during the thefts have been replaced. Customer has initiated patrols of the disused site to deter thieves. | 51 Regan St, St Albans VIC 3021, Australia | Pa0063710 | Vandalism;Copper theft | [6 empty] | Len Green from TIC group 0438986523 advised possible copper theft HV sub broken into. Crew attended to find substation (Margrave-Emily) had been broken into and copper bus bars stolen. Padlocks appear to have been removed with an angle grinder. The high voltage side remained "ALIVE" but the thieves were able still able to remove some copper bus bar from the substation. The customer's switch room has been completely stripped of most of its copper. No reported injuries or fire due to this incident. | Indoor;Other customer electrical equipment | 2 | 2 | 2 |  | SA009 | copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/07/2019 14:15 |  |  | 14119 | Industrial |  | 20190812PWA_03 | Infrastructure (network-based) | -37.7345 | 144.7929 | 1 | Powercor | Report | 17667 | 0.036311 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Other
Cable supply isolated. Pits made safe. Repairs organised. | 16 Old Leakes Rd, Rockbank VIC 3335, Australia | 30268310 | Copper theft | [6 empty] | Report received of copper theft- UG pit, feeding public lighting, live cables exposed Crew arrived to find 180 meters of underground cable had been stolen from between pits between pole LIS 749426 to pole 749432. Cable has been stolen from these pits on other occasions in the past. | Services cable | 2 | 2 | 2 |  | MLN021 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/07/2019 10:45 |  |  | 14121 | Roadway |  | 20190812PWA_05 | Infrastructure (network-based) | -37.7258 | 144.6535 | 1 | Powercor | Report | 17669 | 0.0072801 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Fault crews attended and fitted a new plastic pit lid with securing screws. | 24 Old Leakes Rd, Rockbank VIC 3335, Australia | 30268315 | Vandalism;Copper theft | [6 empty] | A group of Powercor employees were conducting a site visit looking at sites of previous copper thefts, when they found a pit open and the wiring pulled out of the pit and onto the ground, however none of the wiring had been cut or damaged. It is believed that this was an attempted copper theft. There were no reported injuries or fires. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | Vandalism and attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/07/2019 14:22 |  |  | 14123 | Roadway |  | 20190813PWA_02 | Infrastructure (network-based) | -37.7267 | 144.6542 | 1 | Powercor | Report | 17671 | 0.031517 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply and carried out further repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298010 | Copper theft | [5 empty] | 2 | An Electrix public lighting fault crew went out to replace the cable on 5 poles which were previously affected by copper theft. They replaced cable to 5 poles however they didnâ€™t liven up the poles as they had run out of time on the repair. The crew then went there again and found that two bays of cable had been stolen between LIS NO.â€™s .784379-784378-784377 by unknown person. | Services cable | 0 | 0 | 0 |  | MLN022 | copper theft | Damage to network assets | 23/07/2019 16:33 |  |  | 14125 | Roadway |  | 20190813PWA_04 | Infrastructure (network-based) | -37.6871 | 144.5494 | 1 | Powercor | Report | 17673 | 0.0052581 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Supply disconnected | 446-490 BANKS ROAD, MANNERIM VIC 3222 | 30068658 | Vandalism;Theft | [6 empty] | Customer reported a smart meter stolen at 446 - 490 Banks Road, Mannerim. Works presently being done on property. Customer asked for power to be disconnected after incident There was no fire, no reported injuries | Smart meter | 2 | 2 | 2 |  | DDL024 | Theft of meter | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 31/07/2019 17:59 |  |  | 14132 | Residential |  | 20190813PWA_10 | Infrastructure (customer connection) | -38.2281 | 144.584 | 1 | Powercor | Report | 17680 | 0.028373 | Low voltage AC (<1kV) | Avalon Airport | 3222 | Mannerim | Other
On arrival crew arranged for service replacement | 109 Through Rd, Camberwell VIC 3124, Australia | 30176479 | Copper theft | [6 empty] | A passer-by reported exposed cables and a pit at the incident location. The attending crew found an open pit and a new UG cable from pole to pit had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | RD015 | Copper theft | Damage to network assets | 43685.4792 |  |  | 14142 | Roadway |  | 20190814PWA_01 | Infrastructure (network-based) | -37.8416 | 145.0924 | 1 | CitiPower | Report | 17691 | 0.033394 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Other
Repairs undertaken and underground cable installed clear of drain. | 21 HUNTINGTOWER ROAD, ARMADALE VIC 3143 | 30165915 | Working too close to underground cables | [6 empty] | A customer reported a power outage at the incident location. A crew had attended and the fuse was replaced but no fault found. The customer reported an outage again crew attended found that the UG service from pole to pit had been damaged in the nature strip This UG cable was installed a incorrectly some time ago, installed directly through a council storm water drain. There was evidence of repair work on storm water line and it is believed the cable may have been damaged at that time. There was no fire or injury. | Services cable | 2 | 2 | 2 |  | AR013 | Drain maintenance by unknown party | Damage to network assets | 43685.6333 |  |  | 14148 |  |  | 20190814PWA_03 | Infrastructure (network-based) | -37.8541 | 145.0244 | 1 | CitiPower | Report | 17698 | 0.039584 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | Other
site made safe and investigation commenced | 145 DOYLES ROAD, SHEPPARTON EAST VIC 3631 | 33092012 |  |  |  | Not built/maintained to design |  |  | 1 | Powercor crew installing a public light pole have contacted a 22kV underground cable. | Cable | 0 | 0 | 0 |  | STN024 | Location of HV cable confused by versions of drawing, site leveling and realignment of kerb (datum) . | Loss of supply;Damage to network assets | 43807.4514 |  |  | 14150 | Roadway |  | 20190814PWA_05 | Infrastructure (network-based) | -36.3777 | 145.432 | 1 | Powercor | Report | 17703 | 0.01997 | 22kV AC | Shepparton Airport | 3631 | Shepparton East | Dug up
UE dispatched a faults crew. On attendance, the crew found a pole to pit UG service cable had been hit and damaged by an excavator undertaking civil works for gas pipe installation. The faults crew isolated the cable at the pole, and undertook repairs. | 4 MILLARD STREET, BENTLEIGH EAST VIC 3165 | 1801683 | Working too close to underground cables | [5 empty] | 1 | UE received a report of an excavator hitting an underground cable. | Services cable | 0 | 0 | 0 |  |  | The cause was the civil works being undertaken for gas supply to the premises. There was no No Go Zone request made for these works. | Damage to network assets | 43593.4514 |  |  | 14145 | Roadway |  | 20190814UTD_03 | Infrastructure (network-based) | -37.9272 | 145.0648 | 1 | United Energy Distribution | Report | 17694 | 0.035856 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Dug up
Crews attended, isolated supply and performed repairs. | 52 NICHOLSON STREET, WARRNAMBOOL VIC 3280 | 30134187 |  | Wind |  | Corrosion |  |  |  | A customer reported that a pole to pole wire was down and resting on a parked vehicle at the incident location. On arrival the crew found that a bracket had rusted and strong wind caused the bracket to fail, allowing the Blue phase r conductor to fall to the ground alive. The conductor landed on the roof and bonnet of a white VW van registration XAR-859 that was parked in front of 52 Nicholson St, leaving marks on the paintwork. There were no reported injuries or fires, and no other damage was reported. | Conductor (bare) | 2 | 2 | 2 |  | WBL008 | Rusted T bracket failed in strong winds | Damage to network assets | 43777.3604 |  |  | 14152 | Roadway |  | 20190815PWA_02 | Infrastructure (network-based) | -38.3889 | 142.4964 | 1 | Powercor | Report | 17705 | 0.039912 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | AF Other
Crew replaced the Pole Top Connection Box on the Reticulation Pole | 507 SOUTH BOUNDARY ROAD, KYABRAM VIC 3620 | 30556588 |  |  |  | Corrosion;Overheated connection |  |  | 2 | Person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Taps and her bare feet while standing on the wet shower base and waste water outlet. | Services cable | 0 | 0 | 0 |  | KYM003 | Corroded and overheated U/G Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole | Minor shock | 21/07/2019 9:00 |  |  | 14155 | Agricultural |  | 20190815PWA_05 | Infrastructure (customer connection) | -36.3248 | 145.0857 | 1 | Powercor | Report | 17712 | 0.004603 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Kyabram | Connection
30/06 Powercor Fault Crew removed a Birds Nest from the Transformer Pole and completed a visual inspection of all Network Assets and the Metering equipment and confirmed all were in serviceable condition. 14/07 Large Bird Nest and a length of Fencing Wire located on top of the Transformer making intermittent contact between the LV Active and Neutral Bushings on the Transformer. | 280 EIGHT MILE LANE, MORTLAKE VIC 3272 | 32060712 |  | Bird |  |  |  |  | 2 | Person was opening a Sliding Door when she believes she experienced a slight electric shock as she made simultaneous contact with her hand on the metallic Sliding Door and her bare feet whilst standing on the floor. Incident had separate LEI attendances 30/6 and 14/07/2019. | Transformer | 0 | 0 | 0 |  | TRG002 | Bird Incident | Minor shock | 14/07/2019 19:00 |  |  | 14158 | Agricultural |  | 20190816PWA_02 | Infrastructure (network-based) | -38.0514 | 142.9451 | 1 | Powercor | Report | 17876 | 0.033716 | Low voltage AC (<1kV);12.7kV AC (SWER) | Warrnambool Airport Ndb | 3272 | Mortlake | Animal
Fault crew tightened service neutral connection at POA | 13 EGREMONT STREET, FITZROY NORTH VIC 3068 | 30163392 |  |  |  | Overheated connection |  |  | 2 | person was showering at the time; He received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. Voltage tests between an independent earth, the points of contact and various points of the electrical installation, including distribution assets, revealed a loose neutral connection at the POA. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | F037 | Loose Neutral connection at POA end | Minor shock | 30/07/2019 19:54 |  |  | 14161 | Residential |  | 20190816PWA_04 | Infrastructure (customer connection) | -37.784 | 144.9822 | 1 | Powercor | Report | 17870 | 0.033054 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Connection
Crew replaced the stolen HV/LV Copper Earths | 995-1045 RYANS LANE, MELTON VIC 3337 | 32171550 | Copper theft | [6 empty] | Faults Crew have advised that an unknown person(s) have cut through and stolen the HV & LV earths on Pole 136 "RYANS LA P136" 25kVA Three-Phase Pole Sub. Approximately 2 metres of HV & LV Copper Earths have been cut away and stolen/taken. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | MLN012 | Copper theft | Damage to network assets | 13/08/2019 14:54 |  |  | 14162 | Roadway |  | 20190816PWA_05 | Infrastructure (network-based) | -37.6598 | 144.6188 | 1 | Powercor | Report | 17719 | 0.022751 | Earthing cable | Melbourne Airport | 3337 | Melton | Other
Fault crew and LEI dispatched. Isolated supply to bracket, damaged luminaire and cabling replaced. | 644 MAIN ROAD, ELTHAM VIC 3095 | LIS921873 |  |  |  | Defective component |  |  |  | Vet reported dog getting tingles from concrete pole out the front. | Conductor (insulated);Pole (concrete) | 0 | 0 | 0 |  | ELM34 | Animal Incident | Minor shock;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43503.4931 |  |  | 14160 | Roadway |  | 20190816SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18442 | 0.03839 | Low voltage AC (<1kV) | Moorabbin Airport | 3095 | Eltham | AF Other
crew attended and cut tree away fro conductor and repaired line | 127 BROWNS ROAD, TIMBOON VIC 3268 | 33036205 |  | Alive;Fallen;MEC |  |  |  |  | 1 | A customer reported a HV cable on the ground at the incident location. Upon arrival, a crew found that a large tree fell on to HV conductor and the conductor on the ground and a service line | Conductor (bare) | 0 | 0 | 0 |  | TRG003 | Vegetation: Trees Incident | Other vegetation | 13/06/2019 7:56 | 1 | Negligible: no ground fire | 14175 | Roadway |  | 20190819PWA_06 | Infrastructure (network-based) | -38.4618 | 142.9763 | 1 | Powercor | Report | 17733 | 0.026959 | 22kV AC | Warrnambool Airport Ndb | 3268 | Timboon | Trees
All members of the work party ceased work and extinguished the 2sqm grass fire. They checked that no supply was lost to customers in the vicinity and notified their supervisor of what had occurred and no injuries were sustained. | 5 WILLIAM STREET, OAKLEIGH VIC 3166 | 2325899 |  | Heat |  | Conductor clashing | Followed but inappropriate |  | 2 | Zinfra construction crew were replacing LV crossarms using live line techniques and were in the process of re-attaching a 2 core mid-span service. When they re-strained the steel catenary wire that supports the service, the catenary made simultaneous contact with the white and blue phase LV overhead conductors resulting in sparking that started a small grass fire on the nature strip. | Conductor (insulated) | 0 | 0 | 0 |  |  | When the Zinfra construction crew re-strained the steel catenary wire that supports the mid-span service, the catenary made simultaneous contact with the white and blue phase LV overhead conductors. | Grassfire | 43468.5417 | 1 | Localised: less than 10 sq.m | 12265 | Roadway |  | 20190304UTD_02 | Infrastructure (network-based) | -37.9014 | 145.1032 | 1 | United Energy Distribution | Report | 15393 | 0.0029942 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh | Other
Supply isolated and made safe | 54A METROLINK CIRCUIT, CAMPBELLFIELD VIC 3061 |  | Copper theft | [5 empty] | 2 | Unknown person(s) stole underground cable low voltage cable | Cable | 2 | 2 | 2 |  |  | Unknown person stole copper underground cable | Loss of supply | 43588.2951 |  |  | 12273 | Industrial |  | 20190305JEM_01 | Infrastructure (network-based) | -37.6571 | 144.9696 | 1 | Jemena | Report | 15405 | 0.010032 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Other
The LEI conducted voltage tests between an independent earth, the metallic water pipe system connected to earth and the neutral bar at the customers switchboard identified 10V under no load. The same result was also recorded at the neighboring property which was fed off the same pit. NST tests at both properties failed due to a high impedance neutral. The construction crew replaced the faulty T-join feeding the Service pit. | 4 TERRELL COURT, ROXBURGH PARK VIC 3064 |  |  |  |  | Neutral fault |  |  | 2 | The fault was first noticed when the customer was having a shower and received an electric shock while touching the tap with his hand and simultaneously standing bare foot on the wet shower base. | Cable | 2 | 2 | 2 |  |  | The attending construction crew identified the problem has a high impedance of the neutral conductor at the t-join in which fed the pit that serviced the properties at 4 and 6 Terrell Court, Roxburgh Park. | Minor shock | 43588.4424 |  |  | 12278 | Residential |  | 20190305JEM_03 | Infrastructure (customer connection) | -37.6387 | 144.9287 | 1 | Jemena | Report | 15410 | 0.037895 | Low voltage AC (<1kV) | Essendon Airport | 3064 | Roxburgh Park | Connection
work crew made safe | SOMERTON ROAD, GREENVALE VIC 3059 |  | Copper theft | [5 empty] | 2 | Unknown person stole copper (low voltage cable) ex Everglade-Arena substation. | Cable | 2 | 2 | 2 |  |  | Unknown person(s) stole copper cable. | No Go Zone (no contact) | 43588.5104 |  |  | 12287 | Public space |  | 20190306JEM_01 | Infrastructure (network-based) | -37.6355 | 144.9114 | 1 | Jemena | Report | 15420 | 0.007875 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
The LEI carried out voltage tests between an independent earth and the taps and various parts of electrical installation, including the distribution assets, identified a damaged overhead neutral screened service cable. The service cable was replaced. | 80 PRINCES STREET, FLEMINGTON VIC 3031 |  |  |  |  | Neutral fault |  |  | 2 | The customer received an electric shock while she was having shower, when she made simultaneous contact between her hand on the tap and with her bare feet in a wet area in contact with metallic drain. | Neutral screen | 2 | 2 | 2 |  |  | Damaged overhead neutral screened copper service. (What caused the damage is unknown). | Minor shock | 43619.4792 |  |  | 12293 | Residential |  | 20190306JEM_02 | Infrastructure (customer connection) | -37.786 | 144.9341 | 1 | Jemena | Report | 15427 | 0.0028437 | Low voltage AC (<1kV) | Essendon Airport | 3031 | Flemington | OH Cable
Work crew made safe and repaired low voltage conductors. | 143 LANDELLS ROAD, PASCOE VALE VIC 3044 |  | Working too close to overhead lines | [5 empty] | 2 | Third party crane made contact with low voltage overhead conductors while delivering prefab walls, etc. | Conductor (bare) | 2 | 2 | 2 |  |  | Crane delivering prefab without spotter and made contact with overhead low voltage conductors. Crane Hire Company contracted by Metricon: Yes Cranes o Owner - Leon Rubinstein o 0425808056 o admin@yescranehire.com.au o Crane Operator â€“ Michael Costanzo o DOB â€“ 12/01/1955 PTW: o 030504 o Issued â€“ 13/12/18 o Exp - 13/03/19 o Issued by - Carl Skidmore Zinfra. Carl is on leave and has a copy in his car. o Issued to â€“ Adrian Kendall, Metricon Homes o Crane operation work conducted without a spotter Company Responsible for site: o Metricon Homes o Construction Manager â€“ Adrian Kendall o 0428563211 Authorities who attended: o Vic Pol, MFB and Worksafe | Loss of supply;No Go Zone (contact) | 43619.5417 |  |  | 12294 | Residential |  | 20190306JEM_03 | Infrastructure (network-based) | -37.7194 | 144.9441 | 1 | Jemena | Report | 15428 | 0.02623 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Vehicle
A faults crew promptly attended and replaced the damaged FMJB and restored supply to the two properties. | 120 BARRETTS ROAD, LANGWARRIN SOUTH VIC 3911 | 3321371 |  | Heat |  | Overheated connection |  |  | 2 | Pole fire per CFA. An underground cable connection within a pole mounted FMJB at pole No. LIS 3321371 located outside 120 Barretts Road, Langwarrin South overheated and molten metal fell into the dry grass below causing a small 1sqm fire at the base of the pole. | Connection box | 0 | 0 | 0 |  |  | A probable loose connection within the FMJB overheated during warm conditions. | Grassfire | 43527.7674 | 1 | Localised: less than 10 sq.m | 12289 | Roadway |  | 20190306UTD_02 | Infrastructure (network-based) | -38.1865 | 145.1734 | 1 | United Energy Distribution | Report | 15422 | 0.01149 | Low voltage AC (<1kV) | Moorabbin Airport | 3911 | Langwarrin South | Connection
Fault crew dispatched and candled fuse replaced | 800 OLD SYDNEY ROAD, BEVERIDGE VIC 3753 | LIS4718493 |  |  |  | Candled fuse |  |  |  | E0013105 - report of candling fuse | EDO fuse | 0 | 0 | 0 |  | KLO24 | Candled HV EDO fuse. | Pole-top fire | 43588.7868 | 1 | Negligible: no ground fire | 12302 |  |  | 20190307SPN_02 | Infrastructure (network-based) | -37.4702 | 144.9234 | 2 | AusNet Services Distribution | Report | 15609 | 0.02441 | 22kV AC | Wallan (Kilmore Gap) | 3753 | Beveridge | Fuse
crew attended. crew replaced cross-arm, conductors across railway removed. | 701 DANDENONG ROAD, MALVERN VIC 3144 | 30203328 |  |  |  | Leakage |  |  | 1 | Citipower received an alarm indicating a feeder protection operation had occurred. It was found that a HV cross-arm had burnt allowing HV conductors to fall onto traction system passing underneath. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | AR007 | Probable leakage current | Pole-top fire;Significant disruption to the community | 43619.0507 | 1 | Negligible: no ground fire | 12304 | Roadway |  | 20190308PWA_01 | Infrastructure (network-based) | -37.8679 | 145.0307 | 1 | CitiPower | Report | 15442 | 0.034495 | 11kV AC;1500V DC | Moorabbin Airport | 3144 | Malvern | Crossarm
On arrival crew inspected structure, no damage found. | COBDEN-TERANG ROAD, TERANG VIC 3264 | 30043677 |  | Bird | [5 empty] | Report received of a bird flashover at the incident location. On arrival the crew found that a bird had caused a flashover between surge arrestor and its base. The bird fell to ground to ground starting a small grass fire. CFA extinquished the fire. There was no reported injuries. | Surge diverter | 2 | 2 | 2 |  | TRG003 | Bird Incident | Loss of supply;Grassfire | 43649.5833 | 1 | Small: 10 - 1000 sq.m | 12305 | Roadway |  | 20190308PWA_02 | Infrastructure (network-based) | -38.2599 | 142.926 | 1 | Powercor | Report | 15441 | 0.00664 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Animal
Fault crew dispatched and fuse replaced | 25 SPENCERS ROAD, MONOMEITH VIC 3984 | LIS513165 |  |  |  | Candled fuse |  |  |  | E0013286 - report of candled HV fuse | Boric acid | 0 | 0 | 0 |  | LLG11 | Candled HV boric acid fuse. No evidence of ground fire | Pole-top fire | 43619.6458 | 1 | Negligible: no ground fire | 12308 |  |  | 20190308SPN_02 | Infrastructure (network-based) | -38.2048 | 145.5634 | 2 | AusNet Services Distribution | Report | 15445 | 0.0066354 | 22kV AC | Moorabbin Airport | 3984 | Monomeith | Fuse
Fault crew dispatched. Pole still alight when crew arrived. Isolated and called CFA | 16 HUNTS ROAD, LEONGATHA SOUTH VIC 3953 | LIS2010501 |  |  |  | Defective component |  |  |  | E0013786 - Pole fire reported | Connection box | 0 | 0 | 0 |  | LGA23 | The fuse mains box on the pole appears to have melted resulting in 0.5m sq grassfire at base of the pole with melted plastic in the area around the burnt grass. Pole has surface burns and transformer is covered in black soot. Pole still alight when crew arrived. Supply isolated and CFA called. Pole was tested and deemed ok to remain, transformer was replaced with single phase 25kVA. New 95mm ABC leads were installed from the transformer to the new krone box. 35mm leads installed from Krone box to new FOLCB to reconnect the existing underground service (no impact to underground service) | Pole-top fire | 43711.8167 | 1 | Localised: less than 10 sq.m | 12319 |  |  | 20190312SPN_01 | Infrastructure (network-based) | -38.5583 | 145.881 | 1 | AusNet Services Distribution | Report | 15462 | 0.035345 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3953 | Leongatha South | Fuse
In conjunction with a fault crew, the EIO proceeded to undertake tests to prove the integrity of the supply. NST passed with 0.8ohms neutral impedance, this was repeated with a 10amp load which failed the NST. 13.2V was measured on the Tap in the garage with a 10amp Load. The fault was traced back into the street LV reticulation and a series of tests were performed to narrow down the issue. It was found that the Spreaders on the middle of the line had worn the neutral conductor and caused multiple strands to break. Repairs were made by the lines men. Tests were then repeated at the house. NST Passed 0.4ohms. 4.4V measured on the Tap in the Garage with 10amp Load | 6 RITCHIE AVENUE, BLAIRGOWRIE VIC 3942 |  |  |  |  | Neutral fault;Mechanical breakdown |  | Phase to neutral | 1 | Customer reported receiving a tingle that he felt go up his arm whilst touching a tap in the garage washing down cleaning wetsuits. He was bare foot. | LV Spreader;Conductor (bare);Other | 0 | 0 | 0 |  |  | The neutral conductor in the street had been damaged b y the LV Spreader, with strands broken thus increasing the conductor impedance and reducing the neutral return path, increasing volts. | Minor shock | 43588.5 |  |  | 12324 | Residential |  | 20190312UTD_02 | Infrastructure (network-based) | -38.3767 | 144.7727 | 1 | United Energy Distribution | Report | 15469 | 0.03099 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Conductor
Made safe | 20 CALDER PARK DRIVE, TAYLORS HILL VIC 3037 |  | Vandalism;Unauthorised access | [6 empty] | Unknown person(s) have been ripped open the pit and exposed wires. | Cable | 0 | 0 | 0 |  |  | Vandalism by unknown person(s) | Damage to network assets | 15/03/2019 23:19 |  |  | 12333 | Commercial |  | 20190316JEM_01 | Infrastructure (network-based) | -37.7193 | 144.7516 | 1 | Jemena | Report | 15491 | 0.029209 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Taylors Hill | Other
On arrival crew isolated supply, repairs arranged. | 433 BOURKE STREET, MELBOURNE VIC 3000 | 33111907 |  |  |  | Unknown technical factor |  |  |  | Vic Fire reported a possible fire in an indoor substation at the incident location. Upon arrival the CitiPower crew found that the LV panel board ignited. The fire was extinguished by Fire Brigade. There was no reported injuries. | Indoor | 2 | 2 | 2 |  | LQ003 | insufficient remains to effectively determine cause | Plant/equipment | 18/03/2019 8:42 | 1 | Negligible: no ground fire | 12339 | Commercial |  | 20190319PWA_01 | Infrastructure (network-based) | -37.8151 | 144.9611 | 1 | CitiPower | Report | 15558 | 0.037079 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | AF Other
Crew isolated substation nearby and raised fault follow up. Switch cabinet and stolen cable not PCA asset so no police report submitted. | MOUNT MACEDON ROAD, GISBORNE VIC 3440 | 33026018 | Vandalism;Copper theft | [6 empty] | Employee report of switchboard door broken near LIS 450415. On arrival crew found that Vic Roads switching cabinet had been broken open and cable had been stolen that supplies VicRoads ice detection and bridge heating. There was no fire, no reported injuries | Customer installation | 2 | 2 | 2 |  | GSB013 | Vandalism & copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/02/2019 14:45 |  |  | 12341 | Roadway |  | 20190319PWA_02 | Infrastructure (network-based) | -37.4566 | 144.5794 | 1 | Powercor | Report | 15508 | 0.032299 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Gisborne | Other
Damaged cable was disconnected and service pit near LIS 909798 and left off supply at request of Port rep as it will no longer be required | CLIFF STREET, PORTLAND VIC 3305 | 34004050 | Working too close to underground cables | [6 empty] | A Port of Portland rep contacted Powercor advising that a live underground cable had been dug up. When crews arrived they found a Port of Portland excavator working on a traffic roundabout ( property owned by Port of Portland) had dug up a LV underground cable (PL cable) that is currently Powercor owned. There was no fire, No reported shock or injuries. | Services cable | 2 | 2 | 2 |  | PLD004 | Excavation works by excavator | Damage to network assets | 25/02/2019 16:07 |  |  | 12343 | Commercial |  | 20190319PWA_03 | Infrastructure (network-based) | -38.3542 | 141.6142 | 1 | Powercor | Report | 15521 | 0.005787 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | Dug up
Fault crew and LEI dispatched to investigate and make safe | 20 GEMMA STREET, SUNDERLAND BAY VIC 3922 | LIS2809017 |  |  |  | Defective component |  |  |  | E0013834 - Customer reported receiving an electric shock | Connection box | 0 | 0 | 0 |  | PHI11 | Fault crew attended and found neutral had come away at junction box at pole. In consultation with inspector, crew reattached neutral and completed testing. Tests passed and customer's supply restored. | Minor shock | 43741.7188 |  |  | 12338 |  |  | 20190319SPN_01 | Infrastructure (network-based) | -38.5029 | 145.2776 | 2 | AusNet Services Distribution | Report | 15504 | 0.027289 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Sunderland Bay | Connection
Fault crew dispatched to investigate. No damage to DB assets Crews spoke to the operator and pump was moved to a safe location. Once confirmed safe, the crew restored supply. | 108 BOSWORTH ROAD, BAIRNSDALE VIC 3875 | LIS5715092 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth |  | E0014717 - report of 3rd party mobile plant contacting O/H line resulting in a flash over causing feeder to trip | Conductor (bare) | 0 | 0 | 0 |  | BDL4 | Third party contact with OH/ HV conductors. Using one of their pumping trucks, a flashover occurred from the 22KV O/H conductors to the third party's pumping boom located at their work site. East Gippsland Concrete Pumping truck was set up to pump for a slab on the corner of Bosworth and Railway Ct in Bairnsdale. While extending the boom into position it came into contact with the O/H 22kV conductors causing the feeder to trip. The operator was not injured. | No Go Zone (contact) | 14/03/2019 13:38 |  |  | 12340 |  |  | 20190319SPN_02 | Infrastructure (network-based) | -37.8382 | 147.6074 | 1 | AusNet Services Distribution | Report | 15613 | 0.027706 | 22kV AC | Bairnsdale Airport | 3875 | Bairnsdale | Vehicle
On arrival crew isolated supply to allow repairs to be completed. | 3-43 WATERFRONT WAY, DOCKLANDS VIC 3008 | Cp0051179 | Working too close to underground cables |  |  | Fault on customer installation |  |  |  | Report from The District/ Harbour Town site, about a quarter of shopping centre plus residential centre are off, builder working at site next door believe has nicked LV cable coming from sub station (b/w switchboard and substation) on site Nick 0412 654 223 - site has been secured. Crew found LV Red phase protection had operated for a customer side fault at Waterfront 45-Studion substation. There was no fire, no reported injuries. | Customer installation | 2 | 2 | 2 |  | WG032 | builder damaged customers cables during building work | Loss of supply;No Go Zone (contact) | 26/02/2019 14:16 |  |  | 12357 | Commercial |  | 20190320PWA_05 | Infrastructure (network-based) | -37.8135 | 144.9392 | 1 | CitiPower | Report | 15532 | 0.019675 | Low voltage AC (<1kV) | Essendon Airport | 3008 | Docklands | Other
On arrival crew isolated supply and arranged repairs | 49 WALGOOD GROVE, MACEDON VIC 3440 | 32050427 | Vandalism;Copper theft | [6 empty] | A passer-by reported a vandalised Kiosk substation at the incident location. Upon arrival, the crew found that the Kiosk doors have been damaged. Some cable from the Kiosk to the customer installations have been stolen. The Kiosk LV bus was damaged. The customer is Vic Roads and the crew observed their assets also vandalised. There was no fire or reported injuries. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | GSB014 | Vandalism & copper theft at kiosk substation. | Damage to network assets | 27/02/2019 12:42 |  |  | 12358 | Roadway |  | 20190320PWA_06 | Infrastructure (network-based) | -37.4258 | 144.5453 | 1 | Powercor | Report | 15533 | 0.036215 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
On arrival crew isolated supply and carried out repairs | 524 DERRIMUT ROAD, TARNEIT VIC 3029 | 30226559 | Vandalism;Copper theft | [6 empty] | Report relieved that some vandals have cut some copper UG cables at the incident location, nNo smoking or sparking seen. Upon arrival the PCA Field Crew have advised, that an unknown person has removed the pit lids, from the LV Service Pits supplying PL Lights LIS-984333, LIS-984334 & LIS-984335 and have vandalized and have cut through the PL/service cable and pl earthing cables supplying these lights. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit | 2 | 2 | 2 |  | LV001 | Vandalism & copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/02/2019 15:30 |  |  | 12361 | Roadway |  | 20190320PWA_07 | Infrastructure (network-based) | -37.8389 | 144.6902 | 1 | Powercor | Report | 15538 | 0.015738 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Fault crew dispatched. Candled HV EDO Fuse replaced with new and supply restored | 120 ARKELLS LANE, WANDONG VIC 3758 | LIS4700817 |  |  |  | Candled fuse |  |  | 0 | candled EDO HV Fuse | EDO fuse | 0 | 0 | 0 |  | KMS12 | Lightning storm identified in the area suspected to have caused fuse operation and subsequent candling. No evidence of ground fire | Pole-top fire | 20/03/2019 18:40 | 1 | Negligible: no ground fire | 12364 |  |  | 20190321SPN_01 | Infrastructure (network-based) | -37.3749 | 145.0175 | 2 | AusNet Services Distribution | Report | 17764 | 0.026171 | 22kV AC | Wallan (Kilmore Gap) | 3758 | Wandong | Fuse
Section isolated, tree branch removed, and broken conductors re-sleeved. A vegetation inspection organised to confirm sufficient clearance and prevent similar incident occurring in future. | 203 PASCOE VALE ROAD, ESSENDON VIC 3040 | 10596307 |  | Blown branch/vegetation |  |  |  |  | 0 | Council tree branch fell onto low voltage bare conductors and broke 2 phases midspan. This resulted in both conductors falling down to ground (location is opposite 203 Pascoe Vale Road). | Conductor (bare) | 0 | 0 | 0 |  | NS15 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/03/2019 19:57 |  |  | 12381 | Commercial |  | 20190324JEM_02 | Infrastructure (network-based) | -37.7566 | 144.9259 | 1 | Jemena | Report | 15571 | 0.014887 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Trees
Faults crew made safe and disconnected the service. | 55 HAMPTON ROAD, ESSENDON WEST VIC 3040 |  | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | AMI personnel attended site to investigate a non-communicating meter. They found the property was undergoing renovation or demolition and that the overhead service to the house has been damaged. It appeared the service had been struck and pulled by a machine, potentially the excavator on scene. They have broken one of the two wires in the service and left the broken wire hanging down dangerously. They have also pulled the cable enough to strip a length of insulation from the service at the pole end. | Service conductor | 0 | 0 | 0 |  |  | Excavator operator breached No Go Zone to overhead supply service | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/03/2019 10:00 |  |  | 12389 | Residential |  | 20190325JEM_02 | Infrastructure (network-based) | -37.7518 | 144.8832 | 1 | Jemena | Report | 15643 | 0.038889 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon West | Vehicle
Zinfra Service isolated supply to overhead service and made safe | 2 RODMAN STREET, RESERVOIR VIC 3073 |  | Unauthorised work;Unauthorised access |  |  |  |  | Phase to earth | 2 | Zinfra Service crew arrived onsite to commence works to disconnect domestic property and found demolition contractor has commenced demolishing building with supply still connected | Smart meter | 0 | 0 | 0 |  |  | Demolition contractor did not wait for network service crew to arrive to isolate and disconnect service from building as arranged before commencing works. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/03/2019 14:50 |  |  | 12390 | Residential |  | 20190325JEM_03 | Infrastructure (network-based) | -37.7026 | 145.0081 | 1 | Jemena | Report | 15585 | 0.0036354 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Tested and restored supply to all customers. Cards left for two customers with damage | 116 LEE ROAD, WINTON VIC 3673 | LIS 834992 |  | Lightning |  | HV injection |  |  |  | E0016551 - HVI & appliance damage following lightning strike | Any other type;Pole mounted | 0 | 0 | 0 |  | WN6 | Lightning strike to HV overhead electric lines resulting in a HV Injection to property and transformer HV fuses to blow. Repairs to HV lines and fuses replaced. Inspector tested and reconnected effected properties. HV Injections occurred to : - 116 Lee Rd, Winton North - 104 Keenan Rd, Winton North - 486 Ashmead Rd, Winton North | HV injection;Less than $50k damage | 24/03/2019 18:20 |  |  | 12393 |  |  | 20190325SPN_03 | Infrastructure (network-based) | -36.4852 | 146.128 | 1 | AusNet Services Distribution | Report | 15590 | 0.018877 | Low voltage AC (<1kV) | Wangaratta Aero | 3673 | Winton | Lightning
Fault crew dispatched. Burnt HV bushing covers identified and to be replaced. Customers still on supply | 283 MITTA NORTH ROAD, ESKDALE VIC 3701 | LIS5210351 |  | Lightning | [5 empty] | E0016441 - burnt HV bushing Covers on pole top s/stn following lightning strike. | Pole mounted | 0 | 0 | 0 |  | WOTS13 | Burnt HV bushing cover on pole type transformer after lightning strike. A storm had passed through the area prior to the crews arrival. Lots of Lightning in the area. No fuses down on substation and customer still on supply. Follow up raised to replace the bushing covers and check the transformer. | Pole-top fire | 22/03/2019 12:49 | 1 | Negligible: no ground fire | 12394 |  |  | 20190325SPN_04 | Infrastructure (network-based) | -36.457 | 147.2923 | 2 | AusNet Services Distribution | Report | 17797 | 0.034345 | 22kV AC | Wangaratta Aero | 3701 | Eskdale | Lightning
Fault crew dispatched. Candled fuse replaced and supply restored | BELTANA, 4348 KIEWA VALLEY HIGHWAY, DEDERANG VIC 3691 | LIS5200750 |  |  |  | Candled fuse |  |  |  | E0016423 - candled HV fuse reported following storm event | Boric acid | 0 | 0 | 0 |  | WOTS11 | Fault crew attended site following a storm and found 2 fuses had successfully operated but the 3rd had hung-up and candled. | Pole-top fire | 22/03/2019 7:30 | 1 | Negligible: no ground fire | 12395 |  |  | 20190325SPN_05 | Infrastructure (network-based) | -36.4683 | 147.0143 | 2 | AusNet Services Distribution | Report | 15594 | 0.0041262 | 22kV AC | Wangaratta Aero | 3691 | Dederang | Fuse
Operated attended, and confirmed the case and that there was no damage to assets This incident is not deemed to be reportable under the AER F-factor scheme | 99 OSBORNE STREET, WILLIAMSTOWN VIC 3016 |  |  | Wind |  |  |  | Phase to phase | 1 | Council Tree branch in LBRA broke off during storm and contacted HV open wire, causing feeder to trip. Signs of charring on tree branch. | Conductor (bare) | 0 | 0 | 0 |  | NT0-015 | Vegetation: Trees Incident | Singeing or local charring/blackening only | 25/03/2019 1:46 |  |  | 12397 | Public space |  | 20190326JEM_01 | Infrastructure (network-based) | -37.8667 | 144.8979 | 2 | Jemena | Report | 15596 | 0.040825 | 22kV AC | Essendon Airport | 3016 | Williamstown | Trees
The Powercor crew made the site safe. The transformer and substation HV equipment located above the transformer was replaced | 31 WEDGE STREET S, WERRIBEE VIC 3030 | 33071159 |  |  |  | Electrical breakdown;Insulator |  |  |  | customers reported smoke coming from a power pole (LIS 204796) on the north side of Burke St Werribee A Powercor crew attended the site and noted that a 300kVA pole mounted substation (Burke Wedge 22 03 1751) had faulted | Transformer | 0 | 0 | 0 |  | WBE024 | Faulted HV bushing of transformer - believed to be electrical breakdown | Grassfire | 24/03/2019 11:20 | 1 | Localised: less than 10 sq.m | 12400 | Roadway |  | 20190326PWA_02 | Infrastructure (network-based) | -37.9081 | 144.6615 | 1 | Powercor | Report | 15601 | 0.0031852 | 22kV AC | Laverton Raaf | 3030 | Werribee | AF Other
Switching undertaken and cross-arm replaced. | 1971 WILSON ROAD, TONGALA VIC 3621 | 31027063 |  | Wind |  |  |  |  | 1 | Vicfire comms reported sparking wires at intersection of wilsons rd and castles rd. Upon arrival crew found a recent storm had broken a wood crossarm and as a result one phase was sitting in a nearby pepper tree (sparking). Crew made the area safe. Cfa were in attendance and had left prior to crew arrival. There was no broken conductor, no burning in tree, no x-arm fire, no grass fire | Crossarm (wood) | 0 | 0 | 0 |  | ECA005 | storm - crossarm breakage during high winds | Loss of supply | 25/03/2019 17:40 |  |  | 12401 | Roadway |  | 20190326PWA_03 | Infrastructure (network-based) | -36.2401 | 144.9075 | 1 | Powercor | Report | 15602 | 0.019501 | 22kV AC | Shepparton Airport | 3621 | Tongala | Crossarm
crew attended and replaced fuse carriers | 525 BYRNESIDE-KYABRAM ROAD, MERRIGUM VIC 3618 | 33094346 |  | Lightning |  | Fuse failed to eject |  |  | 0 | A powercor crew responding to an outage identified that High voltage fuses had mal-operated and there had been a small ground fire at the base of the pole. | EDO fuse | 0 | 0 | 0 |  | SHP014 | lightning - initiated fuse 'hang up" | Grassfire | 23/03/2019 7:46 | 1 | Small: 10 - 1000 sq.m | 12407 | Roadway |  | 20190327PWA_01 | Infrastructure (network-based) | -36.4021 | 145.132 | 1 | Powercor | Report | 15618 | 0.032355 | 22kV AC | Shepparton Airport | 3618 | Merrigum | Lightning
Crew arrived on site and replaced 6k EDO fuse. No ground fire at site. | 3613 KIEWA VALLEY HIGHWAY, KERGUNYAH SOUTH VIC 3691 | pole 5200685 |  |  |  | Candled fuse |  |  |  | Candled fuse | EDO fuse | 0 | 0 | 0 |  | WOTS11 | EDO fuse failed to operate | Pole-top fire | 27/03/2019 9:30 | 1 | Negligible: no ground fire | 12406 |  |  | 20190327SPN_02 | Infrastructure (network-based) | -36.426 | 147.0373 | 1 | AusNet Services Distribution | Report | 17759 | 0.020706 | 22kV AC | Wangaratta Aero | 3613 | Kergunyah South | Fuse
crew attended and made repairs LEI attended to assess HVI dmage | 82 MCPHERSON STREET, HORSHAM VIC 3400 | 32091677 | Vehicle | [5 empty] | 2 | Powercor crew investigating a supply outage found that a truck had struck a distribution pole causing a High voltage conductor to dislodge and contact the LV conductors below | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | HSM009 | vehicle contact with pole | HV injection;Loss of supply | 26/03/2019 22:15 |  |  | 12414 |  |  | 20190328PWA_01 | Infrastructure (network-based) | -36.722 | 142.2047 | 1 | Powercor | Report | 15626 | 0.015398 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3400 | Horsham | Vehicle
A faults crew was sent who found a series of batteries unsafely connected with no isolation device that was possibly feeding back into the network as there was no anti islanding functions. Supply was immediately disconnected at the pole end and tests were completed to ensure all unsafe wiring, including the batteries, had been isolated. In addition, the solar installation appeared to be non-compliant. A defect notice was left on site advising that a REC will be required to attend and provide the appropriate CES to confirm the property is safe to reconnect. A faults crew attended after a Life Support customer was found to occupy the rear yellow cottage and discussions with the UE Work Practices team concluded that it was unsafe to attempt to provide a temporary supply arrangement to the rear cottage as there could be additional unsafe wiring. The rear occupancy is supplied from the meter enclosure installed at the front residence. The Resource Coordinator contacted the Customer Service Duty Manager and advised the Life Support Customer will be left off supply and they will be required to apply their plan of action in case an unplanned interruption should occur. | 102 BUNGOWER ROAD, SOMERVILLE VIC 3912 | 11008448 |  |  |  | Fault on customer installation |  |  | 2 | At approximately 3.00PM on 27/03/2019, the CFA contacted the United Energy faults and emergencies call centre requesting that supply can be isolated after batteries used for electricity storage have exploded. Itâ€™s uncertain what the occupier was doing at the time, but the explosion required the injured person to be hospitalised. ESV was notified by the CFA. | Customer installation | 1 | 0 | 0 |  |  | Wayne Kelly (UE) contacted ESV at 5.30PM to provide an update with additional information about the dangerous, unsafe wiring that was possibly back feeding into the network. Reference number 11518386 was provided and spoke with the ESV Duty Manger (Sue Sizer) who had arranged to meet Worksafe at the site on 28/03/2019. | Medical attention (first aid/doctor/hospital) | 27/03/2019 15:00 |  |  | 12412 | Residential |  | 20190328UTD_03 | Infrastructure (network-based) | -38.2383 | 145.191 | 1 | United Energy Distribution | Report | 15623 | 0.017734 | Low voltage AC (<1kV) | Moorabbin Airport | 3912 | Somerville | Installation
Emergency high voltage switching took place and the HV conductor was repaired under Access Authority conditions | 31 BOWRINGS ROAD, RED HILL VIC 3937 | 1308143 |  | Wind;Fallen |  |  |  |  | 1 | During strong winds, a Parks tree broke and fell on HV line in Bowrings Rd Red Hill (Bald Hills Nature Reserve), sparking a significant ground and tree fire. A HV spur fuse operated to isolate the line. | Conductor (bare) | 0 | 0 | 0 |  | DMA23 | Vegetation: Trees Incident | Grassfire;Other vegetation | 25/03/2019 13:13 | 1 | Small: 10 - 1000 sq.m | 12413 | Roadway |  | 20190328UTD_04 | Infrastructure (network-based) | -38.3528 | 145.0249 | 1 | United Energy Distribution | Report | 15624 | 0.025492 | 22kV AC | Moorabbin Airport | 3937 | Red Hill | Trees
Crew attended and restored supply. | 11 MONTEREY ROAD, DANDENONG SOUTH VIC 3175 | 211892 | Vandalism;Theft | [5 empty] | 2 | Call received of loss of supply to commercial site Komipharm International. On attendance, crew discovered the three HV fuses had been opened. It is believed that unknown third party were attempting to steal copper from the commercial site. | Pole mounted;No failed asset | 2 | 2 | 2 |  | DVY13 | It is believed that unknown third party were attempting to steal copper from the commercial site. | Loss of supply | 25/03/2019 8:45 |  |  | 12415 | Commercial |  | 20190328UTD_05 | Infrastructure (network-based) | -38.0245 | 145.2207 | 1 | United Energy Distribution | Report | 15627 | 0.027435 | 22kV AC | Moorabbin Airport | 3175 | Dandenong South | Other
UE fault crew attended and repaired damaged on pillar lid - replaced hast & staple. | 142-148 ATLANTIC DRIVE, KEYSBOROUGH VIC 3173 |  | Vandalism;Theft | [5 empty] | 2 | UE received a call to advise that someone has broken the lock off the pillar at the front of the property in an attempt to break into the building. | LV Pillar | 0 | 0 | 0 |  |  | Unknown third party attempting to break into premise. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43772.5563 |  |  | 12416 | Commercial |  | 20190328UTD_06 | Infrastructure (network-based) | -38.0147 | 145.1852 | 1 | United Energy Distribution | Report | 15628 | 0.033731 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Other
fault tamer fuse replaced | 33 DUNKEITH AVENUE, JAN JUC VIC 3228 | 30070945 |  | Lightning |  |  |  |  | 0 | Customers reported intermittent supply. Attending crew found that fault tamer fuse had burnt in half, with the top section of the fuse carrier falling to the ground. | Any other type | 0 | 0 | 0 |  | WPD032 | Lightning | Pole-top fire;Loss of supply | 23/03/2019 8:56 | 1 | Negligible: no ground fire | 12418 | Residential |  | 20190329PWA_02 | Infrastructure (network-based) | -38.3464 | 144.2975 | 1 | Powercor | Report | 15631 | 0.014057 | 22kV AC | Avalon Airport | 3228 | Jan Juc | Lightning
Crew isolated leads | 3 WERONA ROAD, FAIRHAVEN VIC 3231 | 30060390 |  |  |  | Leakage |  |  | 2 | Customer reported transformer on fire. Attending crew found Fuse switch disconnector had overheated | Disconnector/isolator | 0 | 0 | 0 |  | WPD014 | leakage | Pole-top fire | 24/03/2019 22:33 | 1 | Negligible: no ground fire | 12419 | Roadway |  | 20190329PWA_03 | Infrastructure (network-based) | -38.4657 | 144.0812 | 1 | Powercor | Report | 15632 | 0.0057407 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Fairhaven | Fuse
crew Replaced EDO assembly | 6515 BENALLA-TOCUMWAL ROAD, YARROWEYAH VIC 3644 | 30326765 |  | Lightning |  |  |  |  | 2 | Customer reported lightning has struck power pole out the front of property. Crew found lightning had damaged an EDO fuse unit and started a 100m x 20m grass fire, no reported injuries or property damage. | EDO fuse | 0 | 0 | 0 |  | CME015 | Lightning | Grassfire | 29/03/2019 11:34 | 1 | Small: 10 - 1000 sq.m | 12420 | Agricultural |  | 20190329PWA_04 | Infrastructure (network-based) | -35.955 | 145.61 | 1 | Powercor | Report | 15635 | 0.014169 | 22kV AC | Shepparton Airport | 3644 | Yarroweyah | Lightning
Made safe | 4 HUME DRIVE, SYDENHAM VIC 3037 |  | Vandalism;Theft;Unauthorised access | [6 empty] | Unknown person(s) have been ripped open the pit and stole assets. | Cable | 0 | 0 | 0 |  |  | Vandalism by unknown person(s) | Damage to network assets | 43469.634 |  |  | 12429 | Roadway |  | 20190401JEM_03 | Infrastructure (network-based) | -37.7106 | 144.7556 | 1 | Jemena | Report | 16933 | 0.014263 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Sydenham | Other
Site made safe Pole has been cut and damaged wooden HV10 crossarm replaced by HV ASIN2.6 steel crossarm | 3A INDWE STREET, WEST FOOTSCRAY VIC 3012 | A052410 |  |  |  | Leakage |  |  | 2 | Pole top fire caused by earth leakage on LV/HV pole no. A052410 No photo of the incident is available | Crossarm (wood) | 0 | 0 | 0 |  | TH11 | Pole top fire due to tracking | Pole-top fire | 29/03/2019 21:30 | 1 | Negligible: no ground fire | 12432 | Residential |  | 20190402JEM_01 | Infrastructure (network-based) | -37.804 | 144.8699 | 1 | Jemena | Report | 17749 | 0.0086192 | 22kV AC | Essendon Airport | 3012 | West Footscray | Pole
On arrival crew isolated supply and carried out repairs. | 20-24 AJAX ROAD, ALTONA VIC 3018 | 30108857 |  |  |  | Leakage |  |  |  | Vic fire reported a pole fire at incident location. On arrival the crew found a crossarm burnt on one end. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | AL011 | Excessive leakage current | Pole-top fire | 29/03/2019 21:29 | 1 | Negligible: no ground fire | 12434 | Roadway |  | 20190402PWA_03 | Infrastructure (network-based) | -37.8561 | 144.808 | 1 | Powercor | Report | 15654 | 0.031289 | 11kV AC | Laverton Raaf | 3018 | Altona | Crossarm
Crew attended, transferred customers on blue phase to other phases and cut blue phase conductor away removed tiger tails and cancelled permit to work on issue to customer | 6A VILLAMANTA STREET, GEELONG WEST VIC 3218 | 31012701 |  | Wind |  |  |  |  | 2 | Energysafe Victoria passed on a report from a resident advising that the low voltage conductor was contacting the metal roof of the house. House is on corner and greatest concern was with frontage to McNicol street. image provided. | Conductor (bare) | 0 | 0 | 0 |  | GCY014 | Excessive conductor movement under wind after fitting of 'tiger tails" | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/03/2019 14:28 |  |  | 12435 | Residential |  | 20190402PWA_04 | Infrastructure (network-based) | -38.1462 | 144.3517 | 1 | Powercor | Report | 15656 | 0.029962 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Conductor
Section was isolated and high voltage crossarm was replaced with a steel crossarm under access permit | 1 HARDIE ROAD, YARRAVILLE VIC 3013 |  |  |  |  | Leakage |  |  | 1 | Pole top fire involving HV23 wooden crossarm on pole no. A030064 due due to earth leakage No feeder fault occurred Wooden crossarm has been replaced with a steel crossarm A photograph is attached in the "Notes & Findings" section | Crossarm (wood) | 0 | 0 | 0 |  | FW13 | Earth leakage | Pole-top fire | 43619.7403 | 1 | Localised: less than 10 sq.m | 12444 | Industrial |  | 20190403JEM_01 | Infrastructure (network-based) | -37.8188 | 144.8595 | 1 | Jemena | Report | 15668 | 0.015668 | 22kV AC | Essendon Airport | 3013 | Yarraville | Crossarm
Builder advised CP by telephone that works on site have ceased. (builder currently on leave) | 67 TYPE STREET, RICHMOND VIC 3121 | 30189412 | Building too close or within the No Go Zone | [5 empty] | 2 | citipower officer attending site for permit to work request identified construction works . Parts of partially completed building found to be approx 1100mm from 11kv bushings at pole type transformer in glasshouse street. | Pole mounted;Dropper/bridge | 0 | 0 | 0 |  | NR002 | interference | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43681.5 |  |  | 12476 | Construction |  | 20190408PWA_05 | Infrastructure (network-based) | -37.8227 | 145.0095 | 1 | CitiPower | Report | 15708 | 0.021628 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3121 | Richmond | Other
On arrival crew isolated supply and carried out repairs. | 1047 NGALLO ROAD, CARINA VIC 3512 | 31021367 |  |  |  | Leakage |  |  |  | Customer reported wire down in the paddock, wire is only 8 foot off the ground at 1047 Ngallo Road, wire is resting on top of a poly tank and goes over the gateway. Crew found Carina P26 Burnt and broken cross arm There was no ground fire, no property damage and no injuries. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current caused crossarm to catch on fire and fail. | Pole-top fire | 43589.8187 | 1 | Negligible: no ground fire | 12477 | Agricultural |  | 20190408PWA_06 | Infrastructure (network-based) | -35.2868 | 141.0811 | 1 | Powercor | Report | 15710 | 0.03572 | 22kV AC | Mildura Airport | 3512 | Carina | Crossarm
service connections repaired | 96 WESTON STREET, BRUNSWICK VIC 3056 | 30155436 |  |  |  | Corrosion |  |  |  | Person received an electric shock when he was showering and he simultaneously contacted the Metallic taps with his hand and the metallic waste with his foot | Service conductor | 0 | 0 | 0 |  | C028 | Corroded service neutral at pole | Minor shock | 43558.6667 |  |  | 12478 | Residential |  | 20190408PWA_07 | Infrastructure (network-based) | -37.7757 | 144.9693 | 1 | Powercor | Report | 15711 | 0.0245 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
On arrival crew isolated supply and carried out repairs. | 21 GLEN STREET, WALPEUP VIC 3507 | 30097832 |  |  |  | Leakage |  |  |  | Reports of pole fire, crew arrived and CFA and police in attendance. HV cross-arm had burnt out and HV conductors were on LV cross arm. Crew checked and HV conductors have not made contact with LV conductors and no reports of HV injection. No ground fire. No injuries. No third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current caused crossarm to burn and fail | Pole-top fire | 31/03/2019 11:39 | 1 | Negligible: no ground fire | 12479 | Roadway |  | 20190408PWA_08 | Infrastructure (network-based) | -35.1398 | 142.0249 | 1 | Powercor | Report | 15712 | 0.023978 | 22kV AC | Mildura Airport | 3507 | Walpeup | Crossarm
On arrival crew isolated supply and carried out repairs | 5235 MURRAY VALLEY HIGHWAY, NATYA VIC 3597 | 33067603 |  |  |  | Leakage |  |  |  | Customer reported pole fire at incident location. On arrival crew found top of pole had been burnt off at king bolt location There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BBD014 | Excessive leakage current caused pole top to burn off | Pole-top fire | 24/03/2019 10:14 | 1 | Negligible: no ground fire | 12480 | Roadway |  | 20190408PWA_09 | Infrastructure (network-based) | -34.972 | 143.2939 | 1 | Powercor | Report | 15713 | 0.010058 | 22kV AC | Swan Hill Aerodrome | 3597 | Natya | Pole
Fault crew dispatched to investigate. Candled HV BA fuse replaced and supply restored. | 25 ELEANOR DRIVE, SILVAN VIC 3795 | LIS1013469 |  |  |  | Candled fuse |  |  |  | E0018526 - Customer reported "flashes" from pole near their premises. Found to be candled fuse | Boric acid | 0 | 0 | 0 |  | LDL13 | Fault crew attended and found candled 6K BA fuse on the footpath side. No Evidence of ground fire Fuse replaced and supply restored | Pole-top fire | 43589.8229 | 1 | Negligible: no ground fire | 12473 |  |  | 20190408SPN_01 | Infrastructure (network-based) | -37.8476 | 145.4741 | 2 | AusNet Services Distribution | Report | 15704 | 0.013326 | 22kV AC | Moorabbin Airport | 3795 | Silvan | Fuse
The crew isolated the affected area pending further investigation by an LEI and restored supply to the other customers affected by this outage. | 22 BYRNE STREET, YAAPEET VIC 3424 | 32123038 |  |  |  | Leakage |  |  | 1 | Powercor received a report from the CFA of a Pole Fire at 222 Byrne Street Yapeet. A Powercor crew attended at determined that a Pole Fire had occurred on Jeparit Pole 627. The X-arm had burnt through at the X-arm strap bolt and one of the HV conductor had come to rest on a LV conductor on the x-arm below. There was no ground fire or reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | NHL015 | excessive leakage current caused HV crossarm to catch fire and fail. | Pole-top fire;HV injection | 43712.1264 | 1 | Negligible: no ground fire | 12483 | Roadway |  | 20190409PWA_01 | Infrastructure (network-based) | -35.7683 | 142.0542 | 1 | Powercor | Report | 15718 | 0.041559 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3424 | Yaapeet | Crossarm
On arrival crew isolated supply and carried out repairs | 140-182 GRAY COURT, DEANSIDE VIC 3336 | 30107106 | Copper theft | [6 empty] | Report received from an REC to advise partial loss of supply to a property in Gray Court Rockbank. Upon arrival the crew found that someone had attempted to pull down the 3/c twisted grey overhead service. They had also pulled out the LV underground service from an adjacent pit on the fence line. In either attempting to pull down the overhead service or cut through the underground service, the interference with our assets has resulted in the operation of the LV transformer fuse. No assets were stolen, however follow up works were required to repair the damaged overhead service. There was no fire, no reported injuries. | Service conductor;Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Attempted copper theft | Loss of supply;Damage to network assets | 13/03/2019 17:38 |  |  | 13494 | Roadway |  | 20190411PWA_01 | Infrastructure (network-based) | -37.7339 | 144.6955 | 1 | Powercor | Report | 16990 | 0.025204 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Other
On arrival crew confirmed isolation and carried out repairs. | DAVIS ROAD, TARNEIT VIC 3029 | 30276723 | Copper theft | [6 empty] | Public lighting operational Faults Group received an information about a copper theft at the incident location. An fault crew attended and found approx. 300m of P/L service cable had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | TNA013 | copper theft | Damage to network assets | 13/03/2019 9:26 |  |  | 13496 | Roadway |  | 20190411PWA_02 | Infrastructure (network-based) | -37.8439 | 144.6516 | 1 | Powercor | Report | 16742 | 0.039745 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and carried out repairs. | 548 MINYIP-COROMBY ROAD, MINYIP VIC 3392 | 32112021 |  |  |  | Leakage |  |  |  | CFA Brigade reported as per police, pole fire, Cnr Robbins Rd & Coromby-Minyip Rd Minyip, top of pole on fire, Brigade enroute. Due to a pole fire the crew found live SWER conductor hanging approximately 3.6m above road and railway line There was a small ground fire: 50m x 30m = 1,500m2, no property damage, no injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | STL006 | excessive leakage current caused pole top to catch fire. | Grassfire | 43773.3264 | 1 | Medium: 1000 sq.m - 10 ha | 13497 | Agricultural |  | 20190411PWA_03 | Infrastructure (network-based) | -36.4998 | 142.568 | 1 | Powercor | Report | 16968 | 0.035906 | 12.7kV AC (SWER) | Horsham Aerodrome | 3392 | Minyip | Pole
On arrival isolation confirmed and replacement of cable organised. | 6 MCCONCHIE AVENUE, KEW EAST VIC 3102 | 30179070 | Copper theft | [6 empty] | A customer reported what appears to be interference and possible copper theft. On arrival crew found that the underground service cable has been stolen prior to a new connection being made. This cable was a new supply to replace exiting builders temp supply. There was no fire,no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | Q014 | copper theft | Damage to network assets | 19/03/2019 0:10 |  |  | 13499 | Roadway |  | 20190412PWA_01 | Infrastructure (network-based) | -37.7958 | 145.0439 | 1 | CitiPower | Report | 17016 | 0.028264 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | Other
On arrival crew confirmed isolation of supply and untangled conductors | 1091 HEATHCOTE-NAGAMBIE ROAD, COSTERFIELD VIC 3523 | 32052855 | Working too close to overhead lines | [5 empty] | 1 | Jason reported haulage excavator has hit overhead wires at Donelly Lane, next to mine, wires are tangled. Crew found the excavator contacted the 3/2.75 3 phase steel between pole Mid East P7 405052 and P8 405053 at the Mandalay Resources mine, mill site. Work Safe were onsite doing an investigation. There was no fire or reported injuries.. | Conductor (bare) | 2 | 2 | 2 |  | BGO023 | Excavator working at mine site became entangled withe conductors. | Loss of supply;No Go Zone (contact) | 43773.3847 |  |  | 13501 | Commercial |  | 20190412PWA_02 | Infrastructure (network-based) | -36.8891 | 144.7919 | 1 | Powercor | Report | 16941 | 0.00059606 | 22kV AC | Mangalore Airport | 3523 | Costerfield | Vehicle
On arrival crew removed bird from structure, supply was restored | 359 SAN MATEO AVENUE, MILDURA VIC 3500 | 33063508 |  | Bird | [5 empty] | A Sparking Transformer was reported by customers. Sparks reaching ground and started a grass fire. Three magpies flashed over at the top of the substation pole. CFA Attended small scorched area where magpies fell. There was no reported injuries or third party property damage. | Crossarm (steel) | 2 | 2 | 2 |  | MDA034 | Bird Incident | Grassfire | 43773.7597 | 1 | Localised: less than 10 sq.m | 13502 | Roadway |  | 20190412PWA_03 | Infrastructure (network-based) | -34.2055 | 142.1482 | 1 | Powercor | Report | 16939 | 0.037164 | 22kV AC | Mildura Airport | 3500 | Mildura | Animal
The fault crew isolated supply to make safe and allow for repairs to be completed. | 52 MARSH COURT, WOODEND VIC 3442 | 30036024 | Working too close to underground cables |  |  |  |  | Phase to earth |  | A fencing contractor called to advise that his post hole digger operator had hit an electric cable and received a mild shock to the right hand. On arrival the fault crew found that the post hole digger operator had struck a customer's underground service cable between the pit and the house, receiving a mild shock. The operator was still onsite when the crew arrived, the NAO instructed the crew to advise the operator to seek medical advise, which we were told he later did. The fencing contractors had dial before you dig plans, however being a private UG service cable, it didn't appear on their plans. There were no other reported injuries, third party damage or fires. | Services cable | 2 | 2 | 2 |  | WND011 | Fencing contractor drilling post holes on private property | Minor shock | 19/03/2019 13:15 |  |  | 13506 | Residential |  | 20190415PWA_02 | Infrastructure (network-based) | -37.3543 | 144.4636 | 1 | Powercor | Report | 16753 | 0.025045 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Woodend | Dug up
Crew repaired street light cable | 1 GOURLAY ROAD, HILLSIDE VIC 3037 |  | Copper theft | [5 empty] | 2 | Attempted copper theft from street lighting | Cable | 2 | 2 | 2 |  | SHM14 | Unknown person or thief tried to steal copper | Damage to network assets | 16/04/2019 6:58 |  |  | 13523 | Roadway |  | 20190416JEM_02 | Infrastructure (network-based) | -37.693 | 144.7449 | 1 | Jemena | Report | 16773 | 0.012619 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Hillside | Other
Crew arrived to find service in contact with trailer. Service disconnected pole end, made safe. Crew attending evening to replace service.. | 19 CHAMBERS ROAD,ALTONA NORTH,VIC,3025 | 30114666 | Crane, excavator or other construction/farming equipment | [6 empty] | Service wire from pole to this site has been hit by forklift, wire has snapped in half. live end still connected at pole is in contact with a large box trailer in the yard. No fire and no reported injury. | Service conductor | 2 | 2 | 2 |  | AL002 | Forklift traversing site struck service line | Loss of supply;Damage to network assets | 43469.6451 |  |  | 13524 | Industrial |  | 20190416PWA_05 | Infrastructure (network-based) | -37.8424 | 144.841 | 1 | Powercor | Report | 16969 | 0.013905 | Low voltage AC (<1kV) | Laverton Raaf | 3025 |  | Vehicle
The Powercor crew made the site safe. The live cable ends were capped. Pit lids and remnant cables were placed back in pits. New underground cable was not re-installed. Repair will be arranged on follow-up further to discussions within Powercor. | HUME DRIVE, CARLONE SPRINGS VIC 3023 | 60327964 | Vandalism;Copper theft | [6 empty] | A passing member of the public, (Wayne Mob. 0404 510 255), reported possible cable theft with multiple pits opened, cable ends exiting A Powercor crew attended the site and noted that underground cable within a lighting scheme comprising at least 11 steel, vehicular lighting poles had been cut, damaged or stolen. Approx. 440m of 4c x 35mm underground cable was stolen. Remnant cable ends on the ground at each end were found alive and uncapped. This lighting scheme runs parallel to a footpath/walkway and is located in the vicinity of schools at the Lancefield Drive end.pits onto the ground along a 670m stretch of Hume Road in Caroline Springs between Lancefield Drive and Kirkwood Way. There was no fore and no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | SA011 | copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/03/2019 11:51 |  |  | 13526 | Roadway |  | 20190416PWA_06 | Infrastructure (network-based) | -37.7102 | 144.7363 | 1 | Powercor | Report | 16981 | 0.020153 | Low voltage AC (<1kV) | Melbourne Airport | 3023 | Carlone Springs | Other
controller asked the crew was safe and were clear and they confirmed they were all safe and clear and had barricade the area. Fault crew was dispatched. | 54 SUMMIT AVENUE, BELMONT VIC 3216 | 32070671 | Working too close to overhead lines | [5 empty] | 2 | Powercor was advised that a LV conductor came down while Carrying out Tree Clearing. | Conductor (bare) | 0 | 0 | 0 |  | GLE012 | Vegetation: Trees Incident | Loss of supply | 43802.5611 |  |  | 13530 | Residential |  | 20190417PWA_01 | Infrastructure (network-based) | -38.1819 | 144.3289 | 1 | Powercor | Report | 16993 | 0.0030405 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Trees
Crew replaced service line | 7 SALISBURY STREET, WERRIBEE VIC 3030 | 32175388 |  |  |  | Neutral fault |  |  | 2 | Person received an electric shock when he simultaneously contacted the Metallic Meter Box with his hand and Standing bare foot on the ground | Service conductor | 0 | 0 | 0 |  | WBE034 | Damaged Neutral Screen service cable | Minor shock | 43619.7917 |  |  | 13533 | Residential |  | 20190417PWA_02 | Infrastructure (customer connection) | -37.9016 | 144.6663 | 1 | Powercor | Report | 17000 | 0.034439 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | OH Cable
Crew installed a new 4 Wire service | 2 WALKER STREET, BELMONT VIC 3216 | 31012314 |  |  |  | Corrosion;Neutral fault |  |  | 2 | Person was removing and replacing an old galvanised underground water pipe when he felt slight tingles to both hands when coming in contact with the pipe and the ground. | Service conductor | 0 | 0 | 0 |  | GLE012 | neutral corroded and deteriorated | Minor shock | 22/02/2019 12:00 |  |  | 13534 | Industrial |  | 20190417PWA_03 | Infrastructure (customer connection) | -38.1834 | 144.3524 | 1 | Powercor | Report | 17002 | 0.0072731 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | OH Cable
A fault crew attended and undertook repairs to conductors under access authority conditions. The crew attempted to get the details of the driver, but he was not cooperative and refused to give his details. The crew were able to obtain the crane company details off the side of the crane. | 41 CHRISTENSEN STREET, CHELTENHAM VIC 3192 | 1816830 | Vehicle;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | A Franna crane contacted HV lines. Protection operated. No injury occurred. Aluminium conductor sustained some damage. | Conductor (bare) | 2 | 2 | 2 |  | HT02 | The Franna Crane was unloading a shipping container on the side of the road opposite to the powerlines. It appears that after unloading the shipping container, the driver of the crane decided to do a U-turn in the street. This was done with the crane still in the elevated position, and resulted in contact being made with the live OH conductors. | Loss of supply;Damage to network assets | 15/04/2019 9:25 |  |  | 13531 | Roadway |  | 20190417UTD_01 | Infrastructure (network-based) | -37.9497 | 145.0667 | 1 | United Energy Distribution | Report | 17033 | 0.0405 | 22kV AC | Moorabbin Airport | 3192 | Cheltenham | Vehicle
Crews attended and made repairs to assets under access authority conditions. | 37 TUBBARUBBA ROAD, MERRICKS NORTH VIC 3926 | 1105853 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | A truck was delivering produce to a vineyard in Tubbarunna Rd Merricks Nth and has hit the HV line in the property, pulling down the lines and one pole including a pole transformer. The HV fuses operated to isolate the damaged section. | Conductor (bare) | 0 | 0 | 0 |  | MTN24 | The cause of the incident was the truck delivering produce to the farm has hit the overhead HV lines and pulled down the lines and a pole. | Loss of supply;No Go Zone (contact);Damage to network assets | 16/04/2019 16:15 |  |  | 13532 | Agricultural |  | 20190417UTD_02 | Infrastructure (network-based) | -38.3332 | 145.0789 | 1 | United Energy Distribution | Report | 17019 | 0.0046308 | 22kV AC | Moorabbin Airport | 3926 | Merricks North | Vehicle
On arrival crew isolated supply and organised repairs. | 21 BUTTERMINT CRESCENT, MANOR LAKES VIC 3024 | 60381520 | Copper theft | [6 empty] | An electrical contractor, Mark, (Mob. 0403 696 604), rang to report that thieves had attempted to steal cables from an LV pit outside No. 21 Electrical cabling was exposed and damaged at the pit. Mark capped the customer cables, re-inserted them into the pit and restored the lid onto the pit. Mark advised that a lighting cable associated with URD pole LIS 867348 was damaged and disconnected and would need to be re-instated. | Services cable;Services pit | 2 | 2 | 2 |  | WBE014 | copper theft | Damage to network assets | 23/03/2019 14:10 |  |  | 13545 | Roadway |  | 20190418PWA_06 | Infrastructure (network-based) | -37.86 | 144.5933 | 1 | Powercor | Report | 16977 | 0.03277 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Other
On arriival crew isolated supply and carried out repairs | 41-53 ABEY ROAD, COBBLEBANK VIC 3338 | 33104229 | Vandalism;Copper theft | [6 empty] | Powercor crew found vandalised street light cables at the incident location and a discarded screw driver, cables were live and the crew made safe and arranged for repairs, damage was found near LIS 842973. It was observed that 2 phases had been cut at the same time causing a flashover. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | MLN013 | copper theft | Damage to network assets | 26/03/2019 12:56 |  |  | 13555 | Roadway |  | 20190418PWA_15 | Infrastructure (network-based) | -37.7055 | 144.5965 | 1 | Powercor | Report | 16972 | 0.016027 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
Fault crew dispatched. Candled fuse replaced with new 6k BA fuse | 30 WATTLE COURT, LANG LANG VIC 3984 | LIS514134 |  |  |  | Candled fuse |  |  |  | E0018927 - Candled HV Fuse BA 6K. No evidence of ground fire | Boric acid | 0 | 0 | 0 |  | LLG12 | Candled BA HV fuse. No evidence of ground fire | Pole-top fire | 18/04/2019 10:28 | 1 | Negligible: no ground fire | 13549 | Residential |  | 20190418SPN_02 | Infrastructure (network-based) | -38.2768 | 145.5694 | 2 | AusNet Services Distribution | Report | 16928 | 0.0047639 | 22kV AC | Moorabbin Airport | 3984 | Lang Lang | Fuse
On arrival crew isolated supply and carried out repairs. | HOPETOUN PARK ROAD, HOPETOUN PARK VIC 3340 | 30282319 | Copper theft | [6 empty] | Company employee (Jade Polidano) has found service cable between substation (LIS 776693) to the Hopetoun Park Road meter board has been stolen. About 25meters of 50mm2 UG XLPE removed. There was no fire or reported injuries | Services cable | 2 | 2 | 2 |  | BMH006 | copper theft | Damage to network assets | 28/03/2019 15:00 |  |  | 13565 | Roadway |  | 20190423PWA_03 | Infrastructure (network-based) | -37.6857 | 144.5024 | 1 | Powercor | Report | 16960 | 0.0022106 | Low voltage AC (<1kV) | Laverton Raaf | 3340 | Hopetoun Park | Other
isolated for repairs, made safe | 277 BLACK FOREST DRIVE, MACEDON VIC 3440 | 32050256 | Vandalism;Copper theft | [6 empty] | OPTUS MOBILE PTY LIMITED reported wire from transformer to optus shelter hanging 2 meters of the ground bare and live, caused by vandilsim underground wires been pulled out by car, very windy concerned may start fire dry grass around pole. Crew found copper theft damage., i. no ground fires or injuries reported. | Services cable | 2 | 2 | 2 |  | GSB014 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 29/03/2019 13:21 |  |  | 13567 | Roadway |  | 20190423PWA_05 | Infrastructure (network-based) | -37.4331 | 144.5579 | 1 | Powercor | Report | 16826 | 0.021257 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
Fault crews attended and made safe | 9 SALTWATER PROMENADE, POINT COOK VIC 3030 | 30304876 | Vandalism;Copper theft | [6 empty] | Passer by Marc 0423944574 reported that he can see underground wires exposed to Saltwater Promenade, also advised the wires seems to feed the street lights and looks like someone was trying to steal copper, wires are exposed on the middle isle of Saltwater Promenade on the cnr of Spencer Street. No reported injuries or fire. | Services cable | 2 | 2 | 2 |  | LV006 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/03/2019 15:29 |  |  | 13568 | Roadway |  | 20190423PWA_06 | Infrastructure (network-based) | -37.9109 | 144.76 | 1 | Powercor | Report | 16956 | 0.006478 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Crew attended site and replaced damaged service | 1 BALDWIN STREET,ARMADALE,VIC,3143 | 30165839 | Working too close to overhead lines | [6 empty] | Report received that a Service line has been cut by Aborist, The service is currently lying across the ground on the footpath, The Aborist,advises that he has put cones around the area to keep people away. There was no fire and no reported injuries. | Service conductor | 2 | 2 | 2 |  | AR013 | Arborist trimming vegetation | Loss of supply;Damage to network assets | 43469.5167 |  |  | 13572 | Residential |  | 20190423PWA_08 | Infrastructure (network-based) | -37.8551 | 145.0218 | 1 | CitiPower | Report | 16958 | 0.036231 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 |  | Other
Crew report LV cable damaged, damaged section of cable to be removed, requires two straight joints and re-sleeveing. Repairs completed | UNIT 1 1173 ISON ROAD, MANOR LAKES VIC 3024 | 30299824 | Working too close to underground cables | [6 empty] | Powercor received a report that an excavator has contacted Underground cable on Nature Strip opposite 1173 Ison. Conduit Broken, unsure if cable snapped. no smoking or sparking, unsure if supply affected. No permits on site. No reported injury and no fire. | Services cable | 2 | 2 | 2 |  | WBE014 | Excavator contacted underground cable | Damage to network assets | 43469.5417 |  |  | 13574 | Roadway |  | 20190423PWA_10 | Infrastructure (network-based) | -37.8704 | 144.5925 | 1 | Powercor | Report | 16953 | 0.017237 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Dug up
Fault crew attended and replaced the faulty LV isolator | 44 ROSEDALE ROAD, GLEN IRIS VIC 3146 | 2336334 |  | Heat |  | Overheated connection |  |  | 1 | Report received of a transformer fire at pole substation Brownell-Rosedale, however no customer supply affected. On attendance, crew found faulty transformer LV isolator. | Disconnector/isolator | 0 | 0 | 0 |  |  | Cause has been attributed to a combination of high electrical loading on day of high temperatures. | Plant/equipment | 43468.7868 | 1 | Negligible: no ground fire | 13570 | Roadway |  | 20190423UTD_01 | Infrastructure (network-based) | -37.8588 | 145.0711 | 1 | United Energy Distribution | Report | 16829 | 0.015672 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Connection
Fault crew and LEI dispatched. NST completed and passed at POA and switchboard. Loose connections rectified and tightned. Installation retested following repairs and passed. Waste pipe where the plumber received shock tested and no voltage found. Supply restored | 14 OSBORNE STREET, TRARALGON VIC 3844 | LIS2604497 |  |  |  | Not built/maintained to design |  |  |  | Plumber reported receiving an electric shock from pipe while working at property. | POA connection (customer side) | 0 | 0 | 0 |  | TGN43 | Plumber felt tingle off waste pipe at rear of house while unblocking drain. Customer REC reported measuring small voltage on pipe and called AusNet faults. Fault crew and LEI attended site and found a slightly loose connection on the customers side within the POA Fused mains box. Loose connections rectified and tightned. Installation retested following repairs and passed. Waste pipe where the plumber received shock tested and no voltage found. Supply restored | Minor shock | 43716.6424 |  |  | 14308 |  |  | 20190919SPN_03 | Infrastructure (customer connection) | -38.1897 | 146.5334 | 2 | AusNet Services Distribution | Report | 17991 | 0.017957 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Installation
Fault crew dispatched to investigate and make safe. HV was isolated. | 140 MYERS CREEK ROAD, HEALESVILLE VIC 3777 | LIS1409880 |  | Fallen | [5 empty] | Tree contacted and brought down O/H HV conductors | Conductor (bare) | 0 | 0 | 0 |  | WYK24 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/09/2019 8:44 |  |  | 14310 |  |  | 20190919SPN_05 | Infrastructure (network-based) | -37.6289 | 145.5204 | 1 | AusNet Services Distribution | Report | 17995 | 0.014822 | 22kV AC | Moorabbin Airport | 3777 | Healesville | Trees
Street circuit dumped to make safe. Repair of LV conductor organised. | 38 DENNIS STREET, CAMPBELLFIELD VIC 3061 | A086506 | Vehicle |  |  |  |  | Phase to earth | 2 | LV Red Phase and Neutral mains on ground after being pulled down by truck. | Conductor (bare);Aluminium | 0 | 0 | 0 |  | ST12 | Third party vehicle impact | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/09/2019 11:45 |  |  | 14317 | Residential |  | 20190920JEM_01 | Infrastructure (network-based) | -37.643 | 144.942 | 1 | Jemena | Report | 18447 | 0.036837 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Vehicle
On arrival crew made site safe and arranged for repairs. | 27 Daffodil Way, Point Cook VIC 3030, Australia | 60320485 | Copper theft | [6 empty] | Public Lighting Contractor crew Electrix attended a fault and found that there had been cable theft between LIS No. 795764 & 795765, crew noticed the pits lids were dislodged and Approximately 50mtrs of cable stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV010 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/09/2019 9:36 |  |  | 14314 | Roadway |  | 20190920PWA_02 | Infrastructure (network-based) | -37.8995 | 144.7467 | 1 | Powercor | Report | 17999 | 0.016241 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Site made safe Work stopped on site | 990 Norman St, Wendouree VIC 3355, Australia | 30253151 |  |  |  |  | Ineffective planning/procedures/processes |  | 1 | PAL construction project staff were directly supervising excavation works within Ballarat North 66/22kV Zone Substation. BAN008 feeder exit cable was damaged, resulting in a protection operation which isolated supply to 3604 customers. There was no injuries. | Cable | 2 | 2 | 2 |  | BAN008 | Excavator damaged HV cable at location where cable changed offsets. | Loss of supply;No Go Zone (contact);Damage to network assets | 18/09/2019 11:06 |  |  | 14316 | Industrial |  | 20190920PWA_04 | Infrastructure (network-based) | -37.5348 | 143.8468 | 1 | Powercor | Report | 18002 | 0.020934 | 22kV AC | Ballarat Aerodrome | 3355 | Wendouree | Dug up
Abandoned pit removed, guards put around HV & LV earths to deter thieves. | 114 Faulkners Rd, Mount Cottrell VIC 3024, Australia | 30108598 | Copper theft | [6 empty] | Chris from Electrics, LVUGC mains has been cut /stolen of TX pole FAULKNERS RD P6 Trans 1 Crew reports underground mains to an abandoned pit outside 114 Faulkner's Road has been removed, about 3 meters of underground service stolen. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 16/09/2019 8:40 |  |  | 14324 | Roadway |  | 20190924PWA_04 | Infrastructure (network-based) | -37.7564 | 144.6293 | 1 | Powercor | Report | 18013 | 0.0085023 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Mount Cottrell | Other
Crew attended and made the site safe. | 2 MAKER PLACE, TRUGANINA VIC 3029 | 35436558 | Vandalism;Copper theft | [6 empty] | Contractor reports LV Pit nearby Pole LIS 871277 appears to have been vandalised, cables exposed and cut. unsure if supply on. Upon arrival the PCA Field Crew have advised, an unknown person has opened up the 3x Service Pit's s and pulled out and preceded to Cut some of the public Lighting Cables. The LV cables laying on the ground adjacent to the affected pits were found to be ALIVE. There was no fire, no reported injuries or third party property damage | Services cable;Services pit (network) | 2 | 2 | 2 |  | LVN024 | vandalism and copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/09/2019 16:38 |  |  | 14328 |  |  | 20190924PWA_06 | Infrastructure (network-based) | -37.8185 | 144.7323 | 1 | Powercor | Report | 18017 | 0.033458 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
All supplies into the ZSS were remotely de-energised in order to make the site safe and begin rectification works. Multiple crews were dispatched to investigate and carry out repairs. A number of third party cranes were engaged by the crane operator and they began to remove the fallen crane from outside the station when deemed safe to by, and under the supervision of, AusNet crews. WorkSafe were in attendance. Temporary structure erected around/over damaged control room to allow supply restored. Repairs of the damaged control room are ongoing | BERWICK-CRANBOURNE ROAD, CLYDE NORTH VIC 3978 | LIS5637694 | Crane, excavator or other construction/farming equipment | [6 empty] | Whilst operating adjacent to CLN Zone Substation, a large 3rd party crane has toppled over falling into the ZSS fence and onto the control room. | Equipment;Switchyard;Zone substation | 0 | 0 | 0 |  | CLN | A large 3rd party crane being operated outside the station fence by â€œMelbourne Precast Concreteâ€ adjacent to CLN Zone Substation when it toppled over falling into the ZSS fence and onto the substation control room. The control room building has been significantly damaged as a result. Supply de-energised for numerous safety reasons (which also affected the Lang Lang ZSS) leaving 37,975 customers off supply initially but supply restored to all customers within 6-7 hours. It is believed the crane operator was preparing to relocate the crane and began lifting the crane supports/legs before removing the counter weights causing the crane to fall. The control room building has been badly damaged and a temporary structure has been erected around the building to enable the communications, equipment and switch gear within the building to be repaired and put back into service. Rectification works on the control room building is ongoing and the temporary structure will remain in place until this work is completed. | Significant disruption to the community;Damage to network assets | 25/09/2019 15:24 |  |  | 14331 | Other | Zone Substation | 20190926SPN_01 | Infrastructure (network-based) | -38.0946 | 145.3328 | 1 | AusNet Services Distribution | Report | 18023 | 0.022044 | 66kV AC | Moorabbin Airport | 3978 | Clyde North | Vehicle
On arrival crew isolated supply. Customer issued with defect notice to replace service cable. | 88 CUTTRISS ROAD, WERRIBEE SOUTH VIC 3030 | 32171386 | Working too close to underground cables | [6 empty] | A customer reported his contractor has damaged his underground service cable. The excavator is now clear, conduit broken and cables exposed. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | WBE034 | customers contractor excavating on probate property | Loss of supply | 17/09/2019 12:03 |  |  | 14335 | Agricultural |  | 20190930PWA_02 | Infrastructure (customer connection) | -37.9643 | 144.673 | 1 | Powercor | Report | 18027 | 0.0037905 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee South | Dug up
On arrival crew isolated supply and arranged repairs. | 442 ROMSEY ROAD, WOODEND VIC 3442 | 30319279 | Copper theft | [6 empty] | An employee reported pit lids removed and cable exposed at incident address. Crew dispatched and on arrival found evidence of attempted copper theft. 2 pits had been lifted and cable cut. Rope had been tied to one of the cables and snapped as their cuts were not on the same cable. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WND022 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/09/2019 9:15 |  |  | 14340 |  |  | 20190930PWA_05 | Infrastructure (network-based) | -37.3435 | 144.5849 | 1 | Powercor | Report | 18032 | 0.028376 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Other
Crews attended and repaired blue and neutral conductors | 6A MERCER PARADE, NEWTOWN VIC 3220 | 30057934 |  | Within clearances | [5 empty] | A Landscape gardener was removing customer tree when a limb was accidentally dropped on LV street mains; Supply was interrupted to 90 customers when LV fuse operated as expected.. An LV conductor had fallen too ground. Police & SES onsite before crews arrived. No fire, injuries or 3rd party property damage reported | Conductor (bare) | 2 | 2 | 2 |  | GL022 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 21/09/2019 11:52 |  |  | 14348 | Roadway |  | 20191002PWA_02 | Infrastructure (network-based) | -38.1529 | 144.3448 | 1 | Powercor | Report | 18043 | 0.020456 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown | Other
On arrival crew confirmed isolation s and carried out repairs. | 10 ANDREW STREET, SUNSHINE VIC 3020 | 32171698 | Vehicle | [6 empty] | Brimbank City Council reported a wire down over a truck, and that Mark 0432 798 121 was still inside the truck. On arrival the crew reported that the truck was no longer on site. The crew believed fixing point of the service to the pole had come loose, allowing the service to hang low across the street. The truck has then contacted the low hanging service cable causing it to be disconnected from the LV Mains and fall to the ground de-energized. There were no reported injuries, fires or third party damage. | Service cable (insulated) | 2 | 2 | 2 |  | SSE032 | Truck contacted service line | Loss of supply;Damage to network assets | 24/09/2019 8:19 |  |  | 14354 | Roadway |  | 20191003PWA_01 | Infrastructure (network-based) | -37.7813 | 144.841 | 1 | Powercor | Report | 18051 | 0.023064 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | AF Other
On arrival crew isolated supply and carried out repairs. | 89 High St, Northcote VIC 3070, Australia | 30247235 |  |  |  | Overheated connection |  |  |  | MFB reported a fire at incident location. On Barry-High s/s the IPC became loose and melted. As a result the LV bus cable (white phase) on the west circuit came down. This side of the circuit was de energised. Debris from this feel on a vehicle below. There was no fire or reported injuries. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | NC001 | connection ruptured | Loss of supply;Melting or smoking only;Damage to network assets | 27/09/2019 16:44 |  |  | 14356 | Roadway |  | 20191003PWA_03 | Infrastructure (network-based) | -37.78 | 144.9964 | 1 | CitiPower | Report | 18053 | 0.03323 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
Supply isolated repairs arranged | 727 High St, Melton West VIC 3337, Australia | 30298016 | Copper theft | [6 empty] | Customer reported Clarkes Rd/Bulmans Rd - between Western Fwy and High St that Streetlights not working due to pit covers removed and wires exposed - potentially vandalised/removed. Upon arrival the crew found service cables feeding multiple Street lights cable in Bulmans Rd from LIS 784382 to over pass bridge approximately 10 poles exposed and stolen. The time/date of the theft is not known. Crew replaced the cables and made safe. There was no fire, no reported injuries or third party property damage | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN022 | Copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/09/2019 15:21 |  |  | 14359 | Roadway |  | 20191003PWA_06 | Infrastructure (network-based) | -37.6859 | 144.5497 | 1 | Powercor | Report | 18058 | 0.0029572 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
â€¢ Crews has disconnected and abolished the existing OH service and disconnected electricity meter. â€¢ REC/electrician to rectify compliance issues, provide new COES and reschedule new connection. | 29 REGENT STREET, PRESTON VIC 3072 | A080692 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address today with an anytime SO for an abolishment of 1 phase overhead supply and metering (SO: 100101201216) in conjunction with a new connection for a 1 phase overhead supply and metering (SO: 100101204461) â€¢ Existing 1ph service fuse had been removed and dummy fuse inserted (no distributor type) (existing 1ph OH S/L still connected). â€¢ Existing customer mains disconnected and cut away (still connected at existing FOLCB). â€¢ Existing timber meter panel and electricity meter removed. â€¢ No new POA installed (COES states â€œinstallation of new point of attachmentâ€). â€¢ No raiser bracket installed to improve or achieve service heights. â€¢ Attempted contact with electrician was made without success. â€¢ Contact was made with REC and issues explained (REC and electrician are direct persons). â€¢ Property owner was on site (who advised the electrician is her grandson). â€¢ Property owner advised supply has been disconnected and off supply since January 2019. â€¢ Property owner advised that property is currently not tenanted. â€¢ Property owner called her electrician grandson who is currently holidaying in Queensland. Photos are attached in the "Notes & Findings" section | Connection box;Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | CN03 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/09/2019 12:24 |  |  | 14365 | Residential |  | 20191007JEM_01 | Infrastructure (network-based) | -37.7306 | 145.0017 | 1 | Jemena | Report | 18065 | 0.008441 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Following the incident, the site was immediately made safe. The cutter made a phone call to his his immediate supervisor and then called system control to report the fault. The supervisor has then called Area manager for Asplundh who notified Cameron Laing from UE. An Asplundh GF was sent to the site. Asplundh Manager arrived at site interviewed and took relevant photos of site at approx 10.00am , the 2 operators had drug and alcohol tests at 11.30am and GF remained on site till approximately 1.30pm when the service wire was reinstalled. | 12 BRIAN STREET, BENTLEIGH EAST VIC 3165 |  |  | Within clearances |  |  | Poor workmanship |  | 2 | On Monday 16th September 2019 at approximately 8.50am a crew from Enviro Trees were trimming vegetation at 12 Brian St Bentleigh East in a 29ft Versalift EWP. The weather conditions were fine and dry with minimal wind , this was the 5th job for the day and the job was to clear the pole and also a cross service wire (LIS 1802431).The cutter was using a sweeping action with the cutting head above the service wire , the vegetation has pulled the service wire towards the cutting head and made contact causing the service to be cut in half. The cutter has immediately ceased work and alerted the observer who upon closer inspection has prepared a seclusion zone around the pole and service wire that remained in the air and also recoiled back into the front yard at Number 12 Brian st. | Service cable (insulated) | 0 | 0 | 0 |  |  | Two key causes of the incident were poor technique to maintain appropriate clearances whilst cutting vegetation and due to poor positioning of the safety observer. Better positioning of the safety observer may have resulted in clearer communication and greater awareness of proximity to the service cable whilst cutting. | Damaged service wire;Other | 17/09/2019 8:50 |  |  | 14367 | Residential |  | 20191007UTD_01 | Infrastructure (customer connection) | -37.9249 | 145.0516 | 1 | United Energy Distribution | Report | 18097 | 0.011565 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Other
Site made safe and repairs organised. | 2 BANOOL AVENUE, YARRAVILLE VIC 3013 | A099328 | Copper theft | [5 empty] | 2 | Copper theft at the Cable Head Pole at VR-Yarraville traction substation on feeder YVE11. The copper dropper has been removed from about halfway down the pole to the ground. | Pole (wood);Dropper/bridge | 0 | 0 | 0 |  | YVE11 | Copper theft by unknown persons | Damage to network assets | 43718.5042 |  |  | 14369 | Industrial |  | 20191009JEM_01 | Infrastructure (network-based) | -37.8217 | 144.888 | 1 | Jemena | Report | 18072 | 0.028236 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Other
Supply isolated LEI arranged to review HVI cases Crossarm replaced | 12 Andrew Ave, Woodend VIC 3442, Australia | 30033904 | [7 empty] | Following a feeder outage a crossarm was found to have broken at pole 1 Andrews avenue woodend. There was reports of HVI. There was no fire reported. | Crossarm (wood) | 2 | 2 | 2 |  | WND022 | To be advised | HV injection;Loss of supply;Damage to network assets | 13/10/2019 18:46 |  |  | 14380 | Roadway |  | 20191014PWA_02 | Infrastructure (network-based) | -37.3609 | 144.5462 | 1 | Powercor | Notification | 18090 | 0.00064815 | 22kV AC | Melbourne Airport | 3442 | Woodend | Crossarm
Fault crews attended the site and found a damaged LV underground cable from pole to pit in front of #11. Fault crews isolated the supply and the service cable was repaired and put back on supply. | 11 EDITH COURT, BENTLEIGH EAST VIC 3165 | 1801635 | Working too close to underground cables | [5 empty] | 1 | UE received a call from customer that a contractor has dug up an underground cable. | Cable | 0 | 0 | 0 |  |  | The underground cable was damaged by an excavator. | No Go Zone (contact);Damage to network assets | 43779.4479 |  |  | 14377 | Roadway |  | 20191014UTD_02 | Infrastructure (network-based) | -37.9243 | 145.0684 | 1 | United Energy Distribution | Report | 18169 | 0.0049317 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Dug up
Fault crew dispatched Spoke with container lift operator following the incident. He seemed fine and he was advised to seek medical advice now or if he experiences any issues over the coming days. He had only started working at the site 3 weeks ago and was not aware of the conductors existence prior to the incident nor had his employer discussed this potential hazard. Recommended the Container Lift be inspected by a mechanic prior to further use. The Manager (John Nelson) reported the matter to Worksafe on the day of the incident and provided reference â€œID-00850â€. He also advised that concrete barriers would be placed on the internal roadway the following day to prevent access by the Container Lift and the large tip trucks to avoid any chance of a re-occurrence. O/H conductor repaired and supply restored. Upon completion of repairs the conductors were measured at 7.9m above ground. There was no damage to the poles or insulators either side of the incident. | WODONGA SALEYARDS, 120 WHYTES ROAD, BANDIANA VIC 3691 | LIS5209508 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [6 empty] | Report of Container lift contacting and bringing down O/H HV conductors | Conductor (bare) | 0 | 0 | 0 |  | WOTS25 | Container lift operator had loaded a container on the Container Lift and was waiting for a truck to arrive to load it on. He had his lunch with him in the cabin of the container lift and decided to drive to where his car was parked in the shade to have lunch while he was waiting. He reversed the container lift along the internal roadway and came into contact with the overhead conductor. He heard a sparking noise initially followed by a loud bang and saw a flash out of the corner of his eye. He stopped the Container lift when he noticed conductors on the ground and spot fires in the direction he was travelling. He drove the Container lift forward about 6-10m away from the fallen power lines, exited the Container Lift with a chemical powder fire extinguisher and walked back to extinguish the fire before waiting for another worker and his supervisor to arrive. They inspected the Container Lift and proceeded to drive it away to load the truck. They were not able to continue working though due having no power at the site to operate the weighbridge. The Container lift had been moved and continued to be used after the incident and had a container slung under the yellow platform at the time of the incident. There were flash marks visible on the mast of the Container Lift at a number of sites. As the Container lift had been moved, the height was simulated and the mast of the Contain Lift raised into the height they believed it to have been at the time of the incident. Highest flash marks were measures at 7.2m and the lowest at 6.5m. Two phases of the three conductors had broken and fallen to the ground. The third remaining conductor had some discolouration from the flash but appeared okay. The height of the remaining conductor over the road was measured at 5.9m after the incident. Upon completion of repairs the conductors were measured at 7.9m above ground. There was no damage to the poles or insulators either side of the incident. | Grassfire;No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43475.5938 | 1 | Localised: less than 10 sq.m | 14384 |  |  | 20191015SPN_02 | Infrastructure (network-based) | -36.1471 | 146.9431 | 1 | AusNet Services Distribution | Report | 18100 | 0.030865 | 22kV AC | Wangaratta Aero | 3691 | Bandiana | Vehicle
Crew replaced the pit lid and made safe. | 7A Chardia Ct, Brookfield VIC 3338, Australia | 30293003 | Vandalism | [6 empty] | Customer advised, on Brooklyn Rd - between Clarkes Rd and Botanica Springs Blvd, streetlights aren't working with one them indicates live wires exposed, pit covers removed, appears to have been vandalised. Upon arrival the crew found no cable stolen but damaged pit lid . There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Vandalism | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/09/2019 22:40 |  |  | 14385 | Roadway |  | 20191017PWA_01 | Infrastructure (network-based) | -37.6992 | 144.5429 | 1 | Powercor | Report | 18101 | 0.0050104 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew carried out repairs | Westwood Drive, Burnside Heights VIC 3023 | 30279810 | Vandalism;Copper theft | [6 empty] | Police reported that a security guard reported multiple street light not working , pit covers missing with stolen earth and exposed wiring, poles located on westwood drive, near intersection of tenterfield drive. On arrival crew found Pit lids missing, vandalism and lengths of copper service wire stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | SA007 | Vandalism and copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43475.2403 |  |  | 14390 | Roadway |  | 20191018PWA_02 | Infrastructure (network-based) | -37.7385 | 144.7484 | 1 | Powercor | Report | 18109 | 0.014995 | Low voltage AC (<1kV) | Melbourne Airport | 3023 | Burnside Heights | Other
The crews have disconnected removed and made safe the existing overhead neutral screen service. The crews have completed the new overhead service connection and installed a new 1 phase electricity meter as the condition and status of the existing removed 1 phase meter was unknown. | 214 ORIEL ROAD, HEIDELBERG WEST VIC 3081 | A107758 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address today for a 9.30am Truck Appointment for a 1 phase overhead supply and metering alteration. When the crews arrived they found the existing 1 phase service fuse had been removed with the existing 1 phase neutral screen service still connected. The existing consumer mains, switchboard and installation wiring had all been removed. New installation wiring had been installed and completed and a Certificate of Electrical Safety (COES) issued. The electricity meter had been disconnected and removed and was sitting inside the new switchboard metering enclosure. Application details, COES, EWR and photos are all attached in the "Notes & Findings" section | Neutral screen;Smart meter;Switchboard;Customer wiring | 0 | 0 | 0 |  | NH05 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/10/2019 10:57 |  |  | 14394 | Residential |  | 20191021JEM_01 | Infrastructure (network-based) | -37.7414 | 145.041 | 1 | Jemena | Report | 18114 | 0.038774 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg West | Other
On arrival crew isolated pole and carried out repairs | Storers Rd, Tyrrell Downs VIC 3533, Australia | 32159175 | Crane, excavator or other construction/farming equipment | [6 empty] | Report received from a landowner of a pole down and line in contact with tractor. On arrival crew found a SWER pole had been knocked over by tractor engaged in farm operations. The SWER line was entangled with the tractor cab. There was no fire, although there was scorch marks on the tyres. The operator reported tingles in the legs and appeared to be suffering from shock, he was encouraged by bystanders to attend local hospital for a prudent medical check. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SHL002 | Tractor struck pole | Medical attention (first aid/doctor/hospital);Damage to network assets | 19/10/2019 5:45 |  |  | 14392 | Agricultural |  | 20191021PWA_02 | Infrastructure (network-based) | -35.2959 | 142.9033 | 1 | Powercor | Report | 18113 | 0.026396 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3533 | Tyrrell Downs | Vehicle
Fault crews attended the site and found the underground cable was dug up by an excavator (damage to outer sheath only). Fault crews isolated the area and inspected the damaged cable. ESV was notified of the incident, #12654343. The cable was repaired and returned to service. | 47 TALBOT CRESCENT, KOOYONG VIC 3144 | 9687628 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | UE received a call that construction workers have dug up a live HV underground cable. No sparks, shocks or flames were reported. | Cable | 0 | 0 | 0 |  | K7 | Damage to the cable was caused by the excavator. A Permit To Work was on issue and current at the time of the incident. | No Go Zone (contact) | 21/10/2019 17:30 |  |  | 14402 | Other | rail corridor | 20191022UTD_01 | Infrastructure (network-based) | -37.8414 | 145.0362 | 1 | United Energy Distribution | Report | 18129 | 0.031705 | 11kV AC | Moorabbin Airport | 3144 | Kooyong | Dug up
Electricity and gas isolated. Gas pipe removed and LV cable repaired | 4 Lewalan St, Grovedale VIC 3216, Australia | 30257658 | Working too close to underground cables | [6 empty] | Following a report of a gas leak, it was discovered that at some time in the past a gas directional bore had broken the LV underground conduit and damaged the cable insulation. The gas installation is believed to occurred over 12 months ago. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | WPD012 | Directional bore for gas installation | No Go Zone (contact);Damage to network assets | 43534.6028 |  |  | 14411 | Roadway |  | 20191023PWA_04 | Infrastructure (network-based) | -38.1985 | 144.345 | 1 | Powercor | Report | 18145 | 0.027694 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Grovedale | Dug up
Supply isolated repairs arranged | 193-295 Brooklyn Rd, Brookfield VIC 3338, Australia | 30293002 | Copper theft | [6 empty] | A passerby called to report wires exposed at the corner of Brooklyn Rd/Botanical Springs Blvd. Upon arrival the fault crew found that thieves had first cut the pit connector at the base of LIS-787601 thinking that it would be supplying the rest of the lights heading east along Brooklyn Rd, however that light is supplied from another direction. The thieves left the P/L cable cut and exposed at this location but stole no cable here. The thieves then proceeded east to the following pole at LIS-787602 where the fault crew also found live/exposed cables. Between LIS-787602 east up to LIS-787610, the thieves removed approx. 335m of 4/c 16mm P/L service cable. All pits between LIS-787602 and LIS-787610 were left open with only the pit connectors to be found inside the pits. All P/L cable between these poles was removed. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43626.8153 |  |  | 14413 | Roadway |  | 20191023PWA_06 | Infrastructure (network-based) | -37.6991 | 144.5424 | 1 | Powercor | Report | 18147 | 0.03267 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
ATTEND SITE, MADE SAFE, REPLACED folcb. | 104 INGLES ROAD, DEVON NORTH VIC 3971 | LIS2624667 |  | Animal | [5 empty] | Report of pole mounted fuse mains box fire and subsequent ground fire | Connection box | 0 | 0 | 0 |  | FTR12 | FOLCB burnt due to wildlife shorting to ground . | Pole-top fire;Grassfire | 23/10/2019 0:59 | 1 | Localised: less than 10 sq.m | 14415 |  |  | 20191024SPN_01 | Infrastructure (network-based) | -38.5335 | 146.59 | 1 | AusNet Services Distribution | Report | 18151 | 0.037314 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3971 | Devon North | Fuse
directly to the service fuse on the meter panel bypassing the meter for this phase only. Wiring has been rectified and meter panel replaced on site by the REC and a prescribed COES issued on site and supply restored . Crews remained on site for an extended period of time so rectification works could be completed and supply restored as the site is registered as Life Support. Two appointments will be charged instead of one due to the extended time spent on site assisting REC address the issues. | 14 BRIDLINGTON DRIVE, GREENVALE VIC 3059 | A060512 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended a 8am truck appointment this morning where the REC was replacing a deteriorated chipboard meter panel that had been issued with a level 2 defect with a new fire rated compliant panel. Whilst on site the crews identified a meter bypass where the white phase load side tail was removed from the meter and connected Photos and COES attached in the "Notes & Findings" section | Smart meter | 0 | 0 | 0 |  | COO21 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/10/2019 8:00 |  |  | 14418 | Residential |  | 20191025JEM_01 | Infrastructure (network-based) | -37.6383 | 144.8951 | 1 | Jemena | Report | 18155 | 0.0094618 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
Crew attended and ensured that there was no issues, and listed the site for a FFU to replace the stretched cable. | 55 Welwyn Parade, Deer Park VIC 3023, Australia | 32177667 | Vandalism;Copper theft | [6 empty] | An REC called to report a possible theft, on arrival the crew found that an unknown person had damaged a new pole to pit LV UG cable in an attempted theft. The crew stated that someone had attempted to pull the UG cable out of the conduits from the pit end, but the attempt had failed and the perpetrator had given up and must have left empty handed. The UG cable was not yet connected to supply. There was no fire or reported injuries | Services cable | 2 | 2 | 2 |  | SU021 | Attempted copper theft | Damage to network assets | 43687.434 |  |  | 14429 | Roadway |  | 20191029PWA_02 | Infrastructure (network-based) | -37.7605 | 144.7719 | 1 | Powercor | Report | 18172 | 0.034603 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Other
Fault crew dispatched. Candled HV fuse removed and replaced with new | ENVYDALE, 96 HIBBERSON ROAD, HUON VIC 3695 | LIS5217174 |  |  |  | Candled fuse |  |  |  | Report of candled HV Fuse | Boric acid | 0 | 0 | 0 |  | WOTS13 | Candled 6k BA HV Fuse | Pole-top fire | 27/10/2019 17:00 | 1 | Negligible: no ground fire | 14431 |  |  | 20191029SPN_02 | Infrastructure (network-based) | -36.2657 | 147.1002 | 2 | AusNet Services Distribution | Report | 18175 | 0.0092488 | 22kV AC | Wangaratta Aero | 3695 | Huon | Fuse
The crew isolated the HV cable and left the kiosk substation out of service due to unsafe installation. A defect notice was issued to the customer. | Western Ring Rd, Laverton North VIC 3026, Australia | 41067460 | Vandalism;Copper theft | [6 empty] | A Powercor employee reported that while driving on the Western ring road, he noticed that the doors of the Kiosk substation â€˜WESTERN RING-GEELONG HWYâ€™ were opened. On inspection of the kiosk, he found that a HV fuse had blown out and one of the HV cables had been attempted to cut into with a grinder, just below the red phase elbow. The Kiosk substation is a radial fed and supplies a Telstra tower. The crew found that there were significant damage to the Telstra installations at the site and copper cables had been stolen from the customer assets. There was no fire or reported injuries. | Pad mounted equipment/kiosk;Other customer electrical equipment | 2 | 2 | 2 |  | BLT021 | Copper theft and vandalism | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43748.6417 |  |  | 14439 | Public space |  | 20191030PWA_02 | Infrastructure (network-based) | -37.8268 | 144.8134 | 1 | Powercor | Report | 18185 | 0.0098125 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3026 | Laverton North | Other
Supply isolated, service replaced. Customer issued with a defect to repair POA. | 24 CREEK STREET, MELTON SOUTH VIC 3338 | 30110649 | Working too close to overhead lines | [6 empty] | A contractor reported an excavator hit a service wire at the incident location. Upon arrival, a Powercor crew found that the service had been brought down by the excavator. The POA had also been damaged. There was no fire or reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | MLN011 | Excavator struck service line. | Loss of supply;No Go Zone (contact) | 43748.5694 |  |  | 14440 | Residential |  | 20191030PWA_03 | Infrastructure (network-based) | -37.7046 | 144.5784 | 1 | Powercor | Report | 18186 | 9.6065e-05 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Vehicle
Faults crew attended and repaired the white phase LV conductor prior to replacing the 250amp white and blue phase DIN fuses at the east circuit of "Morey-Glamis" substation. First thing the following day, an urgent toolbox alert was outworked to all crews prior to commencing shift. An investigation commenced and a copy of the incident investigation, along with findings is to be provided to PAL CP UE Head of Vegetation Hugh Vickers Willis. The Asplundh General Manger created the following recommendations for action items as a result of this incident are as per below: â€¢ Urgent Toolbox Alert relating to this incident outworked to all crews (Completed on day of incident prior to next shift) â€¢ Employees involved stood down immediately pending investigation (Completed on day of incident) â€¢ Drug & Alcohol test on both individuals (Completed with negative on all test- no drug or alcohol present) â€¢ Follow up toolbox alert relating to the findings of this incident to all crews â€¢ Removal of authorisation for EWP Operations for Joaquin Ferrari & Mohammed Nordin effective immediately on the Powercor Citipower & United Energy networks â€¢ Removal of authorisation for EWP Operations for Joaquin Ferrari & Mohammed Nordin effective immediately on all Asplundh contracts â€¢ Joaquin Ferrari & Mohammed Nordin to remain authorised on the Powercor Citipower & United Energy and Asplundh contracts in the roles of Notification/ Inspection or Chipper operation â€¢ Asplundh National Safety & Compliance Manager to undertake a review of the systems utilised to assess the workers involved in the incident and determine reason they were not effective in preventing this incident (based on individuals being involved in an incident prior) â€¢ Subcontractor Enviro Trees provided a formal written notice relating to unsatisfactory safety performance â€¢ Revaluation of all Enviro Trees employees with Field Competency Assessments undertaken by Carl Van Helsdingen, Asplundh Operations Manager- United Energy (jointly with a nominated representative from PAL CP UE) to ensure the actions/findings resulting in this incident are isolated to the crew involved and not systemic of the subcontractor â€¢ Asplundh to under random Job Behavioural Observations on crews across the United Energy & Powercor networks on a nominated date (jointly with a nominated representative from PAL CP UE), to ensure the actions/findings resulting in this incident are isolated to the crew involved and not systemic of the subcontractor â€¢ All Asplundh employees and subcontractor employees to undertake Asplundh Tap Into Safety scenario based hazard and risk training prior to 31st December 2019. | 3 VARDON AVENUE, BEAUMARIS VIC 3193 | 1820791 |  | Within clearances |  |  | Followed but inappropriate |  | 1 | A vegetation management crew (Enviro Tree Management) was clearing trees from overhead electric lines for United Energy and clashed conductors with a telescopic saw whilst maneuvering the EWP. The crew immediately ceased work and contacted the United Energy faults and emergencies call centre. No injuries were reported and 27 customers were affected by the outage. | Conductor (bare) | 0 | 0 | 0 |  | BR06 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 31/10/2019 11:31 |  |  | 14442 | Roadway |  | 20191031UTD_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | United Energy Distribution | Report | 18680 | 0.035652 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Beaumaris | Other
Pole replaced | Unnamed Road, Telopea Downs VIC 3420, Australia | 30087080 |  |  |  | Leakage |  |  |  | Pole replaced due to pole fire. no ground fire reported. | Pole (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 43655.6264 | 1 | Negligible: no ground fire | 14444 | Agricultural |  | 20191101PWA_02 | Infrastructure (network-based) | -35.9039 | 141.1475 | 1 | Powercor | Report | 18197 | 0.021045 | 12.7kV AC (SWER) | Horsham Aerodrome | 3420 | Telopea Downs | Pole
crew attended, isolated and repaired cable | 99 KENNEWELL STREET, WHITE HILLS VIC 3550 | 30546912 | Working too close to underground cables | [5 empty] | 1 | Report of Third party bored into HV U/G cable at incident location. Crew found civil contractor working putting in a water main, bored into HV cable. | Cable | 0 | 0 | 0 |  | EHK033 | working close to HV cable | Loss of supply;Damage to network assets | 31/10/2019 9:32 |  |  | 14449 | Roadway |  | 20191104PWA_03 | Infrastructure (network-based) | -36.7177 | 144.3073 | 1 | Powercor | Report | 18207 | 0.033042 | 22kV AC | Bendigo Airport | 3550 | White Hills | Dug up
The crew made the site safe and removed the 2C twisted grey service cable and issued the customer a defect. | 91 GREVILLEA CRESCENT, HOPPERS CROSSING VIC 3029 | 33073674 |  |  |  | Overheated connection |  |  | 1 | VIC Fire reported Service wire sparking and melted , started grass fire. Upon arrival the PCA Faults Crew have found that the POA/FOLCB at House No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029 has overheated, failed and melted and burnt away. The resultant hot melted plastic from the POA above has fallen onto the ground below causing a small grass fire of approximately 3m x4m, within the front yard of No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029 The MFB attended site and the grass fire was extinguished. | Service cable (insulated);Customer wiring | 0 | 0 | 0 |  | LV009 | connection malfunction at point of supply | Loss of supply;Grassfire | 43476.0861 | 1 | Small: 10 - 1000 sq.m | 14451 | Residential |  | 20191104PWA_05 | Infrastructure (customer connection) | -37.8586 | 144.7149 | 1 | Powercor | Report | 18211 | 0.036326 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Installation
crew attended, isolated and completed repairs | 31 WOOLTON AVENUE, THORNBURY VIC 3071 | 30184890 |  |  |  | Overheated connection |  |  | 1 | Resident reported a flash of electricity that was seen & heard shooting down to footpath on the pole located on the Cnr Spencer Street & Woolton Avenue, Thornbury . Attending crew found connection had parted from gas switch. | Conductor (covered uninsulated) | 0 | 0 | 0 |  | NC013 | connection failure at gas switch | Pole-top fire | 18/10/2019 15:45 | 1 | Negligible: no ground fire | 14457 |  |  | 20191106PWA_01 | Infrastructure (network-based) | -37.7611 | 144.9967 | 1 | CitiPower | Report | 18218 | 0.020439 | 11kV AC | Essendon Airport | 3071 | Thornbury | Connection
crew attended and undertook repairs | 3 HOLBORN PATH, WYNDHAM VALE VIC 3024 | 30554674 | Working too close to underground cables | [5 empty] | 2 | Contractor reported that an excavator belonging to Casabene Plumbing (Site contact - 0431008964) has dug up an underground cable. Orange hazard tape has been removed, conduit casing has been cracked and black cable has been exposed. On arrival the crew found that an excavator had dug up a low voltage underground service causing a small crack on the conduit. The LV service cable was exposed but there was no damage done to the cable. | Services cable | 0 | 0 | 0 |  | WBE014 | works in vicinity of cables | Damage to network assets | 43779.5507 |  |  | 14461 | Roadway |  | 20191106PWA_02 | Infrastructure (network-based) | -37.8459 | 144.593 | 1 | Powercor | Report | 18225 | 0.018046 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Dug up
LEI and Fault crew disptached. LEI identified this property and the neighbouring property (#165), which are both supplied from same pit, measured 89V to independant earth. LEI isolated supplies to both properties. New cable installed from pole to pit, all tests carried out and passed following repairs. | 163 MILAWA-BOBINAWARRAH ROAD, MILAWA VIC 3678 | LIS5100263 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [6 empty] | Customer reports receiving electric shock when touching switchboard | Cable | 0 | 0 | 0 |  | WN5 | Underground supply cable to pit failed and lost the nuetral conductor to the supply pit. Customer reported receiving electric shock. REC attended property and observed equipment was not operating correctly. REC turned off supply and, with Main Neutral lifted from bar, measured 89V to ind earth. Fault crew identified the cable supplying the pit from the adjacent pole had been badly damaged (presumibly by an excavator when recent sewer works were carried out) and had been left in the ground and on supply with a failed neutral conductor. | Minor shock | 43507.4187 |  |  | 14458 |  |  | 20191106SPN_01 | Infrastructure (network-based) | -36.4473 | 146.4316 | 1 | AusNet Services Distribution | Report | 18477 | 0.0081644 | Low voltage AC (<1kV) | Wangaratta Aero | 3678 | Milawa | Dug up
Fault crews were dispatch to the site. Upon inspection, it was confirmed that the HV cross-arm was burnt. Emergency switching was undertaken to isolate the section of the fault. The cross-arm was replaced under access authority conditions. | 255 STATION STREET, EDITHVALE VIC 3196 | 3303709 |  |  |  | Leakage |  |  | 1 | UE received a call advising of a broken HV cross-arm. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | CRM35 | The cause is likely to be due to HV insulator tracking across the HV cross-arm. | Pole-top fire | 43626.8507 | 1 | Negligible: no ground fire | 14459 | Roadway |  | 20191106UTD_01 | Infrastructure (network-based) | -38.0427 | 145.1114 | 1 | United Energy Distribution | Report | 18224 | 0.0070231 | 22kV AC | Moorabbin Airport | 3196 | Edithvale | Crossarm
Fault crew dispatched. | 145 BOUNDARY ROAD, WOLLERT VIC 3750 | LIS599306 |  |  |  |  | Followed but inappropriate |  |  | Emergency services report pole top fire. BA HV fuse tube had burnt in half. No photos of the incident avilalble. | Boric acid | 0 | 0 | 0 |  | EPG13 | Most probable cuase is incorrect installation. No photos or failed equipment was available for detailed investigations to confirm the root cause. | Pole-top fire | 43566.8625 | 1 | Negligible: no ground fire | 14467 |  |  | 20191107SPN_02 | Infrastructure (network-based) | -37.5925 | 145.0153 | 2 | AusNet Services Distribution | Report | 18883 | 0.028201 | 22kV AC | Essendon Airport | 3750 | Wollert | Pole
The crew disconnected and removed service wire at the pole end (LIS number 24407) and issued a defect noticed to customer. | 48 KINGS ROAD, ST ALBANS, 3021 | 30111899 | Working too close to overhead lines | [6 empty] | caller reported and excavator has clipped an overhead service and it has snapped On arrival the crew found that an excavator had made contact with the overhead service wire, causing it to break about 2mtrs out from the POA and damaged the customerâ€™s fuse box. The service was live on the ground. The excavator was trenching for renovation work on this property. | Service cable (insulated) | 0 | 0 | 0 |  | SSE031 | The excavator was working close to service while trenching for renovation work on this property. | Damage to network assets | 14/10/2019 15:34 |  |  | 14469 | Residential |  | 20191108PWA_01 | Infrastructure (network-based) | -37.7374 | 144.7804 | 1 | Powercor | Report | 18236 | 0.028519 | Low voltage AC (<1kV) | Melbourne Airport | 3021 |  | Vehicle
crew made safe by isolating the HV and LV supply | 145 WOLLAHRA RISE, WYNDHAM VALE VIC 3024 | 32162956 | Copper theft | [6 empty] | Crew responding to power issues/outages in the area found unknown persons have stolen the HV & LV earths from top to bottom at the pole, and also stolen approx. 70m of 16mm underground service cable between the pole sub and pit located down the road on the other side of the pole . | Services cable | 0 | 0 | 0 |  | WBE014 | copper theft | Loss of supply;Damage to network assets | 19/10/2019 8:13 |  |  | 14476 | Residential |  | 20191108PWA_08 | Infrastructure (network-based) | -37.8687 | 144.6267 | 1 | Powercor | Report | 18243 | 0.017686 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
Fault crew along with civil crew dug up and repaired damaged section of LV underground service cable and put back into service. | 25 DOOLAN STREET, WERRIBEE VIC 3030 | 30103120 | Working too close to underground cables | [5 empty] | 1 | Report received advising that a street light underground cable had been hit by a contractor undertaking telecommunications work in the nature strip. Upon arrival the fault crew found that a contractor has struck and broken both the conduit and 16mm 2/c service within it, which in turn has interrupted supply to the property. | Services cable | 0 | 0 | 0 |  | WBE024 | Telecommunications cabling undertaken near cables | Loss of supply;No Go Zone (contact) | 18/10/2019 15:01 |  |  | 14478 | Roadway |  | 20191111PWA_01 | Infrastructure (network-based) | -37.911 | 144.6535 | 1 | Powercor | Report | 18245 | 0.038476 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
Candled HV fuse removed and replaced with new. Supply restored | 161 SMITHS BEACH ROAD, SMITHS BEACH VIC 3922 | LIS2808411 |  |  |  | Candled fuse |  |  |  | Candled BA HV Fuse | Boric acid | 0 | 0 | 0 |  | PHI12 | Candled HV BA Fuse on spur tee-off. No evidence of ground fire. | Pole-top fire | 43780.4451 | 1 | Negligible: no ground fire | 14483 |  |  | 20191111SPN_02 | Infrastructure (network-based) | -38.4977 | 145.2575 | 1 | AusNet Services Distribution | Report | 18251 | 0.014172 | 22kV AC | Moorabbin Airport | 3922 | Smiths Beach | Fuse
Fault crew dispatched. O/H line de-energised, pole straightened and existing stay repaired with new makeoff | BERGAMIN PASTORAL, 3240 OLD SALE ROAD, TRAFALGAR VIC 3824 | LIS2202004 |  |  |  | Corrosion |  |  |  | Customer reported low conductors and dead cows | Conductor (bare);Guy wire | 0 | 0 | 0 |  | MOE22 | Pole stay failed above ground at the make off due to corrosion causing pole to lean resulting in low conductors in paddock. Cows electrocuted when they contacted the low conductors. Following repairs conductor ground clearance is approx. 6.95 metres at its lowest point. No evidence of ground fire | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Fatality of livestock, pet or companion animal | 26/10/2019 23:05 |  |  | 14484 |  |  | 20191112SPN_01 | Infrastructure (network-based) | -38.0937 | 146.1393 | 1 | AusNet Services Distribution | Report | 18253 | 0.02067 | 22kV AC | Morwell (Latrobe Valley Airport) | 3240 | Trafalgar | Pole
Made safe, removed bird off ACR Follow up to repair damaged leads initiated | 5651 WESTERN HIGHWAY, GERANG GERUNG VIC 3418 | 30546090 |  | Bird |  |  |  |  | 2 | Emergency services reported a crow on transformer causing sparks and small grass fire. Crew removed bird off ACR P205 Gerang. | ACR/OCR | 0 | 0 | 0 |  | NHL015 | Bird Incident | Grassfire | 43810.3035 | 1 | Small: 10 - 1000 sq.m | 14489 | Roadway |  | 20191113PWA_02 | Infrastructure (network-based) | -36.3715 | 141.8602 | 1 | Powercor | Report | 18268 | 0.0079549 | 22kV AC | Horsham Aerodrome | 3418 | Gerang Gerung | Animal
repairs made | 147 GREYTHORN ROAD, BALWYN NORTH VIC 3104 | 30189323 | Working too close to overhead lines | [5 empty] | 1 | A garbage truck hit a tree branch at the incident location and the tree branch flicked a conductor of LV circuit. Upon arrival, a CitiPower crew found that the conductor had been damaged and the repairs arranged. The council attended the tree clearing works. | Conductor (bare) | 0 | 0 | 0 |  | WD013 | rubbish truck operating near OH lines | Loss of supply;Damage to network assets | 30/10/2019 12:24 |  |  | 14493 | Roadway |  | 20191113PWA_04 | Infrastructure (network-based) | -37.8029 | 145.0974 | 1 | CitiPower | Report | 18263 | 0.0075706 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Vehicle
Fault crews and EIO attended the site to investigate. EIO measured 7V between neutral and independent earth, and the same value was measured on the gas pipe. Upon inspection, fault crews found loose connections at the pole end of the service cable and reterminated the connections. NST passed and supply was left on. | UNIT 1 32 FAIRWAY STREET, FRANKSTON VIC 3199 | 3307925 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE received a call from customer that a plumber received a shock from a gas pipe under the house whilst repairing a leak. | Service cable (insulated) | 0 | 0 | 0 |  |  | The cause was loose connections at the pole end of the service cable. | Minor shock | 43657.3299 |  |  | 14494 | Residential |  | 20191113UTD_02 | Infrastructure (network-based) | -38.136 | 145.1334 | 1 | United Energy Distribution | Report | 18264 | 0.026931 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Stopped work, Joint accessed and new cover fitted. works completed | 38 Aylesbury Drive Altona | 30238815 |  |  |  | Defective component |  |  | 1 | Flash over occurred between neutral and blue phase whilst completing live low voltage mains tee joint. Whilst tightening connector on blue phase with insulated tool, head of tool made contact between neutral and blue phase. It was found that the insulated cover fitted to the neutral had a small nick which allowed the flash to occur. | Cable | 0 | 0 | 0 |  | BLT022 | Flash over between neutral and blue phase due to small nick in covering on neutral | Loss of supply | 16/08/2019 15:25 |  |  | 14501 | Roadway |  | 20191118PWA_01 | Infrastructure (network-based) | -37.8536 | 144.8257 | 1 | Powercor | Report | 18272 | 0.020758 | Low voltage AC (<1kV) | Laverton Raaf |  |  | AF Other
crew attended and made safe | Bulmans Road Western freeway overpass. Melton West 3777 | 30298012 | Copper theft | [5 empty] | 2 | Powercor received a report of Underground wires exposed, 5 pit lids removed along the highway.. attending crew found supplies to 7 lighting poles had been stolen from both sides of freeway | Services cable;Services pit (network);Pole (steel) | 0 | 0 | 0 |  | MLN022 | copper theft | Loss of supply;Damage to network assets | 21/10/2019 10:00 |  |  | 14507 | Roadway |  | 20191121PWA_02 | Infrastructure (network-based) | -37.6862 | 144.5495 | 1 | Powercor | Report | 18285 | 0.033053 | Low voltage AC (<1kV) | Laverton Raaf | 3777 |  | Other
Repairs arranged | 1233 TIMBOON-CURDIEVALE ROAD, CURDIEVALE VIC 3268 | 31033493 | Working too close to overhead lines | [5 empty] | 2 | A customer reported that a service was pulled down by a truck at the incident location. Upon arrival, a Powercor crew found that the service had been pulled down by an unknown truck. The truck details are not available | Service cable (insulated) | 0 | 0 | 0 |  | TRG005 | service appears to have beet hit by unknown truck | Damage to network assets | 22/10/2019 8:25 |  |  | 14509 | Roadway |  | 20191121PWA_04 | Infrastructure (network-based) | -38.5124 | 142.88 | 1 | Powercor | Report | 18287 | 0.029425 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Curdievale | Vehicle
site made safe repairs carried out | 379 Barrakee-Buckrabanyule Rd, Buckrabanyule VIC 3525, Australia | 32027791 |  |  |  | Overheated connection |  |  |  | A crew attended a fault on a SWER ACR BORUNG P81, no cause for the outage was located. The crew departed to site , but a short time later a grass fire was observed emanating from near the incident location. CFA extinguished fire, police attended There was a ground fire of around 16.5 hectares, There was no injuries and potentially fencing and pasture burnt (unconfirmed) | Pole mounted | 2 | 2 | 2 |  | CTN001 | Lv leads on substation overheated | Grassfire | 21/11/2019 8:56 | 1 | Large: more than 10 ha | 14517 |  |  | 20191122PWA_01 | Infrastructure (network-based) | -36.2636 | 143.4952 | 1 | Powercor | Notification | 18298 | 0.032344 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3525 | Buckrabanyule | AF Other
no further work undertaken, integrity of substation earths checked and backfilled | Lot 5 COASTAL BOULEVARD, OCEAN GROVE VIC 3226 | 41115708 | Unauthorised access | [5 empty] | 2 | Bank of large conduits has installed conduits into "Live" kiosk. No permit to work on issue | Pad mounted equipment/kiosk | 0 | 0 | 0 |  | DDL024 | un-authorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/11/2019 11:30 |  |  | 14533 | Commercial |  | 20191125PWA_03 | Infrastructure (network-based) | -38.2478 | 144.5404 | 1 | Powercor | Report | 18325 | 0.015646 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3226 | Ocean Grove | Other
Made safe fixed and restored. | 17 BADEN DRIVE, HEATHCOTE JUNCTION VIC 3758 | LIS912182 |  | Blown branch/vegetation | [5 empty] | Report of tree contacting and bringing down O/H HV conductors | Conductor (bare) | 0 | 0 | 0 |  | KLO14 | Semi-mature swamp gum trunk failure (stem failure) in extreme winds making contact with conductors bringing one phase to ground. No obvious defects were identifiable so failure could not have been predicted. | Grassfire | 21/11/2019 15:00 | 1 | Small: 10 - 1000 sq.m | 14527 |  |  | 20191125SPN_02 | Infrastructure (network-based) | -37.3686 | 145.0395 | 1 | AusNet Services Distribution | Report | 18315 | 0.04044 | 22kV AC | Wallan (Kilmore Gap) | 3758 | Heathcote Junction | Trees
Fault Truck isolated HV Cable and supply restored to rest of High Voltage feeder. HV cable was uncovered, repaired, tested and placed back into service. | 54 INDUSTRIAL PARK DRIVE, LILYDALE VIC 3140 | Beresford Ind Pk 3 (Indoor S/Stn) | Working too close to underground cables | [6 empty] | Report of civil contractor damaging HV U/G Cable: contractor was boring and installing private conduit in a private road when the borer damaged the HV Conduit. Works were almost completed and borer came into contact with High Voltage. This caused the protection to operate and resulted in feeder outage. Refer to the photo of the site. | Cable | 0 | 0 | 0 |  | LDL22 | Failure to identify U/G HV cable by third party | No Go Zone (contact) | 23/11/2019 14:36 |  |  | 14529 | Industrial |  | 20191125SPN_04 | Infrastructure (network-based) | -37.748 | 145.3514 | 2 | AusNet Services Distribution | Report | 18319 | 0.0057546 | 22kV AC | Moorabbin Airport | 3140 | Lilydale | Dug up
ON arrival crew isolated supply and replaced service | 11 ELIZABETH STREET, SPRING GULLY VIC 3550 | 32054109 |  |  |  | Mechanical breakdown |  |  |  | Report received from customer of service wire on ground and small patch of burnt grass in front yard. Service is still attached at pole end and draped across roadway. There was no injuries or third party property damage. | Service cable (insulated) | 2 | 2 | 2 |  | BET007 | Insulation breakdown | Grassfire | 25/11/2019 19:06 | 1 | Localised: less than 10 sq.m | 14535 | Residential |  | 20191126PWA_01 | Infrastructure (customer connection) | -36.7862 | 144.2909 | 1 | Powercor | Report | 18327 | 0.033429 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Spring Gully | OH Cable
Branch removed supply restored | 515 Springvale Rd, Girgarre East VIC 3616, Australia | 33097486 |  | Blown branch/vegetation |  |  |  |  | 2 | Vicfire called in event at the incident location advising that there had been a fire possibly causing damage to a PCA asset. On arrival the crew found a small branch entangled in the ACR structure. The ACR had tripped, but the branch was on the supply side and still buzzing There was a small fire started. There was no injuries and minor damage to fence posts. | ACR/OCR | 2 | 2 | 2 |  | SHP014 | Vegetation: Trees Incident | Grassfire | 25/11/2019 17:52 | 1 | Small: 10 - 1000 sq.m | 14536 | Roadway |  | 20191126PWA_02 | Infrastructure (network-based) | -36.4302 | 145.1138 | 1 | Powercor | Report | 18329 | 0.037758 | 22kV AC | Shepparton Airport | 3616 | Girgarre East | Trees
Service isolated. REC engaged to repair Point of attachment damage | 79 ELIZABETH STREET, CASTLEMAINE VIC 3450 | 32043190 | Vehicle | [6 empty] | NAO advised by dispatch that a service wire had been pulled from a fascia. Earlier an earth moving company (not known) was completing works in the vicinity and was passing through when one of their vehicles managed to pull the service from the fascia There was no fire, no reported injuries | Service cable (insulated) | 2 | 2 | 2 |  | CMN002 | unknown vehicle struck service | Damage to network assets | 22/10/2019 19:21 |  |  | 14539 | Residential |  | 20191126PWA_04 | Infrastructure (customer connection) | -37.0693 | 144.1983 | 1 | Powercor | Report | 18333 | 0.015898 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Vehicle
The testers in the room immediately mobilised a fire extinguisher and isolated the 415VAC supply from the distribution board on the other side of the room. By isolating the 415VAC supply the fire stopped and the fire extinguisher was not used. The manufacturer of the equipment (Swedish Neutral) has been contacted and engaged to assist with the investigation and the equipment panel has been made availabe to Swedish Neutral to confirm there are no other issues and confirm there is no secondary damage caused by the fault. No human or procedural factors were identified and Swedish Neutral believe this is nothing more than a component failure and have confirmed they are comfortable for all other units to go into service. All existing and new REFCL inverter breaking resistors are to be inspected and electrically tested prior to energisation. No REFCL is to be placed into service until tests are carried out and the results provided to and cleared by the REFCL commissioning engineer | 339 WHITTLESEA-KINGLAKE ROAD, KINGLAKE CENTRAL VIC 3757 |  |  |  |  | Defective component;Unknown technical factor |  |  |  | E0018514 - Fire in REFCL inverter cabinet. During Primary Fault Throw (PFT) testing this morning a loud bang was heard followed by a fire in the top section of the GFN inverter cabinet, in the REFCL room at Kinglake (KLK) zone substation. | REFCL inverter cabinet;Other | 0 | 0 | 0 |  | KLK | Red Phase calibration was carried out with no issues. White phase calibration was then carried out and completed successfully, however a loud bang was heard at its conclusion. Sparks and burning was observed on the top part of the inverter. Upon investigation, the top right hand side fan compartment was on fire and the braking resistor within it badly burnt. The breaking resistors are used to absorb excess energy produced by the inverter during REFCL calibration operation. In this case, a faulty breaking resistor failed and caught fire due to the excessive heat that was generarted as a result of breaking the resistor loop. The breaking resistor was destroyed by the incident. No injuries to personnel were sustained. Following the incident, the inverter was isolated, the covers removed and the unit inspected. It was noted that some molten metal may have dripped through the inverter cabinet and, due to possible contamination from molten metal, the entire inverter cabinet was replaced. The manufacturer of the equipment (Swedish Neutral) has been contacted and engaged to assist with the investigation and the equipment panel has been made availabe to Swedish Neutral to confirm there are no other issues and confirm there is no secondary damage caused by the fault. No human or procedural factors were identified and Swedish Neutral believe this is nothing more than a component failure and have confirmed they are comfortable for all other units to go into service. | Other electricity related | 43589.4583 | 1 | Negligible: no ground fire | 13489 |  |  | 20190410SPN_01 | Infrastructure (network-based) | -37.5144 | 145.3164 | 1 | AusNet Services Distribution | Report | 16726 | 0.006147 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3757 | Kinglake Central | AF Other
HV10 wooden crossarm replaced | 91-119 CRAIG STREET, SPOTSWOOD VIC 3015 | pole no. A059706 |  | Humidity |  | Leakage |  |  | 1 | Pole top fire on a HV switch. Photos have been attached in the "Notes & Findings" section | Pole top | 0 | 0 | 0 |  | NT16 | Electrical leakage | Pole-top fire | 43742.5444 | 1 | Negligible: no ground fire | 13495 | Roadway |  | 20190411JEM_01 | Infrastructure (network-based) | -37.8354 | 144.8865 | 1 | Jemena | Report | 16734 | 0.034462 | 22kV AC | Essendon Airport | 3015 | Spotswood | Crossarm
The attending Jemena fault crew replaced the Clamp on the Overhead Service Neutral Conductor termination at the reticulation pole and completed an NST test which indicated a Pass result. The attending LEI conducted final voltage tests between an independent earth to plumbing fixtures where the electric shock occurred, neutral bar at main switchboard, which confirmed 0.4 Volts AC. A final NST test was completed which confirmed a Pass result. The installation was left ON Supply. | 32 GLENARD DRIVE, EAGLEMONT VIC 3084 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | Customer received an electric shock when she made simultaneous contact between her hands on the Shower Taps and her bare feet while standing on the shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the taps and the distribution assets, identified a defective Clamp on the O/H Service Neutral Conductor termination at the reticulation pole. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipe. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of 20 volts on the water piping system. TechSafe report is attached in the "Notes & Findings" section. | Service conductor;Copper | 0 | 0 | 0 |  |  | A defective Clamp on the Overhead Service Neutral Conductor termination at the reticulation pole. | Minor shock | 43803.6201 |  |  | 13503 | Residential |  | 20190412JEM_01 | Infrastructure (network-based) | -37.7636 | 145.0694 | 1 | Jemena | Report | 16992 | 0.030294 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Eaglemont | Connection
Repairs arranged | 59-65 BUCKHURST STREET, SOUTH MELBOURNE VIC 3025 | 30167753 | Copper theft | [5 empty] | 2 | A person reported a break in and cable theft at the incident location. On arrival the crew found that approx. 14-15m of 70mm bare copper had been removed from various earthing points throughout the substation enclosure. No live cables appeared to have been touched. The thieves had gained access via a door adjacent to a building site. The theft was reported to the police. There were no reported injuries or other damage. | Earth/earthing | 2 | 2 | 2 |  | E021 | Copper theft | Damage to network assets | 19/03/2019 9:56 |  |  | 13508 | Industrial |  | 20190415PWA_04 | Infrastructure (network-based) | -37.8304 | 144.9514 | 1 | CitiPower | Report | 17011 | 0.040422 | Earthing cable | Essendon Airport | 3025 | South Melbourne | Other
Crew made safe isolating customer supply in pit, to allow REC to carry out repairs. | 54 LANGDON STREET, PORTARLINGTON VIC 3223 | 33046342 | Working too close to underground cables | [6 empty] | Customer reported their Builder escavated and hit underground cables from pit to meter, REC needs supply disconnected to commence repairs. No injuries, no ground fire. | Customer installation | 2 | 2 | 2 |  | DDL021 | builder excavation on private property damaged customers underground mains | Loss of supply | 20/03/2019 11:38 |  |  | 13509 | Residential |  | 20190415PWA_05 | Infrastructure (network-based) | -38.1198 | 144.6526 | 1 | Powercor | Report | 16985 | 0.033241 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Portarlington | Dug up
On arrival crew isolated supply and carried out repairs. | 148 SALTWATER PROMENADE, POINT COOK VIC 3030 | 30304886 | Vandalism;Copper theft | [6 empty] | Adam from Electrics was out fixing street light faults and reported some cables in service pits at base of Street lights had been cut and/or pulled out by unknown person/s. There was no fire, no reported injuries or third property damage. | Services cable;Services pit | 2 | 2 | 2 |  | LV004 | copper theft and vandalism | Damage to network assets | 21/03/2019 10:16 |  |  | 13517 | Roadway |  | 20190416PWA_03 | Infrastructure (network-based) | -37.9114 | 144.7652 | 1 | Powercor | Report | 16983 | 0.0099225 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew carried out repairs | 74 SHUTER AVENUE, GREENDALE VIC 3341 | 30115520 | Copper theft | [6 empty] | Crew found earth cut away from substation about 2/3 meters removed.. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BMH003 | Copper theft | Damage to network assets | 22/03/2019 0:30 |  |  | 13521 | Roadway |  | 20190416PWA_04 | Infrastructure (network-based) | -37.563 | 144.3154 | 1 | Powercor | Report | 16982 | 0.01172 | Earthing cable | Avalon Airport | 3341 | Greendale | Other
Fire authority attended and put out fire. Fault crew attended and replaced 1m section of conductor under access authority conditions. | 316 WORSLEY ROAD, BANGHOLME VIC 3175 | 206801 |  |  |  | Corrosion;Mechanical breakdown |  |  | 1 | During strong winds, a HV tie failed resulting in the HV conductor falling to the ground and starting a small grass fire. An upstream HV fuse operated to isolate supply. | Conductor (bare);Copper;Insulator tie wires/connections | 0 | 0 | 0 |  | DVY24 | HV tie wire failure was the cause of the conductor dropping to the ground. | Grassfire | 25/03/2019 16:13 | 1 | Localised: less than 10 sq.m | 13516 | Roadway |  | 20190416UTD_01 | Infrastructure (network-based) | -38.0603 | 145.1829 | 1 | United Energy Distribution | Report | 18386 | 0.022867 | 22kV AC | Moorabbin Airport | 3175 | Bangholme | Connection
Emergency high voltage switching was completed to restore supply to customers while maintaining safety isolation at the fault site. The cross arm was replaced under Access Authority conditions. | 12 DENDY STREET, BRIGHTON VIC 3186 | 1804866 |  | Precipitation;Prone to salt deposition |  | Leakage |  |  | 1 | At 7:40am on 30/3/2019, an ACR of feeder NB35 Reclosed and tripped to lockout. The patrol found the HV intermediate cross-arm on the T-off pole on the corner of Dendy St and Ramsay Street had burnt off at the strap. | Crossarm (wood) | 0 | 0 | 0 |  | NB35 | Electrical tracking occurred as a result of rain after a long period of dry weather. The cross-arm eventually broke and allowed =the conductors to clash triggering the protection to operate. | Pole-top fire;Loss of supply | 30/03/2019 7:40 | 1 | Negligible: no ground fire | 13525 | Roadway |  | 20190416UTD_05 | Infrastructure (network-based) | -37.9192 | 144.9906 | 1 | United Energy Distribution | Report | 17036 | 0.0074502 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Crossarm
The CFA attended the site and extinguished the fire. UE Fault crews attended and inspected the pole for damage. NO damage was sustained. | 241 ARTHURS SEAT ROAD, RED HILL VIC 3937 | 9863702 |  | Animal |  |  |  |  | 1 | At 3:30 am on 3/4/2019, feeder CB reclosed an held. Subsequently, a call was received from the CFA advising of a fire around UE pole in Red Hill. Inspection of the site revealed a fire start due to a possum contact on the pole structure. | Conductor (ABC);Conductor (bare) | 0 | 0 | 0 |  | DMA15 | Animal Incident | Grassfire | 43528.1458 | 1 | Small: 10 - 1000 sq.m | 13527 | Roadway |  | 20190416UTD_06 | Infrastructure (network-based) | -38.37 | 145.0071 | 2 | United Energy Distribution | Report | 17034 | 0.03674 | 22kV AC | Moorabbin Airport | 3937 | Red Hill | Animal
Site was made safe by Jemena Work Party and referred to depot to conduct repairs | 250 RACECOURSE ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | TE#179581 - Report from customer advising pit lids in street lifted and exposed underground cables. | Services cable;Copper | 0 | 0 | 0 |  | SBY13 | Copper theft of street light cable at two locations in Racecourse Rd corner of Elizabeth drive, Sunbury | Damage to network assets | 17/04/2019 16:12 |  |  | 13538 | Peri-urban |  | 20190417JEM_01 | Infrastructure (network-based) | -37.5565 | 144.7345 | 1 | Jemena | Report | 16790 | 0.032845 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Fault Crew re-terminated neutral conductor of the ABC O/H Service Cable at the Reticulation Pole | 3 STURT STREET, KYNETON VIC 3444 | 32044939 |  |  |  | Neutral fault;Mechanical vibration |  |  | 2 | person was in the Bathroom showering when she received an electric shock as she made simultaneous contact with her hand on the metal Shower Rose and her bare feet while standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  | WND014 | High impedance neutral - loose ABC O/H Service Neutral Conductor termination located at the Reticulation Pole. | Minor shock | 13/03/2019 6:00 |  |  | 13542 | Residential |  | 20190418PWA_04 | Infrastructure (network-based) | -37.2465 | 144.4597 | 1 | Powercor | Report | 16991 | 0.010564 | Low voltage AC (<1kV) | Bendigo Airport | 3444 | Kyneton | Connection
LEI confirmed HVI at 5 properties. Service cable disconnected to 1375 Bunyip-River Rd, requires REC to repair damaged POA & switchboard. LV circuit isolated, repaired and supply restored. Reinstalled LV conductor and measured 7 & 8 m over driveways with lowest height measured at 5.5m mid span. | 1375 BUNYIP RIVER ROAD, IONA VIC 3815 | LIS511829 & LIS511831 | Vehicle |  |  |  |  | Phase to earth | 1 | E0018894 - Truck contacted O/H HV and LV conductors resulting in HV injection and LV conductor on ground | Conductor (bare) | 0 | 0 | 0 |  | WGL12 | Truck contacted HV and LV conductors resulting in HVI. Fault crew confirmed no damage to HV conductors but LV was down between LIS511829 and LIS511831. ACR BW1656 tripped to lockout. LEI confirmed HVI at 5 properties. Service cable disconnected to 1375 Bunyip-River Rd, requires REC to repair damaged POA & switchboard. LV circuit isolated, repaired and supply restored. Reinstalled LV conductor and measured 7 & 8 m over driveways with lowest height measured at 5.5m mid span. | HV injection;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/04/2019 12:09 |  |  | 13544 | Roadway |  | 20190418SPN_01 | Infrastructure (network-based) | -38.1235 | 145.7013 | 1 | AusNet Services Distribution | Report | 16798 | 0.00030208 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3815 | Iona | Vehicle
Fault crew dispatched. Fire was already out upon arrival. Blown fuse replaced and supply restored. No failed/damaged assets, no repairs required. Follow up visit organised to fit appropriate animal proofing to s/stn | 55 QUARRY ROAD, YALLOURN NORTH VIC 3825 | LIS2216241 |  | Bird | [5 empty] | E0018955 - report of birds nest on transformer bushing caught fire resulting in small ground fire (1mx1m) | Pole mounted | 0 | 0 | 0 |  | MOE14 | Bird Incident | Pole-top fire;Grassfire | 20/04/2019 17:03 | 1 | Localised: less than 10 sq.m | 13561 |  |  | 20190422SPN_05 | Infrastructure (network-based) | -38.1566 | 146.3846 | 2 | AusNet Services Distribution | Report | 16925 | 0.036064 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Yallourn North | Animal
Fault crew dispatched and supply isolated. No damage to AusNet assets. Customer issued with defect for REC to replace box. Fault crew installed new LV wiring from Tx to new FOLCB. New mains box installed and new mains run for cust. | 390 MCDOWELL ROAD, WOOLAMAI VIC 3995 | LIS2800401 |  |  |  | Defective component;Fault on customer installation |  |  |  | E0018953 - customer owned pole mounted junction box fire | Connection box;Customer installation | 0 | 0 | 0 |  | WGI34 | Customer owned fuse mains box has caught fire and melted. Customer mains were connected directly to this junction box installed 4m up pole LIS2800401 which also served as customer's POS. No evidence of ground fire. Failure believed to be from loose connection. | Pole-top fire | 20/04/2019 9:34 | 0 | Negligible: no ground fire | 13562 | Agricultural |  | 20190422SPN_06 | Infrastructure (network-based) | -38.5021 | 145.5408 | 1 | AusNet Services Distribution | Report | 17051 | 0.017819 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | Woolamai | Connection
Fault crew dispatched and 6k BA HV fuse replaced with new | 470 WARNEET ROAD, WARNEET VIC 3980 | LIS517465; WARNEET P88 |  |  |  | Candled fuse |  |  |  | E0019046 - Report of Candled HV 6k BA fuse | Boric acid | 0 | 0 | 0 |  | CRE33 | Candled 6k Boric Acid HV fuse | Pole-top fire | 24/04/2019 12:00 | 1 | Negligible: no ground fire | 13586 | Roadway |  | 20190426SPN_01 | Infrastructure (network-based) | -38.2204 | 145.3158 | 2 | AusNet Services Distribution | Report | 17079 | 0.013981 | 22kV AC | Moorabbin Airport | 3980 | Warneet | Fuse
Isolated HV conductor and repaired line | 2 ALDINGA DRIVE, BUNBARTHA VIC 3634 | 33097110 |  | Fallen |  |  |  |  | 0 | Customer advised that tree fell across bare overhead mains and reported smoking from wire/tree. Attending crew found A tree had fallen directly across all three phases and tree had caught fire. There were small fires where the conductors had been brought to ground. | Conductor (bare) | 0 | 0 | 0 |  | SHN011 | Vegetation: Trees Incident | Loss of supply;Grassfire | 26/04/2019 14:46 | 1 | Localised: less than 10 sq.m | 13592 | Roadway |  | 20190429PWA_03 | Infrastructure (network-based) | -36.2574 | 145.351 | 1 | Powercor | Report | 16859 | 0.0052326 | 22kV AC | Shepparton Airport | 3634 | Bunbartha | Trees
Crew replaced the existing corroded O/H Service Cable | 43 RICHARDSON STREET, NATHALIA VIC 3638 | 32184971 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal Tap and her bare feet while standing on the wet tiled shower base. | Service conductor | 0 | 0 | 0 |  | NKA002 | Corroded Overhead Service Neutral Conductor - in span | Minor shock | 43773.4583 |  |  | 13598 | Residential |  | 20190429PWA_04 | Infrastructure (customer connection) | -36.0551 | 145.2025 | 1 | Powercor | Report | 16940 | 0.013712 | Low voltage AC (<1kV) | Shepparton Airport | 3638 | Nathalia | OH Cable
Crew re-terminated the existing O/H Service Cable at the Customerâ€™s FOLCB | 54 SIMONS ROAD, LEOPOLD VIC 3224 | 31012125 |  |  |  | Corrosion |  |  | 2 | person was showering when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet while standing on the wet shower base. | Aluminium twisted (grey) | 0 | 0 | 0 |  | DDL014 | Corroded O/H Service Neutral Conductor termination at the Customerâ€™s FOLCB | Minor shock | 25/03/2019 5:30 |  |  | 13599 | Residential |  | 20190429PWA_05 | Infrastructure (customer connection) | -38.1855 | 144.4704 | 1 | Powercor | Report | 16975 | 0.025637 | Low voltage AC (<1kV) | Avalon Airport | 3224 | Leopold | Connection
police notified cable replaced | 227 FEATHERBROOK DRIVE, POINT COOK VIC 3030 | 30304596 | Copper theft | [5 empty] | 2 | NBNCo reported a supply outage, attending crew found 160M of underground cable to the pit had been stolen | Services cable | 0 | 0 | 0 |  | WBE034 | copper theft | Loss of supply;Damage to network assets | 43559.6944 |  |  | 13603 | Roadway |  | 20190430PWA_03 | Infrastructure (network-based) | -37.9067 | 144.7151 | 1 | Powercor | Report | 16946 | 0.036094 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew isolated supply and carried out repairs. | 303-329 SINCLAIRS ROAD, DEANSIDE VIC 3336 | 30110259 | Copper theft | [6 empty] | Customer reported someone has cut the wire that comes down the pole to feed the pit. REC Jim can see a grinder has gone right through it, possible copper thief. no supply. Upon arrival the PCA Field Crew have advised that an unknown person has removed/pulled the LV fuses from the FOLCB and proceeded to cut into/cut through the 40mm white conduit and 16mm 4/c lv service cable on the pole - this was evident by the grinder marks on the pole and through the conduit and cable, as a result of the cut through the 16mm 4/c lv service cable this has come down slightly into the conduit on the pole.. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 43559.3125 |  |  | 13631 | Roadway |  | 20190506PWA_02 | Infrastructure (network-based) | -37.7411 | 144.7064 | 1 | Powercor | Report | 16912 | 0.0014294 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Other
Crew attended and replaced FSD | 27-29 WELSFORD STREET, SHEPPARTON VIC 3630 | 30259528 |  |  |  | Overheated connection |  |  | 2 | Powercor crew responding to a fault found a LV Fused Gang Operated Fused dis-connector switch [FSD] had burnt out | Any other type | 0 | 0 | 0 |  | SHN023 | overheated connection in FSD | Pole-top fire | 15/04/2019 15:59 | 1 | Negligible: no ground fire | 13632 | Roadway |  | 20190506PWA_03 | Infrastructure (network-based) | -36.3752 | 145.3992 | 1 | Powercor | Report | 16913 | 0.0089618 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Connection
line isolated for fire supression, assets inspected. | 3 MAJORS LINE ROAD, TOOBORAC VIC 3522 | 33032221 | Vehicle | [5 empty] | 2 | External fire caused by traffic event and required plant to push trees in vicinity of line. Vicfire requested PAL attendance to inspect assets due to fire caused by vehicle accident on the Northern Hwy at the intersection of Majors Rd, Tooborac. Fault crew requested line be de-energised as a 30 tonne excavator was pushing burning trees over in the vicinity of 22kV conductors when they arrived. Poles inspected with one wood pole found to have some superficial charring at its base, pole 556A Heathcote. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | BGO023 | Traffic event resulting in external fire | Loss of supply | 18/04/2019 19:50 |  |  | 13633 | Roadway |  | 20190506PWA_04 | Infrastructure (network-based) | -37.0314 | 144.7947 | 1 | Powercor | Report | 16937 | 0.036302 | 22kV AC | Wallan (Kilmore Gap) | 3522 | Tooborac | Vehicle
LEI and fault crew dispatched. Customer mains were disconnected in pit and underground cable was reconfigured to allow customer back on supply until Ausnet replace/fix underground cable. Following rectification and repair works NST and all tests carried out and passed | 155 MILDRENS ROAD, BARNAWARTHA VIC 3688 | LIS5210068 |  |  |  | Defective component |  | Phase to earth |  | E0019259 - Customer was using taps in Kitchen and received a shock from the tap. He then went out to his meter box and received a shock from the metal frame. | Services cable | 0 | 0 | 0 |  | BWA23 | Underground service cable had sustained damage, Red phase to earth and neutral. Red fuse at FOLCB was sparking when removed and red hot despite no load. | Minor shock | 43621.1458 |  |  | 13630 | Residential |  | 20190506SPN_01 | Infrastructure (network-based) | -36.0453 | 146.7119 | 2 | AusNet Services Distribution | Report | 16911 | 0.034787 | Low voltage AC (<1kV) | Wangaratta Aero | 3688 | Barnawartha | UG Cable
Fault crew attended and disconnected the service and issued defect to No 41 Orange St for damage to POA. Details obtained of the concrete pump that caused the damage. | 39 ORANGE STREET, BENTLEIGH EAST VIC 3165 | 2326593 | Working too close to overhead lines | [5 empty] | 1 | A concrete pump truck working in property 39 Orange St Bentleigh hit and damaged the aerial service line going to No 41 Orange St. | Service conductor | 0 | 0 | 0 |  |  | The cause was the works occurring on the property at No. 39 Orange St where a concrete pump truck was working. There was no NGZ request made prior to this incident. | Loss of supply;Damage to network assets | 18/04/2019 15:08 |  |  | 13628 | Construction |  | 20190506UTD_01 | Infrastructure (network-based) | -37.9174 | 145.0781 | 1 | United Energy Distribution | Report | 16908 | 0.040434 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Vehicle
Crew capped cable and made safe | 26 LANDSCAPE PLACE, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Stolen underground cable | Cable | 2 | 2 | 2 |  | SBY13 | Unknown person has stolen underground mains to be numbers 26 & 28 Landscape Place | Damage to network assets | 43651.3319 |  |  | 13638 | Residential |  | 20190507JEM_01 | Infrastructure (network-based) | -37.5529 | 144.7074 | 1 | Jemena | Report | 16919 | 0.017167 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
CFA extinguished fire and assets checked | 690 CRAVEN ROAD, TATURA VIC 3616 | 30133198 |  | Prone to dust deposition |  | Leakage |  |  |  | Vic Fire report a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase intermediate pole had ignited. | Pole (wood) | 0 | 0 | 0 |  | MNA034 | excessive leakage current | Pole-top fire | 21/04/2019 18:31 | 1 | Negligible: no ground fire | 13642 | Agricultural |  | 20190507PWA_03 | Infrastructure (network-based) | -36.4669 | 145.2778 | 1 | Powercor | Report | 16965 | 0.033574 | 22kV AC | Shepparton Airport | 3616 | Tatura | Pole
On arrival crew isolated supply and arranged repairs. | 548 LEAKES ROAD, TRUGANINA VIC 3029 | 30331244 | Working too close to underground cables | [5 empty] | 1 | A contractor dug up a 22kV UG cable at the incident location. The protection operated. Upon arrival, a fault crew found that the UG cable had been damaged by a excavato. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | LV002 | Use of excavator near underground cable | Damage to network assets | 43560.4229 |  |  | 13643 | Roadway |  | 20190507PWA_04 | Infrastructure (network-based) | -37.8358 | 144.7093 | 1 | Powercor | Report | 16978 | 0.0035579 | 22kV AC | Laverton Raaf | 3029 | Truganina | Dug up
The UE representative stopped and spoke to the site manager who responded that he was unsure how the signage was installed. The site manager was informed that the signage was installed in breach of the No Go Zone and that this would be escalated to the regulator. | 93 WARRIGAL ROAD, HUGHESDALE VIC 3166 |  | Working too close to overhead lines | [5 empty] | 2 | At a construction site on Warrigal Rd Hughsedale where a No Go Zone permit was on issue, it was noted that the developer has installed advertising signage on the protective timber hoarding attached to the scaffold that had been erected under shut-down conditions. That is, the signage had been erected after the scaffold, without our knowledge and with the street mains live. | Conductor (bare) | 2 | 2 | 2 |  |  | Signage was installed without No Go Zone procedures being followed. | No Go Zone (no contact) | 43681.4167 |  |  | 13637 | Construction |  | 20190507UTD_01 | Infrastructure (network-based) | -37.9005 | 145.0866 | 2 | United Energy Distribution | Report | 17078 | 0.024483 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3166 | Hughesdale | Other
reported only - pending advice | 182 QUEEN STREET, ALTONA VIC 3018 | 32164239 | Working too close to overhead lines | [5 empty] | 2 | Powercor crew advise that strut has been installed under neighbors service in association with building and scaffolding on adjacent property | Service conductor | 0 | 0 | 0 |  | AL012 | interference | No Go Zone (contact) | 43682.7188 |  |  | 13669 |  |  | 20190513PWA_01 | Infrastructure (network-based) | -37.8704 | 144.8226 | 2 | Powercor | Report | 17067 | 0.030142 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
Fault crews attended and after emergency high voltage switching was completed to minimise the number of customers affected, undertook repairs to the OH lines. Repairs were completed under Access Authority conditions. A LEI was dispatched to the site and undertook investigation to determine any damage to customers appliances and equipment. Faults crew also assisted the LEI to inspect properties in the vicinity. Procedures as indicated in the work instruction for HV injections has been followed. | 3 VALLEY ROAD, FRANKSTON VIC 3199 | 3314971 |  | Blown branch/vegetation |  |  |  |  | 1 | At 2156hrs on 7/05/2019, a 22kV feeder CB reclosed and opened to lockout. During high winds, a branch from a private tree in 3 Valley Rd broke and fell onto the HV conductors in the street and contacted the LV resulting in HV injection into neighbouring properties. | Conductor (bare) | 0 | 0 | 0 |  | FSH34 | Vegetation: Trees Incident | HV injection;Loss of supply | 43651.9139 |  |  | 13685 | Roadway |  | 20190520UTD_02 | Infrastructure (network-based) | -38.1602 | 145.1479 | 1 | United Energy Distribution | Report | 17089 | 0.013858 | 22kV AC | Moorabbin Airport | 3199 | Frankston | Trees
A UE fault crew attended and replaced the damaged aerial service line. | 23 VAUTIER STREET, ELWOOD VIC 3184 | 2308260 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | UE received a report of a "cherry picker" hitting a service line. The line was still attached at the house and disconnected at the pole. | Service conductor | 0 | 0 | 0 |  |  | A third party vegetation contractor undertaking vegetation pruning has hit the aerial service line with their EWP, causing it to break at the pole end. | Loss of supply;Damage to network assets | 43651.5819 |  |  | 13686 | Residential |  | 20190520UTD_03 | Infrastructure (network-based) | -37.8866 | 144.9863 | 1 | United Energy Distribution | Report | 17090 | 0.031641 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | Vehicle
A UE fault crew attended and isolated supply to the damaged UG consumers mains from the service pit. An EIO was also dispatched to investigate the shock. The inspector arrived at the site and noted that the worker who had received the shock had drilled through the customers underground consumers mains at a point within the brick cavity and the mains were also run in such a way that they were not at a minimum depth of 500mm below ground level going into the pit and were only just below the surface of the sidewalk concrete. | 34A NEW STREET, BRIGHTON VIC 3186 |  |  |  |  | Fault on customer installation | Unknown work practice factor | Three phase | 2 | UE received a report from NBN of an underground consumer's mains being hit with a diamond tip core drill. The person undertaking the core drilling works for NBN claims he felt a shock. | Customer installation | 0 | 0 | 0 |  |  | Dinesh Kumar Bhatta was diamond core drilling through the front brick fence at a depth around a few hundred mm. Working from the customers side of the fence drilling towards the street, he drilled through the customers underground conduit and through 3 phase consumers mains (all 3 phases) leaving only the neutral intact. He was wearing some worn material type gloves and rubber sole work boots. | Minor shock | 43804.5681 |  |  | 13687 | Residential |  | 20190520UTD_04 | Infrastructure (network-based) | -37.9285 | 144.9942 | 1 | United Energy Distribution | Report | 17091 | 0.002588 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Dug up
A Fault crew was dispatched to isolate the consumer mains at the service pit. An EIO was also dispatched to investigate the shock. ESV representative Greg Johnson also attended, and spoke by phone with UE's Wayne Kelly regarding the background to this incident. | 43 KESHAVA GROVE, DANDENONG VIC 3175 | [5 empty] | Poor or no communication;Failure to use correct PPE | Phase to earth | 1 | On 13 May, UE received request to isolate supply to an UG consumer mains from the service pit. On attendance, the fault crew were also advised that an REC had received an electric shock when attempting to work on the live consumer mains. | Customer installation | 0 | 0 | 0 |  |  | On 13 March UE received a request from an REC for isolation due to an illegal bypass wiring. UE attended the site and isolated supply at the meter panel by removing the service fuse. On the 13 May, the REC attended the site and attempted to perform repairs to the illegal wiring. However, the illegal wiring was on the consumers mains below the meter enclosure, and therefore upstream of the isolation. The person undertaking the repair work did not confirm the isolation by testing if the consumers mains was live, and has subsequently made contact with live conductor and received a shock. | Minor shock | 13/05/2019 11:00 |  |  | 13688 | Residential |  | 20190520UTD_05 | Infrastructure (network-based) | -38.0006 | 145.1972 | 1 | United Energy Distribution | Report | 17093 | 0.029014 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong | Other
Initial NST carried out and passed. Volts on Tap 3.5V with 28A Tightened loose connections at pole junction box and incoming links at customer meter Corrosion on neutral of customer service fixed. NST carried out following repairs passed 0.5ohm with 0.5V on neutral | 153 BULLUMWAAL ROAD, WY YUNG VIC 3875 | BDL2 |  |  |  | Corrosion;Fault on customer installation |  | Phase to earth |  | E0020127 - Customer was turning on taps in shower when he felt a slight tingle. He stated this has happened on more than one occasion. | Connection box;Customer installation | 0 | 0 | 0 |  | LIS1605281 | Junction box on pole found to have slightly loose connections. Slight corrosion identified on neutral of customer service at mains box and loose connections at meter incoming links identified. | Minor shock | 16/05/2019 17:00 |  |  | 13690 | Residential |  | 20190521SPN_02 | Infrastructure (customer connection) | -37.8046 | 147.6161 | 2 | AusNet Services Distribution | Report | 17095 | 0.0034537 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Wy Yung | Connection
Fault crew dispatched to make safe and carry out repairs. Crew confirmed the Truck driver was ok and uninjured. Fault crew isolated the line and completed repairs, 8m ground clearance confirmed following repairs. Supply restored. | MILLRING, 374 HENDERSONS ROAD, TOONGABBIE VIC 3856 | LIS2603016 | Working too close to overhead lines |  |  |  |  | Phase to earth |  | E0020129 - Customer report truck contacting overhead SWER conductor. | SWER conductor;Pole top | 0 | 0 | 0 |  | TGN31 | Upon arrival, the fault crew found a tip truck with tipper raised and driver still in the vehicle which had made contact with the overhead SWER conductor. Conductor was not damaged but P-Bracket on adjacent pole had been damaged when the truck pulled the conductor. SWER ACR locked out when fault occurred. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 15/05/2019 14:30 |  |  | 13692 |  |  | 20190521SPN_03 | Infrastructure (network-based) | -38.085 | 146.6601 | 1 | AusNet Services Distribution | Report | 17331 | 0.032177 | 12.7kV AC (SWER) | Morwell (Latrobe Valley Airport) | 3856 | Toongabbie | Vehicle
On 3 April 2019, M&S crew re-attended for a re-scheduled 11.00am Truck Appointment for a 1ph OH supply upgrade to 3ph OH supply. Prior to the Truck Appointment, Jemena Network Connections (Jasleen) contacted the M&S supervisor Frank Vecchio with the REC on the other line with Jasleen asking if he could remove the service fuse and the distributors electricity meter. The REC was categorically advised by Jasleen from Network Connections that he is not permitted to interfere with our remove the distributors electricity meter. Upon the crews arrival please see attached photos. The REC has again removed the service fuse, disconnected the existing 1ph mains and removed the distributors electricity meter which was laying on the ground. Zinfra compliance officer spoke to the the REC who showed a complete lack of interest or care and argued that he was given permission by Jemena Network Connections to do what he did which we know he wasnâ€™t. | 66 WALTER STREET, ASCOT VALE VIC 3032 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address today for a single (1hr) 11.00am TA for a 1ph OH supply upgrade to 3ph OH supply. When the crews arrived the REC had already removed the 1ph service fuse, pulled the existing 1ph consumers mains out from the metering position (they remained connected at the 1ph FOLCB), removed the distributors electricity meter which was sitting on the ground and removed the MSB and existing meter panel and installed new 3ph mains, new MSB and metering panel. The crew were unable to complete a new 3ph OH service upgrade due to the existing POA location (which the REC intended on reusing) being located in a non-compliant inaccessible location above a bull nose veranda and the existing 1ph neutral screen OH service connected to a small SEC junction box that also serviced other customers. Whilst the crews were on site, the REC reinstated the existing 1ph mains and the customer was placed back on supply under the existing 1ph supply arrangement. The LEI was on site and a prescribed CES was provided for the new MSB and meter panel and the reinstatement of the existing 1ph mains. The REC has been advised of the compliant POA location requirement and has been advised to contact Network Connections to rebook appointments. The REC has been advised of the time allocated for a single Truck Appointment and any time outside the maximum 1hr will require further appointments. Customer carding is also required for other affected customers when disconnecting the existing 1ph OH NS service. Photos and other relevant documents are attached in the "Notes & Findings" section | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43557.5833 |  |  | 13700 | Residential |  | 20190523JEM_04 | Infrastructure (network-based) | -37.7738 | 144.9066 | 2 | Jemena | Report | 17112 | 0.0072836 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Other
The supply was disconnected and made safe. | 4 BURNS GROVE, KINGSBURY VIC 3083 |  | Unauthorised access | [5 empty] | 2 | Metering & Service crew attended the site for an overhead supply and metering customer upgrade. When the crews arrived they found the REC had removed the service fuse, disconnected the customer mains at the metering position, removed the existing meter panel and meter (which was sitting on the ground with the seals removed, covers open and cables disconnected and removed) and a new meter panel and MSB installed with new consumer mains, 600mm POA raiser bracket and 1ph FOLCB. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/04/2019 13:10 |  |  | 13701 | Residential |  | 20190523JEM_05 | Infrastructure (network-based) | -37.7181 | 145.0323 | 2 | Jemena | Report | 17117 | 0.011241 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Kingsbury | Other
The crew have made the electrical installation safe and were able to assist in removing the connected customer mains from the existing FOLCB. | 10 MENZIES STREET, BRAYBROOK VIC 3019 |  | Unauthorised access | [5 empty] | 2 | Metering and Service crew attended the site for a 1ph supply and metering alteration. When the crews arrived they found: â€¢ The service fuse had been removed with the deteriorated customer mains still connected to the FOLCB but cut away somewhere within the premises. â€¢ The Distributors electricity meter had been disconnected and was sitting in the old metering enclosure. â€¢ A new 1ph FOLCB, customer mains, meter panel and MSB had been installed and a prescribed COES issued. â€¢ The metering position located behind a privately locked security door within the private domestic premises. â€¢ The existing overhead neutral screen service connected to a small SEC junction box on the pole with another service for the neighboring property. | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43681.4535 |  |  | 13702 | Residential |  | 20190523JEM_06 | Infrastructure (network-based) | -37.7821 | 144.8534 | 1 | Jemena | Report | 17116 | 0.017493 | Low voltage AC (<1kV) | Essendon Airport | 3019 | Braybrook | Other
The shared servicing arrangement could not be left in the unsatisfactory and unsafe condition. To make the arrangement safe, the customer at number 8 was required to be disconnected from supply. | 6 CALBOURNE STREET, PRESTON VIC 3072 |  | Unauthorised access | [5 empty] | 2 | The crew attended the site for an overhead service and metering upgrade. When the crew arrived they discovered a non-preferred grey twist overhead service supplying both 6 & 8 Calbourne St. The REC had removed the service fuse for number 6 Calbourne St, cut away the existing customer mains behind the existing meter panel and removed the electricity meter which the crew found lying on the ground. The REC installed new customer mains, meter panel and a new POA/FOLCB in a position that was not suitable. | Aluminium twisted (grey);Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/03/2019 6:47 |  |  | 13703 | Residential |  | 20190523JEM_07 | Infrastructure (network-based) | -37.7493 | 144.9843 | 1 | Jemena | Report | 17115 | 0.020797 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Fault crew dispatched. Candled EDO HV fuse removed and replaced with new. Followup visit scheduled to replace EDO fuse units wit Boric Acid | 146 MCKERNANS ROAD, BALMATTUM VIC 3666 | LIS3901372 |  |  |  | Candled fuse |  |  |  | E0020336 - Candled HV fuse | Any other type | 0 | 0 | 0 |  | BN001 | Burnt fuse tube hung-up during storm event resulting in EDO HV fuse candling. No evidence of ground fire | Pole-top fire | 22/05/2019 18:32 | 1 | Negligible: no ground fire | 13706 |  |  | 20190524SPN_01 | Infrastructure (network-based) | -36.7181 | 145.6501 | 2 | AusNet Services Distribution | Report | 17123 | 0.0060903 | 22kV AC | Shepparton Airport | 3666 | Balmattum | Fuse
Crew isolated supply | 700 SUNBURY ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Street light copper stolen | Cable | 2 | 2 | 2 |  |  | Person unknown stole copper | Damage to network assets | 28/05/2019 7:34 |  |  | 13719 | Roadway |  | 20190528JEM_03 | Infrastructure (network-based) | -37.5959 | 144.7583 | 1 | Jemena | Report | 17136 | 0.040203 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Fire extinguished, no damage to assets | 97 FRANCIS STREET, BELMONT VIC 3216 | 30268132 |  | Animal | [5 empty] | Report received of possum flashover which in turn ignited pole top There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | GLE012 | Animal Incident | Pole-top fire | 15/03/2019 20:18 | 1 | Negligible: no ground fire | 13717 | Roadway |  | 20190528PWA_01 | Infrastructure (network-based) | -38.1809 | 144.348 | 1 | Powercor | Report | 17134 | 0.015281 | 22kV AC | Avalon Airport | 3216 | Belmont | Animal
Crews made site safe and replaced pole A052176, broken LV crossarm (on pole A052169), and service line between poles A052176 and A052169 and restored supply to customers. | 11 PARKER STREET, FOOTSCRAY VIC 3011 | 10565588 | Vehicle | [5 empty] | 2 | Truck contacted service line outside 11 Parker Street, Footscray running between poles A052176 and A052169 as it was travelling West. As result, pole A052176 was snapped and LV crossarm on pole A052169 was broken. The service line fell to ground in a de-energised state. | Service conductor;Copper;Neutral screen | 0 | 0 | 0 |  | FE06 | Truck contacting overhead lines | Loss of supply;Damage to network assets | 30/05/2019 13:00 |  |  | 13739 | Roadway |  | 20190530JEM_01 | Infrastructure (network-based) | -37.8068 | 144.9016 | 1 | Jemena | Report | 17159 | 0.034668 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
On arrival crew isolated supply and carried out repairs. | 1170 SAYERS ROAD, TARNEIT VIC 3029 | 30118784 | Copper theft | [6 empty] | A copper theft was reported at the incident location. The attended crew observed HV & LV earthing of substation pole ( LIS 200738) had been stolen. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | TNA023 | Copper theft | Damage to network assets | 23/04/2019 13:43 |  |  | 13735 | Roadway |  | 20190530PWA_01 | Infrastructure (network-based) | -37.8415 | 144.6269 | 1 | Powercor | Report | 17154 | 0.0049988 | Earthing cable | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply | 37 COSMO ROAD, TRENTHAM VIC 3458 | 30033561 | Unauthorised work;Unauthorised access | [6 empty] | REC reported a stolen meter at the incident location. Upon arrival, the Powercor crew observed a demolished house at the location/property. The crew believed the house had been demolished a long time ago. The meter, meter board was missing and underground service exposed. There was no fire or reported injuries | Services cable;Smart meter;Meter board (including fuses) | 2 | 2 | 2 |  | WND024 | Demolition of structure | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 24/04/2019 13:08 |  |  | 13736 | Residential |  | 20190530PWA_02 | Infrastructure (network-based) | -37.3931 | 144.3203 | 1 | Powercor | Report | 17155 | 0.036242 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3458 | Trentham | Other
Fault Crew replaced the corroded O/H Neutral Screened Service Cable | 82 MACISAAC ROAD, MOOROOPNA VIC 3629 | 30138666 |  |  |  | Corrosion |  |  | 2 | person was opening the Metal Meter Enclosure to check the Main Switchboard when he received an electric shock as she made simultaneous contact between his hand on the metal Meter Enclosure and his feet while standing on the concrete ground | Neutral screen | 0 | 0 | 0 |  | MNA013 | corroded service cable | Minor shock | 15/04/2019 19:00 |  |  | 13737 | Residential |  | 20190530PWA_03 | Infrastructure (customer connection) | -36.379 | 145.342 | 1 | Powercor | Report | 17156 | 0.025083 | Low voltage AC (<1kV) | Shepparton Airport | 3629 | Mooroopna | OH Cable
The crew have disconnected and made safe the unauthorised BTS pole and analogue meter at number 11 Snyder Ct and issued a defect notice on site (Defect notice J24810) | 9 SNYDER COURT, TULLAMARINE VIC 3043 |  | Unauthorised access | [5 empty] | 2 | Crews have attended the above address today at 9 Snyder Ct Tullamarine with a SO for a new connection for a new 3ph UG permanent supply. The neighbouring property at 11 Snyder Ct was carded and notified last week due to the UG pit located on the property boundary between numbers 9 & 11 Snyder Ct only having single port connecters and a 1ph UG supply servicing number 11 Snyder Ct. When the crews attended today they found a builders temporary supply (BTS) pole at number 11 Snyder Ct supplied underground (UG) with a 1ph supply and an old analogue meter (8163645) on the BTS pole and the address on the meter panel labelled as 9 Snyder Ct. Further this this I made contact with Kerrie from CPC who advised that the meter number 8163645 is registered to number 9 Snyder Ct and not number 11 Snyder Ct. Further to this JenViewer shows an existing UG service to number 9 Snyder Ct and no UG service to number 11 Snyder Ct. The crew have disconnected and made safe the unauthorised BTS pole and analogue meter at number 11 Snyder Ct and issued a defect notice on site (Defect notice J24810) Photos, CES, EWR, Defect Notice are attached in the Notes and Findings section Further to the above, the crews are unable to complete a new 3ph UG permanent connection to 9 Snyder Ct. 1. There is still an UG service showing on JenViewer (GIS system) and an analogue meter registered to number 9. 2. The RECâ€™s EWR and CES as well as the SO issued is conflicting as to what is required on site. The installation on site is a BTS pole, The EWR has ticked Temp In Perm Connection with a note â€œBuilders Supply Pole To Serve As Permanent Positionâ€, The CES states â€œBuilders Supply Poleâ€, The SO raised is for Temp In Perm and the customer on site Jim Borle advised he requires a permanent connection not a Builders Supply Pole. | Cable;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43618.4514 |  |  | 13758 | Residential |  | 20190531JEM_08 | Infrastructure (network-based) | -37.7152 | 144.8686 | 1 | Jemena | Report | 17178 | 0.027241 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Other
The crews disconnected and abolished the OH service line and made safe. | 11 FRANK STREET, COBURG VIC 3058 |  | Unauthorised access | [5 empty] | 2 | M&S crews have attended the above address today with a SO for an abolishment of supply and metering. When the crews arrived they found the customer consumers mains wiring had been disconnected and removed and the Distributors electricity meter removed and not on site. Abolishment form and photos attached in the Notes and Findings section | Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43498.5326 |  |  | 13761 | Residential |  | 20190531JEM_11 | Infrastructure (network-based) | -37.7455 | 144.9602 | 1 | Jemena | Report | 17181 | 0.005353 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
Site made safe | 55 ROSELEIGH BOULEVARD, SYDENHAM VIC 3037 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address today with a SO for a new 3ph UG temp/perm supply. Please see attached photos of the temp/perm metering enclosure and pole and electrical installation. The support pole was not suitably installed and secured in the ground and the enclosure and pole was extremely unstable and moving excessively with exposed UG conduits and earthing conductors. Apart from the electrical installation issues, the crew were also unable to energise and meter the installation as they were restricted with access and working space due the concrete slab preparation works. EWR and COES are also attached. | Cable;Earth/earthing | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/02/2019 21:06 |  |  | 13764 | Residential |  | 20190531JEM_14 | Infrastructure (network-based) | -37.7076 | 144.7724 | 1 | Jemena | Report | 17184 | 0.018406 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Sydenham | Other
During the 1hr TA the crews were in constant contact with compliance trying to service the new 3ph supply but could need meet min compliance requirements previously advised to the REC. The REC is going to reinstate the existing 1ph mains and wiring back into the metering location, issue a prescribed COES and raise an AH TA though Network connections for the crew to return to connect and meter the customer under its original supply arrangement | 60 BELLEVUE AVENUE, ROSANNA VIC 3084 |  | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address today for an 11.00am Truck Appointment (TA) for a 1ph-3ph OH supply and metering upgrade. Prior to todayâ€™s TA, Compliance Officer had spoken to the REC on the phone on 2 occasions when the REC had called the compliance line. On the first occasion it was explained to the REC the min boundary crossing requirements, min driveway clearance heights for his and the neighbouring property, max raiser bracket service angle (60 deg open hook, 70 deg closed loop), clearance from other assets (communications cable), the requirement for 2 TAâ€™s if all works could not be completed within a single 1hr TA and not to disconnect and remove distributors metering equipment and assets if re-using the same metering position. On the second occasion the REC called to request a midspan connection from an open wire service on the same side of the road with communication services on a catenary wire directly below the distributors open wire service to which he was explained no we cannot provide you with this type of connection and all the above information from the first telephone call was reiterated to him. On both occasions the REC fully acknowledged that he understood everything the was explained to him and advised that his new 3ph OH supply will comply with the VSIRâ€™s and Jemena policy requirements and he would book 2 TAâ€™s (disconnect & reconnect). When the crews arrived today they found and assessed: 1. Only a single TA had been booked and scheduled for 11.00am 2. The REC had removed the existing 1ph service fuse, removed the existing distributors 1ph meter which was laying on the ground, removed the existing metering panel and wiring and had installed a new metering panel in the existing location along with new 3ph mains to a new POA location and 900mm open hook type raiser bracket. 3. The new 3ph overhead service exceeded the max boundary crossing requirement of 2m down the adjoining neighbouring property. This was measured at approx. 2.4m. Although not a major issue however there is customer vegetation below the OH service line 4. The overhead service clearance was a max 4.2 over the driveway (min 4.6m required) 5. The OH service angle from the raiser bracket POA exceeded the max 60deg for an open hook type and 70deg for closed loop type and was pulling the raiser at an almost 90deg angle. Photos are attached in the Notes and Findings section | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/02/2019 13:10 |  |  | 13766 | Residential |  | 20190531JEM_16 | Infrastructure (network-based) | -37.7387 | 145.0642 | 1 | Jemena | Report | 17186 | 0.025887 | Low voltage AC (<1kV) | Essendon Airport | 3084 | Rosanna | Other
Site made safe | 8 MIKADO STREET, HADFIELD VIC 3046 |  | Unauthorised access | [5 empty] | 2 | M&S crew attended the above address today with a SO for an abolishment of service line and electricity meter 88373 (NMI 6001172485) When the crew arrived they found the site had been completely demolished including the electricity service line and meter. Please see attached Jemena Portal customer abolishment application, SO and photos from when the crew attended. There is a new BTS pole on site awaiting connection (No SO raised for this NC) | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/02/2019 11:18 |  |  | 13767 | Residential |  | 20190531JEM_17 | Infrastructure (network-based) | -37.7054 | 144.94 | 1 | Jemena | Report | 17187 | 0.028965 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
On arrival crew carried out repairs. | 42 LEATHER STREET, BREAKWATER VIC 3219 | 32088640 | Working too close to underground cables | [6 empty] | A contractor reported an earthing dug up at the incident location. The attended crew found that the earthing cable of a switch pole had been excavated and damaged. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | GLE021 | excavator struck earth cable | Damage to network assets | 26/04/2019 14:47 |  |  | 13740 |  |  | 20190531PWA_01 | Infrastructure (network-based) | -38.1861 | 144.3741 | 1 | Powercor | Report | 17160 | 0.0055382 | Earthing cable | Avalon Airport | 3219 | Breakwater | Dug up
On arrival crew isolated supply and carried out repairs. | 68 HESLOP ROAD, BEVERFORD VIC 3590 | 32161041 |  |  |  | Leakage |  |  |  | Customer reported a pole fire at the incident location. On arrival crew reported end burnt of wooden crossarm. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 43470.1875 | 1 | Negligible: no ground fire | 13773 | Roadway |  | 20190603PWA_02 | Infrastructure (network-based) | -35.241 | 143.4719 | 1 | Powercor | Report | 17193 | 0.03912 | 22kV AC | Swan Hill Aerodrome | 3590 | Beverford | Crossarm
On arrival crew isolated supply and carried out repairs. | 436 MYALL STREET, CARDROSS VIC 3496 | 31019592 |  |  |  | Leakage |  |  |  | Vic fire reported a pole fire at the incident location. On arrival the crew found that a pole fire had occurred resulting in the pole being burnt between the HV and LV crossarms. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 43501.0049 | 1 | Negligible: no ground fire | 13774 | Roadway |  | 20190603PWA_03 | Infrastructure (network-based) | -34.3024 | 142.1424 | 1 | Powercor | Report | 17194 | 0.014294 | 22kV AC | Mildura Airport | 3496 | Cardross | Pole
Crew isolated and repaired conductors | EASTERN CREEK ROAD, NEWFIELD VIC 3268 | 30044317 |  | Wind;Fallen;Dead |  |  |  |  | 1 | Powercor became aware that a line protection recloser had operated interrupting supply to some 360 customers . Attending crew found that that a poplar tree had fallen across HV conductors. | Conductor (bare) | 0 | 0 | 0 |  | TRG003 | Vegetation: Trees Incident | Loss of supply | 29/05/2019 6:48 |  |  | 13775 | Roadway |  | 20190603PWA_04 | Infrastructure (network-based) | -38.5811 | 143.0135 | 1 | Powercor | Report | 17197 | 0.039384 | 22kV AC | Warrnambool Airport Ndb | 3268 | Newfield | Trees
On arrival crew isolated supply and made arrangements for repairs. | 10 LEMON ROAD, BALWYN NORTH VIC 3104 | 30189376 | Copper theft | [6 empty] | Customer at 10 Lemon Road Balwyn North advises new pit to be installed. His property is temporarily connected to the overhead. He advises it appears that some one has taken the new cable between the pit and the pole. Crew attended to find copper 4 core stolen between pole and pit. Cable guards damaged during the theft. About 4meters of cable stolen. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | WD013 | Copper theft | Damage to network assets | 43529.2812 |  |  | 13778 | Roadway |  | 20190603PWA_07 | Infrastructure (network-based) | -37.7931 | 145.101 | 1 | CitiPower | Report | 17201 | 0.034449 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
On arrival crew isolated supply and carried out repairs. | DOHERTYS ROAD, TARNEIT VIC 3029 | 30353388 | Vandalism;Copper theft | [6 empty] | A company employee, reported a copper theft at the incident location. Upon arrival, The fault crew that the 180m of 16mm 4C P/L service cable had been stolen. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43682.5597 |  |  | 13781 | Roadway |  | 20190603PWA_10 | Infrastructure (network-based) | -37.8194 | 144.6904 | 1 | Powercor | Report | 17204 | 0.04086 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
On arrival crew isolated supply and commenced repairs. LEI checking for HVI | 430 POPLAR AVENUE, ORRVALE VIC 3631 | 32191135 | Vehicle | [6 empty] | A car driven into a termination substation pole at the incident location. Upon arrival a crew found that the pole on the ground and also damages on the next pole. A inspector was called to assess HVI as there is damaged equipment. There was no fire, no reported injuries. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | STN011 | Car collided with pole | HV injection;Damage to network assets | 43561.5931 |  |  | 13793 | Roadway |  | 20190604PWA_06 | Infrastructure (network-based) | -36.3991 | 145.4579 | 1 | Powercor | Report | 17216 | 0.020947 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3631 | Orrvale | Vehicle
UE dispatched a fault crew and an EIO to investigate. At the time the crew attended, it was daylight and the light was off. The pole was tested and no volts were detected on the pole surface. At the time of the incident, the light was operating. The attending faults crew activated the PE cell at the light fitting, turning the light on. This resulted in the pole becoming live, with volts measured to an independent earth of between 130 to 230V. The fault crew isolated the light pole at the base and removed the light fitting. A subsequent test to independent earth confirmed the pole was no longer live. | 40 WELLS ROAD, SEAFORD VIC 3198 | 8818465 |  |  |  | Defective component |  | Phase to earth | 0 | UE received a report of a traffic control worker receiving a shock from a steel public lighting pole while installing temporary traffic signs. | Public lighting;Pole (steel) | 0 | 0 | 0 |  |  | The fact that this steel public lighting pole was only energised when the lantern was operating shows that the 250W HPS was faulty. The faulty lantern somehow energised the steel pole. UEâ€™s standard construction drawings for public lighting pole shows that the active to the lantern is always fused and the surface of the steel pole is bonded to the neutral. When the pole was energised by the faulty lantern, there should be enough current going through the fuse to cause the fuse to operate. In this incident, the fuse did not operate when the pole was energised so it is suspected that the internal wiring at the base of the public lighting pole was faulty (e.g. broken connection or loose connection). | Minor shock;Medical attention (first aid/doctor/hospital) | 43713.2604 |  |  | 13794 | Roadway |  | 20190604UTD_03 | Infrastructure (network-based) | -38.1187 | 145.1365 | 1 | United Energy Distribution | Report | 17217 | 0.028179 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Connection
On arrival crew isolated supply and carried out repairs. | 5 TYLDEN-WOODEND ROAD, TYLDEN VIC 3444 | 30266574 | Copper theft | [6 empty] | A company employee, reported a copper theft at the incident location. He observed that the P/L UG cables approx. 50 m have been stolen. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WND024 | Copper theft | Damage to network assets | 16/05/2019 14:06 |  |  | 13796 | Roadway |  | 20190605PWA_01 | Infrastructure (network-based) | -37.3262 | 144.4068 | 1 | Powercor | Report | 17362 | 0.0025567 | Low voltage AC (<1kV) | Melbourne Airport | 3444 | Tylden | Other
Supply isolated at three sites. Defect notices issued, site made safe. Restoration of cables to be completed by Vic Rail. | 2 SYDNEY STREET, ALBION VIC 3020 | 30114141 | Copper theft | [6 empty] | V LINE PTY LTD, Michael from MOG reported several pits with pit lids lifted, wires pulled and cut. Possible steal attempt. Crew attended to find pit lids moved and low voltage underground service cable cut and stolen / removed between customers pit and private lighting belonging to Vic rail. Three pits targeted each supplies Vic-rail public lights. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | SSE014 | Copper theft | Damage to network assets | 17/05/2019 12:30 |  |  | 13797 | Public space |  | 20190605PWA_02 | Infrastructure (network-based) | -37.7848 | 144.8221 | 1 | Powercor | Report | 17220 | 0.017692 | Low voltage AC (<1kV) | Laverton Raaf | 3020 | Albion | Other
Fault crew dispatched. Street light had burnt out and was extinguished prior to fault crew arrival. Supply isolated and disconnect at pit. Damaged P/L removed and replaced with new. | 96 KELLETTS ROAD, ROWVILLE VIC 3178 | LIS5806314 |  |  |  | Unknown technical factor |  |  |  | report of street light fire | Public lighting | 0 | 0 | 0 |  | FGY31 | Street light found burnt but fire had been extinguished prior to fault crew arrival. Supply isolated and disconnect at pit and P/L luminaire replaced. No evidence of ground fire. Investigation conducted but inconclusive, suspected internal fault but unable to ascertain exact cause of luminaire failure which lead to fire. | Pole-top fire | 31/05/2019 23:52 | 1 | Negligible: no ground fire | 13811 | Roadway |  | 20190605SPN_01 | Infrastructure (network-based) | -37.9121 | 145.2503 | 1 | AusNet Services Distribution | Report | 17235 | 0.026582 | Low voltage AC (<1kV) | Moorabbin Airport | 3178 | Rowville | AF Other
UE dispatched a fault crew and an EIO to investigate the cause of the shocks. On attendance, the bus shelter had been isolated by the REC and no volts were measured. The EIO conducted an NST test and all other tests with and without load; NST failed with high neutral impedance. The fault crew isolated the consumers mains at the pit and carried out testing, with the UG service supplying the pit also failing the NST test. The issue was referred to the UG section to replace the UG service cable. At the same time, the company managing the bus shelter undertook to install new consumers mains. | 493 WHITEHORSE ROAD, MITCHAM VIC 3132 | 9576011 |  |  |  | Unknown technical factor |  |  | 0 | UE received a report from an REC of unknown members of the public receiving tingles to hands from a bus shelter at 493-511 Whitehorse Rd Mitcham. | Services cable | 0 | 0 | 0 |  |  | A fault in the UG service cable appears to be the cause of the bus shelter becoming live. | Minor shock | 27/05/2019 10:30 |  |  | 13802 | Public space |  | 20190605UTD_02 | Infrastructure (network-based) | -37.8163 | 145.1931 | 1 | United Energy Distribution | Report | 17225 | 0.01744 | Low voltage AC (<1kV) | Moorabbin Airport | 3132 | Mitcham | UG Cable
On arrival crew isolated supply and carried out repairs. | FITZROY GARDENS, 230-298 WELLINGTON PARADE, EAST MELBOURNE VIC 3002 | 30209543 | Working too close to underground cables | [6 empty] | Contractor trenching in the Fitzroy Gardens (installing irrigation system) has inadvertantly dug up low voltage public light cables at two locations. The damage occurred a day prior to CitiPower being notified. CitiPower were advised on the 24/5/2019 at 07:05am. The live low voltage exposed cable was left overnight presenting hazard to the public. There were no reports of injury or fire due to this incident. | Services cable | 2 | 2 | 2 |  | MP001 | Excavation works by trencher | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/05/2019 14:00 |  |  | 13816 | Public space |  | 20190606PWA_03 | Infrastructure (network-based) | -37.8127 | 144.9788 | 1 | CitiPower | Report | 17253 | 0.022727 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Dug up
Jemena Faults were contacted to attend to disconnect supply with trouble order no. 184013 raised | 153 MELBOURNE AVENUE, GLENROY VIC 3046 | A050277 | Unauthorised access | [5 empty] | 2 | Metering and Servicing discovered another unauthorised and illegal overhead Builder's Temporary Supply (BTS) connection this afternoon with an unauthorised analogue legacy meter and distributor's seal from another network. Photos are attached in the "Notes & Findings" section Nearmap Google street view shows an original existing residential dwelling with an overhead service line JenViewer shows an active permanent (Non BTS) overhead service line with an active residential NMI 6001170530 and meter number 0077049 Nearmap Google earth shows the demolition of the existing residential dwelling occurred somewhere between 4.4.2018 and 25.8.2018 and construction at the property commenced somewhere between 24.2.2019 and 19.4.2019 Jemena Portal shows no record of any applications for abolishment of supply and metering for this NMI or address, no record of any applications for an OH BTS supply and there is currently no applications for any new connection requests. | Smart meter | 0 | 0 | 0 |  | PV13 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43504.8868 |  |  | 14179 | Residential |  | 20190820JEM_02 | Infrastructure (network-based) | -37.703 | 144.9205 | 1 | Jemena | Report | 17738 | 0.029094 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Other
Fault Crew replaced the corroded O/H Neutral Screened Service Cable | 19 BATMAN AVENUE, SHEPPARTON VIC 3630 | 32191847 |  |  |  | Corrosion |  | Phase to earth |  | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact with one hand on the Shower Rose and his bare feet whilst standing on the wet shower base and metal waste water outlet. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | SHN021 | Corroded Neutral Screen Conductor mid span of an O/H Aluminium Neutral Screened Service Cable | Minor shock | 43654.4167 |  |  | 14178 | Residential |  | 20190820PWA_02 | Infrastructure (customer connection) | -36.3627 | 145.3886 | 1 | Powercor | Report | 17737 | 0.029627 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | OH Cable
Fault Crew replaced the existing O/H Service Cable | 34 GLENELG STREET, PORTLAND VIC 3305 | 31017685 |  |  |  | Corrosion |  |  |  | person was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Taps and his bare feet whilst standing on the wet shower base and waste water outlet. | Service cable (insulated) | 0 | 0 | 0 |  | PLD004 | Corroded O/H Service Neutral Conductor under the Helical Cable Termination | Minor shock | 30/07/2019 10:00 |  |  | 14182 | Residential |  | 20190820PWA_04 | Infrastructure (customer connection) | -38.3523 | 141.6019 | 1 | Powercor | Report | 17744 | 0.037365 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland | OH Cable
Fault crew dispatched. Failed FOLCB removed and replaced with new. | 2904 GEMBROOK-LAUNCHING PLACE ROAD, GEMBROOK VIC 3783 | LIS416465 |  |  |  | Defective component |  |  |  | Report of LV use box fire | Connection box | 0 | 0 | 0 |  | ofr23 | LV fuse box on pole caught fire. A suspected low voltage loose service cable connection within the fused mains box causing it to fail and ignite as a result. The fire was contained within the box only and there was no damage to pole and no evidence of ground fire. | Pole-top fire | 13/08/2019 11:30 | 1 | Negligible: no ground fire | 14192 | Roadway |  | 20190821SPN_05 | Infrastructure (network-based) | -37.9311 | 145.5571 | 2 | AusNet Services Distribution | Report | 17934 | 0.037969 | Low voltage AC (<1kV) | Moorabbin Airport | 3783 | Gembrook | Connection
UE fault crew attended and replaced the damaged 2 core aerial service line. The height of the service line was confirmed to be complaint to UE standards. | 10 FRENCH AVENUE, EDITHVALE VIC 3196 | 9601412 | Working too close to overhead lines | [5 empty] | 1 | UE received a report of an aerial service line that was hit and damaged by an excavator undertaking excavation works in the property. | Service cable (insulated) | 0 | 0 | 0 |  |  | The cause was the excavator undertaking works within the property in close proximity to the aerial service line. There was no No Go Zone permit on issue for the works. works being undertaken | Loss of supply;Damage to network assets | 43593.4146 |  |  | 14187 | Residential |  | 20190821UTD_01 | Infrastructure (network-based) | -38.0386 | 145.1131 | 1 | United Energy Distribution | Report | 17812 | 0.01603 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Edithvale | Vehicle
Fault crew were dispatched to investigate and made the site safe. Broken LV was identified and replaced. | 26 COOLABAH STREET, MOOROOLBARK VIC 3138 | LIS 1012506 |  |  |  | Defective component |  |  |  | Report of a dog receiving an electric shock. | Crossarm (wood);Pole (concrete) | 0 | 0 | 0 |  | cpk13 | Fault crew attended the site and found the LV crossarm had broken and live LV conductors were contacting the crossarm straps resulting in the concrete pole becoming live. No evidence of fire or any further damage. While the crossarm had broken it remained in position and did not fall to ground or come into contact with any other assets. The pole is in an LBRA area and was last inspected in 2017 when it was assessed and deemed to be fit for service and classified as a P900. The arm was due to be re-assessed in September 2019, the inspection photos had been taken in preparation for the re-assessment of the crossarm but had not yet been assessed prior to this incident occurring. | Minor shock | 18/08/2019 13:44 |  |  | 14200 | Roadway |  | 20190822SPN_01 | Infrastructure (network-based) | -37.7771 | 145.3098 | 1 | AusNet Services Distribution | Report | 17875 | 0.024075 | Low voltage AC (<1kV) | Moorabbin Airport | 3138 | Mooroolbark | Crossarm
The crew have disconnected, removed and made safe the 1 phase overhead service line. The REC will be rectifying and completing the 3 phase arrangement works on site and will be calling Network Connections to arrange an After Hours return visit. | 247 Union Rd, Moonee Ponds VIC 3039, Australia | A129130 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address for a 9.30am Truck Appointment for a 1 phase overhead to 3 phase overhead supply and metering upgrade. When the crews arrived the REC had already removed the existing 1 phase service fuse and disconnected and removed the existing 1 phase distributors electricity meter which was sitting on the ground. The REC had not yet completed all his works and the LEI on site had not yet issued a COES due to some compliance issues. Photos are attached in the "Notes & Findings" section | Smart meter | 0 | 0 | 0 |  | FT26 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/08/2019 10:16 |  |  | 14214 | Residential |  | 20190826JEM_02 | Infrastructure (network-based) | -37.771 | 144.9162 | 1 | Jemena | Report | 18455 | 0.0097986 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Other
On arrival crew isolated supply, confirmed no injuries. Repairs carried out. | 211 Portland-Nelson Rd, Portland VIC 3305, Australia | 30090086 | Working too close to overhead lines | [5 empty] | 1 | Caller reported wires down at property. On arrival crew found a large container forklift had made contact with HV conductors and brought down 2 outside phases of a 3 phase line between KRT-PLD No 2 P574 & P575. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | PLD003 | Raised container fork lift struck overhead line | No Go Zone (contact);Damage to network assets | 24/08/2019 9:30 |  |  | 14210 | Commercial |  | 20190826PWA_01 | Infrastructure (network-based) | -38.3227 | 141.5703 | 1 | Powercor | Report | 17841 | 0.0016713 | 22kV AC | Portland (Cashmore Airport) | 3305 | Portland | Vehicle
On arrival crew isolated supply and carried out repairs | 6 Landale Rd, Toorak VIC 3142, Australia | 30215880 |  | Wind;Alive;Council | [5 empty] | Various residents on the same area reported no power to their homes and wires on ground. On arrival, the crew found one phase of the LV overhead conductor was broken and lying on the ground. There was no ground fire, no third party damaged and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TK009 | Vegetation: Trees Incident | Damage to network assets | 19/08/2019 18:37 |  |  | 14215 | Roadway |  | 20190827PWA_01 | Infrastructure (network-based) | -37.8395 | 145.0057 | 1 | CitiPower | Report | 17846 | 0.034904 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Trees
Crew have disconnected supply to this pit. Area made safe. | 60-62 STRATHTULLOH CIRCUIT, STRATHTULLOH VIC 3338 | 60165269 | Vandalism;Copper theft | [6 empty] | Customer advised UG pit broken into and wires exposed - pulled out 2-3m. Crew advise lid removed from underground pit and attempted theft of copper services. Exposed live wires left lying near the pit. Crew believe thief may have been disturbed which resulted in preventing the theft. Broken snatch rope attached to the service was left behind. There was no fire, no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN012 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/08/2019 13:00 |  |  | 14221 | Roadway |  | 20190828PWA_01 | Infrastructure (customer connection) | -37.7392 | 144.6033 | 1 | Powercor | Report | 17853 | 0.026022 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Strathtulloh | Other
ON arrival crew isolated supply and carried out repairs. | Cemetery Rd, Bridgewater on Loddon VIC 3516, Australia | 30028602 |  |  |  | Unknown technical factor |  |  |  | A pole fire was reported by a customer. On arrival, A Powercor crew found that the LV fuse box on the pole caught fire. There was fallen debris but no ground fire There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BET001 | Insufficient remains to determine cause. | Pole-top fire | 27/08/2019 9:26 | 1 | Negligible: no ground fire | 14224 | Roadway |  | 20190828PWA_03 | Infrastructure (network-based) | -36.6091 | 143.9497 | 1 | Powercor | Report | 17862 | 0.031436 | Low voltage AC (<1kV) | Bendigo Airport | 3516 | Bridgewater On Loddon | Connection
Site made safe and repairs made. No Go Zone Breach investigation conducted by Jemena works practices. | 38 GLENBARRY ROAD, CAMPBELLFIELD VIC 3061 | A097406 | Building too close or within the No Go Zone | [5 empty] | 2 | â€¢ Third party Excavator operator has dug up, pulled and broken the HV earth around the kiosk substation (GLENBARRY 38-ADRIAN) while trying to repair a blocked sewer pipe. â€¢ Plumbing contractor did not have a Permit to Work or Dial Before You Dig plans and were within the No Go Zone, and also took it upon themselves to join the earth together via jumper leads. â€¢ Work has ceased until Zinfra make repairs. â€¢ The sewer repairs were completed prior to Zinfra arriving on site. â€¢ One of the two blockages was due to a Jemena earth rod going through the sewer pipe. | Copper;Pad mounted equipment/kiosk;Earth/earthing | 0 | 0 | 0 |  | BD13 | No Go Zone infringement: Earth broken by third party excavator | No Go Zone (no contact);Damage to network assets | 43505.4583 |  |  | 14235 | Industrial |  | 20190902JEM_01 | Infrastructure (network-based) | -37.6611 | 144.9595 | 1 | Jemena | Report | 18454 | 0.036743 | Earthing cable | Essendon Airport | 3061 | Campbellfield | Dug up
supply isolated and LEI attended | 45 LILLY STREET, CLIFTON HILL VIC 3068 | 30169261 |  |  |  |  | Not followed |  | 2 | Crew repairing insulation on leads to fuse switch disconnect unit on pole identified incorrect polarity on restoration | Services pit (network);Disconnector/isolator | 0 | 0 | 0 |  | F028 | Connection error | Less than $50k damage | 43564.4167 |  |  | 14250 | Residential |  | 20190905PWA_02 | Infrastructure (network-based) | -37.7887 | 144.997 | 1 | CitiPower | Report | 18056 | 0.016053 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Clifton Hill | AF Other
On arrival crew isolated supply and carried out repairs | 29 Trooper Drive, Rockbank VIC 3335, Australia | 60626486 | Working too close to underground cables | [6 empty] | A contractor, Winslow, reported a dug up at the incident location. Upon arrival, a Powercor crew found that the UG service cable and the pit had been damaged. When the crew arrival, no one from the Winslow on the site. No other damages were found. There was no fire, no reported injuries or third party property damage. | Cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | excavation works in new estate | Damage to network assets | 27/08/2019 13:28 |  |  | 14254 | Roadway |  | 20190906PWA_03 | Infrastructure (network-based) | -37.7216 | 144.6737 | 1 | Powercor | Report | 17925 | 0.023852 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Dug up
The faults crew arrived to find the REC had replaced the fused mains junction box. The REC had completed an exchange with the service cable remaining alive and hadn't waited for the faults crew to attend and isolate at the pole end to enable the safe replacement of the FMJB. The faults crew checked the connections for tightness and supply was re-connected after the completion of installation tests. | 79 COLLINS STREET, MENTONE VIC 3194 |  | Unauthorised work | [5 empty] | 2 | REC No. 17957 Justin Stewart contacted the United Energy faults and emergencies call centre requesting that a faults truck attend as he has to replace a defective multi phase fuse mains box and needs to disconnect the customer. | Service cable (insulated) | 0 | 0 | 0 |  |  | The REC had completed unsafe work as the multi phase service conductors remained alive. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 21/08/2019 8:00 |  |  | 14253 | Residential |  | 20190906UTD_01 | Infrastructure (customer connection) | -37.9796 | 145.0621 | 2 | United Energy Distribution | Report | 17922 | 0.014356 | Low voltage AC (<1kV) | Moorabbin Airport | 3194 | Mentone | Other
The Powercor crew made site safe and isolated supply. A FFU was created to repair the damage and install new service cable. | 41-53 Abey Rd, Melton South VIC 3338, Australia | 60347056 | Copper theft | [6 empty] | A Powercor employee, reported Open pits At Abey road, Melton South, suspected copper theft. On arrival the Crew found that about 10 service pits had their concrete lids removed and on some of them there were wires exposed hanging out of the pits. The 4 core service cables were cut and removed from the pits. Approximately 500 meters of cable were stolen or damaged. 8 Public lighting poles had lost supply. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43505.7465 |  |  | 14259 |  |  | 20190909PWA_03 | Infrastructure (network-based) | -37.7056 | 144.5964 | 1 | Powercor | Report | 17931 | 0.013549 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
On arrival crew isolated supply LEI attending. Faults crew and CTA worked to identify a high impedance neutral IPC connection where the neutral of the shared service connected to the ABC street mains at the pole. Testing using an independent earth confirmed about 3 to 4 V on the customers MEN & points of contact. IPC connection was replaced and testing repeated. NST testing passed | 4 PRINCES CLOSE, PRAHRAN VIC 3181 | 30340143 |  |  |  | Corrosion |  | Phase to earth |  | REC reported broken neutral, Customer had a shock off taps, REC claimed 230volts between neutral and earth, 420volts when turned off main switch, Advised not to touch anything. There was no report of fire. | Connector/termination | 2 | 2 | 2 |  | BC007 | IPC at pole that connected service neutral to ABC distribution cable was high impedance | Minor shock | 43747.4306 |  |  | 14265 | Residential |  | 20190911PWA_02 | Infrastructure (customer connection) | -37.8494 | 144.9944 | 1 | CitiPower | Report | 17943 | 0.028405 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Prahran | AF Other
Fault crew and LEI dispatched to make safe and investigate. Pit repaired and supply restored | 39 WOOLAMAI BEACH ROAD, CAPE WOOLAMAI VIC 3925 | LIS2810072 |  |  |  | Defective component |  |  |  | Customer reported smoke from pit and received shock from wire fence | Services pit (network) | 0 | 0 | 0 |  | WGI31 | Customer reported seeing smoke from pit whilst picking up rubbish from ground near the service pit when they felt a small tingle through fingers from wire fence. Failed and burnt out pit connector believed to be the cause of the shock. No evidence of fire | Minor shock | 15/07/2019 10:06 |  |  | 14277 | Roadway |  | 20190916SPN_01 | Infrastructure (customer connection) | -38.525 | 145.3349 | 1 | AusNet Services Distribution | Report | 17956 | 0.024818 | Low voltage AC (<1kV) | Moorabbin Airport | 3925 | Cape Woolamai | Connection
Crew attended substation and secured the doors. Earths replaced the following day. | 445 Dynon Rd, West Melbourne VIC 3003, Australia | CP0002410 | Vandalism;Copper theft | [6 empty] | Call center advised substation not secure. Rear Personal door has been removed/stolen from Substation FEDERAL FELTERS Trans Crew attended substation and report substation has been broken into and copper earths have been removed from the three transformers, three RMUs and from the low voltage board. The substation door has been damaged and presently cannot be closed. There was no fire, no reported injuries or third party property damage. | Indoor | 2 | 2 | 2 |  | DA015 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43625 |  |  | 14278 | Commercial |  | 20190917PWA_01 | Infrastructure (network-based) | -37.8013 | 144.9129 | 1 | CitiPower | Report | 17958 | 0.022903 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
Fault crew dispatched to investigate and make safe. LV supply isolated and failed junction box and P/L replaced. | 3 STRADBROKE CRESCENT, SURF BEACH VIC 3922 | 2809385 |  | Prone to salt deposition |  | Corrosion |  |  |  | Report of pole fire. | Connection box;Public lighting;Pole (concrete) | 0 | 0 | 0 |  | WGI32 | Upon arrival, the fault crew identified the ground at the base of the pole seemed to be smoking and there was a small burn mark on the ground at the base of the pole. The grass around the pole was brown. The ground was smouldering but there was no flame. The concrete pole was live when the fault crew arrived. Further investigation identified that the connections at the street light had burnt and the neutral connection was burnt off in the junction box both as a result of corrosion. It appears the pole had become live as a result of the active conductor supplying the light in the junction box and the light bracket. | Grassfire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/08/2019 15:14 | 1 | Localised: less than 10 sq.m | 14279 | Roadway |  | 20190917SPN_01 | Infrastructure (network-based) | -38.5092 | 145.2923 | 1 | AusNet Services Distribution | Report | 17959 | 0.0086632 | Low voltage AC (<1kV) | Moorabbin Airport | 3922 | Surf Beach | Connection
Fault crew dispatched. Candled EDO fuse removed and replaced with new | 415 TIMBARRA ROAD, BUCHAN VIC 3885 | LIS1904854 |  |  |  | Candled fuse |  |  |  | Report of Candled HV fuse | EDO fuse | 0 | 0 | 0 |  | BDL41 | Candled 5k EDO SWER Fuse | Pole-top fire | 43564.2708 | 1 | Negligible: no ground fire | 14284 |  |  | 20190917SPN_04 | Infrastructure (network-based) | -37.5082 | 148.1365 | 2 | AusNet Services Distribution | Report | 17964 | 0.0056065 | 12.7kV AC (SWER) | Bairnsdale Airport | 3885 | Buchan | Fuse
On arrival crew determined cause, no asset damage found | 2 Bolton Rd, Wyndham Vale VIC 3024, Australia | 30276558 | Vehicle | [5 empty] | 1 | Customer reported Loud zapping from power lines the lines were shaking loud bang and a big puff of smoke and all power went out, there is also now a wire down lots of school kids in area. On arrival crew found that an unknown vehicle/truck had struck telecommunication cables and flicked them into HV conductors. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE014 | Unknown vehicle struck communication cable | Loss of supply;Significant disruption to the community | 18/09/2019 15:26 |  |  | 14305 | Roadway |  | 20190919PWA_01 | Infrastructure (network-based) | -37.8859 | 144.6265 | 1 | Powercor | Report | 17988 | 0.037255 | 22kV AC | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
On arrival crew isolated supply and carried out repairs. | Hazelvale, 503 Drumanure Rd, Invergordon VIC 3636, Australia | 32184425 |  | Alive;MEC;Property owner/customer | [5 empty] | Customer called reporting wire down at back of his property which has caused a fire. On Arrival, crew found a tree had fallen across a slack span of conductor, breaking the wires mid span and bringing them to ground. A small burn section was found under the conductors approx. the size of a "dinner plate". No injury or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | NKA001 | Vegetation: Trees Incident | Grassfire | 21/09/2019 2:15 | 1 | Localised: less than 10 sq.m | 14319 | Agricultural |  | 20190923PWA_02 | Infrastructure (network-based) | -36.1312 | 145.5592 | 1 | Powercor | Report | 18007 | 0.028485 | 22kV AC | Shepparton Airport | 3636 | Invergordon | Trees
A feeder CB operated to clear the fault. Emergency switching was undertaken to isolate the faulty section. The pole and cross-arm were replaced under access authority conditions. | 289 LAWRENCE ROAD, MOUNT WAVERLEY VIC 3149 | 602198 |  | Precipitation;Industrial or urban pollution |  |  |  |  | 1 | A feeder CB tripped and locked out. Patrol of feeder found a broken cross-arm. On close inspection, it was discovered that a pole top fire occurred. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | EB12 | The cause has been attributed to the centre phase insulator tracking in light rain conditions and caused the pole fire. | Pole-top fire | 43747.2326 | 1 | Negligible: no ground fire | 14320 | Roadway |  | 20190923UTD_01 | Infrastructure (network-based) | -37.8801 | 145.1406 | 1 | United Energy Distribution | Report | 18009 | 0.013985 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Pole
On arrival crew carried our repairs. | 211-229 FAULKNERS ROAD, MOUNT COTTRELL VIC 3024 | 33073470 | Copper theft | [6 empty] | A contractor advised that he has found the earth have been stolen from substation at incident location. Crew arrived to find earth has been cut away from transformer pole to ground level. About four meters of copper earth stolen. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | copper theft | Damage to network assets | 16/09/2019 8:30 |  |  | 14323 |  |  | 20190924PWA_03 | Infrastructure (network-based) | -37.7612 | 144.6286 | 1 | Powercor | Report | 18012 | 0.037618 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
Crews attended, isolated supply and performed repairs. | 455 TORQUAY ROAD, ARMSTRONG CREEK VIC 3217 | 30076210 | Working too close to underground cables | [6 empty] | A representative of Winslow Constructions, called Powercor to report that their excavator had hit UG cables at the incident location. On arrival the crew found that the excavator had dug up two UGs that were running together, causing the FOLCB boxes to be dislodged from their mounting positions on the pole. There was no fire, no reported injuries. | Services cable;Connection box | 2 | 2 | 2 |  | WPD024 | Excavation works | No Go Zone (contact);Damage to network assets | 16/09/2019 15:55 |  |  | 14325 | Roadway |  | 20190924PWA_05 | Infrastructure (network-based) | -38.2253 | 144.3369 | 1 | Powercor | Report | 18014 | 0.01803 | Low voltage AC (<1kV) | Avalon Airport | 3217 | Armstrong Creek | Dug up
Site made safe. Jemena Works Practices and ESV advised and are attending. Ambulance attended and assessed parties (driver and passenger) as not requiring treatment. 9 Customers interrupted (for short period), supply has been restored. Repaired LV mains, replaced white phase fuse. Police and WorkCover called but did not attend. | 133-135 COWPER STREET, FOOTSCRAY VIC 3011 | A137150 | Working too close to overhead lines | [5 empty] | 2 | Suez garbage bin pickup truck (IVECO make, registration 1GY3OZ) operated and lifted the bin which came into contact with LV overhead mains, measured at 6.3 metres above ground. Mild electric shock reported when parties (driver and passenger) contacted vehicle on exiting, | Conductor (bare) | 0 | 0 | 0 |  | FE06 | No Go Zone breach | Minor shock;Loss of supply;No Go Zone (contact) | 30/09/2019 12:54 |  |  | 14339 | Roadway |  | 20190930JEM_02 | Infrastructure (network-based) | -37.8072 | 144.9018 | 1 | Jemena | Report | 18445 | 0.011791 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Vehicle
Site made safe and damaged underground cables to be repaired. No.3 transformer was put back into service and all feeders transferred. Jemena Works Practices are investigating the incident. | 395 BUCKLEY STREET, ABERFELDIE VIC 3040 | [5 empty] | Not followed |  | 2 | While carrying out planned upgrade works in Essendon (ES) zone substation, Zinfra engaged a demolition contractor to demolish redundant No.2 transformer concrete cubicle and footings While attempting to remove redundant concrete footings using a ripping hook, the excavator damaged the outer sheathing and earth screen of two live 11kV underground cables of No.1 transformer No.1 transformer was supplying all ES customers (16,889) and fortunately, no customers were lost supply as a result of this incident. Investigation report is being finalised by Jemena Works Practices and will be made available. For more information, please contact Brian Polifrone (Work Practices, Standards & Quality Manager) on 0408579385 | Cable;Zone substation | 0 | 0 | 0 |  |  | Mobile plant excavating in the vicinity of live 11kV cables without adequate supervision and appropriate risk mitigation controls resulted in damage to two live 11kV transformer cables | Damage to network assets | 43475.6118 |  |  | 14349 | Industrial |  | 20191002JEM_02 | Infrastructure (network-based) | -37.7543 | 144.8937 | 1 | Jemena | Report | 18426 | 0.014767 | 11kV AC | Essendon Airport | 3040 | Aberfeldie | Dug up
Conductor isolated and repaired LEI called in to assess potential damage to residential supplies | 59 TOWNSEND ROAD, WHITTINGTON VIC 3219 | 30065423 |  |  |  | Overheated connection |  |  |  | HV conductor parted at connection on tee pole fell through LV and landed on traffic signals. local residents reported loud bang and fireball. There was evidence of HVI damage to traffic light signals. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | GLE024 | most likley undetected conductor damage from fault previous evening | HV injection;Loss of supply;Damage to network assets | 43475.7819 |  |  | 14347 | Roadway |  | 20191002PWA_01 | Infrastructure (network-based) | -38.1813 | 144.3893 | 1 | Powercor | Report | 18042 | 0.036414 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3219 | Whittington | Conductor
Fault crews attended the site and isolated supply to the street light pole. Upon inspection, the street light head was burnt out and subsequently replaced. was advised that the property was undergoing demolition and supply abolishment was planned for 30th August. The abolishment had not taken place so the crew abolished the meter and supply to the property. | 102 HAUGHTON ROAD, OAKLEIGH VIC 3166 | 8804026 |  |  |  | Overheated connection |  |  | 1 | UE received a call that a street light had melted and MFB were onsite. | Public lighting | 0 | 0 | 0 |  |  | The cause is unknown, but is likely due to an overheated connection. | Plant/equipment | 43654.3056 | 1 | Negligible: no ground fire | 14361 | Roadway |  | 20191004UTD_01 | Infrastructure (network-based) | -37.908 | 145.098 | 1 | United Energy Distribution | Report | 18060 | 0.0039711 | Low voltage AC (<1kV) | Moorabbin Airport | 3166 | Oakleigh | Connection
Crew replaced the cables and made safe. | 73 Old Geelong Rd Service Rd, Laverton North VIC 3026, Australia | 34013088 | Copper theft | [6 empty] | Passerby advised that exposed wires sticking out of the ground at the above incident location. Upon arrival the crew found service cables 50m of 16mm 4c UG cable stolen. The time/date of the theft is not known. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV006 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/09/2019 21:45 |  |  | 14364 | Roadway |  | 20191007PWA_03 | Infrastructure (network-based) | -37.8487 | 144.7727 | 1 | Powercor | Report | 18064 | 0.01965 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Other
Replaced fuse: Boric acid Fuse carrier replaced. | 10 BACK EILDON ROAD, THORNTON VIC 3712 | 4711025 |  |  |  | Age |  |  | 0 | Candled fuse: Boric Acid fuse carrier had hung up and burnt in half. There was no fire on the ground. | Boric acid | 0 | 0 | 0 |  | ruba 12 | Fuse Candled: The top and bottom contact of the fuse carrier were still in place in the Unit. Fuses carrier had jammed closed and failed to dislodge once fuse link had operated. There was no fire on the ground. | Pole-top fire | 43656.3875 | 1 | Negligible: no ground fire | 14368 |  |  | 20191008SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18069 | 0.03055 | 22kV AC | Moorabbin Airport | 3712 | Thornton | Fuse
Jemena crews were dispatched and site made safe by disconnecting service line to number 3 Bonwick St. Jemena crews later replaced the services to #3 and #1 Bonwick St, also ran new 3 core service to service pole. Following the replacement of the overhead service both properties were connected to supply. At this stage the attending LEI conducted all required VESI tests which recorded a pass result. Further voltage tests between an independent earth and various points of the electrical installation, including the neutral bar at the customers switchboard and metallic water pipe system recorded a voltage of less than >0.5 volts. | 3 BONWICK STREET, FAWKNER VIC 3060 | A030929 |  |  |  | Age |  | Neutral to earth | 2 | Yarra Valley Water contractor received electric shock while working on water supply to 3 Bonwick St, Fawkner Licensed Electrical Inspector (LEI) requested to attend site to investigate reported electric shock received from the water meter. No contact details of the person involved in the reported incident. Upon LEI arriving the Jemena faults crew had isolated supply and were in the process of replacing the overhead services due to the condition of the neutral screen cable. Unable to test for volts on earthing system prior to services being replaced. Jemena crews were told by Yarra Valley Water worker that the contractor who received electric shock was taken to hospital for check up. TechSafe report is attached in the "Notes & Findings" section | Neutral screen | 0 | 0 | 0 |  | CN10 | Broken neutral on the service line | Minor shock | 14/10/2019 11:57 |  |  | 14381 | Residential |  | 20191014JEM_01 | Infrastructure (customer connection) | -37.7064 | 144.9647 | 1 | Jemena | Report | 18091 | 0.039475 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | OH Cable
Site made safe | 29 YOUELL STREET, FOOTSCRAY VIC 3011 | A041074 | Working too close to underground cables | [5 empty] | 2 | An unknown subcontractor working for John Holland and CPB Contractors (CPBJH), the preferred Design & Construct Joint Venture chosen to deliver the West Gate Tunnel Project, were installing drainage infrastructure in a trench bottom of Youell St (Maribyrnong St end) using non-destructive (NDD digging method) and in the process, damaged the insulation of an out of commision (OOC) HV feeder cable. We were not lucky not to experience a supply loss, because if contact had been made with the underground cable on the other side of trench, we would have lost a feeder (YVE22) â€¢ There was a Permit to Work (PTW) in place for the drainage works (JO37293) whose conditions (maintaining 500mm from underground cable) were breached â€¢ New PTW was issued 11/10/19 (J037315) Photos and copy of PTW are attached in the "Notes & Findings" section | Cable | 0 | 0 | 0 |  | YVE22 | No Go Zone breach | No Go Zone (no contact) | 43687.6806 |  |  | 14383 | Industrial |  | 20191015JEM_01 | Infrastructure (network-based) | -37.8104 | 144.9044 | 1 | Jemena | Report | 18167 | 0.0077662 | 22kV AC | Essendon Airport | 3011 | Footscray | Dug up
Fault crew dispatched. O/H HV conductor repaired and re-strung . Supply restored | 620 BEENAK EAST ROAD, GEMBROOK VIC 3783 | LIS417099 |  | Fallen | [5 empty] | Report of tree fallen onto O/H HV conductors resulting in ground fire. | Conductor (bare) | 0 | 0 | 0 |  | OFR23 | Vegetation: Trees Incident | Grassfire | 43475.0333 | 1 | Localised: less than 10 sq.m | 14382 |  |  | 20191015SPN_01 | Infrastructure (network-based) | -37.9349 | 145.5993 | 2 | AusNet Services Distribution | Report | 18094 | 0.015411 | 22kV AC | Moorabbin Airport | 3783 | Gembrook | Trees
On arrival crew isolated supply and carried out repairs LEI attended to check premises for HVI | 5 Bradwell St, Kealba VIC 3021, Australia | 30113150 |  |  |  | Electrical breakdown;Unknown technical factor |  |  | 1 | Multiple reports received of a power outage and loud bangs from residents near to incident locations. On arrival crews found following: Near the corner of Bradwell street and Harefeild crescent some .3KM from the zone substation: HV conductor had parted at bridging connector, allowing conductor to fall to ground. HV leads were damaged at the adjacent gas switch,. AT Hedgley- Driscolls substation some 1.5KM from the zone substation there was flash marks on HV fuses and exit flash marks at LV earth position at ground level. SA002 feeder CB operated to Lockout. There was a number of customers potentially effected by High Voltage Injection (20+) There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | SA002 | It is thought that the incident commenced with the fault which occurred at â€œHedgley-Driscollsâ€ substation pole. The resultant fault currents are believed to have caused subsequent electrical rupture | HV injection;Loss of supply;Significant disruption to the community | 18/10/2019 22:54 |  |  | 14391 | Roadway |  | 20191021PWA_01 | Infrastructure (network-based) | -37.7374 | 144.8234 | 1 | Powercor | Report | 18132 | 0.02074 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3021 | Kealba | Conductor
Field crews attended the site and was advised the customer's son received tingles from the bathroom light switch within the last hour. EIO attended the site and conducted tests which were within normal range. Field crews inspected the connections at the FOLCB on the pole and found a poor neutral connection. They replaced the connection and NST passed. Supply was reconnected and left on. | 2 BERWEN STREET, CHELSEA VIC 3196 | 3302742 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE identified abnormal voltage behaviour from their data analytics at a customer's meter and remotely isolated supply. | Connection box | 0 | 0 | 0 |  |  | The cause was a poor neutral connection at the pole end. | Minor shock | 16/10/2019 21:55 |  |  | 14403 | Residential |  | 20191022UTD_02 | Infrastructure (network-based) | -38.0478 | 145.1121 | 1 | United Energy Distribution | Report | 18130 | 0.037817 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Connection
On arrival crew isolated supply and carried out repairs. | 193-295 BROOKLYN ROAD, BROOKFIELD VIC 3338 | 30293003 | Copper theft | [6 empty] | A public lighting fault crew went out to fault case for an area fault at the incident location. On arrival crew found that service cable had been stolen at eight sites. These cables had been replaced following a similar incident on 3rd of August. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43534.5819 |  |  | 14410 | Roadway |  | 20191023PWA_03 | Infrastructure (network-based) | -37.6992 | 144.5429 | 1 | Powercor | Report | 18144 | 0.034347 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
Repairs completed, lantern replaced | 46B Mountjoy Parade, Lorne VIC 3232, Australia | 30273992 |  |  |  | Unknown technical factor |  |  |  | A customer called to report that on the previous night, the street light opposite No 50, was on fire, and that the lens fell on a truck, they also claim that they called 000 at the time, but no call was received by Powercor. On arrival the crew found the streetlight had overheated and was badly damaged and melted, the remains of the lens was on the ground. There was no ground fire, and no reported third party damage. | Public lighting | 2 | 2 | 2 |  | CLC005 | Unable to determine cause due to damage | Pole-top fire | 43565.3889 | 1 | Negligible: no ground fire | 14412 | Roadway |  | 20191023PWA_05 | Infrastructure (network-based) | -38.5378 | 143.9752 | 1 | Powercor | Report | 18146 | 0.022318 | Low voltage AC (<1kV) | Avalon Airport | 3232 | Lorne | AF Other
Site made safe | 192 WEST STREET, HADFIELD VIC 3046 | A130997 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address today with a Supply Order to abolish service line and meter. When the crew arrived on site they found the property has already been demolished and new dwelling already built on the property and no service line and meter on site. Photos are attached in the "Notes & Findings" secction | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | PV23 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/10/2019 13:31 |  |  | 14419 | Residential |  | 20191025JEM_02 | Infrastructure (network-based) | -37.7021 | 144.9393 | 1 | Jemena | Report | 18156 | 0.018262 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Hadfield | Other
Crew isolated supply and completed switching to re-supply town repairs in progress | 20 COHUNA-LEITCHVILLE ROAD, COHUNA VIC 3568 | 32030524 | Blown detritus | Wind |  |  |  |  | 1 | Powercor received a report of shed blowing into conductor. On arrival crew found a shed roof on top of HV conductors and 1 bay of HV conductors were down. No ground fire. Protection had operated. No third party damage or injury. | Conductor (bare) | 0 | 0 | 0 |  | CHA003 | severe weather event | Damage to network assets | 25/10/2019 3:50 |  |  | 14417 | Peri-urban |  | 20191025PWA_01 | Infrastructure (network-based) | -35.814 | 144.2135 | 1 | Powercor | Report | 18204 | 0.0095567 | 22kV AC | Swan Hill Aerodrome | 3568 | Cohuna | Other
On arrival crew isolated supply and carried out repairs. | 2446 Sunraysia Hwy, Turriff VIC 3488, Australia | 32159041 |  |  |  | Rot |  |  | 1 | Customer reported loss of supply. On arrival crew found a deteriorated crossarm and one conductor had fallen to ground causing a small grass fire (30m x 20m). The fire self extinguished. There was no injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | OYN005 | Deteriorated crossarm | Grassfire | 25/10/2019 7:00 | 1 | Small: 10 - 1000 sq.m | 14420 | Agricultural |  | 20191028PWA_01 | Infrastructure (network-based) | -35.4255 | 142.461 | 1 | Powercor | Report | 18158 | 0.00028472 | 22kV AC | Swan Hill Aerodrome | 3488 | Turriff | Crossarm
New service installed, rectifying and clearance issues to public lighting bracket | 74 COMMERCIAL STREET, MERBEIN VIC 3505 | 33065942 |  |  |  | Electrical breakdown |  |  |  | Powercor fault crew attending an partial supply / intermittent supply failure involving a 3 phase grey twisted overhead service cable revealed that the overhead service which was still energized and sparking, the service was in contact with a public lighting bracket and had worn through the insulation, arcing between phases. The fault crew was quickly approached by a member of the public whose vehicle was parked beneath the service cable in question, and pointed out the extensive molten Aluminium that had fallen onto the vehicle. There was no fire or reported injuries | Service cable (insulated) | 2 | 2 | 2 |  | MBN031 | Service line contacting street light bracket | Loss of supply;Damage to network assets | 43656.6431 |  |  | 14428 | Roadway |  | 20191029PWA_01 | Infrastructure (network-based) | -34.168 | 142.0599 | 1 | Powercor | Report | 18171 | 0.02585 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Merbein | OH Cable
Fault crew and LEI dispatched to make safe, investigate and repair. Repaired and replaced damaged fuse. | 20 EDINBURGH ROAD, LILYDALE VIC 3140 | LIS1000076 |  | Fallen | [5 empty] | Report of HVI. Conductors brought down by tree. | Conductor (bare) | 0 | 0 | 0 |  | LDL21 | Vegetation: Trees Incident | HV injection | 27/10/2019 10:09 |  |  | 14432 |  |  | 20191029SPN_03 | Infrastructure (network-based) | -37.7805 | 145.3496 | 2 | AusNet Services Distribution | Report | 18177 | 0.015358 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Conductor
Supply isolated repairs completed | 10 Godfrey St, Rockbank VIC 3335, Australia | 30548369 | Copper theft | [6 empty] | Public Lighting team reported, Electrix Public Lighting crew attended a public lighting fault at incident location, on arrival the crew found that there was 1 bay of 50m cable missing between poles 871177 and 871175 which had been stolen, two lights are currently off at this site, no photos were taken. No fire or reported injuries | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43656.5549 |  |  | 14438 |  |  | 20191030PWA_01 | Infrastructure (network-based) | -37.7165 | 144.6692 | 1 | Powercor | Report | 18184 | 0.025701 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
CFA attended site to extinguish the fire. Damaged Voltage regulator removed from service and replaced with new. Surge diverters replaced and supply restored | 3170 BASS HIGHWAY, ANDERSON VIC 3995 | LIS2800755 |  |  |  | Defective component;Electrical breakdown |  |  |  | Surge diverter failed during REFCL stress testing resulting in ground fire. | Surge diverter;Voltage regulator | 0 | 1 | 0 |  | WGI23 | A surge diverter has failed at Voltage Regulator site during REFCL stress testing resulting in ground fire which stopped at and was contained by the concrete bund. CFA attended site to extinguish the fire. Damaged Voltage regulator removed from service and replaced with new. Surge diverters replaced and supply restored | Plant/equipment | 24/10/2019 14:18 | 1 | Localised: less than 10 sq.m | 14437 |  |  | 20191030SPN_01 | Infrastructure (network-based) | -38.5276 | 145.4466 | 1 | AusNet Services Distribution | Report | 18183 | 0.02376 | 22kV AC | Moorabbin Airport | 3170 | Anderson | AF Other
crew assessed site span to be re-sagged | 215 Farm Road, Cocoroc, VIC, 3030 | 30304230 |  |  |  | Conductor clashing |  |  | 1 | MMBW report grass fire possibly due to conductor clash between lis 799280 and 799276. PCA Faults Crew attended site and at first could not find any evidence of any grass fire within the span from Pole 2 LIS-799276 south west to Pole 3 LIS-799280, After further investigations the crew advised that they discovered a grass fire of approx. 30m x 30m, some 20m south of the conductors. | Conductor (bare) | 0 | 0 | 0 |  | WBE033 | possible clashing during to high winds | Grassfire | 43507.4167 | 1 | Small: 10 - 1000 sq.m | 14448 | Agricultural |  | 20191104PWA_02 | Infrastructure (network-based) | -37.9263 | 144.6471 | 1 | Powercor | Report | 18205 | 0.0063032 | 22kV AC | Laverton Raaf | 3030 |  | Conductor
Made safe and repaired | 5 WARANGA DRIVE, WARANGA SHORES VIC 3612 | 33089098 |  | Alive;Property owner/customer | [5 empty] | Customer reported wire down hanging from pole and down onto grass, has caused fire, Fire brigade has just arrived to put fire out, at incident location. Crew found a customers tree had damaged an O/H HV conductor, starting a 800m2 ground fire, no property damage, no injuries, Vegetation Crew working nearby assisted with clean-up. | Conductor (bare) | 0 | 0 | 0 |  | SHP014 | Vegetation: Trees Incident | Grassfire | 43476.5042 | 1 | Small: 10 - 1000 sq.m | 14450 | Roadway |  | 20191104PWA_04 | Infrastructure (network-based) | -36.5331 | 145.0586 | 1 | Powercor | Report | 18209 | 0.022796 | 22kV AC | Shepparton Airport | 3612 | Waranga Shores | Trees
Fault crew dispatched and damaged centre phase insulator replaced. Supply restored. | 126 WALLER STREET, BENALLA VIC 3672 | LIS3903114 |  | Bird | [5 empty] | Feeder CB tripped on fault as a result of bird contacting O/H HV conductors resulting in ground fire | Conductor (bare);Insulators | 0 | 0 | 0 |  | BN4 | Bird Incident | Bushfire | 43476.6542 | 1 | Small: 10 - 1000 sq.m | 14466 |  |  | 20191107SPN_01 | Infrastructure (network-based) | -36.56 | 145.9661 | 2 | AusNet Services Distribution | Report | 18231 | 0.022773 | 22kV AC | Wangaratta Aero | 3672 | Benalla | Animal
The Powercor crew replaced all cut off pit connectors and reconnected all cables inside pits | 178 PAYNES ROAD, THORNHILL PARK VIC 3335 | 30554313 | Copper theft | [6 empty] | caller reported copper theft from U/G pits feeding P/L outside Thornhill Estate near intersection of Murray Rd and Paynes Rd Rockbank On arrival the Crew found that 6 P/L service pits had their concrete lids removed and wires were pulled out and exposed hanging out of the pits, pit connectors were cut off but no cable had been stolen from the pits. | Services cable;Services pit (network) | 0 | 0 | 0 |  | MLN021 | attempted copper theft | Damage to network assets | 14/10/2019 19:57 |  |  | 14470 | Roadway |  | 20191108PWA_02 | Infrastructure (network-based) | -37.7184 | 144.6363 | 1 | Powercor | Report | 18237 | 0.001088 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Other
crew attended and isolated supply, follow up works initiated to replace cabing | 38 Black Bottom Road, Brewster, 3352. | 30314282 | Copper theft | [5 empty] | 2 | Member of the public reported public lights out at the incident intersection / address. Crew attended and found multiple pits had been illegally entered and public light cable stolen from them | Services cable | 0 | 0 | 0 |  | BAS011 | copper theft from lighting supplies | Damage to network assets | 22/10/2019 0:00 |  |  | 14471 | Roadway |  | 20191108PWA_03 | Infrastructure (network-based) | -37.4548 | 143.5351 | 1 | Powercor | Report | 18238 | 0.0074537 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 |  | Other
Note: Maranda who received the electric shock was not in attendance at the time the attending LEI was on site. Maranda's aunt, Stefania Sorrentino, who was also the home owner was the person who reported the incident and was the source of the information. Upon arrival to site the attending LEI conducted a test between an independent earth to the pool water in which the electric shock had been received, with 11V AC recorded. A further test at the installation main switchboard recorded 20V AC on the neutral bar. A further NST test ws conducted at the switchboard recording a failed result. At this stage a Jemena truck crew was called to investigate further. The attending faults crew was able to identify a loose neutral on the customers side within the FOLCB. At this point this connection was tightened. Following this an NST at the customers main switchboard recorded a pass result. A secondary test at the pool was conducted with 408mV measured. The installation was left on supply and Stefania was instructed to contact Jemena immediately if another incident occurred. | 1A ARBOR STREET, ALPHINGTON VIC 3078 | A011132 |  |  |  | Neutral fault |  |  | 2 | The electric shock was received when Maranda was swimming in the pool approximately 2 weeks ago. Whilst exiting the pool, she received an electric shock when making simultaneous contact with the water in the swimming pool and the pool deck with her arm. At the time Maranda had thought it to be a static electric shock. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a loose neutral connection, resulting in a higher than normal impedance within the neutral service conductor. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and metallic water pipe system was sufficient to cause a voltage rise of 11 Volts on the water piping system and between the points of contact. | POA connection (customer side) | 0 | 0 | 0 |  | FF96 | Poor neutral connection at FOLCB (customer side) | Minor shock | 43780.5757 |  |  | 14482 | Residential |  | 20191111JEM_03 | Infrastructure (customer connection) | -37.7794 | 145.0347 | 1 | Jemena | Report | 18249 | 0.020272 | Low voltage AC (<1kV) | Essendon Airport | 3078 | Alphington | Installation
Fault truck and LEI dispatched. Loose Neutral identified within POA on neighbours installation (#20). Defect notice issued to neighbouring property. POA rectified and supply restored following completion of repairs and all tests passed | 24 CASSELLS ROAD, RESEARCH VIC 3095 | LIS919235 |  |  |  | Unidentified customer fault |  |  |  | Customer reported receiving electric shock | POA connection (customer side) | 0 | 0 | 0 |  | ELM13 | Loose Neutral identified within POA of neighbours installation (#20). Defect notice issued to neighbouring property. POA rectified and supply restored following completion of repairs and all tests passed | Minor shock | 15/10/2019 19:02 |  |  | 14479 | Residential |  | 20191111SPN_01 | Infrastructure (customer connection) | -37.6974 | 145.1852 | 2 | AusNet Services Distribution | Report | 18246 | 0.018367 | Low voltage AC (<1kV) | Essendon Airport | 3095 | Research | Installation
site inspected and supply restored | OSICKAS WINERY, 39 OSICKAS LANE, GRAYTOWN VIC 3608 | 32051166 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Crew investigating supply outage found wheel tracks and materials dumped beneath line and arc marks on conductor. No vehicles/Tip Truck at site when crew arrived. | Conductor (bare) | 0 | 0 | 0 |  | BGO023 | tip truck unloading under line | Loss of supply | 43810.4069 |  |  | 14488 | Agricultural |  | 20191113PWA_01 | Infrastructure (network-based) | -36.8471 | 144.9284 | 1 | Powercor | Report | 18258 | 0.035509 | 22kV AC | Mangalore Airport | 3608 | Graytown | Vehicle
Fault crew and LEI dispatched. Neutral connection in pole mounted junction box repaired. All tests carried out/passed and supply restored | 2 HALCYON AVENUE, THE PATCH VIC 3792 | LIS1305008 |  |  |  | Defective component |  |  |  | customer and advised she received a tingle off shower | Connection box | 0 | 0 | 0 |  | BGE11 | Poor neutral connection at pole mounted junction box resulting in Electric Shock. | Minor shock | 43657.3944 |  |  | 14487 | Residential |  | 20191113SPN_01 | Infrastructure (customer connection) | -37.8862 | 145.3908 | 2 | AusNet Services Distribution | Report | 18256 | 0.030263 | Low voltage AC (<1kV) | Moorabbin Airport | 3792 | The Patch | Connection
15/11/2019 - Trouble order number 1351432 was created and a faults crew attended and removed the meter and overhead service. | 9 THE BOULEVARDE, DONCASTER VIC 3108 |  | Unauthorised work | [5 empty] | 2 | 29/08/2019 - Meter 917554 was installed at 37 Kangerong Avenue, Dromana but disappeared and ceased to communicate with no evidence of United Energy representatives attending. 22/10/2019 - The above meter starting communicating again at a new location and a site visit was arranged to asses the situation. The meter was found installed on a Builders Supply Pole (BSP) located at 9 The Boulevarde, Doncaster with no truck appointments, Retailer Service Orders or CES provided. In summary, there was no service or trouble orders found for either site. A meter technician investigation found the Dromana site is now a vacant block and the Doncaster site has recently commenced construction activities. It appears that unknown persons installed a XLPE service to the BSP and it was observed that older style service line tap connectors were used at the pole end and there wasn't an earth connected at the BSP. | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  |  | Unknown persons have relocated a meter and installed an overhead service to a BSP with no MEC involvement or CES provided. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43657.6146 |  |  | 14500 | Residential |  | 20191118UTD_01 | Infrastructure (customer connection) | -37.7773 | 145.1301 | 1 | United Energy Distribution | Report | 18271 | 0.037574 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | Other
Fault crews arrived at the site and the site was made safe. It was identified that a tree branch fell on the overhead HV lines and potentially may have caused HVI. EIO arrived on site to investigate and confirmed HVI. Fault crews repaired the overhead lines and restored supply to customers. | FLAT 1 6 OAKLEIGH CRESCENT, ORMOND VIC 3204 | 2320140 |  | Fallen |  | HV injection |  |  | 1 | UE identified abnormal supply to customers from its data analytics and feeder CB operated to isolate the fault. | Conductor (bare) | 0 | 0 | 0 |  | BT9 | Vegetation: Trees Incident | HV injection | 43780.3229 |  |  | 14504 | Roadway |  | 20191120UTD_01 | Infrastructure (network-based) | -37.9075 | 145.0419 | 1 | United Energy Distribution | Report | 18278 | 0.0033044 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3204 | Ormond | Trees
Crew attended and made safe | 121 JAMES MELROSE DRIVE, BROOKFIELD VIC 3338 | 30300200 | Copper theft | [5 empty] | 2 | Customer report of driving down street noticed the covers are off at least 2 of the pillars and cables are exposed on the ground, customer said he heard a loud bang around 10pm last night (wasn't sure if involved with this) also said they are near the park but wasn't sure of exact address. Crew made safe -2 public lights to reconnected and test lis#795179 and lis#795178. | Services cable;Services pit (network) | 0 | 0 | 0 |  | MLN013 | Attempted Copper Theft | Damage to network assets | 43476.4667 |  |  | 14506 | Roadway |  | 20191121PWA_01 | Infrastructure (network-based) | -37.7104 | 144.5557 | 1 | Powercor | Report | 18280 | 0.033748 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
All installations on the affected circuits were isolated on the afternoon of the incident. Following the completion of the repairs to the HV and aerial earth conductors, several LEI's began to inspect the accessible installations, re-energise the properties and issue damage cards. All installations on the Peterson Ave circuit were restored the night of the incident with LEI's returning the next morning to restore supply to installations on the Elizabeth St and Malcolm St circuit. | F Cox Reserve, Coburg North VIC 3058 | A036379 and A034854 |  | Blown branch/vegetation |  |  |  |  | 2 | HVI resulting from a tree branch falling on the HV open wire conductors running between Elizabeth St and Peterson Ave, resulting in small grassfire. The HV conductors came into contact with the aerial earth conductor running between poles A036379 and A034854. This aerial earth conducted connected to the LV neutral conductor of two separate street circuits on Elizabeth St and Peterson Ave, resulting in a HV injection into the LV circuits. No photos are available for this incident. | Conductor (bare) | 0 | 0 | 0 |  | CN08 | Vegetation: Trees Incident | HV injection;Loss of supply;Grassfire | 21/11/2019 9:34 | 1 | Localised: less than 10 sq.m | 14510 | Residential |  | 20191122JEM_01 | Infrastructure (network-based) | -37.7341 | 144.9827 | 1 | Jemena | Report | 18425 | 0.0076771 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3058 | Coburg North | Trees
Broken conductor strand cut away and remaining strands secured until follow up action is undertaken. | 525 Glenelg Hwy, Streatham VIC 3351, Australia | 30083878 |  | Lightning | [5 empty] | Vic fire reported wires down causing grass fire. On arrival crew found a broken strand of HV conductor had been intermittently brushing across phases. The sparks from this started a grass fire, observed and extinguished by CFA personnel. There was a small fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | ART033 | Strand broke away from conductor | Grassfire | 21/11/2019 11:57 | 1 | Small: 10 - 1000 sq.m | 14519 | Agricultural |  | 20191122PWA_02 | Infrastructure (network-based) | -37.6923 | 143.0087 | 1 | Powercor | Report | 18304 | 0.018656 | 22kV AC | Ballarat Aerodrome | 3351 | Streatham | Conductor
Service was replaced. | Gerber Rd Monbulk VIC 3793 | LIS1320862 |  | Lightning | [5 empty] | Report of tree contacting and bringing down O/H conductor with possible ground fire. | Service cable (insulated) | 0 | 0 | 0 |  | BGE11 | Ground fire started by lightning, not caused by network asset. | Grassfire | 21/11/2019 20:23 | 0 | Localised: less than 10 sq.m | 14515 |  |  | 20191122SPN_02 | Infrastructure (network-based) | -37.8846 | 145.42 | 2 | AusNet Services Distribution | Report | 18295 | 0.011546 | Low voltage AC (<1kV) | Moorabbin Airport | 3793 |  | Trees
Faults crew attended the site and made it safe. They repaired the HV lines and restored supply. | 389 TUCKS ROAD, SHOREHAM VIC 3916 | 1313635 |  | Wind;Fallen |  |  |  |  | 1 | During a high wind event, a customer's tree has fallen over the HV lines on Tucks Rd which resulted in a small grass fire that the CFA extinguished. UE protection operated to isolate the fault. ESV was notified, report #12847040. | Conductor (bare) | 0 | 0 | 0 |  | DMA23 | Vegetation: Trees Incident | Grassfire | 21/11/2019 16:55 | 1 | Small: 10 - 1000 sq.m | 14518 | Roadway |  | 20191122UTD_01 | Infrastructure (network-based) | -38.4125 | 145.0143 | 1 | United Energy Distribution | Report | 18299 | 0.01636 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3916 | Shoreham | Trees
Site made safe Isolated substation HV fuses Replaced LV bushings and transformer Repaired LV underground cable | 115 DUNCANS LANE, DIGGERS REST VIC 3427 | A005100 | Copper theft | [5 empty] | 2 | Work crew advised Attempted Copper theft at Substation Pole A005100 Duncans Lane South 3 underground LV bushings damaged, Substation will require redressing | Cable;Pole mounted | 0 | 0 | 0 |  | SHM11 | Attempted copper theft | Damage to network assets | 24/11/2019 8:48 |  |  | 14524 | Roadway |  | 20191124JEM_01 | Infrastructure (network-based) | -37.6405 | 144.7432 | 1 | Jemena | Report | 19746 | 0.041428 | Low voltage AC (<1kV) | Melbourne Airport | 3427 | Diggers Rest | Other
The crew made site safe, rolled up burnt down cable and a FFU was created to replace damaged conductor.. | 293 State Route 41, Altona Meadows VIC 3028, Australia | 30118601 |  | Wind |  | Conductor clashing |  |  |  | City West Water, reported pole to pole wire is broken, wire down, crossing over driveway and road. Fire is out and police is on site. On arrival the crew found that the LV O/H service conductor between poles LIS-214017 and LIS-214018 was broken and lying on the ground over the driveway and on the grass. There was a small area of burnt grass. There was no reported injuries nor third party property damage. | Service conductor (bare) | 2 | 2 | 2 |  | LVN022 | Severe wind storm | Grassfire | 21/11/2019 14:35 | 1 | Localised: less than 10 sq.m | 14534 | Roadway |  | 20191125PWA_04 | Infrastructure (network-based) | -37.874 | 144.7894 | 1 | Powercor | Report | 18326 | 0.0074433 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Conductor
Dispatched fault crew to investigate and make safe. Crew found fuse had become hot and melted some plastic. Crew replaced fire damaged service fuse and fuse holders. No other fire damage to meter board. | 5213 PRINCES HIGHWAY, NEWMERELLA VIC 3886 | LIS1905995 |  |  |  | Electrical breakdown |  |  |  | Report of fire on customer meter board | Meter board (including fuses) | 0 | 0 | 0 |  | NLA34 | Fuse and fuse holder overheated and melted fuse holder and some plastic. | Meter board | 23/11/2019 12:29 | 1 | Negligible: no ground fire | 14528 | Other | Motel | 20191125SPN_03 | Infrastructure (customer connection) | -37.7401 | 148.4205 | 1 | AusNet Services Distribution | Report | 18317 | 0.0022708 | Low voltage AC (<1kV) | Bairnsdale Airport | 3886 | Newmerella | Installation
Fault crew dispatched. Candled HV fuse removed and replaced with new. Supply restored | 2 DAPHNE DRIVE, MOE SOUTH VIC 3825 | LIS2202289 |  |  |  | Candled fuse |  |  |  | Report of candled HV Fuse | Any other type | 0 | 0 | 0 |  | MOE31 | Candled HV Fuse | Pole-top fire | 25/11/2019 5:16 | 1 | Negligible: no ground fire | 14530 |  |  | 20191125SPN_05 | Infrastructure (network-based) | -38.2164 | 146.2576 | 1 | AusNet Services Distribution | Report | 18321 | 0.026185 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Moe South | Fuse
Assisted ESV | 467 THE ESPLANADE . ST LEONARDS 3223 | 32085774 | under investigation;Other | [5 empty] | 1 | ESV advised of HV contact and serious injury, requested EWP to assist investigation | Conductor (bare);Service cable (insulated) | 0 | 0 | 0 |  | DDL013 | unknown TBC | Loss of supply;Medical attention (first aid/doctor/hospital);No Go Zone (contact) | 25/11/2019 15:28 |  |  | 14537 | Residential |  | 20191126PWA_03 | Infrastructure (network-based) | -38.1652 | 144.7162 | 1 | Powercor | Report | 18331 | 0.00025694 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3223 |  | Other
The crew isolated the street circuit and performed repairs. | 10 SCOTSBURN GROVE, TOORAK VIC 3142 | 60138330 | Working too close to underground cables | [6 empty] | A customer called to report an excavator had ripped up an underground pit at the incident location. On arrival the crew found that the pit to No10 Scotsburn Grove and the mains cable feeding it had been damaged. A report came through that the customer had called ESV and reported that the pit was actually on his property. The crew took measurements and said that the pit was definitely on the road reserve, and that the demolition crew using the excavator had cut approx. 500mmm of the footpath away from around the pit. The demolition crew were working for the owner builder. There were no reported injuries or fires. | Cable;Services cable;Services pit (network) | 2 | 2 | 2 |  | AR005 | Customers builder using excavator dug up pit and cable | No Go Zone (contact);Damage to network assets | 22/10/2019 12:05 |  |  | 14540 | Roadway |  | 20191126PWA_05 | Infrastructure (customer connection) | -37.8435 | 145.0217 | 1 | CitiPower | Report | 18334 | 0.0011447 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Dug up
The attending LEI carried out all subsequent testing procedures, including:- Voltage tests from independent earth spike to - metallic plumbing fixtures, Neutral bar of the customers main switchboard, Customerâ€™s plumbing fixtures and where victim received the electric shock, recorded various voltages as the load increased to the property NST - failed test result. The attending LEI identified a severely corroded neutral terminal at customers FOLCB. Service crew disconnected service line to property. A new twisted service was installed. NST - passed. Impedance of 0.3 ohms and 0.5 volts recorded. Supply was restored to property and left ON | 1 VICTORY PARADE, ASCOT VALE VIC 3032 |  |  |  |  | Corrosion |  |  | 2 | The owner of the property was using front tap when she received an electric shock by making simultaneous contact with her hand and the metallic water pipe while kneeling on the wet surface. A fault was identified at the point of attachment. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise up to 20V on the water piping system. TechSafe report attached in the "Notes & Findings" section | Service conductor;Neutral screen;Connection box | 0 | 0 | 0 |  |  | Severely corroded neutral terminal at customer's FOLCB located at the point of attachment | Minor shock | 24/04/2019 14:53 |  |  | 13582 | Residential |  | 20190424JEM_01 | Infrastructure (customer connection) | -37.7809 | 144.9106 | 1 | Jemena | Report | 16844 | 0.028059 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Connection
Jemena UG crew made repairs to vandalised sections of UG cable and restored power to street lights. | CALDER PARK DRIVE, TAYLORS HILL VIC 3037 | 11591366 | Vandalism;Copper theft | [5 empty] | 2 | Unknown persons vandalised underground electricity pits along Calder Park Drive, North of Hume Drive | Cable;Services pit | 0 | 0 | 0 |  | SHM21 | vandalism / attempted copper theft | Damage to network assets | 26/04/2019 9:55 |  |  | 13587 | Roadway |  | 20190426JEM_02 | Infrastructure (network-based) | -37.7098 | 144.755 | 1 | Jemena | Report | 16851 | 0.025249 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Taylors Hill | Other
Fault crew and LEI dispatched to investigate. Transformer supplying property replaced and LV earthing rectified at s/stn. LEI conducted tests following rectification works and all passed | 187 CARBOOR UPPER ROAD, CARBOOR VIC 3678 | LIS5100597 |  |  |  | Defective component;Not built/maintained to design |  | Phase to earth |  | E0019140 - Report of resident and plumber receiving electric shock | Earth/earthing;Transformer | 0 | 0 | 0 |  | WN5 | Resident made contact with the earthed portions of the meter panel and received an shock. Separately, a plumber also received a shock from the new copper piping he was installing as part of renovation works to relocate a hot water service. Customer installation has no main earth electrode and MEN at the main switchboard. Instead, the site is connected directly to the LV earth on pole s/stn in the form of 6mm cable run with consumer mains. LV and HV earth at transformer found to be 170 ohms and 70 ohms respectively. Transformer replaced and earthing rectified. Customer installation passed all tests following repair works and supply restored. High LV and HV earth readings are currently being investigated separately | Minor shock | 30/04/2019 15:06 |  |  | 13601 | Residential |  | 20190430SPN_01 | Infrastructure (network-based) | -36.6535 | 146.5354 | 1 | AusNet Services Distribution | Report | 16921 | 0.040766 | Low voltage AC (<1kV) | Wangaratta Aero | 3678 | Carboor | AF Other
substation isolated and earth rectified | 597 WALLACEDALE-BYADUK ROAD, WALLACEDALE VIC 3303 | 30087598 |  |  |  | Earth fault |  |  | 2 | customer reports earth is burning where it meets the pole. Crew attended site to find SWER earth getting very hot near base of pole. Appears to have ignited a small grass fire about 0.5m2. | Earth/earthing | 0 | 0 | 0 |  | HTN002 | High resistance in earthing system | Grassfire | 43470.4549 | 1 | Localised: less than 10 sq.m | 13616 |  |  | 20190501PWA_06 | Infrastructure (network-based) | -37.9284 | 141.8468 | 1 | Powercor | Report | 16893 | 0.0031863 | 12.7kV AC (SWER) | Hamilton Airport | 3303 | Wallacedale | AF Other
Fault crew dispatched. Candled HV fuse removed and replaced with new. Supply restored | 331 Soldiers Rd Barnawartha VIC 3688 | LIS 5235940 |  |  |  | Candled fuse |  |  |  | Report of Candling Fuse | Boric acid | 0 | 0 | 0 |  | BWA22 | BA HV fuse has candled | Pole-top fire | 43470.2632 | 1 | Negligible: no ground fire | 13615 |  |  | 20190501SPN_03 | Infrastructure (network-based) | -36.0953 | 146.6571 | 2 | AusNet Services Distribution | Report | 16890 | 0.032171 | 22kV AC | Wangaratta Aero | 3688 |  | Fuse
supply isolated pending pole replacement | 617 MCEWEN ROAD, WYUNA VIC 3620 | 31027332 |  |  |  | Age;Rot |  |  | 1 | Customer reported loud bang and power went out. Crew attended site to find broken HV cross-arm on Harris P5, with a flash over and pole fire on Tongala East -P79 | Conductor (bare);Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | KYM004 | cross-arm on pole 5 broke due to deterioration. | Pole-top fire | 43470.5625 | 1 | Negligible: no ground fire | 13621 | Roadway |  | 20190502PWA_01 | Infrastructure (network-based) | -36.2547 | 145.0319 | 1 | Powercor | Report | 16901 | 0.031523 | 22kV AC | Shepparton Airport | 3620 | Wyuna | Crossarm
ON arrival repairs carried out | 2 OLD LEAKES ROAD, ROCKBANK VIC 3335 | 30268314 | Copper theft | [6 empty] | P/L Fault Group was called street light cable theft at the incident location.. A contractor, Electrix, attended and repairs have been completed on the day. The contractor also found a small cable cutter that was left at the incident location. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 43559.4167 |  |  | 13627 | Roadway |  | 20190506PWA_01 | Infrastructure (network-based) | -37.7259 | 144.6517 | 1 | Powercor | Report | 16907 | 0.029655 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Crew assessed and have initiated replacement | 149 COMMERCIAL STREET, MERBEIN VIC 3505 | 32151664 |  | Prone to dust deposition |  | Leakage |  |  | 1 | Vic Fire reported a pole fire at the incident location. Upon arrival crew found that an intermediate crossarm had burnt through at the kingbolt, dropping down onto the LV cross arm below | Crossarm (wood) | 0 | 0 | 0 |  | MBN031 | excessive leakage current | Pole-top fire | 23/04/2019 14:37 | 1 | Negligible: no ground fire | 13644 | Roadway |  | 20190507PWA_05 | Infrastructure (network-based) | -34.1678 | 142.0658 | 1 | Powercor | Report | 16970 | 0.0037708 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3505 | Merbein | Crossarm
crew attended and replaced HV cross-arm | 2135 FIFTEENTH STREET, IRYMPLE VIC 3498 | 30099579 |  |  |  | Leakage |  |  | 1 | A pole fire reported at the incident location. The attending crew found the HV strain cross-arm had burnt | Crossarm (wood) | 0 | 0 | 0 |  | MDA023 | excessive leakage current | Pole-top fire | 23/04/2019 14:42 | 1 | Negligible: no ground fire | 13646 | Residential |  | 20190507PWA_06 | Infrastructure (network-based) | -34.2358 | 142.1713 | 1 | Powercor | Report | 16980 | 0.010596 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Fault crew were dispatched and they disconnected the supply to the Dairy | 110 WATERLOO ROAD, MOE VIC 3825 |  |  |  |  | Fault on customer installation |  |  |  | E0019255 - Customer reported electric shock from excavator following contact with U/G cable | Cable | 0 | 0 | 0 |  | MOE23 | Fault crew attend the site previously, disconnected the supply to house but second point of supply not identified, so it was left on supply. Customer demolishing the Dairy and pulled the old customer cable but left on supply. 2nd point of supply did not have a meter, so it was not identified. | Minor shock;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43560.4528 |  |  | 13639 |  |  | 20190507SPN_01 | Infrastructure (network-based) | -38.181 | 146.245 | 1 | AusNet Services Distribution | Report | 16944 | 0.039872 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Moe | Dug up
Supply isolated and cross arm replaced. | 264 COORONG AVENUE, IRYMPLE VIC 3498 | 32148573 |  |  |  | Leakage |  |  | 1 | Customer reported wire down at the incident location. Upon arrival crew found that a Tee Off cross-arm burnt off at eye bolt position. Supply remained on as the conductor remained aloft suspended by the bridging cable. | Crossarm (wood) | 0 | 0 | 0 |  | RCT021 | excessive leakage | Pole-top fire | 24/04/2019 16:45 | 1 | Negligible: no ground fire | 13649 | Roadway |  | 20190508PWA_01 | Infrastructure (network-based) | -34.2716 | 142.162 | 1 | Powercor | Report | 17012 | 0.0060359 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
crew attended, isolated and replaced cross-arm | 214 BACCHUS MARSH ROAD, CORIO VIC 3214 | 32073948 |  |  |  | Leakage |  |  | 1 | Vic Fire reported a pole fire at the service road of this incident location. The attended crew made the site safe and repairs arranged | Crossarm (wood) | 0 | 0 | 0 |  | FNS011 | excessive leakage current | Pole-top fire | 26/04/2019 10:18 | 1 | Negligible: no ground fire | 13651 | Roadway |  | 20190508PWA_03 | Infrastructure (network-based) | -38.067 | 144.359 | 1 | Powercor | Report | 17014 | 0.039965 | 22kV AC | Avalon Airport | 3214 | Corio | Crossarm
Lv cross-arm replaced | 39 TOOLE STREET, HOPETOUN VIC 3396 | 32098179 |  |  |  | Leakage |  |  | 2 | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that an LV crossarm had burned through on a HC / LV 2 way tee off pole. The Powercor pole was also burned at the kingbolt location. | Crossarm (wood) | 0 | 0 | 0 |  | HSM003 | excessive leakage current | Pole-top fire | 43470.241 | 1 | Negligible: no ground fire | 13652 | Roadway |  | 20190508PWA_04 | Infrastructure (network-based) | -35.725 | 142.3616 | 1 | Powercor | Report | 17015 | 0.021569 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3396 | Hopetoun | Crossarm
Crew isolated customer underground mains at pit and removed fuses from folcb | 12 STRONG STREET, WARRNAMBOOL VIC 3280 | 30135810 | Working too close to underground cables | [6 empty] | NATIONAL HAULAGE (AUST) PTY LTD, REC David Roberts REC#16052 is calling in to report a team working at the site has dug through underground mains, vehicle is still attached to mains, needs site isolated to remove vechicle and repair. Everyone on site is safe. Clear access to site, There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | WBL004 | Post hole digger struck service cable | Loss of supply;Damage to network assets | 43681.6458 |  |  | 13658 | Commercial |  | 20190510PWA_01 | Infrastructure (network-based) | -38.3775 | 142.4596 | 1 | Powercor | Report | 17054 | 0.021214 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Dug up
On arrival crew confirmed isolation and arranged repairs | 14 DUGGAN STREET, BALWYN NORTH VIC 3104 | 30191994 | Copper theft | [6 empty] | An electrician at a house construction site at the incident location reported that the UG cable between the pole and the pit had been stolen. On arrival the crew found that an unknown person had stolen approx. 10m of 4 core LV UG cable between the pole and the pit. There were no reported injuries or fires. | Services cable | 2 | 2 | 2 |  | WD013 | Copper theft | Damage to network assets | 43712.3611 |  |  | 13659 | Residential |  | 20190510PWA_02 | Infrastructure (network-based) | -37.7965 | 145.09 | 1 | CitiPower | Report | 17055 | 0.029927 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
On arrival isolation confirmed and repairs arranged | 440-448 POINT COOK ROAD, POINT COOK VIC 3030 | 30546465 | Vandalism;Copper theft | [6 empty] | Paul from Parabar reported that someone had cut wires in in a pit at the incident location. On arrival the crew found that the LV UG service cable feeding street lights had been cut at four pits over a 150m distance, between LIS-823809 & LIS-770982. The service cable was still in the conduits, the crew thought the thieves may have been disturbed or were planning on returning to steal the cable later. There were no reported injuries or fires. | Services cable;Services pit | 2 | 2 | 2 |  | LV004 | Attempted copper theft | Damage to network assets | 43712.4479 |  |  | 13660 | Roadway |  | 20190510PWA_03 | Infrastructure (network-based) | -37.9146 | 144.7509 | 1 | Powercor | Report | 17056 | 0.0032454 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew isolated supply and arranged repairs. | 65 YORKSHIRE CLOSE, BATESFORD VIC 3213 | 34021996 | Working too close to underground cables | [6 empty] | Robert from DKM Earthworks reported that they were doing backhoe work out the front of the incident location when they "nicked" an LV UG Cable. On arrival the crew found that an LV UG cable had the outer sheath slightly damaged, when the cable was unearthed. The crew said that the cable location was not exactly where it was shown in the MOCS, as there was a big loop where the service cable came away from the service tee joint. There were no injuries or fire reported. | Services cable | 2 | 2 | 2 |  | GL015 | backhoe struck cable. | No Go Zone (contact) | 43712.4139 |  |  | 13661 | Residential |  | 20190510PWA_04 | Infrastructure (network-based) | -38.0932 | 144.2613 | 1 | Powercor | Report | 17057 | 0.013436 | Low voltage AC (<1kV) | Avalon Airport | 3213 | Batesford | Dug up
crew lowered Peru | 1990A WESTERN FREEWAY, AINTREE VIC 3336 | 33072379 |  |  |  |  | Not followed;Ineffective planning/procedures/processes |  | 1 | A PAL crew were using a PERU to maneuver a pole in preparation for standing that pole. Whilst slewing the PERU unit contacted 22kV overhead conductors. | Conductor (bare) | 0 | 0 | 0 |  | MLN021 | Designated Safety Observer not appointed for pole relocation task Failed to maintain SAD to existing OH 22kV conductors | Loss of supply | 43713.4264 |  |  | 13664 | Roadway |  | 20190510PWA_06 | Infrastructure (network-based) | -37.7341 | 144.6697 | 1 | Powercor | Report | 17066 | 0.032596 | 22kV AC | Laverton Raaf | 3336 | Aintree | Other
Fault crew dispatched. Old Grey TW service replaced with new XLPE service cable and, following repair, final NST test performed and passed. Supply restored to customer | 1528-1536 BASS HIGHWAY, GRANTVILLE VIC 3984 | LIS2802948 |  |  |  | Defective component |  |  |  | E0019226 - Customer reported receiving slight tingles off the cyclone fencing gate when opening and notice sparking at a gate and blue flashes at the hinges when opening | Aluminium twisted (grey);Connection box | 0 | 0 | 0 |  | LLG13 | Fault attended and identified neutral service connection had broken away at the pole junction box. Service cable replaced with XLPE service cable and, following repair, final NST test performed and passed. | Minor shock | 43529.3986 |  |  | 13671 |  |  | 20190513SPN_01 | Infrastructure (customer connection) | -38.409 | 145.5288 | 1 | AusNet Services Distribution | Report | 17069 | 0.0082292 | Low voltage AC (<1kV) | Moorabbin Airport | 3984 | Grantville | Connection
pole replaced. | MYALL ROAD, LASCELLES VIC 3487 | 32159145 |  |  |  | Leakage |  |  | 2 | Customer reported pole in paddock has burnt to the ground in past 24 hours, not currently on fire, paddock is on Mitchell road between where it meets Myall School Bus Road and Sea Lake-Lascelles Road. Crew found SWER pole had been burnt due to pole fire, minor ground fire damage around where pole was. | Pole (wood) | 0 | 0 | 0 |  | OYN005 | excessive leakage | Pole-top fire;Grassfire | 13/05/2019 12:26 | 1 | Localised: less than 10 sq.m | 13678 | Agricultural |  | 20190514PWA_05 | Infrastructure (network-based) | -35.5008 | 142.7171 | 1 | Powercor | Report | 17076 | 0.03481 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3487 | Lascelles | Pole
Isolated and replaced FSD | BELMONT PRIMARY SCHOOL, 51 MT PLEASANT ROAD, BELMONT VIC 3216 | 31010963 |  |  |  | Overheated connection |  |  | 2 | Belmont Primary School advises top of pole is on fire, pole is located directly at front of the school and at school crossing. Powercor crew arrived to find a fuse switch disconnect (FSD) device had overheated and caught fire. The Fire brigade had extinguished the fire prior to the crew attending. | Disconnector/isolator | 0 | 0 | 0 |  | GCY023 | overheated connection | Pole-top fire | 13/05/2019 9:00 | 1 | Negligible: no ground fire | 13679 | Public space |  | 20190514PWA_06 | Infrastructure (network-based) | -38.1706 | 144.3423 | 1 | Powercor | Report | 17077 | 0.0050625 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
Attend site. No fire found on arrival. solated from HV TX switch and made safe.. Replaced LV panel. | 15 RIVER GUM AVENUE, BENALLA VIC 3672 | 3920472 |  | Animal | [5 empty] | E0020177 - LV fuse units melted. | Any other type | 0 | 0 | 0 |  | bn006 | rats nest inside the LV side of the kiosk substation cause LV fuses to melt. | Plant/equipment | 17/05/2019 20:10 | 1 | Negligible: no ground fire | 13683 |  |  | 20190520SPN_01 | Infrastructure (network-based) | -36.5602 | 145.9974 | 1 | AusNet Services Distribution | Report | 17778 | 0.039655 | Low voltage AC (<1kV) | Wangaratta Aero | 3672 | Benalla | Animal
Crossarm replaced | 2172 FIFTEENTH STREET, IRYMPLE VIC 3498 | 31021116 |  |  |  | Leakage |  |  |  | Vic fire reported pole fire at incident location | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire | 24/03/2019 2:48 | 1 | Negligible: no ground fire | 13709 | Roadway |  | 20190527PWA_02 | Infrastructure (network-based) | -34.2396 | 142.1755 | 1 | Powercor | Report | 17126 | 0.017336 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Crossarm replaced | 28 HANKINSON LANE, PIANGIL VIC 3597 | 32162865 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location | Crossarm (wood) | 2 | 2 | 2 |  | SHL002 | Excessive leakage current | Pole-top fire | 31/03/2019 8:15 | 1 | Negligible: no ground fire | 13711 | Roadway |  | 20190527PWA_03 | Infrastructure (network-based) | -35.0702 | 143.3354 | 1 | Powercor | Report | 17128 | 0.034811 | 22kV AC | Swan Hill Aerodrome | 3597 | Piangil | Crossarm
Crossarm replaced | 13 MURRAY VALLEY HIGHWAY, BOUNDARY BEND VIC 3599 | 32143607 |  |  |  | Leakage |  |  |  | Pole fire found at incident location | Crossarm (wood) | 2 | 2 | 2 |  | BBD021 | Excessive leakage current | Pole-top fire | 31/03/2019 15:06 | 1 | Negligible: no ground fire | 13712 | Roadway |  | 20190527PWA_04 | Infrastructure (network-based) | -34.7185 | 143.1496 | 1 | Powercor | Report | 17129 | 0.003647 | 22kV AC | Swan Hill Aerodrome | 3599 | Boundary Bend | Crossarm
Powercor crew isolated the Kiosk A fault follow-up was generated to replace the damaged Kiosk substation. | 1A BOBBORA COURT, TAYLORS LAKES VIC 3038 | 17978879 | [7 empty] | Customers and Fire Brigade reported BOBBORA-ADMIRALS 300kVA Kiosk on fire. LV switchboard end of the kiosk was burnt out internally. Fire brigade extinguished the fire. There was no ground fire, no reported injuries or third party property damage. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | SA003 | To be advised | Plant/equipment | 27/05/2019 21:52 | 1 | Negligible: no ground fire | 13721 | Public space |  | 20190528PWA_04 | Infrastructure (network-based) | -37.7086 | 144.7881 | 1 | Powercor | Notification | 17138 | 0.01712 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3038 | Taylors Lakes | UG Cable
On arrival crew confirmed isolation. Waiting on police to release the scene to allow asset assessment | 127 INDI AVENUE, RED CLIFFS VIC 3496 | 33105027 | Vehicle | [5 empty] | 1 | Police reported a vehicle has struck a pole at incident location with at least one fatality. Hv conductor dislodged and contacted crossarm. There was no fire, no injuries related to electricity, all assets remain in the air. | Pole (concrete) | 2 | 2 | 2 |  | RCT023 | Vehicle struck pole | Loss of supply;Damage to network assets | 27/05/2019 20:45 |  |  | 13722 | Roadway |  | 20190528PWA_05 | Infrastructure (network-based) | -34.3059 | 142.1961 | 1 | Powercor | Report | 17360 | 0.008897 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Vehicle
On arrival crew isolated supply and carried out repairs. | 40 ROCKFIELD WAY, RAVENHALL VIC 3023 | 30545291 | Vandalism;Copper theft | [6 empty] | Report of copper theft at incident location. Crew found damage and vandalism to 15 pits and 12 lights. Cable damaged but not removed. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | TNA011 | Attempted copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43742.5625 |  |  | 13723 | Roadway |  | 20190528PWA_06 | Infrastructure (network-based) | -37.7777 | 144.748 | 1 | Powercor | Report | 17141 | 0.00086921 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Ravenhall | Other
on arrival crew carried out repairs. | 47 SIMPSON STREET, BALLAN VIC 3342 | 32171912 | Working too close to underground cables | [6 empty] | BRG Drainage & Civil Earth Works, Ben Gleeson reported he has cut through an underground conduit at incident location. Supply is still on. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BMH003 | Using excavator struck LV conduit. | No Go Zone (contact);Damage to network assets | 43773.4299 |  |  | 13724 | Roadway |  | 20190528PWA_07 | Infrastructure (network-based) | -37.5991 | 144.2297 | 1 | Powercor | Report | 17142 | 0.025919 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3342 | Ballan | Dug up
Site made safe Resleeved white phase conductor and installed spreaders Reinstated broken bridges | 10 TUPPAL PLACE, KEILOR EAST VIC 3033 |  |  | Wind |  | Conductor clashing |  |  | 2 | Bare aluminium conductor steel-reinforced LV cable fell to ground due to windy conditions (wind gusts up to 65 km/hour) which caused conductor clashing | Conductor (bare);Aluminium;Steel;Dropper/bridge | 2 | 2 | 0 |  | AW07 | Windy conditions (gusts up to 65 km/hour) caused conductor clashing and resulted in bare conductors on the ground | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/05/2019 11:45 |  |  | 13734 | Roadway |  | 20190529JEM_01 | Infrastructure (network-based) | -37.7315 | 144.8629 | 1 | Jemena | Report | 17153 | 0.03164 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | Conductor
A Powercor crew attended and made the site safe. Repairs arranged. | 431-533 TROUPS ROAD S, TRUGANINA VIC 3029 | 33071976 | Copper theft | [6 empty] | A customer called to advise of stolen underground cable both within the Troups Rd road reserve and within private property at 431 Troups Rd South. Found evidence of the underground cables being dug up and cable stolen from the pole end to sheds on their property. There were no shocks, reported injuries or ground fire. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 20/04/2019 12:51 |  |  | 13728 | Roadway |  | 20190529PWA_04 | Infrastructure (network-based) | -37.7724 | 144.6637 | 1 | Powercor | Report | 17146 | 0.038461 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
A Powercor crew attended and made the site safe. | 2 SQUADRON ROAD, POINT COOK VIC 3030 | 30346226 | Vandalism;Copper theft | [6 empty] | Victoria Police reported LV pit lids tampered with and cables apparently stolen across several pits. The crew reported cable ends cut at 5 pits or more, west of Squadron Road, and a possible attempt at cable pull-out. There were no shocks, reported injuries or ground fire. | Services cable;Services pit | 2 | 2 | 2 |  | LV006 | Copper theft & vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/04/2019 9:01 |  |  | 13729 | Roadway |  | 20190529PWA_05 | Infrastructure (network-based) | -37.9112 | 144.7635 | 1 | Powercor | Report | 17148 | 0.025947 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
A Powercor crew attended and made the site safe. The attending Powercor crew were able to reconnect the cables at the NBN supply point. Arrangements made to replace lighting cables | 87 HARGRAVE AVENUE, POINT COOK VIC 3030 | 30311292 | Vandalism;Copper theft | [6 empty] | NBN Co. reported electrical cable exposed at an LV pit and that he can see an attempted cable theft at the pit on the corner of Featherbrook Drive & Hacketts Road next to a pole. There was no supply to NBN assets and the NBN meter display was blank. Powercor Fault crew attended the site and noted a greater zone of interference, damage and cable theft to Powercor LV assets along Hacketts Rd., between Featherbrook Drive and Hargrave Avenue to the north. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WBE013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/04/2019 14:39 |  |  | 13730 | Roadway |  | 20190529PWA_06 | Infrastructure (network-based) | -37.901 | 144.7161 | 1 | Powercor | Report | 17149 | 0.030751 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
The Powercor Fault crew attended and made the site safe. and carried out repairs. defect issued to customer to repair their damage. | 783 COBURNS ROAD, HARKNESS VIC 3337 | 32174296 | Copper theft | [6 empty] | REC for Melton City Council reported a theft of cables at an LV pit opposite Coburns Rd P58 substation in Toolern Vale There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | MLN014 | Copper theft | Damage to network assets | 22/04/2019 12:41 |  |  | 13731 | Roadway |  | 20190529PWA_07 | Infrastructure (network-based) | -37.6339 | 144.5731 | 1 | Powercor | Report | 17150 | 0.0083287 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Harkness | Other
On arrival crew isolated supply and carried out repairs. | 39 ARGYLL CIRCUIT, MELTON WEST VIC 3337 | 34006918 | Working too close to underground cables | [6 empty] | REC reported an underground service cable dug up at the incident location. Upon arrival the fault crew found that the cable had been damaged. There was no fire no reported injuries. | Services cable | 2 | 2 | 2 |  | MLN022 | Excavator contacted underground service cable. | No Go Zone (contact);Damage to network assets | 24/04/2019 10:35 |  |  | 13738 |  |  | 20190530PWA_04 | Infrastructure (network-based) | -37.6724 | 144.5602 | 1 | Powercor | Report | 17157 | 0.022269 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Dug up
Site made safe | 7 THORNYCROFT STREET, CAMPBELLFIELD VIC 3061 |  | Unauthorised access | [5 empty] | 2 | Crew attended the above address today with a supply outage for a new 3ph connection and direct meter. Please see attached photos (in Notes and FIndings section) of the unprotected consumers mains below the metering and SPD panel not buried to the correct depth and without suitable mechanical protection. Certificate of electrical safety and electrical works request also attached. REC and LEI details are recorded in the Other Information Sources section | Cable | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 20/11/2018 15:02 |  |  | 13755 | Residential |  | 20190531JEM_05 | Infrastructure (network-based) | -37.6469 | 144.9421 | 2 | Jemena | Report | 17175 | 0.02311 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Other
Site made safe | 9 ARNOLD COURT, PASCOE VALE VIC 3044 |  | Unauthorised access | [5 empty] | 2 | Our M&S crews attended the above address today with SOâ€™s to energise and meter 3 new units. Upon arrival they found suicide leads connected to the unit switchboard. Please see attached photos, EWRâ€™s and CESâ€™s in the Notes and FIndings section | Switchboard | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43263.7431 |  |  | 13756 | Residential |  | 20190531JEM_06 | Infrastructure (network-based) | -37.7218 | 144.934 | 2 | Jemena | Report | 17176 | 0.03436 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
There were two other Neutral screen overhead services connected to the small SEC Junction box servicing numbers 40 & 42 Linda St. It was confirmed that neither of these customers were life support customers and they were able to disconnect supply to the small SEC Junction box to disconnect and remove the unsafe neutral screen overhead service to 38 Linda St. They crews were then able to complete the new connection with a CES provided on site which appears to have been certified in March 2018. | 38 LINDA STREET, COBURG VIC 3058 |  | Unauthorised access | [5 empty] | 2 | Crews attended the above address today for a 9.30am truck appointment with a service order for an abolishment in conjunction with a new connection. Please see attached photos of the existing neutral screen overhead service to the property which was still connected at the pole into a small SEC junction box and was hanging energised and live at the customer point of attachment end. Compliance officer spoke to the REC Nick who advised the neutral overhead service was always like this when he arrived at the property and he installed PVC tape on the end of the live and exposed neutral screen cable. REC Nick also advised that he reported the unsafe service to Jemena Faults. Compliance officer called and spoke to Janette at Dispatch (Jemena Control Room) who advised she has nothing for that address, except a 5 day defect in 2017 for a vegetation issue. The crew also advised that the electricity meter was also missing from site. REC is Reddy Electrical Solutions, REC number 24746 Photos, COES and EWR are attached in Notes and Findings section | Service conductor;Neutral screen;Connection box | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 17/01/2019 10:47 |  |  | 13757 | Residential |  | 20190531JEM_07 | Infrastructure (network-based) | -37.7506 | 144.9594 | 1 | Jemena | Report | 17177 | 0.0055498 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
Site made safe | 7 PANDANUS COURT, HEIDELBERG WEST VIC 3081 |  | Unauthorised access | [5 empty] | 2 | M&S crew attended the above address today with a SO for an abolishment of service line and electricity meter 02247 (NMI 6001071968) When the crew arrived they found the site had been completely demolished including the electricity service line and meter. Abolishment form and photos are attached | Service conductor;Smart meter | 0 | 0 | 0 |  |  | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43649.3965 |  |  | 13770 | Residential |  | 20190531JEM_20 | Infrastructure (network-based) | -37.7445 | 145.0451 | 1 | Jemena | Report | 17190 | 0.03763 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg West | Other
fuse carrier replaced | 774 CHILDERS COVE ROAD, THE COVE VIC 3268 | 33105330 |  | Lightning |  | Fuse failed to eject |  |  | 2 | Vic Fire reports a pole fire at 784 Childers Cove Rd The Cove. Crew attended to find that EDO fuse on 22kV substation had mal-operated. | EDO fuse | 0 | 0 | 0 |  | WBL012 | Bird Incident | Pole-top fire | 29/05/2019 9:00 | 1 | Negligible: no ground fire | 13742 | Agricultural |  | 20190531PWA_03 | Infrastructure (network-based) | -38.4884 | 142.7011 | 1 | Powercor | Report | 17162 | 0.02549 | 22kV AC | Warrnambool Airport Ndb | 3268 | The Cove | Fuse
on arrival crew isolated supply and carried out repairs. | 2901 RAINBOW-NHILL ROAD, JEPARIT VIC 3423 | 32120285 |  |  |  | Leakage |  |  |  | Report received of a cross arm fire due to leakage current. Incident found during outage data review. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | NHL016 | Excessive leakage current | Pole-top fire | 14/12/2018 15:33 | 1 | Negligible: no ground fire | 13745 | Agricultural |  | 20190531PWA_06 | Infrastructure (network-based) | -36.0525 | 141.8397 | 1 | Powercor | Report | 17165 | 0.00050463 | 22kV AC | Horsham Aerodrome | 3423 | Jeparit | Crossarm
On arrival crew isolated supply and arranged repairs. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298012 | Vandalism;Copper theft | [6 empty] | a Powercor employee (Ardeer depo), reported exposed UG wires next to LIS 784381. Believe result of someone stealing the copper. Near intersection of Bulmans and Western Hwy. On arrival the Crew found that 5 service pits had been interfered with and the lights on 5 poles. The pit lids had been removed from the pit and live wires were exposed hanging out of the pits. The service cable had been cut and removed from every pit and approximately 250 meters of 16mm 4C cable was stolen. There was no fire and no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN022 | Copper theft | Damage to network assets | 27/03/2019 16:54 |  |  | 13749 | Roadway |  | 20190531PWA_08 | Infrastructure (network-based) | -37.6862 | 144.5495 | 1 | Powercor | Report | 17169 | 0.031284 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
On arrival crew isolated supply and carried out repairs. | 578 HUME DRIVE, FRASER RISE VIC 3336 | 30322077 | Vandalism;Copper theft | [6 empty] | Dominic from â€˜ZINFRAâ€™ advised that at Hume drive, near Galliber parade, 8-10 pit lids have been taken off and wires are exposed, hanging out of pits. New subdivision area. On arrival the Crew found that about 6 service pits had their concrete lids removed. One of the pits, near pole LIS-827981, had the wires hanging out and the service cable in this pit had been cut and attempted to be pulled out. IPC connectors were damaged. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | SA011 | Attempted copper theft and Vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/04/2019 16:08 |  |  | 13752 | Roadway |  | 20190531PWA_09 | Infrastructure (network-based) | -37.7114 | 144.7233 | 1 | Powercor | Report | 17172 | 0.016712 | Low voltage AC (<1kV) | Melbourne Airport | 3336 | Fraser Rise | Other
On arrival crew isolated supply and carried out repairs. | 610 DAVIS ROAD, TARNEIT VIC 3029 | 30103568 | Vandalism;Copper theft | [6 empty] | Mitch, (Powercor employee) reported to control room that UG pit has been vandalized. On arrival the Crew found that the service pit near poleLIS-214782, located on Davis rd, had been smashed and cables inside pit had been ripped out in an attempt to pull out the service cable. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | TNA023 | attempted copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 27/04/2019 12:48 |  |  | 13754 | Roadway |  | 20190531PWA_10 | Infrastructure (network-based) | -37.8146 | 144.6571 | 1 | Powercor | Report | 17174 | 0.0025961 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
HV underground isolated, and has been left isolated. | OLYMPIC VILLAGE PRIMARY, 152 SOUTHERN ROAD, HEIDELBERG WEST VIC 3081 |  | Working too close to underground cables | [5 empty] | 2 | During planned works, found damage to conduit and sheath of live HV underground cable Alamein Rd east side north of Southern Rd, boundary of Olympic Village Primary school that appears to been have caused by the installation of a new fence above the HV cable. Unsure as to date of damage. | Cable | 0 | 0 | 0 |  | NH05 | It appears that construction of fence post holes for replacement fence resulted in damage to underground cable conduit and sheath. | No Go Zone (contact);Damage to network assets | 43471.3785 |  |  | 13771 | Commercial |  | 20190601JEM_01 | Infrastructure (network-based) | -37.7413 | 145.0418 | 1 | Jemena | Report | 17191 | 0.034897 | 22kV AC | Essendon Airport | 3081 | Heidelberg West | Dug up
On arrival crew isolated supply and carried our repairs. | 248 MURCHISON-LONGWOOD ROAD, WAHRING VIC 3608 | 30131754 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer reported that he has hit a power pole at the incident location. Upon arrival, the fault crew found that a tractor hit the pole and the pole and conductors on the ground. There was no fire or reported injuries. | Pole (wood) | 2 | 2 | 2 |  | MNA034 | Tractor collided with pole during agricultural work | Damage to network assets | 43682.5597 |  |  | 13780 |  |  | 20190603PWA_09 | Infrastructure (network-based) | -36.6859 | 145.295 | 1 | Powercor | Report | 17203 | 0.028619 | 12.7kV AC (SWER) | Mangalore Airport | 3608 | Wahring | Vehicle
On arrival crew isolated supply and commenced repairs. Driver transported to hospital by ambulance | 83 CROCKFORD STREET, PORT MELBOURNE VIC 3207 | 30205533 | Vehicle | [6 empty] | Emergency Services reports a car into a pole at the incident location. Emergency Services mention that pole was down and (LV) wires were down, and that they saw sparks when lines were down. Pole was resting on top of the car. There was no fire. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | MG001 | Vehicle struck pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43743.6792 |  |  | 13782 | Roadway |  | 20190603PWA_11 | Infrastructure (network-based) | -37.834 | 144.949 | 1 | CitiPower | Report | 17205 | 0.03323 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Vehicle
On arrival crew isolated supply and carried out repairs. | 10 MODAL PLACE, ALTONA VIC 3018 | 30231426 | Vandalism;Copper theft | [6 empty] | Crew reported 3 pits that have been vanadalised near LIS numbers 989354, 989353 & 989352. Neutral & Active also cut, cables feeding street lights stolen. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | LVN022 | Copper theft and vandalism | Damage to network assets | 14/05/2019 12:19 |  |  | 13789 | Roadway |  | 20190604PWA_03 | Infrastructure (network-based) | -37.8507 | 144.7922 | 1 | Powercor | Report | 17212 | 0.025375 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
On arrival crew isolated supply and carried out repairs. | STATION ROAD, NEW GISBORNE VIC 3438 | 30338646 | Vandalism;Copper theft | [6 empty] | PAL employee reported street light has the pit open on roundabout, southbound side when coming off freeway heading towards Melbourne, cables hanging out, closest LIS 845128, street lights not working. Crew found copper theft at incident location, made safe. Note: Copper theft had previously been reported at this location on Friday 10th May 2019, | Services cable;Services pit | 2 | 2 | 2 |  | GSB013 | copper theft and vandalism | Damage to network assets | 14/05/2019 19:00 |  |  | 13791 | Roadway |  | 20190604PWA_04 | Infrastructure (network-based) | -37.4719 | 144.5921 | 1 | Powercor | Report | 17214 | 0.019703 | Low voltage AC (<1kV) | Melbourne Airport | 3438 | New Gisborne | Other
On arrival crew isolated supply and carried out repairs. | 27-29 MORLEY AVENUE, WYE RIVER VIC 3234 | 30055580 | Working too close to underground cables | [6 empty] | A builder reported an UG service dug up at the incident location. Upon arrival, the crew found that the UG service had been dug up. There was no fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | CLC013 | Excavator struck underground service line. | Damage to network assets | 16/05/2019 9:15 |  |  | 13792 | Roadway |  | 20190604PWA_05 | Infrastructure (network-based) | -38.6381 | 143.8909 | 1 | Powercor | Report | 17215 | 0.0065856 | Low voltage AC (<1kV) | Avalon Airport | 3234 | Wye River | Dug up
On arrival crew isolated supply and carried out repairs. | 83-105 ABEY ROAD, COBBLEBANK VIC 3338 | 30336489 | Vandalism;Copper theft | [6 empty] | Passerby notified that pits at incident location are exposed with lids off. Approximately 235m of 4c 16mm LV Service Cable has been cut away and stolen from the LV Service Pit at PL Lighting Pole LIS-842962, Abey Rd heading east to LV Service Pit at PL Lighting Pole LIS-842966 The crew advised that the LV cables at the LV Service Pit at PL LIS-842962 had Live LV tails laying on the ground. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN011 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 20/05/2019 20:26 |  |  | 13804 | Roadway |  | 20190605PWA_07 | Infrastructure (network-based) | -37.7047 | 144.5888 | 1 | Powercor | Report | 17363 | 0.028003 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
On arrival crew isolated supply and carried out repairs. | 783 COBURNS ROAD, HARKNESS VIC 3337 | 32174296 | Copper theft | [6 empty] | MELTON CITY COUNCIL, REC Bruce reported underground cables from underground pit to meter have been ripped up/stolen, been vandalized with wires exposed and copper has been taken. Note: There has been a minimum of 4 similar incidents at this site over the past 6 months. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN032 | Copper theft | Damage to network assets | 21/05/2019 12:21 |  |  | 13805 | Roadway |  | 20190605PWA_08 | Infrastructure (network-based) | -37.6339 | 144.5731 | 1 | Powercor | Report | 17228 | 0.0044699 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Harkness | Other
Crew isolated supply and issued defect for customer repairs. | 94-118 GREIGS ROAD, TRUGANINA VIC 3029 | 32167989 | Vandalism;Copper theft | [6 empty] | Owner reports power lost. Energy Meter, Serial number 6118139 at front of house and customer mains stolen. Crew arrived to find meter had been removed from front of house, house had been burgled and many items within stolen. Melton Police notified, | Services cable;Smart meter | 2 | 2 | 2 |  | MLN021 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/05/2019 10:30 |  |  | 13806 | Roadway |  | 20190605PWA_09 | Infrastructure (network-based) | -37.7461 | 144.6805 | 1 | Powercor | Report | 17229 | 0.016351 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Under review, applicant requested to advice on status of relocation/retirement options. | 9 OSMENT STREET, ARMADALE VIC 3143 | 30165196 | Building too close or within the No Go Zone | [5 empty] | 2 | A rail signal gantry was found to have been installed over a section of insulated service cable between poles. A permit to work had previously been issued to metro trains for a mobile crane to operate in the vicinity of the cable. The gantry work site related to Metro Rail Tunnel Project. | Service conductor | 0 | 0 | 0 |  | AR004 | structure erected near line | No Go Zone (no contact) | 23/05/2019 8:30 |  |  | 13807 | Other | railway corridor | 20190605PWA_10 | Infrastructure (network-based) | -37.8528 | 145.0156 | 1 | CitiPower | Report | 17333 | 0.0079931 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | Other
Powercor Side / cables have had no damage, pits made safe and meter boards tested. Defect notices issued and left in meter board. | 48 AMBASSADOR CRESCENT, POINT COOK VIC 3030 | 30546606 | Vandalism;Copper theft | [6 empty] | Job dispatched to Crew due to a number of Power-downs in the area - there were no customer calls. Area affected is a residential URD Estate, with homes currently under construction. Upon arrival the PCA Field Crew have advised, that an unknown person has opened up the Service Pits and Cut the customer mains cable on the load side of the IPC's and preceeded to the MSB and cut the other end of the cable. There was no fire or reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WBE013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/05/2019 20:51 |  |  | 13808 | Roadway |  | 20190605PWA_11 | Infrastructure (network-based) | -37.8845 | 144.71 | 1 | Powercor | Report | 17231 | 0.0061192 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Repairs completed | 39 GREVILLEA ROAD, KINGS PARK VIC 3021 | 30150045 | Vandalism | [6 empty] | A Powercor crew found that the earthing of remote gas switch at the incident location had been cut. However no cable had been taken away. There was no fire, no reported injuries. | Earth/earthing | 2 | 2 | 2 |  | SA009 | Vandalism | Damage to network assets | 23/05/2019 13:09 |  |  | 13809 | Roadway |  | 20190605PWA_12 | Infrastructure (network-based) | -37.7294 | 144.7767 | 1 | Powercor | Report | 17232 | 0.025581 | Earthing cable | Melbourne Airport | 3021 | Kings Park | Other
Site made safe | 2 OLD RIDDELL ROAD, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Stolen street light cable | Cable | 0 | 0 | 0 |  |  | Person unknown stole copper | Damage to network assets | 43622.384 |  |  | 13819 | Roadway |  | 20190606JEM_01 | Infrastructure (network-based) | -37.5555 | 144.7012 | 1 | Jemena | Report | 17248 | 0.027375 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew isolated supply and carried out repairs. | REMLAW STATION ROAD, VECTIS VIC 3401 | 32090809 |  |  |  | Leakage |  |  |  | Customer reported loss of supply and wire down near their place, on arrival the work crew found a pole fire had occurred resulting in the top of the pole burning off and the conductors fell to the ground. There was a small ground fire 1m sq. There was no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | HSM006 | Excessive leakage current | Pole-top fire;Grassfire | 43591.2014 | 1 | Localised: less than 10 sq.m | 13813 | Roadway |  | 20190606PWA_01 | Infrastructure (network-based) | -36.661 | 142.1168 | 1 | Powercor | Report | 17237 | 0.041603 | 22kV AC | Horsham Aerodrome | 3401 | Vectis | Pole
The site was made safe, and repairs are to be carried out. | 462 MORRIS ROAD, TRUGANINA VIC 3029 | 30287966 | Vandalism;Copper theft | [6 empty] | A public lighting fault crew attended the incident location due to the street lights being out. On arrival they discovered that unknown persons had stolen the copper underground cable between the following pits: 744887, 782473, 782474, 782475 & 782476. There were no reported injuries or fires, and the matter was reported to the Police. | Services cable;Services pit | 2 | 2 | 2 |  | TNA013 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43591.525 |  |  | 13843 | Roadway |  | 20190611PWA_03 | Infrastructure (network-based) | -37.841 | 144.7081 | 1 | Powercor | Report | 17276 | 0.0091562 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Other
Police attended the site as a shovel was left at the gate. Crew secured the live mains by fitting new pit connectors allowing for reconnection of supply when new consumer mains replaced | 5 KRONKS LANE, WOODEND NORTH VIC 3442 | 30354464 | Vandalism;Copper theft | [6 empty] | Customer reported copper Theft. Copper cables were cut at the pit connectors and live Powercor underground cable mains left alive. Metering cabinet had been broken into and mains stripped out of the conduit. This site has been vandalized/theft a number of times now. There was no fire and no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | WND023 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43622.0806 |  |  | 13844 | Roadway |  | 20190611PWA_04 | Infrastructure (network-based) | -37.3228 | 144.5244 | 1 | Powercor | Report | 17277 | 0.014485 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend North | Other
On arrival crew isolated supply and organised repairs. | 140 STATION ROAD, NEW GISBORNE VIC 3438 | 30338649 | Copper theft | [6 empty] | Powercor employee reported repeat copper theft from PL circuits on both south bound & north bound on ramps to the Calder Hwy at Gisborne. U/G cable theft between lis 845137 & 845141 south bound on ramp U/G cable theft between lis 845161 & 845163 North bound on ramp" Approximately 200M of 16mm Cu cable was stolen from the 2 neighbouring locations, the north bound section has now been targeted on 4 occasions. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | GSB013 | Copper theft | Damage to network assets | 43622.6771 |  |  | 13846 | Roadway |  | 20190611PWA_05 | Infrastructure (network-based) | -37.4727 | 144.5941 | 1 | Powercor | Report | 17280 | 0.040775 | Low voltage AC (<1kV) | Melbourne Airport | 3438 | New Gisborne | Other
On arrival crew isolated supply and carried out repairs. | 12 BEECH STREET, CAMBERWELL VIC 3124 | 10757150 | Working too close to underground cables | [6 empty] | Contractor (Envision Homes PTY LTD) reported hitting an underground cable and damaging it. On arrival, the crew found an Low Voltage service cable (pole to pit) had been hit and damaged due to customer excavations. There was no ground fire, no third party damaged and no reported injuries. | Services cable | 2 | 2 | 2 |  | RD001 | Excavator hit the LV underground service cable | No Go Zone (contact);Damage to network assets | 43622.6118 |  |  | 13847 | Roadway |  | 20190611PWA_06 | Infrastructure (network-based) | -37.8412 | 145.0857 | 1 | CitiPower | Report | 17281 | 0.019958 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Dug up
Fault crew dispatched and confirmed tree clearers have dropped a tree onto O/H HV conductors. Tree Clearers still on site and no injuries sustained. The operator ceased work and notified Ausnet of the incident and waited onsite until the fault crew attended. Repairs carried out to straighten pole, install new stay and re-string conductors. | OMEO HIGHWAY, OMEO VIC 3896 | LIS1605774 | Working too close to overhead lines | Within clearances | [5 empty] | E0021140 - Tree Clearer contacted AusNet advising a tree has fallen onto HV wires in the street. Fault crew dispatched and confirmed tree clearers have dropped a tree onto O/H HV conductors. The impact has resulted in the stay wire breaking and has subsequently lead to the pole leaning. | Conductor (bare) | 0 | 0 | 0 |  | BDL8 | Vegetation: Trees Incident | No Go Zone (contact) | 43775.4028 |  |  | 13845 | Agricultural |  | 20190611SPN_03 | Infrastructure (network-based) | -37.0614 | 147.6015 | 2 | AusNet Services Distribution | Report | 17279 | 0.011711 | 22kV AC | Bairnsdale Airport | 3896 | Omeo | Other
On arrival crew carried out repairs | 2 KILSYTH AVENUE, TOORAK VIC 3142 | 30162022 | Working too close to underground cables | [6 empty] | MRS STEPHANIE SCHALKEN, Stephanie advised there were workman working on footpath out the front of her property this morning when power went out. She's not sure who they were working for but they have left. She did approach them & adv her power had gone out. Adrian of Citywide Electrical (0419145658) Called to report on behalf of Colin on site (0429227277). Believes that wires have been cut into/stolen from electrical pit at the address, and wires are exposed. Lid is currently on pit, On arrival crew found that Contractor cut into low voltage underground cable with a demolition saw. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit | 2 | 2 | 2 |  | TK014 | contractor using demolition saw cut cable | Loss of supply;Damage to network assets | 43775.4167 |  |  | 13855 | Roadway |  | 20190612PWA_05 | Infrastructure (network-based) | -37.8415 | 145.0118 | 1 | CitiPower | Report | 17291 | 0.018753 | Low voltage AC (<1kV) | Essendon Airport | 3142 | Toorak | Other
New earth to be installed on pole. | 1-7 CHIFLEY DRIVE, PRESTON VIC 3072 |  | Copper theft | [5 empty] | 2 | Unknown person stole copper from pole no. A078691 | Earth/earthing | 0 | 0 | 0 |  | EP07 | Unknown person stole copper | Damage to network assets | 13/06/2019 8:00 |  |  | 13880 | Roadway |  | 20190613JEM_01 | Infrastructure (network-based) | -37.755 | 145.0286 | 1 | Jemena | Report | 17319 | 0.027791 | 6.6kV AC | Essendon Airport | 3072 | Preston | Other
Isolated and made safe. Replaced damaged Jemena assets (copper underground cable) | 65 BARRYMORE ROAD, GREENVALE VIC 3059 |  | Theft | [5 empty] | 2 | Copper theft of streetlight LV underground cable Barrymore Rd Greenvale. | Services cable | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 13/06/2019 15:00 |  |  | 13892 | Roadway |  | 20190613JEM_02 | Infrastructure (network-based) | -37.6518 | 144.9005 | 1 | Jemena | Report | 17334 | 0.028177 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
Site made safe. Crew performed repairs. | 269 BELAR AVENUE, IRYMPLE VIC 3498 | 30099314 |  |  |  | Leakage |  |  |  | Cross arm fire due to leakage current. Incident found during outage data review. No ground fire | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire | 43385.741 | 1 | Negligible: no ground fire | 13879 | Agricultural |  | 20190613PWA_09 | Infrastructure (network-based) | -34.2474 | 142.196 | 1 | Powercor | Report | 17317 | 0.027584 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Crew made site safe and performed repairs. | 242 LATROBE TERRACE, GEELONG WEST VIC 3218 | 30069174 |  |  |  | Leakage |  |  |  | Cross arm fire due to leakage current. Incident found during outage data review. No ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | GCY014 | Excessive leakage current | Pole-top fire | 16/12/2018 8:15 | 1 | Negligible: no ground fire | 13883 | Roadway |  | 20190613PWA_12 | Infrastructure (network-based) | -38.1466 | 144.3527 | 1 | Powercor | Report | 17322 | 0.03766 | 22kV AC | Avalon Airport | 3218 | Geelong West | Crossarm
Crew made site safe. Repaired damage. | 12 FIRST AVENUE, ST LEONARDS VIC 3223 | 32087947 |  |  |  | Overheated connection |  |  |  | Transformer LV isolator burnt off causing small burn marks at base of pole. Incident found during outage data review. Small ground fire 0.1 sqm | Disconnector/isolator | 2 | 2 | 2 |  | DDL013 | connection failure | Grassfire | 31/12/2018 12:45 | 1 | Localised: less than 10 sq.m | 13887 | Roadway |  | 20190613PWA_14 | Infrastructure (network-based) | -38.1683 | 144.7159 | 1 | Powercor | Report | 17326 | 0.012763 | Low voltage AC (<1kV) | Avalon Airport | 3223 | St Leonards | Connection
On arrival crew replaced fuse. | 170 GIRGARRE EAST ROAD, TATURA VIC 3616 | 33088618 |  |  |  | Candled fuse |  |  |  | Customer reports sparking from pole top. On arrival crew found that a boric acid fuse had hung up and was candling. There was no ground fire, no reported injuries or third party property damage. Event found during outage data review. | Boric acid | 2 | 2 | 2 |  | MNA021 | Corrosion | Pole-top fire | 43556.8278 | 1 | Negligible: no ground fire | 13888 | Roadway |  | 20190613PWA_15 | Infrastructure (network-based) | -36.4547 | 145.2033 | 1 | Powercor | Report | 17622 | 0.020598 | 22kV AC | Shepparton Airport | 3616 | Tatura | Fuse
UE contractor attended with the Police. Supply to the premise was disconnected in the service pit, and a defect notice issued on the premise. | 13 SUNFLOWER COURT, KEYSBOROUGH VIC 3173 |  | Vandalism;Theft;Unauthorised work | [6 empty] | UE received advice of illegal wiring at a "crop house" in Keysborough. | Services pit;Smart meter;No failed asset;Meter board (including fuses);Customer installation | 2 | 2 | 2 |  |  | The cause was wilful tamp[erring with UE service assets fro the purpose of running a crop house. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43502.7083 |  |  | 13886 | Residential |  | 20190613UTD_02 | Infrastructure (network-based) | -38.0038 | 145.1637 | 1 | United Energy Distribution | Report | 17325 | 0.016277 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Other
The asset inspector reported the shock to his supervisor who reported to UE control room. A fault crew was dispatched in conjunction with an EIO to investigate. The EIO took voltage measurements using an independent earth. 0.2VAC measured on the concrete pole and pole guard and surrounds. 13VAC measured on the Solid blue conductor within the two pair telco cable. 92VAC measured on the Solid Orange cable within the two pair telco cable. The fault crew followed the cable back to its source, a Telco connection box located just above. Tests on the earthed telco support line had 0.2VAC and no other signs of a cause at that point. The fault crew made the end of the cable safe enough to coil up and attached to the telco line out of the reach of the public. The telecommunications company was notified and requested to identify the issue and isolate the cable. | 15 MALABAR ROAD, BLACKBURN VIC 3130 | 7039117 |  |  |  | Fault on customer installation |  | Phase to earth | 2 | An Asset Inspector was undertaking an inspection of a UE concrete pole that had a telecommunication cable left wrapped around the pole. In order to take a photo of the LIS number, the inspector moved the telecommunications cable and received a shock to his right forearm. The inspector then checked the two paired cable with a LV5 tester and the cable sparked as the metal tip touched the two pairs. | Customer installation | 2 | 2 | 2 |  |  | The cause of why the telecommunications cable was live at 92V has not been determined. | Minor shock | 43530.4861 |  |  | 13889 | Roadway |  | 20190613UTD_03 | Infrastructure (network-based) | -37.8174 | 145.1408 | 1 | United Energy Distribution | Report | 17342 | 0.0043704 | Low voltage AC (<1kV) | Moorabbin Airport | 3130 | Blackburn | AF Other
A fault crew was dispatched to undertake repairs to the LV mains conductors. In addition, a No Go Zone officer also attended the site to initiate No Go Zone processes. Prior to this incident, there were no No Go Zone requests received for this site. | 48A ELWERS ROAD, ROSEBUD VIC 3939 |  | Working too close to overhead lines |  |  |  |  | Phase to phase |  | UE received a report of a crane contacting live low voltage overhead conductors while unloading steel girders from the back of a truck. The truck mounted crane made contact with the white and blue phase low voltage conductors resulting in the white phase being burnt to the ground. No injuries were sustained through this incident. | Conductor (bare) | 0 | 0 | 0 |  |  | The cause of the incident was the unloading of material from a truck located under live bare Low Voltage conductors. The No Go Zone was not applied by the building site. | Loss of supply;Damage to network assets | 43775.4583 |  |  | 13891 | Construction |  | 20190613UTD_05 | Infrastructure (network-based) | -38.3598 | 144.9181 | 1 | United Energy Distribution | Report | 17330 | 0.012557 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Vehicle
The Powercor crew made the site safe, disconnected the supply at the service pit and left a defect notice in the meter box. | 39 LANCASHIRE DRIVE, WERRIBEE VIC 3030 | 30546457 | Vandalism;Copper theft | [6 empty] | Customer reported to Powercor control room that someone has cut behind the meter of property #39 on Lancashire drive Werribee which has resulted in a live meter/consumer mains. The Powercor Crew found that the meter at the incident location have been vandalised and the consumer mains have been cut at the meter box in an attempt to steal the cable.. The crew advised that the cable was live and require to be repaired and reconnected in the meter box.. There was no fire, nor reported injuries | Services cable;Services pit;Customer installation | 2 | 2 | 2 |  | WBE031 | Attempted copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43775.6181 |  |  | 13893 | Residential |  | 20190614PWA_01 | Infrastructure (network-based) | -37.9127 | 144.6081 | 1 | Powercor | Report | 17335 | 0.0015822 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Other
Area isolated, pole replaced supply restored. | 195 CRAWFORDS ROAD, WERRIBEE SOUTH VIC 3030 | 30111980 | Crane, excavator or other construction/farming equipment | [6 empty] | Reports farmer has hit a pole. Pole snapped at the base and leaning. Crew arrived to find wires on the ground and pole broken at its base. Farmer received minor bump injury (non electrical ) during the incident and left site to seek medical assistance. There was no fire. | Pole (wood) | 2 | 2 | 2 |  | WBE034 | Vehicle struck power pole | Damage to network assets | 43775.4306 |  |  | 13894 | Agricultural |  | 20190614PWA_02 | Infrastructure (network-based) | -37.9503 | 144.718 | 1 | Powercor | Report | 17336 | 0.0054363 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Vehicle
Fault crew dispatched and candled HV EDO Fuse replaced. | 21 KALIMNA JETTY ROAD, KALIMNA VIC 3909 | LIS1901592 |  |  |  | Candled fuse |  |  |  | E0021472 - report of candled fuse | EDO fuse | 0 | 0 | 0 |  | BDL6 | Candled EDO HV Fuse. No evidence of ground fire | Pole-top fire | 43561.7132 | 1 | Negligible: no ground fire | 13904 |  |  | 20190618SPN_02 | Infrastructure (network-based) | -37.8779 | 147.9582 | 2 | AusNet Services Distribution | Report | 17350 | 0.013348 | 22kV AC | Bairnsdale Airport | 3909 | Kalimna | Fuse
Made safe | 45 BUCKLAND WAY, SUNBURY VIC 3429 |  | Copper theft | [5 empty] | 2 | Unknown person stole copper from transformer and customer | Cable | 0 | 0 | 0 |  |  | Copper theft | Damage to network assets | 18/06/2019 16:50 |  |  | 13907 | Public space |  | 20190619JEM_02 | Infrastructure (network-based) | -37.609 | 144.7233 | 1 | Jemena | Report | 17353 | 0.0048634 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Kiosk substation and transformer isolated and earthed to make safe, then replaced | 125 BUNTING ROAD, BROOKLYN VIC 3012 |  | Vehicle |  |  |  |  | Three phase | 1 | Customer excavator which was in "traveling mode" contacted external cabinet of kiosk substation, moving frame and causing flashover on LV bus (see Trouble Event 182050) This is not considered a No Go Zone infringement or breach as the excavator was not in "working mode" | Pad mounted equipment/kiosk | 1 | 1 | 0 |  | TH21 | Excavator reversed into Kiosk-type substation pushing frame and damaging LV bus. | Loss of supply;Damage to network assets | 20/06/2019 14:00 |  |  | 13909 | Industrial |  | 20190621JEM_01 | Infrastructure (network-based) | -37.8112 | 144.8404 | 1 | Jemena | Report | 17383 | 0.0087396 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Vehicle
On arrival crew isolated supply and repairs undertaken | 110 EVANS ROAD, LOVELY BANKS VIC 3213 | 31011781 |  |  |  | Overheated connection |  |  |  | Vicfire & customer reported a pole fire at the incident location. When crews arrived they found a FOLCB located on the pole had caught on fire. Molten plastic and hot debris had dropped into the cable guard below resulting in a secondary fire start to the enclosed customer conduit and cable. No ground fire start found or injuries reported. | Services cable;Connection box | 2 | 2 | 2 |  | CRO022 | Insufficient remains to determine cause | Pole-top fire | 22/06/2019 17:03 | 1 | Negligible: no ground fire | 13910 | Roadway |  | 20190624PWA_01 | Infrastructure (network-based) | -38.0739 | 144.309 | 1 | Powercor | Report | 17384 | 0.013562 | Low voltage AC (<1kV) | Avalon Airport | 3213 | Lovely Banks | Connection
LEI identified splash-marks on the white and blue phases of the LV cables and a meter that required replacement at 100 Reigate Road Highton, no further damage was identified. | 100 REIGATE ROAD, HIGHTON VIC 3216 | 32081901 | Working too close to overhead lines | [6 empty] | Crew advised LV outage caused by private tree cutters dropping branch on to LV conductors, causing clashing, now some customers are having issues. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | WPD011 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact);Damage to network assets | 21/06/2019 9:21 |  |  | 13911 | Roadway |  | 20190624PWA_02 | Infrastructure (network-based) | -38.1602 | 144.3184 | 1 | Powercor | Report | 17385 | 0.0082014 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Other
Crew performed a controlled outage, replaced cross arm and restored supply | 3573 GEELONG-BACCHUS MARSH ROAD, PARWAN VIC 3340 | 32163946 |  |  |  | Leakage |  |  |  | An employee reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. There was no ground fire. There were no reported injuries or third party property damages. | Crossarm (wood) | 2 | 2 | 2 |  | BMH006 | Excessive leakage current cause crossarm fire | Pole-top fire | 18/06/2019 8:44 | 1 | Negligible: no ground fire | 13913 |  |  | 20190624PWA_04 | Infrastructure (network-based) | -37.7682 | 144.4399 | 1 | Powercor | Report | 17387 | 0.025546 | 22kV AC | Avalon Airport | 3573 | Parwan | Crossarm
On arrival crew isolated supply and carried out repairs | 22 ALBERT STREET, BRUNSWICK EAST VIC 3057 | 30160363 |  |  |  | Age |  |  |  | Customers reported LV conductor on ground and drapped across car. On arrival crew found broken conductor at incident site. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | C028 | most likely cause attributed to embrittlement due to work hardening of the copper, and as such is a random failure. | Loss of supply | 25/06/2019 18:23 |  |  | 13922 | Roadway |  | 20190627PWA_01 | Infrastructure (network-based) | -37.7707 | 144.979 | 1 | CitiPower | Report | 17399 | 0.028035 | Low voltage AC (<1kV) | Essendon Airport | 3057 | Brunswick East | Conductor
On arrival crew isolated supply and carried out repairs. | 28 NANGILOC CRESCENT, WERRIBEE VIC 3030 | 60071893 |  |  |  | Corrosion |  |  |  | Vic Fire reported pillar on fire, On arrival crew found LV pillar had been on fire which was extinguished by CFA. No reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | WBE024 | Overheated connection | Grassfire;Plant/equipment | 26/06/2019 9:36 | 1 | Localised: less than 10 sq.m | 13923 | Roadway |  | 20190627PWA_02 | Infrastructure (network-based) | -37.9119 | 144.6673 | 1 | Powercor | Report | 17400 | 0.029219 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
CFA attended and extinguished the fire. Powercor Fault Crew attended, isolated the electricity supply to make safe before they then made repairs and restored supply | Unnamed Road, Minimay VIC 3413, Australia | 30086961 |  |  |  | Leakage |  |  |  | Vic Fire reported that powerlines that started a grass fire at the incident location. On arrival the fault crew found that approx. 40cm had burned off the top of a SWER pole, allowing the conductor to drop into the scrub in the span below, igniting a fire in that scrub. The burned area was contained within the scrubland reserve on the southern fringe of the Little Desert National Park, and was estimated by CFA to be in the order of 1.6 hectares There was no injuries. | Conductor (bare);Pole (wood);Insulators | 2 | 2 | 2 |  | HSM004 | Excessive leakage current | Grassfire | 25/11/2019 16:48 | 1 | Medium: 1000 sq.m - 10 ha | 14541 | Agricultural |  | 20191127PWA_01 | Infrastructure (network-based) | -36.6477 | 141.2623 | 1 | Powercor | Report | 18335 | 0.0016285 | 12.7kV AC (SWER) | Horsham Aerodrome | 3413 | Minimay | Pole
Fault crews arrived at site and it was made safe. Upon inspection, a branch from a large tree had fallen onto the HV conductors which caused it to clash with the LV and created a HVI. EIO arrived on site and confirmed the HVI. Fault crews repaired the pole and conductors and supply was restored. | 73 PARK ROAD, CHELTENHAM VIC 3192 | 1822074 |  | Wind;Fallen |  |  |  |  | 1 | During a high wind event, UE received a call from customer that there was a loud bang outside this address and UE protection operated on the feeder supplying this area. | Conductor (bare) | 0 | 0 | 0 |  | CM13 | Vegetation: Trees Incident | HV injection | 21/11/2019 9:55 |  |  | 14546 | Roadway |  | 20191127UTD_03 | Infrastructure (network-based) | -37.964 | 145.0451 | 1 | United Energy Distribution | Report | 18342 | 0.017052 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3192 | Cheltenham | Trees
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole, resulting in a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Service Neutral connection in the Pole Top Connection Box at the Reticulation Pole with an IPC and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 22 MCGENNAN STREET, WARRNAMBOOL VIC 3280 | 33098870 |  |  |  | Corrosion |  | Phase to earth |  | Mr Harry Lee had noticed lights dimming and appliances not working correctly and proceeded to the Main Switchboard and Meter Enclosure to investigate. Mr Lee received an electric shock when he contacted the metal Meter Enclosure with his hand whilst standing on the wet ground. | Connection box | 2 | 2 | 2 |  | WBL004 | Corroded connection in junction box | Minor shock | 43716.7083 |  |  | 14551 | Roadway |  | 20191128PWA_02 | Infrastructure (network-based) | -38.3885 | 142.4665 | 1 | Powercor | Report | 18347 | 0.0056319 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
On arrival supply isolated and repairs carried out. | 151 Campbell Ave, Irymple VIC 3498, Australia | 32151419 |  |  |  | Leakage |  |  |  | CFA called to advise pole fire and wire down at the incident location. Crew arrived and found HV cross arm was burning and part of cross arm had burnt out, dropping HV insulator and line to the ground. CFA and Police in attendance. Cable was still sparking due to backfeed. There was a small ground fire (1 mtr), no reported injuries or third party property damage. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire;Grassfire | 30/11/2019 7:27 | 1 | Localised: less than 10 sq.m | 14571 | Roadway |  | 20191202PWA_03 | Infrastructure (network-based) | -34.2728 | 142.199 | 1 | Powercor | Report | 18370 | 0.039014 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Crew assess the condition of HV Stay pole. Access to pole was limited due to other Services doing investigation so crew will return later to assess and replace the pole. | Balwyn Rd, Balwyn North VIC 3104, Australia | 30295060 | Vehicle | [6 empty] | MFB reported a vehicle had hit HV stay pole at the above incident location. On arrival, the crew found the HV stay pole had cracked at the ground level of the pole due to the heavy vehicle contact. Crew advised by emergency services that the person driving the car was deceased. These was no ground fire. | Pole (wood) | 2 | 2 | 2 |  | WD011 | Vehicle collided with aerial stay pole | Damage to network assets | 30/11/2019 20:39 |  |  | 14573 | Roadway |  | 20191202PWA_05 | Infrastructure (network-based) | -37.7815 | 145.0873 | 1 | CitiPower | Report | 18372 | 0.035706 | Not applicable | Essendon Airport | 3104 | Balwyn North | Vehicle
Fault crews attended the site and the site was made safe. Upon inspection, the junction box installed on the pole was burnt out. The junction box was replaced and supply was restored. | 18 GREENDALE ROAD, BENTLEIGH EAST VIC 3165 | 1801649 |  |  |  | Overheated connection |  |  | 1 | UE received a call for a pole fire and were advised that MFB were onsite. | Connection box | 0 | 0 | 0 |  | CDA24 | The cause was a poor connection in the junction box. | Plant/equipment | 18/11/2019 0:05 | 1 | Negligible: no ground fire | 14580 | Roadway |  | 20191203UTD_03 | Infrastructure (network-based) | -37.9278 | 145.0688 | 1 | United Energy Distribution | Report | 18379 | 0.013881 | 22kV AC | Moorabbin Airport | 3165 | Bentleigh East | Connection
On arrival crew isolated supply and carried out repairs. LEI inspected for HVI - Non found | 62 Moonah St, Red Cliffs VIC 3496, Australia | 32153101 |  |  |  | Leakage |  |  |  | CFA reported pole fire at above address. When crew arrived, they found a cross arm that had burnt and conductors that had fallen onto LV. Closer inspection showed damage to LV and HV insulators. LEI could find no evidence of property damage. There was no ground fire, no injuries or property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 30/11/2019 8:53 | 1 | Negligible: no ground fire | 14582 | Roadway |  | 20191204PWA_01 | Infrastructure (network-based) | -34.2909 | 142.1792 | 1 | Powercor | Report | 18603 | 0.040289 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
On arrival crew inspected assets, all found servicable. | 2094 Curr Rd, Tongala VIC 3621, Australia | 30128199 | Unknown external/community factor | [5 empty] | 2 | CFA reported a grass fire at the incident location. On arrival, a Powercor crew found that a ground fire about 15*60Sqm area. Scorch marks on the pole base up to 1.5m There was no electrical cause found for the fire and no protection operations. The cause of fire has not been found. | Pole (wood) | 2 | 2 | 2 |  | KYM004 | No electrical cause found | Grassfire | 29/11/2019 14:58 | 0 | Small: 10 - 1000 sq.m | 14584 | Roadway |  | 20191204PWA_03 | Infrastructure (network-based) | -36.2538 | 144.9814 | 1 | Powercor | Report | 18391 | 0.0039097 | Not applicable | Shepparton Airport | 3621 | Tongala | Installation
Fault crew and LEI dispatched. Customer REC repaired damaged to customer installations and supply restored following completion/passed tests. | 34 NELSON ROAD, LILYDALE VIC 3140 | LIS1006029 |  | Blown branch/vegetation | [5 empty] | Report of tree contacting O/H HV and LV conductors resulting in HVI | Conductor (bare) | 0 | 0 | 0 |  | LDL22 | Vegetation: Trees Incident | HV injection | 26/10/2019 10:35 |  |  | 14591 |  |  | 20191205SPN_01 | Infrastructure (network-based) | -37.7463 | 145.3427 | 2 | AusNet Services Distribution | Report | 18413 | 0.038966 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Trees
Fault crew dispatched. CFA extinguished fire | LOT 1 FIRTH ROAD, BENALLA VIC 3672 | LIS3910727 |  | Bird | [5 empty] | Report of bird contacting O/H HV conductors resulting in ground fire | Conductor (bare);Pole top | 0 | 0 | 0 |  | BN1 | Bird Incident | Grassfire | 29/11/2019 20:40 | 1 | Large: more than 10 ha | 14593 |  |  | 20191205SPN_03 | Infrastructure (network-based) | -36.5705 | 145.932 | 2 | AusNet Services Distribution | Report | 18415 | 0.0078414 | 22kV AC | Wangaratta Aero | 3672 | Benalla | Animal
Fault crew dispatched to investigate and make safe. | 67 LEWIS ROAD, WANTIRNA SOUTH VIC 3152 | LIS1218894 |  | Bird | [5 empty] | Report of bird contacting bare O/H assets on pole resulting in flashover | Pole top | 0 | 0 | 0 |  | BRA11 | Bird Incident | Pole-top fire | 30/11/2019 1:09 | 1 | Negligible: no ground fire | 14595 |  |  | 20191205SPN_04 | Infrastructure (network-based) | -37.8639 | 145.2525 | 1 | AusNet Services Distribution | Report | 18419 | 0.0048819 | 22kV AC | Moorabbin Airport | 3152 | Wantirna South | Animal
On arrival crew isolated supply and carried out repairs. | 11 STRATHTULLOH CIRCUIT, STRATHTULLOH VIC 3338 | 33105868 | [7 empty] | Report received of grass fire at incident location. On arrival crew found that a FOLCB had overheated and resultant sparks caused a small grass fire (5 x 30m) There was no injuries or third party property damage | Connection box | 2 | 2 | 2 |  | MLN011 | To be advised | Grassfire | 43628.3646 | 1 | Small: 10 - 1000 sq.m | 14600 | Roadway |  | 20191209PWA_01 | Infrastructure (network-based) | -37.7456 | 144.6055 | 1 | Powercor | Notification | 18427 | 0.034758 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Strathtulloh | Fuse
On arrival crew isolated supply and carried out repairs. | 1981 RAINBOW-NHILL ROAD, RAINBOW VIC 3424 | 32120528 |  | Alive | [5 empty] | A call was received from the CFA stating that a wire had come down at the above address and had caused a fire. Powercor crew arrived onsite they found that the HV SWER conductor between Pole 33 and 34 Lake Hindmarsh had broken mid span and caused a grass fire. At the point that the conductor broke, a extremely large cactus was growing and it appears that the cactus had made contact with the HV conductor causing the fire and conductor failure. he fire burnt approx. 15 acres of grass, bush and cactus plantation. CFA attended and extinguished the fire. THere was no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | NHL015 | Rapid growth vegetation encroachment | Grassfire | 43658.5826 | 1 | Medium: 1000 sq.m - 10 ha | 14603 | Agricultural |  | 20191209PWA_04 | Infrastructure (network-based) | -35.9809 | 141.842 | 1 | Powercor | Report | 18432 | 0.019693 | 12.7kV AC (SWER) | Horsham Aerodrome | 3424 | Rainbow | Trees
On arrival crew isolated line and carried out repairs. | 1060 Satimer Rd, Wando Vale VIC 3312, Australia | 32127115 | Working too close to overhead lines | [6 empty] | A tree harvester cut down a tree and a branch fell on to a SWER line at the incident location. Upon arrival, a Powercor crew found that the SWER conductor on the ground. There were no injuries or fire. | Conductor (bare) | 2 | 2 | 2 |  | HTN006 | Plantation harvesting | Loss of supply;No Go Zone (contact);Damage to network assets | 43750.4167 |  |  | 14614 | Forest - plantation |  | 20191210PWA_07 | Infrastructure (network-based) | -37.4584 | 141.5381 | 1 | Powercor | Report | 18461 | 0.024784 | 12.7kV AC (SWER) | Hamilton Airport | 3312 | Wando Vale | Other
Fault crews attended the site to investigate and identified that a fence post was installed adjacent to the LV pillar at an unknown date/time and damaged the LV underground cable. The LV underground circuit was isolated at the pillar and the cable was repair before supply was restored. | 222 FRANKSTON-FLINDERS ROAD, FRANKSTON SOUTH VIC 3199 | 3317438 | Working too close to underground cables | [5 empty] | 1 | UE data analytics identified that an LV circuit has lost power in the middle of the night affecting 17 customers which included 1 life support customer. | Services cable | 0 | 0 | 0 |  | FSH33 | The cause of the incident was a customer's contractor installing a fence post hard up next to the LV underground pillar which damaged the LV underground cable. | No Go Zone (contact);Damage to network assets | 21/11/2019 0:30 |  |  | 14616 | Residential |  | 20191210UTD_01 | Infrastructure (network-based) | -38.1748 | 145.1386 | 1 | United Energy Distribution | Report | 18463 | 0.03095 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston South | Dug up
on arrival crew isolated supply and carried out repairs. | Shanahans Rd, Mount Cottrell VIC 3024, Australia | 33077381 | Copper theft | [6 empty] | A Powercor operator found a copper theft at the incident location while he was patrolling the line. A fault crew attended to the site and found 4m of pole substation LV earthing had been stolen. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | TNA023 | copper theft | Damage to network assets | 43780.4583 |  |  | 14621 | Roadway |  | 20191211PWA_01 | Infrastructure (network-based) | -37.811 | 144.6205 | 1 | Powercor | Report | 18470 | 0.019277 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival service removed to allow REC to repair POA | 301 EIGHTH STREET, MILDURA VIC 3500 | 33064623 | Crane, excavator or other construction/farming equipment | [6 empty] | Customer reported, pole to house wire broken at house end, fallen on top of excavator that drove into it, no persons inside excavator,. There was no fire or reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | MBN023 | Excavator drove into service line | Damage to network assets | 13/11/2019 9:27 |  |  | 14627 |  |  | 20191211PWA_06 | Infrastructure (customer connection) | -34.1722 | 142.1466 | 1 | Powercor | Report | 18478 | 0.030117 | Low voltage AC (<1kV) | Mildura Airport | 3500 | Mildura | Vehicle
On arrival crew made safe and organised repairs | 31 Murrindal St, Werribee VIC 3030, Australia | 30352292 | Working too close to underground cables | [6 empty] | Report received that plumbers on construction site have uncovered an orange conduit. Works stopped and exclusion zone set up. Upon arrival the fault crew found that a 16mm 4/c underground service cable in a 63mm conduit had been exposed and damaged caused to the 63mm conduit. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE023 | Excavations work | Damage to network assets | 14/11/2019 8:08 |  |  | 14629 | Roadway |  | 20191211PWA_08 | Infrastructure (network-based) | -37.9162 | 144.6433 | 1 | Powercor | Report | 18480 | 0.022558 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Dug up
On arrival crew inspected asset and carried out repairs. | Mt Warrenheip Rd, Dunnstown VIC 3352, Australia | 32003387 | Copper theft | [6 empty] | Field crew found LV earth missing on substation at incident location. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BAN011 | Copper theft | Damage to network assets | 17/11/2019 12:37 |  |  | 14631 | Roadway |  | 20191211PWA_10 | Infrastructure (network-based) | -37.5732 | 143.9609 | 1 | Powercor | Report | 18482 | 0.040281 | Earthing cable | Ballarat Aerodrome | 3352 | Dunnstown | Other
Fault crew dispatched. Failed joint box removed. Service cable repaired. | 18 PEARCE ROAD, LIMA EAST VIC 3673 | LIS3908199 |  |  |  | Moisture ingress |  |  |  | Report of junction box fire and subsequent ground fire | Connection box | 0 | 0 | 0 |  | BN6 | Joint box failure | Pole-top fire;Grassfire | 43781.3958 | 1 | Localised: less than 10 sq.m | 14624 |  |  | 20191211SPN_01 | Infrastructure (network-based) | -36.7884 | 145.9694 | 1 | AusNet Services Distribution | Report | 18475 | 0.015997 | Low voltage AC (<1kV) | Wangaratta Aero | 3673 | Lima East | Connection
On arrival crew isolated suppl and commenced repairs. | 67 A300, Castlemaine VIC 3450, Australia | 32045518 |  | Bird | [5 empty] | Vic fire reported explosion and fire and incident location. On arrival crew found that a bat had caused a flashover on 66kv conductor resulting in 66kv conductors coming in contact with 22kv circuit below. There was a small grass fire (30m x 30m) , no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BETS-CMN | Bird Incident | Grassfire | 43720.0264 | 1 | Small: 10 - 1000 sq.m | 14633 | Public space |  | 20191212PWA_01 | Infrastructure (network-based) | -37.0721 | 144.207 | 1 | Powercor | Report | 18484 | 0.036326 | 22kV AC;66kV AC | Bendigo Airport | 3450 | Castlemaine | Animal
Crew attended and inspected pole for damage. Broken sheds found on footpath side power filled fuse unit. Fault followup raised for repairs. | 12 Centenary Ct, Stawell VIC 3380, Australia | 33053400 |  | Bird | [5 empty] | VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a substation pole. The resultant fault current caused the feeder CB to reclose and the bird to fall to the ground, resulting in a ground fire (approx. 8m x 2m) on road reserve and a 2m section of a customer front yard at 12 Centenary Crt. There were no reported injuries or third party damage | Pole mounted | 2 | 2 | 2 |  | STL007 | Bird Incident | Grassfire | 43781.816 | 1 | Small: 10 - 1000 sq.m | 14634 |  |  | 20191212PWA_02 | Infrastructure (network-based) | -37.0675 | 142.7941 | 1 | Powercor | Report | 18485 | 0.030706 | 22kV AC | Horsham Aerodrome | 3380 | Stawell | Animal
On arrival crew isolated line and carried out repairs | 1 Woodlea Cl, Strathfieldsaye VIC 3551, Australia | 32051730 |  | Blown branch/vegetation |  |  |  |  | 1 | During wind storm tree fallen on overhead conductors. There was no fire, no reported injuries or third party property damage. protection operated as expected | Conductor (bare) | 2 | 2 | 2 |  | BGO013 | Wind storm | Damage to network assets | 21/11/2019 13:44 |  |  | 14636 | Roadway |  | 20191212PWA_04 | Infrastructure (network-based) | -36.7949 | 144.3409 | 1 | Powercor | Report | 18487 | 0.017339 | 22kV AC | Bendigo Airport | 3551 | Strathfieldsaye | Trees
On arrival the crew made site safe and replaced the stolen earth and 240mm 4C AL cable. | 1090 Tarneit Rd, Tarneit VIC 3029, Australia | 30545767 | Copper theft | [6 empty] | A Powercor employee, reported a stolen pole earth , and possible stolen LV mains cable at pole substation TARNEIT-CLEMENTINE on pole LIS-868490. On arrival the fault crew found that the high voltage earth (copper cable) had been cut, removed from the pole and pulled out of the ground. An AL cable (not in service) attached to the pole had been cut near ground and removed from the pole. There was no fire, no reported injuries or third party property damage. | Services cable;Earth/earthing | 2 | 2 | 2 |  | BLTS-BMH | copper theft | Damage to network assets | 22/11/2019 12:15 |  |  | 14639 |  |  | 20191213PWA_01 | Infrastructure (network-based) | -37.8129 | 144.6764 | 1 | Powercor | Report | 18490 | 0.032608 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3029 | Tarneit | Other
Fault crews attended the site to investigate. Upon inspection, the branch has fallen onto HV conductors during strong winds. The site was made safe and repairs were made on the pole top construction. | 79 BENT STREET, MCKINNON VIC 3204 | 2308461 |  | Wind;Fallen |  |  |  |  | 1 | During a strong wind event, UE received a call that a branch has fallen onto the conductors and it was sparking. UE protection operated to isolate the feeder and MFB were on site. | Conductor (bare) | 0 | 0 | 0 |  | EW14 | Vegetation: Trees Incident | Other vegetation | 43720.8542 | 1 | Negligible: no ground fire | 14646 | Roadway |  | 20191213UTD_02 | Infrastructure (network-based) | -37.9115 | 145.0387 | 1 | United Energy Distribution | Report | 18497 | 0.034704 | 11kV AC | Moorabbin Airport | 3204 | Mckinnon | Trees
AW9 feeder patrolled and site made safe | Easement ex Westfield Shopping Town |  |  | Lightning |  |  |  |  | 1 | Lightning strike caused grassfire adjacent to AW09 (feeder) overhead conductor in easement ex-Westfield shopping town. No photos are available for this incident. | Conductor (bare) | 0 | 0 | 0 |  | AW09 | Lightning strike | Grassfire | 21/11/2019 14:44 | 1 | Medium: 1000 sq.m - 10 ha | 14657 | Public space |  | 20191217JEM_03 | Infrastructure (network-based) | -37.7155 | 144.8858 | 1 | Jemena | Report | 18511 | 0.039684 | 22kV AC | Essendon Airport |  |  | Lightning
Fault crew attended & inspected conductors, supply was restored. | 1000 Byrneside-Kyabram Rd, Merrigum VIC 3618, Australia | 30129834 | Working too close to overhead lines | [5 empty] | 1 | Following an ACR operation to lockout, a customer called to report an excavator had contacted the overhead power lines on their property. The excavator operator was positioning the machine to the work location with boom elevated and made contact with the overhead conductors. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | SHP014 | Excavator being moved with boom elevated | Loss of supply;No Go Zone (contact) | 14/12/2019 9:45 |  |  | 14652 | Agricultural |  | 20191217PWA_01 | Infrastructure (network-based) | -36.3608 | 145.132 | 1 | Powercor | Report | 18505 | 0.015969 | 22kV AC | Shepparton Airport | 3618 | Merrigum | Vehicle
Voltage tests between an independent earth and various parts of the electrical installation including the distribution assets,identified a corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customer's POA, causing a higher than normal impedance within the neutral service conductor. The Customer's REC replaced the deteriorated Single Phase FOLCB at the Customer's POA. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 121 SAXTON STREET, NUMURKAH VIC 3636 | 31027168 |  |  |  | Corrosion |  | Phase to earth |  | Mr Mark Montague was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Tap and his bare feet while standing on the wet shower base and waste water outlet. | POA connection (customer side) | 2 | 2 | 2 |  | NKA004 | Corroded connection | Minor shock | 16/08/2019 5:00 |  |  | 14664 | Residential |  | 20191218PWA_05 | Infrastructure (customer connection) | -36.0885 | 145.4335 | 1 | Powercor | Report | 18519 | 0.010111 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Installation
The crew isolated supply to the damaged underground cable and arrange for the ATL to contact the customer. | Rosebank Village, 21 Charlotte St, Sebastopol VIC 3356, Australia | 33001168 |  | Bird | [5 empty] | A call was received from the CFA of an explosion on a pole at the incident location. When the crew arrived onsite they found that a crow had flashed on a HV switch. he flashover caused minor damage to the HV switch and associated BA fuse unit. The fault current from the flashover had cause damage to a customers owned underground service on the pole and also had burnt through the metal band-it holding the underground cable guards on the pole. There was no fire, no reported injuries or third party property damage. | Disconnector/isolator;Pole (concrete) | 2 | 2 | 2 |  | BAS034 | Bird Incident | Damage to network assets | 43720.541 |  |  | 14668 | Roadway |  | 20191218PWA_07 | Infrastructure (network-based) | -37.6004 | 143.845 | 1 | Powercor | Report | 18523 | 0.025021 | 22kV AC | Ballarat Aerodrome | 3356 | Sebastopol | Animal
A voltage test between the waste and the conductive metallic tap resulted with 23 Volts at various points of the installation with reference to an independent earth, including the distribution assets, investigations revealed the service neutral conductor was corroded. CitiPower linesman repaired the service & CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 37 MACEDON AVENUE, BALWYN NORTH VIC 3104 | 30180370 |  |  |  | Corrosion |  | Phase to earth |  | Lisa received an electric shock when she simultaneously contacted the Metallic tap with her hand and metallic waste with her foot | Service cable (insulated) | 2 | 2 | 2 |  | WD022 | corroded neutral service conductor | Minor shock | 23/08/2019 13:30 |  |  | 14673 | Residential |  | 20191219PWA_05 | Infrastructure (network-based) | -37.7897 | 145.0738 | 1 | CitiPower | Report | 18528 | 0.0028854 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | OH Cable
Due to the tenantâ€™s circumstances and the LEIâ€™s ETA the Powercor Fault Crew were instructed to disconnect supply to allow the attending REC to replace the defective / corroded FOLCB. A visual inspection by the attending LEI of the existing O/H Service Cable and FOLCB identified a corroded O/H Service Neutral Conductor termination in the Customers FOLCB located at the POA, which was confirmed as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable with a new ABC O/H Service Cable, which was terminated in the new FOLCB at the Customerâ€™s POA and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 3 5 KRONE AVENUE, SHEPPARTON VIC 3630 | 32187002 |  |  |  | Corrosion |  | Phase to earth |  | Ms Kaya Barbour was in the Bathroom showering when she believes she experienced a minor electric shock as she made simultaneous contact with her hand on the metallic Shower Taps and her bare feet whilst standing on the wet shower base and metallic waste outlet. | POA connection (network side) | 2 | 2 | 2 |  | STN022 | Corroded connection in folcb | Minor shock | 27/08/2019 0:00 |  |  | 14677 | Residential |  | 20191219PWA_07 | Infrastructure (customer connection) | -36.3941 | 145.4033 | 1 | Powercor | Report | 18532 | 0.025258 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a loose U/G Service Neutral connection in the FOLCB located on the Reticulation Pole which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew reterminated the loose U/G Service Neutral connection at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 19 Wallace St, Congupna VIC 3633, Australia | 33093208 |  |  |  | Mechanical breakdown |  | Phase to earth |  | Mr Ben Jones was in the Bathroom showering when he received an electric shock as he made simultaneous contact with one hand on the Shower Tap and his bare feet whilst standing on the wet shower base and metal waste water outlet. | Connection box | 2 | 2 | 2 |  | SHN024 | loose connection in connection box | Minor shock | 43505 |  |  | 14680 | Roadway |  | 20191219PWA_10 | Infrastructure (network-based) | -36.2999 | 145.4367 | 1 | Powercor | Report | 18535 | 0.0031458 | Low voltage AC (<1kV) | Shepparton Airport | 3633 | Congupna | Connection
A Zinfra faults crew attended and secured the LV pillar that was damaged when the pillar lid was removed from its base. | 4 MOONBRIA WAY, TEMPLESTOWE VIC 3106 |  | Unauthorised work;Unauthorised access | [5 empty] | 2 | Rocco (no phone number) contacted the United Energy faults and emergencies call centre advising that he'll be in attendance after "builders" working at no 2 Moonbria Way went to the the green electricity box on the nature strip and removed the seal They continued and turned the electricity supply off to make electrical repairs. Rocco advised they proceeded to reseal the LV pillar with zip ties to secure to the base but the box remains loose with live cables enclosed that can be accessible to the public. The builders have damaged the pillar lid where the seals go through and this requires repairs. | Services cable;LV Pillar | 0 | 0 | 0 |  |  | It was uncertain what task the builder was trying to achieve at the time of the event. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43567.6875 |  |  | 14675 | Public space |  | 20191219UTD_01 | Infrastructure (customer connection) | -37.7731 | 145.1598 | 1 | United Energy Distribution | Report | 18530 | 0.036439 | Low voltage AC (<1kV) | Moorabbin Airport | 3106 | Templestowe | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination in the Pole Type Junction Box located at the Reticulation Pole, which was identified as the cause of the high impedance associated with the return path of the neutral current. The attending Powercor Fault Crew reterminated the corroded O/H Service Neutral Conductor connection at the Pole Type Junction Box located at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 69 VERDON STREET, WARRNAMBOOL VIC 3280 | 33098147 |  |  |  | Corrosion |  | Phase to earth |  | Mr Brayden Hotker was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet whilst standing on the wet shower base and waste water outlet. | Connection box | 2 | 2 | 2 |  | WBL012 | Corroded connection in junction box | Minor shock | 43505.2292 |  |  | 14682 |  |  | 20191220PWA_02 | Infrastructure (network-based) | -38.3864 | 142.5082 | 1 | Powercor | Report | 18539 | 0.0114 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Sent inspection, restore cct. Fuse mains box was damaged, fire area in front of box. Customer Fuse Box replaced and n other damage found. o further action required. | 30 HOVELL STREET, WODONGA VIC 3690 | 5204893 | Vehicle | [6 empty] | Truck hit pole. Conductor to ground. small grass fire (4mx5m) located underneath customer FMB. Refer to photos attached. | Conductor (bare) | 0 | 0 | 0 |  | WO14 | truck hit pole, LV conductor to ground, confirmed HVI | Grassfire | 18/12/2019 13:42 | 1 | Small: 10 - 1000 sq.m | 14685 | Residential |  | 20191220SPN_02 | Infrastructure (network-based) | -36.1143 | 146.8952 | 1 | AusNet Services Distribution | Report | 18545 | 0.040885 | Low voltage AC (<1kV) | Wangaratta Aero | 3690 | Wodonga | Vehicle
circuit isolated and tree branch removed from open wire LV. | 84 High St, Maldon VIC 3463, Australia | 32050537 |  | Blown branch/vegetation | [5 empty] | Customer reported broken branch laying across mains wires at incident location, not reachable from ground, smallish branch. Crew found tree branch caused conductors to clash starting small 300mm x 300mm ground fire, There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CMN004 | Vegetation: Trees Incident | Grassfire | 20/12/2019 15:48 | 1 | Localised: less than 10 sq.m | 14690 | Roadway |  | 20191223PWA_04 | Infrastructure (network-based) | -36.9894 | 144.0647 | 1 | Powercor | Report | 18551 | 0.03526 | Low voltage AC (<1kV) | Bendigo Airport | 3463 | Maldon | Trees
Crew replaced burnt out connection box. | 76 Collins St, Thornbury VIC 3071, Australia | 30194938 |  |  |  | Overheated connection |  |  |  | Passerby reported that Pole Corner of Tharrat St and Collins. Pole dropping molten material onto the ground. Started a fire but is out now. On arrival Crew advise connection box overheated. Debris form overheated box has ignited a small grass fire (6 by 4m approx.). The fire self extinguished. | Connection box | 2 | 2 | 2 |  | NC004 | connection failure | Grassfire | 20/12/2019 19:10 | 1 | Small: 10 - 1000 sq.m | 14694 | Roadway |  | 20191223PWA_07 | Infrastructure (network-based) | -37.7555 | 145.0083 | 1 | CitiPower | Report | 18555 | 0.0072882 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Connection
Ongoing work suspended pending investigations with ESV involvement. | Stud Rd, Rowville VIC 3178, Australia | [5 empty] | Incorrect electrical isolation and/or permits |  | 2 | AusNet Services is a UE HV Customer connected to feeder LD33. AusNet Servicesâ€™ HV contractor submitted an application for a VSCAP (instead of a SCAP) for 4th December to isolate, earth and remove droppers from CHP MGS DN9470. They have bypassed UEâ€™s Service Provider Zinfra. As a HV customer, they are not permitted to access the UE Network via a third party. However, on 4th December 2019 the customer have breached procedures by undertaking the following: â€¢ Issuing SCAP to themselves â€¢ Engaging Third Party (Magnetic) and bypassing UE processes to operate UEâ€™s asset CHP MGS DN9470 â€¢ Third Party (Magnetic) issuing an EAP on UEâ€™s asset and removing droppers upstream of CHP MGS DN9470 | Dropper/bridge | 0 | 0 | 0 |  | LD 33 | Breach of procedures and interference to netwok assets. | Damage to network assets | 43567.3333 |  |  | 14701 | Commercial |  | 20191224UTD_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | United Energy Distribution | Report | 18563 | 0.037939 | 22kV AC | Moorabbin Airport | 3178 | Rowville | Other
Fire extinguished by MFB and site made safe HV isolators replaced | 12 HAMPSTEAD ROAD, MAIDSTONE VIC 3012 | A025397 |  |  |  | Overheated connection |  |  | 2 | Small grass fire at base of pole as a result of failed HV isolator during feeder fault. | Disconnector/isolator;Any other type | 0 | 0 | 0 |  | BY14 | Failure of High Voltage Isolator. | Grassfire | 30/12/2019 13:29 | 1 | Localised: less than 10 sq.m | 14712 | Roadway |  | 20191230JEM_01 | Infrastructure (network-based) | -37.7808 | 144.8722 | 1 | Jemena | Report | 18639 | 0.016269 | 22kV AC | Essendon Airport | 3012 | Maidstone | Connection
PCA crews undertook required repairs and restored supply | 460 Chocolyn Rd, Camperdown VIC 3260, Australia | 30047237 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a pole fire at the incident address. When crews arrived they found a FOLCB on substation pole had failed resulting in a equip fire and small (9x2m) grd fire. CFA crews extinguished the fire. No injuries or property damage was reported. | Connection box | 2 | 2 | 2 |  | CDN004 | Insufficient remains to determine direct cause | Grassfire | 25/12/2019 23:54 | 1 | Small: 10 - 1000 sq.m | 14706 | Roadway |  | 20191230PWA_04 | Infrastructure (network-based) | -38.1867 | 143.1862 | 1 | Powercor | Report | 18568 | 0.0020127 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3260 | Camperdown | Connection
On arrival crew isolated supply and carried out repairs. | 23 Bright St, California Gully VIC 3556, Australia | 32032597 | Blown detritus | Wind |  |  |  |  | 1 | Vic fire reported an umbrella has blown onto HV line and wire down which started small grass fire . Crew found that an outdoor table umbrella had been caught by a gust of wind and had been thrown into the HV. The centre phase of the three phase line has as a result burnt to the ground and started a grassfire in road reserve and creek reserve There were no reported electrical injuries (Ambulance onsite were treating a resident for smoke inhalation.) | Conductor (bare) | 2 | 2 | 2 |  | EHK023 | Outdoor umbrella blew into line | Grassfire | 25/12/2019 14:51 | 1 | Medium: 1000 sq.m - 10 ha | 14708 | Roadway |  | 20191230PWA_06 | Infrastructure (network-based) | -36.7225 | 144.2654 | 1 | Powercor | Report | 18643 | 0.02075 | 22kV AC | Bendigo Airport | 3556 | California Gully | Other
A faults crew attended and found there were no vehicles involved and the service appears to have been intentionally damaged by those persons on site. The building is partially demolished but the area near the POA is yet to be touched. As it was likely these persons may cause further risk to public safety, the overhead service was removed. | 196 MARINE PARADE, HASTINGS VIC 3915 |  | Vandalism | [5 empty] | 2 | Caller reports that a truck got hooked onto the service wire but is now detached. No shocks and the wire is still connected at both ends but is sparking at the POA whenever it moves. Wire not low to reach from the ground and they have turned off the main switch. | Service cable (insulated) | 0 | 0 | 0 |  |  | Intentionally not following the demolition and electricity assets process and cutting corners to hasten the work. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/12/2019 10:30 |  |  | 14709 | Residential |  | 20191230UTD_01 | Infrastructure (customer connection) | -38.2929 | 145.1913 | 1 | United Energy Distribution | Report | 18571 | 0.0326 | Low voltage AC (<1kV) | Moorabbin Airport | 3915 | Hastings | Vehicle
Fire extinguished. Transformer lead and service were replaced. | 2A SIXTH AVENUE, ANGLESEA VIC 3230 | 33041664 |  | Wind |  | Mechanical vibration |  |  |  | Vicfire reported Transformer explosion - powerdown at this address. Crew attended to find ground fire under substation 5m*10m, The grass fire was extinguished by customer and CFA also attended. There was no reported injuries. | Dropper/bridge;Service cable (insulated) | 2 | 2 | 2 |  | WPD021 | Transformer lead and service insulation rubbed through causing short circuit. | Grassfire | 30/12/2019 13:35 | 1 | Small: 10 - 1000 sq.m | 14718 | Roadway |  | 20191231PWA_04 | Infrastructure (network-based) | -38.4231 | 144.1769 | 1 | Powercor | Report | 18748 | 0.0083287 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | AF Other
On arrival supply isolated and repairs carried out | 1004 Broughton Rd, Kaniva VIC 3419, Australia | 32100682 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through at the kingbolt and had broken There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 30/12/2019 22:51 | 1 | Negligible: no ground fire | 14720 | Agricultural |  | 20191231PWA_06 | Infrastructure (network-based) | -36.3162 | 141.3004 | 1 | Powercor | Report | 18582 | 0.04034 | 22kV AC | Horsham Aerodrome | 3419 | Kaniva | Crossarm
On arrival crew isolated supply and carried out repairs. | 146-148 MONTAGUE STREET, SOUTH MELBOURNE VIC 3205 | 30167035 |  |  |  | Leakage |  |  |  | Report received of conductors down at incident location. On arrival crew advised of pole fire, road side the high voltage isolator has burnt of at its securing bolt and half the cross-arm has broken off. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MG009 | Excessive leakage current | Pole-top fire | 31/12/2019 5:02 | 1 | Negligible: no ground fire | 14726 | Roadway |  | 20191231PWA_11 | Infrastructure (network-based) | -37.8319 | 144.9511 | 1 | CitiPower | Report | 18601 | 0.015801 | 11kV AC | Essendon Airport | 3205 | South Melbourne | Crossarm
On arrival crew isolated supply and carried out repairs. | 8576 NATIMUK-FRANCES ROAD, NEUARPURR VIC 3413 | 32090113 |  | Lightning | [5 empty] | Vic Fire reported a grass fire at the incident location. On arrival the fault crew found that a surge diverter connected to the substation pole at the incident location had flashed over causing a small grass fire at the base of the pole. There was no reported injuries or third party property damage. | Surge diverter | 2 | 2 | 2 |  | HSM004 | Surge diverter flashed over | Grassfire | 30/12/2019 20:40 | 1 | Localised: less than 10 sq.m | 14729 | Roadway |  | 20200102PWA_01 | Infrastructure (network-based) | -36.7395 | 141.0518 | 1 | Powercor | Report | 18591 | 0.027315 | 22kV AC | Horsham Aerodrome | 3413 | Neuarpurr | AF Other
On arrival crew isolated supply and carried out repairs. | 12 Corella Rd, Sunshine West VIC 3020, Australia | 32166103 |  |  |  | Leakage |  |  |  | Report received of Low conductors in Corella rd Sunshine West. Crew advise pole fire roadside phase strain cross-arm has burnt through. Roadside phase with insulators attached is hanging in midair. Possible high voltage injection, LEI on site Miles Tobias. No ground fire no person injured. | Crossarm (wood) | 2 | 2 | 2 |  | SU035 | Excessive leakage current | Pole-top fire;HV injection | 31/12/2019 10:39 | 1 | Negligible: no ground fire | 14731 | Roadway |  | 20200102PWA_03 | Infrastructure (network-based) | -37.7954 | 144.8049 | 1 | Powercor | Report | 18593 | 0.025689 | 22kV AC | Laverton Raaf | 3020 | Sunshine West | Crossarm
On arrival crew isolated supply and carried out repairs. | 42 Green Gully Rd Service Rd, Keilor VIC 3036, Australia | 30114080 |  |  |  | Leakage |  |  |  | Crew advise pole fire intermediate arm has burnt through at kingbolt. No ground fire or reported injury. | Crossarm (wood) | 2 | 2 | 2 |  | SA002 | Excessive leakage current. | Pole-top fire | 31/12/2019 4:50 | 1 | Negligible: no ground fire | 14732 | Roadway |  | 20200102PWA_04 | Infrastructure (network-based) | -37.723 | 144.8274 | 1 | Powercor | Report | 18594 | 0.0059051 | 22kV AC | Melbourne Airport | 3036 | Keilor | Crossarm
On arrival crew isolated supply and carried out repairs | 13 RAYMOND ROAD, LAVERTON NORTH VIC 3026 | 30115647 |  | Lightning | [5 empty] | Customer reported lightning has struck the pole and its been smoking and there has been sparks coming out as well, also adv its burnt out black at some parts Crew attended to find HV tee-off arm broken, conductors hanging with insulators attached. MFB attended to extinguish pole fire. Large chunks of the wooden cross-arm on the ground, No ground fire, no reported injuries. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | LVN032 | Lightning strike | Pole-top fire | 31/12/2019 7:00 | 1 | Negligible: no ground fire | 14736 | Roadway |  | 20200102PWA_08 | Infrastructure (network-based) | -37.8198 | 144.8078 | 1 | Powercor | Report | 18598 | 0.0065567 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Lightning
Site made safe and HV crossarm replaced | 48 JESICA ROAD, CAMPBELLFIELD VIC 3061 | A013782 |  |  |  | Leakage |  |  | 1 | End of HV crossarm burnt off at the bolt holding the HV fuse bracket | Conductor (bare);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | ST23 | Earth leakage | Pole-top fire | 31/12/2019 12:12 | 1 | Negligible: no ground fire | 14749 | Industrial |  | 20200103JEM_04 | Infrastructure (network-based) | -37.6579 | 144.9562 | 1 | Jemena | Report | 18633 | 0.003772 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Crossarm
Emergency switching performed. Dumped feeder to allow MFB to extinguish fire. Site made safe. HV crossarm and switch replaced. | 83 BAYVIEW STREET, WILLIAMSTOWN VIC 3016 | A071392 |  |  |  | Leakage |  |  | 1 | HV crossarm fire resulting in HV standoff insulator detaching from crossarm. Photos are unavailable for this incident. | Crossarm (wood);Insulators | 0 | 0 | 0 |  | NT15 | Earth leakage | Pole-top fire | 31/12/2019 10:29 | 1 | Negligible: no ground fire | 14756 | Residential |  | 20200103JEM_11 | Infrastructure (network-based) | -37.8593 | 144.8867 | 1 | Jemena | Report | 18622 | 0.041597 | 22kV AC | Laverton Raaf | 3016 | Williamstown | Crossarm
On arrival crew isolated supply and carried out repairs. | 47 Antimony Mine Rd, Coimadai VIC 3340, Australia | 30107875 |  |  |  | Leakage |  |  |  | Crew reported a hv crossarm fire at the incident location. CFA on site to extinguish the fire. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MLN022 | Excessive leakage current | Pole-top fire | 31/12/2019 11:04 | 1 | Negligible: no ground fire | 14742 | Roadway |  | 20200103PWA_04 | Infrastructure (network-based) | -37.6102 | 144.5114 | 1 | Powercor | Report | 18608 | 0.003169 | 22kV AC | Melbourne Airport | 3340 | Coimadai | Crossarm
On arrival crews isolated supply and carried out repairs | 94 Forrest St, Ardeer VIC 3022, Australia | 31034122 | Recreation - Helium (party) balloons | [6 empty] | Customer reported HV lines on ground and has started a small fire at incident location. Crew attended site and found the incident was caused by balloons released by unknown persons coming in contact with the over head conductors. The resultant contact caused sparks to fall onto the nature strip and adjacent reserve causing a small grass fire (10x20mtrs) The incident cause the 22kv conductor to rupture and fall to ground. The fault current also caused the connections at Pole 19 lis 25672 ( in Forest st 600mts from original fault) to fail allowing the conductor to fall onto the roadway. There was suspected HVI. There was no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | SSE033 | Balloons release by unknown person struck line causing flashover | Grassfire | 43831.4674 | 1 | Small: 10 - 1000 sq.m | 14744 |  |  | 20200103PWA_06 | Infrastructure (network-based) | -37.7839 | 144.8139 | 1 | Powercor | Report | 18610 | 0.020975 | 22kV AC | Laverton Raaf | 3022 | Ardeer | Other
Site made safe and HV crossarm replaced | 155 BAMFIELD ROAD, HEIDELBERG WEST VIC 3081 | A110840 |  |  |  | Leakage |  |  | 1 | Earth leakage ignited a pole top fire which resulting in failure of white phase king bolt on HV crossarm, subsequently causing the HV crossarm (together with HV isolators) to snap and hang low | Pole top;Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | NH03 | Earth leakage | Pole-top fire | 20/12/2019 15:17 | 1 | Negligible: no ground fire | 14761 | Industrial |  | 20200104JEM_02 | Infrastructure (network-based) | -37.7318 | 145.0571 | 1 | Jemena | Report | 18627 | 0.035625 | 22kV AC | Essendon Airport | 3081 | Heidelberg West | Pole
On arrival crew isolated supply and commenced repairs | 1 OLD MURRAY ROAD, HUNTLY VIC 3551 | 32035322 |  | Wind;Alive;Fallen;MEC | [5 empty] | Call received from Vic Fire reporting wires down and requesting urgent isolation of power. Crew were escorted by CFA to area where a SWER wire was down between Wallenjoe Pole 2 and Wallenjoe Pole 3 and found a tree had fallen on a SWER line. Damage to rural fencing , no injuries reported. | Conductor (bare) | 2 | 2 | 2 |  | EHK031 | Vegetation: Trees Incident | Grassfire | 43922.6694 | 1 | Large: more than 10 ha | 14766 | Agricultural |  | 20200106PWA_01 | Infrastructure (network-based) | -36.6485 | 144.3195 | 1 | Powercor | Report | 18634 | 0.020186 | 12.7kV AC (SWER) | Bendigo Airport | 3551 | Huntly | Trees
Field crew upon arrival identified that a tractor had made contact with the HV causing a connection on a bridge at the tee off to burn off. Non traversable lowest point was 4m on arrival then 7m once re-sagged. Traversable lowest point (where tractor contacted wire) 5m on arrival and 8m once cable has been repaired and re-sagged. Final heights are now within code. | 5667 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859 | 2513225 | Crane, excavator or other construction/farming equipment | [6 empty] | Tractor made contact with HV reuslting in damage to powerlines and ground fire. | Conductor (bare) | 0 | 0 | 0 |  | mfa22 | Tractor made contact with HV resulting in damage to powerline. | Grassfire | 30/12/2019 17:09 | 1 | Small: 10 - 1000 sq.m | 14772 | Agricultural |  | 20200106SPN_05 | Infrastructure (network-based) | -37.9684 | 146.9405 | 1 | AusNet Services Distribution | Report | 18647 | 0.009713 | 22kV AC | Morwell (Latrobe Valley Airport) | 3859 | Tinamba | Vehicle
Crew replaced HV crossarm. 24 customers interrupted to replace crossarm | 127 BRIDGEWATER ROAD, CRAIGIEBURN VIC 3064 | A022053 |  | Precipitation |  | Leakage |  |  | 1 | Earth leakage / tracking causing pole top fire and HV crossarm to break | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | ST32 | Earth leakage or tracking in light rain | Pole-top fire;Loss of supply | 44013.1007 | 1 | Negligible: no ground fire | 14775 | Residential |  | 20200107JEM_02 | Infrastructure (network-based) | -37.6107 | 144.9279 | 1 | Jemena | Report | 19736 | 0.014929 | 22kV AC | Melbourne Airport | 3064 | Craigieburn | Crossarm
On arrival crew isolated supply and carried out repairs. | 112 STRICKLAND STREET, ASCOT VIC 3551 | 33021191 |  | Fallen | [5 empty] | Customer reported tree branch had come down & brought down service wire and a grass fire had occurred nearby. On arrival, crew found that a grey twisted wire road crossing had a tree branch on it and had been pulled at the junction box on the substation pole that it was coming from. There a patch of grass ignited (3x3mtr) around 10 metres from the pole. There was no injuries, no third party property damage. | Service cable (insulated) | 2 | 2 | 2 |  | EHK033 | Vegetation: Trees Incident | Grassfire | 43922.7611 | 1 | Localised: less than 10 sq.m | 14791 | Roadway |  | 20200107PWA_07 | Infrastructure (network-based) | -36.6953 | 144.3306 | 1 | Powercor | Report | 18670 | 0.039868 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Ascot | Trees
replaced defective ba fuse | 250 SNOWY RIVER ROAD, WULGULMERANG EAST VIC 3885 | 1904373 |  |  |  | Candled fuse |  |  |  | BA fuse candling | Boric acid | 0 | 0 | 0 |  | BDL41 | 12K BA fuse candled | Pole-top fire | 23/12/2019 13:56 | 1 | Negligible: no ground fire | 14783 |  |  | 20200107SPN_04 | Infrastructure (network-based) | -37.0846 | 148.2603 | 1 | AusNet Services Distribution | Report | 18739 | 0.030543 | 22kV AC | Bairnsdale Airport | 3885 | Wulgulmerang East | Fuse
Fuse and TX replaced | 240 HILDEBRAND ROAD, COTTLES BRIDGE VIC 3099 | 919192 |  |  |  | Candled fuse |  |  |  | CANDLED FUSE | Any other type | 0 | 0 | 0 |  | DRN23 | HV Candled Fuse at Sub | Pole-top fire | 19/12/2019 16:10 | 1 | Negligible: no ground fire | 14787 |  |  | 20200107SPN_06 | Infrastructure (network-based) | -37.5931 | 145.2426 | 1 | AusNet Services Distribution | Report | 18666 | 0.017271 | 22kV AC | Wallan (Kilmore Gap) | 3099 | Cottles Bridge | Fuse
The pillar was replaced AND SITE REINSTATED | 2 JENHILL COURT, ROWVILLE VIC 3178 | 260075464 |  |  |  | Earth fault |  |  |  | low voltage paralleling pillar in the open position failed | LV Pillar | 0 | 0 | 0 |  | FGY12 | It is suspected the failure was caused by a loose connection or insulation breakdown causing a phase to ground earth fault | Grassfire | 21/12/2019 21:40 | 1 | Localised: less than 10 sq.m | 14795 |  |  | 20200107SPN_12 | Infrastructure (network-based) | -37.9178 | 145.2669 | 1 | AusNet Services Distribution | Report | 18675 | 0.018095 | Low voltage AC (<1kV) | Moorabbin Airport | 3178 | Rowville | Connection
The crew made the site safe, removed the damaged P/L pole and restored supply to customers affected. Works to re-install P/L Pole to be organized for next day on the morning. | Palmers Rd, Truganina VIC 3029, Australia | 30331789 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [6 empty] | Multiple customers reported outage. Daniel Hallowell (0409 604 926), from Winslow constructions, reported that a Roller crane, had hit a Public lighting pole, the pole had snapped at the base and made contact with 22kV overhead conductors. On arrival the crew found that a worker from Winslow Constructions was operating an Roller crane and hit the Public lighting pole LIS-837940, the pole snapped at the base and contacted overhead the 22kV conductors between poles LIS-737000 and LIS- 852579. The 66kv and 22kv cb's tripped The poles are located on Palmers road near the intersection with Dohertys road, Truganina. approx. 60m South from Dohertys road. There was no fire no reported injuries or third party property damage. | Conductor (bare);Pole (steel) | 2 | 2 | 2 |  | LV003 | Crane contacted lighting pole | Loss of supply;No Go Zone (contact);Damage to network assets | 44013.8729 |  |  | 14801 | Roadway |  | 20200108PWA_04 | Infrastructure (network-based) | -37.8253 | 144.7489 | 1 | Powercor | Report | 18685 | 0.0011713 | 22kV AC;66kV AC | Laverton Raaf | 3029 | Truganina | Vehicle
On arrival crew isolated supply and carried out repairs. | 25 Learmonth Rd, Wendouree VIC 3355, Australia | 32014213 |  |  |  | Leakage |  |  |  | Report received of pole on fire at incident location. On arrival crew found pole alight at king bolt position. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BAN004 | Excessive leakage current | Pole-top fire | 43952.3812 | 1 | Negligible: no ground fire | 14818 | Roadway |  | 20200109PWA_05 | Infrastructure (network-based) | -37.5359 | 143.8193 | 1 | Powercor | Report | 18705 | 0.012088 | 22kV AC | Ballarat Aerodrome | 3355 | Wendouree | Pole
Crew isolated and repaired | 20 VICTORIA STREET, PYRAMID HILL VIC 3575 | 30567286 |  |  |  | Leakage |  |  |  | Vic Fire reported pole fire and wire low at above address and crossing railway line. Concerned that train could hit line. On arrival crew found that cross-arm was burning from the King Bolt on both HV cross arms No injury or third party damage. No ground fire. | Pole (wood) | 2 | 2 | 2 |  | CHA006 | Excessive leakage current | Pole-top fire | 43952.741 | 1 | Negligible: no ground fire | 14822 |  |  | 20200109PWA_08 | Infrastructure (network-based) | -36.0553 | 144.1144 | 1 | Powercor | Report | 18710 | 0.034061 | 22kV AC | Bendigo Airport | 3575 | Pyramid Hill | Crossarm
Fault truck dispatched to make safe and investigate. Switch inspected and found ok. Supply restored once fire put out. | 246 RESEARCH-WARRANDYTE ROAD, NORTH WARRANDYTE VIC 3113 | 1206694 |  | Animal | [5 empty] | Report of loud bang, fire crew attended small ground fire at base of pole with poletop switch. Feeder tripped. Crew/truck dispatched to make safe and investigate. | Pole top;Any other type | 0 | 0 | 0 |  | RWN34 | Animal Incident | Grassfire | 43922.0229 | 1 | Localised: less than 10 sq.m | 14817 | Residential |  | 20200109SPN_02 | Infrastructure (network-based) | -37.7351 | 145.2211 | 1 | AusNet Services Distribution | Report | 18704 | 0.015747 | 22kV AC | Moorabbin Airport | 3113 | North Warrandyte | Animal
Crew isolated and repaired. | 6 Murray St, Shepparton VIC 3630, Australia | 32189142 |  |  |  | Leakage |  |  |  | Vic Fire reported cross-arm burning through. On arrival, crew found cross arm burning at fuse holder bolt on HV cross-arm. Assets were still secure to cross arm. No injuries, no ground fire, no third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | MNA024 | Excessive leakage current | Pole-top fire | 43952.8542 | 1 | Negligible: no ground fire | 14826 | Roadway |  | 20200110PWA_03 | Infrastructure (network-based) | -36.4036 | 145.398 | 1 | Powercor | Report | 18715 | 0.010813 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Crossarm
Crew isolated and repaired. | 63 Johns Rd, Red Cliffs VIC 3496, Australia | 32153003 |  |  |  | Leakage |  |  |  | Reported as all supply fail, crew attended and found pole fire with cross arm burnt through at fuse holder and conductor hanging beside pole below transformer. No ground fire. No injuries or third party damage. No reports of HVI. | Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 43952.816 | 1 | Negligible: no ground fire | 14829 | Roadway |  | 20200110PWA_06 | Infrastructure (network-based) | -34.2848 | 142.2101 | 1 | Powercor | Report | 18718 | 0.015813 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Crew isolated and repaired | 66 Oak Ave, Birdwoodton VIC 3505, Australia | 30096077 |  |  |  | Leakage |  |  |  | Report from customer of Pole top/crossarm has caught fire and fallen to the ground. Fire is now out however wires/assets are still hanging off the pole. Crew arrived, they found that the cross arm had burnt from the king bolt. No ground fire, no injuries, no third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | MBN014 | Excessive leakage current | Pole-top fire | 43983.6715 | 1 | Negligible: no ground fire | 14833 | Agricultural |  | 20200110PWA_10 | Infrastructure (network-based) | -34.208 | 142.0638 | 1 | Powercor | Report | 18725 | 0.0014306 | 22kV AC | Mildura Airport | 3505 | Birdwoodton | Crossarm
Crew isolated and repaired | 156 Madang Rd, Robinvale Irrigation District Section E VIC 3549, Australia | 30097348 |  |  |  | Leakage |  |  |  | Customer report of low wire at above address. Crew attended site and found that a cross arm had burnt through at the cross arm strap bolt and one of the conductors was hanging at approx. 5m. No ground fire at site. No injuries or third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | RVL001 | Excessive leakage current | Pole-top fire | 43983.5215 | 1 | Negligible: no ground fire | 14834 | Roadway |  | 20200110PWA_11 | Infrastructure (network-based) | -34.6616 | 142.7595 | 1 | Powercor | Report | 18727 | 0.0096481 | 22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section E | Crossarm
On arrival crew isolated supply and carried out repairs. | 1230 WIMMERA HIGHWAY, QUANTONG VIC 3401 | 32097564 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. Upon arrival, a Powercor crew found that a cross arm bunt through and fallen apart. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | HSM004 | Excessive leakage current | Pole-top fire | 44105.6438 | 1 | Negligible: no ground fire | 14855 |  |  | 20200113PWA_07 | Infrastructure (network-based) | -36.7392 | 142.0851 | 1 | Powercor | Report | 18759 | 0.040955 | 22kV AC | Horsham Aerodrome | 3401 | Quantong | Crossarm
Supply isolated, x-arm replaced | 48 VISE ROAD, BAMAWM VIC 3561 | 30121008 |  |  |  | Leakage |  |  |  | CFA reported pole fire at the incident location. Upon arrival crew found that an intermediate x-arm on a substation pole ( Hann 8 ) burnt through at the kingbolt position, conductors remained aloft held up via x-arm straps. No ground fire or 3rd party damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHP012 | Excessive leakage current | Pole-top fire | 44105.8903 | 1 | Negligible: no ground fire | 14857 | Roadway |  | 20200113PWA_09 | Infrastructure (network-based) | -36.2953 | 144.5629 | 1 | Powercor | Report | 18761 | 0.033164 | 22kV AC | Bendigo Airport | 3561 | Bamawm | Crossarm
On arrival crew isolated supply and carried out repairs. | E Judds Rd, Yanac VIC 3418, Australia | 32109482 |  |  |  | Leakage |  |  |  | Passing motorist reported broken Xarm and pole fire in paddock. Crew attended and found top of pole burnt off and Xarm burnt thru at king bolt. No CFA attended No ground fire start. No shock or third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 44136.3653 | 1 | Negligible: no ground fire | 14859 | Agricultural |  | 20200114PWA_02 | Infrastructure (network-based) | -36.1068 | 141.406 | 1 | Powercor | Report | 18763 | 0.015882 | 22kV AC | Horsham Aerodrome | 3418 | Yanac | Crossarm
Faults crew attended the site and upon investigation, it was identified a pillar was burnt out and caused a small grass fire in the garden bed, approximately 1mx1m. The site was isolated and made safe. The pillar and cables were repaired before supply was restored. | 42 LIPTON DRIVE, FRANKSTON VIC 3199 | 8819961 |  |  |  | Overheated connection |  |  | 1 | UE received a call that mulch fire has impacted a distribution kiosk. MFB are heading to the site. | LV Pillar | 0 | 0 | 0 |  | FSH22 | The cause of the fire was a burnt out pillar. | Grassfire | 17/12/2019 13:10 | 1 | Localised: less than 10 sq.m | 14862 | Roadway |  | 20200114UTD_02 | Infrastructure (network-based) | -38.159 | 145.154 | 1 | United Energy Distribution | Report | 18768 | 0.02008 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | AF Other
Faults crew attended the site and inspections found the pole was blackened but there was no damage on the pole. The grass was burnt on both sides of the pole, approximately 60sq m. There was no cause found for the fire. It is suspected that a bird made contact with the conductors and fell and caused the grass fire. | 347 BROWNS ROAD, RYE VIC 3941 | 1315973 |  | Bird |  |  |  |  | 1 | UE received a call to assess fire damage after a shrub fire. | Conductor (bare) | 0 | 0 | 0 |  | STO21 | Bird Incident | Grassfire | 27/12/2019 18:45 | 1 | Small: 10 - 1000 sq.m | 14870 | Roadway |  | 20200114UTD_07 | Infrastructure (network-based) | -38.3955 | 144.8186 | 1 | United Energy Distribution | Report | 18776 | 0.014146 | 22kV AC | Moorabbin Airport | 3941 | Rye | Animal
Crews attended and performed repairs, the CFA attended and extinguished the fire. | 468 Mywee Rd, Strathmerton VIC 3641, Australia | 30256137 |  | Alive;Fallen | [5 empty] | A customer called to say that wires were down and a fire had started, and he had called the CFA. On arrival the crew found that a tall gum tree located approx. 15m from the line had fallen over the HV conductors, causing one of the conductors to break and fall to the ground. This resulted in a grassfire of approx. 30m x 40m in size. There were no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | NKA003 | Vegetation: Trees Incident | Grassfire | 14/01/2020 13:00 | 1 | Medium: 1000 sq.m - 10 ha | 14876 | Agricultural |  | 20200115PWA_02 | Infrastructure (network-based) | -35.8838 | 145.4947 | 1 | Powercor | Report | 18790 | 0.033117 | 22kV AC | Shepparton Airport | 3641 | Strathmerton | Trees
The crew had to wait some time to get to the pole as the huge fire was being extinguished by CFA. There was a thunder storm in the area. Supply isolated and repairs arranged | Nioka, 601 Modesty Ln, Burrumbeet VIC 3352, Australia | 32007305 |  | Lightning | [5 empty] | Vic Fire reported a fallen pole might have caused a ground fire at the incident location. Upon arrival, a Powercor crew found the area was burning. No fallen pole was seen. There was a thunder storm in the area. The pole and assets were damaged by the fire No network fault was found to cause this fire or supply interruption during this time period at the location or the feeder. There were no reported injuries | Pole (wood) | 2 | 2 | 2 |  | BAS011 | Lightning strike assets burnt as a result of fire | Grassfire;Damage to network assets | 15/01/2020 15:46 | 0 | Large: more than 10 ha | 14888 | Agricultural |  | 20200117PWA_01 | Infrastructure (network-based) | -37.5173 | 143.5736 | 1 | Powercor | Report | 18805 | 0.025297 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3352 | Burrumbeet | Lightning
On arrival crew isolated supply and carried out repairs | Geggies Rd, Corindhap VIC 3352, Australia | 30005750 |  | Lightning | [5 empty] | A Powercor crew was called to an All Supply Failure report at the Dereel Sth SWER Isolating Substation. When the crew arrived onsite they discovered that a lightning strike had damage a surge diverter mounted on the pole and part of the damaged surge diverter had fallen to the ground causing a small grass fire. The fire burnt approx. 10 sq m of dry grass. | Pole mounted;Surge diverter | 2 | 2 | 2 |  | BAS022 | Lightning strike to assets | Grassfire | 15/01/2020 18:24 | 1 | Localised: less than 10 sq.m | 14890 | Agricultural |  | 20200117PWA_03 | Infrastructure (network-based) | -37.8744 | 143.7657 | 1 | Powercor | Report | 18808 | 0.0043206 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3352 | Corindhap | Lightning
Crew and inspector organised to investigate, make safe and repair. Inspections found Injection had occurred to the blue phase only. Customers connected to the blue phase required new Meters. Fault crew replaced the damaged Meters. No damage was found to customers property, only the Meters were damaged. | 40 NELSON ROAD, LILYDALE VIC 3140 | 1005886 |  | Lightning;Precipitation;Wind;Fallen | [5 empty] | High Voltage Injection. Tree came down into HV and pushed in LV. | Conductor (bare) | 0 | 0 | 0 |  | LDL22 | Vegetation: Trees Incident | HV injection | 15/01/2020 22:00 |  |  | 14886 | Residential |  | 20200117SPN_01 | Infrastructure (network-based) | -37.7465 | 145.3445 | 1 | AusNet Services Distribution | Report | 19327 | 0.0071169 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3140 | Lilydale | Trees
Fault crews attended the site to investigate. Upon inspection, it was identified long grass had grown around the pillar and a tractor hit the pillar when it was mowing the lawn. The site was isolated and made safe. The pillar was repaired and supply was restored. | 915 FRANKSTON-DANDENONG ROAD, CARRUM DOWNS VIC 3201 | 621893 | Vehicle | [5 empty] | 1 | UE received a call that a customer has hit a pillar with a lawn mower and now there is only part supply to the house. The pillar is broken and wires are exposed. | LV Pillar | 0 | 0 | 0 |  | CRM14 | The lawn mower was mowing the long grass and damaged the pillar. | Damage to network assets | 14/12/2019 20:10 |  |  | 14898 | Roadway |  | 20200117UTD_02 | Infrastructure (network-based) | -38.0747 | 145.1931 | 1 | United Energy Distribution | Report | 18816 | 0.02516 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Vehicle
On arrival crew isolated supply and carried out repairs. | 122-132 SIMSON STREET, PORTARLINGTON VIC 3223 | 32070815 |  |  |  | Overheated connection |  |  |  | Vicfire reported a pole fire. Attending crew found that a LV switch disconnector had failed There was no ground fire , no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | DDL013 | connection failure | Pole-top fire | 30/05/2019 8:21 | 1 | Negligible: no ground fire | 13822 | Roadway |  | 20190606PWA_08 | Infrastructure (network-based) | -38.1247 | 144.6645 | 1 | Powercor | Report | 17252 | 0.013025 | Low voltage AC (<1kV) | Avalon Airport | 3223 | Portarlington | Connection
On arrival supply isolated repairs organised Defect notice to be issued. | 337 PRINCES HIGHWAY, CORIO VIC 3214 | 32083357 | Vandalism;Copper theft | [6 empty] | Michael (MOGS) 0429930831 advises damage to meter board and wires exposed at U/G pit. Crew arrived to find vandalized meter and pit lid removed wires cut but no cable removed. There was no fire, no reported injuries. | Services cable;Services pit;Smart meter | 2 | 2 | 2 |  | FNS021 | Attempted copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 30/05/2019 13:00 |  |  | 13823 | Residential |  | 20190606PWA_09 | Infrastructure (network-based) | -38.074 | 144.3701 | 1 | Powercor | Report | 17254 | 0.035454 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Other
On arrival crew isolated supply and carried out repairs. | 240 LANCASTER-MOOROOPNA ROAD, LANCASTER VIC 3620 | 30222670 |  | Bird |  | Overheated connection |  |  | 2 | Following a report of the HV fuse down at the incident location, crews attended and found that lightning had struck the HV OH conductors mid-span. Insulation was burnt from a section of LV transformer leads adjacent to the FOLCB . A birds nest inside the FOLCB was scorched - refer image There was no ground fire, no reported injuries. | Connection box;Dropper/bridge | 0 | 0 | 0 |  | KYM003 | Bird Incident | Pole-top fire | 31/05/2019 8:49 | 1 | Negligible: no ground fire | 13824 | Agricultural |  | 20190606PWA_10 | Infrastructure (network-based) | -36.3226 | 145.1639 | 1 | Powercor | Report | 17339 | 0.0075671 | Low voltage AC (<1kV) | Shepparton Airport | 3620 | Lancaster | Lightning
Fault crew dispatched. Damaged street light removed and replaced with new | 46 HOWITT AVENUE, EASTWOOD VIC 3875 | LIS5655908 |  |  |  | Defective component |  |  |  | report of street light fire | Public lighting | 0 | 0 | 0 |  | BDL42 | Street light appears to have failed internally resulting in it burning. Investigation carried out but inconclusive, unable to determine cause of failure. | Pole-top fire | 43591.7292 | 1 | Negligible: no ground fire | 13815 | Roadway |  | 20190606SPN_01 | Infrastructure (network-based) | -37.8118 | 147.6285 | 2 | AusNet Services Distribution | Report | 17240 | 0.037833 | Low voltage AC (<1kV) | Bairnsdale Airport | 3875 | Eastwood | AF Other
On arrival crew isolated supply and carried out repairs. | 245-255 DOHERTYS ROAD, LAVERTON NORTH VIC 3026 | 30114188 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a transformer on fire at the incident location. Upon arrival a Powercor crew found that a service termination box on a Pole Substation had melted. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | LV021 | corrossion | Pole-top fire | 43561.4722 | 1 | Negligible: no ground fire | 13832 |  |  | 20190607PWA_05 | Infrastructure (network-based) | -37.8269 | 144.7696 | 1 | Powercor | Report | 17264 | 0.025049 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Connection
On arrival crew isolated supply and carried out repairs. | MURDEDUKE, 730 CRESSY ROAD, WINCHELSEA VIC 3241 | 30056488 | Working too close to overhead lines | [5 empty] | 1 | A customer reported that a mains wire had been brought down by a truck at the incident location. On arrival the crew found a tipper truck in the raised position had contacted the overhead 12.7kV SWER conductor, causing the conductor to fall to the ground and laying over a tractor. There were no reported shocks, injuries or fires. | Conductor (bare) | 2 | 2 | 2 |  | WIN011 | Tipper unloading under line | No Go Zone (contact);Damage to network assets | 43622.6132 |  |  | 13833 | Agricultural |  | 20190607PWA_06 | Infrastructure (network-based) | -38.1997 | 143.9109 | 1 | Powercor | Report | 17265 | 0.024751 | 12.7kV AC (SWER) | Avalon Airport | 3241 | Winchelsea | Vehicle
On arrival crew isolated supply and carried out repairs | 14 MINIFIE AVENUE, ANGLESEA VIC 3230 | 33043992 |  |  |  | Unknown technical factor |  |  |  | Emergency Services reported a pole fire and a grass fire at the incident location. On arrival the crew found that a 3 phase FOLCB had overheated and dropped hot debris to the ground, resulting in a small ground fire of less than 1 metre square at the base of the pole. There were no reported injuries. | Connection box | 2 | 2 | 2 |  | WPD021 | Insufficient remains to determine cause | Pole-top fire;Grassfire | 43622.4389 | 1 | Localised: less than 10 sq.m | 13834 | Roadway |  | 20190607PWA_07 | Infrastructure (network-based) | -38.4111 | 144.1849 | 1 | Powercor | Report | 17266 | 0.036068 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
On arrival supply isolated | 97-121 MURRAY ROAD, THORNHILL PARK VIC 3335 | 30108502 | Vandalism;Copper theft | [6 empty] | Powercor metering employee originally reported the incident earlier in the day after he was sent to site to investigate a no supply to meter case. He found that the service pit supplying the property at 97-121 Murray Rd had been disturbed with the pit connectors cut away and service cable hanging out of the pit. The meter panel at the house as well as the house itself had been considerably damaged, however the thieves didn't dispose of or take the meters. There was no fire, no reported injuries. | Services cable;Services pit;Meter board (including fuses) | 2 | 2 | 2 |  | MLN021 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43591.6681 |  |  | 13835 | Roadway |  | 20190607PWA_08 | Infrastructure (network-based) | -37.715 | 144.6292 | 1 | Powercor | Report | 17267 | 0.0029155 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Other
On arrival crew arranged for repairs to be carried out | 2187-2225 DIGGERS REST-COIMADAI ROAD, TOOLERN VALE VIC 3337 | 31024674 | Copper theft | [6 empty] | Ian 0419593303 advising new pit installed at this site for subdivision. He is advising the pit has been opened and it appears all cables within have been removed, damage to pit and appears damage inside the pit. There was no fire and no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN012 | copper theft | Damage to network assets | 43775.5903 |  |  | 13857 | Roadway |  | 20190612PWA_07 | Infrastructure (network-based) | -37.6145 | 144.5505 | 1 | Powercor | Report | 17293 | 0.031104 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
service cabling to service pole replaced | 27 NORTHUMBERLAND ROAD, SUNSHINE NORTH VIC 3020 | 32170409 |  |  |  | Mechanical breakdown |  |  | 2 | person went to have a shower and received an electric shock while touching the tap with his hand and simultaneously standing bare foot on the wet metal bathtub base. | Service conductor | 0 | 0 | 0 |  | SSE032 | faulty service cable crossing road | Minor shock | 43742.75 |  |  | 13867 | Residential |  | 20190612PWA_14 | Infrastructure (customer connection) | -37.776 | 144.8408 | 1 | Powercor | Report | 17303 | 0.034987 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | OH Cable
LEI tightened customer main neutral connection, Truck also remade Neutral connection at pole | 9 THEOBALD STREET, THORNBURY VIC 3071 | 30194322 |  |  |  | Neutral fault;Mechanical vibration |  |  | 2 | The citipower meter insights program identified an issue with the supply at the installation. After initial contact was made with the customer they reported receiving shocks from the carpark bollard and exit door (when both touched at same time). | Service conductor;Customer installation | 0 | 0 | 0 |  | FF097 | Loose connection/s | Minor shock | 43591.375 |  |  | 13868 | Commercial |  | 20190612PWA_15 | Infrastructure (customer connection) | -37.7561 | 145.0273 | 1 | CitiPower | Report | 17306 | 0.020712 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Connection
A fault crew was dispatched in conjunction with an EIO to investigate shock occurrence. The EIO conducted tests at the location where the shock occurred and measured 1.6V. NST and all other tests with and without load also passed. The fault crew was requested to check single phase over head line and FOLCB. The crew found the pole end connections were good, but found loose active an d neutral connections at the customer FOLCB. The crew tightened these connections, and subsequent testing all passed. | 24 DALSTEN GROVE, MOUNT ELIZA VIC 3930 |  |  |  |  | Fault on customer installation |  |  | 2 | UE received report of a customer receiving minor shock from shower taps. | Connector/termination;Connection box | 0 | 0 | 0 |  |  | Loose connections in the FOLCB. | Minor shock | 25/05/2019 12:15 |  |  | 13865 | Residential |  | 20190612UTD_01 | Infrastructure (customer connection) | -38.1845 | 145.0934 | 1 | United Energy Distribution | Report | 17301 | 0.035397 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Connection
Crew made site made safe and carried put repairs | 83 DANKS STREET, ALBERT PARK VIC 3206 | 30172683 |  |  |  | Leakage |  |  |  | Cross-arm fire due to leakage current. Fire incident found during review of outage data for fire incidents. No ground fire | Crossarm (wood) | 2 | 2 | 2 |  | AP003 | Excessive leakage current | Pole-top fire | 43353.4847 | 1 | Negligible: no ground fire | 13871 | Roadway |  | 20190613PWA_01 | Infrastructure (network-based) | -37.845 | 144.9477 | 1 | CitiPower | Report | 17309 | 0.040362 | 11kV AC | Essendon Airport | 3206 | Albert Park | Crossarm
Crew made site safe and repaired damage | 400 K ROAD, WERRIBEE SOUTH VIC 3030 | 32171538 |  |  |  | Candled fuse |  |  |  | HV Fuse candled and caught fire. Fire incident found during outage data review. No ground fire | EDO fuse | 2 | 2 | 2 |  | WBE034 | Excessive leakage current | Pole-top fire | 43291.4632 | 1 | Negligible: no ground fire | 13872 | Roadway |  | 20190613PWA_02 | Infrastructure (network-based) | -37.943 | 144.674 | 1 | Powercor | Report | 17318 | 0.0048565 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Fuse
Crew made site safe and carried out repairs. | 2 HARRISON COURT, HIGHTON VIC 3216 | 30225004 |  |  |  | Overheated connection |  |  |  | Pole top fire due to service line failure. Incident found during outage data review. No ground fire | Service conductor | 2 | 2 | 2 |  | WPD011 | Connection failure | Pole-top fire | 43324.859 | 1 | Negligible: no ground fire | 13874 | Roadway |  | 20190613PWA_04 | Infrastructure (customer connection) | -38.1712 | 144.3234 | 1 | Powercor | Report | 17312 | 0.023209 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
Crew made site safe and carried out repairs. | 119 SMITHS ROAD, BARRAPORT WEST VIC 3537 | 30554617 |  | Lightning | [5 empty] | Pole fire due to lightning strike. Found during outage data review. Ground fire 300 sqm | Pole (wood) | 2 | 2 | 2 |  | CTN001 | Lightning strike on pole | Grassfire | 43355.6382 | 1 | Small: 10 - 1000 sq.m | 13877 | Agricultural |  | 20190613PWA_07 | Infrastructure (network-based) | -36.0026 | 143.5456 | 1 | Powercor | Report | 17315 | 0.036834 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3537 | Barraport West | Lightning
KTS-TMA 66KV FDR A/RC Suppressed Ausnet was notified of this incident in the week beginning 10 June 2019. A surveyor went out to site and measured the clearance beneath the 66KV line to be 6.00m, which is below the 6.7m minimum for 66kV. A project manager visited the site on several occasions and did not find anyone to discuss this issue with. There are no markers or signage to indicate who is undertaking the works. The customer has been advised to remove the stockpile of rocks. This has now been confirmed to be removed from under the line (9 Aug 2019). | 22-40 KEILOR PARK DRIVE, KEILOR EAST VIC 3033 | . | Working too close to overhead lines | [5 empty] | 2 | NO GO ZONE INTRUSION - A civil contractor has stockpiled gravel and raised the ground level beneath the KTS-TMA 66kV subtransmission line. The height is 6.0m and the minimum No Go Zone clearance must be no less than 6.7m. They have made contact with a Ausnet fibre optic cable and installed 2 makeshift poles to hold up displaced Ausnet fibre optic underneath Jemena's subtransmission feeder. â€¢ A Jemena No Go Zone permit to work (PTW) had not been issued for this site/work â€¢ A PTW (21909) was issued for 16a Keilor Park Dr Keilor East and expired 8 June 2019. Issued to Brett Worsfold of Pelligra Construction. This may be the same site. | Conductor (bare);Communication cable/equipment;Customer installation | 0 | 0 | 1 | AUSNET SERVICES | KTS-TMA 66kV | Civil contractor using land to stockpile gravel | No Go Zone (no contact) | 17/06/2019 16:32 |  |  | 13902 | Industrial |  | 20190617JEM_01 | Infrastructure (network-based) | -37.734 | 144.8507 | 2 | Jemena | Report | 17530 | 0.0051019 | 66kV AC | Essendon Airport | 3033 | Keilor East | Other
UE dispatched a fault crew in conjunction with an EIO to investigate. The EIO undertook voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, and revealed a defective neutral service connection at the neutral crimp joint at the Ceramic Fuse Mains Box causing the neutral to have a high impedance. The fault crew replaced the bare copper neutral tail and crimp joint and NSTed the Service Cable and at the customers Main Switchboard. NST passed at both locations. | 18 SOLWAY STREET, ASHBURTON VIC 3147 |  |  |  |  | Neutral fault |  | Phase to earth | 2 | The UE Network Analytics, through the AMI meter, detected a high impedance neutral at 18 Solway St Ashburton. At the same time, UE received a report of a customer receiving tingles form the taps. | Customer installation | 0 | 0 | 0 |  |  | The cause was the failed connection of the neutral tail into the ceramic fused mains box at the point of supply. | Minor shock | 43805.3347 |  |  | 13899 | Residential |  | 20190617UTD_03 | Infrastructure (customer connection) | -37.8721 | 145.0713 | 1 | United Energy Distribution | Report | 17344 | 0.002022 | Low voltage AC (<1kV) | Moorabbin Airport | 3147 | Ashburton | Connection
UE dispatched an UG crew who isolated the damaged service cable. The damaged cable was subsequently replaced and supply restored to the two premises affected. | 10 RENVER ROAD, CLAYTON VIC 3168 |  | Working too close to underground cables | [5 empty] | 2 | UE received a report of an LV underground cable hit in the street by a drilling contractor. A pole to pit UG service cable in conduit had been damaged. | Services cable | 0 | 0 | 0 |  |  | The civil works contractor undertook works in the street without obtaining a No Go Zone permit for works in the vicinity of a live underground cable. | Loss of supply;Damage to network assets | 14/06/2019 13:40 |  |  | 13900 | Roadway |  | 20190617UTD_04 | Infrastructure (network-based) | -37.918 | 145.1435 | 1 | United Energy Distribution | Report | 17345 | 0.038863 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Dug up
On arrival crew isolated supply, repairs pending | 24 OLD LEAKES ROAD, ROCKBANK VIC 3335 | 30268315 | Vandalism;Copper theft | [6 empty] | Customer reported that wire is sparking on pole outside this address, Crew found the site with live cables exposed and smoking, roughly 15m of cable was stolen across the road LIS 749433, a further 60 meters was stolen on a previous date, left isolated at pole LIS 111200. There was no fire, no reported injuries. | Services cable;Services pit | 2 | 2 | 2 |  | MLN021 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/06/2019 9:28 |  |  | 13916 | Roadway |  | 20190625PWA_01 | Infrastructure (network-based) | -37.7267 | 144.6542 | 1 | Powercor | Report | 17390 | 0.0068495 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
CFA on site and Extinguished Fire. Fault crew isolated supply and replaced failed LV fuse box with new. Damaged LV U/G cable replaced between pole electrical service pit. Supply restored | 1 TWITES ROAD, BENA VIC 3946 | LIS2008545 |  |  |  | Defective component |  |  |  | Ground fire reported at base of pole. MFB on site | Connection box | 0 | 0 | 0 |  | LGA23 | Fault crew attended and found LV fuse box had failed and melted. LV U/G cable had also suffered damage at the fuse box. Suspected bad connections at the LV Fuse box which resulted in fire. | Grassfire | 25/06/2019 10:14 | 1 | Localised: less than 10 sq.m | 13920 | Roadway |  | 20190626SPN_01 | Infrastructure (network-based) | -38.4562 | 145.7006 | 1 | AusNet Services Distribution | Report | 17396 | 0.030317 | Low voltage AC (<1kV) | Moorabbin Airport | 3946 | Bena | Connection
supply isolated crossarm replaced | 74 BARKLY STREET, WARRNAMBOOL VIC 3280 | 30544142 |  |  |  | Leakage |  |  |  | Call from customer reporting pole fire outside 74 barkly st. No ground fire, no injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WBL008 | Excessive leakage current | Pole-top fire | 26/04/2019 0:45 | 1 | Negligible: no ground fire | 13945 | Roadway |  | 20190701PWA_08 | Infrastructure (network-based) | -38.3859 | 142.4916 | 1 | Powercor | Report | 17423 | 0.034684 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Crossarm
On arrival supply isolated and repairs completed | 1298 STRATHALLAN ROAD, BAMAWM VIC 3561 | 32179127 |  | Blown branch/vegetation |  |  |  |  | 1 | During wind storm Large Cyprus tree on the other side of the road fell across conductors. The impact brought conductors to ground and fractured pole 10 . There was no fire and no reported injuries | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | ECA012 | Severe wind storm | Significant disruption to the community;Damage to network assets | 29/06/2019 4:34 |  |  | 13946 |  |  | 20190702PWA_01 | Infrastructure (network-based) | -36.2564 | 144.6013 | 1 | Powercor | Report | 17425 | 0.041093 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3561 | Bamawm | Trees
Supply isolated repairs completed LEI checked installations for HVI | 3 HUNTER STREET, TATURA VIC 3616 | 33088665 |  | Blown branch/vegetation |  |  |  |  | 1 | High Winds brought Street Tree down across HV LV Cables in Hunter Street Tatura. All LV Cable on the ground and one phase of the HV. LEI in attendance to check for HVI. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | MNA014 | Severe wind storm | HV injection;Loss of supply;Significant disruption to the community;Damage to network assets | 29/06/2019 16:28 |  |  | 13947 | Roadway |  | 20190702PWA_02 | Infrastructure (network-based) | -36.4383 | 145.223 | 1 | Powercor | Report | 17427 | 0.026888 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3616 | Tatura | Trees
Supply isolated repairs completed | 3347 PYRENEES HIGHWAY, MOOLORT VIC 3465 | 30023583 |  | Blown branch/vegetation |  |  |  |  | 1 | Following MRO007 fdr lockout during wind storm report received of conductor broken and on the ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO007 | Wind blown debris hit line | Damage to network assets | 29/06/2019 14:46 |  |  | 13948 | Roadway |  | 20190702PWA_03 | Infrastructure (network-based) | -37.062 | 143.8781 | 1 | Powercor | Report | 17429 | 0.017366 | 22kV AC | Ballarat Aerodrome | 3347 | Moolort | Other
Crew removed the offending frond, assessed for damage & restored supply | 30 BENALLA ROAD, SHEPPARTON VIC 3630 | 31033732 |  | Within clearances | [5 empty] | Customer from "good guys warehouse" reported transformer fire at the incident location. Upon arrival crew found that a frond from an adjacent palm tree was making contact with the HV transformer dropper of "Zurcas 2E" substation, this caused the frond to burn due to the contact with the HV. 1 HV fuse operated at Zurcas 2E. No ground fire, injury or 3rd party damage transpired . | Dropper/bridge | 2 | 2 | 2 |  | STN021 | Palm Fond inside clearance | Other vegetation | 16/03/2019 12:27 | 1 | Negligible: no ground fire | 13952 | Roadway |  | 20190702PWA_05 | Infrastructure (network-based) | -36.3879 | 145.4267 | 1 | Powercor | Report | 17433 | 0.026862 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Trees
On arrival crew isolated supply and carried out repairs. | 180 BROWNS-SCARSDALE ROAD, SCARSDALE VIC 3351 | 30005437 |  |  |  | Unknown technical factor |  |  |  | VicFire reported a pole fire. On arrival the fault crew found a melted FOLCB at incident location. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS021 | Insufficient remains to determine cause. | Pole-top fire | 29/06/2019 0:16 | 1 | Negligible: no ground fire | 13956 | Roadway |  | 20190703PWA_01 | Infrastructure (network-based) | -37.6664 | 143.6739 | 1 | Powercor | Report | 17447 | 0.006147 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Scarsdale | Connection
An EIO and fault crew were dispatched to investigate. Testing by the EIO included voltage tests between an independent earth and various points of the installation. A voltage of 25V was measured. At the switchboard a voltage of 205V was measured between the Active and the Neutral bar. A visual inspection of the service cable revealed possible deterioration of the insulation. The fault crew replaced the service cable. All tests were repeated and passed, with volts measured to an independent earth of 1V. | 5 MARTIN STREET, MOUNT MARTHA VIC 3934 | 1314265 |  |  |  | Neutral fault |  | Phase to earth | 1 | UE received report of customer receiving tingles form sink in laundry and metal taps. | Service conductor;Aluminium twisted (grey) | 0 | 0 | 0 |  |  | It appears the deteriorated insulation of the service cable provided reduced insulation between active and neutral conductors. | Minor shock | 21/06/2019 15:15 |  |  | 13955 | Residential |  | 20190703UTD_01 | Infrastructure (customer connection) | -38.2843 | 144.9946 | 1 | United Energy Distribution | Report | 17446 | 0.0083924 | Low voltage AC (<1kV) | Moorabbin Airport | 3934 | Mount Martha | OH Cable
Fault Crew retired the Pole Connection Box and replaced the existing O/H Copper Neutral Screened Service with a new Twisted O/H Service Cable | 40 BOTANIC ROAD, WARRNAMBOOL VIC 3280 | 33100200 |  |  |  | Corrosion |  |  |  | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the shower taps and his bare feet whilst standing on the wet shower base. | Service conductor;Neutral screen;Connection box | 0 | 0 | 0 |  | WBL004 | Corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole. | Minor shock | 20/05/2019 10:00 |  |  | 13971 |  |  | 20190705PWA_04 | Infrastructure (network-based) | -38.3732 | 142.4888 | 1 | Powercor | Report | 17464 | 0.036012 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
fault crew remade the neutral connection at the pole | 357 ALBERT STREET, BRUNSWICK VIC 3056 | 30160346 |  |  |  | Corrosion |  |  | 2 | Person received an electric shock at the time when she made simultaneous contact with the metallic tap in the back yard with her hand whilst standing on the general mass of earth in bare feet. | Service conductor;Dropper/bridge | 0 | 0 | 0 |  | WB014 | Corroded Neutral connection at pole end | Minor shock | 28/04/2019 8:00 |  |  | 13973 | Residential |  | 20190705PWA_06 | Infrastructure (network-based) | -37.7681 | 144.956 | 1 | CitiPower | Report | 17466 | 0.0088831 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
The LV parallel list for Harold-Hurtle substation was amended and two additional parallels were closed restoring supply to the 92 customers affected. An investigation was conducted, refer to the "Notes and Findings" section for a copy of the report Key recommendations from the report are as follows: â€¢ Issue a reminder to all Operations Planner team members to ensure peer checking of switching instructions occurs prior to hand over to Network Operations and Control. â€¢ Implement a revised format for LV parallel lists with a check / closed step numbering aligning with the marked up circuit diagrams. â€¢ Issue a Memorandum to Network Coordinators to re-enforce the LV checking / clearing switching instruction process for LV parallels and LV isolations. | 52 WALTER STREET, ASCOT VALE VIC 3032 | [5 empty] | Ineffective planning/procedures/processes |  | 2 | Planned work was to be undertaken for the replacement of a HV/LV pole (A008424) in Newsome Street and HV cross arm replacement on pole A008423 in Newsome corner of Walter Street Ascot Vale. This required the isolation of HV and LV supplies to Hurtle-Newsom S/Stn, with all affected customers confirmed as notified. HV supply was also required to be isolated to Hillside-Hurtle S/Stn and Harold Hurtle S/Stnâ€™s. LV parallels were closed in accordance with the LV parallel list and marked up diagrams and substation LV isolators opened as per the switching instruction. At approximately 07:58hrs the Electricity Network Operator (ENO) in accordance with switching instruction (SWI # 67724 - Step 17) isolated the Low Voltage circuits at Harold-Hurtle S/Stn. A short time later a customer notified the crews on site that no customer notification had been given for the outage. The ENO in discussion with the Network Operations Supervisor confirmed that the LV parallels for Harold Hurtle S/Stn had been omitted. The SWI was amended to include two additional LV parallels, these two open points were closed and supply was restored to the affected customers. The ENO continued to switch the network as per the SWI. As a result of this switching error the interruption affected 92 customers for approximately 3 minutes. No special needs or life support customers were affected by this outage. | Transformer | 0 | 0 | 0 |  |  | The root cause of this incident can be attributed to a planned switching and isolation task. The major contributing factors were: â€¢ An incorrect and incomplete version of the LV parallel list was attached to the HV switching instruction, which led to parallels not being closed to maintain customer supplies. â€¢ Operations planner peer checking and Network Operations Control Room checking and clearing process did not prevent the error and unplanned customer supply interruption. | Loss of supply | 23/05/2019 7:58 |  |  | 13982 | Residential |  | 20190708JEM_01 | Infrastructure (network-based) | -37.7732 | 144.906 | 1 | Jemena | Report | 17480 | 0.010898 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Ascot Vale | Other
Fault crew dispatched. Damaged FOLCB removed and replaced with new. Supply restored | 490 COOPER STREET, EPPING VIC 3076 | LIS5712445 |  |  |  | Defective component |  |  |  | MFB report pole fire at FOLCB | Connection box | 0 | 0 | 0 |  | EPG34 | Fuse box failure believed to be due to poor connections | Pole-top fire | 43562.9437 | 1 | Negligible: no ground fire | 13978 |  |  | 20190708SPN_04 | Infrastructure (network-based) | -37.6453 | 144.9756 | 1 | AusNet Services Distribution | Report | 17475 | 0.026976 | Low voltage AC (<1kV) | Essendon Airport | 3076 | Epping | Connection
Fault crew dispatched to investigate. Supply isolated and damaged street light removed and replaced with new | 1 JEFFREY STREET, HAMPTON PARK VIC 3976 | LIS505164 |  |  |  | Defective component |  |  |  | report of street light fire | Public lighting | 0 | 0 | 0 |  | HPK23 | Street light on pole LIS505164 caught fire and burnt. Fire likely resulted from failed ignitor or PE Cell. | Pole-top fire | 43531.8222 | 1 | Negligible: no ground fire | 13979 |  |  | 20190708SPN_05 | Infrastructure (network-based) | -38.0382 | 145.2548 | 1 | AusNet Services Distribution | Report | 17477 | 0.034593 | Low voltage AC (<1kV) | Moorabbin Airport | 3976 | Hampton Park | AF Other
Fault crews attended and removed the device under access authority conditions. Notification has been raised to remove the out of service conductors. | 1099 SPRINGVALE ROAD, KEYSBOROUGH VIC 3173 | 637149 | Theft;Copper theft | [5 empty] | 2 | A Zinfra network operator, whilst driving, noticed an unusual device, with a rope to the ground, attached to an out of service HV overhead line. On closer inspection, it was discovered the device was a "home made" cutting device, intended to cut the OH conductor. | Conductor (bare);Steel | 2 | 2 | 2 |  | NP34 | The attempted conductor theft by unknown persons failed as the home made cutters were not able to cut the steel conductor. It appears the cutters were installed onto the line using some form of long stick. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/06/2019 14:30 |  |  | 13984 | Public space |  | 20190708UTD_01 | Infrastructure (network-based) | -38.0162 | 145.1402 | 1 | United Energy Distribution | Report | 17482 | 0.039743 | 22kV AC | Moorabbin Airport | 3173 | Keysborough | Other
No action taken as the meter and service ar not longer there. | 8 WICKLOW STREET, PASCOE VALE VIC 3044 |  | Theft;Unauthorised work | [5 empty] | 2 | Metering & Service crews attended the site for an abolishment of supply and metering in conjunction with a new connection for an overhead BTS pole. When the crew arrived they found a demolished and vacant site prepared for a new construction with no service line or metering on site. | Service conductor;Smart meter | 2 | 2 | 2 |  |  | Unknown persons removed Jemena service and meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43531.4653 |  |  | 14007 | Residential |  | 20190716JEM_01 | Infrastructure (customer connection) | -37.7187 | 144.9432 | 2 | Jemena | Report | 17508 | 0.011691 | Low voltage AC (<1kV) | Essendon Airport | 3044 | Pascoe Vale | Other
Site made safe New connection has been put on hold until the No Go Zone issue has been resolved | 18 WARRAGUL STREET, DALLAS VIC 3047 |  | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | No Go Zone assessor visited 18 Warragul St Dallas and found the overhead service cable supplying 16 Warragul St crossing the boundary was making contact with the new structure's roof at 18 Warragul St The service cable had tiger battens installed where contact had been made with the roof structure Neither Zinfra or Jemena had installed the battens on the overhead service. It is unknown where the tiger battens came from and who had installed them The underground cable is also exposed from the pit to the meter which is in use There is no record of a Jemena No Go Zone request for assessment or permit to work for this work site Photos and a copy of the Electrical Works Request (EWR) are attached in the "Notes & Findings" section. | Conductor (ABC) | 0 | 0 | 0 |  | BD11 | The builder had not contacted Jemena for a No Go Zone assessment or permit to work, prior to building the new house and making contact with the adjacent property's overhead service | No Go Zone (contact) | 43531.3153 |  |  | 14011 | Residential |  | 20190717JEM_01 | Infrastructure (network-based) | -37.67 | 144.9347 | 1 | Jemena | Report | 17651 | 0.028808 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Dallas | Other
Fault crew dispatched. Failed 250W HPS street light removed and replaced with new | 70 GRANGE BOULEVARD, BUNDOORA VIC 3083 | LIS906948 |  |  |  | Defective component |  |  |  | Report of street light fire. | Public lighting | 0 | 0 | 0 |  | WT9 | 250W HPS street light has failed and caught fire. Investigation concluded the fire originated at the terminal block within the luminaire as a result of an unknown failure. | Pole-top fire | 43806.9799 | 1 | Negligible: no ground fire | 14018 | Public space |  | 20190717SPN_01 | Infrastructure (network-based) | -37.7089 | 145.051 | 2 | AusNet Services Distribution | Report | 17533 | 0.026597 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Bundoora | AF Other
Fault crew dispatched. Site made safe and switch bypassed to restore supply to customers. Failed switch replaced with new at followup visit | 12 TENNYSON AVENUE, KILSYTH VIC 3137 | LIS1005921 |  |  |  | Defective component |  |  | 2 | Pole fire reported by customer | Disconnector/isolator | 0 | 0 | 0 |  | CYN13 | The centre phase bushing of the manual gas switch has failed resulting in fire. The fire was contained on the pole top and there was no evidence of ground fire. The investigation was inconclusive and the exact cause of the bushing failure and subsequent fire is unknown at this time. | Pole-top fire | 15/07/2019 9:00 | 1 | Negligible: no ground fire | 14020 | Roadway |  | 20190717SPN_03 | Infrastructure (network-based) | -37.8037 | 145.3057 | 1 | AusNet Services Distribution | Report | 17537 | 0.006956 | 22kV AC | Moorabbin Airport | 3137 | Kilsyth | Connection
Repairs made to the damaged underground cable | 40 MONOMEATH DRIVE, MICKLEHAM VIC 3064 |  | Copper theft | [5 empty] | 2 | Attempted copper theft from service pit of underground cable. | Cable | 2 | 2 | 2 |  |  | Unknown person tried to steal copper from the pit | Damage to network assets | 15/07/2019 16:33 |  |  | 14021 | Roadway |  | 20190718JEM_01 | Infrastructure (network-based) | -37.5269 | 144.9121 | 1 | Jemena | Report | 17538 | 0.027271 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3064 | Mickleham | Other
The pole and pole butt have been taken to the Tullamarine Depot and quarantined. The incident was reported to Worksafe 12:48 pm, they deemed it a non-reportable incident and would not attend site ESV were notified Inc Number : 12132279, they would not attend site will contact Jemena on Monday for further information. | 35 Cowper St, Footscray VIC 3011, Australia | 33756474 | Vehicle |  |  |  | Followed but inappropriate |  | 1 | During the planned works (Cowper Street south of Winfield street in Footscray - 4 spans of HV & LV to be converted to underground) a pole fell hitting a Jemena truck cabin breaking the windscreen and damaging the cabin. The pole and pole butt have been taken to the Tullamarine Depot, quarantined for investigations. Final incident investigation is attached in the "Notes & Findings" section. | Pole (wood) | 0 | 0 | 0 |  | FE6 | Contributing Factors towards the pole failure were identified as follows: The work crew did not complete a detailed assessment of the poles within the work zone to establish their serviceability prior to the commencement of work The work crew did not temporarily support the pole prior to creating an unknown out of balance load on it The pole had suffered significant vehicle impact fractures rendering it Unserviceable The asset inspector failed to interpret assessment results for the pole as Limited Life at its last programmed inspection (Oct 2017) | Damage to network assets | 20/07/2019 11:30 |  |  | 14030 | Commercial |  | 20190722JEM_01 | Infrastructure (network-based) | -37.8011 | 144.9044 | 1 | Jemena | Report | 18232 | 0.031652 | 22kV AC | Essendon Airport | 3011 | Footscray | Pole
Made safe, repaired and restored supply. | 43 CHEDDAR ROAD, RESERVOIR VIC 3073 | A031770 or A031771 | Vehicle |  |  | Conductor clashing |  |  | 1 | A vehicle hit stay wire on HV/LV pole causing the HV conductors to clash and 2phs came down to ground. | Conductor (bare) | 0 | 0 | 0 |  | TT10 | A vehicle impact with the stay wire causing it to exert force on the pole, causing the HV conductors to sway resulting in conductor clashing. The HV conductors were not strung tightly because this will have the undesirable pull on the pole (older construction with skinny conductors). | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/07/2019 6:55 |  |  | 14038 | Residential |  | 20190722JEM_02 | Infrastructure (network-based) | -37.7103 | 145.0117 | 1 | Jemena | Report | 17559 | 0.019998 | 22kV AC | Essendon Airport | 3073 | Reservoir | Vehicle
On arrival crew inspected assets , no damage noted. | 1 SPRINGFIELD DRIVE, MILDURA VIC 3500 | 30333970 |  | Bird | [5 empty] | Call received from Vic Fire of pole fire at incident location. On arrival crew found a small burnt area of nature reserve adjacent to a concrete pole. CFA had extinguished the fire. There were no reported injuries or third party property damage. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | MDA034 | Bird Incident | Grassfire | 19/07/2019 12:00 | 1 | Localised: less than 10 sq.m | 14028 | Roadway |  | 20190722PWA_01 | Infrastructure (network-based) | -34.2134 | 142.1484 | 1 | Powercor | Report | 17547 | 0.01628 | 22kV AC | Mildura Airport | 3500 | Mildura | Animal
On arrival crew isolated supply and carried out repairs. | 2B WAIORA ROAD, CAULFIELD NORTH VIC 3161 | 30219934 | Vehicle | [6 empty] | Resident reported Coles truck struck a large tree branch that has fallen and brought down wires at the above incident location. On arrival, the crew found a Low Voltage (LV) overhead service cable had been pulled down by a tree branch that a Coles truck had struck. There was no fire, no reported injuries. | Service conductor | 2 | 2 | 2 |  | AR004 | Vegetation: Trees Incident | Damage to network assets | 43776.6653 |  |  | 14037 | Roadway |  | 20190722PWA_06 | Infrastructure (network-based) | -37.8639 | 145.0152 | 1 | CitiPower | Report | 17558 | 0.01215 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Vehicle
On arrival crew isolated supply and carried out repairs | 1 JAMES STREET, PORT FAIRY VIC 3284 | 33101343 |  |  |  | Rot |  |  |  | A customer reported wires on the ground at the incident location. Upon arrival, a crew found that an LV crossarm had broken allowing the LV conductors to contact the ground. Where the conductors were in contact with ground they were observed to be emitting steam. The wet condition did not allow a fire ignition. No injuries or third party damages have been reported. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | KRT022 | Crossarm failure presumed due to internal decay | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43776.4125 |  |  | 14039 | Public space |  | 20190723PWA_01 | Infrastructure (network-based) | -38.3888 | 142.2334 | 1 | Powercor | Report | 17562 | 0.008316 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Crossarm
The crew isolated supply and made area safe to undertake repairs. | 34A-36A MCINTYRE ROAD, SUNSHINE NORTH VIC 3020 | 31024013 | Vehicle | [6 empty] | Emergency services reported that a car had hit a pole and wires were on the ground at the incident location. Pole leaning at 45 degrees, wires were previously arching and sparking and over a road On arrival the crew found that a car had hit the HV/LV pole LIS-15176 at 36 McIntyre road, resulting in the pole leaning approximately at 45 degrees toward the roadside and the LV overhead conductors across the road were hanging less than 1 meter from the to ground. Driver transported to hospital. There was no fire, no HVI reported | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SSE012 | Vehicle collided with pole | Significant disruption to the community;Damage to network assets | 23/07/2019 4:35 |  |  | 14060 | Roadway |  | 20190725PWA_02 | Infrastructure (network-based) | -37.774 | 144.8294 | 1 | Powercor | Report | 17585 | 0.019799 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3020 | Sunshine North | Vehicle
UE dispatched a fault crew. On attendance, the fire was out. Repairs to the underground cable were instigated. | 318 BURWOOD HIGHWAY, BURWOOD VIC 3125 |  |  |  |  | Overheated connection |  |  | 1 | UE received a report from the fire authority of a fire in a service pit. The pit is located in the median strip in Burwood Hwy. On attendance, the fire in the pit was out. | Services pit | 0 | 0 | 0 |  |  | The cause was not evident, but may be attributed to a loose connection or moisture ingress resulting in overheating. | Plant/equipment | 17/07/2019 6:25 | 1 | Negligible: no ground fire | 14057 | Roadway |  | 20190725UTD_01 | Infrastructure (network-based) | -37.8511 | 145.1222 | 1 | United Energy Distribution | Report | 17582 | 0.030297 | Low voltage AC (<1kV) | Moorabbin Airport | 3125 | Burwood | Connection
Further to advising the customer to attend hospital, UE dispatched an EIO and fault crew to investigate. On attendance, it was noted that the cover for the FOLCB was on the deck. The EIO arranged for supply to be disconnected from the pole and issued a defect for the height of the FOLCB. The customer went to her local medical clinic (Chelsea Heights Medical Centre, 205 Thames Promenade, Chelsea Heights) where she was referred to Frankston Hospital Emergency Department due to anomalous readings in her ECG. | 80 ARGYLE AVENUE, CHELSEA VIC 3196 | [5 empty] | Unknown work practice factor | Phase to earth | 2 | UE received report from customer of POA sparking and power going off. Customer also reported that she touched the connection box with her broom and now has tingles down one side. The customer was advised to go to hospital asap. | Connection box | 0 | 0 | 0 |  |  | Mrs Holloway received an electric shock while she was dusting the outside of the house with a damp plastic handled duster in preparation for vacating the property when she made simultaneous contact with the uncovered Fused Overhead Line Connection Box and the wet timber deck. It is unclear why the connection box cover had fallen. It is known that a crew had attended the premise in May to reconnect supply after a defect on the FOLCB had been actioned. UE is investigating with Zinfra on possible error by the attending crew in May. For the purpose of this report, the cause is likely to be attributed to a work practice issue. | Medical attention (first aid/doctor/hospital) | 13/07/2019 20:22 |  |  | 14058 | Residential |  | 20190725UTD_02 | Infrastructure (customer connection) | -38.0536 | 145.1261 | 1 | United Energy Distribution | Report | 17583 | 0.013363 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Other
UE dispatched a fault crew. On arrival, the fire authority were in attendance where an excavator had hit and damaged the overhead LV conductors emanating from Dandenong Hastings McKays 2S pole substation. The crew made repairs to the damaged conductors, and replaced blown LV fuses to restore supply. | 1290 DANDENONG-HASTINGS ROAD, CRANBOURNE SOUTH VIC 3977 | 3301218 | Working too close to overhead lines | [5 empty] | 1 | UE received a report of an excavator making contact with powerlines. | Conductor (bare) | 0 | 0 | 0 |  |  | A third party contractor was undertaking excavation works under the overhead LV lines and made contact with the lines. There was no No Go Zone request for the excavation works at this site. | Damage to network assets | 18/07/2019 14:45 |  |  | 14062 | Roadway |  | 20190725UTD_03 | Infrastructure (network-based) | -38.15 | 145.2256 | 1 | United Energy Distribution | Report | 17587 | 0.010916 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne South | Vehicle
On arrival crew isolated supply and carried out repairs | 310 HORNE ROAD, WARRNAMBOOL VIC 3280 | 30241936 |  |  |  | Leakage |  |  |  | A customer reported a smoking pole at the incident location. On arrival crew found pole top smoking and evidence of previous fire. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | WBL005 | Excessive leakage current | Pole-top fire | 16/07/2019 11:38 | 1 | Negligible: no ground fire | 14069 | Agricultural |  | 20190729PWA_01 | Infrastructure (network-based) | -38.3592 | 142.5391 | 1 | Powercor | Report | 17595 | 0.022411 | 12.7kV AC (SWER) | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
On arrival crew isolated supply and carried out repairs. | MALLEE HIGHWAY, MANANGATANG VIC 3546 | 30099720 |  |  |  | Leakage |  |  |  | Report from customer of burnt crossarm and conductors hanging low. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN003 | Excessive leakage current | Pole-top fire | 43469.4097 | 1 | Negligible: no ground fire | 14080 | Agricultural |  | 20190730PWA_06 | Infrastructure (network-based) | -35.0266 | 142.7464 | 1 | Powercor | Report | 17620 | 0.027211 | 22kV AC | Swan Hill Aerodrome | 3546 | Manangatang | Crossarm
Fault crews made site safe and repaired | 706 GILBERT ROAD, RESERVOIR VIC 3073 | A149446 | Vehicle |  |  |  |  | Phase to earth | 1 | A truck with an Excavator on tray has struck the Optus line and brought down pole and conductors | Conductor (bare);Pole (wood);Communication cable/equipment | 0 | 0 | 1 | Optus, Telstra and Foxtel lines down | CN07 | A truck with an Excavator on tray has struck the Optus line and brought down pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43685.4271 |  |  | 14097 | Residential |  | 20190808JEM_03 | Infrastructure (network-based) | -37.7196 | 144.9934 | 1 | Jemena | Report | 18466 | 0.016325 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3073 | Reservoir | Vehicle
The attending Powercor Fault Crew replaced the existing OH Service Cable and waited on site for an LEI to attend to complete the investigation | 10 DANIEL DRIVE, MORIAC VIC 3240 | 30075571 |  |  |  | Corrosion |  |  | 1 | person was in the Bathroom showering and reported receiving a slight electric shock when he made simultaneous contact between his hand on the shower tap and his bare feet while standing on the wet conductive shower base. | Aluminium twisted (grey);POA connection (network side) | 0 | 0 | 0 |  | WIN022 | Corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customer's POA. | Minor shock | 30/06/2019 10:44 |  |  | 14127 | Residential |  | 20190813PWA_06 | Infrastructure (customer connection) | -38.2435 | 144.1709 | 1 | Powercor | Report | 17675 | 0.023454 | Low voltage AC (<1kV) | Avalon Airport | 3240 | Moriac | Connection
Fault Crew inserted a Temporary Neutral Conductor Bridge to bypass the corroded Macintyre Sleeve Joint on the O/H Neutral Reticulation Conductor and remade all connections | 12 WATERSUN ROAD, JAN JUC VIC 3228 | 30264629 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom showering when she received an electric shock as she made simultaneous contact with her hand on the metal tap and her bare feet while standing on the wet conductive shower base. | Conductor (bare) | 0 | 0 | 0 |  | WPD021 | Corroded Macintyre Sleeve Joint on the O/H Neutral Reticulation Conductor | Minor shock | 15/07/2019 10:00 |  |  | 14128 | Residential |  | 20190813PWA_07 | Infrastructure (network-based) | -38.3525 | 144.2931 | 1 | Powercor | Report | 17676 | 0.030376 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc | Connection
Fault crew attended and made safe. | Blackhill Rd, Toolern Vale VIC 3337, Australia | 30109671 | Copper theft | [6 empty] | Customer reported theft of underground service cable resulting in loss of supply to single customer. On arrival crew observed pit lid removed and service cable removed. There was no fire, no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN012 | Copper theft | Damage to network assets | 43473.0806 |  |  | 14129 | Roadway |  | 20190813PWA_08 | Infrastructure (network-based) | -37.6247 | 144.6497 | 1 | Powercor | Report | 17677 | 0.0067627 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
On arrival crew isolated supply and carried out repairs. | 559 Coburns Rd, Melton West VIC 3337, Australia | 30344876 | Vandalism;Copper theft | [6 empty] | Customer reported: Pit lid is missing. Pit vandalised, wires exposed and street lights not working. Copper theft: stole 1bay of 60 meters of 16 mm cable supplying 2 PL poles from lis number 851752 to 851753. There was no fire, no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN032 | Copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43504.0681 |  |  | 14130 | Roadway |  | 20190813PWA_09 | Infrastructure (network-based) | -37.6523 | 144.5744 | 1 | Powercor | Report | 17678 | 0.012881 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Melton West | Other
UE dispatched a fault crew to investigate the loss of supply. Once informed by the customer of receiving a shock, an EIO was also dispatched. The EIO undertook testing, and found 5 volts present on the neutral. The fault crew checked the connections in the pole mounted connection box and found the neutral terminal was corroded. The connection was repaired and testing confirmed that the voltage reduced to 1 volt on the neutral. | 11 POTTER STREET, BLACK ROCK VIC 3193 | 9825102 |  |  |  | Corrosion;Neutral fault |  | Phase to earth | 1 | UE received a call from a customer advising of a loss of supply. On attendance, the customer also advised that her husband had received a shock from the meter box. | Connection box | 0 | 0 | 0 |  |  | The cause was a corroded neutral connection in the pole mounted connection box. | Minor shock | 43593.4306 |  |  | 14147 | Residential |  | 20190814UTD_04 | Infrastructure (network-based) | -37.9632 | 145.0138 | 1 | United Energy Distribution | Report | 17696 | 0.0097373 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Black Rock | Connection
Site made safe | 167 EASTWOOD STREET, KENSINGTON VIC 3031 | A030298 |  |  |  | Leakage |  |  | 1 | Pole top fire There are no photos available This fire start was found to be a reportable incident during the annual review of 2018-19 AER F-factor reportable fire starts | Crossarm (wood) | 0 | 0 | 0 |  | WMTSFT1 | Pole top fire due to tracking | Pole-top fire | 43413.6375 | 1 | Negligible: no ground fire | 14168 | Residential |  | 20190819JEM_01 | Infrastructure (network-based) | -37.7963 | 144.9317 | 1 | Jemena | Report | 17726 | 0.0080313 | 66kV AC | Essendon Airport | 3031 | Kensington | Pole
MFB extinguished the fire Site made safe and public lighting lantern was replaced | 135A BELL STREET, COBURG VIC 3058 | A111280 |  |  |  | Defective component |  |  | 2 | Public lighting lantern High pressure sodium (HPS) luminaire fire This fire start was found to be a reportable incident during the annual review of 2018-19 AER F-factor reportable fire starts There were no photos available for this incident | Public lighting | 0 | 0 | 0 |  | CS03 | Public lighting lantern failure | Other electricity related | 43292.8271 | 1 | Negligible: no ground fire | 14169 | Public space |  | 20190819JEM_02 | Infrastructure (network-based) | -37.7411 | 144.9637 | 1 | Jemena | Report | 17835 | 0.018168 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | AF Other
Site made safe and public lighting lantern replaced | 144 BOLDREWOOD PARADE, RESERVOIR VIC 3073 | A034511 |  |  |  | Defective component |  |  | 2 | Public lighting lantern High Pressure Sodium (HPS) luminaire fire This fire start was found to be a reportable incident during the annual review of 2018-19 AER F-factor reportable fire starts There were no photos available for this incident | Public lighting | 0 | 0 | 0 |  | TT0-011 | Public lighting lantern fire | Other electricity related | 25/12/2018 5:32 | 1 | Negligible: no ground fire | 14170 | Residential |  | 20190819JEM_03 | Infrastructure (network-based) | -37.7124 | 145.0228 | 1 | Jemena | Report | 17840 | 0.023422 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | AF Other
Site made safe and crossarm replaced | 207 LIBERTY PARADE, HEIDELBERG WEST VIC 3081 | A039071 |  |  |  | Leakage |  |  | 2 | Crossarm fire due to tracking This fire start was found to be a reportable incident during the annual review of 2018-19 AER F-factor reportable fire starts Photo is attached in the "Notes & Findings" section | Crossarm (wood) | 0 | 0 | 0 |  | TTSEP | Pole top fire due to tracking | Pole-top fire | 43648.0257 | 1 | Negligible: no ground fire | 14172 | Residential |  | 20190819JEM_04 | Infrastructure (network-based) | -37.7439 | 145.0356 | 1 | Jemena | Report | 17730 | 0.029022 | 66kV AC | Essendon Airport | 3081 | Heidelberg West | Crossarm
Candled Powder Filled fuse removed and replaced with new | 56-72 CANTERBURY ROAD, MONTROSE VIC 3765 | LIS1005239 |  |  |  | Candled fuse |  |  |  | Report of candled HV fuse | Powder filled | 0 | 0 | 0 |  | CYN21 | Fuse appears to have been damaged, allowing water to enter the fuse element resulting in fuse candling. | Pole-top fire | 15/08/2019 10:00 | 1 | Negligible: no ground fire | 14194 | Commercial |  | 20190821SPN_06 | Infrastructure (network-based) | -37.8168 | 145.3258 | 2 | AusNet Services Distribution | Report | 17935 | 0.024027 | 22kV AC | Moorabbin Airport | 3765 | Montrose | Fuse
Fault crew dispatched. Fire was extinguished by fire bridage. Failed FOLCB removed and replaced with new. Supply restored. | 1395 BASS HIGHWAY, GRANTVILLE VIC 3984 | Pole LIS 2802989 |  |  |  | Defective component;Unknown technical factor |  |  |  | Report of FOLCB fire | Connection box | 0 | 0 | 0 |  | LLG13 | A faults crew was called to a pole fire and, upon arrival, the crew found an FOLCB that had caught fire. No evidence of ground fire. The FOLCB was completely destroyed and it was not possible to determine the cause of the failure and subsequent fire due to the amount of damage. The FOLCB had melted and molten plastic fell to the ground but did not cause a ground fire as conditions were very wet. | Pole-top fire | 19/08/2019 11:57 | 1 | Negligible: no ground fire | 14196 |  |  | 20190821SPN_07 | Infrastructure (network-based) | -38.3996 | 145.5374 | 2 | AusNet Services Distribution | Report | 17936 | 0.030162 | Low voltage AC (<1kV) | Moorabbin Airport | 3984 | Grantville | Connection
The UE fault crew isolated the transformer and removed the birds nest. The transformer was replaced under access authority conditions. | LOT 16 GERARDS WAY, TYABB VIC 3913 | 1112692 |  | Bird |  |  |  |  | 1 | UE received reports of loss of supply to four customers in Tyabb. On attendance, the fault crew found a birds nest on the pole transformer had caught fire and burnt the transformer bushings, and resulted in the operation of a HV fuse. | Pole mounted | 0 | 1 | 0 |  | HGS22 | Bird Incident | Other vegetation | 43685.0924 | 1 | Negligible: no ground fire | 14189 | Roadway |  | 20190821UTD_02 | Infrastructure (network-based) | -38.2749 | 145.1596 | 1 | United Energy Distribution | Report | 17814 | 0.034775 | 22kV AC | Moorabbin Airport | 3913 | Tyabb | Animal
UE dispatched a fault crew and an EIO to investigate. On inspection, it was found that the neutral connection was burnt off at the mains connection box, and the mains connection box was found to be damaged. The faults crew disconnected supply at pole and POA and issued a defect for an REC to complete rectification works. | 32 HOURIGAN AVENUE, CLAYTON VIC 3168 |  |  |  |  | Customer installation connection box.;Neutral fault;Other |  | Phase to earth | 1 | The UE networks Analytics system identified an installation with voltage issues. Soon after, the customer reported receiving tingles from the taps. | POA connection (customer side) | 0 | 0 | 0 |  |  | The cause of the neutral failure and subsequent tingles was the damaged customer FOLCB. | Minor shock | 43777.4868 |  |  | 14197 | Residential |  | 20190821UTD_04 | Infrastructure (customer connection) | -37.9179 | 145.1248 | 1 | United Energy Distribution | Report | 17823 | 0.039311 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Installation
UE dispatched a fault crew to investigate the outage. On attendance they found a broken HV fuse unit had made contact with LV conductors. An EIO was called in to investigate for damage to installation wiring and appliances. The EIO confirmed that HVI had occurred with damage found to some installations. The fault crew undertook emergency switching to isolate the faulty section, and proceeded to make repairs under access authority conditions. The procedure as indicated in the work instruction for HV injections has been followed for restoring supply to affected customers. | 179 DEVONPORT DRIVE, FINGAL VIC 3939 | 1306046 |  |  |  | Mechanical breakdown |  |  | 1 | UE received call from customer advising of loss of supply with a subsequent call stating sparks from wires. On attendance, crews found during the wind event of that day, a broken HV fuse unit made contact with the LV conductors below and resulted in a HVI to customer installations. | HV fuse assembly;Conductor (bare);Other | 0 | 0 | 0 |  | STO21 | The cause of the HVI was the failure of the HV fuse assembly unit which occurred during the high wind event of that day. | HV injection | 43716.3361 |  |  | 14199 | Roadway |  | 20190822UTD_01 | Infrastructure (network-based) | -38.413 | 144.8437 | 1 | United Energy Distribution | Report | 17825 | 0.014117 | 22kV AC | Moorabbin Airport | 3939 | Fingal | Fuse
UE dispatched an EIO and faults crew to investigate. Testing was conducted with and without load which showed a reading of 1.7V at shock points. The fault crew inspected overhead line and mains connection box and found customer neutral conductor burnt, loose and signs of heat damage. The property was isolated and defect issued for mains box replacement. The consumers mains also to be checked due to heat damage and may require replacement. | 3 SHEOKE GROVE, SORRENTO VIC 3943 |  |  |  |  | Neutral fault;Overheated connection |  | Phase to earth | 2 | UE received a report from an REC of air-conditioner contractors receiving tingles from air-conditioning pipes, and residents feeling tingles from outside shower tap. | POA connection (customer side) | 2 | 2 | 2 |  |  | The cause appears to be a loose or degraded connection which resulted in heat damage. | Minor shock | 16/08/2019 8:03 |  |  | 14203 | Residential |  | 20190822UTD_04 | Infrastructure (customer connection) | -38.36 | 144.7531 | 1 | United Energy Distribution | Report | 17829 | 0.0084491 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Installation
Fault crew dispatched. P/L removed and replaced with new | 334-338 BAYSWATER ROAD, BAYSWATER NORTH VIC 3153 | LIS1201602 |  |  |  | Defective component |  |  |  | Report of P/L fire on pole LIS1201602 | Public lighting | 0 | 0 | 0 |  | BWR23 | P/L fire on pole LIS1201602. P/L removed and replaced with new. Cause of failure unknown, Investigation inconclusive and did not determine cause of fire. | Pole-top fire | 43319.8653 | 1 | Negligible: no ground fire | 14216 | Roadway |  | 20190827SPN_01 | Infrastructure (network-based) | -37.8314 | 145.2692 | 2 | AusNet Services Distribution | Report | 17847 | 0.035602 | Low voltage AC (<1kV) | Moorabbin Airport | 3153 | Bayswater North | AF Other
Fault crew dispatched and supply isolated. Failed fused mains box removed and replaced with new. | RANKIN STREET, ALBERTON VIC 3971 | LIS2608518 |  |  |  | Overheated connection |  |  |  | Report of pole fire. Fused Mains box has burnt and melted. | Connection box | 0 | 0 | 0 |  | FTR23 | Fused Mains box has burnt and melted on pole LIS2608518. Hot joint/connection within the connection box likely due to proximity to coastal area. | Pole-top fire | 43111.3118 | 1 | Negligible: no ground fire | 14217 |  |  | 20190827SPN_02 | Infrastructure (network-based) | -38.6126 | 146.6594 | 1 | AusNet Services Distribution | Report | 17873 | 0.0031944 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3971 | Alberton | Fuse
Fault crew dispatched. P/L fitting removed and replaced with new | 144 COLCHESTER ROAD, BAYSWATER NORTH VIC 3153 | LIS1208636 |  |  |  | Defective component;Unknown technical factor |  |  |  | MFB report street light on fire | Public lighting | 0 | 0 | 0 |  | CYN13 | Street light has failed. Cause of failure unknown. Investigation conducted but inconclusive and unable to determine cause of failure. | Pole-top fire | 43138.7681 | 1 | Negligible: no ground fire | 14218 | Roadway |  | 20190827SPN_03 | Infrastructure (network-based) | -37.8158 | 145.3053 | 2 | AusNet Services Distribution | Report | 17850 | 0.028273 | Low voltage AC (<1kV) | Moorabbin Airport | 3153 | Bayswater North | AF Other
Fault crew dispatched and supply isolated in pit. Failed P/L fitting removed and replaced with new | 17 PRINCE STREET, ROSEDALE VIC 3847 | LIS2601128 |  |  |  | Defective component;Unknown technical factor |  |  |  | Report of street light fire on pole | Public lighting | 0 | 0 | 0 |  | TGN41 | P/L fitting has failed and melted. on pole. Failed P/L fitting removed and replaced with new. Cause of failure unknown. Investigation conducted but inconclusive and unable to determine cause of failure. | Pole-top fire | 19/07/2018 21:08 | 1 | Negligible: no ground fire | 14220 | Roadway |  | 20190827SPN_04 | Infrastructure (network-based) | -38.1514 | 146.7881 | 1 | AusNet Services Distribution | Report | 17913 | 0.0020972 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3847 | Rosedale | AF Other
A faults crew attended and checked for damage to the UG service cables, with no issues found. The damaged service pit was subsequently replaced. | 4 PLYMOUTH STREET, BENTLEIGH EAST VIC 3165 | 2318932 | Working too close to underground cables | [5 empty] | 2 | UE received a report from a building site supervisor that an excavator has pulled a service pit our of the ground. Supply to the site was no affected. | Services pit (network) | 0 | 0 | 0 |  |  | The cause was the civil works being undertaken for the site. | No Go Zone (contact);Damage to network assets | 13/08/2019 9:02 |  |  | 14225 | Construction |  | 20190828UTD_01 | Infrastructure (customer connection) | -37.92 | 145.0675 | 1 | United Energy Distribution | Report | 17863 | 0.01514 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Dug up
A UE Fault crew attended and isolated supply at the base of the pole. With traffic control in place, the Public Lighting lantern was replaced. | 15 FLETCHER ROAD, FRANKSTON VIC 3199 | 8819028 |  |  |  | Overheated connection |  |  | 1 | UE received a report of a street light on fire near the Bayside Shopping Centre. | Public lighting | 0 | 0 | 0 |  |  | The cause is unknown, but is likely due to an overheated connection. | Plant/equipment | 25/08/2019 23:49 | 1 | Negligible: no ground fire | 14227 | Roadway |  | 20190828UTD_03 | Infrastructure (network-based) | -38.1402 | 145.1271 | 1 | United Energy Distribution | Report | 17865 | 0.03338 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
The attending Powercor Fault Crew reterminated the existing U/G Service Neutral Conductor at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. The LEI also advised the Owner of the property to consider engaging an REC to investigate the installation of an Equipotential Earth Bonding Conductor to the Waste Water Pipe in the Bathroom Shower to minimise the risk of any potential difference between conductive building materials and the waste water pipe. | 2971 PRINCES HIGHWAY, PORT FAIRY VIC 3284 | 33102252 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Pauline Mathews was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Taps and her bare feet whilst standing on the wet shower base and metallic waste water outlet. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded U/G Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole, resulting in a higher than normal impedance within the neutral service conductor. | Connection box | 2 | 2 | 2 |  | KRT013 | Corroded neutral connection at pole | Minor shock | 43504.6458 |  |  | 14238 | Residential |  | 20190903PWA_01 | Infrastructure (network-based) | -38.3882 | 142.17 | 1 | Powercor | Report | 17883 | 0.013998 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Connection
The attending Powercor Fault Crew disconnected and removed the existing O/H Neutral Screened Service Cable pending electrical remediation work by the Customerâ€™s REC to replace the corroded Mains Connection Box at the POA and reterminate the existing Consumers Mains. The Installation was left OFF supply pending repairs by an REC. A Customer Installation Defect Notice was issued accordingly. | 37 HAVELOCK STREET, BEAUFORT VIC 3373 | 30011483 |  |  |  | Corrosion |  | Phase to earth |  | Mr Ryan Kopk was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Taps and his bare feet whilst standing on the wet shower base and waste water outlet. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Consumers Main Neutral Conductor termination at the Single Phase Mains Connection Box located at the Customerâ€™s POA, which was the cause of the high impedance in the neutral supply system. | POA connection (customer side) | 2 | 2 | 2 |  | BAS011 | Corroded Single Phase Mains Connection Box located at the Customerâ€™s POA. | Minor shock | 43473.875 |  |  | 14242 | Residential |  | 20190903PWA_02 | Infrastructure (customer connection) | -37.4325 | 143.385 | 1 | Powercor | Report | 17887 | 0.0065185 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3373 | Beaufort | Installation
Fault crews met police on site for report of illegal wiring. EIO arrived on site to investigate. Crews isolated supply at the pit and the site was made safe. EIO found the meter panel fuse had been tampered with. The meter wasn't bypassed, but the meter panel fuse was bypassed with a link which had evidence of arcing damage to the metal meter enclosure. | UNIT 3 38 GLENOLA ROAD, CHELSEA VIC 3196 | 3306158 | Illegal wiring |  |  |  |  | Phase to earth | 1 | UE contractor advised UE of suspected illegal wiring. Police were executing a search warrant and attempted to switch main breaker. Upon opening the meter panel, an officer received an electric shock. | Meter board (including fuses) | 0 | 0 | 0 |  | CRM15 | The cause was due to illegal wiring to bypass the meter fuse. | Minor shock (unconfirmed) | 20/11/2019 12:55 |  |  | 14545 | Residential |  | 20191127UTD_02 | Infrastructure (network-based) | -38.0557 | 145.1231 | 1 | United Energy Distribution | Report | 18341 | 0.022575 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Other
Voltage test between an independent earth and various points of the electrical installation including the distribution assets revealed a corroded neutral conductor service tail located at the POA. Supply to installation was disconnected by Powercor Faults Crew and no stray voltages where detected on 20/09/19 when tested by CTA. REC new Raiser Bracket, 1ph Mains, Main Switchboard and Earthing system. Customer. Supply reconnected by Faults Crew. LEI on site. | 409 SOUTH STREET, BALLARAT CENTRAL VIC 3350 | 30236223 |  |  |  | Corrosion |  | Phase to earth |  | Customer was showering at the time he received an electric shock when he made simultaneous contact with the metallic water tap with his hand whilst standing on the wet shower base. | Neutral screen;Connector/termination | 2 | 2 | 2 |  | BAS012 | corroded neutral conductor service tail | Minor shock | 20/07/2019 0:00 |  |  | 14550 | Residential |  | 20191128PWA_01 | Infrastructure (customer connection) | -37.5696 | 143.848 | 1 | Powercor | Report | 18346 | 0.037968 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat Central | Connection
On arrival crew isolated supply and carried out repairs. | 59 Johnston St, Port Melbourne VIC 3207, Australia | 30205440 | Vehicle | [6 empty] | MFB and member of the public (Leigh ph 0427319917) reported sparking and pole and wires on the ground. On arrival it was found a truck had made contact with optus catenary cable causing pole and conductors to fall to ground. Two cars were also damaged in the incident. There was no fire, no reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | AR003 | Truck contacted communication cables | Damage to network assets | 43535.6667 |  |  | 14558 | Roadway |  | 20191129PWA_01 | Infrastructure (network-based) | -37.8432 | 144.9437 | 1 | CitiPower | Report | 18355 | 0.032233 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Vehicle
Supply isolated repairs arranged | 42 Wiltshire Rd, Macedon VIC 3440, Australia | 30141744 | Copper theft | [6 empty] | Customer report of exposed cables. Crew found no damage or Copper stolen, just Pit Lids lifted/removed, Police on-site due to property theft at adjacent site. There was no report of fire or injuries | Services cable;Services pit (network) | 2 | 2 | 2 |  | WND011 | attempted Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43596.5625 |  |  | 14560 | Roadway |  | 20191129PWA_03 | Infrastructure (network-based) | -37.4374 | 144.5512 | 1 | Powercor | Report | 18357 | 0.027591 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
Crew made safe, 11kV switches opened and locked, substation de-energized. Note: Substation is scheduled to commence de-commissioning Monday 11/11/19. No need to restore stolen equipment. No FFU required. | 413 St Kilda Rd, Melbourne VIC 3004, Australia | CP0003477 | Copper theft | [6 empty] | Report of sub broken into and copper theft at 409 St Kilda Rd (R). substation. Crew attended substation to find door damaged by forced entry, the LV ACBs had been opened by the thieves then copper bus bar stolen form the substation. Note: Substation is scheduled to commence de-commissioning Monday 11/11/19. There was no reported fire or injuries. | Indoor | 2 | 2 | 2 |  | MP036 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43657.5 |  |  | 14564 | Commercial |  | 20191129PWA_06 | Infrastructure (network-based) | -37.8375 | 144.9761 | 1 | CitiPower | Report | 18361 | 0.035194 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Other
On arrival crew isolated supply and com[plated repairs. LEI attended due to reported HVI | 28 King Albert Ave, Leitchville VIC 3567, Australia | 30029109 |  |  |  | Leakage |  |  |  | Customer called reporting pole caught fire and smoldering. When crew arrived, they found that cross arm had burnt and outer phase (red phase) had dropped onto the LV cross arm. Crew called an LEI who attended and advised a HVI had occurred. No ground fire, no injuries that we have been made aware of. | Crossarm (wood) | 2 | 2 | 2 |  | CHA005 | Excessive leakage current | Pole-top fire;HV injection | 30/11/2019 8:47 | 1 | Negligible: no ground fire | 14570 | Roadway |  | 20191202PWA_02 | Infrastructure (network-based) | -35.9054 | 144.3014 | 1 | Powercor | Report | 18369 | 0.024185 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3567 | Leitchville | Crossarm
On arrival crew inspected assets for damage, followup raised to replace insulator | 5 Shorthorn Ct, Shepparton VIC 3630, Australia | 33095210 |  |  |  | Unknown technical factor |  |  |  | CFA reported pole fire that caused grass fire at the incident location. When crew arrived they found an area of burnt grass approx. 4m x 18m in road reserve. Crew inspected pole and found evidence of a flash over from burn marks on east side of HV insulator but couldn't find any evidence of what had caused it or when. There was no protection operations in the area. | Conductor (bare);Insulators | 2 | 2 | 2 |  | SHTSHN1 | Suspected flash-over no direct cause found | Grassfire | 30/11/2019 12:10 | 1 | Small: 10 - 1000 sq.m | 14572 | Roadway |  | 20191202PWA_04 | Infrastructure (network-based) | -36.3475 | 145.4117 | 1 | Powercor | Report | 18371 | 0.018897 | 66kV AC | Shepparton Airport | 3630 | Shepparton | AF Other
Fault crews attended the site and the site was made safe. Upon inspection, the bushing and leads to a gas switch installed on the pole were burnt out. Supply was isolated and the switch was replaced. | 66 PARER STREET, BURWOOD VIC 3125 | 7048034 |  |  |  | Incorrect design |  |  | 1 | UE received a call about flames on a wire hanging over the footpath. | Any other type | 0 | 0 | 0 |  | BW22 | The cause was the gas switch was not built to the current UE construction standard - there was excessive stress on the lead connections which caused the switch to fail. | Plant/equipment | 43566.9618 | 1 | Localised: less than 10 sq.m | 14579 | Roadway |  | 20191203UTD_02 | Infrastructure (network-based) | -37.8456 | 145.1045 | 1 | United Energy Distribution | Report | 18378 | 0.037137 | 11kV AC | Moorabbin Airport | 3125 | Burwood | AF Other
Fault crews patrolled the line and identified burnt marks on the bridging cross-arm. The cross-arm was subsequently replaced. | 226-236 WELLINGTON ROAD, CLAYTON VIC 3168 | 622882 |  |  |  | Leakage |  |  | 1 | UE detected a fault on the network and the CB operated to isolate the fault. | Crossarm (wood) | 0 | 0 | 0 |  | SVTS-EB | The cause was tracking across an insulator which burnt the wooden cross-arm. | Pole-top fire | 26/11/2019 6:10 | 1 | Negligible: no ground fire | 14581 | Roadway |  | 20191203UTD_04 | Infrastructure (network-based) | -37.9177 | 145.1492 | 1 | United Energy Distribution | Report | 18380 | 0.040648 | 66kV AC | Moorabbin Airport | 3168 | Clayton | Crossarm
On arrival crew isolated supply and carried out repairs. | 410 Perkins Rd, Cowangie VIC 3506, Australia | 32150598 |  |  |  | Leakage |  |  |  | Report from LSA Barry Gregg of pole fire at above address. Crew arrived and found pole that appeared to have been burning all day. There was a lot of burnt debris from the pole but no ground fire had occurred and commented that site was very sandy. No third party damage or injuries. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive l;leakage current | Pole-top fire | 30/11/2019 17:49 | 1 | Negligible: no ground fire | 14583 | Agricultural |  | 20191204PWA_02 | Infrastructure (network-based) | -35.3191 | 141.3634 | 1 | Powercor | Report | 18382 | 0.031025 | 22kV AC | Mildura Airport | 3506 | Cowangie | Pole
Crew repaired and reinstated cable from fuse units to pole to pit | 131-199 TOWNSINGS ROAD, DIGGERS REST VIC 3427 | A111909 | Copper theft | [5 empty] | 2 | Work crew advised copper stolen from fused modular junction box (MJB) at substation pole (Townsings Rd-P64 substation) | Services cable | 0 | 0 | 0 |  | SBY13 | Copper theft | Damage to network assets | 21/11/2019 11:19 |  |  | 14589 | Peri-urban |  | 20191205JEM_02 | Infrastructure (network-based) | -37.6066 | 144.6655 | 1 | Jemena | Report | 18411 | 0.022384 | Low voltage AC (<1kV) | Melbourne Airport | 3427 | Diggers Rest | Other
Fault crew dispatched. Candled HV fuse removed and replaced with new | 125 TROVATELLO PLACE, TYERS VIC 3844 | LIS2626341 |  |  |  | Candled fuse |  |  |  | Report of HV fuse Candling | EDO fuse | 0 | 0 | 0 |  | TGN31 | Candled HV fuse | Pole-top fire | 22/11/2019 23:30 | 1 | Negligible: no ground fire | 14592 |  |  | 20191205SPN_02 | Infrastructure (network-based) | -38.1287 | 146.4859 | 2 | AusNet Services Distribution | Report | 18414 | 0.021082 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Tyers | Fuse
On arrival crew crew patrolled line , replaced fuse | 1 Hipwell Rd, Gunbower VIC 3566, Australia | 33018378 |  |  |  | Fuse failed to eject |  |  |  | CFA reported a fire under a pole last night at the incident location and CFA extinguished the fire. Crew replaced HV fuse and believed small grass fire was from some time ago (no CFA on site) . On 5/12 following CFA advise crew re attended site and confirmed the fire area of 5*60m Sqm The crew also did not find the cause of fire or the fuse operation. | EDO fuse | 2 | 2 | 2 |  | CHA005 | fuse hung up | Grassfire | 43567.6028 | 1 | Small: 10 - 1000 sq.m | 14596 | Roadway |  | 20191206PWA_01 | Infrastructure (network-based) | -35.9416 | 144.3771 | 1 | Powercor | Report | 18420 | 0.0027813 | 22kV AC | Bendigo Airport | 3566 | Gunbower | Fuse
On arrival assets inspected no damage found | Leitchville-Kerang Rd, Leitchville VIC 3567, Australia | 33021956 |  | Bird | [5 empty] | CFA reported a ground fire at the incident location. On arrival, a Powercor crew found a 200 Sqm ground fire . There was no reported injuries or third party property damage. | Crossarm (steel);Pole (concrete) | 2 | 2 | 2 |  | CHA005 | Bird Incident | Grassfire | 43720.3583 | 1 | Small: 10 - 1000 sq.m | 14602 | Roadway |  | 20191209PWA_03 | Infrastructure (network-based) | -35.8997 | 144.2864 | 1 | Powercor | Report | 18430 | 0.011365 | 2.2kV AC | Bendigo Airport | 3567 | Leitchville | Animal
29 Customers Impacted. Operator patrolled area, identified cause, made safe and restored supply. Zinfra repaired a broken strand on HV overhead conductor that was still live at the time and found burn marks at a different location on the Phase that tripped today. The Zinfra Network Operators have spoken to the on-site supervisor and asked him to erect warning barricades to nominate an exclusion zone with warning signs advising live overhead powerlines. | 579 DIGGERS REST-COIMADAI ROAD, DIGGERS REST VIC 3427 | A011101 | Building too close or within the No Go Zone;Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | Zinfra Network Operators responded to a HV Fault where a 15A BA Fuse operated at #52280. On patrol of feeder found at 579 Diggers-Coimadai Rd Diggers Rest, a civil excavation company was reinstating a land fill and has now increased the natural level of the ground closer to the HV overhead conductor. It appeared that a tip truck had made contact with the HV overhead conductor on at least 2 occasions. No Permit to Work was issued | Conductor (bare) | 0 | 0 | 0 |  | SHM11 | No Go Zone breach | No Go Zone (contact) | 43720.3569 |  |  | 14609 | Construction |  | 20191210JEM_01 | Infrastructure (network-based) | -37.6299 | 144.6695 | 1 | Jemena | Report | 18438 | 0.0097581 | 22kV AC | Melbourne Airport | 3427 | Diggers Rest | Vehicle
on arrival crew made safe and organised repairs. | 81 Gordon Ave, Mildura VIC 3500, Australia | 30276448 | Vehicle | [6 empty] | A truck contacted a zone substation communication cable at the incident location. On arrival, a Powercor crew found that the comm. cable on the ground. It is believed the cable had become detached from a support pole and when contacted by the truck it has flicked up and contacted the overhead 22kv conductors. There was no fire or reported injuries. | Conductor (bare);Communication cable/equipment | 2 | 2 | 2 |  | MDA023 | Truck hit communication cable | Loss of supply;Damage to network assets | 43720.4625 |  |  | 14615 | Roadway |  | 20191210PWA_08 | Infrastructure (network-based) | -34.2431 | 142.1121 | 1 | Powercor | Report | 18464 | 0.0093218 | 22kV AC | Mildura Airport | 3500 | Mildura | Vehicle
On arrival crew isolated supply and arranged repairs. | Navan Park, Kurunjang VIC 3337, Australia | 30272150 | Copper theft | [6 empty] | Customer reported electricity pit has had lid removed (lid still onsite next to pit), wires are exposed, pit on nature strip on Navan park side of roundabout, corner Centenary ave but on the Coburns road side close to street light. On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen the LV Service Cable within the LV Service Pit supplying PL Lighting Poles. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN032 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43749.8139 |  |  | 14617 | Roadway |  | 20191210PWA_09 | Infrastructure (network-based) | -37.672 | 144.5705 | 1 | Powercor | Report | 18465 | 0.037066 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Other
On arrival crew made safe defect issued to customer for repairs to POA | 156 GREEN GULLY ROAD, KEALBA VIC 3021 | 32174180 | Vehicle | [6 empty] | Customer reported a delivery truck ripped out service wire from house end, still connected to pole and down over footpath and neighbor's driveway at the incident location. There was damage to the customers POA. There was no fire or reported injuries. | POA connection (network side);Service cable (insulated) | 2 | 2 | 2 |  | SA002 | Delivery van struck service line | Loss of supply;Damage to network assets | 13/11/2019 13:28 |  |  | 14628 | Residential |  | 20191211PWA_07 | Infrastructure (customer connection) | -37.7286 | 144.8192 | 1 | Powercor | Report | 18479 | 0.00027894 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kealba | Vehicle
On arrival crew inspected site replaced connectors and restored supply. | 121 James Melrose Dr, Brookfield VIC 3338, Australia | 30300201 | Copper theft | [6 empty] | Report received to advise of pits opened and cables exposed along James Melrose Drive. Upon arrival the fault crew found that thieves had attempted to steal the underground P/L service cable. but were unsuccessful in doing so, only managing to cut the pit connectors off within the pits at the base of 2 poles only. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/11/2019 11:56 |  |  | 14630 | Roadway |  | 20191211PWA_09 | Infrastructure (network-based) | -37.7104 | 144.556 | 1 | Powercor | Report | 18481 | 0.026918 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew isolated supply and carried out repairs. | 1686 Romsey Rd, Romsey VIC 3434, Australia | 32042999 |  |  |  | Mechanical breakdown |  |  |  | During a fault patrol a crew found a small ground fire (2 x 2 mtrs) at the incident location. The fault and fire was caused by a dislodged earth wire contacting an EDO fuse unit. There was no injuries or third party property damage. Fire was extinguished by fault crew | Pole mounted | 2 | 2 | 2 |  | WND012 | Dislodged earth wire | Grassfire | 43750.4674 | 1 | Localised: less than 10 sq.m | 14635 | Roadway |  | 20191212PWA_03 | Infrastructure (network-based) | -37.346 | 144.7028 | 1 | Powercor | Report | 18486 | 0.024539 | 22kV AC | Wallan (Kilmore Gap) | 3434 | Romsey | AF Other
On arrival crew isolated supply and carried out repairs. | 6 Exter La, Rockbank VIC 3335, Australia | 30542092 | Copper theft | [6 empty] | A passerby, named Chris, reported on Friday afternoon (22/11/19), that a pit at the base of pole LIS-864775 had a missing lid and cables were exposed. On arrival, the Crew found that 14 P/L service pits had their concrete lids removed and wires were cut and stolen. Approximately 400 meters of 4C copper cable were stolen. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/11/2019 16:52 |  |  | 14638 | Roadway |  | 20191212PWA_06 | Infrastructure (network-based) | -37.7167 | 144.6556 | 1 | Powercor | Report | 18489 | 0.022138 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply and arranged for repairs. | 56 Papas View, Wyndham Vale VIC 3024, Australia | 30555426 | Working too close to underground cables | [6 empty] | A contractor reported a cable dug up at the incident location. Upon arrival, the Powercor crew found that a Public lighting cable had been dug up by an excavator. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE014 | Excavator damaged cable | Damage to network assets | 29/11/2019 10:50 |  |  | 14640 | Roadway |  | 20191213PWA_02 | Infrastructure (network-based) | -37.8465 | 144.5908 | 1 | Powercor | Report | 18491 | 0.021819 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Dug up
An EIO attended the site to investigate. The EIO was advised that the customer received a shock to his right hand when he touched the pipe after removing a water meter at 7Eleven. 7Eleven and the car wash share the same supply pillar. NST tests at 7Eleven and the car wash both passed. There was no change to current or volts when the car wash was isolated. However, the current dropped from 2A-30A during normal shop operation, to 0.7A when 7Eleven was isolated. EIO issued a defect to 7Eleven. | 77 MITCHAM ROAD, DONVALE VIC 3111 |  |  |  |  | Unidentified customer fault |  | Phase to earth | 1 | UE received a call that a customer has received a shock from a large water meter while replacing the meter. | Customer wiring | 0 | 0 | 0 |  |  | The cause is likely to be the customer's wiring at 7Eleven. | Minor shock | 43567.0382 |  |  | 14647 | Commercial |  | 20191213UTD_03 | Infrastructure (customer connection) | -37.797 | 145.1799 | 1 | United Energy Distribution | Report | 18498 | 0.016056 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | Installation
Recapped supply underground cable in pit and made safe. | 550 RESERVOIR ROAD, SUNBURY VIC 3429 | A003443 | Copper theft | [5 empty] | 2 | Copper theft of LV underground cables from supply pit at base of transformer pole to approximately 25 metres from telecommunications hut top of hill. | Cable;Copper | 0 | 0 | 0 |  | SBY13 | Copper theft | Loss of supply | 15/12/2019 4:31 |  |  | 14649 | Roadway |  | 20191215JEM_01 | Infrastructure (customer connection) | -37.5681 | 144.6753 | 1 | Jemena | Report | 18500 | 0.034149 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Site made safe and crossarm replaced HV injection was ruled out | 53A MITCHELL PARADE, PASCOE VALE SOUTH VIC 3044 | A093964 |  |  |  | Rot |  |  | 1 | CS2 feeder trip, operator attended and found HV wires down on LV mains Crossarm failure had caused HV conductors to come down onto LV mains, resulting in pole top fire No photos are available for this incident | Conductor (bare);Aluminium | 0 | 0 | 0 |  | CS02 | Crossarm failure caused HV conductors to come down onto LV conductor | Pole-top fire;Loss of supply | 26/11/2019 5:45 | 1 | Negligible: no ground fire | 14658 | Residential |  | 20191217JEM_04 | Infrastructure (network-based) | -37.74 | 144.9343 | 1 | Jemena | Report | 18512 | 0.0052407 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3044 | Pascoe Vale South | Crossarm
Site made safe An LEI was required to investigate the potential high voltage injection following high voltage cables making contact with low voltage reticulation cables. The attending LEI conducted a thorough damage assessment of all accessible network and customer assets, recording no sings of damage or indication that a high voltage injection had taken place. Following the attending Jemena faults crew repairing the assets the LEI informed them that supply was safe to restore to the installations. | 8 MAIN STREET, COBURG VIC 3058 | A050129 |  |  |  | Rot |  |  | 1 | CS13 feeder trip. Report of "explosion", operator attended and found wires down but not on the ground. Damaged HV crossarm at pole A050129 outside 8 Main St, Coburg had resulted in HV conductors falling onto LV mains and starting a pole top fire Photos are unavailable for this fire start incident | Conductor (bare);Aluminium | 0 | 0 | 0 |  | CS13 | Damaged HV crossarm | Pole-top fire | 26/11/2019 6:34 | 1 | Negligible: no ground fire | 14659 | Residential |  | 20191217JEM_05 | Infrastructure (network-based) | -37.7403 | 144.9627 | 1 | Jemena | Report | 18538 | 0.01436 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3058 | Coburg | Crossarm
On arrival crew isolated supply and carried out repairs. LEI attended, no shock detected | 951 Mount Cottrell Rd, Melton South VIC 3338, Australia | 30341004 | Copper theft | [6 empty] | Following a customer report of a potential electric shock a fault crew attended the incident location. On arrival a crew found part of substation earth had been cut away (2 mtrs). There was no fire, no third party damage. | Earth/earthing | 2 | 2 | 2 |  | DPTS-MLN1 | Copper theft | Damage to network assets | 18/11/2019 15:03 |  |  | 14653 | Roadway |  | 20191217PWA_02 | Infrastructure (network-based) | -37.7177 | 144.6185 | 1 | Powercor | Report | 18506 | 0.03549 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distributorâ€™s assets identified a burnt "Open Circuit" Neutral Conductor Connection between the ABC Reticulation Conductor and the Three Wire Wire Aluminium Twisted Service Cable (U/G Dress Down) supplying the FOLCB on the Reticulation Pole opposite the property, resulting in a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the Three Wire Wire Aluminium Twisted Service Cable (U/G Dress Down) between the ABC Reticulation Conductors and the FOLCB on the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 112 DIAMOND GULLY ROAD, MCKENZIE HILL VIC 3451 | 31007500 |  |  |  | Corrosion |  | Phase to earth |  | A Plumber carrying out plumbing work within the crawl space under the house received an electric shock when he cut into and separated the copper gas pipe whilst creating a tee joint in the copper pipe work. | Connector/termination;Service cable (insulated) | 2 | 2 | 2 |  | CMN002 | corroded connection | Minor shock | 16/08/2019 14:30 |  |  | 14665 | Roadway |  | 20191218PWA_06 | Infrastructure (customer connection) | -37.0715 | 144.1873 | 1 | Powercor | Report | 18520 | 0.031049 | Low voltage AC (<1kV) | Bendigo Airport | 3451 | Mckenzie Hill | Connection
Fault crews attended the site to investigate. The site was isolated. Upon inspection, it was identified that the pole was burnt between two cross-arms. There was no evidence of fire on the ground. The pole was scheduled for replacement within the next two weeks. | 383 WARRIGAL ROAD, CHELTENHAM VIC 3192 | 1825384 |  |  |  | Leakage |  |  | 1 | UE received a call that there was a power pole on fire. MFB were on site. | Pole (wood) | 0 | 0 | 0 |  | HT11 | The cause for the pole fire was tracking across the insulators. | Pole-top fire | 43750.3125 | 1 | Negligible: no ground fire | 14666 | Roadway |  | 20191218UTD_01 | Infrastructure (network-based) | -37.9533 | 145.0765 | 1 | United Energy Distribution | Report | 18521 | 0.037462 | 66kV AC | Moorabbin Airport | 3192 | Cheltenham | Pole
oltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Customers FOLCB and corrosion at two points along the Outer Sheathing of the O/H Neutral Screened Service Cable, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the deteriorated Three Wire O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | UNIT 1 3 SUZANNE CRESCENT, WARRNAMBOOL VIC 3280 | 30136925 |  |  |  | Corrosion |  | Phase to earth |  | Ms Emily Barnes was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Tap and her bare feet while standing on the wet shower base and waste water outlet. | POA connection (network side);Service cable (insulated) | 2 | 2 | 2 |  | WBL006 | Corroded connection | Minor shock | 20/08/2019 0:00 |  |  | 14672 | Residential |  | 20191219PWA_04 | Infrastructure (customer connection) | -38.3609 | 142.4674 | 1 | Powercor | Report | 18527 | 0.041532 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
A voltage test between the dishwasher frame and the conductive metallic tap resulted with 52 Volts found at various points of the installation with reference to an independent earth, investigations on site revealed the service neutral conductor was corroded at the FOLCB. Powercor linesman repaired the service & CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 45 EDWARDS DRIVE, ALTONA MEADOWS VIC 3028 | 30116788 |  |  |  | Corrosion |  | Phase to earth |  | Terry received an electric shock when he simultaneously contacted the Metallic tap with his hand and metallic frame of the dishwasher with his other hand | POA connection (network side) | 2 | 2 | 2 |  | LV003 | Corroded connection at folcb | Minor shock | 24/09/2019 14:07 |  |  | 14674 | Residential |  | 20191219PWA_06 | Infrastructure (customer connection) | -37.8865 | 144.7769 | 1 | Powercor | Report | 18529 | 0.027059 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Neutral Bridge Connection located on the Reticulation Pole forming part of the O/H Street Mains, causing a higher than normal impedance within the neutral supply system. The attending Powercor Fault Crew cleaned and reterminated the corroded O/H Neutral Bridge Connection at the Reticulation Pole and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 2 Feiglin Rd, Shepparton VIC 3630, Australia | 30133599 |  |  |  | Corrosion |  | Phase to earth |  | Ms Lyn Campbell was in the Bathroom showering when she received an electric shock as she made simultaneous contact with one hand on the metallic Shower Tap and her bare feet whilst standing on the wet shower base and waste water outlet. | Connector/termination | 2 | 2 | 2 |  | STN021 | Corroded connection | Minor shock | 43505 |  |  | 14681 | Roadway |  | 20191220PWA_01 | Infrastructure (network-based) | -36.3999 | 145.4253 | 1 | Powercor | Report | 18536 | 0.010541 | Low voltage AC (<1kV) | Shepparton Airport | 3630 | Shepparton | Connection
Crew attended and preformed repairs. | 3673 Pyramid-Yarraberb Rd, Raywood VIC 3570, Australia | 30030175 | [7 empty] | Following a line outage, the fault crew patrolling found that Pole 26 Yarraberb SWER Line had broken off near ground level, causing the substation pole to fall to the ground. There was no fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | EHK024 | To be advised | Loss of supply;Damage to network assets | 19/12/2019 4:23 |  |  | 14683 | Agricultural |  | 20191220PWA_03 | Infrastructure (network-based) | -36.5386 | 144.1402 | 1 | Powercor | Notification | 18540 | 0.023234 | 12.7kV AC (SWER) | Bendigo Airport | 3673 | Raywood | Pole
Fire area was isolated and made safe. Fire extinguished | 1 OLD WARBURTON ROAD, WARBURTON VIC 3799 | between 1408905 and 1408912 |  | Fallen;Dead | [5 empty] | Crew reported tree on conductor and fire in the area | Conductor (bare) | 0 | 0 | 0 |  | WYK13 | Vegetation: Trees Incident | Bushfire | 19/12/2019 14:30 | 1 | Localised: less than 10 sq.m | 14684 |  |  | 20191220SPN_01 | Infrastructure (network-based) | -37.6948 | 145.8032 | 1 | AusNet Services Distribution | Report | 18543 | 0.027874 | 22kV AC | Moorabbin Airport | 3799 | Warburton | Trees
On arrival crew isolated supply and carried out repairs | 565 Trawalla S Estate Rd, Nerrin Nerrin VIC 3351, Australia | 32057787 |  | Blown branch/vegetation | [5 empty] | SWER ACR Trawalla P10A tripped to Lock out at 16:13hrs. Shortly afterwards a report of a "fire in the area - pole fire" was recieved. Crews patrolled the line and found an extinguished paddock fire at the incident address together with 3 bays of SWER conductor down on the ground. Evidence of a tree branch on the ground near Trawalla P22. On arrival crew found the fire had been extinguished by persons unknown There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CDN006 | Vegetation: Trees Incident | Grassfire | 20/12/2019 16:13 | 1 | Medium: 1000 sq.m - 10 ha | 14687 |  |  | 20191223PWA_01 | Infrastructure (network-based) | -37.7741 | 143.0617 | 1 | Powercor | Report | 18548 | 0.029997 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3351 | Nerrin Nerrin | Conductor
On arrival crew isolated supply and carried out repairs. | 12 Beach Rd, Aireys Inlet VIC 3231, Australia | 31039147 |  |  |  | Overheated connection |  |  |  | Customer reported service down the side of pole on fire. On arrival the crew found a single phase fuse box had burnt and caused a small fire that was quickly extinguished by locals and CFA who were on site. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | WPD014 | Insufficient remains to determine cause | Grassfire | 28/12/2019 20:37 | 1 | Localised: less than 10 sq.m | 14710 | Roadway |  | 20191230PWA_07 | Infrastructure (network-based) | -38.4604 | 144.1054 | 1 | Powercor | Report | 18572 | 0.032612 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Aireys Inlet | Fuse
CFA attended and extinguished the fire. PAL fault crew attended and isolated the section of damaged overhead power lines to make safe prior to replacing the broken crossarm and making other repairs before restoring electricity supply. | 1485 DELACOMBE WAY, MININERA VIC 3351 | 30084285 |  | Wind;Fallen | [5 empty] | Vic Fire reported a wire had come down from a pole and had started a grass fire at the incident location. On arrival the fault crew found that a tree had fallen from the other side of the road (outside clearance space) and had fallen across the overhead distribution wires, breaking a HV crossarm, and causing a grass fire below. There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | ART033 | Vegetation: Trees Incident | Grassfire | 30/12/2019 19:31 | 1 | Medium: 1000 sq.m - 10 ha | 14717 | Roadway |  | 20191231PWA_03 | Infrastructure (network-based) | -37.5668 | 142.8977 | 1 | Powercor | Report | 18579 | 0.013895 | 22kV AC | Hamilton Airport | 3351 | Mininera | Trees
Fire self extinguished, connection replaced, supply restored. | 50 Quail Cres, Melton VIC 3337, Australia | 30300618 |  |  |  | Corrosion |  |  |  | Following reports of outage crew found a burnt out copper to aluminium connection on north side transformer bus. Molten particles had caused a number of small spot fires in the grass below. There was no reported injuries or property damage. | Connector/termination | 2 | 2 | 2 |  | MLN032 | Overheated connection | Grassfire | 30/12/2019 14:00 | 1 | Localised: less than 10 sq.m | 14719 | Roadway |  | 20191231PWA_05 | Infrastructure (network-based) | -37.6778 | 144.571 | 1 | Powercor | Report | 18581 | 0.02241 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
Tree limb removed | 5 HIGHVIEW ROAD, BALWYN NORTH VIC 3104 | 30180008 |  | Blown branch/vegetation | [5 empty] | Customer reported hearing 2 loud bangs at the time the power flickered then went out. Crew reported a tree branch made contact with the HV conductor causing the phases to make contact causing sparks to fall resulting in a 1x1m ground fire. There was no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | WD011 | Vegetation: Trees Incident | Grassfire | 30/12/2019 19:49 | 1 | Localised: less than 10 sq.m | 14725 | Roadway |  | 20191231PWA_10 | Infrastructure (network-based) | -37.7841 | 145.0791 | 1 | CitiPower | Report | 18600 | 0.011566 | 11kV AC | Essendon Airport | 3104 | Balwyn North | Trees
On arrival crew isolated supply and carried out repairs. LEI arranged to check for HVI | 5 FINDON AVENUE, CAULFIELD NORTH VIC 3161 | 30219923 |  | Lightning | [5 empty] | Report received of a pole being hit by lightning at the incident location. On arrival the crew found end burnt off crossarm and conductors on ground. There was a possibility of HV injection. There was no ground fire, no reported injuries | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | AR004 | Lightning strike on pole | Pole-top fire;HV injection | 31/12/2019 4:40 | 1 | Negligible: no ground fire | 14727 | Roadway |  | 20191231PWA_12 | Infrastructure (network-based) | -37.8636 | 145.0166 | 1 | CitiPower | Report | 18589 | 0.028611 | 11kV AC | Moorabbin Airport | 3161 | Caulfield North | Lightning
On arrival crew arranged for line isolation and carried out repairs. | 49 HOTHAM STREET, ST KILDA EAST VIC 3183 | 30218625 |  |  |  | Leakage |  |  |  | Vic fire reported pole fire in Hotham st outside BC zone substation. Crew advise pole fire due to tracking, fire brigade on site have extinguished fire. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | AR-BC | Excessive leakage current | Pole-top fire | 31/12/2019 5:00 | 1 | Negligible: no ground fire | 14730 | Roadway |  | 20200102PWA_02 | Infrastructure (network-based) | -37.8647 | 145.0003 | 1 | CitiPower | Report | 18592 | 0.014674 | 66kV AC | Moorabbin Airport | 3183 | St Kilda East | Pole
On arrival crew isolated supply and carried out repairs. | 56 Argyle St, St Kilda VIC 3182, Australia | 30211577 |  |  |  | Leakage |  |  |  | Following report of pole fire, on arrival crew found cross-arm mounted with HV isolators has broken due to cross-arm fire. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SK009 | Excessive leakage current | Pole-top fire | 31/12/2019 6:20 | 1 | Negligible: no ground fire | 14737 | Roadway |  | 20200102PWA_09 | Infrastructure (network-based) | -37.8626 | 144.9859 | 1 | CitiPower | Report | 18602 | 0.029422 | 11kV AC | Essendon Airport | 3182 | St Kilda | Crossarm
Site made safe HV crossarm replaced and network restored | 10 PARK DRIVE, KEILOR EAST VIC 3033 | A095620 |  |  |  | Leakage |  |  | 2 | HV crossarm fire due to earth leakage High voltage injection ruled out by inspector Photos are unavailable for this incident | Conductor (bare) | 0 | 0 | 0 |  | BY11 | Earth leakage | Pole-top fire | 31/12/2019 4:28 | 1 | Negligible: no ground fire | 14748 | Residential |  | 20200103JEM_03 | Infrastructure (network-based) | -37.7485 | 144.8609 | 1 | Jemena | Report | 18614 | 0.021965 | 22kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
Site made safe and replaced 66kV crossarm | 131 ROSAMOND ROAD, MAIDSTONE VIC 3012 | A009426 |  |  |  | Leakage |  |  | 1 | Pole top fire resulting in 66kV crossarm falling onto 22kV line Photos are unavailable for this incident | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | SubT Feeder BY-ES | Earth leakage | Pole-top fire | 31/12/2019 5:00 | 1 | Negligible: no ground fire | 14754 | Roadway |  | 20200103JEM_09 | Infrastructure (network-based) | -37.7781 | 144.885 | 1 | Jemena | Report | 18620 | 0.0089676 | 22kV AC;66kV AC | Essendon Airport | 3012 | Maidstone | Crossarm
Emergency switching performed Dumped section of HV and replaced HV crossarm and isolators Network returned to normal | 88 ELEANOR STREET, FOOTSCRAY VIC 3011 | A064748 |  |  |  | Leakage |  |  | 1 | HV crossarm fire resulting in broken off HV isolators. Photos are unavailable for this incident | Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | FW08 | Earth leakage | Pole-top fire | 31/12/2019 7:46 | 1 | Negligible: no ground fire | 14757 | Roadway |  | 20200103JEM_12 | Infrastructure (network-based) | -37.7958 | 144.8849 | 1 | Jemena | Report | 18623 | 0.0046817 | 22kV AC | Essendon Airport | 3011 | Footscray | Crossarm
Crew isolated faulted area and replaced the burnt arm with a new steel arm and new insulators. | 3 Pryors Rd, Horsham VIC 3400, Australia | 30078377 |  |  |  | Leakage |  |  |  | Report received of a pole fire at the incident location. Crew advise cross-arm burnt on LIS 433, Pryors Lane P1. LEI confirmed no high voltage injection. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | HSM009 | Excessive leakage current | Pole-top fire | 31/12/2019 2:20 | 1 | Negligible: no ground fire | 14743 | Roadway |  | 20200103PWA_05 | Infrastructure (network-based) | -36.7043 | 142.2153 | 1 | Powercor | Report | 18609 | 0.038319 | 22kV AC | Horsham Aerodrome | 3400 | Horsham | Crossarm
Crew attended and isolated affected switch. Damage was cut away to make safe. Installed two new Krone boxes and one 3 phase fuse mains box | 2 DICKSON STREET, KINGSVILLE VIC 3012 | A103413 |  |  |  | Overheated connection |  |  | 1 | LV krone switch failure resulting in pole top fire | Pole top;Disconnector/isolator | 0 | 0 | 0 |  | FW08 | Krone switch failure | Pole-top fire | 21/12/2019 4:47 | 1 | Negligible: no ground fire | 14760 | Residential |  | 20200104JEM_01 | Infrastructure (network-based) | -37.8059 | 144.8846 | 1 | Jemena | Report | 19710 | 0.028905 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Kingsville | AF Other
Pulled fuses at pole to isolate supply, installed new IPCs in pit to make safe. Issued defect J01410 on customer mains. | 1760 MICKLEHAM ROAD, MICKLEHAM VIC 3064 | A020428 | Copper theft | [5 empty] | 2 | Copper theft of approximately 70 metres of LV underground customer mains between Jemena and Telstra pits. | Services cable;Services pit (customer) | 0 | 0 | 0 |  | COO11 | Copper theft. Unknown person removed LV underground customer mains. | Loss of supply | 43922.6757 |  |  | 14762 | Peri-urban |  | 20200104JEM_03 | Infrastructure (customer connection) | -37.5706 | 144.8754 | 1 | Jemena | Report | 18628 | 0.027895 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Other
Electrical network operator attended and advised control room of cause and damage, requested immediate arc supression on subsidiary on 22kV on same pole Supply isolated and repairs initiated by Jemena under access permit. | 56 ROSEHILL ROAD, KEILOR EAST VIC 3033 | A093373 |  |  |  | Insulator;Leakage |  | Three phase | 1 | MFB reported "sparking pole" opposite 56 Rosehill Road, Keilor East HV crossarm fire resulted in footpath side eye bolt pulling through the 66kV crossarm on pole A093373 HV fuses and surge diverters operated at Rosehill-Rose and Judith-Brees substations Photos are unavailable for this incident | Pole top;Crossarm (wood);Insulators | 0 | 0 | 0 |  | KTS-ES 66kV | Earth leakage resulted in HV crossarm fire, which in turn caused the eye bolt to pull through HV crossarm and to hang in close proximity to subsidiary 22KV Distribution. | Pole-top fire | 43952.5042 | 1 | Negligible: no ground fire | 14763 | Residential |  | 20200105JEM_01 | Infrastructure (network-based) | -37.7476 | 144.8797 | 1 | Jemena | Report | 18629 | 0.0094988 | 66kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
crew dispatched to investigate and make safe. | tramway rd cnr bonds lane Hazelwood North | 2616413 |  | Bird | [5 empty] | bird contacted conductor . Grass fire observed at base of pole. | Conductor (bare) | 0 | 0 | 0 |  | mwl24 | Bird Incident | Grassfire | 27/12/2019 14:30 | 1 | Small: 10 - 1000 sq.m | 14769 | Industrial |  | 20200106SPN_02 | Infrastructure (network-based) | -38.2708 | 146.4334 | 1 | AusNet Services Distribution | Report | 18640 | 0.006088 | 22kV AC | Morwell (Latrobe Valley Airport) |  |  | Animal
On arrival crew isolated supply and commenced repairs. | 42 Victoria St, Richmond VIC 3121, Australia | 30221059 |  |  |  | Mechanical breakdown |  |  |  | The Trustee for Salvation Army reported ground fire at base of a pole at the above incident location. On arrival, the crew found a Low Voltage (LV) overhead service cable insulation had been deteriorated and contacted the metal supporting bracket livening up the Tramways steel pole. The base of pole was found to be smoldering and smoking but no sign of flame or fire due to concrete foot path surface. There was no reported injuries or third party property damage. | Pole (steel) | 2 | 2 | 2 |  | B023 | service insulation compromised by metal bracket | Melting or smoking only | 43952.4986 |  |  | 14776 | Roadway |  | 20200107PWA_01 | Infrastructure (network-based) | -37.8099 | 144.9931 | 1 | CitiPower | Report | 18654 | 0.038696 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | OH Cable
Staff dispatched to investigate and make safe. Tree fallen and clashed 66/22/LV, all conductors ok. Tree fallen clear. Broken tie on 22kv at lis #1220862, G&B construction crew required to replace broken tie. lis #1220683; | 70 HEATHMONT ROAD, HEATHMONT VIC 3135 | 1220862 |  | Fallen;Council | [5 empty] | Tree caught fire after contact with HV | Conductor (bare) | 0 | 0 | 0 |  | RWT22 | Vegetation: Trees Incident | Other vegetation | 22/12/2019 13:54 | 1 | Negligible: no ground fire | 14779 | Residential |  | 20200107SPN_02 | Infrastructure (network-based) | -37.8274 | 145.2432 | 1 | AusNet Services Distribution | Report | 18784 | 0.022027 | 22kV AC | Moorabbin Airport | 3135 | Heathmont | Trees
Fault trucks dispatched to investigate and repair | 3202 WANGARATTA-WHITFIELD ROAD, EDI VIC 3678 | 5101611 |  | Fallen |  |  |  |  | 1 | WN5 Fdr CB trip via GFN operation. Reported grassfire and wires down. | Conductor (bare) | 0 | 0 | 0 |  | wn5 | Vegetation: Trees Incident | Grassfire | 24/12/2019 18:25 | 1 | Medium: 1000 sq.m - 10 ha | 14782 | Agricultural |  | 20200107SPN_03 | Infrastructure (network-based) | -36.6245 | 146.4021 | 1 | AusNet Services Distribution | Report | 18661 | 0.010078 | 22kV AC | Wangaratta Aero | 3202 | Edi | Conductor
CFA put out fire. Crew despatched to investigate and make safe. No damage to Ausnet assets. | 1 STEVENS STREET, SALE VIC 3850 | 2503175 |  | Bird | [5 empty] | Bird (pelican) flew into lines - Grass fire started at base of pole. | Conductor (bare) | 0 | 0 | 0 |  | SLE31 | Bird Incident | Grassfire | 16/12/2019 21:46 | 1 | Medium: 1000 sq.m - 10 ha | 14785 | Residential |  | 20200107SPN_05 | Infrastructure (network-based) | -38.1225 | 147.0812 | 1 | AusNet Services Distribution | Report | 18722 | 0.030713 | 66kV AC | Bairnsdale Airport | 3850 | Sale | Animal
Arrived on site measured 10 volts on tap and main neutral. Tested supply NST failed Truck removed Neutral and tested passed. All back on passed NST No volts on Neutral | 31 LOUISE STREET, LALOR VIC 3075 |  |  |  |  | Earth fault |  |  |  | Electrocution or Imminent risk of electrocution | Customer earthing | 0 | 0 | 0 |  |  | Electric Shock . Tested supply NST failed | Minor shock | 43862.716 |  |  | 14796 |  |  | 20200107SPN_13 | Infrastructure (customer connection) | -37.6681 | 145.0287 | 1 | AusNet Services Distribution | Report | 18676 | 0.032876 | Low voltage AC (<1kV) | Essendon Airport | 3075 | Lalor | Installation
On arrival crew isolated supply and carried out repairs. | 1090 Barham River Rd, Apollo Bay VIC 3233, Australia | 33104356 | Working too close to overhead lines | [6 empty] | A customer reported a power outage and also a tree down at the incident location. On arrival crew found that a tree clearing contractor engaged by the customer had fallen a large tree across the HV conductors. There was no fire, no injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CLC006 | Vegetation: Trees Incident | Loss of supply;No Go Zone (contact);Damage to network assets | 44013.4104 |  |  | 14800 |  |  | 20200108PWA_03 | Infrastructure (network-based) | -38.7167 | 143.6421 | 1 | Powercor | Report | 18683 | 0.0042627 | 22kV AC | Avalon Airport | 3233 | Apollo Bay | Other
Crew isolated and repaired. | 11 RAILWAY TERRACE, OUYEN VIC 3490 | 32150815 |  |  |  | Leakage |  |  |  | Report from Vic Fire that pole on fire at above address. When crew arrived they found that the cross arm had burnt through from the cross arm strap bolt. The outer phase of the HV had fallen onto the LV cross-arm. Crew confirmed no HVI had occurred. There was no ground fire, no injury, no third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN007 | Excessive leakage current | Pole-top fire | 43952.6799 | 1 | Negligible: no ground fire | 14805 | Roadway |  | 20200108PWA_07 | Infrastructure (network-based) | -35.0751 | 142.3181 | 1 | Powercor | Report | 18689 | 0.032609 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3490 | Ouyen | Crossarm
Crew dispatched to investigate and make safe. Pole and cross arm replaced, | 1 LYONS ROAD, CROYDON NORTH VIC 3136 | 1217188 |  |  |  | Electrical breakdown |  |  |  | Pole fire. Pole top burnt. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | CPK11 | Pole burnt 75% through at kingbolt due to dirt and water tracking and leaking electrical current over insulator through damp pole to ground. | Pole-top fire | 43952.5549 | 1 | Negligible: no ground fire | 14811 | Residential |  | 20200108SPN_05 | Infrastructure (network-based) | -37.7693 | 145.2887 | 1 | AusNet Services Distribution | Report | 18697 | 0.032273 | 22kV AC | Moorabbin Airport | 3136 | Croydon North | Pole
On arrival crew isolated supply and carried out repairs. | 66 Horsham Rd, Dimboola VIC 3414, Australia | 32121199 |  |  |  | Leakage |  |  |  | Report received report of pole fire at incident location. On arrival crew found a pole top burnt off and crossarm burnt. There was a small grass fire of 10 sq m, no injuries. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | HSM006 | Excessive leakage current | Pole-top fire | 43952.6521 | 1 | Small: 10 - 1000 sq.m | 14815 | Agricultural |  | 20200109PWA_03 | Infrastructure (network-based) | -36.456 | 142.0508 | 1 | Powercor | Report | 18702 | 0.017699 | 22kV AC | Horsham Aerodrome | 3414 | Dimboola | Crossarm
On arrival crew isolated supply and carried out repairs. | 61 HAWKINS ROAD, MINIMAY VIC 3413 | 30139567 |  |  |  | Leakage |  |  |  | Vic fire reported Pole fire and grass fire. On arrival crew found a SWER pole burnt in half and a grass fire There was no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | HSM004 | Excessive leakage current | Pole-top fire;Grassfire | 43952.5236 | 1 | Medium: 1000 sq.m - 10 ha | 14816 | Agricultural |  | 20200109PWA_04 | Infrastructure (network-based) | -36.7349 | 141.1416 | 1 | Powercor | Report | 18703 | 0.030167 | 12.7kV AC (SWER) | Horsham Aerodrome | 3413 | Minimay | Pole
On arrival crew isolated supply and carried out repairs. LEI investigated for HVI, non found. | 647 PRAIRIE-ROCHESTER ROAD, BAMAWM VIC 3561 | 30120470 |  |  |  | Leakage |  |  |  | Reports from customers of dim lights and broken cross arm with wire down. On arrival, crews found cross arm had burnt and broken at EDO holder and dropped to ground and a HV conductor was hanging over LV conductor. Crew identified possible HVI and inspector called to investigate. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHP012 | Excessive leakage current | Pole-top fire | 43952.7604 | 1 | Negligible: no ground fire | 14819 | Agricultural |  | 20200109PWA_06 | Infrastructure (network-based) | -36.3029 | 144.6166 | 1 | Powercor | Report | 18706 | 0.021294 | Low voltage AC (<1kV);22kV AC | Bendigo Airport | 3561 | Bamawm | Crossarm
BA fuse was replaced | 19 CRIGHTONS ROAD, KOOROOMAN VIC 3953 | 2008257 |  |  |  | Candled fuse |  |  |  | Candled HV fuse | Boric acid | 0 | 0 | 0 |  | lga13 | CANDLED HV FUSE | Pole-top fire | 43831.3257 | 1 | Negligible: no ground fire | 14821 |  |  | 20200109SPN_03 | Infrastructure (network-based) | -38.4534 | 145.994 | 1 | AusNet Services Distribution | Report | 18709 | 0.021985 | 22kV AC | Morwell (Latrobe Valley Airport) | 3953 | Koorooman | Fuse
Replaced candeled 6amp E.D.O fuse | 37 PEACHES ROAD, FOSTER NORTH VIC 3960 | 2027084 |  | Lightning |  | Candled fuse |  |  |  | CANDLED FUSE | EDO fuse | 0 | 0 | 0 |  | LGA13 | cause lightning | Pole-top fire | 43922.9799 | 1 | Negligible: no ground fire | 14823 |  |  | 20200109SPN_04 | Infrastructure (network-based) | -38.59 | 146.1448 | 1 | AusNet Services Distribution | Report | 18712 | 0.041426 | 22kV AC | Morwell (Latrobe Valley Airport) | 3960 | Foster North | Fuse
Crew isolated and repaired. | 289 Happy Valley Rd, Robinvale Irrigation District Section C VIC 3549, Australia | 32145857 |  |  |  | Leakage |  |  |  | Report from Vic FIre of pole fire at 201 Shaggy Ridge Rd Robinvale Crew attended and found cross arm had burnt and broke at the cross-arm strap bolt and the outer phase was being held up by the stays off the strain. No ground fire, no injury, no third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | RVL001 | Excessive leakage current | Pole-top fire | 43952.9674 | 1 | Negligible: no ground fire | 14827 | Agricultural |  | 20200110PWA_04 | Infrastructure (network-based) | -34.6369 | 142.7444 | 1 | Powercor | Report | 18716 | 0.018832 | 22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section C | Crossarm
Crew isolated and repaired. | 50 DICKINSON ROAD, VINIFERA VIC 3591 | 32159107 |  |  |  | Leakage |  |  |  | Vic Fire reported pole fire at above address. On arrival, crew found cross arm hanging from top of pole and still alight. Burning appears to have occurred at Kingbolt. No HVI suspected. No ground fire, no injuries, no third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL002 | Excessive leakage current | Pole-top fire | 43952.8896 | 1 | Negligible: no ground fire | 14828 | Agricultural |  | 20200110PWA_05 | Infrastructure (network-based) | -35.1991 | 143.3826 | 1 | Powercor | Report | 18717 | 0.0080718 | 22kV AC | Swan Hill Aerodrome | 3591 | Vinifera | Crossarm
The place made safe and repairs have been arranged. | 8224 MURRAY VALLEY HIGHWAY, KERANG EAST VIC 3579 | 32032025 |  |  |  | Leakage |  |  |  | A Powercor fault crew patrolling a faulted SWER line and found a pole fire at the incident location. The pole top ignited but no ground fire reported. | Pole (wood) | 2 | 2 | 2 |  | KGT003 | Excessive leakage current | Pole-top fire | 43983.1882 | 1 | Negligible: no ground fire | 14832 | Agricultural |  | 20200110PWA_09 | Infrastructure (network-based) | -35.7862 | 144.0295 | 1 | Powercor | Report | 18723 | 0.013626 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3579 | Kerang East | Pole
Crew isolated and replaced pole. | 2862 HATTAH-ROBINVALE ROAD, LIPAROO VIC 3549 | 32140710 |  |  |  | Leakage |  |  |  | ZSS trip to lockout at Wemen Zone Substation. Crew arrived and found a pole fire on 66/22kV pole where 22kV crossarm had burnt through at the king bolt and dropped the top of the pole with the 66kV down to ground. No ground fire, no injury, no third party damage. | Pole (wood) | 2 | 2 | 2 |  | WMN021 | Excessive leakage current | Pole-top fire | 43983.6813 | 1 | Negligible: no ground fire | 14835 | Roadway |  | 20200110PWA_12 | Infrastructure (network-based) | -34.7946 | 142.5649 | 1 | Powercor | Report | 18728 | 0.021362 | 22kV AC;66kV AC | Mildura Airport | 3549 | Liparoo | Crossarm
On arrival crew isolated supply and carried out repairs. | 60 Alkera Rd, Invermay VIC 3352, Australia | 30003992 |  |  |  | Overheated connection |  |  |  | Vic Fire reported a ground fire at the incident location. A Powercor crew found that FOLCB on the pole (LIS 45326) overheated and fallen debris caused 6*30 grass fire. The fire damage to a customer's fence. There was no reported injuries. | Connection box | 2 | 2 | 2 |  | BAN007 | Corrosion | Grassfire | 44075.6375 | 1 | Small: 10 - 1000 sq.m | 14846 |  |  | 20200113PWA_01 | Infrastructure (network-based) | -37.5301 | 143.888 | 1 | Powercor | Report | 18745 | 0.017674 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Invermay | Connection
Supply isolated & LV isolator replaced | 3 Milroy St, Bendigo VIC 3550, Australia | 32037243 |  |  |  | Overheated connection |  |  |  | Customer at incident address reported sparks dropping from pole and starting ground fire at base of pole. Upon arrival fault crew found that white phase LV isolator at substation "Milroy Valentine 8" had failed and dropped molten material to ground, commencing small fire at base of pole. There was no reported injuries or third party property damage. | Disconnector/isolator | 2 | 2 | 2 |  | BET002 | corrosion | Grassfire | 44075.7965 | 1 | Localised: less than 10 sq.m | 14851 | Roadway |  | 20200113PWA_03 | Infrastructure (network-based) | -36.7513 | 144.2732 | 1 | Powercor | Report | 18755 | 7.7546e-05 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Bendigo | AF Other
Supply isolated, fire extinguished, X-arm replaced. | 6 FITZGERALD STREET, SHEPPARTON VIC 3630 | 30129783 |  |  |  | Leakage |  |  |  | Customer reported pole top sparking and smoking, Upon arrival crew found that intermediate HV/LV pole had ignited at the HV X-arm kingbolt position No ground fire or 3rd party damage. | Pole (wood) | 2 | 2 | 2 |  | SHN022 | Excessive leakage current | Pole-top fire | 44105.8674 | 1 | Negligible: no ground fire | 14854 | Roadway |  | 20200113PWA_06 | Infrastructure (network-based) | -36.3622 | 145.4117 | 1 | Powercor | Report | 18758 | 0.020045 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Pole
Supply isolated, X-arm replaced | 775 C391, Kialla VIC 3631, Australia | 30130476 |  |  |  | Leakage |  |  |  | CFA reported pole fire at incident location, Upon arrival crew found that an intermediate X-arm on substation pole ( Doyles Lane South P45 ) had ignited and burnt through at the kingbolt position, conductors remained aloft held up by x-arm straps. No ground fire or 3rd party damage. | Crossarm (wood) | 2 | 2 | 2 |  | STN021 | Excessive leakage current | Pole-top fire | 44105.9583 | 1 | Negligible: no ground fire | 14856 | Roadway |  | 20200113PWA_08 | Infrastructure (network-based) | -36.4345 | 145.4317 | 1 | Powercor | Report | 18760 | 0.0078796 | 22kV AC | Shepparton Airport | 3631 | Kialla | Crossarm
The CitiPower crew isolated the Low Voltage Circuit and waiting for the SES to clear the tree before commencing repairs. | 857 GLENFERRIE ROAD, KEW VIC 3101 | 30181036 |  | Alive;Fallen;Property owner/customer | [5 empty] | CitiPower Report room where advised by Yarra Trams that a tree has fallen on overhead conductors. On attendance the CitiPower faults crew found a private tree from Methodist Ladies College has fallen on the CitiPower overhead Low Voltage conductors between pole 14964 and pole 14965. As a result the crossarm snapped at pole 14964 and the Low Voltage conductor came into contact with the Yarra Trams centenary which also failed. No shocks, fire , no Injuries, No third party damage | Conductor (bare) | 2 | 2 | 2 |  | Q006 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 44075.9792 |  |  | 14860 |  |  | 20200114PWA_03 | Infrastructure (network-based) | -37.8126 | 145.0373 | 1 | CitiPower | Report | 18764 | 0.0254 | Low voltage AC (<1kV) | Essendon Airport | 3101 | Kew | Trees
Line isolated, repairs carried out. | 220 Park Rd, Maryborough VIC 3465, Australia | 32020616 | [7 empty] | CFA reported pole fire & ground fire at incident location. Upon arrival fault crew found that HV cable head had failed at termination ejecting molten material to ground and commencing a small ground fire of 3m x 8m in size, on the road verge extending slightly into an adjacent property. There was no reported injuries | Cable | 2 | 2 | 2 |  | MRO005 | To be advised | Grassfire | 13/01/2020 16:41 | 1 | Small: 10 - 1000 sq.m | 14866 |  |  | 20200114PWA_05 | Infrastructure (network-based) | -37.0246 | 143.7498 | 1 | Powercor | Notification | 18771 | 0.034432 | 22kV AC | Ballarat Aerodrome | 3465 | Maryborough | OH Cable
Faults crew attended the site and upon investigation, it was identified the LV krone box on the pole substation had melted and caused a small grass. ESV was notified, ref #13042502. The site was isolated and made safe. The krone box was replaced before supply was restored. | 377 NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 3308817 |  |  |  | Overheated connection |  |  | 1 | UE received a call the pole outside Quest Apartments was sparking. | Connection box | 0 | 0 | 0 |  | FTN22 | The LV krone box melted and caused a small grass fire. | Grassfire | 21/12/2019 23:55 | 1 | Localised: less than 10 sq.m | 14868 | Roadway |  | 20200114UTD_05 | Infrastructure (network-based) | -38.1374 | 145.124 | 1 | United Energy Distribution | Report | 18795 | 0.0040775 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston | Connection
Faults crew attended the site and upon inspection, it was found a large council tree fell through LV lines which caused the lines to hit the ground and start a grass fire. The site was isolated and made safe. The lines were repaired and supply was restored. | 60-62 MCGOWANS ROAD, DONVALE VIC 3111 | 7067313 |  | Fallen;Council |  |  |  |  | 1 | UE received a call that a tree has pulled down wire which started a grass fire but the fire is now out. | Conductor (bare) | 0 | 0 | 0 |  | NW13 | Vegetation: Trees Incident | Grassfire | 30/12/2019 18:35 | 1 | Small: 10 - 1000 sq.m | 14871 | Roadway |  | 20200114UTD_08 | Infrastructure (network-based) | -37.7926 | 145.1865 | 1 | United Energy Distribution | Report | 18777 | 0.031369 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | Trees
Faults crew attended the site and upon inspection, there were track marks on the insulator and the cross-arm was burnt. The cross-arm broke and HV conductor dropped into the LV causing a HVI. ESV were notified, ref #13086073. LEI arrived on site and confirmed the HVI. The site was isolated and made safe. The cross-arm was replaced and the conductors were repaired before supply was restored. | 2 NEVILLE STREET, BOX HILL SOUTH VIC 3128 | 7029573 |  |  |  | Leakage |  |  | 1 | UE received a call from MFB, advising of a broken cross-arm. | Crossarm (wood) | 0 | 0 | 0 |  | BH31 | The cause of the cross-arm fire was tracking across the insulator which broke the cross-arm and caused the HV conductor to drop into the LV. | Pole-top fire | 31/12/2019 5:30 | 1 | Negligible: no ground fire | 14873 | Roadway |  | 20200114UTD_10 | Infrastructure (network-based) | -37.8408 | 145.1113 | 1 | United Energy Distribution | Report | 18780 | 0.018351 | 22kV AC | Moorabbin Airport | 3128 | Box Hill South | Crossarm
As a precaution the crew isolated supply to the SWER substation . The crew left the fire ground at this point for safety reasons. The crew completed checks of the HV Fuse unit, Transformer, LV wiring, LV fuse boxes and earth system. The crew tested the HV and LV earths on this pole and both passed. The crew also carried out NST tests of the customers underground mains to confirm they where in a fit state for service. | Unnamed Road, Rocky Point VIC 3377, Australia | 32117250 |  |  |  | no cause found;Other |  |  |  | A report was received from the CFA of a pole down due to a fire at the above address. A Powercor crew attended and determined that a grass fire was burning around the pole at the incident location. There was no fallen pole. The fire burnt in the order of 80HA of grassland There were no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | ART033 | No electrical cause found, case treated as external fire ignited in vicinity of substation Pole | Grassfire | 14/01/2020 14:42 | 0 | Large: more than 10 ha | 14875 | Agricultural |  | 20200115PWA_01 | Infrastructure (network-based) | -37.3252 | 142.8503 | 1 | Powercor | Report | 18786 | 0.013098 | 12.7kV AC (SWER) | Hamilton Airport | 3377 | Rocky Point | AF Other
CFA put fire out and crossarm was changed | 685 DIVISION ROAD, MURROON VIC 3243 | 30052618 |  |  |  | Leakage |  |  |  | CFA reported a pole fire in Division Road, Murroon. Crew attended and confirmed a crossarm fire on pole 2 Murroon Spur, no ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | WIN011 | Excessive leakage current | Pole-top fire | 43952.3076 | 1 | Negligible: no ground fire | 14879 | Agricultural |  | 20200115PWA_04 | Infrastructure (network-based) | -38.4376 | 143.8114 | 1 | Powercor | Report | 18792 | 0.032955 | 22kV AC | Avalon Airport | 3243 | Murroon | Crossarm
CFA attended site and put out grass fire in the nature strip & base of the pole. Supply was restored | 248 EDGARS ROAD, THOMASTOWN VIC 3074 | 908987 | Unmanned balloon (advertising or drone) | [6 empty] | Ground fire. Found balloon with silver tape on HV conductors | Conductor (bare) | 0 | 0 | 0 |  | TT9 | Silver tape from a balloon on HV found onsite as suspect to cause the fire at pole# 908987. | Grassfire | 14/01/2020 16:00 | 1 | Localised: less than 10 sq.m | 14874 | Residential |  | 20200115SPN_01 | Infrastructure (network-based) | -37.6728 | 145.0018 | 1 | AusNet Services Distribution | Report | 18782 | 0.026063 | 22kV AC | Essendon Airport | 3074 | Thomastown | Other
Fault crews and EIO attended the site to investigate. Upon inspection, the neutral block had burnt out and there was a voltage rise on the earthing system. Supply to the premise was isolated and the REC replaced the connection box. EIO tested the installation and supply was restored. | 6 MOROTAI STREET, SORRENTO VIC 3943 | 1306283 |  |  |  | Overheated connection |  | Phase to neutral | 1 | UE received a call that a customer has received tingles off the meter panel and the lights went off the previous night. | Connection box | 0 | 0 | 0 |  | STO13 | The cause was a burnt out neutral connection. | Minor shock | 16/12/2019 15:00 |  |  | 14877 | Residential |  | 20200115UTD_01 | Infrastructure (customer connection) | -37.8242 | 145.166 | 1 | United Energy Distribution | Report | 18788 | 0.022954 | Low voltage AC (<1kV) | Moorabbin Airport | 3943 | Sorrento | Connection
New earth to be installed | 689 BARKLY STREET, WEST FOOTSCRAY VIC 3012 | A129571 | Copper theft | [5 empty] | 2 | Unknown person has stolen copper | Pole (wood);Earth/earthing | 0 | 0 | 0 |  | FW16 | Copper theft by unknown person(s) | Damage to network assets | 16/01/2020 10:06 |  |  | 14884 | Roadway |  | 20200116JEM_01 | Infrastructure (network-based) | -37.7966 | 144.8684 | 1 | Jemena | Report | 19357 | 0.036101 | Earthing cable;Other | Essendon Airport | 3012 | West Footscray | Other
Supply isolated repairs completed | 130 PEACES ROAD, LEITCHVILLE VIC 3567 | 32033752 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CHA005 | Excessive leakage current | Pole-top fire | 43470.2875 | 1 | Negligible: no ground fire | 13924 | Agricultural |  | 20190627PWA_03 | Infrastructure (network-based) | -35.9203 | 144.2188 | 1 | Powercor | Report | 17401 | 0.037811 | 22kV AC | Bendigo Airport | 3567 | Leitchville | Crossarm
On arrival crew isolated supply and carried out repairs | SERDI PARK, 278 KNOX ROAD, ROMSEY VIC 3434 | 31006494 |  |  |  | Unknown technical factor |  |  |  | Transformer failed and caught fire CFA attended There was no ground fire, no reported injuries or third party property damage. | Transformer | 2 | 1 | 2 |  | WND012 | No cause determined | Plant/equipment | 27/05/2019 21:49 | 1 | Negligible: no ground fire | 13929 | Roadway |  | 20190628PWA_01 | Infrastructure (network-based) | -37.3557 | 144.7218 | 1 | Powercor | Report | 17406 | 0.0089815 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3434 | Romsey | AF Other
Crew unable to contact owner. Follow up to request container to be relocated | 99 BOWEN STREET, ECHUCA VIC 3564 | 33082212 | Building too close or within the No Go Zone | [5 empty] | 2 | Passerby reported someone has placed a shipping container under a transformer in Bowen Street Echuca, very close to HV wires. Crew identified shipping container was some 2m from the bottom of the Transformer. | Conductor (insulated);Transformer | 0 | 0 | 0 |  | ECA003 | placement of container near substation pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/06/2019 9:13 |  |  | 13930 | Roadway |  | 20190628PWA_02 | Infrastructure (network-based) | -36.132 | 144.7648 | 1 | Powercor | Report | 17407 | 0.026569 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3564 | Echuca | Other
Jemena fault crew made safe in pit by isolating tails. | 395 Somerton Rd, Meadow Heights VIC 3048, Australia | 10961545 | Vandalism;Unauthorised access | [5 empty] | 2 | Attempted copper theft at 48/395 Somerton Rd, Meadow Heights. This pit supplies the Telstra base station, adjacent to the Transmission tower, located South of intersection of Somerton Rd, and Aitken Blvd. | Cable | 0 | 0 | 0 |  | COO11 | Attempted copper theft. | Damage to network assets | 29/06/2019 1:06 |  |  | 13933 |  |  | 20190629JEM_01 | Infrastructure (network-based) | -37.6389 | 144.9109 | 1 | Jemena | Report | 17410 | 0.039971 | Low voltage AC (<1kV) | Melbourne Airport | 3048 | Meadow Heights | Other
crew isolated supply and have replaced service | 47 ROGERSON STREET, AVONDALE HEIGHTS VIC 3034 |  |  |  |  | Neutral fault |  |  | 2 | Customer received electric shock from copper pipes in house | Service conductor | 0 | 0 | 0 |  |  | broken service neutral | Minor shock | 30/06/2019 13:14 |  |  | 13935 | Residential |  | 20190630JEM_02 | Infrastructure (customer connection) | -37.7643 | 144.8576 | 1 | Jemena | Report | 17412 | 0.0058981 | Low voltage AC (<1kV) | Essendon Airport | 3034 | Avondale Heights | OH Cable
The attending Powercor Fault Crew cleaned and re-terminated the existing O/H Service Neutral Conductor connections at the Pole Type Junction Box located at the Reticulation Service Pole | 194 PRINCES HIGHWAY, PORT FAIRY VIC 3284 | 32196144 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hands on the shower taps and his bare feet whilst standing on the wet shower base. | Aluminium twisted (grey) | 0 | 0 | 0 |  | KRT022 | Corroded O/H Grey Twisted Service Neutral Conductor termination in the Pole Type Connection Box located at the Reticulation Service Pole. | Minor shock | 43530.375 |  |  | 13936 | Roadway |  | 20190701PWA_01 | Infrastructure (network-based) | -38.3682 | 142.2333 | 1 | Powercor | Report | 17413 | 0.036719 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Connection
crew attended and replaced damaged service cable | 6 CHALLENGER CLOSE, WHITTINGTON VIC 3219 | 32086020 |  |  |  | Corrosion |  |  | 2 | Person as in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the metal Shower Taps and his bare feet whilst standing on the wet shower base. | Service conductor;Neutral screen | 0 | 0 | 0 |  | GLE024 | corroded service - in span | Minor shock | 43652.3542 |  |  | 13937 | Roadway |  | 20190701PWA_02 | Infrastructure (customer connection) | -38.1807 | 144.3935 | 1 | Powercor | Report | 17414 | 0.011333 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Whittington | OH Cable
Fault crew attended and replaced the damaged street light, including rewiring to supply. | 403 MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316285 |  |  |  | Overheated connection |  |  | 1 | UE received a report from the fire authority of a fire on a pole. On attendance, the fault crew found a street light had melted. | Public lighting | 0 | 0 | 0 |  |  | The cause was unknown but could be attributed to a possible overheated connection. | Plant/equipment | 43530.6181 | 1 | Negligible: no ground fire | 13950 | Roadway |  | 20190702UTD_01 | Infrastructure (network-based) | -38.3691 | 144.7712 | 1 | United Energy Distribution | Report | 17431 | 0.031703 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Connection
Site made safe and pole replaced. | 2169 CRESWICK NEWSTEAD ROAD CAMPBELLTOWN 3364 | 32043668 |  | Lightning |  |  |  |  | 2 | Customer reported wire low enough to be touched, roughly 1m off ground, sheep are hanging around wire. Crew found SWER pole requires replacement damaged by lightning strike and conductor hanging low. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CMN002 | Damage from lightning strike - possibly 1-2 weeks ago | Fatality of livestock, pet or companion animal | 43592.5472 |  |  | 13983 |  |  | 20190708PWA_01 | Infrastructure (network-based) | -37.2225 | 143.9354 | 1 | Powercor | Report | 17481 | 0.015743 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3364 |  | Lightning
Fault crew dispatched and candled EDO HV fuse replaced | 15 VICTORIA STREET, PORT ALBERT VIC 3971 | LIS2624442 |  |  |  | Candled fuse |  |  |  | Fuse candling | EDO fuse | 0 | 0 | 0 |  | FTR23 | Candled EDO HV Fuse | Pole-top fire | 43623.8194 | 1 | Negligible: no ground fire | 13976 |  |  | 20190708SPN_02 | Infrastructure (network-based) | -38.6725 | 146.6926 | 1 | AusNet Services Distribution | Report | 17471 | 0.00022685 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Port Albert | Fuse
SES on site attending scene. Fault crew dispatched and came across the incident scene involving a downed helicopter. Control advised of the incident and the nature of the fault (conductors down) to the network causing ACR to operate. Supply isolated and conductor cut clear. Repairs carried out and supply restored the following day. | MANSFIELD-WOODS POINT ROAD, MANSFIELD VIC 3722 | LIS3915079 | Manned aircraft | [5 empty] | 1 | Report of helicopter contacting O/H HV conductor | Conductor (bare) | 0 | 0 | 0 |  | MSD1 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43623.6292 |  |  | 13977 |  |  | 20190708SPN_03 | Infrastructure (network-based) | -37.1742 | 146.1446 | 2 | AusNet Services Distribution | Report | 17473 | 0.011052 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Other
Fault crew dispatched and candled fuse replaced with new | 560 MCDOUGAL ROAD, NEERIM SOUTH VIC 3831 | LIS2706750 |  |  |  | Candled fuse |  |  |  | Report of fuse candling | Boric acid | 0 | 0 | 0 |  | WGL24 | Boric Acid HV fuse has candled | Pole-top fire | 43715.25 | 1 | Negligible: no ground fire | 13989 |  |  | 20190710SPN_02 | Infrastructure (network-based) | -38.0429 | 146.0092 | 2 | AusNet Services Distribution | Report | 17490 | 0.0223 | 22kV AC | Morwell (Latrobe Valley Airport) | 3831 | Neerim South | Fuse
The electrical inspected carried out voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a high impedance in the neutral screened overhead service cable feeding the installation. With 50V recorded on this installations earthing system under load. Jemena crew replaced single phase neutral screen service with new xlpe service. | 45 FISCHER STREET, COBURG VIC 3058 |  |  |  |  | Corrosion |  |  | 2 | An electric shock was noticed while the customer whilst she was showering and simultaneously made contact with the metallic water tap with her hand and standing on the wet shower base. | Service conductor | 0 | 0 | 0 |  |  | The corrosion of the overhead service cable appeared to be the result of water entering the outer sheath via a small perforation in the cable, the cause of which is unknown. | Minor shock | 43776.7049 |  |  | 13992 | Residential |  | 20190711JEM_02 | Infrastructure (customer connection) | -37.7335 | 144.9539 | 1 | Jemena | Report | 17493 | 0.017949 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | OH Cable
isolated and replaced transformer | UNIT 1 140 BIGGS STREET, ST ALBANS VIC 3021 | 30543930 |  |  |  | Defective component |  |  | 2 | Person reports receiving an electric shock every time she use the shower. | Transformer | 0 | 0 | 0 |  | SA005 | internal transformer fault | Minor shock | 43684.5 |  |  | 14002 | Residential |  | 20190715PWA_05 | Infrastructure (network-based) | -37.7375 | 144.8069 | 1 | Powercor | Report | 17503 | 0.040304 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | AF Other
Crews attended, isolated the supply and performed repairs. | 9-13 ANTHONY STREET, MELBOURNE VIC 3000 | 35334793 | Working too close to underground cables | [6 empty] | A company representative from Comdain Gas called to report that one of their employees had struck an underground cable with a jackhammer. On arrival the crew found the jackhammer had struck an LV UG cable, the jackhammer operator was not injured and did not receive a shock. There were no reported injuries, or other reported damage. | Cable | 2 | 2 | 2 |  | JA042 | Using jackhammer contacted LV cable, Failure of contractors to identify cable location prior to using jackhammer. | No Go Zone (contact);Damage to network assets | 43531.441 |  |  | 14003 | Roadway |  | 20190715PWA_06 | Infrastructure (network-based) | -37.8094 | 144.9591 | 1 | CitiPower | Report | 17504 | 0.0050995 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew isolated supply and carried out repairs | 20 SPRINGS ROAD, BROWN HILL VIC 3350 | 32000612 |  |  |  | Overheated connection |  |  |  | A customer reported transformer and wire on fire at the incident location. The attended crew found that an insulated HV dropper on the substation pole ignited. There was no ground fire. | Dropper/bridge | 2 | 2 | 2 |  | BAN015 | overheated connection | Pole-top fire | 43562.4528 | 1 | Negligible: no ground fire | 14005 | Roadway |  | 20190715PWA_08 | Infrastructure (network-based) | -37.5467 | 143.9119 | 1 | Powercor | Report | 17506 | 0.03175 | 22kV AC | Ballarat Aerodrome | 3350 | Brown Hill | Connection
Crew replaced fuse | 115 WARRION HILL ROAD, WARRION VIC 3249 | 30054866 |  |  |  | Fuse failed to eject |  |  |  | Following customer supply problems crew found EDO fuse burnt in half. There was no ground fire, no reported injuries or third part property damage. | EDO fuse | 2 | 2 | 2 |  | CLC003 | Excessive leakage current | Pole-top fire | 43652.659 | 1 | Negligible: no ground fire | 14015 | Roadway |  | 20190717PWA_03 | Infrastructure (customer connection) | -38.2142 | 143.5453 | 1 | Powercor | Report | 17529 | 0.017075 | 22kV AC | Ballarat Aerodrome | 3249 | Warrion | Fuse
Crew arrived on site and made safe and began repairs | 716-734 HIGH STREET, RESERVOIR VIC 3073 | Pole No A077081 | Vehicle |  |  |  |  | Phase to earth | 1 | Truck has crashed into an HV/LV pole, causing it to break and resulting in HV and LV conductors to hit the ground. | Conductor (bare);Service conductor;Pole (wood);Pole top;Public lighting | 0 | 0 | 0 |  | CN7 | Truck crashed into pole causing it to break, resulting in HV and LV conductors on ground. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 18/07/2019 13:28 |  |  | 14026 | Commercial |  | 20190719JEM_01 | Infrastructure (network-based) | -37.7274 | 145.006 | 1 | Jemena | Report | 17545 | 0.024833 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3073 | Reservoir | Vehicle
Crew isolated the damaged cable. Cable repaired and reinstated. | 101 LONSDALE STREET, MELBOURNE VIC 3000 | 30205967 | Working too close to underground cables | [6 empty] | Contractor working on traffic lights at the incident location have contacted and damaged a low voltage underground main with a jack hammer. No fuses blown and no customers lost supply. There was no fire and no reported injuries due to this incident. | Cable | 2 | 2 | 2 |  | WA035 | Cable contacted while using a mini jack hammer | No Go Zone (contact);Damage to network assets | 43562.4167 |  |  | 14023 | Roadway |  | 20190719PWA_01 | Infrastructure (network-based) | -37.8103 | 144.9695 | 1 | CitiPower | Report | 17540 | 0.0022581 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
On arrival crew made site safe repairs initiated | CALDER HIGHWAY, MACEDON VIC 3440 | 32049435 | Copper theft | [6 empty] | VIC Police while on patrol came across what they believed to be copper theft at Regional Road Installation site at Pole#119 Woodened South. Powercor crew attended and confirmed. The copper was a temporary supply for the Public Road Lights after a previous copper theft of the major installation for heating of the overpass bridge. The temporary supply had only been disconnected yesterday 3rd July 2019. There was no fire, no reported injuries. | Customer installation | 2 | 2 | 2 |  | GSB014 | Copper theft | Damage to network assets | 43562.0049 |  |  | 14024 | Public space |  | 20190719PWA_02 | Infrastructure (network-based) | -37.4152 | 144.5448 | 1 | Powercor | Report | 17542 | 0.015987 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
On arrival crew inspected asset and carried out repairs | 15 ROSSER STREET, BRUNSWICK VIC 3056 | CP0011337 | Vandalism;Copper theft | [6 empty] | God Father's Pizza (Robin - 0431191560) reported shop lights flickering in his shop and street traffic lights were off. On arrival, the crew found a 'Rosser-Victoria (R)' kiosk substation door damage and ripped open. There was an apparent attempt of copper theft and thieves caused the transformer to trip. There was no fire and no reported injuries | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | WB004 | Vandalism and attempted copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 14/07/2019 14:58 |  |  | 14048 | Commercial |  | 20190724PWA_01 | Infrastructure (network-based) | -37.7674 | 144.9604 | 1 | CitiPower | Report | 17570 | 0.028431 | Low voltage AC (<1kV);6.6kV AC | Essendon Airport | 3056 | Brunswick | Other
Crew isolated the pole and all supply restored. One property will be off until pole replaced. | WHITE ROAD, WOORINEN NORTH VIC 3589 | 32161264 |  |  |  | Leakage |  |  |  | Vic Fire reported Wires down and pole on fire reported at Intersection of White Rd and Nth Sth Rd Beverford. On arrival found that pole top had burnt thru and toppled over all insulators and phases still connected. There was no ground fire, no reported injuries or third party property damage Crew isolated the pole and all supply restored. One property will be off until pole replaced. | Pole (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 24/07/2019 11:30 | 1 | Negligible: no ground fire | 14052 | Roadway |  | 20190724PWA_03 | Infrastructure (network-based) | -35.2317 | 143.451 | 1 | Powercor | Report | 17576 | 0.0014039 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen North | Pole
Crew organized a public lighting head unit to be replaced the next day | 1122 BURKE ROAD, BALWYN NORTH VIC 3104 | 30167864 |  |  |  | Corrosion |  |  |  | MFB reported a pole fire at the above incident location. Upon crew arrival, they reported a faulty 150W public lighting head unit which had caught on fire. There was no reported injuries or ground fire. | Public lighting | 2 | 2 | 2 |  | L022 | Overheated connection | Pole-top fire | 16/07/2019 18:44 | 1 | Negligible: no ground fire | 14053 | Roadway |  | 20190724PWA_04 | Infrastructure (network-based) | -37.7948 | 145.0638 | 1 | CitiPower | Report | 17578 | 0.030366 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | Connection
On arrival The crew made the site safe by removing the transformer HV fuses. | 1212-1218 LEAKES ROAD, ROCKBANK VIC 3335 | 33071818 | Vandalism;Copper theft | [6 empty] | Metering group (MOG) reported that the underground service to 1212 Leakes Rd had been stolen along with the HV/LV earth at the same pole. Upon arrival the fault crew found that the pole, located on the property had the consumer mains which run between the abandoned house and the customer fuse box located on the crossarm at the pole stolen. The thieves also stole the HV & LV earth from ground level up to the transformer. There was no fire or reported injuries. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 17/07/2019 14:45 |  |  | 14055 | Public space |  | 20190724PWA_06 | Infrastructure (network-based) | -37.7319 | 144.6461 | 1 | Powercor | Report | 17580 | 0.025178 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3335 | Rockbank | Other
On arrival crew isolated supply and carried out repairs. | 22 HENRY STREET, GLENTHOMPSON VIC 3293 | 31017493 | Vehicle | [6 empty] | Vic Fire reported truck hit pole at incident location, wire resting on truck. Crew found driver still in truck, made safe, driver reported braking around bend and trailer slid into pole, no injuries, possible HVI but no damage initially found, follow-up to 1 x replace service cable and inspect remaining property 18/07/2019. There was no fire, no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | HTN005 | Semi trailer slid into pole | Loss of supply;Damage to network assets | 17/07/2019 14:05 |  |  | 14070 | Roadway |  | 20190729PWA_02 | Infrastructure (network-based) | -37.6353 | 142.548 | 1 | Powercor | Report | 17596 | 0.0091273 | Low voltage AC (<1kV);22kV AC | Hamilton Airport | 3293 | Glenthompson | Vehicle
On arrival crew isolated supply and carried out repairs. | 39-155 BERTIE STREET, PORT MELBOURNE VIC 3207 | 30205968 |  |  |  | Leakage |  |  |  | Inspector found pole top burnt at incident location. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | MG014 | Excessive leakage current | Pole-top fire | 21/11/2018 16:22 | 1 | Negligible: no ground fire | 14075 | Roadway |  | 20190730PWA_01 | Infrastructure (network-based) | -37.8297 | 144.939 | 1 | CitiPower | Report | 18106 | 0.024878 | 11kV AC | Essendon Airport | 3207 | Port Melbourne | Pole
Crew attended site and have isolated the kiosk, site made safe. repairs to be scheduled. | 11 CAMPASPE WAY, POINT COOK VIC 3030 | 156461273 | Copper theft | [6 empty] | Following a report of possible theft at development site a crew attended incident location. Thieves have broken the lock on a kiosk substation Hacketts-Dunnings . Then they removed the bar copper from the high voltage end and also cut and removed copper screen wires from two of the three high voltage 22kV cables, before leaving site. The kiosk's door was left ajar and loud buzzing noises were coming from the kiosk. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | LV004 | Copper theft | Damage to network assets | 22/07/2019 11:22 |  |  | 14086 | Public space |  | 20190802PWA_02 | Infrastructure (network-based) | -37.8824 | 144.7196 | 1 | Powercor | Report | 17629 | 0.022738 | Earthing cable | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew isolated supply and arranged repairs. | 137 COWRA AVENUE EX, IRYMPLE VIC 3498 | 32145825 | Working too close to underground cables | [6 empty] | REC reported a post hole digger has cut through an under ground cable from the transformer to pit, customer has no power, On arrival crew found a LV U/G cable from pole to pit dig up by third party. There was no frin, no reported injuries or third party property damage | Services cable | 2 | 2 | 2 |  | MDA023 | Post hold digger struck service cable | No Go Zone (contact);Damage to network assets | 24/07/2019 17:05 |  |  | 14102 | Roadway |  | 20190809PWA_03 | Infrastructure (network-based) | -34.2588 | 142.1128 | 1 | Powercor | Report | 17647 | 0.0053056 | Low voltage AC (<1kV) | Mildura Airport | 3498 | Irymple | Dug up
On arrival crew carried out repairs | 1865-1881 Mount Cottrell Rd, Mount Cottrell VIC 3024, Australia | 32167725 | Copper theft | [6 empty] | A company employee, reported a copper theft at the incident location. Jade said that he found that the HV and LV earths on the sub pole â€˜MT COT S GREIGS P20 â€˜ had been stolen by an unknown party. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN011 | Copper theft | Damage to network assets | 25/07/2019 19:35 |  |  | 14109 | Roadway |  | 20190809PWA_04 | Infrastructure (network-based) | -37.777 | 144.6079 | 1 | Powercor | Report | 17655 | 0.0088218 | Earthing cable | Laverton Raaf | 3024 | Mount Cottrell | Other
On arrival crew carried out repairs | 2 Black Forest Rd, Little River VIC 3211, Australia | 33042049 | Copper theft | [6 empty] | A contractor reported exposed wires hanging on a pole at the incident location. Upon arrival the crew found that the earthing cable of the single phase substation had been cut away. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | FNS022 | Copper theft | Damage to network assets | 25/07/2019 9:24 |  |  | 14110 | Agricultural |  | 20190809PWA_05 | Infrastructure (network-based) | -37.8856 | 144.4759 | 1 | Powercor | Report | 17656 | 0.016198 | Earthing cable | Avalon Airport | 3211 | Little River | Other
Bird nest removed, substation structure inspected for damage | 43 COWIE ROAD, GIRGARRE VIC 3624 | 32189817 |  | Bird | [5 empty] | Customer reported pole fire at the incident location, customer also advised that a large Crow's nest was built on the structure in question & believe that to be the source of the fire. Upon arrival crew found that a birds nest was built on the termination substation structure, material within the nest was believed to be conductive & when a rain event commenced a flashover occurred that commenced combustion of the nesting materials. The fire soon self extinguished with the precipitation. No ground fire occurred, no damage to 3rd party. | Pole mounted | 2 | 2 | 2 |  | SHP011 | Bird Incident | Pole-top fire | 26/07/2019 19:12 | 1 | Negligible: no ground fire | 14111 |  |  | 20190809PWA_06 | Infrastructure (network-based) | -36.4036 | 144.9614 | 1 | Powercor | Report | 17657 | 0.037769 | 22kV AC | Shepparton Airport | 3624 | Girgarre | Animal
Fault crew dispatched and failed gas switch replaced. Supply restored | 107 GOLF LINKS ROAD, BERWICK VIC 3806 | LIS2601658157 |  | Bird | [5 empty] | Pole fire reported | Any other type;Pole (concrete) | 0 | 1 | 0 |  | CLN14 | Bird Incident | Pole-top fire | 43745.8625 | 1 | Negligible: no ground fire | 14105 | Residential |  | 20190809SPN_05 | Infrastructure (network-based) | -38.044 | 145.3306 | 2 | AusNet Services Distribution | Report | 18070 | 0.031953 | 22kV AC | Moorabbin Airport | 3806 | Berwick | Animal
Fault crew dispatched. Damaged street light head removed and replaced with new | 257 PLENTY RIVER DRIVE, GREENSBOROUGH VIC 3088 | LIS5811828 |  |  |  | Defective component |  |  |  | CFA reported street light fire | Public lighting | 0 | 0 | 0 |  | ELM31 | A faulty igniter appears to be the likely cause for the luminaire failure and subsequent fire | Pole-top fire | 28/07/2019 19:00 | 1 | Negligible: no ground fire | 14106 | Residential |  | 20190809SPN_06 | Infrastructure (network-based) | -37.6829 | 145.1142 | 2 | AusNet Services Distribution | Report | 17706 | 0.028521 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | AF Other
Fault crew dispatched to investigate and carry out repairs. | 10 MORLEY STREET, ORBOST VIC 3888 | LIS1907893 |  | Blown branch/vegetation | [5 empty] | Report of tree falling into and bringing down O/H LV conductors | Conductor (bare) | 0 | 0 | 0 |  | NLA32 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/07/2019 8:55 |  |  | 14108 | Roadway |  | 20190809SPN_07 | Infrastructure (network-based) | -37.7098 | 148.4594 | 1 | AusNet Services Distribution | Report | 17707 | 0.037854 | Low voltage AC (<1kV) | Bairnsdale Airport | 3888 | Orbost | Trees
Repairs were effected where possible. Fault follow-up required to replace the missing lighting cable. | 41-53 ABEY ROAD, COBBLEBANK VIC 3338 | 30336498 | Copper theft | [6 empty] | Reported several pits open and cables stolen, along Abey Rd, Melton South Attending Powercor fault crew noted another approx. 100 route metres of underground lighting cable cut and stolen. Live cable end had been left exposed at LIS 842973. Pulling chain and rope found at two locations. There were no shocks, injuries or ground fire. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 28/07/2019 11:40 |  |  | 14117 | Roadway |  | 20190812PWA_01 | Infrastructure (network-based) | -37.7056 | 144.5964 | 1 | Powercor | Report | 17665 | 0.0020185 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
On arrival crew isolated supply and arranged repairs | 7 HERCULES DRIVE, TRUGANINA VIC 3029 | 30543481 | Working too close to underground cables | [6 empty] | A Landscaping crew from ESEO Pty Ltd called to report that they had scraped an LV UG cable at the incident location. When the crew arrived on site, they found that a cable feeding streetlights in a new estate had been damaged. The crew noted that the landscaping crew were scraping the surface soil away with a bobcat to allow for laying turf. The exact depth of the cable prior to the contact could not be determined due to the earthworks. There were no injuries or fires. | Services cable | 2 | 2 | 2 |  | LV002 | Lanscaping works using bobcat | Damage to network assets | 30/07/2019 10:49 |  |  | 14122 | Roadway |  | 20190813PWA_01 | Infrastructure (network-based) | -37.8171 | 144.715 | 1 | Powercor | Report | 17670 | 0.0193 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Dug up
Low voltage circuit isolated, repairs completed and supply restored. | 352 VICTORIA PARADE, EAST MELBOURNE VIC 3002 | 30206918 | Working too close to underground cables | [5 empty] | 1 | Contractors (subcontracting for TPG) installing conduits using in Victoria parade using a Grundamat borer have bored through the service cable to no. 352 &354 Victoria Parade. Two low voltage fuses operated cutting supply to two customers. | Services cable | 0 | 0 | 0 |  | MP055 | Contractor using borer struck cable | Loss of supply;No Go Zone (contact);Damage to network assets | 23/07/2019 9:23 |  |  | 14137 | Roadway |  | 20190813PWA_15 | Infrastructure (network-based) | -37.8093 | 144.9833 | 1 | CitiPower | Report | 17685 | 0.029699 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Dug up
service replaced | 116 RENNIE STREET, THORNBURY VIC 3071 | 30199995 |  |  |  | Corrosion |  |  | 2 | person received an electric shock when he contacted the metallic garden tap with his hand whilst making simultaneous contact with the general mass of earth | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | NC004 | Corroded service line | Minor shock | 43473.4792 |  |  | 14138 | Residential |  | 20190813PWA_16 | Infrastructure (customer connection) | -37.7525 | 144.984 | 1 | CitiPower | Report | 17686 | 0.035597 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | OH Cable
crew tightened loose connection | 68 MCKEAN STREET, FITZROY NORTH VIC 3068 | 30163604 |  |  |  | Overheated connection |  |  | 2 | Person received an electric shock when he contacted the metallic garden tap with his hand whilst making simultaneous contact with the general mass of earth with his feet | Service cable (insulated) | 0 | 0 | 0 |  | F033 | Loose neutral connection at CitiPower pole | Minor shock | 31/07/2019 10:00 |  |  | 14139 | Residential |  | 20190813PWA_17 | Infrastructure (customer connection) | -37.7896 | 144.9853 | 1 | CitiPower | Report | 17687 | 0.041072 | Low voltage AC (<1kV) | Essendon Airport | 3068 | Fitzroy North | Connection
CFA extinguished fire. Crew to replace pole. | 400 BLACK FOREST ROAD, LITTLE RIVER VIC 3211 | 30140889 | Vandalism | [6 empty] | VicFire reported pole fire at the above location. Crew attended and found unknown persons had started a fire at the base of pole. CFA and police in attendance. No shocks, injuries or third party damage. | Pole (wood) | 2 | 2 | 2 |  | FNS022 | Fire started by unknown person | Grassfire;Damage to network assets | 14/08/2019 8:52 | 0 | Localised: less than 10 sq.m | 14151 | Roadway |  | 20190815PWA_01 | Infrastructure (network-based) | -37.8847 | 144.4833 | 1 | Powercor | Report | 17704 | 0.040628 | 22kV AC | Avalon Airport | 3211 | Little River | Other
Supply isolated repairs carried out | 6 Nealie St, Cardross VIC 3496, Australia | 32145619 |  |  |  | Leakage |  |  |  | Pole fire reported by Vic Fire at incident location. On arrival crew found pole had burnt from below HV crossarm to stay position. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire;Damage to network assets | 43777.1792 | 1 | Negligible: no ground fire | 14153 | Roadway |  | 20190815PWA_03 | Infrastructure (network-based) | -34.3065 | 142.1642 | 1 | Powercor | Report | 17708 | 0.027627 | 22kV AC | Mildura Airport | 3496 | Cardross | Pole
The crew removed and abolished the overhead service and recovered the electricity meter. | 28 MOORE CRESCENT, RESERVOIR VIC 3073 |  | Unauthorised work | [5 empty] | 2 | Metering & Service crew attended with a service order for an abolishment of the service and meter. When they arrived they found the service fuse at the POA had been removed and the electricity meter being removed and the meter being placed in the front yard of the property. Asbestos and demolishing personal were on site. Energy Safe Victoria were conducting an audit at the time of the incident. | Smart meter;Service cable (insulated) | 2 | 2 | 2 |  |  | Unknown person removed service fuse and disconnected the meter. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/08/2019 10:30 |  |  | 14156 | Residential |  | 20190816JEM_01 | Infrastructure (customer connection) | -37.7197 | 145.001 | 1 | Jemena | Report | 17713 | 0.031588 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Crews attended and performed repairs | 478 Learmonth-Sulky Rd, Blowhard VIC 3352, Australia | 30001657 | Copper theft | [6 empty] | A Powercor employee reported a broken earth on Learmonth Pole1 (LIS-3177) possibly cut with an axe. On arrival the crew found that unknown person/s had cut an approx. 2 metre section of copper earth wire on the switch pole. There were axe marks on the pole where the copper had been cut, but the marks were not recent, and the copper may have been removed sometime in the past. There were no reported injuries or fire. | Earth/earthing | 2 | 2 | 2 |  | BAN006 | Copper theft | Damage to network assets | 13/08/2019 10:17 |  |  | 14157 | Roadway |  | 20190816PWA_01 | Infrastructure (network-based) | -37.4449 | 143.7937 | 1 | Powercor | Report | 17714 | 0.029017 | Earthing cable | Ballarat Aerodrome | 3352 | Blowhard | Other
Fault Crew replaced the Multi Phase FOLCB | 44 WEST STREET, RUSHWORTH VIC 3612 | 30247167 |  |  |  | Corrosion |  |  | 2 | person was using a Pressure Washer when he received an electric shock as he made simultaneous contact with one hand on the earthed metallic body of the Pressure Washer and his feet whilst standing on a wet concrete drive. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded Service Neutral Conductor termination at the Network FOLCB located on the Reticulation Pole forming part of the U/G Service supplying the property | Service cable (insulated) | 0 | 0 | 0 |  | SHP014 | Corroded Service Neutral Conductor termination at the Network FOLCB located on the Reticulation Pole forming part of the U/G Service supplying the property | Minor shock | 29/07/2019 9:00 |  |  | 14163 | Residential |  | 20190816PWA_06 | Infrastructure (network-based) | -36.59 | 145.0258 | 1 | Powercor | Report | 17720 | 0.023992 | Low voltage AC (<1kV) | Mangalore Airport | 3612 | Rushworth | Connection
On arrival supply isolated and meter replaced. | 9 BARCLAY STREET, THORNHILL PARK VIC 3335 | MLN021 | Vandalism | [6 empty] | REC reported broken meter and exposed wiring at premises. On arrival crew found damaged vandalised meter. damage caused by unknown party. There was no fire, no injuries or third party property damage | Smart meter | 2 | 2 | 2 |  | 155791671 | Vandalism by unknown persons | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 14/08/2019 12:33 |  |  | 14167 | Residential |  | 20190819PWA_02 | Infrastructure (customer connection) | -37.7092 | 144.6279 | 1 | Powercor | Report | 17734 | 0.020435 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | Other
On arrival crew isolated supply and carried out repairs | 1 Hilda Cres, Hawthorn VIC 3122, Australia | 30180397 |  | Within clearances | [5 empty] | Various residents on the same area reported no power to their homes and wires on ground. On arrival, the crew found one phase of the LV overhead conductor was broken and lying on the ground. There was no ground fire, no third party damaged and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | CL013 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 15/08/2019 18:18 |  |  | 14171 | Roadway |  | 20190819PWA_03 | Infrastructure (network-based) | -37.8191 | 145.0285 | 1 | CitiPower | Report | 18274 | 0.0030787 | Low voltage AC (<1kV) | Essendon Airport | 3122 | Hawthorn | Trees
On arrival crew inspected assets - No damage found | Treasury Pl, East Melbourne VIC 3002, Australia | 30324584 | Working too close to underground cables | [6 empty] | City of Melbourne reported a cable dug up at the incident location. Upon arrival, a CitiPower crew found that a contractor excavated beside the cable path but no damage has been done to the cable. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MP009 | Landscaping works near underground service cable | No Go Zone (no contact) | 15/08/2019 14:00 |  |  | 14174 | Public space |  | 20190819PWA_05 | Infrastructure (network-based) | -37.8136 | 144.9766 | 1 | CitiPower | Report | 17732 | 0.0053924 | Low voltage AC (<1kV) | Essendon Airport | 3002 | East Melbourne | Dug up
UE fault crews attended and determined that directional bore works had hit and damaged an underground supply to the street lights. A No Go Zone permit was on issue for the works. The crews isolated the supply at the LV cabinet in the street, and made repairs to the cable. | 7 MAIN STREET, MORNINGTON VIC 3931 | 9940624 | Working too close to underground cables | [5 empty] | 1 | UE received a report that an underground LV cable had been hit and damaged by directional boring works. When the cable was hit the street lights went out. | Cable | 0 | 0 | 0 |  |  | The cause was the directional boring. A no go zone permit was on issue. | Damage to network assets | 43593.2118 |  |  | 14184 | Roadway |  | 20190820UTD_01 | Infrastructure (network-based) | -38.2168 | 145.0367 | 1 | United Energy Distribution | Report | 17747 | 0.024454 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Dug up
Fault crew were on site rectifying a faulty P/L luminaire when the flashover occurred Supply isolated and cable repaired. | 26 JERSEY CRESCENT, OFFICER VIC 3809 | LIS5825404 |  |  |  | Moisture ingress;Defective component |  |  |  | Public lighting cable flashed over in pit | Cable;Services pit (network) | 0 | 0 | 0 |  | OFR21 | Fault crew were attending fault to rectify a faulty P/L luminaire. Crew proceeded to open the pit to isolate supply to the P/L when the UG cables flashed over as the pit lid was removed and the public lighting cables melted in the pit. No injuries were sustained and no evidence of fire 6mm XLPE P/L cable insulation had been damaged at some stage, most likely during installation, causing water to enter the cable causing the short. | Singeing or local charring/blackening only | 23/06/2019 23:00 |  |  | 14185 | Roadway |  | 20190821SPN_01 | Infrastructure (network-based) | -38.0703 | 145.3868 | 2 | AusNet Services Distribution | Report | 17810 | 0.023097 | Low voltage AC (<1kV) | Moorabbin Airport | 3809 | Officer | UG Cable
House at no.46 was defected (customers main box, POA and mains cable). Defect no: 02724. Crew replaced service and installed breakaway device. The builder requested No Go Zone (NGZ) assessment on 27/06/2019. NGZ assessor assessed the site on 04/07/2019. Permit issued, tiger mats and warning signs installed. | 44 GARNET STREET, NIDDRIE VIC 3042 | A062562 | Working too close to overhead lines;Vehicle | [5 empty] | 2 | A tip truck dropping of materials to the site, drove off with the tray up, which pulled down the service onto the truck and ripped off fascia to house at No.46. | Service cable (insulated) | 2 | 2 | 2 |  | ES21 | No Go Zone breach. Economix tip truck pulled down service. | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/06/2019 13:36 |  |  | 14208 | Residential |  | 20190823JEM_03 | Infrastructure (customer connection) | -37.7475 | 144.8874 | 1 | Jemena | Report | 18193 | 0.0019502 | Low voltage AC (<1kV) | Essendon Airport | 3042 | Niddrie | Other
Metering & Servicing crews have disconnected, removed and made safe the live hanging S/L. | 1 Marie Ave, Heidelberg Heights VIC 3081, Australia | A109288 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the address today with a SO for an abolishment of electricity supply and electricity meter. When they attended site, they found a vacant block of land with no dwelling with the overhead supply still connected to open wire asset in the street cut and just left hanging live and no electricity meter on site Photos are attached in the "Notes & Findings" section | Smart meter | 0 | 0 | 0 |  | NH05 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/08/2019 12:24 |  |  | 14209 | Residential |  | 20190826JEM_01 | Infrastructure (network-based) | -37.7387 | 145.0495 | 1 | Jemena | Report | 18457 | 0.030572 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg Heights | Other
Crew replaced the cables and made safe. | BULMANS ROAD, MELTON WEST VIC 3337 | 30298011 | Copper theft | [6 empty] | Customer Matt Hassett reported vandalised U/G pits. Upon arrival the crew found service cables feeding multiple Street lights (from LIS 784380 to 784377) exposed and stolen. The time/date of the theft is not known. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN022 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 16/08/2019 18:15 |  |  | 14211 | Roadway |  | 20190826PWA_02 | Infrastructure (network-based) | -37.6866 | 144.5495 | 1 | Powercor | Report | 17842 | 0.015068 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
ON arrive site made safe and repairs initiated. | 28 Brooklyn Park Dr, Brookfield VIC 3338, Australia | 30112005 | Copper theft | [6 empty] | Customer advised special reader has attended the site and advised fuse in and no supply at meters. Upon arrival the crew found the following items stolen: Approx 3m 70mm bare copper (HV earth) -Approx 25m Copper mains cable from FOLCB at pole to pit) - approx 30m of Copper consumer mains cables from pit to meter position There was no fire no reported injuries. | Services cable;Earth/earthing | 2 | 2 | 2 |  | MLN022 | Copper theft | Loss of supply;Damage to network assets | 19/08/2019 13:45 |  |  | 14212 | Roadway |  | 20190826PWA_03 | Infrastructure (network-based) | -37.6974 | 144.5256 | 1 | Powercor | Report | 17843 | 0.015064 | Low voltage AC (<1kV);Earthing cable | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew carried out repairs | Unit 2/20 Glenville Dr, Melton VIC 3337, Australia | 60229127 | Vandalism;Copper theft | [6 empty] | Customer Neil reported possible attempted copper theft, sliced wires at front of property at footpath and wires exposed. Upon arrival the crew found pit opened, pit connectors cut at line side, exposed live conductors hanging out of pit at pit outside 1/20, 2/20 and 22 GLENVILLE DRIVE, MELTON. There was no copper stolen at any pit. There was no fire, no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Attempted copper theft and vandalism | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/08/2019 9:06 |  |  | 14213 | Roadway |  | 20190826PWA_04 | Infrastructure (network-based) | -37.6873 | 144.5925 | 1 | Powercor | Report | 17844 | 0.039336 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Other
On arrival crew isolated supply and arranged repairs | 21 Manor Lakes Blvd, Wyndham Vale VIC 3024, Australia | 34027929 | Copper theft | [6 empty] | Report received from customer that between Armstrong Rd & Ballan Rd, 6 pits lids have been lifted, can see cable hanging out of top of pits, possible stolen cable; noticed street lights not working last night. Upon arrival the fault crew found that approximately 250m of 16mm 4/c public lighting cable had been stolen . The theft of the cable at these sections meant that there was no supply to a total of 20 lights supplied from the two affected public lighting circuits. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WBE014 | Copper theft | Damage to network assets | 24/08/2019 15:18 |  |  | 14222 | Roadway |  | 20190828PWA_02 | Infrastructure (network-based) | -37.8769 | 144.613 | 1 | Powercor | Report | 17854 | 0.0066412 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Other
Fault crew dispatched to investigate and make safe. Crew contacted control room to isolate and make it safe. Transformer removed and replaced with new complete with new krone box and HV dropper leads. | 18 MACKINTOSH ROAD, NEERIM SOUTH VIC 3831 | LIS2700235 |  |  |  | Unknown technical factor |  |  |  | Report of grass fire in vicinity of pole | Circuit breaker;Transformer | 0 | 1 | 0 |  | WGL24 | Crew arrived and found the grass beneath the transformer was burnt, but no fire was present when crew arrived. Transformer had a slow oil leak from the HV bushing and had failed but attending crew advised the fire did not start from the transformer. Investigation conducted but exact cause of fire inconclusive. Attending crew advised civil works had taken place in the vicinity and the grass fire may have been caused by the circuit breaker on pole. | Grassfire | 43618.5521 | 1 | Small: 10 - 1000 sq.m | 14223 |  |  | 20190828SPN_01 | Infrastructure (network-based) | -38.0173 | 145.9736 | 1 | AusNet Services Distribution | Report | 17855 | 0.019554 | 22kV AC | Morwell (Latrobe Valley Airport) | 3831 | Neerim South | AF Other
On arrival crew carried out repairs to conductor. LEI checked for HVI non found | 137 Smith St, Thornbury VIC 3071, Australia | 30199754 | Working too close to overhead lines | [6 empty] | A crew investigating a feeder fault, reported finding damage consistent with something contacting the 11kV HV overhead conductor. On further investigation they found that a crane had contacted the HV. There were no reported injuries or fires. | Conductor (bare) | 2 | 2 | 2 |  | NC015 | Crane contacted HV overhead line | No Go Zone (contact);Damage to network assets | 28/08/2019 8:11 |  |  | 14232 | Roadway |  | 20190829PWA_02 | Infrastructure (network-based) | -37.7566 | 144.99 | 1 | CitiPower | Report | 17871 | 0.010148 | 11kV AC | Essendon Airport | 3071 | Thornbury | Vehicle
Fault crew and LEI dispatched, line isolated and made safe. O/H conductors repaired and re-strung. Supply restored | 170 OLD BAKER ROAD, WANDIN EAST VIC 3139 | LIS1011486 |  | Blown branch/vegetation |  | HV injection |  |  | 1 | report of HVI and conductors down | Conductor (bare) | 0 | 0 | 0 |  | WYK12 | Vegetation: Trees Incident | HV injection | 21/08/2019 14:47 |  |  | 14243 | Roadway |  | 20190903SPN_03 | Infrastructure (network-based) | -37.8026 | 145.4466 | 1 | AusNet Services Distribution | Report | 17892 | 0.033034 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3139 | Wandin East | Trees
Site made safe and incident reported to ESV | 84A Kyle Rd, Altona North VIC 3025, Australia | A136333 | Working too close to underground cables | [5 empty] | 2 | 22kv Line tripped under fault conditions. Operator Isolated and Earthed cable to investigate fault. Found 22KV underground cable exposed and damaged by third party excavator. ESV was informed via their call centre, Reference number 12403629 â€¢ Multiworks was working for Zinfra as a sub-contractor on the West Gate tunnel project, Zinfra was engaged by John Holland to prepare mono pole tower footings inside the Ausnet Terminal Station. â€¢ Multiworks excavator operator has dug up concrete cover slabs inside the terminal station and struck Jemenaâ€™s underground BLTS-MB29 feeder cables. â€¢ Fault occurred at 16:18 Thursday 5/09/19, Zinfra crew attended but ran out of hours that night and returned at approximately 10:30am 6/09/19 to further investigate location of fault. â€¢ While operator was stepping out approximate location he came across the deep excavation and found underground cable uncovered and damaged. â€¢ Multiworks excavator crew on site told the operator that they had hit this cable the day prior but had not reported it yet. â€¢ Multiworks is preparing an investigation report for Zinfra West Gate Tunnel Projects team: James Morton - Senior Project Manager, Dylan Hocking - Site Engineer, Christos Litsios - HSE Advisor Delivery Projects | Cable | 0 | 0 | 0 |  | blts-mb29 22kv line | Third party Excavator damaged 22KV Live undergound cable inside Brooklyn Terminal Station. | No Go Zone (contact) | 43594.6792 |  |  | 14255 | Construction |  | 20190906JEM_01 | Infrastructure (network-based) | -37.8257 | 144.8575 | 1 | Jemena | Report | 18453 | 0.015712 | 22kV AC | Laverton Raaf | 3025 | Altona North | Dug up
Remaining cable was removed from the pole and coiled within the pit. | 54 Alexandra St, St Kilda East VIC 3183, Australia | 60659729 | Vandalism;Copper theft | [6 empty] | The builder at 54 Alexandra St, St Kilda East advised the low voltage copper cable from Pole LIS-32024 to the pit on the property boundary had been stolen and damaged. The cable was not yet live and not connected to the overhead mains. There was no fire and no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | BC013 | vandalism and copper theft | Damage to network assets | 27/08/2019 15:46 |  |  | 14256 | Roadway |  | 20190906PWA_04 | Infrastructure (network-based) | -37.8651 | 145.0031 | 1 | CitiPower | Report | 17927 | 0.0018738 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | St Kilda East | Other
On arrival crew confirmed isolation of LV and removed vehicle and personel. Repairs to conductor arranged | 21 Saleyards Rd, Kyneton VIC 3444, Australia | 33026964 | Vehicle | [5 empty] | 1 | Report received of wire down and tip truck with tray up and people inside. People told to stay inside vehicle until crew attends. On arrival crew found that tipper had contacted LV conductor, tray was still raised. Low voltage fuses blown and minor damage to the conductor resulted. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WND023 | Tip truck contacted line | Damage to network assets | 43533.4292 |  |  | 14260 | Roadway |  | 20190909PWA_04 | Infrastructure (network-based) | -37.2374 | 144.4616 | 1 | Powercor | Report | 17933 | 0.0015926 | Low voltage AC (<1kV) | Bendigo Airport | 3444 | Kyneton | Vehicle
On arrival supply isolated and defect issued to customer for repair work. | Unnamed Road, Altona Meadows VIC 3028, Australia | 30105371 | Vandalism | [6 empty] | A customer reported their premises has been vandalised and power supply and meter board also damaged at the incident location. Upon arrival, The Powercor crew found that the customer's property had been damaged and the meter board also damaged. There were stolen property but no damage to the service cable. THe LV fuses had been operated by persons unknown. The crew isolated the power supply and a defect notice issued. | Meter board (including fuses);Customer wiring | 2 | 2 | 2 |  | LV003 | Vandalism | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43564.4757 |  |  | 14261 | Public space |  | 20190910PWA_01 | Infrastructure (customer connection) | -37.8984 | 144.7897 | 1 | Powercor | Report | 17937 | 0.0098704 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Other
On arrival crew arranged for repairs to be carried out. | 6 Maleela Ave, Balwyn VIC 3103, Australia | 30173526 | Copper theft | [6 empty] | Customer reported the wire from pole to pit has been stolen. Crew reports the new underground cable between pole and pit has been stolen before it was energized, about 25meters of 16mm2 4 core taken. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | L010 | copper theft | Damage to network assets | 43594 |  |  | 14262 | Roadway |  | 20190910PWA_02 | Infrastructure (network-based) | -37.814 | 145.0721 | 1 | CitiPower | Report | 17939 | 0.0021713 | Low voltage AC (<1kV) | Moorabbin Airport | 3103 | Balwyn | Other
On attendance by fault crew, they deemed the POA to be safe but discovered exposed wiring along the frame of the house. A defect notice was issued and the service fuse removed to isolate supply. | 9 HEATHER STREET, BENTLEIGH EAST VIC 3165 | 2321427 | Caused by contractor | [5 empty] | 2 | UE received a report from the owner of a house that demolishers have begun demolition work without the supply being abolished, creating an unsafe situation. | POA connection (customer side) | 2 | 2 | 2 |  |  | Demolition works progressed without abolishment process. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43594.7562 |  |  | 14267 | Construction |  | 20190911UTD_03 | Infrastructure (customer connection) | -37.92 | 145.058 | 1 | United Energy Distribution | Report | 17945 | 0.015564 | Low voltage AC (<1kV) | Moorabbin Airport | 3165 | Bentleigh East | Other
Repairs organised | 26 QUEENS ROAD, MELBOURNE VIC 3004 | 30213189 |  |  |  | Unknown technical factor |  |  |  | Report of lantern fire at incident location. MFB attended and extinguished pole fire. There was no ground fir, no reported injuries or third party property damage. | Public lighting | 2 | 2 | 2 |  | SK019 | Insufficient remains to determine cause | Pole-top fire | 43807.7688 | 1 | Negligible: no ground fire | 14269 | Roadway |  | 20190912PWA_01 | Infrastructure (network-based) | -37.8416 | 144.9761 | 1 | CitiPower | Report | 17947 | 0.035297 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | AF Other
UE dispatched a fault crew and an EIO to investigate. The EIO undertook testing with Voltages measured between an independent earth and various points of the concrete pole. Inspection of the pole mounted junction box revealed an incorrectly terminated neutral bond. The concrete pole neutral bond conductor was found terminated to the white phase terminal. Â The faults crew proceeded to isolate the service and removed the bonding off the pole. | 23 STATION STREET, BURWOOD VIC 3125 | 7038266 |  |  |  |  | Unknown work practice factor | Phase to earth | 2 | UE received a report of an NBN worker receiving a shock from a live service pole while undertaking works. The NBN worker received an electric shock while he was kneeling next to a concrete service pole when he made simultaneous contact between the pole and the damp nature strip. | Connection box;Pole (concrete) | 2 | 2 | 2 |  |  | The NBN worker received the electric shock due to the â€œstep potentialâ€ between the live pole and the area of the ground that he was kneeling on. The cause of the incorrect connection of the neutral bond to the white phase terminal in the pole junction box is being investigated. | Minor shock | 43747.5312 |  |  | 14270 | Roadway |  | 20190912UTD_01 | Infrastructure (network-based) | -37.8544 | 145.1191 | 1 | United Energy Distribution | Report | 17985 | 0.015097 | Low voltage AC (<1kV) | Moorabbin Airport | 3125 | Burwood | AF Other
ESV notified via their contact centre reference no. 12452069 Site made safe, inspected all affected premises for safety and carried out repairs The construction crews returned in the afternoon and replaced the pole. Following the pole replacement, an Licensed Electrical Inspector returned and re-energised two of the previously inaccessible properties and checked the remaining three properties to confirm if anyone was in attendance. Three properties remain off supply due to no access. | 100 BURKE ROAD N, IVANHOE EAST VIC 3079 | A016990 | Vehicle |  |  | HV injection |  |  | 1 | A car lost control and hit the concrete pole on the nature strip outside #100 Burke Rd. The force of the impact caused the HV open wire conductors to break away from the insulators and fall onto the LV open wire conductors below. This resulted in a high voltage (HV) injection into the LV circuit. All installations on the affected circuit were isolated on the night of the incident. Following the completion of the repairs to the LV conductors, a Licensed Electrical Inspector returned the following morning and began to inspect the accessible installations and re energise the properties and issue damage cards. TechSafe report is attached in the "Notes & Findings" section | Conductor (bare);Aluminium;Pole (concrete) | 0 | 0 | 0 |  | HB24 | Car hit pole causing HV & LV conductors to come down which resulted in a HV injection | HV injection | 14/09/2019 21:10 |  |  | 14273 | Residential |  | 20190915JEM_01 | Infrastructure (network-based) | -37.7714 | 145.0642 | 1 | Jemena | Report | 17984 | 0.0017731 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3079 | Ivanhoe East | Vehicle
Crew isolated supply to the street lights | 836 AITKEN BOULEVARD, CRAIGIEBURN VIC 3064 | A141392 | Copper theft | [5 empty] | 2 | Unknown person has stolen street light copper | Cable | 0 | 0 | 0 |  | COO11 | Unknown person stole copper | Damage to network assets | 17/09/2019 1:00 |  |  | 14280 | Roadway |  | 20190917JEM_01 | Infrastructure (network-based) | -37.6352 | 144.9107 | 1 | Jemena | Report | 18450 | 0.011179 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
On arrival crew made safe and carried out repairs | 11 LITTLE BOUNDARY ROAD, LAVERTON NORTH VIC 3026 | 30319290 | Working too close to underground cables | [6 empty] | A contractor reported an earthing dug up at the incident location. The attending crew found that approximately three to four meters of HV earth at the incident location was dug up. with one earth pin being removed and approximately two meters of 70mm earth being damaged. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | BLT016 | excavator struck earth cable | Damage to network assets | 43717.6354 |  |  | 14282 | Roadway |  | 20190917PWA_02 | Infrastructure (network-based) | -37.8236 | 144.8234 | 1 | Powercor | Report | 17962 | 0.024538 | Earthing cable | Laverton Raaf | 3026 | Laverton North | Dug up
Checked all pits back to damaged street light and recapped exposed de-energised underground mains cables. | 975 Leakes Rd, Rockbank VIC 3335, Australia | 30542088 | Copper theft | [6 empty] | While attending a fault, crew found adjoining street lights had their underground supply mains stolen, traced back to exposed live cable at lis 864771, made safe/capped off exposed cables and left in pit. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43474.2118 |  |  | 14285 | Roadway |  | 20190917PWA_03 | Infrastructure (network-based) | -37.7162 | 144.6553 | 1 | Powercor | Report | 17965 | 0.0047708 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Crews attended, isolated supply and performed repairs. | 255 CHAPEL STREET, PRAHRAN VIC 3181 | 30207716 |  |  |  | Corrosion |  |  |  | Emergency services reported a tramline issue at the incident location, and requested power lines to be checked. On arrival the crew found that a aerial catenary had become dislodged from a building, causing the cables to hang lower and a tram to contact overhead cables. The resulting damage included low voltage CitiPower public lighting cables falling to the ground . The crew reported that the MFB had cordoned off the area of the downed cables when the crew arrived. There was no reported third party damage, and no reported injuries. | Guy wire;Public lighting | 0 | 0 | 0 |  | BC007 | Support assembly attached to building deteriorated | Damage to network assets | 43808.5931 |  |  | 14286 | Commercial |  | 20190917PWA_04 | Infrastructure (network-based) | -37.85 | 144.9937 | 1 | CitiPower | Report | 17966 | 0.019383 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Prahran | AF Other
Fault crew dispatched. Site made safe and pole inspected for damage. Failed dropper replaced to temporarily restore supply. Pole replaced in followup job. | BRUCE AVENUE, SURF BEACH VIC 3922 | LIS2809410 |  |  |  | Defective component |  |  |  | Pole fire reported on transformer pole | Pole (wood);Crossarm (steel);Dropper/bridge | 0 | 0 | 0 |  | BDL41 | Pole fire reported on transformer pole. Pole is a termination pole with a pole mounted transformer installed on the supply side of the pole. HV fuses were installed on the back of the pole with the centre phase connection between the fuse and the over head going over the top of the steel termination arm. Upon investigation, it appears that the centre phase dropper cable failed at the tail, coming to rest on the term arm. The line and substation fuses failed to operate and the dropper/crossarm continued to be back-fed through the transformer resulting in a pole top fire. Fire was contained at the pole top and did not make it to the ground as it was a particularly wet night. | Pole-top fire | 43655.359 | 1 | Negligible: no ground fire | 14290 |  |  | 20190917SPN_07 | Infrastructure (network-based) | -37.5082 | 148.1365 | 1 | AusNet Services Distribution | Report | 17970 | 0.012286 | 12.7kV AC (SWER) | Bairnsdale Airport | 3922 | Surf Beach | OH Cable
Fault crew dispatched. Candled 6k BA HV fuse removed and replaced with new. Supply restored | 1059 MYERS CREEK ROAD, TOOLANGI VIC 3777 | LIS1400989 |  |  |  | Candled fuse |  |  |  | Report of candled fuse | Boric acid | 0 | 0 | 0 |  | WYK24 | 6k BA HV fuse has candled | Pole-top fire | 43778.2743 | 1 | Negligible: no ground fire | 14293 |  |  | 20190918SPN_01 | Infrastructure (network-based) | -37.5635 | 145.5039 | 2 | AusNet Services Distribution | Report | 17973 | 0.011417 | 22kV AC | Wallan (Kilmore Gap) | 3777 | Toolangi | Fuse
Fault crew and LEI dispatched and identified broken neutral connection at LV bushing on transformer. Fault crew replaced the failed neutral connection. Effected premesis isolated and inspected by LEI and tested prior to restoration of supply. LEI issued reports of damage and defect notices for installations requiring an REC. | WARRA STREET, TALLANGATTA VIC 3700 | LIS5218464 |  |  |  | Neutral fault;Defective component |  |  |  | Report of neutral fault effecting multiple premises. | Pole mounted;Transformer | 0 | 1 | 0 |  | WOTS13 | A broken neutral connection at LV bushing on transformer is believed to be the cause of th HVI. The majority of the premises supplied by Warra Queen substation were affected by the failed neutral connection and the affected premises experienced multiple appliances failures. | Less than $50k damage | 29/07/2019 3:17 |  |  | 14295 | Residential |  | 20190918SPN_02 | Infrastructure (network-based) | -36.2132 | 147.1744 | 1 | AusNet Services Distribution | Report | 18050 | 0.037951 | Low voltage AC (<1kV) | Wangaratta Aero | 3700 | Tallangatta | Connection
Fault crew dispatched. O/H conductors isolated and made safe. Tree removed and O/H conductors repaired. | 16 FAIRY DELL ROAD, TECOMA VIC 3160 | LIS1306840 |  | Fallen |  |  |  |  | 1 | Tree has fallen into and brought down HV and LV conductors during strong weather conditions. Refer to the attached site photos (showing site onditions and construction post repairs). | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | HV injection | 43807.5521 |  |  | 14298 |  |  | 20190918SPN_03 | Infrastructure (network-based) | -37.9106 | 145.3417 | 1 | AusNet Services Distribution | Report | 18039 | 0.023477 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Tecoma | Trees
LEI and fault crew dispatched to investigate and make safe. Area cleared around redundant supply pit and missing pit lid replaced. Service crew removed both redundant active and neutral conductors from connector blocks in pit. | 385 BERWICK-CRANBOURNE ROAD, CLYDE NORTH VIC 3978 | 2601769526 |  |  |  | Not built/maintained to design | Not followed |  |  | Contractor reported receiving slight shock from ground near electrical pit While removing temporary construction fence | Services pit (network) | 0 | 0 | 0 |  | CLN13 | Contractor reported receiving slight shock from ground near electrical pit while removing temporary construction fence. He was picking up a concrete base which was located directly over the redundant supply pit when he received a shock. The pit was damaged and was missing the cover. Grass had grown over and obscured the pit and associated cabling. The exposed cable was the original customer under ground supply cable from the previous building which had been demolished some time ago. It is unknown how this cable remained energised after abolishment. | Minor shock | 19/08/2019 11:53 |  |  | 14300 | Residential |  | 20190918SPN_04 | Infrastructure (customer connection) | -38.1136 | 145.328 | 1 | AusNet Services Distribution | Report | 17981 | 0.017223 | Low voltage AC (<1kV) | Moorabbin Airport | 3978 | Clyde North | UG Cable
On arrival crew assessed assets, no damage found | 307 Palmers Rd, Truganina VIC 3029, Australia | 30346196 | Working too close to overhead lines | [5 empty] | 1 | Following a feeder interruption a customer reported an excavator passed under line causing a flashover. On arrival crew found an excavator had contacted the overhead 22kv conductors. Crew reported a spotter was onsite but had failed to observe the conductors overhead. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | LV003 | Excavator struck conductors | Loss of supply;No Go Zone (contact) | 18/09/2019 15:33 |  |  | 14306 | Roadway |  | 20190919PWA_02 | Infrastructure (network-based) | -37.826 | 144.7489 | 1 | Powercor | Report | 17989 | 0.029661 | 22kV AC | Laverton Raaf | 3029 | Truganina | Vehicle
Feeder switched out and repairs conducted | 3 GELLIBRAND CRESCENT, RESERVOIR VIC 3073 | A027736 |  |  |  | Leakage |  |  | 1 | Pole top fire resulting from atmospheric conditions | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | TT11 | Earth leakage | Pole-top fire | 21/01/2020 10:11 | 1 | Negligible: no ground fire | 14920 | Residential |  | 20200121JEM_01 | Infrastructure (network-based) | -37.7032 | 145.0087 | 1 | Jemena | Report | 18848 | 0.037238 | 22kV AC | Essendon Airport | 3073 | Reservoir | Pole
On arrival crew isolated supply and carried out repairs. | 413 Ballarat-Carngham Rd, Bunkers Hill VIC 3352, Australia | 33007578 |  |  |  | Corrosion |  |  |  | Vic Fire reported a grass fire at the incident location, evidently started by Powercor assets On arrival crew found that a porcelain fuse box had overheated igniting grass below. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS011 | Overheated connection | Grassfire | 18/01/2020 14:29 | 1 | Small: 10 - 1000 sq.m | 14916 | Roadway |  | 20200121PWA_02 | Infrastructure (network-based) | -37.5644 | 143.764 | 1 | Powercor | Report | 18842 | 0.00096296 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Bunkers Hill | Connection
Sent crew to make safe, investigate and repair. Fuse was replaced. | 30 Christoffersens Rd, Nerrena VIC 3953, Australia | 2001124 |  | Lightning |  | Candled fuse |  |  | 2 | Candled HV EDO Fuse at pole 2001124. No apparent fire damage to the ground around the pole was observed. Fuse was replaced. Refer to site photos. | EDO fuse | 0 | 0 | 0 |  | LGA14 | Suspected lightning/storm impact. | Pole-top fire | 20/01/2020 8:51 | 1 | Negligible: no ground fire | 14913 | Agricultural |  | 20200121SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18837 | 0.010424 | 22kV AC | Moorabbin Airport | 3953 | Nerrena | Fuse
On arrival crew isolated supply and carried out repairs. | 99 Back Boga Rd, Swan Hill VIC 3585, Australia | 32161148 |  |  |  | Corrosion |  |  |  | Vic fire reported wires down at incident location, caused grass fire. On arrival crew found a FMB had overheated debris ignited grass below. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | SHL005 | Overheated connection | Grassfire | 19/01/2020 17:26 | 1 | Small: 10 - 1000 sq.m | 14923 |  |  | 20200122PWA_01 | Infrastructure (network-based) | -35.3699 | 143.5475 | 1 | Powercor | Report | 18853 | 0.029494 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 26 ELIZABETH ROAD, PORTSEA VIC 3944 | 1307150 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply. | Crossarm (wood) | 0 | 0 | 0 |  | STO13 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.4271 | 1 | Negligible: no ground fire | 14935 | Roadway |  | 20200122UTD_06 | Infrastructure (network-based) | -38.3301 | 144.7137 | 1 | United Energy Distribution | Report | 18865 | 0.037708 | 22kV AC | Avalon Airport | 3944 | Portsea | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. ESV was notified, ref #13116343. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 29 DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806826 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply. | Crossarm (wood) | 0 | 0 | 0 |  | MC9 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.4896 | 1 | Negligible: no ground fire | 14939 | Roadway |  | 20200122UTD_09 | Infrastructure (network-based) | -37.9885 | 145.1005 | 1 | United Energy Distribution | Report | 18869 | 0.040366 | 22kV AC | Moorabbin Airport | 3195 | Mordialloc | Crossarm
Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. ESV was notified, ref #13116345. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 16 NELLBERN ROAD, MOORABBIN VIC 3189 | 1816585 |  |  |  | Leakage |  |  | 1 | UE feeder protection operated and faults crew patrolled the line to investigate and found a pole top fire. | Crossarm (wood) | 0 | 0 | 0 |  | HT8 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.6215 | 1 | Negligible: no ground fire | 14940 | Roadway |  | 20200122UTD_10 | Infrastructure (network-based) | -37.9389 | 145.0667 | 1 | United Energy Distribution | Report | 19221 | 0.022451 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Crossarm
EDO was found to be candling when crew arrived. No evidence of fire in the area. Crew replaced the EDO and inserted and supply restored. | 160 LANES ROAD, NICHOLSON VIC 3882 | 596312 |  |  |  | Candled fuse |  |  |  | Candled HV fuse | EDO fuse | 0 | 0 | 0 |  | BDL41 | Candled fuse. | Pole-top fire | 23/01/2020 8:36 | 1 | Negligible: no ground fire | 14945 | Agricultural |  | 20200123SPN_03 | Infrastructure (network-based) | -37.8167 | 147.7128 | 1 | AusNet Services Distribution | Report | 18878 | 0.02792 | 22kV AC | Bairnsdale Airport | 3882 | Nicholson | Fuse
Faults crew attended the site to investigate. Upon inspection, it was identified that the 3phase fuse mains box on the service pole was burnt. ESV was notified, ref #13241384. The site was isolated and made safe. The FMB was replaced. | 33A BROWNS ROAD, MAIN RIDGE VIC 3928 | 8831401 |  |  |  | Overheated connection |  |  | 1 | UE received a call there was a fire on a power pole. | Disconnector/isolator | 0 | 0 | 0 |  | RBD12 | The cause was melted fuse mains box. | Plant/equipment | 23/01/2020 6:50 | 1 | Negligible: no ground fire | 14948 | Roadway |  | 20200124UTD_01 | Infrastructure (network-based) | -38.3989 | 144.9397 | 1 | United Energy Distribution | Report | 18884 | 0.0068183 | Low voltage AC (<1kV) | Moorabbin Airport | 3928 | Main Ridge | Fuse
Sent fault crew to make safe, investigate and organise repairs. Replaced 6A BA fuse on substation pole. Refer to attached site photos. | 190 HUNTS LANE, STEELS CREEK VIC 3775 | 1006993 |  |  |  | Age;Fuse failed to eject |  |  |  | Report of candled BA HV Fuse. Grass fire observed underneath. Refer to attached site photos. | Boric acid | 0 | 0 | 0 |  | CPK12 | Candled BA fuse due to internal degradation. | Grassfire | 25/01/2020 13:51 | 1 | Medium: 1000 sq.m - 10 ha | 14962 | Agricultural |  | 20200128SPN_03 | Infrastructure (network-based) | -37.5834 | 145.3897 | 1 | AusNet Services Distribution | Report | 18909 | 0.014111 | 22kV AC | Wallan (Kilmore Gap) | 3775 | Steels Creek | Fuse
The demolition workers appeared to have clashed the Optus cable attached to the catenary cable and flicked it up into the HV and LV overhead conductors. When the faults crew arrived on the corner of Ferntree Gully Road and Westerfied Drive, there were no witnesses able to provide cause details. A high voltage injection was suspected and a LEI was dispatched to investigate. The site was made safe and the LV supply isolated with the HV conductors checked for damage. The faults crew unhooked the Optus cable from the LV conductors and there was evidence of conductor clashing and a LEI was dispatched to investigate any damage that may have occurred to customers appliances. The LEI checked occupancies in the vicinity and no damage was sustained with supply restored at 2.50PM. | 452 FERNTREE GULLY ROAD, NOTTING HILL VIC 3168 | 611796 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | 22kV feeder GW 05 circuit breaker successfully reclosed to lockout affecting 1623 customers. Caller named Phil (0434 602 742 resides at 14 Avonhurst Drive) advised the UE faults and emergencies call centre that a demolition company did something at the pole when the power went out and they left straight away. | Conductor (bare) | 0 | 0 | 0 |  | GW 05 | The cause appeared to be demolition workers completing 'high risk construction' activities using earthmoving equipment under or adjacent to powerlines and other assets and clearances not being maintained. | Loss of supply;No Go Zone (contact) | 24/01/2020 12:10 |  |  | 14967 | Roadway |  | 20200129UTD_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | United Energy Distribution | Report | 18903 | 0.021475 | 22kV AC | Moorabbin Airport | 3168 | Notting Hill | Vehicle
Sent crew to make safe, investigate and organise repairs. Electrical inspector inspected the installations nd found no dmage except for faulty meter displays. Fault crew responded and replaced damaged meters and carried out tests. | 417 Main Rd, Montmorency VIC 3094, Australia | 900711 |  | Blown branch/vegetation |  |  |  |  | 2 | Report of fallen tree branch on power lines. HV hit LV conductors cuasing HVI. | Conductor (bare) | 0 | 0 | 0 |  | ELM34 | Vegetation: Trees Incident | HV injection | 43863.7215 |  |  | 14997 |  |  | 20200203SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Report | 18950 | 0.036801 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3094 | Montmorency | Trees
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm from a ground type substation was burnt and broken. ESV was notified, ref #13142340. The site was isolated and made safe. The cross-arm was replaced and supply was restored | 5 POWLETT STREET, MOORABBIN VIC 3189 | 1816317 |  |  |  | Leakage |  |  | 1 | UE received calls from customers advising of no supply and UE feeder circuit breaker operated. | Crossarm (wood) | 0 | 0 | 0 |  | HT13 | The cause of the fire was tracking across the insulator. | Pole-top fire | 44075.184 | 1 | Negligible: no ground fire | 15003 | Commercial |  | 20200203UTD_02 | Infrastructure (network-based) | -37.9472 | 145.0744 | 1 | United Energy Distribution | Report | 18959 | 0.019917 | 22kV AC | Moorabbin Airport | 3189 | Moorabbin | Crossarm
Emergency response and made the site safe. Line restoration is in progress. | 680 BALLAN ROAD, MOORABOOL VIC 3213 | 137 to 143 inclusive | [6 empty] | 1 | Storm Impacting Transmission Lines. Six towers collapsed plus one tower was damaged/unserviceable. | Tower | 0 | 0 | 0 |  | 500kV MLTS-HGTS no.1 & MLTS-MOPS no.2 | severe wind intensity. Under investigations. | Damage to network assets | 31/01/2020 14:24 |  |  | 15004 | Agricultural |  | 20200204SPN_01 | Infrastructure (network-based) | -37.993 | 143.6397 | 1 | AusNet Services Transmission | Notification | 18960 | 0.024615 | 500kV AC | Ballarat Aerodrome | 3213 | Moorabool | AF Other
Crew dispactched to investigate and make safe. Transformer leaking oil and fire observed, No grass fire. Crew found blown transformer after lighting storm. No fire observed on arrival to Transformer or any fire on ground. Damage Transformer removed and replaced. Old transformer transported to yard in Spill tray and site check. No other damage. No other follow up required. | 141 YULUNGAH ROAD, TRAFALGAR VIC 3824 | 2206060 |  | Lightning | [5 empty] | 22kV pole top transformer caught on fire. | Pole mounted | 0 | 1 | 0 |  | MOE22 | Transformer hit by lightning. | Pole-top fire | 24/01/2020 13:00 | 1 | Negligible: no ground fire | 15014 |  |  | 20200204SPN_03 | Infrastructure (network-based) | -38.1748 | 146.1337 | 1 | AusNet Services Distribution | Report | 19688 | 0.029976 | 22kV AC | Morwell (Latrobe Valley Airport) | 3824 | Trafalgar | AF Other
Fault crews attended the site to investigate. Upon inspection, it was identified that the gas switch on the pole had failed as there was smoke coming from it. It is suspected that the switch was damaged by a lightning strike earlier. ESV was notified, ref #13186841. The site was isolated and made safe. The switch was replaced and supply was restored. | 38 EUMERALLA GROVE, MOUNT ELIZA VIC 3930 | 3313495 |  | Lightning |  |  |  |  | 1 | UE received a call that a customer heard a dull explosion nearby the property prior to the outage and UE feeder circuit breaker operated. | Any other type | 0 | 0 | 0 |  | MTN22 | It is suspected that the switch was damaged by a lightning strike earlier. | Plant/equipment | 15/01/2020 23:15 | 1 | Negligible: no ground fire | 15007 | Roadway |  | 20200204UTD_02 | Infrastructure (network-based) | -38.2081 | 145.1011 | 1 | United Energy Distribution | Report | 18963 | 0.031159 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Lightning
Fault crews attended the site to investigate. Upon inspection, it was identified the boric acid fuse failed and burnt the bottom contact off which started a 1m2 ground fire. The site was isolated and made safe. The fuse was replaced and supply was restored. | 307 SANDY POINT ROAD, SOMERS VIC 3927 | 1108966 |  |  |  | Electrical breakdown |  |  | 1 | UE was advised by MFB there was a pole fire at this site. | Boric acid | 0 | 0 | 0 |  | HGS23 | the cause was a failed BA fuse. | Grassfire | 31/01/2020 23:50 | 1 | Localised: less than 10 sq.m | 15011 | Roadway |  | 20200204UTD_04 | Infrastructure (network-based) | -38.3765 | 145.147 | 1 | United Energy Distribution | Report | 18969 | 0.02348 | 22kV AC | Moorabbin Airport | 3927 | Somers | Fuse
Faults crew attended the site to investigate. Upon inspection, it was identified that two wooden HV cross-arms were burnt. There was no evidence of HVI. The site was isolated and made safe. The cross-arms were replaced and supply was restored. | UNIT 1 24 ROOKS ROAD, NUNAWADING VIC 3131 | 7033741 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply and UE feeder protection CB operated. | Crossarm (wood) | 0 | 0 | 0 |  | NW22 | The cause of the fire was tracking across the insulators. | Pole-top fire | 19/01/2020 18:40 | 1 | Negligible: no ground fire | 15017 | Roadway |  | 20200204UTD_06 | Infrastructure (network-based) | -37.8202 | 145.1853 | 1 | United Energy Distribution | Report | 18976 | 0.0036389 | 22kV AC | Moorabbin Airport | 3131 | Nunawading | Crossarm
On arrival crew isolated supply and carried out repairs. | Sunraysia Hwy, Birchip VIC 3483, Australia | 32016825 |  |  |  | Leakage |  |  |  | Vicfire attended to extinguish pole fire at the incident location. On arrival crew found crossarm burnt in half at king bolt position. The railway side conductor was approx. 1m from the ground but was over rail reserve and as such not a threat to the general public. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CTN001 | Excessive leakage current | Pole-top fire | 43832.4722 | 1 | Negligible: no ground fire | 15032 | Public space |  | 20200205PWA_04 | Infrastructure (network-based) | -36.0357 | 142.8997 | 1 | Powercor | Report | 18999 | 0.027022 | 22kV AC | Swan Hill Aerodrome | 3483 | Birchip | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the HV fuse was candling. The site was isolated and made safe. The fuse was replaced and supply was restored. | 69 TRANMERE AVENUE, CARNEGIE VIC 3163 | 2327301 |  |  |  | Candled fuse |  |  | 1 | UE received calls from customer about dim lights and appliances struggling to work. | Powder filled | 0 | 0 | 0 |  | EM10 | The cause was a HV fuse candling. | Plant/equipment | 21/01/2020 6:15 | 1 | Negligible: no ground fire | 15025 | Roadway |  | 20200205UTD_05 | Infrastructure (network-based) | -37.8931 | 145.0606 | 1 | United Energy Distribution | Report | 18988 | 0.023657 | 22kV AC | Moorabbin Airport | 3163 | Carnegie | Fuse
On arrival crew isolated supply and allow CFA to clear vegetation | 365 KOONDROOK-MURRABIT ROAD, KOONDROOK VIC 3580 | 33021888 |  | Fallen | [5 empty] | Customer reported wire down, started small grass fire. at incident location. There was no conductor damage. CFA on site There was a small ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | KGT003 | Vegetation: Trees Incident | Grassfire | 22/01/2020 17:13 | 1 | Localised: less than 10 sq.m | 15038 | Agricultural |  | 20200206PWA_02 | Infrastructure (network-based) | -35.6245 | 144.0914 | 1 | Powercor | Notification | 19008 | 0.011343 | 22kV AC | Swan Hill Aerodrome | 3580 | Koondrook | Trees
Crew on site extinguished fire and made the site safe by isolating and applying earths. | 596 COMBIENBAR ROAD, CLUB TERRACE VIC 3889 | 1905411 | Working too close to overhead lines | [6 empty] | Third party tree clearers while cutting trees dropped tree onto live HV Conductor causing line to come down and caused small ground fire. | Conductor (bare) | 0 | 0 | 0 |  | CNR3 | Vegetation: Trees Incident | Grassfire | 43984.5611 | 1 | Localised: less than 10 sq.m | 15040 |  |  | 20200206SPN_02 | Infrastructure (network-based) | -37.5396 | 148.9362 | 1 | AusNet Services Distribution | Report | 19012 | 0.024249 | 22kV AC | Gabo Island Lighthouse | 3889 | Club Terrace | Trees
Lines were isolated and earthed to make safe for emergency services. Repairs carried out | 10420 PRINCES HIGHWAY, ALLANSFORD VIC 3277 | 32198465 | Vehicle | [6 empty] | Vicfire advised car hit pole, car on fire and pole down. On arrival crew found a 66/22kV pole was hit by a car and had fallen onto the road. Crew did not approach the scene as they were informed 1 of the 2 occupants was deceased. There was no asset or ground fire, | Pole (wood) | 2 | 2 | 2 |  | TRG-WBL1 | Vehicle accident | Not involving electrocution;Damage to network assets | 31/01/2020 22:30 |  |  | 15042 | Roadway |  | 20200207PWA_02 | Infrastructure (network-based) | -38.3885 | 142.568 | 1 | Powercor | Report | 19014 | 0.0012616 | 22kV AC;66kV AC | Warrnambool Airport Ndb | 3277 | Allansford | Vehicle
Damaged asset isolated and repaired, ACR reset and power restored. Farmer advised to be more vigilant in the future. | Mcloughlans Rd, Jeffcott VIC 3480, Australia | 32015477 | Working too close to overhead lines | [6 empty] | Gavin from KP Sait reports truck in paddock has hit main wires, vehicle has moved away but wire hanging low. Crew attended site and report tip truck contacted swer line at incident location. There was no fire, no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | CTN006 | Tipper contacted SWER line | No Go Zone (contact) | 30/01/2020 13:22 |  |  | 15044 | Agricultural |  | 20200207PWA_04 | Infrastructure (network-based) | -36.2752 | 143.1817 | 1 | Powercor | Report | 19016 | 0.010639 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3480 | Jeffcott | Vehicle
Crew made safe and completed repairs. | 10 WANDSWORTH AVENUE, DEER PARK VIC 3023 | 30118460 |  |  |  | Corrosion |  |  |  | Customer reported wire down and grass fire at incident location . MFB attended to control 0.5m x 0.5m grass fire. Attending crew found the fire was caused by a burnt out IPC on East bus fuse white phase hitting the ground after LV main cable broke at connection. No injuries or property damage. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | SU021 | Overheated IPC connector | Grassfire | 30/01/2020 18:37 | 1 | Localised: less than 10 sq.m | 15046 | Roadway |  | 20200207PWA_06 | Infrastructure (network-based) | -37.7644 | 144.768 | 1 | Powercor | Report | 19018 | 0.014185 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Connection
Line isolated by ACR operation. HV Crossarm changed and line restored to normal | 3188 Kulkyne Way, Colignan VIC 3494, Australia | 31020287 |  |  |  | Leakage |  |  |  | HV 22Kv Wooden Crossarm burnt off HV Angle top circuit of HV Angle and Tee Off - small ground fire There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT013 | Excessive leakage current | Pole-top fire;Grassfire | 23/01/2020 13:50 | 1 | Small: 10 - 1000 sq.m | 15050 | Forest - native (not park) |  | 20200207PWA_09 | Infrastructure (network-based) | -34.5174 | 142.3757 | 1 | Powercor | Report | 19022 | 0.035736 | 22kV AC | Mildura Airport | 3188 | Colignan | Crossarm
Excavator clear of the line prior to crew attending. Crossarm straightened and cable re-sagged | 340A AVOCA-BEALIBA ROAD, RATHSCAR WEST VIC 3465 | 33012522 | Working too close to overhead lines | [6 empty] | On farm land 3 tonne excavator digging a trench made contact with MRO008 22Kv Feeder. REFCL on the feeder tripped a number of times before going to lock out. Plant Operator was unaware at the time of the contact . There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | MRO008 | Excavator struck overhead conductors | No Go Zone (contact) | 28/01/2020 14:35 |  |  | 15053 | Agricultural |  | 20200207PWA_12 | Infrastructure (network-based) | -37.0326 | 143.4793 | 1 | Powercor | Report | 19025 | 0.027398 | 22kV AC | Ballarat Aerodrome | 3465 | Rathscar West | Vehicle
On arrival crew isolated HV capacitor | 2267 MURRAY VALLEY HIGHWAY, VINIFERA VIC 3591 | 33069333 | [7 empty] | Customer reported fire on top of pole and sparking wires. at incident location. Upon arrival crew found that the fire had been extinguished by the CFA. There appears to have been a HV capacitor fault, no damage to pole. There was no ground fire, no reported injuries or third party property damage. | Pole mounted | 2 | 1 | 2 |  | SHL002 | to be advised | Pole-top fire | 43923.9007 | 1 | Negligible: no ground fire | 15058 | Roadway |  | 20200210PWA_02 | Infrastructure (network-based) | -35.2079 | 143.4021 | 1 | Powercor | Notification | 19031 | 0.026307 | 22kV AC | Swan Hill Aerodrome | 3591 | Vinifera | AF Other
Crews attended, isolated supply and performed repairs. | 9 PERRIN CIRCUIT, TARNEIT VIC 3029 | 30341527 | Copper theft | [5 empty] | 2 | Customer advised he was working in the area and found exposed UG cables and thought someone may have been trying to steal it. On arrival the crew found that persons unknown had attempted to steal LV UG street light cable, by attaching a strap to the cables at a pit and apparently driving away. The end of the cables were damaged, but no cable was actually stolen. The attempted theft was reported online to the Police. there were no reported injuries or other damage | Cable | 0 | 0 | 0 |  | TNA023 | Attempt to steal LV UG street light cable, | Damage to network assets | 13/12/2019 12:05 |  |  | 15071 | Residential |  | 20200211PWA_06 | Infrastructure (network-based) | -37.8202 | 144.698 | 1 | Powercor | Report | 19049 | 0.020763 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Other
Crew made site safe. Fault follow up listed for contractor to replace cables. | A300, Mount Rowan VIC 3352 | 30554138 | Copper theft | [5 empty] | 2 | Passerby reported cable hanging out of pit at base of public lighting pole at roundabout. A crew attended and found a pit at the base of public lighting pole LIS 877173 had been opens and U/G cables feeding public light LIS 877172 had been cut and removed. | Cable | 0 | 0 | 0 |  | BAN009 | Copper theft | Damage to network assets | 16/12/2019 17:03 |  |  | 15074 | Roadway |  | 20200211PWA_09 | Infrastructure (network-based) | -37.5185 | 143.8448 | 1 | Powercor | Report | 19053 | 0.011709 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Other
On arrival crew isolated supply and carried out repairs. | 207 Belar Ave, Irymple VIC 3498, Australia | 32141632 |  |  |  | Leakage |  |  |  | Vic Fire reported pole fire at above location. When crew arrived they were able to isolate before HV cross arm collapsed. HV cross arm burnt through at king bolt. No injuries or third party damage. No ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | RCT011 | Excessive leakage current | Pole-top fire | 44076.2931 | 1 | Negligible: no ground fire | 15077 |  |  | 20200211PWA_11 | Infrastructure (network-based) | -34.2428 | 142.2015 | 1 | Powercor | Report | 19056 | 0.031859 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
Crew removed hazards, organized repairs and made site safe. | Francis Road Mount Macedon 3441 | 30038247 |  | Fallen |  |  |  |  | 1 | Tree fallen onto HV conductors between P30 and P31 Alton Rd LIS:918425, no ground fire, | Conductor (bare) | 0 | 0 | 0 |  | GSB014 | Vegetation: Trees Incident | Damage to network assets | 22/01/2020 15:08 |  |  | 15089 | Agricultural |  | 20200211PWA_18 | Infrastructure (network-based) | -37.3816 | 144.5828 | 1 | Powercor | Report | 19069 | 0.013248 | 22kV AC | Melbourne Airport | 3441 |  | Trees
Sent Electrical Inspector to make safe, investigate and organise repairs. Crew repaired failed neutral connection and carried out tests to senure safe installation. | 12 WELLSFORD STREET, YACKANDANDAH VIC 3749 | 5201593 |  |  |  | Age |  |  |  | Report of customer receiving a tingle when touching the tap handles. | Aluminium twisted (grey);Service cable (insulated) | 0 | 0 | 0 |  | WOTS11 | Neutral connection failed. Refer to the attached photo of the failed connection. | Minor shock | 43658.3639 |  |  | 15069 | Residential |  | 20200211SPN_04 | Infrastructure (network-based) | -36.3132 | 146.8412 | 1 | AusNet Services Distribution | Report | 19050 | 0.022178 | Low voltage AC (<1kV) | Wangaratta Aero | 3749 | Yackandandah | Connection
crew attended, isolated and made repairs | 1491 OLD LINDSAY ROAD, STRATHDOWNIE VIC 3312 | 32131144 |  | Precipitation;Humidity |  | Leakage |  |  | 1 | Fire brigade advised of a pole fire possibly caused by a ground fire. The attending crew identified that a pole fire had occurred and spread into grassland. An area estimated to be several acres (1.5 Ha) of private pasture was burnt. No damage to fencing of nearby pine plantation. No injuries reported | Pole (wood) | 0 | 0 | 0 |  | HTN002 | pole top fire, from probable leakage, resulted in grass fire | Pole-top fire;Grassfire | 44137.6507 | 1 | Medium: 1000 sq.m - 10 ha | 15091 | Agricultural |  | 20200212PWA_01 | Infrastructure (network-based) | -37.6473 | 141.0233 | 1 | Powercor | Report | 19468 | 0.02562 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3312 | Strathdownie | Pole
Crew removed hazards, organized repairs and made site safe. | 45 ELIZABETH STREET, NATHALIA VIC 3638 | 31026875 |  | Fallen |  |  |  |  | 1 | Customer called to advise tree had fallen on conductor outside his residence. Upon arrival crew found that a tree had fallen across 4-wire bare LV between LIS-1416 and LIS-8622. There was no broken conductor however the LV termination arm at LIS-1416 had broken. | Conductor (bare) | 0 | 0 | 0 |  | NKA002 | Vegetation: Trees Incident | Damage to network assets | 43832.6826 |  |  | 15093 | Residential |  | 20200212PWA_03 | Infrastructure (network-based) | -36.0553 | 145.2041 | 1 | Powercor | Report | 19073 | 0.020902 | Low voltage AC (<1kV) | Shepparton Airport | 3638 | Nathalia | Trees
Crews onsite to isolate the line and issue an EAP to remove the harness from SWER line. | 4 BOWMANS LANE, PENTLAND HILLS VIC 3341 | 4500256 | Misadventure | [5 empty] | 0 | Accidental Contact with HV. | Conductor (bare) | 0 | 0 | 0 |  | MYT12 | A paraglider impacted SWER line. Reports indicate that once the person in the paraglider contacted the mains, they were able to get out of the harness unharmed and just the harness was left touching the mains. | Damage to network assets | 44167.6368 |  |  | 15105 |  |  | 20200212SPN_03 | Infrastructure (network-based) | -36.4467 | 146.6404 | 1 | AusNet Services Distribution | Report | 19087 | 0.010847 | 12.7kV AC (SWER) | Wangaratta Aero | 3341 | Pentland Hills | Other
ATTEND SITE TO MAKE SAFE AND RESTORE SERVICE | 90 LOCH-WONTHAGGI ROAD, LOCH VIC 3945 | 2007693 |  |  |  | Candled fuse |  |  |  | CANDLED FUSE REPORTED | EDO fuse | 0 | 0 | 0 |  | LLG12 | CANDLED FUSE | Pole-top fire | 44167.4014 | 1 | Negligible: no ground fire | 15107 |  |  | 20200212SPN_05 | Infrastructure (network-based) | -38.3763 | 145.7056 | 1 | AusNet Services Distribution | Report | 19091 | 0.0034213 | 22kV AC | Moorabbin Airport | 3945 | Loch | Fuse
Fault crews attended the site to investigate and identified a loose neutral at the POA. The connection was repaired before the customer advised that they had received shocks from the shower tap and outside water tap. LEI attended the site and the NST passed after the repair works. | UNIT 4 9 WOODBINE GROVE, CHELSEA VIC 3196 | 3305983 |  |  |  | Neutral fault |  |  | 1 | UE data analytics identified low volts at the premise. | POA connection (network side) | 0 | 0 | 0 |  | CRM13 | The cause was a loose neutral connection. | Minor shock | 30/12/2019 15:15 |  |  | 15099 | Residential |  | 20200212UTD_02 | Infrastructure (network-based) | -38.0545 | 145.1192 | 1 | United Energy Distribution | Report | 19079 | 0.0069132 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Connection
Crews attended, isolated the supply and arranged to have repairs carried out. | 17 CALDER ALTERNATIVE HIGHWAY, RAVENSWOOD VIC 3453 | 30337207 | Copper theft | [5 empty] | 2 | A member of the public reported pit lids removed and exposed cables at the incident location. On arrival the crew found that unknown persons had opened several underground pits, and stolen approx. 250m of 35mm2 underground cable. There were no reported injuries or fires, and the matter was reported to the Police. | Services cable | 2 | 2 | 2 |  | CMN003 | Copper Theft | Damage to network assets | 43953.3667 |  |  | 15108 | Roadway |  | 20200213PWA_01 | Infrastructure (network-based) | -36.8818 | 144.2092 | 1 | Powercor | Report | 19092 | 0.0034873 | Low voltage AC (<1kV) | Bendigo Airport | 3453 | Ravenswood | Other
Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified corroded connections at the neutral IPC in the supply pit. The attending LEI conducted voltage tests and NST at the installation main switchboard and at the neighbouring property which recorded 25V on the earthing system and a failed NST test. The attending LEI and linesmen uncovered the pit and disconnected the neutral IPC. An NST test was conducted on the incoming neutral which recorded a pass result. The linesmen replaced the IPC and re-terminated all the neutral conductors. An NST test passed at both installations and voltage tests recorded less than 0.5 volts on the earthing system. The LEI conducted voltage tests at the air conditioner and recorded less than 0.5 volts on the metallic outer casing. | 78 AXMINSTER DRIVE, CRAIGIEBURN VIC 3064 | A132228 |  |  |  | Corrosion |  |  | 2 | Darian was in the process of installing a new air conditioner when he received an electric shock when his hand made contact with the earthed condenser unit while he was kneeling on his knees on the bare ground. | Services pit (network) | 2 | 2 | 2 |  | ST32 | Corroded IPC clamp in pit | Minor shock | 13/02/2020 19:34 |  |  | 15118 | Residential |  | 20200214JEM_01 | Infrastructure (network-based) | -37.6027 | 144.9226 | 1 | Jemena | Report | 19104 | 0.024509 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | AF Other
Crew made site safe and reconnected cables in each pit affected. | 370 BRIDGE ROAD, COBBLEBANK VIC 3338 | 30305879 | Copper theft | [5 empty] | 2 | On arrival the Powercor Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen service cables. | Cable | 0 | 0 | 0 |  | MLN021 | Copper theft | Damage to network assets | 29/12/2019 10:36 |  |  | 15120 | Roadway |  | 20200214PWA_04 | Infrastructure (network-based) | -37.7165 | 144.5998 | 1 | Powercor | Report | 19106 | 0.00025463 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Cobblebank | Other
Crew made site safe and reconnected cables in each pit affected. | 687 HIGH STREET, MELTON WEST VIC 3337 | 30298014 | Copper theft | [5 empty] | 2 | On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up the LV Service Pit and and stolen LV Service Cables within. | Cable | 0 | 0 | 0 |  | MLN022 | Copper theft from Service Pits | Damage to network assets | 31/12/2019 15:22 |  |  | 15122 | Roadway |  | 20200214PWA_06 | Infrastructure (network-based) | -37.6857 | 144.5487 | 1 | Powercor | Report | 19108 | 0.023572 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
The crew isolated supply to the area, replaced the damaged transformer and fuse unit. | 218 Yarram Gap Rd, Willaura VIC 3379, Australia | 32098473 |  | Lightning | [5 empty] | A crew was responding to an area fault following a lightning storm. A member of the public stopped the crew and reported a burning fuse tube at the above location. On arrival the crew found that the transformer had been struck by lightning and the EDO fuse tube had hung up and was candling. There was no ground fire or third party damage. | EDO fuse;Transformer | 2 | 2 | 2 |  | ART033 | Lightning strike | Pole-top fire | 14/02/2020 16:18 | 1 | Negligible: no ground fire | 15129 | Roadway |  | 20200217PWA_03 | Infrastructure (network-based) | -37.5279 | 142.7171 | 1 | Powercor | Report | 19116 | 0.019532 | 22kV AC | Hamilton Airport | 3379 | Willaura | Lightning
Crew attended and replaced service | 59 EGGLESTON STREET, OCEAN GROVE VIC 3226 | 32072017 |  |  |  | Corrosion |  |  |  | Plumber was repairing the shed spouting at the property and reported receiving an electric shock to the owner Leonie Saundry. The owner of the property contacted an REC to investigate, wherein the REC installed an Equipotential Bond from the installation Main Earthing system to the metallic Shed Spouting. further investigation found a corroded connection | Service cable (insulated) | 0 | 0 | 0 |  | DDL011 | Corroded connection | Minor shock | 18/10/2019 12:30 |  |  | 15142 | Residential |  | 20200217PWA_11 | Infrastructure (network-based) | -38.2623 | 144.5271 | 1 | Powercor | Report | 19133 | 0.0021817 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a a corroded Neutral Screen Conductor of an O/H Neutral Screened Service Cable, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Single Phase Neutral Screened Service Cable and completed an NST Test which confirmed a Pass result. The installation was left ON supply. | 44 STAMFORD STREET, WENDOUREE VIC 3355 | 32010859 |  |  |  | Corrosion |  | Phase to earth |  | Mrs Erin Crawford was in the Bathroom having a Bath when she received an electric shock as she made simultaneous contact with her hand on the Hot Water Tap and her bare feet on the metallic waste water outlet and water in the Bath. | Service cable (insulated) | 2 | 2 | 2 |  | BAN006 | corroded Neutral Screen Conductor of an O/H Neutral Screened Service Cable | Minor shock | 27/09/2019 23:00 |  |  | 15150 | Roadway |  | 20200218PWA_01 | Infrastructure (customer connection) | -37.5287 | 143.8268 | 1 | Powercor | Report | 19145 | 0.039878 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | OH Cable
Testing using an independent earth to the customers earthing system showed 4 to 6V. CTA and Truck worked to identify the cause as a corroded neutral connection/bar in the Powercor pillar. Truck replaced the neutral bar and remade the connections. Testing carried out after repairs using an independent earth to various points of the installation including the reported point of contact showed <0.5V and NST test passed at MSB. Faults crew replaced the neutral bar in the Powercor pillar and customer was left on supply. | UNIT 2 8 YALONGA AVENUE, WERRIBEE VIC 3030 | 60071438 |  |  |  | Corrosion |  | Phase to earth |  | Adam reports feeling a tingle when using his shower taps. He also reports intermittent dimming lights for some time. | LV Pillar | 2 | 2 | 2 |  | WBE024 | Corroded connection | Minor shock | 19/09/2019 8:00 |  |  | 15155 | Roadway |  | 20200218PWA_03 | Infrastructure (customer connection) | -37.9104 | 144.675 | 1 | Powercor | Report | 19150 | 0.012458 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
CFA reported the fire and attended the fire and extinguished it. Crew replaced EDO fuse carrier | WINTOC, 5269 GLENELG HIGHWAY, GLENTHOMPSON VIC 3293 | 33055592 |  |  |  | Fuse failed to eject |  |  |  | An EDO HV Fuse hung up and a ground fire was found at the base of the pole type substation. | EDO fuse | 0 | 0 | 0 |  | HTN005 | Fuse malfunction | Grassfire | 18/02/2020 6:10 | 1 | Small: 10 - 1000 sq.m | 15165 | Agricultural |  | 20200220PWA_01 | Infrastructure (network-based) | -37.6356 | 142.5118 | 1 | Powercor | Notification | 19166 | 0.013411 | 22kV AC | Hamilton Airport | 3293 | Glenthompson | Fuse
MFB have extinguished fire and Jemena fault crew have made site safe and replaced candled HV fuse. Six customers off supply for duration of works. All restored back to normal. No assets damaged. | 115-131 NAPIER STREET, DIGGERS REST VIC 3427 | A054571 |  |  |  | Candled fuse |  |  | 1 | Centre phase Boric Acid HV fuse candling caused small grass fire (roughly 10sqm) outside 115 Napier St, Diggers Rest. | Boric acid | 0 | 0 | 0 |  | SBY13 | HV fuse candling | Grassfire | 23/02/2020 11:30 | 1 | Localised: less than 10 sq.m | 15172 | Peri-urban |  | 20200223JEM_01 | Infrastructure (network-based) | -37.5683 | 144.6707 | 1 | Jemena | Report | 19179 | 0.022204 | 22kV AC | Melbourne Airport | 3427 | Diggers Rest | Fuse
Site made safe and LV isolator replaced | UNIT 4 12 CHICAGO STREET, MARIBYRNONG VIC 3032 | A029617 |  |  |  | Electrical breakdown |  |  | 2 | Transformer LV isolator (Krone switch) caught fire and melted The voltage of line in which fire start occured is 22kV AC | Disconnector/isolator | 0 | 0 | 0 |  | YVE22 | Electrical failure / deterioration | Other electricity related | 43715.3889 | 1 | Negligible: no ground fire | 15183 | Residential |  | 20200224JEM_01 | Infrastructure (network-based) | -37.7654 | 144.8888 | 1 | Jemena | Report | 19206 | 0.0091215 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3032 | Maribyrnong | AF Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Reticulation Pole, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the existing O/H Neutral Screened Service Cable and completed an NST test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 1024 GREGORY STREET, LAKE WENDOUREE VIC 3350 | 30014183 |  |  |  | Corrosion |  | Phase to earth |  | Ms Kate Jackway was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the Shower Taps and her bare feet whilst standing on the wet shower base and waste water outlet. | Service cable (insulated) | 2 | 2 | 2 |  | BAN005 | Neutral service connection at pole | Minor shock | 14/09/2019 22:30 |  |  | 15174 | Roadway |  | 20200224PWA_02 | Infrastructure (customer connection) | -37.5435 | 143.8447 | 1 | Powercor | Report | 19181 | 0.030234 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Lake Wendouree | Connection
Damaged equipment Gillies Jade switching cabinet has been isolated pending repairs. Overhead conductor corner Honour Ave and Greens Rd has been repaired made safe. | 4 Gillies St, Wyndham Vale VIC 3024, Australia | 30234508 | Vehicle | [6 empty] | Customer reports seeing sparking and flashing coming from wires located opposite his home address. Crew advise high voltage switching cabinet has been damaged by a Holden commodore registration 1EF-8IM, which has collided with the cabinet causing major damage to the cabinet which needs to be replaced. The WBE023 CB operated as designed to remove the damaged equipment at 02:52hours. (5414 customers lost supply). Secondary fault caused conductor to fail at the corner of Honour Ave and Greens Rd. Can be touched from ground level and possible danger to the public. Car believed to have been stolen, driver of vehicle decamped the scene. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Pad mounted equipment/kiosk | 2 | 2 | 2 |  | WBE023 | Vehicle struck cabinet | Loss of supply;Damage to network assets | 31/12/2019 2:52 |  |  | 15177 | Public space |  | 20200224PWA_05 | Infrastructure (network-based) | -37.8904 | 144.6131 | 1 | Powercor | Report | 19184 | 0.028581 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
candled fuse found on substation. Transformer appeared to be ok and crew replaced the fuse re energized and made the site safe. | 4991 MAROONDAH HIGHWAY, ALEXANDRA VIC 3714 | 4714153 |  |  |  | Age;Candled fuse |  |  |  | Report of candling HV EDO fuse at substation. Transformer appeared to be ok and crew replaced the fuse. | EDO fuse | 0 | 0 | 0 |  | RUBA12 | Plausible cuse is age. | Pole-top fire | 23/02/2020 12:24 | 1 | Negligible: no ground fire | 15184 | Roadway |  | 20200224SPN_02 | Infrastructure (network-based) | -37.1922 | 145.6955 | 1 | AusNet Services Distribution | Report | 19193 | 0.0053993 | 22kV AC | Mangalore Airport | 3714 | Alexandra | Fuse
Insulator replaced | 3 Norman St, Ballarat North VIC 3350, Australia | 33006984 |  | Animal | [5 empty] | VICFIRE reported a ground fire start at the at the incident location. A crew attended and found a possum had flashed over at Norman Mathoura P19. The possum fell to the ground and started a grass fire on the road side of approx. 250m2 ( 25mx10m ). CFA was in attendance and extinguished fire. There was no injuries or third party property damage. | Insulators | 2 | 2 | 2 |  | BAN015 | Animal Incident | Grassfire | 23/02/2020 23:55 | 1 | Small: 10 - 1000 sq.m | 15187 | Roadway |  | 20200225PWA_01 | Infrastructure (network-based) | -37.5389 | 143.8804 | 1 | Powercor | Report | 19196 | 0.010933 | 22kV AC | Ballarat Aerodrome | 3350 | Ballarat North | Animal
made site safe. Investigation and reporting to ESV . | 30 TRARALGON WEST ROAD, TRARALGON VIC 3844 | 2606601 |  |  |  |  | Ineffective planning/procedures/processes |  |  | Electric Shock. REC received an electric shock because he believed the ug was abolished | Cable | 0 | 0 | 0 |  | TGN11 | REC received an electric shock because he believed the ug was abolished and not disconnected. On 9th of May 2019 â€“ Retailer requested degeneration of this premise â€“ (request is at recipient discretion) which allows the DB to choose the mode of disconnection â€“DB preferred practice is to disconnect remotely at the Meter. Given the request was degeneration not an abolishment NMI Number 63054238936. See Notes in tab7 | Minor shock | 25/02/2020 14:10 |  |  | 15194 |  |  | 20200225SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19454 | 0.041581 | Low voltage AC (<1kV) | Moorabbin Airport | 3844 | Traralgon | Other
On arrival crew isolated supply and carried out repairs. | Unnamed Road, Fernihurst VIC 3518, Australia | 31002708 |  |  |  | Leakage |  |  |  | Customer reported wires low enough to touch. On arrival crew found a crossarm had burnt in half. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CTN002 | Excessive leakage current | Pole-top fire | 43983.4743 | 1 | Negligible: no ground fire | 15219 | Agricultural |  | 20200228PWA_02 | Infrastructure (network-based) | -36.2258 | 143.8518 | 1 | Powercor | Report | 19248 | 0.019723 | 22kV AC | Bendigo Airport | 3518 | Fernihurst | Crossarm
The attending LEI requested a Powercor Fault Crew to investigate further. The faults crew were able to identify and rectify the high impedance neutral connection at the sub pole. | 186 MURRAY VALLEY HIGHWAY, LAKE BOGA VIC 3584 | 33067867 |  |  |  | Neutral fault |  |  |  | Person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the shower tap and her bare feet while standing on the wet shower base. | Cable | 0 | 0 | 0 |  | KGT004 | Connection malfunction on underground service on pole | Minor shock | 28/10/2019 9:00 |  |  | 15236 | Residential |  | 20200302PWA_04 | Infrastructure (network-based) | -35.4661 | 143.6394 | 1 | Powercor | Report | 19274 | 0.013836 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3584 | Lake Boga | Connection
Crew replaced panel mounted fuse mount | 178-198 PAYNES ROAD, THORNHILL PARK VIC 3335 | 32169125 |  |  |  | Overheated connection |  |  |  | Initially Powercor received a fault for a part supply failure. In the process of undertaking repairs Pasteur Manase Toumoua reports receiving an electric shock to the service truck when he touched the meter panel fuse. | Meter board (including fuses) | 0 | 0 | 0 |  | MLN021 | Meter panel fuse mount had melted allowing contact | Minor shock | 43719.6667 |  |  | 15239 | Other | Church | 20200302PWA_07 | Infrastructure (customer connection) | -37.719 | 144.6361 | 1 | Powercor | Report | 19278 | 0.039778 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Thornhill Park | AF Other
Crew remade all connections | 4 WESTMORE STREET, WARRNAMBOOL VIC 3280 |  |  |  |  | Corrosion;Neutral fault |  |  |  | Person was in the Lounge room and advised he felt a sensation that he described as a minor electric shock as he was attempting to withdraw a Plug Top from a Portable Four Way Power Board which was located on the floor. Further discussions indicated dimming lights | Service cable (insulated) | 0 | 0 | 0 |  |  | Corroded O/H Service Neutral Conductor termination at the Customers FOLCB | Minor shock | 43688.7917 |  |  | 15245 | Residential |  | 20200303PWA_03 | Infrastructure (customer connection) | -38.3723 | 142.4666 | 1 | Powercor | Report | 19284 | 0.032802 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Crew broke, cleaned and remade all connections | 51 CATHERINE STREET, GEELONG WEST VIC 3218 | 32080940 |  |  |  | Corrosion |  |  |  | Plumber experienced what he believed to be an electric shock or sensation when he made simultaneous contact with his hands between the water pipe supplying the Evaporative Cooling unit and the metal Colour Bond roof. | Service cable (insulated) | 0 | 0 | 0 |  | GL022 | Corroded O/H Service Neutral Conductor termination at the Reticulation Pole. | Minor shock | 22/11/2019 10:00 |  |  | 15252 | Residential |  | 20200303PWA_09 | Infrastructure (network-based) | -38.138 | 144.3381 | 1 | Powercor | Report | 19292 | 0.0025405 | Low voltage AC (<1kV) | Avalon Airport | 3218 | Geelong West | Connection
On arrival crew isolated supply and carried out repairs | 251 GEORGE STREET, FITZROY VIC 3065 | 30169680 |  | Blown branch/vegetation | [5 empty] | Report received of conductor down across multiple vehicles. On arrival crew reported the LV neutral conductor had broken due to a tree branch contact during high winds. There was no fire, no reported injuries or third party property damage. There was no people in the cars and no owners present. | Conductor (bare) | 2 | 2 | 2 |  | B021 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 25/02/2020 17:48 |  |  | 15258 | Roadway |  | 20200304PWA_02 | Infrastructure (network-based) | -37.8015 | 144.9815 | 1 | CitiPower | Report | 19302 | 0.02014 | Low voltage AC (<1kV) | Essendon Airport | 3065 | Fitzroy | Trees
Faults crew attended the site to investigate. Upon inspection, it was identified that a tree branch had fallen onto the HV and LV conductors. LEI attended the site and confirmed evidence of HVI. The site was isolated and made safe. The conductors were repaired and supply was restored. | LYNDALE SECONDARY COLLEGE, 170-174 GLADSTONE ROAD, DANDENONG NORTH VIC 3175 | 619701 |  | Fallen |  |  |  |  | 1 | UE received a call that tree branch has fallen onto the power lines and is located outside a school. UE protection on the 22kV feeder operated. | Conductor (bare) | 0 | 0 | 0 |  | LD4 | Vegetation: Trees Incident | HV injection;Other vegetation | 17/01/2020 20:05 | 1 | Negligible: no ground fire | 15260 | Roadway |  | 20200304UTD_02 | Infrastructure (network-based) | -37.9578 | 145.2069 | 1 | United Energy Distribution | Report | 19304 | 0.00019907 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3175 | Dandenong North | Trees
Faults crew attended the site to investigate. Upon inspection, it was identified that a glass disc insulator failed and the pole was burnt. ESV was notified, ref #13435748. The site was isolated and made safe. The insulator was replaced. | 72 GRANGE ROAD, CARNEGIE VIC 3163 | 2328360 |  |  |  | Leakage |  |  | 1 | UE received calls that a power pole was on fire and MFB were on site. | Crossarm (wood) | 0 | 0 | 0 |  | CFD26 | The cause of the fire was tracking across the insulator | Pole-top fire | 19/02/2020 7:20 | 1 | Negligible: no ground fire | 15264 | Roadway |  | 20200304UTD_05 | Infrastructure (network-based) | -37.8861 | 145.047 | 1 | United Energy Distribution | Report | 19308 | 0.026527 | 11kV AC | Moorabbin Airport | 3163 | Carnegie | AF Other
Assisted emergency services rescue with immediate outage, after rescue, that fault crew removed the branch from conductors | 23 MADDEN STREET, BALWYN NORTH VIC 3104 | 30192168 | [6 empty] | 2 | Vic Fire has advised that an arborist stuck in tree. Trees on powerlines, also ladder affected, so unable to get arborist down. Crew attended and assisted in rescue. | Conductor (bare) | 0 | 0 | 0 |  | WD013 | Vegetation: Trees Incident | Minor shock (unconfirmed);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43924.4611 |  |  | 15272 | Roadway |  | 20200305PWA_05 | Infrastructure (network-based) | -37.7972 | 145.0891 | 1 | CitiPower | Notification | 19317 | 0.023758 | 11kV AC | Moorabbin Airport | 3104 | Balwyn North | Trees
The crew has disconnected, removed and made safe the existing 3 phase overhead supply line. The REC has been directed to the portal to make an application for an underground pit supply. | 3 BANCELL STREET, CAMPBELLFIELD VIC 3061 | A037620 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the address today for an 11.00am 3 phase supply and metering alteration request for Overhead-Underground conversion. When the crew arrived they found a 3 phase grey twisted supply line connected to a private pole with the customer mains completely disconnected and removed as well as the existing 3 phase distributors legacy meter. The REC had also installed new 3 phase mains underground mains up the private pole to the existing FOLCB and also installed a new switchboard metering enclosure. When the REC was asked who disconnected and removed the supply, assets and distributors metering he simply replied "it has been off for 15 years" The REC's Electrical Works Request (EWR) also requests an underground supply and pit has been installed. | Aluminium;Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | BD15 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43954.5465 |  |  | 15280 | Residential |  | 20200310JEM_01 | Infrastructure (network-based) | -37.6839 | 144.9637 | 1 | Jemena | Report | 19333 | 0.0026736 | Low voltage AC (<1kV) | Essendon Airport | 3061 | Campbellfield | Other
ON arrival crew isolated supply and carried out repairs. | 55 Hardwicke St, North Melbourne VIC 3051, Australia | 30211720 |  | Blown branch/vegetation | [5 empty] | A member of the public called the CitiPower report room to advise a fallen tree had bought down overhead conductors to ground. Upon arrival the CitiPower faults crew found a council tree had bought down LV overhead conductors onto a car. There was no fire , no reported shocks, no injuries. | Conductor (bare) | 2 | 2 | 2 |  | LS006 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43954.8056 |  |  | 15279 | Roadway |  | 20200310PWA_01 | Infrastructure (network-based) | -37.7971 | 144.9471 | 1 | CitiPower | Report | 19332 | 0.034213 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Trees
Crews isolated damaged area and commenced conductor repairs | 127 HIGH STREET, INVERLEIGH VIC 3321 | 30052957 | [7 empty] | Following a fdr trip to lockout Powercor crews patrolled the line and found a large cypress tree branch had fallen across the HV conductors at the incident location. The tree is located on the road reserve. No fire, injury or third party property damage was reported | Conductor (bare) | 2 | 2 | 2 |  | WIN013 | Vegetation: Trees Incident | Damage to network assets | 44046.1083 |  |  | 15283 |  |  | 20200310PWA_03 | Infrastructure (network-based) | -38.1017 | 144.0481 | 1 | Powercor | Notification | 19338 | 0.034316 | 22kV AC | Avalon Airport | 3321 | Inverleigh | Trees
Sent fault crew to make safe, investigate and orgainse repairs. Customers switchboard was replaced and earthing / bonding completed. AusNet Services OH service was also replaced and load balancing undertaken. Testing and checks completed (neutral+polarity+earth) with recommendation of a follow up by an ENR. | 19 WOODSIDE BEACH ROAD, WOODSIDE VIC 3874 | 2612506 |  |  |  | Out of balance load |  |  |  | Customer got tingles from independent earth at Woodside Beach surf life saving club. Refer to attached photos of the site. | Service cable (insulated);Customer wiring;Customer earthing | 0 | 0 | 0 |  | FTR23 | Initial impedances measured back neutral and earth were 0.3 Ohms indicating a possible parallel Neutral to earth somewhere. | Minor shock | 44046.7063 |  |  | 15287 | Public space |  | 20200310SPN_03 | Infrastructure (customer connection) | -38.5312 | 146.8793 | 1 | AusNet Services Distribution | Report | 19690 | 0.0026794 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3874 | Woodside | AF Other
Fault crews attended the site to investigate. Upon inspection, it was identified that the pole was burnt at the location of the HV tee off cross arm. The site was isolated and made safe. The pole was replaced. | 2549 POINT NEPEAN ROAD, RYE VIC 3941 | 1303874 |  |  |  | Leakage |  |  | 1 | UE was advised by MFB that a power pole was on fire. | Pole (wood) | 0 | 0 | 0 |  | STO23 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43864.2396 | 1 | Negligible: no ground fire | 15286 | Roadway |  | 20200310UTD_01 | Infrastructure (network-based) | -38.3683 | 144.8094 | 1 | United Energy Distribution | Report | 19343 | 0.027111 | 22kV AC | Avalon Airport | 3941 | Rye | AF Other
Jemena fault crew made site safe and organised repairs. | 20A TAMARIN STREET, CRAIGIEBURN VIC 3064 | A090762 | Copper theft | [5 empty] | 2 | Copper theft along Marathon Blvd, between Tamarin St and Taransay Way in Craigieburn. No Customers impacted. Only street lights affected. Cabling at 11 public light poles and 2 underground pits damaged or stolen. | Cable | 0 | 0 | 0 |  | ST11 | Copper theft | Damage to network assets | 44168.5069 |  |  | 15296 | Roadway |  | 20200312JEM_01 | Infrastructure (network-based) | -37.5846 | 144.9036 | 1 | Jemena | Report | 19361 | 0.041034 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Crew isolated the damaged circuit and completed repairs, supply restored. | 605 HOGANS ROAD, TARNEIT VIC 3029 | 31022942 | Working too close to underground cables | [6 empty] | Powercor received advise of an excavator contacting LV underground service cable at the incident location. On arrival the crew advised that an excavator had contacted and damaged an underground service cable. The low voltage fuses at the substation operated. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE012 | Excavator operations | Damage to network assets | 44138.4167 |  |  | 15294 | Roadway |  | 20200312PWA_01 | Infrastructure (network-based) | -37.8593 | 144.6507 | 1 | Powercor | Report | 19359 | 0.031503 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Dug up
On arrival crew isolated supply and carried out repairs. | 221 KEMPS BRIDGE ROAD, GUILDFORD VIC 3451 | 30038431 |  | Within clearances | [5 empty] | A farmer reported a tree took down mains wires at the incident location. On arrival the crew found that the farmer was cutting a tree approx. 15m from the HV Line, when it fell onto the 22kV 3 phase HV conductors. HV conductor broke and fell to the ground causing a small grassfire approx. 10m2 in size. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CMN001 | Vegetation: Trees Incident | Grassfire | 44168.4167 | 1 | Small: 10 - 1000 sq.m | 15300 | Agricultural |  | 20200313PWA_03 | Infrastructure (network-based) | -37.144 | 144.1886 | 1 | Powercor | Report | 19366 | 0.0084699 | 22kV AC | Bendigo Airport | 3451 | Guildford | Trees
REC: reports 60-70 Vts to spouting and approx. 110vts on Razor Bracket at POA. Clear access. Made save by clearing area. | 2 TURNER STREET, NORTH WONTHAGGI VIC 3995 | 2801416 |  |  |  | Unidentified customer fault |  |  |  | high volts on customer installation side | POA connection (customer side) | 0 | 0 | 0 |  | wgi33 | possible out of balance on s/s | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 19/02/2020 10:39 |  |  | 15305 |  |  | 20200316SPN_02 | Infrastructure (customer connection) | -38.596 | 145.5992 | 1 | AusNet Services Distribution | Report | 19374 | 0.035113 | Low voltage AC (<1kV) | Moorabbin Airport | 3995 | North Wonthaggi | AF Other
On arrival crew isolated supply and carried out repairs to underground service cabel. LEI attended and issued a defect notice. | 12 PIONEER DRIVE, DEER PARK VIC 3023 |  | Illegal wiring | [6 empty] | Vic fire requested attendance at house fire. On arrival crew found illegal wiring and tampering with service in pit connections and customers installation.. There was evidence of burning and overheating to service connections and customers wiring. There was no ground fir or reported injuries. | Services cable;Customer wiring | 2 | 2 | 2 |  | SU023 | Illegal tampering of supply | Other electricity related | 14/03/2020 10:34 | 0 | Negligible: no ground fire | 15310 | Residential |  | 20200317PWA_01 | Infrastructure (customer connection) | -37.7806 | 144.7583 | 1 | Powercor | Report | 19380 | 0.039973 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Deer Park | Other
MADE SAFE | 74 SHANLEY STREET, WANGARATTA VIC 3677 | 5103634 | [7 empty] | FIRE IN VECINITY OF APPARATUS | Yet to be determined | 2 | 2 | 2 |  | WN4 | UNDER INVESTIGATION | Pole-top fire | 44107.3993 | 1 | Negligible: no ground fire | 15317 |  |  | 20200318SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19387 | 0.016819 | 22kV AC | Moorabbin Airport | 3677 | Wangaratta | Other
Connection repaired | 225 ESTATE LANE, SMEATON VIC 3364 | 32003566 |  |  |  | Neutral fault |  |  |  | Person was using a petrol driven brush cutter along the fence line in the rear paddock and bent over to move an object on the ground and received an electric shock when his head made contact with the metallic energised electric fence. | Service cable (insulated) | 0 | 0 | 0 |  | BAN009 | Electric fence and neutral connection malfunction | Minor shock | 16/11/2019 12:00 |  |  | 15321 | Residential |  | 20200319PWA_02 | Infrastructure (network-based) | -37.3081 | 143.9779 | 1 | Powercor | Report | 19394 | 0.014832 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3364 | Smeaton | Connection
Crew re-terminated the existing O/H Service Cable | UNIT 2 2 ROTHERWOOD STREET, WENDOUREE VIC 3355 | 32011376 |  |  |  | Corrosion |  |  |  | Person was in the Bathroom showering when he received an electric shock as he made simultaneous contact between his hand on the Shower Rose and his bare feet while standing on the wet shower base and waste water outlet. | Service cable (insulated) | 0 | 0 | 0 |  | BAN001 | Corroded connection | Minor shock | 43567.4583 |  |  | 15326 | Residential |  | 20200319PWA_07 | Infrastructure (network-based) | -37.5252 | 143.8332 | 1 | Powercor | Report | 19400 | 0.038295 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | Connection
Crew have isolated the affected low voltage circuit and an underground faults crew will attend to repair the damage cable and conduit. | 269 HALLETTS WAY, DARLEY VIC 3340 | 30331619 | Working too close to underground cables | [6 empty] | Contractor advised LV conduit in trench has been cut with saw not sure of damage. Crew advise contractor installing an underground supply has cut the wrong conduit causing damage to the cable inside it which was alive at low voltage. No injury or fire. | Cable | 2 | 2 | 2 |  | BMH005 | incorrect Identification of conduit | No Go Zone (contact) | 44138.5764 |  |  | 15328 | Roadway |  | 20200319PWA_09 | Infrastructure (network-based) | -37.6489 | 144.4299 | 1 | Powercor | Report | 19402 | 0.0067326 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Darley | Dug up
Service replaced | 95 BELFORD ROAD, KEW EAST VIC 3102 | 30179243 |  |  |  | Corrosion |  |  |  | As part of the meter insights program this property was identified as having a possible neutral integrity issue and was remotely disconnected for safety. In the courtesy phone call to the customer they mentioned they had received a shock from their oven in the previous week. | Service cable (insulated) | 0 | 0 | 0 |  | Q014 | Corroded/broken neutral in N/S service at customers POA | Minor shock | 23/12/2019 9:00 |  |  | 15330 | Residential |  | 20200319PWA_11 | Infrastructure (network-based) | -37.7938 | 145.0479 | 1 | CitiPower | Report | 19404 | 0.006169 | Low voltage AC (<1kV) | Essendon Airport | 3102 | Kew East | OH Cable
Crew attended and repaired conductor | 470 WESTS ROAD, WERRIBEE VIC 3030 | 33071639 | Working too close to overhead lines | [5 empty] | 1 | A Powercor fault crew attending a fault on WBE023 feeder found that the feeder HV overhead conductors contacted by an excavator at Werribee tip yard at the incident location. The conductor damaged and fell on to the ground. There was a small grass fire about one Sqm but no injures reported. The excavator works for the tip yard but no more details available. The crew made the place safe and all repairs have been completed. The protection operated. | Conductor (bare) | 0 | 0 | 0 |  | WBE023 | unconfirmed contact by mobile plant at site | Grassfire | 18/03/2020 15:39 | 1 | Localised: less than 10 sq.m | 15339 | Other | Refuse management facility | 20200320PWA_02 | Infrastructure (network-based) | -37.9381 | 144.5921 | 1 | Powercor | Notification | 19421 | 0.034472 | 22kV AC | Avalon Airport | 3030 | Werribee | Vehicle
ON arrival crew isolated line , pole straightened and supply restored | CRAIGWOOD, 1944 WINGEEL ROAD, BARUNAH PARK VIC 3329 | 32071929 | Working too close to overhead lines | [6 empty] | Customer reported their tipper truck had caught the SWER line and brought it down low. On arrival the crew found the conductor was still caught on the truck after tipper was lowered about 2m off the ground and a pole was leaning over because of this. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | GL012 | Tipper contacted line | No Go Zone (contact) | 19/03/2020 20:27 |  |  | 15351 | Agricultural |  | 20200323PWA_01 | Infrastructure (network-based) | -38.0052 | 143.8586 | 1 | Powercor | Report | 19436 | 0.040037 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3329 | Barunah Park | Vehicle
Made safe and replaced fuse. No ground fire observed. | 555 GLENGARRY NORTH ROAD, GLENGARRY NORTH VIC 3854 | 2626226 |  |  |  | Candled fuse |  |  |  | Canded 6A EDO fuse. Supply flickering inside house and could see arcing on pole near house. | EDO fuse | 0 | 0 | 0 |  | TGN31 | Candled fuse. | Pole-top fire | 20/02/2020 7:20 | 1 | Negligible: no ground fire | 15350 |  |  | 20200323SPN_01 | Infrastructure (network-based) | -38.0697 | 146.5828 | 1 | AusNet Services Distribution | Report | 19435 | 0.024289 | 22kV AC | Morwell (Latrobe Valley Airport) | 3854 | Glengarry North | Fuse
Fault Crew tightened the Consumers Main Neutral Connection at the Customer's FOLCB at the POA | 20 ETTY STREET, CASTLEMAINE VIC 3450 | 30036531 |  |  |  | Neutral fault |  |  |  | Person was standing in front of the combination Switchboard/Meter Enclosure checking the status of the Circuit Protection Devices following a number of appliances not working, when he received and electric shock as he made simultaneous contact with his lower arm/wrist resting on the metallic Meter Enclosure and his feet whilst standing on the gravel ground. | POA connection (customer side) | 0 | 0 | 0 |  | CMN001 | Loose Consumers Main Neutral Conductor termination at the Customer's FOLCB located at the POA | Minor shock | 43534.2917 |  |  | 15356 | Residential |  | 20200324PWA_02 | Infrastructure (customer connection) | -37.0772 | 144.2082 | 1 | Powercor | Report | 19442 | 0.00022454 | Low voltage AC (<1kV) | Bendigo Airport | 3450 | Castlemaine | Installation
Fault crews attended the site to investigate. Upon inspection, it was identified that the HV connection at the top of the fuse was not latched properly and was burnt. The site was isolated and made safe. The fuse was replaced and supply was restored. | 1 BASS STREET, FLINDERS VIC 3929 | 9864733 |  |  |  | Overheated connection |  |  | 1 | UE received a call from the customer's maintenance contractor, that the overhead connection to the HV fuse was sparking and flaming and caused the customer's equipment to shut down. | Connector/termination | 0 | 0 | 0 |  | DMA23 | the cause was the HV connection was not latched properly. | Pole-top fire | 20/02/2020 10:10 | 1 | Negligible: no ground fire | 15358 | Other | Navy site | 20200324UTD_01 | Infrastructure (network-based) | -38.4774 | 145.0225 | 1 | United Energy Distribution | Report | 19444 | 0.015594 | 22kV AC | Moorabbin Airport | 3929 | Flinders | Connection
Crew arrived on site and made safe, then replaced damaged overhead service line | 1A SLOANE STREET, MARIBYRNONG VIC 3032 | A062698 | Copper theft | [5 empty] | 2 | Unknown person has cut, damaged and attempted to steal overhead service line The photo indicates that a pair of pliers/cutters wielded into the service line | Aluminium;Service cable (insulated) | 2 | 2 | 2 |  | YVE23 | Attempted copper theft | Loss of supply;Damage to network assets | 22/03/2020 19:24 |  |  | 15365 | Commercial |  | 20200325JEM_03 | Infrastructure (network-based) | -37.775 | 144.8851 | 1 | Jemena | Report | 19451 | 0.04 | Low voltage AC (<1kV) | Essendon Airport | 3032 | Maribyrnong | Other
Fault crew dispatched. Supply isolated and candled HV fuse replaced with new. Supply restored. | 459 MEWBURN PARK ROAD, MAFFRA VIC 3860 | LIS2515178 |  |  |  | Candled fuse |  |  |  | report of candled fuse | Boric acid | 0 | 0 | 0 |  | mfa22 | BA HV Fuse has candled. No evidence of ground fire or damage to pole. Candled BA HV fuse replaced with new and supply restored | Pole-top fire | 30/08/2019 18:30 | 1 | Negligible: no ground fire | 14239 | Roadway |  | 20190903SPN_01 | Infrastructure (network-based) | -37.9502 | 146.9518 | 1 | AusNet Services Distribution | Report | 17938 | 0.02488 | 22kV AC | Morwell (Latrobe Valley Airport) | 3860 | Maffra | Fuse
The feeder protection operated to isolate the fault. Fault crews attended and undertook emergency switching to restore supply to customers while isolating the faulty section for repairs. | 257 ERAMOSA ROAD W, MOOROODUC VIC 3933 | 1103528 |  | Fallen |  |  |  |  | 1 | During storm event, a large tree fell onto HV ABC line resulting in the line breaking and falling to the ground. A small fire 10cm sq resulted. | Conductor (ABC) | 0 | 0 | 0 |  | MTN22 | Vegetation: Trees Incident | Grassfire | 43716.4743 | 1 | Localised: less than 10 sq.m | 14241 | Roadway |  | 20190903UTD_01 | Infrastructure (network-based) | -38.2149 | 145.1167 | 1 | United Energy Distribution | Report | 18020 | 0.019492 | 22kV AC | Moorabbin Airport | 3933 | Moorooduc | Trees
Circuit isolated circuit and repairs completed. | 5-7 STRODE STREET, RICHMOND VIC 3121 | 60136412 | Working too close to underground cables | [6 empty] | Contractor installing NBN cables has damaged a low voltage underground mains cable outside the incident address. CitiPower crew advised directional drill installed conduit through a LV Service pit into the low voltage mains causing the low voltage fuses to operate and power lost to the circuit. No fire and no reported injuries due to this incident. | Cable;Services pit (network) | 2 | 2 | 2 |  | NR024 | Directional bore struck cabel | Loss of supply;No Go Zone (contact);Damage to network assets | 29/08/2019 9:00 |  |  | 14257 | Roadway |  | 20190909PWA_01 | Infrastructure (network-based) | -37.8192 | 144.9908 | 1 | CitiPower | Report | 17929 | 0.02217 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Dug up
On arrival crew isolated supply and carried out repairs. | Loddon Plains Rd, Bridgewater North VIC 3516, Australia | 30025529 | Working too close to overhead lines | [6 empty] | Customer reported wire down at incident location. On arrival crew found a n irrigator had contacted the swer conducor. There was no fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | EHK024 | Mobile irrigator operating in pasture paddock | No Go Zone (contact);Damage to network assets | 43717.975 |  |  | 14264 |  |  | 20190911PWA_01 | Infrastructure (network-based) | -36.5192 | 144.0067 | 1 | Powercor | Report | 17941 | 0.011878 | 12.7kV AC (SWER) | Bendigo Airport | 3516 | Bridgewater North | Vehicle
Upon identifying the fault the Jemena fault crew re-terminated the consumer mains and re-made the neutral connection in the service pit and carried out all required VESI tests. Following this the attending LEI carried out voltage tests from an independent earth to various parts of the installation including MEN, switchboard enclosure and brick mortar where the electric shocks had been received, identifying less than 1VAC. An NST test was also carried out at the installation recording a pass result. | 8 SESAME STREET, MICKLEHAM VIC 3064 | A148816 |  |  |  | Neutral fault |  |  | 2 | Person received shock from between mortar and bricks when wet The electric shock was received when Mr Andac Ayvaz was laying bricks at the installation when he simultaneous made contact with the wet mortar and ground. Mr Ayvaz reported only receiving the shock while the mixer was running. Subsequent tests by Jemena fault crew identified a high impedance neutral caused by a bad connection in the service pit. Note: on the arrival of the Licensed Electrical Inspector, that attending fault crew had already repaired the connection at the service pit. TechSafe report attached in the "Notes & Findings" section | Services pit (network) | 0 | 0 | 0 |  | COO11 | Bad neutral connection in pit | Minor shock | 43808.4514 |  |  | 14268 | Residential |  | 20190912JEM_01 | Infrastructure (network-based) | -37.5456 | 144.8905 | 1 | Jemena | Report | 17946 | 0.041622 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Mickleham | Connection
Site made safe Investigation conducted by Jemena works practices | 30 Village Cl, Westmeadows VIC 3049, Australia | A058465 | Building too close or within the No Go Zone | [5 empty] | 2 | â€¢ Crew found that developer/builder has excavated approximately 600mm deep adjacent/around pole A058465 leaving cable/conduit exposed/under depth of 200mm. Concrete spigot pole A058465 supplied via a pillar in reserve adjacent to #19 Yarck Crt at rear of development. â€¢ Crew isolated this supply at pillar mentioned above. â€¢ Builder/site supervisor is saying they want this pole removed as it is in a future lounge room. â€¢ The 200mm deep cable referred to is actually the supply cable to pole A058466. Cable/conduit is actually on the surface. Crew have isolated this supply at pole A058467. â€¢ Builder wants the pole relocated for future driveway. â€¢ No Go Zone assessor advised Maintenance of under depth cable due to builder changing ground level. â€¢ Permit to Work is attached in the "Notes & Findings" section J 036929 - excavation for water pipe near underground HV and LV cables. â€¢ Builder name unknown, only phone number available | Pole (wood) | 0 | 0 | 0 |  | BD07 | No Go Zone infringement | No Go Zone (no contact) | 43533.3889 |  |  | 14271 | Commercial |  | 20190913JEM_01 | Infrastructure (network-based) | -37.6729 | 144.9072 | 1 | Jemena | Report | 18452 | 0.036069 | Low voltage AC (<1kV) | Essendon Airport | 3049 | Westmeadows | Dug up
Unsuccessful reclose on NT17 22KV feeder. ENO patrolled and found HV conductor down opposite # 105 Champion. Area was isolated and earthed and repairs carried out under Access Permit. | 105 CHAMPION ROAD, NEWPORT VIC 3015 | A000772 |  | Unknown environment factor |  |  |  |  | 2 | HV open wire conductor down. Instantaneous Over-Current protection operated in conjunction with Auto-reclose to lock-out, in this scenario there is no possibility of back-feed, therefore the HV conductor was de-energised on the ground. The extremely large phase-to-phase fault current suggests something generated a solid contact between these phases; the actual debris nor the point of contact could be identified. The extremely large phase-to-phase fault current also caused two other connectors to fail, fortunately these did not result in wires down. | Conductor (bare);Connector/termination | 0 | 0 | 0 |  | NT17 | Vegetation: Trees Incident | Loss of supply | 13/09/2019 20:56 |  |  | 14272 | Residential |  | 20190913JEM_02 | Infrastructure (network-based) | -37.8484 | 144.8735 | 1 | Jemena | Report | 18451 | 0.023771 | 22kV AC | Laverton Raaf | 3015 | Newport | Other
Supply isolated and repairs arranged | Exford Rd, Exford VIC 3338, Australia | 30257152 | Copper theft | [6 empty] | Copper has been stolen from U/G pits from 10 streetlights at the incident location. All the streetlights North and South of the circuits have been isolated There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN011 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43747.7292 |  |  | 14289 | Roadway |  | 20190917PWA_05 | Infrastructure (network-based) | -37.7451 | 144.5512 | 1 | Powercor | Report | 17969 | 0.02191 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Exford | Other
Fault crew dispatched and isolated supply. Fallen tree removed and O/H conductors repaired and supply restored | 35 CHERRY TREE ROAD, NYORA VIC 3987 | LIS2025777 |  | Fallen;Council | [5 empty] | Report of Tree contacting and bringing down HV conductors | Conductor (bare) | 0 | 0 | 0 |  | LLG14 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43655.375 |  |  | 14287 | Roadway |  | 20190917SPN_05 | Infrastructure (network-based) | -38.2998 | 145.6392 | 1 | AusNet Services Distribution | Report | 17967 | 0.027897 | 22kV AC | Moorabbin Airport | 3987 | Nyora | Trees
No immediate action was taken by the work crew. This incident was reported to the Zinfra site representative the following morning, approx. 16 hours after the event. Upon Zinfra becoming aware of the incident, AusNet Services was notified, the area was quarantined, and an investigation commenced and an incident summary report prepared. | 70-84 KYLE ROAD, ALTONA NORTH VIC 3025 |  | Working too close to overhead lines;Caused by contractor;Crane, excavator or other construction/farming equipment | [6 empty] | Whilst working with a 25T excavator for foundation works inside Brooklyn Terminal Station, crew from Multiworks (Zinfra subcontractor) clipped and damaged a 22kV cable. Location of the cable was already known. No one was injured and no damage. Incident reported to AusNet Services and Zinfra prepared an incident summary report. | Cable | 0 | 0 | 0 |  |  | A Multiworks (Zinfra subcontractor) work crew was operating a 25t excavator to reshape earth benches around the foundation for a new monopole inside Brooklyn Terminal Station when the excavator's bucket struck a live 22kV cable. The service's location was known to the work crew having previously used non-destructive digging to verify its position. No personnel were injured and no plant or equipment damaged as a result of this incident other than the cable that was struck. Incident reported to AusNet Services and Zinfra prepared an incident summary report. | No Go Zone (contact) | 43717.3375 |  |  | 14288 | Other | Terminal Station | 20190917SPN_06 | Infrastructure (network-based) | -37.8256 | 144.8577 | 0 | AusNet Services Distribution | Report | 17968 | 0.0027824 | 22kV AC | Laverton Raaf | 3025 | Altona North | Dug up
Electrical inspector and jemena fault truck attended and advised neutral burnt out on service side of POA. An NST test was conducted at the installations switchboard which recorded a failed result. Upon further investigation the attending LEI was able to identify a broken neutral at the customers FOLCB. Upon visual inspection all terminals and connection at the FOLCB and link box were corroded. Due to this, a defect was also raised for the customer. The REC on site was able to rectify and supply a new Certificate of electrical safety. The attending Jemena faults crew were able to run a new service to the customers installation Once replaced, an NST was conducted at the customers switchboard with a pass result recorded. Voltage tests between an independent earth and all exposed metallic parts including the point at which the shocks were received now identified a maximum voltage of 3 volts under load. The customer was left on supply. | 14 Hall Rd, Gladstone Park VIC 3043, Australia | A025942 |  |  |  | Neutral fault |  |  | 2 | The fault was noticed when the plumber was working on water pipes and received an electric shock. Voltage tests between an independent earth and all exposed metallic parts identified a high impedance connection in the residents consumer mains neutral conductor (8V under no load and 47V under load). Further voltage tests at the customer earth/neutral bar recorded the same results. Work being performed: Upgrading plumbing line. Note: Plumber no longer on site upon Licensed Electrical Inspector (LEI) arrival. No details left. TechSafe Report attached in the Notes & Findings section. | Conductor (insulated);Connection box | 0 | 0 | 0 |  | AW02 | Neutral burnt out on service side of point of attachment | Minor shock | 18/09/2019 14:20 |  |  | 14302 | Residential |  | 20190918JEM_01 | Infrastructure (network-based) | -37.6918 | 144.8983 | 1 | Jemena | Report | 18448 | 0.02888 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Gladstone Park | Connection
On arrival crew isolated supply and carried out repairs. LEI attended to test for HVI at effected properties. HVI confirmed at a number of properties. | 206 Ginquam Ave, Irymple VIC 3498, Australia | 30097798 |  |  |  | Leakage |  |  |  | Report received from Vic Fire of a crossarm fire at incident location. There was no damage to the pole, the crossarm was burnt in half and HV conductors have fallen into LV below. There was suspected HVI effecting possibly 12 premises. There was no ground fire, no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire;HV injection | 16/09/2019 14:34 | 1 | Negligible: no ground fire | 14292 | Roadway |  | 20190918PWA_01 | Infrastructure (network-based) | -34.2384 | 142.1967 | 1 | Powercor | Report | 17974 | 0.01455 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
On arrival crew isolated supply and carried out repairs. | 3158 WALNUT AVENUE, MILDURA VIC 3500 | 31020923 |  |  |  | Leakage |  |  |  | Vic Fire reported pole fire at incident location. On arrival crew found crossarm on fire, part of crossarm burnt off and conductor hanging low.. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MBN032 | Excessive leakage current | Pole-top fire | 16/09/2019 13:00 | 1 | Negligible: no ground fire | 14294 | Roadway |  | 20190918PWA_02 | Infrastructure (network-based) | -34.228 | 142.1005 | 1 | Powercor | Report | 17975 | 0.037447 | 22kV AC | Mildura Airport | 3158 | Mildura | Crossarm
Crew made site safe and issued a customer defect notice. | 301 IRONBARK ROAD, ROWSLEY VIC 3340 | 30281922 | Copper theft | [6 empty] | Telstra advised cable stolen from pole to pit, cabinet damaged meter hanging, some underground cables have been cut. Crew found customers cables stolen from LIS 776286 to meter board, approximately 250m. There was no fire, no reported injuries. | Services cable;Meter board (including fuses) | 2 | 2 | 2 |  | BMH003 | Copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43747.4431 |  |  | 14296 | Agricultural |  | 20190918PWA_03 | Infrastructure (customer connection) | -37.6857 | 144.36 | 1 | Powercor | Report | 17977 | 0.028708 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Rowsley | Other
Fault crew dispatched and O/H line isolated. Tree removed from O/H HV conductors and blown fuse replaced. No further damage and no evidence of fire. Confirmed no fire, fuse operated and not a reportable incident. | 174-176 OLD SALE ROAD, NEWBOROUGH VIC 3825 | LIS2627679 |  | Fallen |  |  |  |  | 1 | Initial report of branch contacting O/H HV conductors. | Conductor (bare) | 0 | 0 | 0 |  | MOE14 | Vegetation: Trees Incident | Loss of supply | 15/09/2019 23:48 |  |  | 14309 | Roadway |  | 20190919SPN_04 | Infrastructure (network-based) | -38.1702 | 146.2816 | 1 | AusNet Services Distribution | Report | 18073 | 0.0020521 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Newborough | Trees
Crews attended, isolated supply and performed repairs. | 22 Francis St, Lorne VIC 3232, Australia | 30261511 |  |  |  | Unknown technical factor |  |  |  | Vicfire reported a pole fire at the incident location, on arrival the crew found a single phase FOLCB on the pole in front of the incident location address had overheated and caught fire. There was damage to wiring both up and down the pole, however there was no ground fire reported. There were no injuries or third party damage reported. | Connection box | 2 | 2 | 2 |  | CLC005 | Insufficient remains to determine cause | Pole-top fire | 13/09/2019 22:12 | 1 | Negligible: no ground fire | 14313 |  |  | 20190920PWA_01 | Infrastructure (network-based) | -38.5489 | 143.9797 | 1 | Powercor | Report | 17998 | 0.023796 | Low voltage AC (<1kV) | Avalon Airport | 3232 | Lorne | Connection
Crew have isolated supply to this area. A fault follow up has been raised to restore supply to the affected public lights. | 1247 Mount Cottrell Rd, Melton South VIC 3338, Australia | 30345280 | Copper theft | [6 empty] | A maintenance inspector has reported the theft of low voltage underground public lighting cable from pits in Mount Cottrell Road. Crew arrived on site to find pit lids removed and about 215 meters of public light supply cable has been stolen. Cable has been stolen between public lighting pits to public light poles between LIS 852205 to 852211. No reported injuries or fire due to this incident. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN011 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 13/09/2019 0:00 |  |  | 14315 | Roadway |  | 20190920PWA_03 | Infrastructure (network-based) | -37.7364 | 144.615 | 1 | Powercor | Report | 18000 | 0.006081 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
Crew replaced the stolen HV/LV Copper Earths | Mount Cottrell Rd, Melton South VIC 3338, Australia | 30340995 | Copper theft | [5 empty] | 2 | Report received of stolen earths at incident location. On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through and stolen the HV & LV earths on Pole 217 LIS-847574, Single-Phase Pole Sub. Approximately 3m of HV & LV Copper Earths have been cut away and stolen/taken. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 14/09/2019 12:00 |  |  | 14321 | Roadway |  | 20190924PWA_01 | Infrastructure (network-based) | -37.7237 | 144.6174 | 1 | Powercor | Report | 18010 | 0.017462 | Earthing cable | Laverton Raaf | 3338 | Melton South | Other
Crew replaced the stolen HV/LV Copper Earths | 1053-1083 MOUNT COTTRELL ROAD, THORNHILL PARK VIC 3335 | 30340993 | Copper theft | [6 empty] | Report received of stolen earths at incident location. On arrival the PCA Faults Crew have advised that an unknown person(s) have cut through and stolen the HV & LV earths on Pole 215 LIS-847572, Single-Phase Pole Sub. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | MLN021 | Copper theft | Damage to network assets | 14/09/2019 10:19 |  |  | 14322 | Roadway |  | 20190924PWA_02 | Infrastructure (network-based) | -37.7251 | 144.6172 | 1 | Powercor | Report | 18011 | 0.0040324 | Earthing cable | Laverton Raaf | 3335 | Thornhill Park | Other
HV AND LV was isolated and made safe to replace multiple poles damaged by vehicle impact in Murray Rd east of Newlands Rd. All repairs were made and supply restored. Licensed Electrical Inspector was required to attend site to investigate a possible high voltage injection following a car impacting a pole. Upon arriving the attending LEI carried out a damage assessment of the network assets at the point in which the incident had occurred with no apparent splash marks present on the LV conductors or indication that a high voltage injection had occurred. At this stage the attending LEI carried out a further damage assessment of the accessible properties on the circuit. An inspection of the installation meters, customer fuse boxes and accessible switchboards was undertaken with no sign of damage recorded. Following the damage assessment the attending LEI deemed the circuit as safe to restore following the Jemena construction crew completing their works. | 5 QUARRY CIRCUIT, COBURG VIC 3058 | A020478 & A068458 | Vehicle | [5 empty] | 1 | CS3 22KV FDR CB RECLOSED. Report received from emergency services of car into pole. High Voltage conductors on ground. TechSafe report attached in Notes & Findings section. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | CS03 | Vehicle impact into pole | Loss of supply | 25/09/2019 10:11 |  |  | 14329 | Residential |  | 20190925JEM_01 | Infrastructure (network-based) | -37.7355 | 144.9714 | 1 | Jemena | Report | 18446 | 0.032421 | 22kV AC | Essendon Airport | 3058 | Coburg | Vehicle
Supply isolated conductor repaired | 540 New Dookie Rd, Shepparton East VIC 3631, Australia | 33093102 |  |  |  |  | Inappropriate tools/plant/equipment |  | 1 | A Lend Lease G&B Crew contracted to Powercor were attending a P1 fault on P71 Saleyards Spur (LIS-6304), where there was damage to an insulator and the aluminum conductor, believed to have been caused by a previous lightning strike. Whilst the crew were in the process of repairing the conductor, the conductor broke and fell to the ground. On contact with the ground, the conductor started a small grassfire of approx. 3m2. There were no injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHN024 | Apparent Conductor failure | Loss of supply;Grassfire | 25/09/2019 13:07 | 1 | Localised: less than 10 sq.m | 14333 |  |  | 20190926PWA_01 | Infrastructure (network-based) | -36.3646 | 145.4735 | 1 | Powercor | Report | 18025 | 0.02315 | 22kV AC | Shepparton Airport | 3631 | Shepparton East | Lightning
On arrival crew isolated supply and arranged repairs. | 4 Kingsford Dr, Point Cook VIC 3030, Australia | 30288325 | Copper theft | [6 empty] | Report received of a public lighting fault in Kingsford drive , point cook. Crews attended fault and found that there had been cable theft between LIS No. 782844 & 782845. They tested the remaining cable which was found that it was alive so the crew made it safe. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | WBE013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 17/09/2019 0:46 |  |  | 14334 | Roadway |  | 20190930PWA_01 | Infrastructure (network-based) | -37.8969 | 144.7194 | 1 | Powercor | Report | 18026 | 0.016508 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
On arrival crew isolated supply and carried out repairs. | 1260-1284 Mount Cottrell Rd, Melton South VIC 3338, Australia | 30345285 | Copper theft | [6 empty] | Report of cable theft, pits open with cables exposed at incident location. Crew reported approximately 75m of four core 16mm cable had been stolen from LIS 852211 to LIS 852208 and 51m of four core 16mm cable had also been stolen from LIS 852205 to LIS 852206. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN011 | Copper theft | Damage to network assets | 17/09/2019 15:19 |  |  | 14336 | Roadway |  | 20190930PWA_03 | Infrastructure (network-based) | -37.7382 | 144.6147 | 1 | Powercor | Report | 18028 | 0.0056539 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
Supply isolated, customer to arrange repairs | 274 HIGH STREET, KYNETON VIC 3444 | 30149373 | Vandalism;Copper theft | [6 empty] | NBN called in stating wires pulled out of pit and are now on the ground and pit is open at incident location. There was a length of customers underground service cable stolen from the pit to the meter enclosure and damage to the meter enclosure. There was no fire and no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WND014 | copper theft and vandalism | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 17/09/2019 12:36 |  |  | 14337 | Commercial |  | 20190930PWA_04 | Infrastructure (customer connection) | -37.2646 | 144.4725 | 1 | Powercor | Report | 18029 | 0.027138 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3444 | Kyneton | Other
On arrival supplies isolated and repairs arranged | 975 Leakes Rd, Rockbank VIC 3335, Australia | 30542088 | Vandalism;Copper theft | [6 empty] | Report received of disturbed pits, public lights out and public lighting underground service cable stolen. In three adjacent locations 28 pits were interfered with and approximately 340 mtrs of underground cable stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 21/09/2019 9:03 |  |  | 14352 | Roadway |  | 20191002PWA_05 | Infrastructure (network-based) | -37.7162 | 144.6553 | 1 | Powercor | Report | 18048 | 0.0067245 | Low voltage AC (<1kV) | Laverton Raaf | 3335 | Rockbank | Other
Supply isolated and repairs organised. | 58 Olsen Retreat, Caroline Springs VIC 3023, Australia | 30322459 | Copper theft | [6 empty] | Constable Alistair- Caroline Springs Police reports copper has been stolen out of pit on hume drive- between Infinity Dr and Lancefield Dr (thinks roughly at the back of 57 olsen retreat), pit lid is missing, wires pulled out of pit and exposed and burnt grass around the pit. Unsure of any other details of who has done this. On arrival PAL crew have advised that the LV cables were laying on the ground adjacent to the affected pit and were found to be ALIVE, They further advised that a pair of secatier cutters were found at the scene and the were burn marks around the service pit. No injuries have been reported to PAL. | Services cable;Services pit (network) | 2 | 2 | 2 |  | SA011 | Attempted copper theft | Loss of supply;Grassfire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 23/09/2019 14:49 | 1 | Localised: less than 10 sq.m | 14353 | Roadway |  | 20191002PWA_06 | Infrastructure (network-based) | -37.7111 | 144.7325 | 1 | Powercor | Report | 18049 | 0.0061655 | Low voltage AC (<1kV) | Melbourne Airport | 3023 | Caroline Springs | Other
Crew isolated supply and carried out repairs. | 4 LIQUIDAMBER DRIVE, ROMSEY VIC 3434 | 30348976 | Copper theft | [6 empty] | METRICON HOMES PTY LTD reported stolen cables from approx 10 pits at a new development, underground wires exposed. Crew replaced pit connectors on 10 Service pits that have been vandalised and attempted copper theft. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WND022 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 25/09/2019 14:37 |  |  | 14355 | Roadway |  | 20191003PWA_02 | Infrastructure (network-based) | -37.3639 | 144.7469 | 1 | Powercor | Report | 18052 | 0.015866 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3434 | Romsey | Other
On arrival crew isolated supply and carried out repairs | 203 FIFTH STREET, MERBEIN VIC 3505 | 32143135 | Working too close to overhead lines | [6 empty] | Customer reported, the mains wire in between this and neighboring property is on ground, still attached at poles having parted midspan, customer saw flame but not on fire now. Crew believed the property owner at 203 Fifth Street Merbein had a excavator or something similar operating in his property and clashed the lv and brought it down. Customer was contacted and claimed no knowledge of equipment operation. No equipment found on site. There was no fire, no reported injuries or third party property damage | Conductor (bare) | 2 | 2 | 2 |  | MBN014 | unknown equipment caused conductor clash | Loss of supply;Damage to network assets | 27/09/2019 10:37 |  |  | 14357 | Agricultural |  | 20191003PWA_04 | Infrastructure (network-based) | -34.1825 | 142.0474 | 1 | Powercor | Report | 18054 | 0.012926 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Merbein | Vehicle
On arrival crew isolated supply and iniated cleanup | 27 Kyle Rd, Altona North VIC 3025, Australia | 30254605 | Copper theft | [6 empty] | Powercor crew found a transformer that had been vandalised and stripped of copper, oil and contaminants on ground 100-200ltrs of oil spilt around site. There was no fire or reported injuries | Pad mounted equipment/kiosk | 2 | 1 | 2 |  | BLT017 | Copper theft | Damage to network assets | 30/09/2019 10:39 |  |  | 14358 | Industrial |  | 20191003PWA_05 | Infrastructure (network-based) | -37.8297 | 144.8569 | 1 | Powercor | Report | 18098 | 0.033977 | 22kV AC | Laverton Raaf | 3025 | Altona North | Other
An EIO and fault crew were dispatched to investigate and the NST passed. Fault crews checked the connections at the pole end and found a poor connection which was subsequently replaced. After the connection was replaced, NST passed again with slightly better results. | 90 ASHENDEN SQUARE, ROSEBUD VIC 3939 | 1315745 |  |  |  | Corrosion |  | Phase to neutral | 1 | UE received a report that a customer received a shock in the bathroom from the shower tap. | Connector/termination | 0 | 0 | 0 |  | RBD24 | Fault crews found a poor connection which was corroded internally. | Minor shock | 43626.7535 |  |  | 14375 | Residential |  | 20191011UTD_01 | Infrastructure (network-based) | -38.3686 | 144.8905 | 1 | United Energy Distribution | Report | 18084 | 0.025741 | Low voltage AC (<1kV) | Moorabbin Airport | 3939 | Rosebud | Connection
Crews made safe and removed the connection to the open wire service. | 70 VINE STREET, MOONEE PONDS VIC 3039 | A026471 | Unauthorised access | [5 empty] | 2 | M&S crews attended the above address on Saturday 12.10.19 with an abolishment SO (100101208393) to abolish 1 phase overhead supply and metering (NMI: 6001138232) When the crew arrived they found a vacant block of land with no service line or meter on site. As per the photos (attached in the "Notes & Findings" section) the service line had been cut off at the service clamp and was still live and connected to the open wire street reticulation. | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | NS09 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43809.3764 |  |  | 14396 | Residential |  | 20191021JEM_02 | Infrastructure (network-based) | -37.7693 | 144.9339 | 1 | Jemena | Report | 18116 | 0.036613 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Other
Crew have removed and abolished the OH service line and both meters/NMIâ€™s from site and made safe. Application made for abolisment of the second meter on site (meter number 0258640 NMI 6001008213) in conjunction with meter number 030084 and NMI 6001019484 that we have the Supply Order for. | 20 AVALON AVENUE, BROADMEADOWS VIC 3047 | A091632 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address 16.10.19 with a service order for abolishment of supply and metering for meter number 030084 and NMI 6001019484 When the crews arrived on site they found an abandoned property which had extensive damage and appeared to be ready for demolition. The service fuse had already been removed and there was also a second meter and NMI on site (meter number 0258640 NMI 6001008213) which is shown in Jemena's GIS system as Rear of 20 Avalon Ave Broadmeadows to which the crews did not have an abolishment request or Supply Order for. Both meters shown as "De-active" in Jemena's GIS system. The wiring on site indicated that a meter bypass had occurred on site previously. Details and photos are attached in the "Notes & Findings" section. | Aluminium twisted (grey);Smart meter | 0 | 0 | 0 |  | BMS23 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/10/2019 12:18 |  |  | 14397 | Residential |  | 20191021JEM_03 | Infrastructure (network-based) | -37.6898 | 144.9202 | 1 | Jemena | Report | 18123 | 0.0053519 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Other
On arrival crew found fire had been extinguished, no damage to assets found | Shinnicks Rd, Numurkah VIC 3636, Australia | 33086674 | Unknown external/community factor | [6 empty] | Vicfire had reported having been onsite for a small grassfire at incident location. There was no evidence of asset damage or flashovers, no sign of birdlife. Approximately 25 sq meter of roadside grass burnt , there was no injuries. | Pole (concrete) | 2 | 2 | 2 |  | NKA002 | No cause found, no asset damage detected | Grassfire | 20/10/2019 20:15 | 0 | Small: 10 - 1000 sq.m | 14401 | Roadway |  | 20191022PWA_01 | Infrastructure (network-based) | -36.0744 | 145.4042 | 1 | Powercor | Report | 18128 | 0.0062384 | 22kV AC | Shepparton Airport | 3636 | Numurkah | AF Other
Fault crew dispatched. Candled EDO fuse removed and replaced with new | TAKUNUMA, 227 MCKINNONS ROAD, TINAMBA VIC 3859 | LIS2510389 |  |  |  | Candled fuse |  |  |  | Report of candled HV fuse | EDO fuse | 0 | 0 | 0 |  | MFA22 | Candled 6k EDO HV Fuse | Pole-top fire | 24/10/2019 18:42 | 1 | Negligible: no ground fire | 14416 |  |  | 20191025SPN_01 | Infrastructure (network-based) | -37.9677 | 146.8672 | 2 | AusNet Services Distribution | Report | 18153 | 0.017779 | 22kV AC | Morwell (Latrobe Valley Airport) | 3859 | Tinamba | Fuse
The CitiPower faults crew removed the section damaged cable. | 406 St Kilda Rd, Melbourne VIC 3004, Australia | 35009814 | Working too close to underground cables | [6 empty] | A civil contractor working on Melbourne Metro Tunnel project called the CitiPower report room to advised that someone had excavated and hit a CitiPower underground cable. The CitiPower Underground Faults crew attended and found the cables to be de-energized. The CitiPower Faults crew found the on site contractor had MOC's on site. There was no fire or reported injuries. | Services cable | 2 | 2 | 2 |  | SO006 | Excavation works | No Go Zone (contact);Damage to network assets | 43565.7528 |  |  | 14423 | Roadway |  | 20191028PWA_03 | Infrastructure (network-based) | -37.8346 | 144.9742 | 1 | CitiPower | Report | 18162 | 0.028461 | Low voltage AC (<1kV) | Essendon Airport | 3004 | Melbourne | Dug up
Supply isolated. Damaged conductor repaired and supply restored. | 318 High St, Melton VIC 3337, Australia | 30102707 |  |  |  | Corrosion |  |  |  | Report received that a light pole was on fire outside of 318 High St, Melton. Upon arrival the fault crew found that a loose connection on the white phase IPC where the LV lead connects to the open wire LV . This allowed the white phase conductor to burn through and fall. The load side conductor came to rest on top of the veranda of shops at incident location. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MLN023 | Overheated connection | Loss of supply;Damage to network assets | 43595.8146 |  |  | 14424 | Roadway |  | 20191028PWA_04 | Infrastructure (network-based) | -37.683 | 144.5833 | 1 | Powercor | Report | 18163 | 0.013491 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton | Connection
0930hours Reported incident to Ballarat Police #269787 Reviewed cameras on site with policeÂ (3 men,1990 White Ford Ute with tandem trailer with stock crate + small hatch vehicle) Site made safe | Unnamed Road, Elaine VIC 3334, Australia | 20030140 | Theft | [6 empty] | At 2am 3 people entered ELTS by cutting fence South side & then cut pad locks on PA gate (for removal of stolen equipment)Â Equipment removed from tool trailer / 2 x shipping containers. | Terminal substation | 2 | 2 | 2 |  | MEWF TO ELTS | Theft of tools and equipment | Damage to network assets | 43534.0833 |  |  | 14425 | Other | Terminal station | 20191028PWA_05 | Infrastructure (network-based) | -37.7307 | 144.011 | 1 | Transmission Operations Australia (TOA) | Report | 18164 | 0.038233 | Not applicable | Ballarat Aerodrome | 3334 | Elaine | Other
Crew discussed incident with site supervisor but not forthcoming with information, supply restored. | 70 Wollahra Rise, Wyndham Vale VIC 3024, Australia | 32162934 | Working too close to overhead lines | [6 empty] | Customer reports of supply failure at incident location. Appears tip truck has hit overhead between LIS 211271 and LIS 211272, Observed 1 x pole concrete block support. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | WBE014 | Suspected contact by tipper | Loss of supply;No Go Zone (contact) | 28/10/2019 12:53 |  |  | 14433 |  |  | 20191029PWA_03 | Infrastructure (network-based) | -37.8723 | 144.6236 | 1 | Powercor | Report | 18178 | 0.038618 | 22kV AC | Laverton Raaf | 3024 | Wyndham Vale | Vehicle
On arrival crew isolated supply and issued a defect notice for repairs to POA | 70-72 SLOUGH ROAD, ALTONA VIC 3018 | 31023769 | Working too close to overhead lines | [6 empty] | A customer reported an excavator has contacted service cable at the incident location. On arrival, a Powercor crew found that the service and POA had been damaged There was no fire or reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | AL011 | Excavator contacted service line | Loss of supply;No Go Zone (contact) | 43748.5694 |  |  | 14434 | Roadway |  | 20191029PWA_04 | Infrastructure (customer connection) | -37.8598 | 144.8024 | 1 | Powercor | Report | 18179 | 0.013017 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Vehicle
On arrival crew isolated supply and carried out repairs | 1145-1151 GISBORNE-MELTON ROAD, TOOLERN VALE VIC 3337 | 60319293 | Copper theft | [6 empty] | A Powercor crew attending a maintenance work at the incident location found an opened UG pit lid. The crew also observed that the 50m of street light cable from LIS 828370 to LIS 828372 had been stolen. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN012 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43748.4007 |  |  | 14436 | Roadway |  | 20191029PWA_05 | Infrastructure (network-based) | -37.6079 | 144.5906 | 1 | Powercor | Report | 18181 | 0.0049317 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Toolern Vale | Other
Fault crew dispatched. Candled HV fuse removed and replaced with new | CAMBRIDGE ROAD, MOOROOLBARK VIC 3138 | LIS1001092 |  |  |  | Candled fuse |  |  |  | Report of candled HV fuse | Boric acid | 0 | 0 | 0 |  | CYN33 | Candled 25E BA HV Fuse. No evidence of ground fire | Pole-top fire | 29/10/2019 4:55 | 1 | Negligible: no ground fire | 14430 |  |  | 20191029SPN_01 | Infrastructure (network-based) | -37.803 | 145.3445 | 2 | AusNet Services Distribution | Report | 18173 | 0.0013646 | 22kV AC | Moorabbin Airport | 3138 | Mooroolbark | Fuse
Fault crews were dispatch to the site and the underground cable was isolated at the pole and made safe. Upon inspection, it was confirmed that the underground cable was damaged. The service cable was repaired and NST passed. | UNIT 2 22 TENNYSON STREET, ST KILDA VIC 3182 | 2305578 | Working too close to underground cables;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | UE received a call from a contractor who was drilling and reported that water has flooded into a pit which has caused all supply fail. | Services cable | 0 | 0 | 0 |  |  | The cause of the damaged cable is drilling and construction works. | Loss of supply;No Go Zone (contact);Damage to network assets | 21/10/2019 12:15 |  |  | 14435 | Residential |  | 20191029UTD_01 | Infrastructure (network-based) | -37.8716 | 144.9863 | 1 | United Energy Distribution | Report | 18180 | 0.040899 | Low voltage AC (<1kV) | Moorabbin Airport | 3182 | St Kilda | Dug up
Fault crew dispatched. Blown BA HV fuse replaced. Overhead conductors checked, No damage to O/H conductors. Supply restored. | 45 ENGLISH STREET, DONNYBROOK VIC 3064 | LIS928576 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Excavator (from Winslow Construction) contacting O/H HV conductors 22kV. | Conductor (bare) | 0 | 0 | 0 |  | KLO14 | Whilst operating in vicinity of O/H HV conductors, an excavator contacted the O/H conductors causing a fuse to operate. No injuries reported and no damage to O/H conductors. Fuse replaced and supply restored. | No Go Zone (contact) | 29/10/2019 11:00 |  |  | 14441 |  |  | 20191031SPN_01 | Infrastructure (network-based) | -37.5496 | 144.9635 | 1 | AusNet Services Distribution | Report | 18192 | 0.0017454 | 22kV AC | Wallan (Kilmore Gap) | 3064 | Donnybrook | Vehicle
SIte inspected no damage found | 257 Beveridge St, Swan Hill VIC 3585, Australia | 33070207 |  | Bird | [5 empty] | Bird flashed over on pole top and caught fire. There was no ground fire or reported injuries | Pole (concrete) | 2 | 2 | 2 |  | SHL007 | Bird Incident | Pole-top fire | 43533.2944 | 1 | Negligible: no ground fire | 14443 | Roadway |  | 20191101PWA_01 | Infrastructure (network-based) | -35.3426 | 143.5592 | 1 | Powercor | Report | 18196 | 0.0013044 | 22kV AC | Swan Hill Aerodrome | 3585 | Swan Hill | Animal
crew attended | 2 BREESE STREET, BRUNSWICK VIC 3056 | 30159662 | Working too close to overhead lines | [5 empty] | 1 | Citipower operator responding to a feeder protection operation found that crane had contacted HV conductor | Conductor (bare) | 0 | 0 | 0 |  | BK011 | Tower crane working in vicinity of HV line | Loss of supply;No Go Zone (contact) | 30/10/2019 15:16 |  |  | 14445 | Construction |  | 20191101PWA_03 | Infrastructure (network-based) | -37.7601 | 144.9618 | 1 | CitiPower | Report | 18200 | 0.038275 | 11kV AC | Essendon Airport | 3056 | Brunswick | Vehicle
crew attended, isolated line and completed repairs | Calder Hwy, Woosang 3518 | 30229277 | [6 empty] | 1 | Crew were investigating an outage on BETS-CTN 66kV line and found a broken conductor and ground fire | Conductor (bare) | 0 | 0 | 0 |  | BETS-CTN | TBC | Grassfire | 43476.4986 | 1 | Medium: 1000 sq.m - 10 ha | 14452 | Roadway |  | 20191104PWA_06 | Infrastructure (network-based) | -36.3267 | 143.4685 | 1 | Powercor | Notification | 18212 | 0.03787 | 66kV AC | Swan Hill Aerodrome | 3518 |  | Conductor
crew attended and isolated supply prior to completing repairs | 5 MCDONALD STREET, RUSHWORTH VIC 3612 | 30127619 |  |  |  | Overheated connection |  |  |  | Customer reported a pole fire out front of school on McDonald Street, wooden pole. Crew found that FSD had been consumed and required replacement. | Conductor (insulated);Any other type | 0 | 0 | 0 |  | SHP014 | overheated connection | Pole-top fire | 43507.6396 | 1 | Negligible: no ground fire | 14453 | Roadway |  | 20191104PWA_07 | Infrastructure (network-based) | -36.5831 | 145.0136 | 1 | Powercor | Report | 18214 | 0.012809 | Low voltage AC (<1kV) | Mangalore Airport | 3612 | Rushworth | Connection
crew isolated supply and replaced cross-arm | 276 San Mateo Avenue Mildura 3500 | 32147322 |  |  |  | Leakage |  |  |  | Vic Fire reported a Pole fire at intersection of Burrows Street and San Mateo Avenue, fire on HV cross arm. Crew found small fire on pole had started at king bolt. | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | MDA022 | crew advised that leakage from polluted insulator/s was cause | Pole-top fire | 43507.0979 | 1 | Negligible: no ground fire | 14454 | Roadway |  | 20191104PWA_08 | Infrastructure (network-based) | -34.2008 | 142.1538 | 1 | Powercor | Report | 18215 | 0.028846 | 22kV AC | Mildura Airport | 3500 |  | Crossarm
Crew attended, isolated supply and replaced pole top assembly | 159 PATHO CEMETERY ROAD, PATHO VIC 3564 | 33022125 |  |  |  | Leakage |  |  |  | Customer reports of supply failure. Crew found wires down during line patrol due to pole fire, pole top assembly replaced, | Pole (wood) | 0 | 0 | 0 |  | CHA005 | Leakage due to pollution | Pole-top fire | 43535.241 | 1 | Negligible: no ground fire | 14455 | Roadway |  | 20191104PWA_09 | Infrastructure (network-based) | -35.9967 | 144.4742 | 1 | Powercor | Report | 18216 | 0.039885 | 22kV AC | Bendigo Airport | 3564 | Patho | Pole
The PCA Faults Crew undertook an emergency shutdown and replaced the burnt HV Inter Crossarm. | 32 Macedon Street, Hoppers Crossing, VIC, 3029 | 32174345 |  |  |  | Leakage |  |  |  | customer advised that mains wire has come off insulator and is resting on the cross arm, making a sizzling sound. On arrival the PCA Faults Crew have advised that the HV cross arm has burnt. | Crossarm (wood) | 0 | 0 | 0 |  | LV009 | Excessive leakage current | Pole-top fire;Loss of supply | 43507.4715 | 1 | Negligible: no ground fire | 14462 | Roadway |  | 20191106PWA_03 | Infrastructure (network-based) | -37.8701 | 144.705 | 1 | Powercor | Report | 18226 | 0.017847 | 22kV AC | Laverton Raaf | 3029 |  | AF Other
crew attended, made safe and replaced service cable | 29 SUSSEX STREET, SEAHOLME VIC 3018 | 30102723 | Vehicle | [5 empty] | 2 | Customer reported a wire crossing road has been sliced in half by truck driving through and fallen over the road. No supply. Customer said that they saw a truck towing a boat and suddenly they heard a bang and there was no power supply after that On arrival the crew found that a truck had made contact with a Neutral Screen service, the service broke mid span | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | AL014 | reportedly struck by unknown oversize vehicle | Loss of supply;Damage to network assets | 13/10/2019 11:40 |  |  | 14463 | Roadway |  | 20191106PWA_04 | Infrastructure (network-based) | -37.8639 | 144.8409 | 1 | Powercor | Report | 18227 | 0.023138 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Seaholme | Vehicle
crew attended and repaired conductors | 58 Sherwood St, Birchip VIC 3483 | 32018160 |  | Blown branch/vegetation |  |  |  |  | 1 | Crew were patrolling line after a fault and found a tree branch had broken and contacted HV and brought down the red phase of the HV into the LV. Red phase HV conductor damaged. | Conductor (bare) | 0 | 0 | 0 |  | CTN001 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 25/10/2019 3:30 |  |  | 14464 | Residential |  | 20191106PWA_05 | Infrastructure (network-based) | -35.9784 | 142.9198 | 1 | Powercor | Report | 18229 | 0.021214 | Low voltage AC (<1kV);22kV AC | Swan Hill Aerodrome | 3483 | Birchip | Trees
Fault crews were dispatch to the site and the area was made safe. Inspections found no damage to conductors but there were scorch marks on the ground from tires. Conductor clearance measured at 5.6m at the point of contact. Vehicle details unknown. | QUARRY, 191 GEORGE STREET, WANTIRNA SOUTH VIC 3152 | 619559 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | UE control room shows the ACR supplying the area had been locked out and the feeder was patrolled but no cause was identified. On 1st November, UE received a call from a company advising that one of their trucks potentially made contact with HV conductors earlier in the week which coincides with the ACR lock out event. ESV was advised, ref no. 12725329. | Conductor (bare) | 0 | 0 | 0 |  | GW7 | The cause is a quarry vehicle hitting the HV conductor. Conductor clearance measured at 5.6m at the point of contact. Vehicle details unknown. | Grassfire | 28/10/2019 15:55 | 1 | Localised: less than 10 sq.m | 14460 | Industrial |  | 20191106UTD_02 | Infrastructure (network-based) | -37.8847 | 145.2067 | 1 | United Energy Distribution | Report | 18222 | 0.013039 | 22kV AC | Moorabbin Airport | 3152 | Wantirna South | Vehicle
Metering & Servicing crews have disconnected the overhead service at pole A021606 and tied back and issued defect notice J24660 on site. | 13 MORAY STREET, FAWKNER VIC 3060 | A021606 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews have located an unauthorised and illegal overhead Builders Temporary Supply (BTS) connection and metering at this address. As per the attached photos (in the "Notes & Findings" section) the BTS has an older AGL analogue legacy meter connected with a new type of seal not used on the Jemena network. | Smart meter | 0 | 0 | 0 |  | CN04 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/10/2019 14:15 |  |  | 14465 | Residential |  | 20191107JEM_01 | Infrastructure (network-based) | -37.7094 | 144.9627 | 1 | Jemena | Report | 18230 | 0.014302 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | Other
Isolated supply and carried out repairs | 7 GREENE STREET, SPOTSWOOD VIC 3015 | A028141 |  |  |  | Leakage |  |  | 1 | HV crossarm fire HV conductor came off crossarm and hanging low over railway line Train ran over HV conductor | Conductor (bare) | 0 | 0 | 0 |  | FW05 | Earth leakage | Pole-top fire;Damage to network assets | 43810.2979 | 1 | Negligible: no ground fire | 14485 | Other | Railway Line | 20191112JEM_01 | Infrastructure (network-based) | -37.8274 | 144.8713 | 1 | Jemena | Report | 18504 | 0.017157 | 22kV AC | Essendon Airport | 3015 | Spotswood | Crossarm
Due to the nature of the installation at number 9 Vernon, and the safety issue the REC had created and removed the customer from supply, the crew were required to disconnect the small SEC junction box to remove the service line to number 9 Vernon St and make safe the customer installation. Number 11 Vernon was then returned to supply. Checks were completed and number 11 Vernon St is not a registered life support customer. Crew will complete all the neutral screen service upgrades and replacements when they return for their 1.00pm reconnect appointment. | 9 VERNON STREET, SPOTSWOOD VIC 3015 | A028177 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address this morning with a SO for 9.30am disconnect TA and to return for a 1.00pm reconnect TA. When the crew arrived they found the REC had already removed the service fuse, disconnected and removed the MSB and the electricity meter left hanging inside the existing meter surround enclosure. The property was supplied via an overhead neutral screen service which was connected to a small SEC junction box which also had a neutral screen service supplying number 11 Vernon St. The small SEC junction box was located on a service pole which was being supplied by a neutral screen road crossing service. (normal process would be to card and provide notification with a minimum 4 clear business days and re-schedule the appointment) | Neutral screen;Smart meter | 0 | 0 | 0 |  | FW05 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43657.4646 |  |  | 14486 | Residential |  | 20191112JEM_02 | Infrastructure (network-based) | -37.8272 | 144.8724 | 1 | Jemena | Report | 18255 | 0.012554 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Spotswood | Other
crew attended and made safe, supply restored, replacement of fuse unit pending | 130 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631 | 33096475 |  | Bird |  |  |  |  | 1 | A customer reported a loud bang and ground fire at the incident location. Upon arrival, a Powercor fault crew found that a bird flash over resulted in a small ground fire | Boric acid | 0 | 0 | 0 |  | SHN024 | Bird Incident | Grassfire | 43780.5833 | 1 | Small: 10 - 1000 sq.m | 14490 | Agricultural |  | 20191113PWA_03 | Infrastructure (network-based) | -36.3527 | 145.4333 | 1 | Powercor | Report | 18260 | 0.022609 | 22kV AC | Shepparton Airport | 3631 | Grahamvale | Animal
crew attended and replaced BA fuse unit | 30 YELTA ROAD N, MERBEIN VIC 3505 | 33066091 |  | Bird | [5 empty] | CFA reported a grassfire . Upon crew arrival found an extinguished grassfire near the base of the pole. A magpie had caused a flash over on HV fuse. | Boric acid | 0 | 0 | 0 |  | MBN031 | Bird Incident | Grassfire | 13/11/2019 20:33 | 1 | Small: 10 - 1000 sq.m | 14499 | Roadway |  | 20191115PWA_01 | Infrastructure (network-based) | -34.1699 | 142.0421 | 1 | Powercor | Report | 18270 | 0.040123 | 22kV AC | Mildura Airport | 3505 | Merbein | Animal
Repairs arranged | 15 BLOOMFIELD ROAD, GISBORNE VIC 3437 | 30034689 | Working too close to overhead lines | [6 empty] | A contractor reported their excavator flicked over head service at the incident location. Upon arrival, a Powercor crew found that the service had been damaged. He also observed that the road is being upgraded. | Service cable (insulated) | 0 | 0 | 0 |  | GSB013 | Excavator flicked O/H service | Loss of supply;Damage to network assets | 23/10/2019 10:20 |  |  | 14508 | Roadway |  | 20191121PWA_03 | Infrastructure (network-based) | -37.4998 | 144.605 | 1 | Powercor | Report | 18286 | 0.0049699 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Vehicle
Fault crew dispatched. Pole X-arm replaced. pole inspector organised to inspected pole. | 63 NORTHERN AVENUE, NEWBOROUGH VIC 3825 | LIS2208258 |  | Lightning | [5 empty] | Report of lightning strike to pole resulting in damaged insulator and pole fire | Pole (wood);Pole top | 0 | 0 | 0 |  | MOE13 | Currently under investigation. Lightning appears to have struck pole | Pole-top fire | 21/11/2019 18:21 | 1 | Negligible: no ground fire | 14514 |  |  | 20191122SPN_01 | Infrastructure (network-based) | -38.1735 | 146.2871 | 1 | AusNet Services Distribution | Report | 18293 | 0.015177 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Newborough | Lightning
Crew dispatched to investigate and make safe. Crew put out fire on arrival. Surge arrester was was found to be blown and was cut away and customers were restored. | ROSEDALE-HEYFIELD ROAD, ROSEDALE VIC 3847 | LIS2600780 |  |  |  | Electrical breakdown |  |  |  | Grass fire near pole 2600780. | Surge diverter | 0 | 0 | 0 |  | TGN41 | Blown surge arrester on pole 2600780 and started a grass fire. | Grassfire | 21/11/2019 14:30 | 1 | Small: 10 - 1000 sq.m | 14520 |  |  | 20191122SPN_04 | Infrastructure (network-based) | -38.138 | 146.7934 | 1 | AusNet Services Distribution | Report | 18303 | 0.011083 | 22kV AC | Morwell (Latrobe Valley Airport) | 3847 | Rosedale | Installation
CFA attended, fire was out when AusNet crew arrived. Tree was under line with burn marks. The fault crew then proceeded to investigate assets form ground level. No damage to assets found. Fire marks on ground approx. 30mx5m. | MAINTONGOON ROAD, BONNIE DOON VIC 3720 | MSD2 |  | Fallen | [5 empty] | Report of tree contacting O/H HV conductors and fire in the vicinity | Conductor (bare) | 0 | 0 | 0 |  | LIS3912765 | Vegetation: Trees Incident | Grassfire | 21/11/2019 18:38 | 1 | Small: 10 - 1000 sq.m | 14522 |  |  | 20191122SPN_05 | Infrastructure (network-based) | -37.0571 | 145.8603 | 1 | AusNet Services Distribution | Report | 18307 | 0.029359 | 22kV AC | Mangalore Airport | 3720 | Bonnie Doon | Trees
Crew left site undisturbed and referred back to Office, ESV notified | 25 CAPITAL STREET, ALFREDTON VIC 3350 | 30332631 |  |  |  |  | Poor REC workmanship |  | 2 | Powercor crew attended premises to undertake new connection and found meter box and switchboard had not been installed. | Customer wiring | 0 | 0 | 0 |  | BAS024 | Incomplete wiring | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 22/11/2019 16:30 |  |  | 14531 | Residential |  | 20191125PWA_01 | Infrastructure (customer connection) | -37.5495 | 143.8132 | 1 | Powercor | Report | 18323 | 0.040709 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Alfredton | Other
The crew made site safe, replaced the damaged bridges and restored supply. | 18 Mossfiel Dr, Hoppers Crossing VIC 3029, Australia | 32169859 |  |  |  | Corrosion |  |  |  | A Customer reported a Small Fire at base of Pole LIS-971870. CFA attended, Fire extinguished. Supply Off. On arrival the crew found that the LV conductor line bridges had burnt at a substation LV bus fuse termination mounted on pole (LIS-208939). There was a small area of burnt grass at the base of the pole (LIS-208939) caused by fallen hot debris. There was no reported injuries nor third party property damage. | Connector/termination;Dropper/bridge | 2 | 2 | 2 |  | WBE013 | Overheated connection | Grassfire | 21/11/2019 15:44 | 1 | Localised: less than 10 sq.m | 14532 |  |  | 20191125PWA_02 | Infrastructure (network-based) | -37.8765 | 144.6952 | 1 | Powercor | Report | 18324 | 0.018662 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
Sent fault crew to make safe, investigate and repair. Vegetation crew also attended site and observed burn marks on the filed limb. Removed tree branch and restored supply. Refer to attached photos of the incident. | 342 CAMBRIDGE ROAD, MONTROSE VIC 3765 | LIS1001092 |  | Blown branch/vegetation | [5 empty] | Report of tree contacting O/H HV conductor resulting in ground fire. Private decayed tree branch outside vegetation cleared space failed in gusts of wind and made contact with 22 kv conductor. Tree brushed HV conductors between poles 1001092 and 100109. Small fire near asset 2 square metre in size. | Conductor (bare) | 0 | 0 | 0 |  | CYN33 | Vegetation: Trees Incident | Grassfire | 21/11/2019 16:00 | 1 | Localised: less than 10 sq.m | 14526 |  |  | 20191125SPN_01 | Infrastructure (network-based) | -37.803 | 145.3445 | 1 | AusNet Services Distribution | Report | 18313 | 0.013213 | 22kV AC | Moorabbin Airport | 3765 | Montrose | Trees
Fault crew dispatched to make safe, investigate and repair. Pole, crossram and insulators were replaced. | 4 MARJORY STREET, THOMASTOWN VIC 3074 | LIS909037 |  | Precipitation |  | Electrical breakdown;Leakage |  |  |  | Report of crossarm fire. HV INT x-arm failed due to tracking and as a result had snapped in half and was supported by bracing brackets. This tracking has also caused damage to the pole top. There was no ground fire. Please refer to attached photos. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | TT5 | Cause of the fire was tracking on the centre phase insulator and as a result the wooden pole top and xarm had caught fire. | Pole-top fire | 26/11/2019 17:28 | 1 | Negligible: no ground fire | 14543 |  |  | 20191127SPN_01 | Infrastructure (network-based) | -37.6827 | 145.0226 | 1 | AusNet Services Distribution | Report | 18338 | 0.039836 | 22kV AC | Essendon Airport | 3074 | Thomastown | Crossarm
Crew attended site and found tree branch had contacted the HV conductors near pole 4501610. Branch was scorched, but no ground fire was present on site. Crew opened upstream fuses and found the White Phase fuse had operated. Crew returned to site and found branch on the ground, no fire present on the ground. Crew replaced White Phase fuse and closed all fuses to restore supply. | 315 WHITE POST ROAD, EVERTON UPPER VIC 3678 | LIS4501610 |  | Blown branch/vegetation | [5 empty] | Tree branch leaning on HV conductor. Branch was smoldering. No ground fire present on site. | Conductor (bare) | 0 | 0 | 0 |  | WN5 | Vegetation: Trees Incident | Pole-top fire | 26/11/2019 16:11 | 1 | Negligible: no ground fire | 14544 | Agricultural |  | 20191127SPN_02 | Infrastructure (network-based) | -36.4069 | 146.5454 | 1 | AusNet Services Distribution | Report | 18340 | 0.0086852 | 22kV AC | Wangaratta Aero | 3678 | Everton Upper | Trees
Fault crews arrived on site and made it safe. Upon inspection, an ampact failure has caused the HV conductor to fall onto the ground which started a small grassfire. Fault crews repaired the conductors and supply was restored. | 53 BALCOMBE ROAD, MENTONE VIC 3194 | 1820222 |  |  |  | Corrosion |  |  | 1 | UE was advised by MFB that a live wire had fallen onto the ground and started a fire. UE protection operated to isolate the fault. | Conductor (bare) | 0 | 0 | 0 |  | BR4 | The cause of the small grassfire was an ampact which failed and resulted in the live HV conductor falling to the ground. | Grassfire | 30/10/2019 14:35 | 1 | Localised: less than 10 sq.m | 14548 | Roadway |  | 20191127UTD_04 | Infrastructure (network-based) | -37.9816 | 145.066 | 1 | United Energy Distribution | Report | 18406 | 0.0030058 | Low voltage AC (<1kV);11kV AC | Moorabbin Airport | 3194 | Mentone | Connection
Inspected and made safe. | 45 WILLOWMAVIN ROAD, KILMORE VIC 3764 | LIS4716975 |  | Bird |  |  |  | Phase to earth |  | Report of bird contacting O/H conductors resulting in ground fire | Circuit breaker | 0 | 0 | 0 |  | KMS12 | Bird Incident | Grassfire | 28/11/2019 9:42 | 1 | Localised: less than 10 sq.m | 14554 |  |  | 20191128SPN_01 | Infrastructure (network-based) | -37.2806 | 144.9441 | 1 | AusNet Services Distribution | Report | 18351 | 0.039344 | 22kV AC | Wallan (Kilmore Gap) | 3764 | Kilmore | Animal
On arrival crew isolated supply and carried out repairs. No go zone group managing silage relocation | 674 COBDEN-TERANG ROAD, COBRICO VIC 3266 | 30558573 | Working too close to overhead lines | [6 empty] | A company employee reported that a HV line hit by vehicle (silage cart) damaging the conductors and cross arm at the incident location. The silage dump appeared to be adjacent to the HV line. There was no fire or reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG003 | Silage trailer unloading close to overhead line | No Go Zone (contact);Damage to network assets | 21/11/2019 20:49 |  |  | 14569 | Agricultural |  | 20191202PWA_01 | Infrastructure (network-based) | -38.3042 | 143.0203 | 1 | Powercor | Report | 18368 | 0.01006 | 22kV AC | Warrnambool Airport Ndb | 3266 | Cobrico | Vehicle
Site made safe | 125 Vineyard Rd, Sunbury VIC 3429, Australia | A146741 | Vandalism;Theft;Copper theft | [5 empty] | 2 | Unknown person has stolen street light copper | Cable | 2 | 2 | 2 |  | SBY23 | Copper theft | Damage to network assets | 43567.4174 |  |  | 14585 | Roadway |  | 20191204JEM_01 | Infrastructure (customer connection) | -37.5944 | 144.7141 | 1 | Jemena | Report | 18404 | 0.012417 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
NGZ Team Leader attended site. There is scaffold erected and tilers were working on the roof when he attended. He spoke to the roof tiler who wasnâ€™t aware if a Permit To Work (PTW) was on issue. Advised him to not continue with his roof tiling until this was sorted out. NGZ Team Leader then contacted the owner/builder by phone and asked if he had contacted Jemena in relation to working in the vicinity of our assets and also obtaining a PTW. The owner/builder advised that he had not contacted Jemena and did not have a PTW, and that he had contacted the Council regarding the building and was issued all the relevant certificates to build the house where it was. NGZ Team Leader informed him of his requirements when working within the vicinity of our assets and advised him to cease work until this was sorted. NGZ Team Leader then sent his assessor to the site and he took measurements from the house, scaffold etc. to Jemena overhead conductors. - Distance of HV 22kv Conductors from Ground â€“ 8,100mm - Distance from Scaffold Platform to Conductors â€“ 5,200mm - Distance from Tiled Roof to HV Conductors â€“ 3,400mm - Distance from Highest Point of Scaffold to HV Conductors â€“ 3,100mm - Highest Point of the Roof â€“ 6,700mm The owner/builder called NGZ Team Leader later in the day to advise that he had stopped work and all tradesmen were removed from site until this was resolved. | 320 DEEP CREEK ROAD, OAKLANDS JUNCTION VIC 3063 | A037904 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | House being built below the 22kV adjacent to substation on pole A037904 feeder SBY14 near the entrance road off Konagaderra Rd to Deep Creek underground estate. Construction of house was observed by an Optus employee who informed Tom Ruzeu from Jemena, who then contacted NGZ Team Leader to investigate. | Conductor (bare) | 0 | 0 | 0 |  | SBY24 | No Go Zone breach | No Go Zone (no contact) | 27/11/2019 17:19 |  |  | 14597 | Peri-urban |  | 20191206JEM_01 | Infrastructure (network-based) | -37.5329 | 144.837 | 1 | Jemena | Report | 18421 | 0.038045 | 22kV AC | Melbourne Airport | 3063 | Oaklands Junction | Other
Underground crew made repairs to underground cable insulation 2 customers were briefly interrupted during repair works | 35 BONDS LANE, GREENVALE VIC 3059 | A054320 | Working too close to underground cables | [5 empty] | 2 | Unknown contractor reported damaged UG cable (Peter 0435791944), while digging trench to install Underground connection at pole no.A054320 and struck a low voltage underground cable and damaged the outer sheath. No injuries. No customers were off supply. Photos are unavailable for this incident | Cable | 0 | 0 | 0 |  | COO21 | No Go Zone Infringement | No Go Zone (contact);Damage to network assets | 17/01/2020 12:30 |  |  | 14901 | Peri-urban |  | 20200117JEM_01 | Infrastructure (network-based) | -37.6422 | 144.8768 | 1 | Jemena | Report | 18820 | 0.034689 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Dug up
On arrival crew isolated supply and carried out repairs | 38 Rouse St, Port Melbourne VIC 3207, Australia | 30203431 |  | Precipitation |  | Moisture ingress;Not built/maintained to design |  |  |  | Customer reported fire/arching on pole at the above incident location. On arrival, crew noticed LV Crom Box was damaged and melted, There was no ground fire, no injuries or third party damage. | Connection box | 2 | 2 | 2 |  | AP003 | Moisture ingress during severe storm | Pole-top fire | 15/01/2020 17:09 | 1 | Negligible: no ground fire | 14889 | Roadway |  | 20200117PWA_02 | Infrastructure (network-based) | -37.844 | 144.943 | 1 | CitiPower | Report | 19329 | 0.031718 | Low voltage AC (<1kV) | Essendon Airport | 3207 | Port Melbourne | Connection
Inspector and crew organised to investigate, make safe and repair. Confirmed HVI. New pole installed. 2 installations fed from pole had meters replaced. No other damage. All testing carried out and passed. | 2 OLD PLENTY ROAD, SOUTH MORANG VIC 3752 | 917469 |  | Lightning | [5 empty] | Lightning hit pole causing HV conductor to be brought down into LV, causing high voltage injection. | Conductor (bare) | 0 | 0 | 0 |  | SMG23 | Lightning hit pole and severely damaged and split it. This caused HV conductor to be brought down into LV. | HV injection | 16/01/2020 17:31 |  |  | 14887 | Residential |  | 20200117SPN_02 | Infrastructure (network-based) | -37.646 | 145.0929 | 1 | AusNet Services Distribution | Report | 19355 | 0.011769 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3752 | South Morang | Lightning
CFA extinguished fire. Crew dispatched to investigate and make safe. First response crew made site safe. Construction crews carried our repairs on conductors. | 959 BREAK ODAY ROAD, GLENBURN VIC 3717 | 1401202 |  | Blown branch/vegetation | [5 empty] | Ground fire from wire down | Conductor (bare) | 0 | 0 | 0 |  | KLK11 | Vegetation: Trees Incident | Grassfire | 16/01/2020 23:02 | 1 | Small: 10 - 1000 sq.m | 14893 | Residential |  | 20200117SPN_04 | Infrastructure (network-based) | -37.3689 | 145.3537 | 1 | AusNet Services Distribution | Report | 18811 | 0.010953 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3717 | Glenburn | Trees
Fault crews attended the site to investigate. Upon inspection, it was identified the LV krone box was arcing and sparking which caused a small grass fire at the base of the pole substation. ESV was notified, ref #13036024. The site was isolated and made safe. The krone box was replaced and supply was restored. | 38 BRUARONG CRESCENT, FRANKSTON SOUTH VIC 3199 | 3315975 |  |  |  | Overheated connection |  |  | 1 | UE received calls that customers have lost supply. | Disconnector/isolator | 0 | 0 | 0 |  | FSH13 | The cause of the fire was arcing and sparking from an LV krone box. | Grassfire | 20/12/2019 17:20 | 1 | Localised: less than 10 sq.m | 14896 | Roadway |  | 20200117UTD_01 | Infrastructure (network-based) | -38.1595 | 145.1088 | 1 | United Energy Distribution | Report | 18814 | 0.02751 | Low voltage AC (<1kV) | Moorabbin Airport | 3199 | Frankston South | Connection
Fault crews attended the site to investigate and was advised by the customer that he had received a shock from the bathroom tap the previous day. The fault crews identified a broken neutral at POA and replaced the service. EIO attended the site and tested the tap after the repairs and it passed. | 15 YARRINUP AVENUE, CHADSTONE VIC 3148 | 2312414 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE data analytics identified abnormal voltage behavior at the premise. | POA connection (network side) | 0 | 0 | 0 |  | OAK21 | The cause of the shock was a broken neutral at POA. | Minor shock | 30/12/2019 13:45 |  |  | 14900 | Residential |  | 20200117UTD_03 | Infrastructure (network-based) | -37.876 | 145.1048 | 1 | United Energy Distribution | Report | 18819 | 0.018131 | Low voltage AC (<1kV) | Moorabbin Airport | 3148 | Chadstone | Connection
Isolated supply and replaced damaged assets (including pole) on the same night | 1 HOBBS CRESCENT, RESERVOIR VIC 3073 | A018624 |  |  |  | Leakage |  |  | 1 | Pole top fire due to atmospheric conditions resulting in feeder TT10 trip. | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | TT10 | Earth leakage | Pole-top fire | 20/01/2020 18:48 | 1 | Negligible: no ground fire | 14909 | Residential |  | 20200120JEM_01 | Infrastructure (network-based) | -37.7056 | 145.0093 | 1 | Jemena | Report | 18830 | 0.031943 | 22kV AC | Essendon Airport | 3073 | Reservoir | Pole
On arrival crew isolated supply and carried out repairs. LEI attended to reconnect supply | 902 Meridian Rd, Wargan VIC 3505, Australia | 33063262 |  |  |  | Overheated connection |  |  |  | Report received of customers three phase mains box has caught fire. Crew attended to find burnt out three phase mains box. Crew advise loose connection had caused heating and arcing inside the box signs of melting but "NO FIRE". There was no fire, no reported injuries | Connection box | 2 | 2 | 2 |  | MBN014 | Overheated connection | Melting or smoking only | 43781.375 |  |  | 14906 | Agricultural |  | 20200120PWA_04 | Infrastructure (customer connection) | -34.196 | 141.9935 | 1 | Powercor | Report | 18826 | 0.018532 | Low voltage AC (<1kV) | Mildura Airport | 3505 | Wargan | Connection
On arrival crew isolated supply and carried out repairs. | 24 ELIZABETH STREET, WENDOUREE VIC 3355 | 75244598 |  |  |  | Mechanical breakdown |  |  |  | Vic Fire reported a wire down which had caused a grass fire at the incident location. On arrival crew found that a service line had ruptured at the house end roller clamp falling to ground and starting a small grass fire. | Service cable (insulated) | 2 | 2 | 2 |  | BAN004 | Service ruptured at roller clamp | Grassfire | 18/01/2020 15:00 | 1 | Localised: less than 10 sq.m | 14908 | Residential |  | 20200120PWA_06 | Infrastructure (customer connection) | -37.5305 | 143.8344 | 1 | Powercor | Report | 18829 | 0.027729 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | OH Cable
Sent crew to investigate, make safe and repair. Crew repaired the failed ABC conductors, connections and restored supply. | 32 Hume Ln, Mount Dandenong VIC 3767, Australia | 1304263 |  | Wind;Fallen | [5 empty] | Report of fire marks conductor due to tree impact. HV and LV ABC brought down by large tree between poles 1304263 and 130426. Minimal fire marks on conductors and no evidance of ground fire. Refer to the attached site photos for more information. | Conductor (ABC) | 0 | 0 | 0 |  | MDG1 | Vegetation: Trees Incident | Pole-top fire | 20/01/2020 20:35 | 1 | Negligible: no ground fire | 14910 | Residential |  | 20200121SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19685 | 0.029855 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3767 | Mount Dandenong | Trees
Sent crew to make safe, investigate and repair. Bus deenergised and removed with stick. VT was isolated and made safe to extinguish the fire and remove the guard. | 125 GREAT ALPINE ROAD, LUCKNOW VIC 3875 | 5749444 |  |  |  | Leakage |  |  |  | Report of possum guard (behind the 22kV bus No2 VT PF fuse unit) was tracking and caught fire. Bus deenergised and removed with stick. VT was isolated and made safe to extinguish the fire and remove the guard. The area was inside the zone sub and was gravel all around the area, there was no visible signs of fire on the ground. Refer to attached photos. | Powder filled | 0 | 0 | 0 |  | BDL ZSS | Suspected cause was electrical tracking. | Pole-top fire | 19/01/2020 19:45 | 1 | Negligible: no ground fire | 14915 | Industrial |  | 20200121SPN_04 | Infrastructure (network-based) | -37.8081 | 147.6484 | 1 | AusNet Services Distribution | Report | 18840 | 0.015041 | 22kV AC | Bairnsdale Airport | 3875 | Lucknow | Fuse
Fault crews and EIO attended the site to investigate. The EIO measured 5.9V AC and 5.8V AC at the outside tap and shower tap respectively. The incoming neutral was disconnected and NST failed due to overvoltage on the neutral of 10.1V AC. There was no obvious signs of a bad connection or high impedance at the FOLCB. However NST failed at the FOLCB with 7.8V AC on the incoming neutral. Crews re-terminated the neutral connection and the NST passed. The outside and inside taps were retested by EIO and it passed. | 15 TALLANT AVENUE, SORRENTO VIC 3943 | 1302002 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE received a call that a customer received shocks from shower taps, one outside tap and laundry basin tap. This is happening on the ground floor but not upstairs. The previous day, his son also received similar shocks. | POA connection (network side) | 0 | 0 | 0 |  | STO22 | The cause of the shock was possibly a loose neutral connection at the FOLCB. | Minor shock | 29/12/2019 18:40 |  |  | 14911 | Residential |  | 20200121UTD_01 | Infrastructure (network-based) | -38.3517 | 144.7579 | 1 | United Energy Distribution | Report | 18833 | 0.0065903 | Low voltage AC (<1kV) | Avalon Airport | 3943 | Sorrento | Connection
On arrival crew isolated supply and carried out repairs. LEI inspected premises, no HVI damage was found. | 57 Lynott St, Horsham VIC 3400, Australia | 32092095 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had burned through, and dropped the end of the crossarm onto the LV circuit below. There was no HVI found at customers premises, although a number of smart meters were changed due to damage. There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | HSM009 | Excessive leakage current | Pole-top fire;HV injection | 20/01/2020 0:37 | 1 | Negligible: no ground fire | 14924 |  |  | 20200122PWA_02 | Infrastructure (network-based) | -36.7052 | 142.205 | 1 | Powercor | Report | 18854 | 0.028443 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3400 | Horsham | Crossarm
On arrival crew isolated supply and carried out repairs. | Unnamed Road, Moutajup VIC 3294, Australia | 33059281 |  |  |  | Corrosion |  |  |  | Emergency services reported a pole fire at the incident location. A Powercor crew found that the LV fuse box on the pole ignited due to overheated connections. There were no injuries or ground fire. | Connection box | 2 | 2 | 2 |  | HTN005 | Overheated connection | Pole-top fire | 20/01/2020 10:00 | 1 | Negligible: no ground fire | 14926 | Roadway |  | 20200122PWA_04 | Infrastructure (network-based) | -37.6768 | 142.1907 | 1 | Powercor | Report | 18856 | 0.02274 | Low voltage AC (<1kV) | Hamilton Airport | 3294 | Moutajup | Connection
Crews isolated supply to the area, arranged for an LEI to attend, and performed repairs. | 9-15 Williams Rd, Shepparton VIC 3630, Australia | 33093042 | Vehicle | [6 empty] | Customers and emergency services reported that a truck had contacted a pole/transformer at the incident location. On arrival the crew found that a refrigerated Semi-trailer (Rego PARKY 5) had contacted the transformer platform of the Williams-Archer P2 S/S LIS-2692. The truck pushing on the platform caused the pole to lay over and the HV conductors to drop down onto the LV conductors mid-span, resulting in a HVI to several customers. There was no fire, no reported injuries. | Pole mounted | 2 | 2 | 2 |  | STN023 | Truck contacted substation | HV injection;Loss of supply;Damage to network assets | 21/01/2020 11:10 |  |  | 14932 | Roadway |  | 20200122PWA_07 | Infrastructure (network-based) | -36.3808 | 145.4143 | 1 | Powercor | Report | 18862 | 0.0071319 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3630 | Shepparton | Vehicle
Fault crews attended the site to investigate. MFB were already on site. Upon inspection, it was identified that the transformer bearers were burnt and there was a small ground fire at the base of the pole substation as a result of the blown up surge diverters. The initial cause was a fault from helium balloons into 22kV and 66kV conductors at pole 1317021. ESV was notified, ref #13091982. Fault crews assisted MFB to put the fire out and the site was made safe. The surge diverters and bearers were replaced. | 79 PIER STREET, DROMANA VIC 3936 | 1317035 | Recreation - Helium (party) balloons | [5 empty] | 1 | UE was advised by MFB that there was transformer on fire. | Conductor (bare);Surge diverter | 0 | 0 | 0 |  | DMA21 | The initial cause was a fault from helium balloons into 22kV and 66kV conductors at pole 1317021. | Grassfire | 43831.4757 | 1 | Localised: less than 10 sq.m | 14928 | Roadway |  | 20200122UTD_01 | Infrastructure (network-based) | -38.3375 | 144.9705 | 1 | United Energy Distribution | Report | 18858 | 0.025031 | 22kV AC;66kV AC | Moorabbin Airport | 3936 | Dromana | Other
Fault crews attended the site to investigate. Upon inspection, a customer's tree branch had fallen into the HV and LV lines. An LEI attended the site and confirmed HVI. Fault crews isolated the site and made it safe. | 88 THAMES STREET, BOX HILL NORTH VIC 3129 | 7032770 |  | Fallen;Property owner/customer |  |  |  |  | 1 | UE received calls that customers had no power. | Conductor (bare) | 0 | 0 | 0 |  | DC12 | Vegetation: Trees Incident | HV injection | 43922.3576 |  |  | 14931 | Roadway |  | 20200122UTD_03 | Infrastructure (network-based) | -37.813 | 145.1224 | 1 | United Energy Distribution | Report | 18861 | 0.014913 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3129 | Box Hill North | Trees
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt and fell onto the switch on the same pole. There was no evidence of HVI. ESV was notified, ref #13116331. The site was isolated and made safe. The cross-arm and switch were replaced and supply was restored. | 411 CORRIGAN ROAD, KEYSBOROUGH VIC 3173 | 210551 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply. | Crossarm (wood) | 0 | 0 | 0 |  | NP14 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.4688 | 1 | Negligible: no ground fire | 14938 | Roadway |  | 20200122UTD_08 | Infrastructure (network-based) | -37.9913 | 145.1635 | 1 | United Energy Distribution | Report | 18868 | 0.029591 | 22kV AC | Moorabbin Airport | 3173 | Keysborough | Crossarm
Attend site and replace fuse. | 409 NORTH CANAL ROAD, TRAFALGAR VIC 3824 | 2202815 |  |  |  | Candled fuse |  |  |  | Candled HV fuse. | EDO fuse | 0 | 0 | 0 |  | MOE22 | Fuse Candled. | Pole-top fire | 22/01/2020 5:21 | 1 | Negligible: no ground fire | 14944 | Agricultural |  | 20200123SPN_02 | Infrastructure (network-based) | -38.1846 | 146.1301 | 1 | AusNet Services Distribution | Report | 18876 | 0.020638 | 22kV AC | Morwell (Latrobe Valley Airport) | 3824 | Trafalgar | Fuse
MFB called to report ground/grass fire allegedly caused by sparking conductors. Dispatched crew member who found a tree branch had fallen onto lines, they clashed and started 2 small 1m2 fires on either side of the conductors. | 36 KIRWANA GROVE, MONTMORENCY VIC 3094 | 900363 |  | Blown branch/vegetation | [5 empty] | Ground fire. A tree branch had fallen onto lines and started two 1m2 fires . | Conductor (bare) | 0 | 0 | 0 |  | ELM34 | Vegetation: Trees Incident | Grassfire | 22/01/2020 3:04 | 1 | Localised: less than 10 sq.m | 14946 | Residential |  | 20200123SPN_04 | Infrastructure (network-based) | -37.726 | 145.1335 | 1 | AusNet Services Distribution | Report | 18880 | 0.0036956 | Low voltage AC (<1kV) | Essendon Airport | 3094 | Montmorency | Trees
All work on site was stopped. The control room was contacted and a fault crew dispatched. | 6 WARE STREET, LARA VIC 3212 | 30062574 |  |  |  |  | Inappropriate tools/plant/equipment |  | 1 | A vegetation maintenance worker was trimming tree branches from an EWP when a gust of strong wind broke the branch from the cutting point. The branch was blown onto the 22kv conductors by the wind and the cutting crew observed the branch start to smoke, then arcing from the conductors followed by a loud bang. The cutting crew contacted the control room and checked the crew member who was cutting the tree after he returned the EWP to the cradle. An ambulance was called. The cutter was further assessed at a local hospital, but not admitted . | Conductor (bare) | 0 | 0 | 0 |  | FNS021 | Vegetation: Trees Incident | Medical attention (first aid/doctor/hospital) | 23/01/2020 11:30 |  |  | 14965 | Roadway |  | 20200129PWA_02 | Infrastructure (network-based) | -38.0204 | 144.3842 | 1 | Powercor | Report | 18957 | 0.011807 | 22kV AC | Avalon Airport | 3212 | Lara | Trees
Crew dispatched to investigate and make safe. Repairs carried out. | 84 CUTHBERT STREET, HEATHMONT VIC 3135 | 1220505 |  |  |  | Defective component;Electrical breakdown |  |  |  | Report of pole fire due to failed FOLCB causing small grass fire. | Connection box | 0 | 0 | 0 |  | RWT15 | FOLCB failed from possible loose connection causing box to melt and hot plastic falling on the ground. | Pole-top fire;Grassfire | 30/01/2020 5:22 | 1 | Localised: less than 10 sq.m | 14984 | Residential |  | 20200130SPN_02 | Infrastructure (network-based) | -37.8342 | 145.2406 | 1 | AusNet Services Distribution | Report | 18928 | 0.010484 | Low voltage AC (<1kV) | Moorabbin Airport | 3135 | Heathmont | Connection
Crew dispatched to open, Investergate and replace fuses. Cre replaced 6K BA Fuse. | 366 SOUTH GIPPSLAND HIGHWAY, YARRAM VIC 3971 | 2612575 |  |  |  | Age;Candled fuse |  |  |  | Report of HV Fuse candling. No photos of the site is avialalbe. | Boric acid | 0 | 0 | 0 |  | FTR23 | Plausible cause is combination of age and condition. | Pole-top fire | 43892.4389 | 1 | Negligible: no ground fire | 14998 |  |  | 20200203SPN_02 | Infrastructure (network-based) | -38.5485 | 146.7145 | 1 | AusNet Services Distribution | Report | 18952 | 0.022565 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Yarram | Fuse
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 32 SPRINGFIELD ROAD, BLACKBURN VIC 3130 | 639430 |  |  |  | Leakage |  |  | 1 | UE received a call that there was a burning piece of wood from a pole which was on the ground and was still smoldering. | Crossarm (wood) | 0 | 0 | 0 |  | BH12 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.6528 | 1 | Negligible: no ground fire | 15002 | Roadway |  | 20200203UTD_01 | Infrastructure (network-based) | -37.8098 | 145.1454 | 1 | United Energy Distribution | Report | 18958 | 0.034329 | 22kV AC | Moorabbin Airport | 3130 | Blackburn | Crossarm
On arrival crew isolated supply, pole replaced. | Wimmera Hwy, Rupanyup VIC 3388, Australia | 32107806 |  |  |  | Leakage |  |  |  | Vic fire reported a pole fire at the above location on a SWER intermediate pole. There was a small patch of stubble burnt, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | STL006 | Excessive leakage current | Pole-top fire;Grassfire | 43832.3438 | 1 | Localised: less than 10 sq.m | 15015 | Agricultural |  | 20200204PWA_03 | Infrastructure (network-based) | -36.642 | 142.7006 | 1 | Powercor | Report | 18974 | 0.022053 | 12.7kV AC (SWER) | Horsham Aerodrome | 3388 | Rupanyup | Pole
Fault crews attended the site to investigate. Upon inspection, it was identified the LV conductor on the ground was live and caused by a fallen council tree. The fuse did not operate since there was insufficient fault current to trip the fuse. The site was isolated and made safe and the conductor was repaired. | 2 CHARLES STREET, MCCRAE VIC 3938 | 1309768 |  | Fallen;Council |  |  |  |  | 1 | UE was advised by MFB that a tree has caused wires to come down. | Conductor (bare) | 0 | 0 | 0 |  | DMA21 | Vegetation: Trees Incident | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43922.625 |  |  | 15010 | Roadway |  | 20200204UTD_03 | Infrastructure (network-based) | -38.349 | 144.9312 | 1 | United Energy Distribution | Report | 18968 | 0.04009 | Low voltage AC (<1kV) | Moorabbin Airport | 3938 | Mccrae | Trees
Fault crews and LEI attended the fault to investigate. Upon inspection, it was identified that the 66kV wooden cross-arm was rotten and during a heavy rain and strong wind event, the cross-arm broke and the conductor dropped on to the LV white phase below. LEI confirmed evidence of HVI. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 37 PATERSON ROAD, SPRINGVALE SOUTH VIC 3172 | 205374 |  | Precipitation;Wind |  | Rot |  |  | 1 | UE data analytics identified supply loss at multiple premises. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | SS-NP 66kV | during a heavy rain and strong wind event, a rotten cross-arm broke and dropped the conductor into the LV resulting in a HVI. | HV injection | 15/01/2020 20:05 |  |  | 15012 | Residential |  | 20200204UTD_05 | Infrastructure (network-based) | -37.9789 | 145.1519 | 1 | United Energy Distribution | Report | 18970 | 0.032965 | Low voltage AC (<1kV);66kV AC | Moorabbin Airport | 3172 | Springvale South | Crossarm
On arrival crew isolated supply and carried out repairs. | Bacchus Marsh Aerodrome, Cummings Rd, Parwan VIC 3340, Australia | 32177232 | Working too close to overhead lines | [6 empty] | Report received that an excavator working at the incident location has contacted overhead LV conductors. Supply has been lost to Aerodrome. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BMH006 | Excavator operations | Loss of supply;No Go Zone (contact) | 43781.4167 |  |  | 15031 | Roadway |  | 20200205PWA_03 | Infrastructure (network-based) | -37.7298 | 144.4293 | 1 | Powercor | Report | 18998 | 0.016058 | Low voltage AC (<1kV) | Avalon Airport | 3340 | Parwan | Vehicle
removed tree branch and replaced fuses , supply was restored | 453 BUFFALO RIVER ROAD, BUFFALO RIVER VIC 3737 | 4505857 |  | Within clearances | [5 empty] | tree branch fell on 22kV bare conductor. Ph-Ph fault. Ground fire | Conductor (bare) | 0 | 0 | 0 |  | myt22 | Vegetation: Trees Incident | Grassfire | 27/12/2019 0:08 | 1 | Medium: 1000 sq.m - 10 ha | 15029 |  |  | 20200205SPN_05 | Infrastructure (network-based) | -36.5898 | 146.698 | 1 | AusNet Services Distribution | Report | 18994 | 0.020206 | 22kV AC | Wangaratta Aero | 3737 | Buffalo River | Trees
On arrival crew isolated supply and carried out repairs | 1 Woodlea Cl, Strathfieldsaye VIC 3551, Australia | 32051730 | [7 empty] | Customer reported a large tree snapped in half now laying on conductors, wire sagging concerned wire could snap with weight, Crew found small ground fire roughly 1m2, where conductor had arced along the fence before the feeder dropped out There was a small ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | BGO013 | Vegetation: Trees Incident | Grassfire | 31/01/2020 14:47 | 1 | Localised: less than 10 sq.m | 15037 | Roadway |  | 20200206PWA_01 | Infrastructure (network-based) | -36.7949 | 144.3409 | 1 | Powercor | Notification | 19006 | 0.0029537 | 22kV AC | Bendigo Airport | 3551 | Strathfieldsaye | Trees
crew attended and dislodged | CLOVERSIDE, 575 POORNEET ROAD, WEERING VIC 3251 | 30052144 |  | Wind |  |  |  |  | 1 | The Powercor distribution network sustained damage to poles and conductor due to trees being dislodged and uprooted under severe localised wind conditions. A car reportedly contacted and became entangled a steel HV conductor in Poorneet Road, Weering. Ambulance Victoria confirmed that there had not been any injuries. | Conductor (bare) | 0 | 0 | 0 |  | CLC003 | Severe storm cell | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 31/01/2020 14:48 |  |  | 15041 | Roadway |  | 20200207PWA_01 | Infrastructure (network-based) | -38.0756 | 143.7179 | 1 | Powercor | Report | 19013 | 0.035749 | 22kV AC | Ballarat Aerodrome | 3251 | Weering | Trees
Attended site, isolated distribution supplies. CFA had placed 200 m exclusion zone around fallen towers. supplies restored through repairs or HV generator | 400 COLAC-BALLARAT ROAD, CRESSY VIC 3322 | 32065991 |  | Wind |  |  |  |  | 1 | Some 5-7 transmission towers have collapsed, a section of the transmission conductor fell across overhead distribution high voltage near to the section of underground cable crossing. The transmission conductor came to rest across road/s. | Conductor (bare) | 0 | 0 | 0 |  | CLC003 | Severe storm cell | Loss of supply;Significant disruption to the community | 31/01/2020 14:48 |  |  | 15043 | Roadway |  | 20200207PWA_03 | Infrastructure (network-based) | -37.9937 | 143.6582 | 1 | Powercor | Report | 19015 | 0.026596 | 22kV AC;500kV AC | Ballarat Aerodrome | 3322 | Cressy | AF Other
Isolated, made safe and carried out repairs. | 1640 GREAT ALPINE ROAD, SMOKO VIC 3741 | 4502036 | Vehicle | [6 empty] | Car into pole, caused conductor to fall creating grass fire. | Pole (wood) | 2 | 2 | 2 |  | BRT21 | Car crashed into pole. | Grassfire | 44014.6111 | 1 | Small: 10 - 1000 sq.m | 15056 |  |  | 20200207SPN_01 | Infrastructure (network-based) | -36.8277 | 147.0705 | 1 | AusNet Services Distribution | Report | 19029 | 0.0089884 | 22kV AC | Wangaratta Aero | 3741 | Smoko | Vehicle
Crew attended, assisted emergency services to clear tree and then repaired overhead line | 35 NOBLES ROAD, GNARWARRE VIC 3221 | 33104059 |  | Alive |  |  |  |  | 1 | Pine tree fell into during strong easterly wind, igniting trees and causing a small grass fire of approximately 10 by 6 metres. Some damage to 2 sections of farm fencing. No injuries | Conductor (bare) | 0 | 0 | 0 |  | WPD011 | Vegetation: Trees Incident | Grassfire | 44076.5292 | 1 | Small: 10 - 1000 sq.m | 15057 | Roadway |  | 20200210PWA_01 | Infrastructure (network-based) | -38.1528 | 144.1635 | 1 | Powercor | Notification | 19030 | 0.0062905 | 22kV AC | Avalon Airport | 3221 | Gnarwarre | Trees
Crew isolated the service cable and CFA extinguish the fire. | 2094 CURR ROAD, TONGALA VIC 3621 | 33089386 |  | Within clearances | [5 empty] | Customer rang to reported ground fire start at the incident address, A crew attended and found a customers tree had rubbed through the 2W grey service cable from pole to house. This resulted in the service breaking and falling to the ground starting a grass fire. Area burnt estimated at 160m2 ( 4mx40m ), There was no reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | KYM004 | Vegetation: Trees Incident | Grassfire | 43984.4306 | 1 | Small: 10 - 1000 sq.m | 15059 | Residential |  | 20200210PWA_03 | Infrastructure (customer connection) | -36.2542 | 144.9814 | 1 | Powercor | Report | 19034 | 2.4306e-05 | Low voltage AC (<1kV) | Shepparton Airport | 3621 | Tongala | Trees
Site made safe. Crew repaired damage to conduit. | 131-135 FITZGERALD ROAD, LAVERTON NORTH VIC 3026 | 30224015 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | 'Multipipe Contractors' installing conduits damaged Powercor HV underground cable conduit. Crew supplied photos and reported damage to our HV conduits in Dohertys Road by 'Multipipe' working for Winslow. | Cable | 0 | 0 | 0 |  | LVN023 | Contractors installing new conduits contacted and damaged Powercor conduit. | No Go Zone (contact) | 19/11/2019 14:14 |  |  | 15067 | Roadway |  | 20200211PWA_03 | Infrastructure (network-based) | -37.8274 | 144.7854 | 1 | Powercor | Report | 19044 | 0.034814 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Dug up
On arrival crew isolated supply and carried out repairs. | 183 Belar Ave Ext, Red Cliffs VIC 3496, Australia | 32148522 |  |  |  | Leakage |  |  |  | Crew investigated area fault, on arrival found 2 poles consecutive poles that had cross arms burnt. HV wire down. CFA in attendance There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire | 44076.3153 | 1 | Negligible: no ground fire | 15070 | Agricultural |  | 20200211PWA_05 | Infrastructure (network-based) | -34.2758 | 142.1759 | 1 | Powercor | Report | 19416 | 0.021247 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
The crew rejoined the LV earth. | 337 FITZGERALD ROAD, DERRIMUT VIC 3026 | 33105630 | Working too close to underground cables | [5 empty] | 2 | An excavator had hit an earth stake to the pole at the incident location. On arrival the crew found that the excavator had cut the LV earth to Fitzgerald-Kenworth Substation. | Earth/earthing | 0 | 0 | 0 |  | SU035 | No Go Zone infringement | Damage to network assets | 44137.4979 |  |  | 15076 | Industrial |  | 20200211PWA_10 | Infrastructure (network-based) | -37.8068 | 144.788 | 1 | Powercor | Report | 19055 | 0.022964 | Earthing cable | Laverton Raaf | 3026 | Derrimut | Dug up
The crew made the site safe, replaced the pit lid and submitted a Fault Follow Up to have the cable checked and re-tested. | 53 IVANHOE AVENUE, ST ALBANS VIC 3021 | 31022683 | Copper theft | [5 empty] | 2 | Customer calling to advise that pit which was installed at the start of December appears to have been vandalized. The lid was removed and wires exposed. | Cable | 0 | 0 | 0 |  | SA007 | Attempted copper theft | Damage to network assets | 16/12/2019 16:40 |  |  | 15078 | Roadway |  | 20200211PWA_12 | Infrastructure (network-based) | -37.7418 | 144.8141 | 1 | Powercor | Report | 19057 | 0.03058 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Other
Crews attended, isolated supply and performed repairs. | RIFLE RANGE ROAD, GELLIBRAND VIC 3239 | 32064625 | Working too close to overhead lines | [5 empty] | 1 | A Powercor crew attending a feeder fault found that a tree had been brought down and contacted condcutor. This occurred on the edge of an area of active fire and likely associated with fire suppression activities. There were no injures or fire caused by the contact . As this was an area of active bushfire with very limited access available. It is unknown if tree was cut, pushed or fell due to fire damage. Priority was to support fire supression efforts and restoration of supply to Carlisle River township and surrounds. see addittional information | Conductor (bare) | 0 | 0 | 0 |  | CLC006 | Vegetation: Trees Incident | Damage to network assets | 16/01/2020 8:08 |  |  | 15083 | Forest - plantation |  | 20200211PWA_17 | Infrastructure (network-based) | -38.5445 | 143.5156 | 1 | Powercor | Report | 19464 | 0.013089 | 22kV AC | Ballarat Aerodrome | 3239 | Gellibrand | Trees
Crews attended, isolated the supply, and made repairs. | 19 LAMBERT STREET, ARARAT VIC 3377 | 30233775 |  | Within clearances |  |  |  |  | 1 | On arrival the crew found that a large tree had caused the white and blue phase OH LV .064 copper cables to clash together during strong winds. The clashing resulted in the LV conductors falling to the ground alive, on the bitumen road. There were only minor scorch marks on the bitumen from the downed cables. | Conductor (bare) | 0 | 0 | 0 |  | ART034 | Vegetation: Trees Incident | Damage to network assets | 22/01/2020 14:00 |  |  | 15090 | Roadway |  | 20200211PWA_19 | Infrastructure (network-based) | -37.2814 | 142.9262 | 1 | Powercor | Report | 19070 | 0.010897 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3377 | Ararat | Trees
Sent fault crew to make safe, investigate and repair. Crews replaced 3 ph FMB with Krone Box after box melted and leads burnt. | 2G-2H AKUNA AVENUE, TALLANGATTA VIC 3700 | 5218563 |  |  |  | Unknown due to the amount of damage;Other |  |  | 2 | Pole top fire reported. | Disconnector/isolator;Connection box | 0 | 0 | 0 |  | WOTS13 | 3 phase FOLCB caught fire at Akuna Ave Tallangatta. damage to box and overhead service wire. not able to determine cause of fault due to damage | Pole-top fire | 43862.2458 | 1 | Negligible: no ground fire | 15066 | Public space |  | 20200211SPN_03 | Infrastructure (network-based) | -36.2176 | 147.1746 | 1 | AusNet Services Distribution | Report | 19045 | 0.022869 | Low voltage AC (<1kV) | Wangaratta Aero | 3700 | Tallangatta | Connection
Sent Electrical Inspector to make safe, investigate and organise repairs. FOLCB was replaced and loose connection was repaired. | 11 NAUTILUS ROAD, INVERLOCH VIC 3996 | 2809807 |  |  |  | Age;Neutral fault |  |  |  | Report of electric shock. Customer received tingles from bathroom tap. This is due to loose connection on the incoming twisted 2 wire overhead service to the neutral link at the FOLCB. | Aluminium twisted (XLPE) | 0 | 0 | 0 |  | WGI24 | Loose neutral connection at the FOLCB. | Minor shock | 24/12/2019 11:10 |  |  | 15075 | Residential |  | 20200211SPN_05 | Infrastructure (network-based) | -38.6316 | 145.7373 | 1 | AusNet Services Distribution | Report | 19058 | 0.028078 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Connection
Crew removed hazards, organized repairs and made site safe. | 61 MURPHYS ROAD, PIPERS CREEK VIC 3444 | 32044497 |  | Fallen;Property owner/customer |  |  |  |  | 1 | Crew on line patrol from fault current detected previous evening found SWER line broken between Aldous pole 1 and 1A. A large tree branch had fallen on the conductor and broken it. Crew found that protection had operated. Crew advised that tree base is approx. 15m from conductor. No fire was found at impact location. No injuries or third party damage. | Conductor (bare) | 0 | 0 | 0 |  | WND023 | Vegetation: Trees Incident | Damage to network assets | 44014.9972 |  |  | 15092 | Agricultural |  | 20200212PWA_02 | Infrastructure (network-based) | -37.2532 | 144.4974 | 1 | Powercor | Report | 19072 | 0.0066644 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3444 | Pipers Creek | Trees
Crew removed hazards, organized repairs and made site safe. | 14 EDNA STREET, SUNSHINE NORTH VIC 3020 | 30115549 |  | Within clearances |  |  |  |  | 1 | A customer reported a wire on the driveway and their vehicle driven over it accidently and the wire end found sparking at the incident location. Upon arrival, a Powercor crew found that the service had been rubbing a tree and fell on to ground. Then the vehicle driven over. There was no fire or injuries. The supply isolated. The service to be installed. | Service cable (insulated) | 0 | 0 | 0 |  | SSE032 | Vegetation: Trees Incident | Damage to network assets | 20/01/2020 13:30 |  |  | 15094 | Residential |  | 20200212PWA_04 | Infrastructure (network-based) | -37.7716 | 144.8404 | 1 | Powercor | Report | 19074 | 0.0073692 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine North | Trees
UNDER INVESTIGATION | 60 BELLS ROAD, CLYDE VIC 3978 | 508612 | [7 empty] | Machinery contact with HV | Conductor (bare) | 0 | 0 | 0 |  | CLN22 | Machinery contact with HV | Damage to network assets | 44137.9521 |  |  | 15106 |  |  | 20200212SPN_04 | Infrastructure (network-based) | -38.1232 | 145.3648 | 2 | AusNet Services Distribution | Notification | 19088 | 0.032773 | 22kV AC | Moorabbin Airport | 3978 | Clyde | Vehicle
Fault crews attended the site to investigate and was advised by the customer that they received a slight tingle on the bathroom taps and kitchen taps. LEI attended the site and recorded 16.1V at the taps. Fault crews isolated the supply and identified a loose neutral connection at the POA. The connection was repaired and NST passed. Supply was left on. | 41 JEAN STREET, CHELTENHAM VIC 3192 | 1822535 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE data analytics identified abnormal voltage behavior. | POA connection (network side) | 0 | 0 | 0 |  | M23 | The cause was a loose neutral connection at the POA | Minor shock | 43720.1875 |  |  | 15098 | Residential |  | 20200212UTD_01 | Infrastructure (network-based) | -37.9597 | 145.0504 | 1 | United Energy Distribution | Report | 19078 | 0.038627 | Low voltage AC (<1kV) | Moorabbin Airport | 3192 | Cheltenham | Connection
Fault crews attended the site to investigate. Upon inspection, it was identified a tree branch fell on to the HV and LV conductors. LEI attended the site and confirmed evidence of HVI. The site was isolated and made safe. Fault crews repaired the conductors and supply was restored. | 15 BANGALAY AVENUE, FRANKSTON SOUTH VIC 3199 | 3311462 |  | Fallen |  |  |  |  | 1 | UE received a call that the meter was blown up and the fuse was blown off the switchboard. | Conductor (bare) | 0 | 0 | 0 |  | FSH13 | Vegetation: Trees Incident | HV injection | 31/01/2020 20:00 |  |  | 15100 | Roadway |  | 20200212UTD_03 | Infrastructure (network-based) | -38.1701 | 145.118 | 1 | United Energy Distribution | Report | 19080 | 0.034627 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3199 | Frankston South | Trees
Crews attended, isolated supply and performed repairs. | 104 STATION ROAD, GISBORNE VIC 3437 | 30338651 | Copper theft | [5 empty] | 2 | A company employee reported a copper theft at the incident location. He also mentioned that the same nature of theft took place days ago at the same place. This time 500m of street light cables were taken away. The crew made the place safe and repairs have been arranged. | Cable | 0 | 0 | 0 |  | GSB013 | Copper theft | Damage to network assets | 24/12/2019 8:14 |  |  | 15119 | Roadway |  | 20200214PWA_03 | Infrastructure (network-based) | -37.4732 | 144.5946 | 1 | Powercor | Report | 19105 | 0.034566 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
Crews attended, isolated supply and performed repairs. | ROMSEY ROAD, WOODEND VIC 3442 | 30319279 | Copper theft | [5 empty] | 2 | Copper thefts from three poles on the Romsey Road corner of Coach Road. | Cable | 0 | 0 | 0 |  | WND012 | copper theft | Damage to network assets | 31/12/2019 3:52 |  |  | 15121 | Roadway |  | 20200214PWA_05 | Infrastructure (network-based) | -37.3435 | 144.5849 | 1 | Powercor | Report | 19213 | 0.012566 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Other
Tipper Truck hit SWER line. Crew issued permit to remove truck and make safe, No injuries reported. Construction crew resagged the conductor according to standards. Before this incident, no notification was raised in SAP of low conductor so assumption is that clearance was satisfactory. An investigating officer was not sent to site after this incident to measure the clearances. We will raise this issue internally and ensure a DAO (duty availability officer) is sent out every time for such incidents to carry out a proper investigation. | 20 GRANITE LANE, TYNONG VIC 3813 | 510558 | Working too close to overhead lines | [6 empty] | Tipper truck made contact with HV. No injuries. Site made safe and appropriate repairs carried out by construction crew. | Conductor (bare) | 0 | 0 | 0 |  | PHM33 | Tipper truck working too close to line. | No Go Zone (contact) | 13/02/2020 10:43 |  |  | 15111 |  |  | 20200214SPN_01 | Infrastructure (network-based) | -38.072 | 145.6288 | 1 | AusNet Services Distribution | Report | 19096 | 0.024574 | 12.7kV AC (SWER) | Moorabbin Airport | 3813 | Tynong | Vehicle
On arrival crew found the fire extinguished. No damage to assets. | 19 Deavey Ct, Altona VIC 3018, Australia | 33073532 | Recreation - Helium (party) balloons | [6 empty] | MFB reported Sparking wires at end of Jordan Close, Altona. Fire is out in a paddock. On arrival the crew found that metallic balloons had caused a flashover at the incident location. There was a 5 sq metre fire in the paddock. MFB attended. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | ALA006 | Metalic balloon caused flashover | Grassfire | 13/02/2020 20:31 | 1 | Localised: less than 10 sq.m | 15126 | Public space |  | 20200217PWA_01 | Infrastructure (network-based) | -37.8562 | 144.8167 | 1 | Powercor | Report | 19112 | 0.029954 | 22kV AC | Laverton Raaf | 3018 | Altona | Other
Crew attended and replaced connection box | 625 TARNEIT ROAD, HOPPERS CROSSING VIC 3029 | 30105138 |  |  |  | Corrosion |  |  | 2 | Person received minor shocks from water taps at premises | Service cable (insulated) | 0 | 0 | 0 |  | WBE023 | corroded connection at pole connection box | Minor shock | 43534.4375 |  |  | 15131 | Residential |  | 20200217PWA_04 | Infrastructure (network-based) | -37.8533 | 144.6684 | 1 | Powercor | Report | 19119 | 0.0041771 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Connection
Crew replaced servcie | 56 BOYD AVENUE, MOGGS CREEK VIC 3231 | 30068832 |  |  |  | Corrosion |  |  | 2 | person as outside rinsing his Wet-suit at the External Tap located directly below the Meter Enclosure when he received an electric shock as he made simultaneous contact with his hand on the metal Tap and his bare feet whilst standing on the wet ground. | Service cable (insulated) | 0 | 0 | 0 |  | WPD014 | Corroded service connection | Minor shock | 43809.5833 |  |  | 15136 |  |  | 20200217PWA_06 | Infrastructure (network-based) | -38.4634 | 144.0671 | 1 | Powercor | Report | 19126 | 0.0026979 | Low voltage AC (<1kV) | Avalon Airport | 3231 | Moggs Creek | Connection
Faults crew undertook NST testing at the meter which failed. They identified the fault as poorly made IPC neutral connection in the pit. They remade the connection in the pit and repeated NST testing which passed. At the time of CTA arrival the faults truck had rectified the issue. The faults truck and CTA arranged for the meter to be re-connected and put back on supply. Testing was carried out using an independent earth to the customers plumbing and voltage measured was <0.5V. Faults crew remade the IPC connections in the pit, tested and left on supply | 6 FORDE AVENUE, MELTON SOUTH VIC 3338 | 60311210 |  |  |  | Corrosion |  | Phase to earth |  | Meter Insights program identified a neutral impedance issue at a property. Upon contacting the customer (Mohommad and Sadia) Sadia reported receiving what they thought were static shocks from their bathroom taps. | Services cable;Connector/termination | 2 | 2 | 2 |  | MLN011 | IPC connection failed at pit | Minor shock | 43747 |  |  | 15140 | Roadway |  | 20200217PWA_09 | Infrastructure (customer connection) | -37.7132 | 144.5619 | 1 | Powercor | Report | 19130 | 0.019058 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Connection
Crew attended and replaced service | 406 LANDSBOROUGH STREET, BALLARAT NORTH VIC 3350 | 30261918 |  |  |  | Corrosion |  |  |  | Registered Electrical Contractor was engaged to carry out testing of the electrical installation at 406 Landsborough Street Ballarat North following reports by the customer of issues within the electrical installation. Mr Blenkiron was in the Kitchen when he received an electric shock as he made simultaneous contact with his hand on the Kitchen Tap and his arm in contact with the metallic Kitchen Sink. | Service cable (insulated) | 0 | 0 | 0 |  | BAN015 | corroded connection on Servcieat pole | Minor shock | 25/10/2019 9:00 |  |  | 15141 | Residential |  | 20200217PWA_10 | Infrastructure (network-based) | -37.5401 | 143.8666 | 1 | Powercor | Report | 19132 | 0.029139 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat North | Connection
Voltage tests between an independent earth at the points of contact and various points of the electrical installation, including distribution assets, revealed a corroded neutral conductor at the pole end. This condition caused current to flow through the MEN connection and main earthing conductor PCA fault truck removed and replaced the existing service cable connection at pole end. CTA completed required VESI tests | 22 WOODLAND DRIVE, ALBANVALE VIC 3021 | 30120292 |  |  |  | Corrosion |  | Phase to earth |  | Nina received an electric shock when she made simultaneous contact between the metallic taps with her hands and the shower waste and floor with her feet. | Service cable (insulated) | 2 | 2 | 2 |  | SSE031 | corroded neutral conductor at the pole end | Minor shock | 26/09/2019 7:30 |  |  | 15154 | Roadway |  | 20200218PWA_02 | Infrastructure (customer connection) | -37.7457 | 144.7667 | 1 | Powercor | Report | 19149 | 0.0055521 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Albanvale | Connection
Fault crews attended the site to investigate. Upon inspection, it was identified that a burnt out IPC from a pole substation has fallen onto the ground and started a small grass fire which was put out by a passerby. The site was isolated and made safe. The crews repaired the connection and supply was restored. UE was advised the IPC first contacted and damaged the bonnet of a vehicle parked under the pole substation which was gone by the time the crews arrived. Subsequent claim was received by UE in January 2020. | 129 MOUNT ELIZA WAY, MOUNT ELIZA VIC 3930 | 3313700 |  |  |  | Overheated connection |  |  | 1 | UE received calls that customers have experienced loss of supply and an object has dropped to the ground. | Connector/termination | 0 | 0 | 0 |  | FSH12 | the cause was a burnt out IPC dropping to the ground. | Grassfire | 20/12/2019 17:45 | 1 | Localised: less than 10 sq.m | 15148 | Roadway |  | 20200218UTD_01 | Infrastructure (network-based) | -38.1865 | 145.0898 | 1 | United Energy Distribution | Report | 19142 | 0.0092187 | Low voltage AC (<1kV) | Moorabbin Airport | 3930 | Mount Eliza | Connection
Fault crews attended the site to investigate. Upon inspection, it was identified that a large branch from a council tree broke and fell onto the HV. The debris was removed from the site. | 1 WARROCK AVENUE, DONVALE VIC 3111 | 7067545 |  | Fallen;Council |  |  |  |  | 1 | UE received a call that the wires contacting a tree are sparking and on fire. | Conductor (bare) | 0 | 0 | 0 |  | NW13 | Vegetation: Trees Incident | Other vegetation | 13/02/2020 14:12 | 1 | Localised: less than 10 sq.m | 15158 | Roadway |  | 20200218UTD_03 | Infrastructure (network-based) | -37.7983 | 145.1846 | 1 | United Energy Distribution | Report | 19153 | 0.008147 | 22kV AC | Moorabbin Airport | 3111 | Donvale | Trees
fault crew attended and isolated supply | 4 MYVORE COURT, TOORAK VIC 3142 | 30298407 |  |  |  | Moisture ingress |  |  | 2 | contractor received minor electric shock when he was excavating around base of pole to repair/ replace stolen service cable. | Services cable | 0 | 0 | 0 |  | AR003 | Under investigation | Medical attention (first aid/doctor/hospital) | 44167.3611 |  |  | 15164 | Roadway |  | 20200219PWA_01 | Infrastructure (network-based) | -37.846 | 145.0299 | 1 | CitiPower | Report | 19164 | 0.038037 | Low voltage AC (<1kV) | Moorabbin Airport | 3142 | Toorak | Other
The attending Powercor Fault Crew and REC completed a visual inspection and identified a corroded O/H Service Neutral Conductor termination at the FOLCB located at the Customer's POA, causing a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew disconnected and removed the deteriorated O/H Neutral Screened Service Cable from the Reticulation Pole and the POA following the Owner advising the building was infested with Termites and was scheduled to be demolished. | THE PEPPERS, 1008 NULLAWIL SOUTH ROAD, NULLAWIL VIC 3529 |  |  |  |  | Corrosion |  | Phase to earth |  | Mr David Watts was outside when he received an electric shock as he made simultaneous contact with his hand on the metal Downpipe and his feet whilst standing on the the general mass of earth. | POA connection (network side) | 2 | 2 | 2 |  |  | Corroded connection | Minor shock | 16/08/2019 19:00 |  |  | 15176 | Residential |  | 20200224PWA_04 | Infrastructure (customer connection) | -35.875 | 143.1737 | 1 | Powercor | Report | 19183 | 0.016334 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3529 | Nullawil | Connection
Crew replaced the BA fuse and restored supply | 280 COULTERS ROAD, MARDAN VIC 3953 | 2010360 |  |  |  | Candled fuse |  |  |  | Candled fuse 6K BA | Boric acid | 0 | 0 | 0 |  | lga13 | Candled fuse | Pole-top fire | 15/02/2020 13:45 | 1 | Negligible: no ground fire | 15193 |  |  | 20200225SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19209 | 0.031874 | 22kV AC | Moorabbin Airport | 3953 | Mardan | Fuse
TBA | 52 WHEELBARROW ROAD, TRAFALGAR VIC 3824 | LIS 2203072 |  |  |  | Candled fuse |  |  |  | Candled fuse | Any other type | 0 | 0 | 0 |  | MOE22 | candled fuse | Pole-top fire | 25/02/2020 14:34 | 1 | Negligible: no ground fire | 15195 |  |  | 20200225SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19215 | 0.022552 | 22kV AC | Moorabbin Airport | 3824 | Trafalgar | Fuse
Upon inspection, it was identified that the gas switch was hit by lightning and the HV conductor dropped into the LV. LEI attended the site and confirmed evidence of HVI. Gas switch was replaced and supply was restored. | 33 ST GEORGES CRESCENT, ASHBURTON VIC 3147 | 2316042 |  | Lightning |  |  |  |  | 1 | UE 11kV feeder protection operated and fault crews patrolled the feeder. | Conductor (bare);Any other type | 0 | 0 | 0 |  | EM08 | The cause is lightning hitting the switch and the HV conductor dropping into the LV. | HV injection | 14/02/2020 14:20 |  |  | 15210 | Roadway |  | 20200226UTD_03 | Infrastructure (network-based) | -37.8704 | 145.0721 | 1 | United Energy Distribution | Report | 19234 | 0.001691 | 11kV AC | Moorabbin Airport | 3147 | Ashburton | Lightning
Tree has fallen onto HV conductors. Inspector attended and confirmed HVI effecting customer's appliances and damaged meters. Tree removed and conductor repaired. | 10 WILLOW DRIVE, WANGARATTA VIC 3677 | 5107183 |  | Fallen | [5 empty] | Tree falling onto line resulting in HV Injection. Damage to customers' meters and appliances. | Conductor (bare) | 0 | 0 | 0 |  | WN4 | Vegetation: Trees Incident | HV injection | 27/02/2020 11:22 |  |  | 15212 | Residential |  | 20200227SPN_01 | Infrastructure (network-based) | -36.3471 | 146.2919 | 1 | AusNet Services Distribution | Report | 19238 | 0.017529 | Low voltage AC (<1kV);22kV AC | Wangaratta Aero | 3677 | Wangaratta | Trees
crew attended and replaced service cable | 480 TURRONG ROAD, COORIEMUNGLE VIC 3268 | 30566202 | Crane, excavator or other construction/farming equipment | [5 empty] | 2 | REC reported OH line has been brought down, he isnt on site and unsure how happened. Attending crew were advised that a tractor with hay on forks had bought down service line from pole in road to house. | Service cable (insulated) | 0 | 0 | 0 |  | COB011 | Tractor driver was not aware of service line | Damage to network assets | 27/02/2020 15:11 |  |  | 15217 | Agricultural |  | 20200228PWA_01 | Infrastructure (network-based) | -38.5744 | 143.1575 | 1 | Powercor | Report | 19246 | 0.015331 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Cooriemungle | Vehicle
On arrival crew isolated supply and removed tree branch from line | 3571 Murray Valley Hwy, Wood Wood VIC 3596, Australia | 32157058 | [7 empty] | Vic Roads reported tree branch falling on main power lines at incident location, heard a loud bang before noticing branch on wire and arcing causing a small fire which has been extinguished, no ground fire, no injuries, no property damage. | Conductor (bare) | 2 | 2 | 2 |  | SHL002 | To be established | Other vegetation | 15/01/2020 14:51 | 1 | Negligible: no ground fire | 15237 | Roadway |  | 20200302PWA_05 | Infrastructure (network-based) | -35.1036 | 143.3458 | 1 | Powercor | Notification | 19275 | 0.01898 | 22kV AC | Swan Hill Aerodrome | 3571 | Wood Wood | Trees
Crew re-terminated the O/H Service | 5 GOODWIN COURT, CORIO VIC 3214 | 33042515 |  |  |  | Corrosion |  |  |  | Person was in the bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal shower head and her bare feet while standing on the wet shower base. | Service cable (insulated) | 0 | 0 | 0 |  | FNS012 | Loose / corroded neutral connection/s | Minor shock | 43535.7917 |  |  | 15238 | Residential |  | 20200302PWA_06 | Infrastructure (network-based) | -38.0641 | 144.3777 | 1 | Powercor | Report | 19277 | 0.0072419 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Connection
Not immediately unsafe, referred to ESV for site visit | 21 WYNYARD CRESCENT, BALWYN NORTH VIC 3104 | 75084430 | Working too close to overhead lines | [5 empty] | 2 | Employee responding to No go Zone request found scaffolding erected without permit to work. scaffolding was in close vicinity to LV service at POA. visual warning (tiger tails) and LV matting present on service however not arranged through no go Zone | Service cable (insulated) | 0 | 0 | 0 |  | WD013 | Interference | No Go Zone (contact) | 43893.4132 |  |  | 15248 | Residential |  | 20200303PWA_06 | Infrastructure (customer connection) | -37.8034 | 145.0942 | 1 | CitiPower | Report | 19287 | 0.02228 | Low voltage AC (<1kV) | Moorabbin Airport | 3104 | Balwyn North | Other
service replaced by Powercor Faults crew | 27 ANNE ROAD, WOODEND VIC 3442 | 30035933 |  |  |  | Corrosion |  |  |  | Plumber was under the house investigating a gas leak he received an electric shock when he made simultaneous contact with the metallic gas pipe and the damp soil with his hands. | Service cable (insulated) | 0 | 0 | 0 |  | WND022 | Corroded existing Neutral Conductor connection at pole end. | Minor shock | 20/11/2019 13:00 |  |  | 15251 | Residential |  | 20200303PWA_08 | Infrastructure (network-based) | -37.3519 | 144.5398 | 1 | Powercor | Report | 19291 | 0.032422 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Woodend | Connection
Fault/Storm response crews repaired the damaged BN-MSD 66kV line and the BN6 22kV feeder. | 232 MANSFIELD ROAD, BENALLA VIC 3672 | 3906619 |  | Wind;Fallen | [5 empty] | Report of fire near assets. Upon arrival onsite a tree limb was found resting on ground between pole 3906619 and 3906620. Beneath the tree limb were the 66/22kV conductors (some broken), at the edge of the burnt area. Damage was also sustained to the 66/22kV structures at poles 3906619, 3906620 and 3906680. Refer to the attached site photos. This incident was initially incorreclty identified as non-reportable incident, hence the late Osiris reporting. ESV was notified via Call Ref 13303804. | Conductor (bare) | 0 | 0 | 0 |  | BN-MSD 66kV | Vegetation: Trees Incident | Grassfire | 43832.8243 | 1 | Medium: 1000 sq.m - 10 ha | 15249 | Residential |  | 20200303SPN_01 | Infrastructure (network-based) | -36.5743 | 145.9605 | 1 | AusNet Services Distribution | Report | 19290 | 0.030188 | 22kV AC;66kV AC | Wangaratta Aero | 3672 | Benalla | Trees
crew attended, cleared conductor and restored line | 42-100 MCLEANS HIGHWAY, STAUGHTON VALE VIC 3340 | 30252610 |  | Fallen |  |  |  |  | 1 | Powercor received advice of wire broken and limited power. Attending crew found that tree had failed at ground level and brought down one HV conductor. Small ground fire had self extinguished. Residents had not been in attendance recently so it unknown when fire occurred | Conductor (bare) | 0 | 0 | 0 |  | CRO013 | Vegetation: Trees Incident | Grassfire | 43893.6042 | 1 | Small: 10 - 1000 sq.m | 15257 | Agricultural |  | 20200304PWA_01 | Infrastructure (network-based) | -37.8415 | 144.2775 | 1 | Powercor | Notification | 19300 | 0.032649 | 22kV AC | Avalon Airport | 3340 | Staughton Vale | Trees
Upon inspection, it was identified that the wooden cross-arm was burnt. ESV was notified, ref #13151298. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 2215-2221 DANDENONG ROAD, MULGRAVE VIC 3170 | 620496 |  |  |  | Leakage |  |  | 1 | UE 22kV feeder protection operated and fault crews patrolled the feeder and found a pole top fire. | Crossarm (wood) | 0 | 0 | 0 |  | SVW45 | The cause of the fire was tracking across the insulator. | Pole-top fire | 44105.691 | 1 | Negligible: no ground fire | 15262 | Roadway |  | 20200304UTD_03 | Infrastructure (network-based) | -37.9274 | 145.1486 | 1 | United Energy Distribution | Report | 19318 | 0.021304 | 22kV AC | Moorabbin Airport | 3170 | Mulgrave | AF Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was damaged near the POA. The site was isolated and made safe. The service wire was repaired and supply was restored. | 17 LANG STREET, BEAUMARIS VIC 3193 | 1811367 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a customer has cut his service wire while gardening and has part supply. | Service cable (insulated) | 0 | 0 | 0 |  | BR9 | The customer was working too close to the service line. | Loss of supply;No Go Zone (contact) | 24/02/2020 13:55 |  |  | 15263 | Residential |  | 20200304UTD_04 | Infrastructure (network-based) | -37.99 | 145.0307 | 1 | United Energy Distribution | Report | 19307 | 0.01366 | Low voltage AC (<1kV) | Moorabbin Airport | 3193 | Beaumaris | Other
Crew inspected conductor for damage, no damage found, line returned to service. | Sunraysia Hwy, Birchip VIC 3483, Australia | 32016632 | Working too close to overhead lines | [6 empty] | Report of Trucks trailer has come into contact with Power lines. Police attended and instructed driver who reported receiving a shock to go for medical review and get truck inspected. There was no fire. | Conductor (bare) | 2 | 2 | 2 |  | CTN001 | Tipper contacted overhead conductors | Minor shock (unconfirmed);No Go Zone (contact) | 43893.4674 |  |  | 15269 | Roadway |  | 20200305PWA_02 | Infrastructure (network-based) | -35.9986 | 142.9113 | 1 | Powercor | Report | 19314 | 0.01892 | 22kV AC | Swan Hill Aerodrome | 3483 | Birchip | Vehicle
On arrival crew isolated supply and carried out repairs | 69-91 KAURI STREET, RED CLIFFS VIC 3496 | 31020020 |  |  |  | Leakage |  |  |  | A customer reported a cross-arm fire at the incident location. On arrival the crew found that the HV cross-arm on Kauri Coorong P4 (LIS-4796) had burnt in half at the kingbolt, causing the two halves to fall onto the LV cross-arm below. There were no reported ground fires, HVI or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 43924.3681 | 1 | Negligible: no ground fire | 15271 | Roadway |  | 20200305PWA_04 | Infrastructure (network-based) | -34.3045 | 142.185 | 1 | Powercor | Report | 19316 | 0.00092245 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Crews repaired the broken / damaged conductors | 412 Carrs Rd, Anakie VIC 3213, Australia | 30312074 | Working too close to overhead lines | [6 empty] | Powercor received a call from Vic Fire advising of wires down and a fire start at the incident address. When crews arrived they found an excavator being driven on the property had contacted the HV overhead conductor resulting in conductor damage to all three phases and a 20m x 30m grass / paddock fire. No shock or injuries were experienced by the excavator operator who is also the property owner. | Conductor (bare) | 2 | 2 | 2 |  | CRO013 | Excavator struck overhead conductors | Grassfire;No Go Zone (contact);Damage to network assets | 44046.5646 | 1 | Small: 10 - 1000 sq.m | 15282 | Agricultural |  | 20200310PWA_02 | Infrastructure (network-based) | -37.9679 | 144.3008 | 1 | Powercor | Notification | 19336 | 0.0087431 | 22kV AC | Avalon Airport | 3213 | Anakie | Vehicle
Fault crew sent to make safe, investigate and orgainse repairs. Poor connection on the customer's air conditioner. Isolated faulty circuit to air con unit. Customer advised. | 24 BUNYA DRIVE, CAPE WOOLAMAI VIC 3925 | 2812760 |  |  |  | Unidentified customer fault |  |  |  | Customer received an electric shock from garden tap. Poor connection on the customer's air conditioner. Customer advised. | Customer appliance;Other customer electrical equipment | 0 | 0 | 0 |  | WGI32 | Poor connection on the customer's air conditioner. Customer advised. | Minor shock | 43658.6188 |  |  | 15284 |  |  | 20200310SPN_02 | Infrastructure (customer connection) | -38.5213 | 145.3449 | 1 | AusNet Services Transmission | Notification | 19339 | 0.029152 | Low voltage AC (<1kV) | Moorabbin Airport | 3925 | Cape Woolamai | Installation
powercor is investigating rectification options | OAONUI, 1887 MURRAY VALLEY HIGHWAY, BOOSEY VIC 3730 | 30123399 | Working too close to underground cables | [6 empty] | Site investigation was conducted to check cover of LV underground cable after recent roadworks. Crew found that drain had changed cover from some 950mm to 350mm over LV cable. | Cable | 0 | 0 | 0 |  | CME014 | Proximity of civil works in roadway | No Go Zone (no contact) | 13/02/2020 15:33 |  |  | 15295 | Roadway |  | 20200312PWA_02 | Infrastructure (network-based) | -35.9984 | 145.8109 | 1 | Powercor | Report | 19360 | 0.0093125 | Low voltage AC (<1kV) | Shepparton Airport | 3730 | Boosey | Dug up
On arrival crew removed limb and replaced service line. | 30 Howard St, Epsom VIC 3551, Australia | 30286376 |  | Blown branch/vegetation | [5 empty] | Police reported tree branch has detached, resting on Mains Wires, Mains Wires are sparking, unsure if supply affected, sparks falling to the ground. On arrival crew found tree branch had detached and fallen on low voltage conductors and service wire causing arcing and sparking. There was no fire, no reported injuries or third party property damage. | Conductor (bare);Service cable (insulated) | 2 | 2 | 2 |  | EHK033 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43924.7639 |  |  | 15299 | Roadway |  | 20200313PWA_02 | Infrastructure (network-based) | -36.7054 | 144.319 | 1 | Powercor | Report | 19365 | 0.016333 | Low voltage AC (<1kV) | Bendigo Airport | 3551 | Epsom | Trees
On arrival crew isolated supply and carried out repairs. LEI attended to test for HVI - non found | 469 BRUNSWICK ROAD, BRUNSWICK WEST VIC 3055 | 30159559 |  |  |  | Leakage |  |  |  | Customer reporting pole sparking and glowing bright red, coming from the top of the pole. He also thinks xarm is broken. On arrival, faults crew found that a HV cross arm on pole no 46899 had burnt through. There was suspected HVI, test by LEI found no evidence of HVI. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WB013 | Excessive leakage current | Pole-top fire | 13/03/2020 20:39 | 1 | Negligible: no ground fire | 15307 | Roadway |  | 20200316PWA_02 | Infrastructure (network-based) | -37.7751 | 144.944 | 1 | CitiPower | Report | 19377 | 0.0031389 | 6.6kV AC | Essendon Airport | 3055 | Brunswick West | Crossarm
Crews attended, isolated supply, made the site safe and performed repairs. | 8559 PRINCES HIGHWAY, PANMURE VIC 3265 | 32058973 |  |  |  | Overheated connection |  |  |  | A customer called to advise that what he described as a "capacitor" had caught fire on his meter board. On arrival the crew found that one of the meter board fuses had overheated causing minor damage to the wooden meter board. There was no ground fire, no reported injuries or third party property damage. | Meter board (including fuses) | 2 | 2 | 2 |  | TRG004 | connection failure | Meter board | 14/03/2020 13:18 | 1 | Negligible: no ground fire | 15309 | Residential |  | 20200316PWA_04 | Infrastructure (network-based) | -38.3169 | 142.7468 | 1 | Powercor | Report | 19645 | 0.021424 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3265 | Panmure | Installation
25E BA was blown at spur fuse feeding the fault. Site was isolated and made safe. Fire controllled by crew. Refer to attached site photos. | 264 SOUTH MOUNTAIN ROAD, UPPER PLENTY VIC 3756 | 912330 |  | Fallen |  |  |  |  | 1 | Tree brought down line and a fire was found by crew near assets. | Conductor (bare) | 0 | 0 | 0 |  | KLO14 | Vegetation: Trees Incident | Grassfire | 14/03/2020 12:48 | 1 | Small: 10 - 1000 sq.m | 15306 | Forest - plantation |  | 20200316SPN_03 | Infrastructure (network-based) | -37.3938 | 145.0533 | 1 | AusNet Services Distribution | Report | 19376 | 0.00066319 | 22kV AC | Wallan (Kilmore Gap) | 3756 | Upper Plenty | Trees
Crews dispatched to investigate and make safe. BRADLEY FROST WAS TAKEN to hospital this morning and was discharged | 89 CLEAVER ROAD, PIEDMONT VIC 3833 | 2700311 | Working too close to overhead lines |  |  |  | Not followed | Phase to earth | 0 | Bradley Frost on site received shock when he touched the street line with aluminium pipe. | Conductor (bare) | 0 | 0 | 0 |  | WGL24 | Vegetation: Trees Incident | Minor shock;No Go Zone (contact) | 18/03/2020 14:24 |  |  | 15319 | Agricultural |  | 20200318SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19392 | 0.040468 | Low voltage AC (<1kV) | Moorabbin Airport | 3833 | Piedmont | Other
All supplies to the public light shave been isolated sites made safe. Work being planned to have stolen assets replaced. | 23 Wylie Way, Point Cook VIC 3030, Australia | 30298307 | Copper theft | [6 empty] | Crew attending a public lighting fault found approximately 700 mtrs of lighting cable had been stolen. Cables and pits had been disturbed at 9 locations. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV002 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43778 |  |  | 14307 | Roadway |  | 20190919PWA_03 | Infrastructure (network-based) | -37.8968 | 144.7233 | 1 | Powercor | Report | 17990 | 0.018176 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
arrangements made to replace the stolen cables. | Bulmans Rd, Melton West VIC 3337, Australia | 30298008 | Copper theft | [6 empty] | Passer by reported stolen cables from a number of pits. On arrival crew found a number of public lighting pits had been opened and service cable stolen. Cables were stolen from up to 5 locations. Vic roads cabinet also effected. There was no fire and no reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN022 | Copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43808.6903 |  |  | 14311 | Roadway |  | 20190919PWA_04 | Infrastructure (network-based) | -37.688 | 144.5492 | 1 | Powercor | Report | 17996 | 0.02683 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Crew isolated and made safe, repairs arranged. Defect notice issued and left in meter board. | 12 GELATI STREET, MANOR LAKES VIC 3024 | 60627897 | Copper theft | [6 empty] | Builders reports Underground pit exposed after consumer mains stolen. Wires open onto footpath. Upon arrival the PCA Field Crew have advised, that an unknown person has opened up the Service Pit supplying No. 12 Gelati Street, Manor Lakes, 3024 and Cut the customer mains cable on the load side of the IPC's and preceeded to the Main switchboard and cut the other end of the cable with the LV Consumer Mains Cables (pit to switchboard) cut-away and stolen. The LV cables in the service pit were found to be ALIVE upon arrival. There was no reported fire or injuries reported. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WBE014 | Copper theft | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43808.7035 |  |  | 14312 | Residential |  | 20190919PWA_05 | Infrastructure (customer connection) | -37.8687 | 144.5853 | 1 | Powercor | Report | 17997 | 0.011515 | Low voltage AC (<1kV) | Laverton Raaf | 3024 | Manor Lakes | Other
Fault crew and LEI dispatched to investigate. Fault crew identified faulty IPC connection connection at pole. Faulty connection replaced and supply restored following all tests being carried out and passed. | 22 DEE ROAD, MILLGROVE VIC 3799 | LIS1407351 |  |  |  | Defective component |  |  |  | Plumber reported receiving 'tingles' from pipe at hot water service | POA connection (network side) | 0 | 0 | 0 |  | WYK13 | Plumber was attending the residence to work on plug in hot water unit when he received a shock from the copper water pie under the unit. REC was called to property he measured a voltage on the earth and could see equipment was not operating correctly. He turned off switch board and remained onsite to assist with repairs. Fault crew identified faulty IPC connection connection at pole. Faulty connection replaced and supply restored following all tests being carried out and passed. | Minor shock | 18/07/2019 17:22 |  |  | 14303 | Residential |  | 20190919SPN_01 | Infrastructure (customer connection) | -37.7509 | 145.6517 | 2 | AusNet Services Distribution | Report | 17986 | 0.012499 | Low voltage AC (<1kV) | Moorabbin Airport | 3799 | Millgrove | Connection
On arrival crew isolated supply and carried out repairs. | Cardigan St, Carlton VIC 3053, Australia | 30547142 | Working too close to underground cables | [5 empty] | 1 | Contractor (Trade Tech Services) for customer reported hitting an underground cable and damaging it. On arrival, the crew found an High Voltage (HV) 11kV paper lead cable has been cut and damaged due to customer excavations. There was no ground fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BQ041 | Contractor cutting conduits with reciprocating saw | Loss of supply;Significant disruption to the community;Damage to network assets | 21/09/2019 8:54 |  |  | 14318 |  |  | 20190923PWA_01 | Infrastructure (network-based) | -37.8004 | 144.9653 | 1 | CitiPower | Report | 18198 | 0.030736 | 11kV AC | Essendon Airport | 3053 | Carlton | Dug up
A fault crew was dispatched to the site and isolated the fault at the pole. A defect was issued to the affected premise. | 14 STEPHENSONS ROAD, MOUNT WAVERLEY VIC 3149 | 601900 | Working too close to overhead lines | [6 empty] | UE received a report from a customer that an excavator has pulled down the overhead service line supplying a neighbouring property as part of demolition works. | Service cable (insulated) | 0 | 0 | 0 |  |  | An excavator hit a neighbouring overhead service line. | No Go Zone (contact) | 43717.4618 |  |  | 14342 | Residential |  | 20190930UTD_02 | Infrastructure (network-based) | -37.859 | 145.1323 | 1 | United Energy Distribution | Report | 18034 | 0.033049 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Vehicle
Fault crews patrolled the lines and found a council tree branch fallen onto HV and LV overhead lines and damage to Thompsons-Foote kiosk which caused a nearby small grass fire. Fault crews isolated the affected area and made it safe. An EIO was requested on site to inspect neighbouring premises for damage and confirmed that a HVI occurred with damages to customer's appliances, switchboards and meters. Procedures as indicated in the work instruction for HV injections has been followed. | UNIT 2 6 UNION STREET, TEMPLESTOWE LOWER VIC 3107 | 7057860 |  | Blown branch/vegetation |  |  |  |  | 1 | At 5:14am strong winds caused a branch from a council tree to break and drop into HV/LV lines. The feeder protection operated and de-energised the lines. It was confirmed that HVI had occurred to neighbouring residences. | Conductor (bare) | 0 | 0 | 0 |  | BU14 | Vegetation: Trees Incident | HV injection;Significant disruption to the community;Grassfire;Plant/equipment | 21/09/2019 5:15 | 1 | Localised: less than 10 sq.m | 14345 | Roadway |  | 20191001UTD_01 | Infrastructure (network-based) | -37.7567 | 145.1134 | 1 | United Energy Distribution | Report | 18074 | 0.025043 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3107 | Templestowe Lower | Trees
On arrival crew inspected assets no damage found | 105 Norelle Cres, Kangaroo Flat VIC 3555, Australia | 33011824 |  | Bird |  |  |  |  | 1 | A customer reported hearing loud bang, went outside and pole was sparking and cause fire in grass under pole. Supply not affected now but power did go off for a moment, fire is out now. Crew found a bird caused flashover on center phase HV bridge at pole 63 Norelle Cresent. There was a ground fire, no reported injuries or third party property damage. | Pole (concrete);Dropper/bridge | 2 | 2 | 2 |  | BET006 | Bird Incident | Grassfire | 43475.7326 | 1 | Localised: less than 10 sq.m | 14350 | Roadway |  | 20191002PWA_03 | Infrastructure (network-based) | -36.7824 | 144.2305 | 1 | Powercor | Report | 18045 | 0.019123 | 22kV AC | Bendigo Airport | 3555 | Kangaroo Flat | Animal
On arrival supply isolated and repairs completed | 320 Ridge Rd, Tresco VIC 3583, Australia | 33068355 | [7 empty] | Report received of fallen conductor resulting in 100 x 200 square metres of stubble being burnt. On arrival crew found that HV conductor had parted about one metre from the pole. protection operated. There was a ground fire, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | KGT004 | To be advised | Grassfire | 43506.0854 | 1 | Medium: 1000 sq.m - 10 ha | 14351 | Agricultural |  | 20191002PWA_04 | Infrastructure (network-based) | -35.5003 | 143.6792 | 1 | Powercor | Notification | 18046 | 0.030645 | 22kV AC | Swan Hill Aerodrome | 3583 | Tresco | Conductor
Crew removed dog and rabbit and HV SWER supply was restored to the system. LEI was initially called to attend . Customer advised to have partner attend local hospital for observation. | 813 SANDBAR ROAD, LAKE LONSDALE VIC 3381 | PA0079211 |  | Animal | [5 empty] | Customer reports partner received an electric shock when attempting to retrieve dog from inside a ground mounted transformer. Customer reported 1 of the 2 Fox terriers went missing and his partner found the dog motionless partly under a pad mounted SWER S/S on property. Customer partner went to retrieve dog and received an electric shock. Partner returned to house to report shock and customer rang Powercor to attend. Crew arrived and found dog protruding from base of SWER pad mount S/S. After HV supply was isolated on the SWER system, the crew opened the S/S and found dog had contacted an LV bushing of the pad mount. Crew also found a rabbit in the pad mount enclosure. There was no fire. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | STL006 | Customer contacted deceased dog in contact with LV wiring | Minor shock;Fatality of livestock, pet or companion animal | 43595.5493 |  |  | 14362 | Agricultural |  | 20191007PWA_01 | Infrastructure (network-based) | -37.0112 | 142.6395 | 1 | Powercor | Report | 18062 | 0.022873 | Low voltage AC (<1kV) | Horsham Aerodrome | 3381 | Lake Lonsdale | Animal
On arrival crew isolated supply and carried out repairs. | STALEY ROAD, WEMEN VIC 3549 | 32143201 |  |  |  | Corrosion |  |  |  | A Customer reported that a few days ago when he started his pump, the nearby pole dropped a few large sparks that started a small grass fire. On arrival the crew found that a Low Voltage Isolator had overheated and caused hot debris to fall to the ground starting a small grassfire. The Customer told the crew that the initial grassfire was less than 1m2 in size, and the customer stamped it out with his feet. The customer subsequently burnt a larger area himself to create a fire break. There were no reported injuries or third party damage. | Disconnector/isolator;Connector/termination | 2 | 2 | 2 |  | WMN013 | Overheated connection | Grassfire | 43534.45 | 1 | Localised: less than 10 sq.m | 14363 |  |  | 20191007PWA_02 | Infrastructure (network-based) | -34.7386 | 142.6536 | 1 | Powercor | Report | 18063 | 0.0089792 | Low voltage AC (<1kV) | Mildura Airport | 3549 | Wemen | Connection
Fault crew dispatched. Line isolated, broken conductor repaired and supply restored. | 705 METUNG ROAD, METUNG VIC 3904 | LIS1901172 |  | Wind |  | Corrosion;Mechanical breakdown |  |  |  | report of HV conductor on ground resulting in grass fire | Conductor (bare) | 0 | 0 | 0 |  | BDL6 | Conductor has broken midspan resulting in ground fire (approx 1m x 3m). Upon further investigation corrosion was identified on the conductor which is believed to have cause the conductor to break during high winds experienced at the time of failure. Conductor repaired and supply restored. Follow up inspection organised to determine if corrosion present on the remaining O/H conductor. | Grassfire | 43626.5472 | 1 | Localised: less than 10 sq.m | 14370 |  |  | 20191010SPN_01 | Infrastructure (network-based) | -37.8741 | 147.8584 | 2 | AusNet Services Distribution | Report | 18076 | 0.024245 | 22kV AC | Bairnsdale Airport | 3904 | Metung | Conductor
Fault crew dispatched. Isolated and made safe. replaced FOLCB tested and energised services. | 36 HODSON ROAD, WARRANDYTE VIC 3113 | LIS1206025 |  |  |  | Overheated connection |  |  |  | Report of pole fire and subsequent ground fire | Pole (wood);Service cable (insulated) | 0 | 0 | 0 |  | RWN31 | 2 x 4 wire services caught fire in conduit on pole and burnt to FOLCB. | Pole-top fire;Grassfire | 43656.8507 | 1 | Localised: less than 10 sq.m | 14371 |  |  | 20191010SPN_02 | Infrastructure (network-based) | -37.7533 | 145.2122 | 1 | AusNet Services Distribution | Report | 18078 | 0.025353 | Low voltage AC (<1kV) | Moorabbin Airport | 3113 | Warrandyte | Pole
Fault crew dispatched and candled fuse replaced with new, checked all connections. | PRINCES HWY, LAKE TYERS BEACH VIC 3909 | NLA34 |  |  |  | Candled fuse |  |  |  | Fuse Candling | Boric acid | 0 | 0 | 0 |  | LIS1903088 | Candled HV Boric Acid Fuse | Pole-top fire | 43718.3958 | 1 | Negligible: no ground fire | 14372 |  |  | 20191010SPN_03 | Infrastructure (network-based) | -37.8512 | 148.0393 | 2 | AusNet Services Distribution | Report | 18081 | 0.011521 | 22kV AC | Bairnsdale Airport | 3909 | Lake Tyers Beach | Fuse
Site made safe | 13 HIGH STREET, COBURG VIC 3058 | A048482 | Unauthorised access | [5 empty] | 2 | Crews attended the above address today with a SO for abolishment of overhead supply and metering. When they arrived on site there was no overhead service or electricity meter and the original property demolished and a new property half constructed. Abolishment request and photos attached in the "Notes & Findings" section. For further information, please contact Jason Ford (Compliance Offer/Electrical Inspector) on 1300 855 824 or jason.ford@zinfra.com.au | Copper;Neutral screen;Smart meter | 0 | 0 | 0 |  | CS02 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43748.6069 |  |  | 14373 | Residential |  | 20191011JEM_01 | Infrastructure (network-based) | -37.7391 | 144.9559 | 1 | Jemena | Report | 18082 | 0.035865 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
Site made safe | 8 COMMERCIAL ROAD, FOOTSCRAY VIC 3011 | A038371 | Unauthorised access | [5 empty] | 2 | Crews attended site 26.9.19 with a SO for the abolishment of service line and meter. When the crews arrived they found no service line or meter on site. (VESI abolishment request form attached) Crews attended site again on 1.10.19 with a SO for a new 3 phase undergroun supply and metering (EWR and COES forms attached in the Notes & Findings section). Whilst on site completing this new connection they found the original electricity meter in the rubbish bin. | Smart meter | 0 | 0 | 0 |  | FE06 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/08/2019 10:57 |  |  | 14374 | Residential |  | 20191011JEM_02 | Infrastructure (network-based) | -37.7929 | 144.8926 | 1 | Jemena | Report | 18083 | 0.0037859 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Other
On arrival Crew inspected site, no damage found. Arrangements made to have crossarm strap re-attached. | 10 Harrier Dr, Invermay Park VIC 3350, Australia | 32011052 |  | Bird |  |  |  |  | 1 | Vic fire reported a small ground fire ( 5 x 1 mts) at the base of a pole at the incident location. On arrival the crew noticed that one HV crossarm strap had become loose, but was not in contact with conductors. The fire start has been attributed to a bird contact although a bird was not found at the site. There was no injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | BAN011 | Bird Incident | Grassfire | 13/10/2019 19:06 | 1 | Localised: less than 10 sq.m | 14378 | Roadway |  | 20191014PWA_01 | Infrastructure (network-based) | -37.5295 | 143.8652 | 1 | Powercor | Report | 18088 | 0.0014097 | 22kV AC | Ballarat Aerodrome | 3350 | Invermay Park | Animal
Fault crew and LEI dispatched. Tree branch removed and service cable reinstated and FOLCB replaced with new. Supply restored following completion of repair work and all tests carried out and passed | 4 AURA VALE ROAD, MENZIES CREEK VIC 3159 | LIS5699346 |  | Blown branch/vegetation | [5 empty] | Customer reported receiving a slight tingle to his fingers and service cable down. | Services cable | 0 | 0 | 0 |  | BGE22 | Vegetation: Trees Incident | Minor shock | 21/09/2019 10:23 |  |  | 14379 |  |  | 20191014SPN_01 | Infrastructure (customer connection) | -37.9238 | 145.4003 | 2 | AusNet Services Distribution | Report | 18089 | 0.028 | Low voltage AC (<1kV) | Moorabbin Airport | 3159 | Menzies Creek | Trees
Fault crew dispatched. Tree branch removed, Candled HV fuse removed and replaced with new | 18 KOONWARRA-INVERLOCH ROAD, KOONWARRA VIC 3954 | LIS2001276 |  | Blown branch/vegetation |  | Candled fuse |  |  |  | Report of fuse candling | Any other type | 0 | 0 | 0 |  | LGA14 | Vegetation: Trees Incident | Pole-top fire | 16/10/2019 9:00 | 1 | Negligible: no ground fire | 14386 |  |  | 20191017SPN_01 | Infrastructure (network-based) | -38.5486 | 145.9438 | 1 | AusNet Services Distribution | Report | 18103 | 0.0090301 | 22kV AC | Morwell (Latrobe Valley Airport) | 3954 | Koonwarra | Trees
A Fault crew attended the site and rectified the connections. Installation tests were completed that confirmed the fault had been rectified and supply was left on. | 40 ESSEX ROAD, MOUNT WAVERLEY VIC 3149 | 2314052 | Unauthorised work | [5 empty] | 2 | United Energy metering subcontractor (Smart Metering Services) attended the property for a solar meter investigation and suspected the meter has been tampered with. The meter technician believed the meter enclosure had been relocated and a review of United Energy records show there had been no truck appointments or calls from the owner/occupier. The relocation by unknown persons inadvertently transposed the line and load conductors at the single phase meter terminal. | Connection to meter | 0 | 0 | 0 |  |  | It appears the single phase meter was relocated without notification to United Energy and was incorrectly wired. | Damage to network assets | 43748.5625 |  |  | 14389 | Residential |  | 20191018UTD_01 | Infrastructure (customer connection) | -37.8632 | 145.1171 | 1 | United Energy Distribution | Report | 18108 | 0.035995 | Low voltage AC (<1kV) | Moorabbin Airport | 3149 | Mount Waverley | Other
On arrival crew isolated supply and carried out repairs | 33 Pender St, Thornbury VIC 3071, Australia | 30196524 | Working too close to overhead lines | [6 empty] | MFB called to report a pole and wires down at the incident location. On arrival the crew found that an excavator working on the vacant block at 31 Pender St, contacted the service cable to 29 Pender St, resulting in the service pole in front of 33 Pender St breaking off and falling to the ground. There were no reported injuries, fires, or third party damage. | Pole (concrete);Service cable (insulated) | 2 | 2 | 2 |  | NC004 | Excavator snagged service cable which caused service pole to fail | No Go Zone (contact);Damage to network assets | 43534.5681 |  |  | 14395 | Roadway |  | 20191021PWA_03 | Infrastructure (network-based) | -37.7538 | 145.0044 | 1 | CitiPower | Report | 18115 | 0.018392 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | Vehicle
Crew replaced pit lid and arrangements made to repair cable | 125 PARK STREET, MOONEE PONDS VIC 3039 | A138865 | Copper theft | [5 empty] | 2 | Attempted copper theft of underground cable from underground pit | Cable;Services pit (customer) | 2 | 2 | 2 |  | ES13 | Unknown persons tried to steal copper | Damage to network assets | 21/10/2019 8:35 |  |  | 14404 | Roadway |  | 20191022JEM_01 | Infrastructure (network-based) | -37.761 | 144.9091 | 1 | Jemena | Report | 18444 | 0.030374 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Other
On arrival crew isolated supply and arranged repairs. | 81 State Route 38, Sunshine VIC 3020, Australia | 30107756 | Vehicle | [6 empty] | Customers reported wires have been bought down by a large truck, wires are on the ground in the street and driveway, customer also has no power. Also truck driving down street pulled wire going from pole to house, has caused damage to customers house, supply is still on, wire is now lying on side of street with a branch next to it, Fire brigade on site to cordoned off area. On arrival crew found damaged O/H service & damaged LV overhead conductor. There was no fire and no reported injuries. | Conductor (bare);Service cable (insulated) | 2 | 2 | 2 |  | SSE013 | Truck struck services and conductor | Loss of supply;Damage to network assets | 43475.5826 |  |  | 14405 | Roadway |  | 20191022PWA_02 | Infrastructure (network-based) | -37.7864 | 144.8412 | 1 | Powercor | Report | 18133 | 0.0091829 | Low voltage AC (<1kV) | Essendon Airport | 3020 | Sunshine | Vehicle
On arrival crew isolated supply and carried out repairs. | 218 POINT COOK ROAD, POINT COOK VIC 3030 | 34028034 | Copper theft | [6 empty] | Following a public lighting fault report a crew attended the incident site. They found copper theft at seven sites around 218 point cook rd, point cook. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV008 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43475.9444 |  |  | 14406 | Roadway |  | 20191022PWA_03 | Infrastructure (network-based) | -37.8893 | 144.7555 | 1 | Powercor | Report | 18134 | 0.024531 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Point Cook | Other
Crew attended site and repaired the broken conductor and restored supply. | 1309 EDI-CHESHUNT ROAD, WHITFIELD VIC 3733 | LIS5101874 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | Report of truck contacting and bringing down O/H SWER conductor. 3/2.75 Steel SWER conductor brought down by truck between 5101874 & 5101875. 2 FUSES blown at ISO. | Conductor (bare) | 0 | 0 | 0 |  | WN5 | Truck in paddock hit swer wire ,breaking wire and causing two hv fuse at iso S/S to blow . | No Go Zone (contact) | 21/10/2019 20:20 |  |  | 14399 | Agricultural |  | 20191022SPN_01 | Infrastructure (network-based) | -36.7328 | 146.4282 | 1 | AusNet Services Distribution | Report | 18779 | 0.021163 | 12.7kV AC (SWER) | Wangaratta Aero | 3733 | Whitfield | Vehicle
Fault crews and EIO attended the site to investigate. EIO measured 120V on the neutral. Fault crews found the incoming neutral had broken away at the FOLCB and the FOLCB was subsequently replaced. Supply was restored, tested and left on. | 334 MAIN CREEK ROAD, MAIN RIDGE VIC 3928 | 9829160 |  |  |  | Neutral fault |  | Phase to neutral | 1 | UE received a call that a customer received an electric shock at a VET clinic. | Connection box | 0 | 0 | 0 |  |  | The incident was caused by the incoming neutral breaking away from the FOLCB. | Minor shock | 21/10/2019 14:55 |  |  | 14407 | Commercial |  | 20191022UTD_03 | Infrastructure (network-based) | -38.3914 | 144.9721 | 1 | United Energy Distribution | Report | 18135 | 0.018765 | Low voltage AC (<1kV) | Moorabbin Airport | 3928 | Main Ridge | Connection
On arrival crew isolated supply and carried out repairs. | 11b Leader St, Truganina VIC 3029, Australia | 60349390 | Working too close to underground cables | [6 empty] | Report received from landscaper that they have exposed a LV pit at incident site and wores are exposed. On arrival crew found an LV pit had been dislodged and damaged. Landscaper claimed pit had been buried and was struck when the top layer of soil was scrapped away. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV003 | Landscaping using bobcat | No Go Zone (contact);Damage to network assets | 43506.3681 |  |  | 14408 | Roadway |  | 20191023PWA_01 | Infrastructure (network-based) | -37.8265 | 144.7469 | 1 | Powercor | Report | 18142 | 0.0033796 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Truganina | Dug up
On arrival crew isolated supply and carried out repairs. | 10 Grahamvale Rd, Grahamvale VIC 3631, Australia | 33095149 | Working too close to underground cables | [6 empty] | Report of underground conduit dug up with excavator, conduit and wire within conduit is broken, On arrival crew found Excavator cleaning out old water channel and back filling with crushed rock. Crew found damaged underground service cable and conduit. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | SHN024 | Excavator maintaining channel | No Go Zone (contact);Damage to network assets | 43506.5556 |  |  | 14409 |  |  | 20191023PWA_02 | Infrastructure (network-based) | -36.3635 | 145.4319 | 1 | Powercor | Report | 18143 | 0.032556 | Low voltage AC (<1kV) | Shepparton Airport | 3631 | Grahamvale | Dug up
Fault crew dispatched. Candled HV Fuse removed and replaced with new | 56 REYNOLDS ROAD, PAKENHAM VIC 3810 | LIS504298 |  |  |  | Candled fuse |  |  |  | Report of candled HV Fuse | Boric acid | 0 | 0 | 0 |  | OFR23 | Candled Boric Acid HV fuse | Pole-top fire | 25/10/2019 17:18 | 1 | Negligible: no ground fire | 14426 |  |  | 20191028SPN_02 | Infrastructure (network-based) | -38.0319 | 145.4932 | 2 | AusNet Services Distribution | Report | 18165 | 0.0036667 | 22kV AC | Moorabbin Airport | 3810 | Pakenham | Fuse
Crew isolated, repaired and tested | 25 HESLING COURT EAST BENDIGO 3550 | 33022712 | Working too close to underground cables | [5 empty] | 2 | Civil contractor reported underground cable damaged, exposed wires, area made safe at incident location. Crew found borer went through 50mm LV underground, replaced with new 50mm cable | Services cable | 0 | 0 | 0 |  | BET005 | Boring close to LV cable | Loss of supply;No Go Zone (contact) | 31/10/2019 14:21 |  |  | 14447 | Roadway |  | 20191104PWA_01 | Infrastructure (network-based) | -36.7513 | 144.3151 | 1 | Powercor | Report | 18202 | 0.0060162 | Low voltage AC (<1kV) | Bendigo Airport | 3550 |  | Dug up
Supply isolated and defect notice issued. | 37 MAKLAND DRIVE, DERRIMUT VIC 3026 | 30256692 | Bypass of meter | [5 empty] | 1 | Call received about a case of illegal wiring (a bypass behind the meter board had been installed) where the resultant circuit overload caused the property service pit to melt along with the 4-core 35mm service between the LV service tee joint and pit. The fault crew were initially responding to this outage, as the kiosk LV circuit fuses supplying the LV mains street circuit to #37 had blown all 3 fuses (as a result of the overload at #37). Further investigation by the fault crew lead them to a pile of timber which was stacked on top of the already buried service pit located within the nature strip. Police were called to attend on site before the crew made the site safe by isolating supply to the property and issuing a defect notice | Services cable;Services pit (network);Smart meter;Connection to meter | 0 | 0 | 0 |  | SU035 | meter bypassed and high electrical load | Damage to network assets | 20/10/2019 8:55 |  |  | 14472 | Residential |  | 20191108PWA_04 | Infrastructure (customer connection) | -37.7857 | 144.7758 | 1 | Powercor | Report | 18239 | 0.028748 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Derrimut | Other
The Powercor crew made site safe, isolated supply and repair connections inside the pits and install new service cable between the 2 pits. | 1254 MT COTTRELL ROAD,ROCKBANK,VIC,3338 | 30345278 | Copper theft | [6 empty] | Customer reported exposed wires at UG pit locations at new estate site 'Millstone Estate'. Wires exposed are found at pits located at base of new streetlights at the intersection of Mount Cottrell Road and several pits located on Renaissance Drive (new road). Likely due to theft or vandalism. On arrival the Crew found that 7 P/L service pits had their concrete lids removed and wires were cut and exposed hanging out of the pits in an attempt to pull out the cables from every pit. The thieves were only able to pull out the cables between the 2 pits near the intersection with Mount Cottrell road and approximately 70 meters of 16mm 4 core cable were stolen. | Cable;Services cable | 0 | 0 | 0 |  | MLN011 | copper theft | Damage to network assets | 14/10/2019 11:23 |  |  | 14473 | Roadway |  | 20191108PWA_05 | Infrastructure (network-based) | -37.7368 | 144.6143 | 1 | Powercor | Report | 18240 | 0.036536 | Low voltage AC (<1kV) | Laverton Raaf | 3338 |  | Other
Police notified, underground mains isolated from supply at the substation pole, OPTUS to arrange replacement of mains cable from underground pit at property boundary. | 1 MIDDLE GULLY ROAD, MACEDON VIC 3440 | 32048066 | Copper theft | [6 empty] | Copper theft of customers assets from Powercor Underground Pit to Optus Installation [100metres in length] 20 metres of Powercor 4 core 35mm Underground cable damaged but not stolen. Damage to Powercor assets on substation pole LV Mains Box vandalised | Services cable;Customer wiring | 0 | 0 | 0 |  | GSB-WND2 | copper theft | Loss of supply;Damage to network assets | 15/10/2019 6:16 |  |  | 14474 | Other | Communications tower | 20191108PWA_06 | Infrastructure (customer connection) | -37.4005 | 144.5419 | 1 | Powercor | Report | 18241 | 0.028877 | Low voltage AC (<1kV) | Melbourne Airport | 3440 | Macedon | Other
requested worksafe to attend site | 174 HIGH STREET, BELMONT VIC 3216 | 23831309 | Working too close to overhead lines | [5 empty] | 2 | employee reported a breach of the No Go Zone rules by roof plumbers when attending a fault 27/07/2019 at approximately 21:00 pm. During return visit to get picture observed a worker in the No Go Zone. Worksafe was contacted . Chris from Worksafe called me back and said they would talk to the roofer about breaking the No Go Zone. Worksafe Incident No 29071911BHKSL - call taker Kate. | Conductor (ABC) | 0 | 0 | 0 |  | GCY012 | working close to LVABC on roof | No Go Zone (no contact) | 29/07/2019 10:00 |  |  | 14496 | Commercial |  | 20191113PWA_05 | Infrastructure (network-based) | -38.1747 | 144.343 | 2 | Powercor | Report | 18266 | 0.039334 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Other
Fault crew dispatched. Contractor advised to remain clear. Cable isolated and cable repaired (straight through joint installed). Blown fuses also replaced. | 21 CAMPBELL COURT, WARRANDYTE VIC 3113 | LIS1205832 | Working too close to underground cables | [6 empty] | U/G LV service hit by third party with HDD (horizontal direction drilling) equipment | Services cable | 0 | 0 | 0 |  | RWN26 | Contractor working too close to U/G LV cables and potentially digging/drilling too deep. | No Go Zone (contact) | 43780.5312 |  |  | 14503 |  |  | 20191119SPN_01 | Infrastructure (network-based) | -37.746 | 145.1942 | 1 | AusNet Services Distribution | Report | 18789 | 0.0022801 | Low voltage AC (<1kV) | Moorabbin Airport | 3113 | Warrandyte | Dug up
CFA extinguished the grass fire. | 8 Geddes Rd, Creswick VIC 3363, Australia | 33007412 |  | Blown branch/vegetation | [5 empty] | Crew reports that a branch has broken of a gum tree and contacted the overhead line between P1 and P2 Flem spur line The branch caught fire and started a ground fire when it came to rest on the ground under the 22kV overhead line. There was a small ground fire, no reported injuries or third party property damage. | Conductor (bare) | 0 | 0 | 0 |  | BAN009 | Vegetation: Trees Incident | Grassfire | 21/11/2019 14:30 | 1 | Small: 10 - 1000 sq.m | 14521 | Roadway |  | 20191122PWA_03 | Infrastructure (network-based) | -37.4066 | 143.8938 | 1 | Powercor | Report | 18308 | 0.039093 | 22kV AC | Ballarat Aerodrome | 3363 | Creswick | Trees
Made safe, repairs to be completed at later date. | 394 Ryrie St, East Geelong VIC 3219, Australia | 30326451 | Working too close to underground cables | [6 empty] | Report of Directional Drilling contractor on site. LV cable damaged by Directional Drilling. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | GCY024 | Direction bore struck cable | No Go Zone (contact) | 28/10/2019 11:44 |  |  | 14553 | Roadway |  | 20191128PWA_04 | Infrastructure (network-based) | -38.1534 | 144.3735 | 1 | Powercor | Report | 18349 | 0.025509 | Low voltage AC (<1kV) | Avalon Airport | 3219 | East Geelong | Dug up
Supply isolated and repairs carried out | 59 Harding St, Winchelsea VIC 3241, Australia | 30224609 | Working too close to underground cables | [6 empty] | A contractor reported an UG dug up at the incident location. Upon arrival,. On arrival a Powercor crew found that the UG cable and conduit had been damaged by an excavator. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | WIN011 | Excavation works | No Go Zone (contact);Damage to network assets | 28/10/2019 10:00 |  |  | 14555 | Roadway |  | 20191128PWA_05 | Infrastructure (network-based) | -38.2429 | 143.9955 | 1 | Powercor | Report | 18352 | 0.028572 | Low voltage AC (<1kV) | Avalon Airport | 3241 | Winchelsea | Dug up
On arrival crew isolated supply and arranged repairs. | A8, Ercildoune VIC 3352, Australia | 30314336 | Copper theft | [6 empty] | A Powercor crew found a vandalised UG P/L pits at the incident location. The crew has investigated the area and found about five pit lids had been opened and about 200m of P/L cables had been stolen. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | BAS011 | Copper theft | Damage to network assets | 29/10/2019 10:00 |  |  | 14556 |  |  | 20191128PWA_06 | Infrastructure (network-based) | -37.4649 | 143.5829 | 1 | Powercor | Report | 18353 | 0.027037 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Ercildoune | Other
Disconnected supply to 29-31 McArthurs Road. Defect notice issued. Overhead service and FOLCB removed from site. | 29-31 MCARTHURS ROAD, ALTONA NORTH VIC 3025 | 32164527 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [6 empty] | An unknown person reported a service wire had been struck by a tree branch and had come away from the pole. Fault crews attended and found the 35mm 4c overhead service and FOLCB had been ripped from the building. A builder working nearby advised an excavator had made contact with the overhead service. The excavator operator(s) left the site before fault crews attended. There was no fire or reported injuries. | Service cable (insulated);Customer wiring | 2 | 2 | 2 |  | BLT017 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 30/10/2019 8:04 |  |  | 14557 | Roadway |  | 20191128PWA_07 | Infrastructure (customer connection) | -37.8353 | 144.8414 | 1 | Powercor | Report | 18407 | 0.021797 | Low voltage AC (<1kV) | Laverton Raaf | 3025 | Altona North | Vehicle
Supply isolated, aerial earth replaced 1 Customer interrupted to allow Zinfra to make repairs and restore supply. | 27-35 MCDONALD ROAD, BROOKLYN VIC 3012 | A029028 | Working too close to overhead lines | [5 empty] | 2 | At approximately 14:50 a forklift made contact with JEN LV overhead assets (Aerial Earth cable from the street pole to the transformer pole on site) off Bunting Road, Brooklyn | Conductor (covered uninsulated) | 2 | 2 | 0 |  | TH21 | No Go Zone breach | No Go Zone (contact) | 28/11/2019 14:51 |  |  | 14561 | Industrial |  | 20191129JEM_01 | Infrastructure (network-based) | -37.812 | 144.8464 | 1 | Jemena | Report | 19082 | 0.020576 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Other
On arrival crew isolated supply and carried out repairs. | 1-2 Trantara Ct, East Bendigo VIC 3550, Australia | 30333400 | Copper theft | [6 empty] | Customer reported, about 4 or 5 lights around the north-east corner of the intersection are not working, the lights on the south side of the intersection appear to be working correctly. Crew found three underground service pits where damaged by vandals live cables where cut and left exposed on ground, There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | EHK021 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43596.4354 |  |  | 14559 | Roadway |  | 20191129PWA_02 | Infrastructure (network-based) | -36.7426 | 144.3157 | 1 | Powercor | Report | 18356 | 0.0034954 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | East Bendigo | Other
Supply isolated repairs organised. | 127 Brooklyn Rd, Brookfield VIC 3338, Australia | 30306517 | Copper theft | [6 empty] | Reported as Suspected cable theft - Matt has come cross live cables on footpath - crew required to attend ASAP On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen the LV Service Cable within the LV Service Pits supplying the PL Lighting Poles. The LV cables were found to be ALIVE at the service pit at the base of P06N LIS-812452 There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN013 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43596.4243 |  |  | 14562 | Roadway |  | 20191129PWA_04 | Infrastructure (network-based) | -37.7012 | 144.5611 | 1 | Powercor | Report | 18359 | 0.0043831 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Brookfield | Other
On arrival crew isolated supply and carried out repairs. | 15 Weeks Ave, Melton West VIC 3337, Australia | 30553805 | Copper theft | [6 empty] | A passer -by reported an exposed wires at the incident location. Upon arrival, a Powercor crew found that the ug cables on P/L circuits had been stolen. There were open pits at 135 Brooklyn Rd Brookfield 3338. However no cable theft was found at this location. There was no fire or reported injuries. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN014 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43627.4583 |  |  | 14563 | Roadway |  | 20191129PWA_05 | Infrastructure (network-based) | -37.6654 | 144.535 | 1 | Powercor | Report | 18360 | 0.022546 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
Assisted ESV with investigation arrangements made to relocate neighbors service to Mid span | 467 THE ESPLANADE, ST LEONARDS VIC 3223 | 32085774 | Building too close or within the No Go Zone | [5 empty] | 2 | ESV advised of HV contact on this site, during investigations a breach of permit to work conditions to LV was identified | Conductor (bare);Service cable (insulated) | 0 | 0 | 0 |  | DDL013 | Apparent non compliance with permit to work | No Go Zone (contact) | 25/11/2019 15:23 |  |  | 14565 | Construction |  | 20191129PWA_07 | Infrastructure (network-based) | -38.1652 | 144.7162 | 1 | Powercor | Report | 18363 | 0.026532 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3223 | St Leonards | Other
EIO arrived on site to investigate. EIO conducted tests on the installation and it all passed. There is damage to customer's appliances and installation. There is no HV reticulation present in the street and the EIO suspects a lightning strike occurred during the storm which caused a surge in both the power and telecommunications. | 10 ST LEONARDS CLOSE, NOBLE PARK VIC 3174 |  |  | Lightning |  |  |  |  | 1 | UE received a call that customer received a shock while talking on his phone during charging. The power went out and some appliances were no longer working. | Customer appliance | 0 | 0 | 0 |  |  | The EIO suspects a lightning strike occurred during the storm which caused a surge in both the power and telecommunications. | Minor shock | 25/11/2019 12:55 |  |  | 14567 | Residential |  | 20191129UTD_02 | Infrastructure (customer connection) | -37.9736 | 145.161 | 1 | United Energy Distribution | Report | 18365 | 0.0299 | Low voltage AC (<1kV) | Moorabbin Airport | 3174 | Noble Park | Lightning
On arrival crew isolated supply and carried out repairs. | N S Rd, Beverford VIC 3590, Australia | 32160282 |  |  |  | Leakage |  |  |  | CFA reported lines down with small fire. When crew arrived they found that the HV cross arm had burnt on one side and the conductor had dropped but was still in the air. No injuries or third party damage. No ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 43477.4958 | 1 | Negligible: no ground fire | 14575 | Roadway |  | 20191203PWA_01 | Infrastructure (network-based) | -35.2252 | 143.4541 | 1 | Powercor | Report | 18374 | 0.027256 | 22kV AC | Swan Hill Aerodrome | 3590 | Beverford | Crossarm
On arrival crew isolated supply and carried out repairs. | 195 Tyntynder Central Rd, Tyntynder VIC 3586, Australia | 32157266 |  |  |  | Leakage |  |  |  | CFA called advising pole fire at above address. When crew arrived, they found that the top of the pole had burnt and cross arm had broken. Conductors were still on cross arm which was hanging on top of pole. No injuries, no ground fire, no third party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 43477.4951 | 1 | Negligible: no ground fire | 14576 | Roadway |  | 20191203PWA_02 | Infrastructure (network-based) | -35.2483 | 143.524 | 1 | Powercor | Report | 18375 | 0.019723 | 22kV AC | Swan Hill Aerodrome | 3586 | Tyntynder | Pole
On arrival crew isolated supply and carried out repairs. | 68 Woodgate Rd, Murraydale VIC 3586, Australia | 32157209 |  |  |  | Leakage |  |  |  | Customer reported pole outside property was burnt at top of pole and wires were low. On arrival crew found broken cross-arm that had snapped in two and burn damage around the king bolt. CFA on site. No ground fire, no injuries no third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | SHL004 | Excessive leakage current | Pole-top fire | 30/11/2019 9:56 | 1 | Negligible: no ground fire | 14577 | Roadway |  | 20191203PWA_03 | Infrastructure (network-based) | -35.2834 | 143.5654 | 1 | Powercor | Report | 18376 | 0.00067245 | 22kV AC | Swan Hill Aerodrome | 3586 | Murraydale | Crossarm
Fault crews arrived on site to investigate. Upon inspection, it was identified that a tree has fallen onto the LV conductors due to high wind conditions. The site was made safe and the crews removed the branch. | 3564 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1302728 |  | Wind;Fallen |  |  |  |  | 1 | UE received a call that the conductor was on a tree and the tree was on fire. MFB has attended the site. | Conductor (bare) | 0 | 0 | 0 |  | STO22 | Vegetation: Trees Incident | Other vegetation | 26/11/2019 11:10 | 1 | Negligible: no ground fire | 14586 | Roadway |  | 20191204UTD_01 | Infrastructure (network-based) | -38.324 | 144.7329 | 1 | United Energy Distribution | Report | 18408 | 0.0054572 | Low voltage AC (<1kV) | Avalon Airport | 3564 | Portsea | Trees
Fault crews attended the site to investigate. Upon inspection, it was identified that there was a fire on the HV cross-arm which caused the HV conductors to dislodge and clash with the other conductors. The fault current from the short circuit caused a secondary fault on HV bridges at another pole which created a HVI into customer premises. | UNIT 3 36 CLYDE STREET, BOX HILL NORTH VIC 3129 | 7035489 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have lost power and UE protection operated on the feeder supplying this area. | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | DC12 | The cause of the cross-arm fire is due to tracking across the insulator. | Pole-top fire;HV injection | 26/11/2019 5:25 | 1 | Negligible: no ground fire | 14587 | Residential |  | 20191204UTD_02 | Infrastructure (network-based) | -37.8092 | 145.1282 | 1 | United Energy Distribution | Report | 18409 | 0.028491 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3129 | Box Hill North | Crossarm
Isolated electrical apparatus and replaced under LV Access Permit | 122 WOODLAND DRIVE, GISBORNE VIC 3437 | A055573 | Copper theft | [5 empty] | 2 | Copper theft of LV underground cables from pole type transformer LV Isolators @ WOODLAND DR-P2 (Feeder SBY13), to customer pit at base of pole. | Service cable (insulated) | 0 | 0 | 0 |  | SBY13 | Copper theft | Loss of supply | 43689.4618 |  |  | 14599 | Industrial |  | 20191208JEM_01 | Infrastructure (customer connection) | -37.5177 | 144.5839 | 1 | Jemena | Report | 18424 | 0.039236 | Low voltage AC (<1kV) | Melbourne Airport | 3437 | Gisborne | Other
On arrival theft confirmed, replacement organised. | 6 Briggs St, Laverton VIC 3028, Australia | 32174497 | Copper theft | [6 empty] | ALINOR GROUP CONST. & DEVELOPMENT PTY LTD, Mo Barakac (Site Superviser) of the site) reports the cable which normally runs from UG pit to the pole has been stolen recently - he has arrived to set up to get the properties connected but cannot do so until this has been replaced. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV006 | copper theft | Damage to network assets | 43657.6632 |  |  | 14607 | Roadway |  | 20191210PWA_01 | Infrastructure (network-based) | -37.8521 | 144.778 | 1 | Powercor | Report | 18436 | 0.0034757 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Laverton | Other
On arrival crew made safe and arranged repairs | 12 FELSTEAD DRIVE, TRUGANINA VIC 3029 | 30331290 | Working too close to underground cables | [6 empty] | A contractor reported an earthing cable damage at the incident location. Upon arrival, a Powercor crew found that the Kiosk ( CLEARWATER-FELSTEAD 2) earthing had been damaged. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | LVN024 | The contractor has been excavating the area for landscaping work. | No Go Zone (contact);Damage to network assets | 43657.5 |  |  | 14608 |  |  | 20191210PWA_02 | Infrastructure (network-based) | -37.8225 | 144.7606 | 1 | Powercor | Report | 18437 | 0.017519 | Earthing cable | Laverton Raaf | 3029 | Truganina | Dug up
On arrival crew isolated supplies and carried out repairs. | 291-343 Harkness Rd, Melton West VIC 3337, Australia | 30552562 | Vandalism;Copper theft | [6 empty] | Alan Osgood ph 0418708337 - is currently doing the streetscapes and they have noticed 4 pits overnight have had copper theft. cables exposed and hanging out of pits, could be live. they are in the garden beds and nature strips along Harkness rd. On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen the LV Service Cable within the LV Service Pit supplying PL Lighting. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN014 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43657.5465 |  |  | 14610 | Roadway |  | 20191210PWA_03 | Infrastructure (network-based) | -37.6615 | 144.5357 | 1 | Powercor | Report | 18439 | 0.0050856 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | Other
The crew made the site safe Isolated power and repaired all 3 phases and neutral conductor | 191 Esplanade, Altona VIC 3018, Australia | 30111396 | Recreation - Kites | Wind | [5 empty] | A customer saw large kite from kite surfer hit powerlines & thinks it may have landed in someones yard. He saw large flash & power went out. On arrival the PCA Faults Crew have advised that a gust of wind has picked up a large-kite from within Altona Beach and sent it towards the north across The Esplanade. The kite surfers kite was wrapped around the LV Conductors between LIS-2499 and LIS-2500. The kite was not in operation and unmanned, there was no fire, no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | AL012 | Wind blew kite into line | Loss of supply;Damage to network assets | 43749.6375 |  |  | 14611 | Roadway |  | 20191210PWA_04 | Infrastructure (network-based) | -37.8705 | 144.8268 | 1 | Powercor | Report | 18502 | 0.031565 | Low voltage AC (<1kV) | Laverton Raaf | 3018 | Altona | Other
The crew made the site safe and a fault-follow up has been raised to replace the stolen 16mm 4/c LV Service Cables. | 490-528 COBURNS ROAD, KURUNJANG VIC 3337 | 30315247 | Copper theft | [6 empty] | Email recieved open pit with wires exposed in front of 559-583 Coburns rd. On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up a number of pits and stolen the LV Service Cable within the LV Service Pit supplying 4 PL Lighting Poles There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN032 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43780.6778 |  |  | 14622 | Roadway |  | 20191211PWA_02 | Infrastructure (network-based) | -37.6551 | 144.5738 | 1 | Powercor | Report | 18471 | 0.041277 | Low voltage AC (<1kV) | Melbourne Airport | 3337 | Kurunjang | Other
On arrival crew arranged for repairs. | 33 TOPCLIFFE CRESCENT, TRUGANINA VIC 3029 | 30264053 | Working too close to overhead lines | [6 empty] | A Powercor employee found that a stay wire came off due to excavation at the incident location. It is a road construction site and the contractor excavating the area. Contractor did not advise Powercor of damage. There was no fire, no reported injuries or third party property damage. | Guy wire | 2 | 2 | 2 |  | ATS-WBE | earth moving plant contacted stay wire | Damage to network assets | 43780.375 |  |  | 14623 | Roadway |  | 20191211PWA_03 | Infrastructure (network-based) | -37.8391 | 144.7434 | 1 | Powercor | Report | 18472 | 0.041302 | Not applicable | Laverton Raaf | 3029 | Truganina | Dug up
On arrival supply isolated and repairs organised | 53 SAYERS ROAD, WILLIAMS LANDING VIC 3027 | 30308464 | Copper theft | [6 empty] | Crews attended a Patrol fault found lighting not working at six sites at incident location. approx. 280 mtrs of public lighting cable had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV007 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43810.059 |  |  | 14625 | Roadway |  | 20191211PWA_04 | Infrastructure (network-based) | -37.8545 | 144.7511 | 1 | Powercor | Report | 18474 | 0.023118 | Low voltage AC (<1kV) | Laverton Raaf | 3027 | Williams Landing | Other
Supply isolated and repairs carried out | Yaldeenie, 139 Sheehans Rd, Romsey VIC 3434, Australia | 30308712 |  | Blown branch/vegetation |  |  |  |  | 1 | During Wind storm limb fell contacting swer line bringing conductor to ground at incident location. Protection operated as expected. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WND012 | Severe wind storm | Damage to network assets | 43810.6785 |  |  | 14626 | Roadway |  | 20191211PWA_05 | Infrastructure (network-based) | -37.3321 | 144.771 | 1 | Powercor | Report | 18507 | 0.040432 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3434 | Romsey | Trees
The affected mains cable was temporarily re-jointed and re-installed into the existing LV pillar. A Fault Follow-up action was created to complete repairs | 55 Rathdowne Cct, Melton West VIC 3337, Australia | 60075855 |  |  |  | Overheated connection |  |  |  | Fire brigade reported POA fuse mains box at this address had caught fire. Powercor fault crew attended and noted smoke coming from the combined LV cable joint/fused servicing pillar at this address. A heavy soot layer had deposited on pillar internal components. There were no shocks, injuries or ground fire. | LV Pillar | 2 | 2 | 2 |  | MLN032 | Overheated mains cable | Melting or smoking only | 43477.9069 |  |  | 14641 | Roadway |  | 20191213PWA_03 | Infrastructure (network-based) | -37.6755 | 144.5639 | 1 | Powercor | Report | 18492 | 0.035811 | Low voltage AC (<1kV) | Laverton Raaf | 3337 | Melton West | UG Cable
Crew isolated supply to enable repairs to be completed. | 1224 ROCHFORD ROAD, NEWHAM VIC 3442 | 30544341 | Vandalism;Copper theft | [6 empty] | Report of attempted theft of underground cables to NBN Tower, cut wires at ends and tried to pull wires out, exposed cables hanging out. There was no fire, no reported injuries | Services cable;Customer wiring | 2 | 2 | 2 |  | WND013 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43720.6813 |  |  | 14660 | Commercial |  | 20191218PWA_01 | Infrastructure (customer connection) | -37.3123 | 144.5996 | 1 | Powercor | Report | 18514 | 0.033325 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3442 | Newham | Other
The crew made the site safe and a fault-follow up has been raised to replace the stolen 16mm 4/c LV Service Cables. | 1256 Mount Cottrell Rd, Melton South VIC 3338, Australia | 30345282 | Copper theft | [6 empty] | Report received of attempted copper theft at incident location. On arrival crew found a number of pits open and approx. 120 metres of lv service cable had been stolen. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN011 | Copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43750.8083 |  |  | 14661 | Roadway |  | 20191218PWA_02 | Infrastructure (network-based) | -37.7371 | 144.6149 | 1 | Powercor | Report | 18515 | 0.035451 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Service Neutral Conductor termination at the Pole Type Connection Box located at the Reticulation Pole, resulting in a higher than normal impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the Neutral Connection in the Pole Top Connection Box with a IPC and re terminated the O/H Neutral Service Conductor at the Reticulation Pole and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 72 Cox St, Port Fairy VIC 3284, Australia | 33099125 |  |  |  | Corrosion |  | Phase to earth |  | Ms Oscar Petti was in the Bathroom showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet while standing on the wet shower base and metallic waste water outlet. | Connection box | 2 | 2 | 2 |  | KRT022 | Corroded connection | Minor shock | 14/08/2019 17:00 |  |  | 14662 | Roadway |  | 20191218PWA_03 | Infrastructure (network-based) | -38.3848 | 142.2304 | 1 | Powercor | Report | 18517 | 0.032228 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Connection
Fault crews and EIO attended the site to investigate. Upon inspection, it was identified that a possum caused a flashover on the pole top which resulted in the UE protection to operate. The HV preform failed and it dropped into the LV overhead which caused a HVI. The site was isolated and the network was repaired before supply was restored. | UNIT 2 1111-1115 HEATHERTON ROAD, NOBLE PARK VIC 3174 | 628025 |  | Animal |  |  |  |  | 1 | UE received a call that the street light was smoking, sparking and melting plastic onto the road. | Conductor (bare) | 0 | 0 | 0 |  | NP25 | Animal Incident | HV injection | 43781.9132 |  |  | 14667 | Roadway |  | 20191218UTD_02 | Infrastructure (network-based) | -37.9648 | 145.173 | 1 | United Energy Distribution | Report | 18522 | 0.012469 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3174 | Noble Park | Animal
Voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the customer switch board, the water pipes and fixtures the roof of the veranda and other metal fixtures detected voltages ranging from 4 to 12 Volts. Investigations identified the neutral screen service neutral conductor was failing. The attending Powercor line workers removed the damaged neutral screen service and installed a new 2 core aluminium twisted service. All VESI testing was performed and passed. A final NST Test was carried out on the installation by the attending LEI which confirmed a Pass result. The Installation was left ON supply. | 113 BALLANTYNE STREET, THORNBURY VIC 3071 | 30199810 |  |  |  | Corrosion |  | Phase to earth |  | Mr Chris Gowland was cutting the copper water service pipe at the front of the property in an excavation in order to repair the pipe. He received a shock when he made simultaneous contact between the water in the excavation with his hand and his knees on the ground. | Service cable (insulated) | 2 | 2 | 2 |  | NC013 | Deteriorated service line | Minor shock | 17/08/2019 19:45 |  |  | 14669 | Roadway |  | 20191219PWA_01 | Infrastructure (network-based) | -37.7576 | 144.9914 | 1 | CitiPower | Report | 18524 | 0.010957 | Low voltage AC (<1kV) | Essendon Airport | 3071 | Thornbury | OH Cable
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified an inherent voltage in the Private Overhead Electric Line (POEL) likely caused by voltage drop in the 600 Metre length of O/H Consumers Mains, resulting in a high impedance in the neutral reticulation system. The LEI requested the Report Room to arrange a Fault Crew and LEI to reattend the property at 14:00 Hours 23 August 2019, when the Customer was available to provide access. | 213 NERRUM AVENUE, RED CLIFFS VIC 3496 | 30232336 |  |  |  | Out of balance load |  | Phase to earth |  | Ms Rebecca Mc Kay was in the Bathroom showering when she received an electric shock as she made simultaneous contact with her hand on the metal Shower Tap and her bare feet while standing on the wet shower base and metallic waste water outlet. | Private overhead electric line (POEL) | 2 | 2 | 2 |  | RCT023 | caused by voltage drop in the 600 Metre length of O/H Consumers Mains. | Minor shock | 19/08/2019 16:45 |  |  | 14670 | Residential |  | 20191219PWA_02 | Infrastructure (customer connection) | -34.2892 | 142.216 | 1 | Powercor | Report | 18525 | 0.023418 | Low voltage AC (<1kV) | Mildura Airport | 3496 | Red Cliffs | Installation
Voltage tests between an independent earth at the points of contact and various points of the electrical installation, including distribution assets, revealed a broken neutral conductor within the twisted service. CP fault truck replaced the service cable to the property CTA completed required VESI recording pass results | UNIT 2 22 WESTBURY STREET, ST KILDA EAST VIC 3183 | 30218827 |  |  |  | Corrosion |  | Phase to earth |  | Vincent received an electric shock when he made simultaneous contact between the metallic shower taps with his hands and the metal shower waste with his feet. | Service cable (insulated) | 2 | 2 | 2 |  | BC015 | neutral failure in service line | Minor shock | 19/08/2019 7:00 |  |  | 14671 | Residential |  | 20191219PWA_03 | Infrastructure (network-based) | -37.8605 | 144.9969 | 1 | CitiPower | Report | 18526 | 0.034448 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | St Kilda East | OH Cable
Protection operated as designed. Site made safe and pole replaced. | 52 GLENELG STREET, COOLAROO VIC 3048 | A039091 |  |  |  | Defective component |  | Phase to earth | 1 | Subtransmission pole A039091 in easement off Glenelg St in Coolaroo snapped midpole between high voltage and subtransmission crossarms, resulting in 66kV line falling to ground and causing damage to high voltage conductors and communication cable. No injuries were sustained. 30m2 grass fire extinguished by Fire Services. 437 customers initially impacted, 36 customers left off supply to make repairs. Secondary fault was also found - white phase HV conductor down at midspan isolators at Hume Highway west side south of Hume-Stanley substation. | Pole (wood) | 0 | 0 | 0 |  | 66Kv BD-VCO & ST12 | Structural pole defect (in the form of multiple knots) | Grassfire | 29/12/2019 6:23 | 1 | Small: 10 - 1000 sq.m | 14702 | Industrial |  | 20191229JEM_01 | Infrastructure (network-based) | -37.6483 | 144.9343 | 1 | Jemena | Report | 19882 | 0.018782 | 22kV AC;66kV AC | Essendon Airport | 3048 | Coolaroo | Pole
On arrival crew isolated supply and carried out repairs. | Ballarat-Daylesford Rd, Newlyn VIC 3364, Australia | 33005282 |  |  |  | Corrosion |  |  |  | Vic fire reported a ground fire at the incident location. Upon arrival, a Powercor crew found an overheated isolator connection had burnt out dropping molten particles on the the grass below. This resulted in a 120 sq section of roadside being burnt. There was no reported injuries or third party property damage, | Disconnector/isolator | 2 | 2 | 2 |  | BAN008 | Overheated connection | Grassfire | 24/12/2019 13:04 | 1 | Small: 10 - 1000 sq.m | 14703 | Roadway |  | 20191230PWA_01 | Infrastructure (network-based) | -37.444 | 143.9805 | 1 | Powercor | Report | 18565 | 0.033397 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3364 | Newlyn | Connection
On arrival crew isolated supply and carried out repairs. | 204 Balkins Rd, Hamilton VIC 3300, Australia | 30090118 |  |  |  | Corrosion |  |  |  | Customer reported burnt out mains box. When crews arrived they found a failed FOLCB on Substation pole. There was small spots of burning amongst the long grass at the base of the pole. There was no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | HTN006 | Overheated connection | Grassfire | 24/12/2019 16:22 | 1 | Localised: less than 10 sq.m | 14704 |  |  | 20191230PWA_02 | Infrastructure (network-based) | -37.7197 | 141.9629 | 1 | Powercor | Report | 18566 | 0.030586 | Low voltage AC (<1kV) | Hamilton Airport | 3300 | Hamilton | Connection
Site mad safe lantern to be replaced | 35 Pleasant Rd, Hawthorn East VIC 3123, Australia | 30201569 |  |  |  | Overheated connection |  |  |  | Report received of street light on fire. Crew attended to find public light lantern had caught fire and was burnt out. Fire had self extinguished. No ground fire. | Public lighting | 2 | 2 | 2 |  | CL011 | No cause established due to damage sustained | Pole-top fire | 24/12/2019 22:15 | 1 | Negligible: no ground fire | 14705 | Roadway |  | 20191230PWA_03 | Infrastructure (network-based) | -37.8346 | 145.0507 | 1 | CitiPower | Report | 18567 | 0.0050972 | Low voltage AC (<1kV) | Moorabbin Airport | 3123 | Hawthorn East | AF Other
On arrival branch has been pruned away form the line. | 14 Grauers Rd, Allansford VIC 3277, Australia | 32198150 |  | Blown branch/vegetation | [5 empty] | Vicfire reported branch landed on conductors causing sparking and grass fire. On arrival crew reported small grass fire under line (1m*1m) started by customer's tree branch contacting 22kV overhead conductors outside the incident address. Fire is out and branch has been pruned away form the line. | Conductor (bare) | 2 | 2 | 2 |  | WBL002 | Vegetation: Trees Incident | Grassfire | 30/12/2019 11:00 | 1 | Localised: less than 10 sq.m | 14715 |  |  | 20191231PWA_01 | Infrastructure (network-based) | -38.3859 | 142.6078 | 1 | Powercor | Report | 18599 | 0.0094016 | 22kV AC | Warrnambool Airport Ndb | 3277 | Allansford | Trees
MFB & CFA extinguishing the fire. Powercor to repair / replace damage to substation when safe to do so. More tin sheets on the warehouse appear to be loose and may come down. Crew to wait for wind to ease or sheets to be secured before making repairs. | 38 Dohertys Rd, Laverton North VIC 3026, Australia | PA0121380 | Blown detritus | Wind | [5 empty] | Vic fire requested attendance required at factory fire. Some tin roof has blown onto HV conductors and caused a grassfire . Crew advise that a tin roofing sheet has come loose in strong winds and has been blown of the warehouse at 38 Dohertys Road onto its substation known as Dohertys 34-Cherry. Resulting in substation fire and a large grass fire in a vacant paddock to its east. Grass fire approximately 50m*300m. Grass fire has been extinguished by the CFA & MFB who were on site. There were no reported injuries. | Outdoor | 2 | 2 | 2 |  | LVN032 | Wind blown roof sheeting landed on substation | Grassfire | 30/12/2019 13:15 | 1 | Medium: 1000 sq.m - 10 ha | 14716 | Commercial |  | 20191231PWA_02 | Infrastructure (network-based) | -37.8286 | 144.8078 | 1 | Powercor | Report | 18644 | 0.031049 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Other
Site made safe HV crossarm and HV fuses replaced, network restored | 53 RACHELLE ROAD, KEILOR EAST VIC 3033 | A058363 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to earth leakage, resulting in HV powder-filled fuse unit coming down onto LV conductor No high voltage injection (cleared by inspector) | Conductor (bare);Powder filled | 0 | 0 | 0 |  | AW06 | Earth leakage | Pole-top fire | 31/12/2019 4:02 | 1 | Negligible: no ground fire | 14746 | Residential |  | 20200103JEM_01 | Infrastructure (network-based) | -37.746 | 144.8721 | 1 | Jemena | Report | 18612 | 0.012019 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3033 | Keilor East | Crossarm
Site made safe and HV crossarm replaced Network restored HVI Claim JEN 1903, Claim on 57 greenvale Drive | 58 GREENVALE DRIVE, GREENVALE VIC 3059 | A041739 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to earth leakage Photos are not available for this incident | Conductor (bare) | 0 | 0 | 0 |  | COO21 | Earth leakage | Pole-top fire;HV injection;Loss of supply;Damage to network assets | 31/12/2019 4:44 | 1 | Negligible: no ground fire | 14747 | Residential |  | 20200103JEM_02 | Infrastructure (network-based) | -37.6431 | 144.8866 | 1 | Jemena | Report | 19711 | 0.0076308 | 22kV AC | Melbourne Airport | 3059 | Greenvale | Crossarm
NAO instructed crew to remove the LV service cable but to leave meters, NAO felt it best for crew to make safe & avoid interaction with the resident. Bendigo police contacted. It is anticipated that supply would need to be restored to premise some time in near future when the welfare of the customer is established by police. | 20 WESLEY STREET, KANGAROO FLAT VIC 3555 | 75453380 | Unauthorised access | [6 empty] | Crew were sent to a abolishment demand from resident Upon arrival crew confirmed that customer attempted to cut through the LV service cable, he brought out a knife stating that he had attempted to cut through the service with that very knife. Crew briefly questioned the customer, whether they had received a shock attempting to cut through the service, he claimed he did not receive a shock. Customer claimed that he was being charged too much for electricity and wanted to permanently removed supply to dwelling ( in residential area ). There was no fire, no reported shock. | Service cable (insulated) | 2 | 2 | 2 |  | BET006 | Interference to service line by customer | Damage to network assets | 28/03/2020 15:00 |  |  | 15390 | Residential |  | 20200331PWA_01 | Infrastructure (customer connection) | -36.8021 | 144.2388 | 1 | Powercor | Report | 19483 | 0.0267 | Low voltage AC (<1kV) | Bendigo Airport | 3555 | Kangaroo Flat | Other
fault crew replaced NS service cable | 31 WILLIAM STREET, LORNE VIC 3232 | 32069292 |  |  |  | Corrosion |  |  |  | Person was in bathroom showering and reported tingles from taps | Service cable (insulated) | 0 | 0 | 0 |  | CLC014 | corroded connection on service cable | Minor shock | 43658.375 |  |  | 15397 | Residential |  | 20200331PWA_07 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | Powercor | Report | 19512 | 0.011527 | Low voltage AC (<1kV) | Moorabbin Airport | 3232 | Lorne | Connection
fault truck attended and removed service | 26 KAMBALDA CIRCUIT, KINGS PARK VIC 3021 | 32177641 |  |  |  | Electrical breakdown;Mechanical breakdown |  |  |  | person reported receiving shocks from concrete pathway and grass in back yard | Service cable (insulated) | 0 | 0 | 0 |  | SA009 | Replacement guttering had penetrated active insulation of service cable at POA | Minor shock | 27/11/2019 16:00 |  |  | 15402 | Residential |  | 20200331PWA_12 | Infrastructure (customer connection) | -37.7314 | 144.7717 | 1 | Powercor | Report | 19496 | 0.016836 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kings Park | OH Cable
Fault crews attended the site to investigate. Upon inspection, it was identified that the white phase active was burnt at POA. There was no actual fire on crew arrival. The site was isolated and made safe. The white phase connection was replaced. | 13 LANYON STREET, DANDENONG SOUTH VIC 3175 | 24599 |  |  |  | Overheated connection |  |  | 1 | UE received a call from a customer that the service wire where it connects to the hook on the property was on fire but is now only smoking. | Connector/termination | 0 | 0 | 0 |  | DSH31 | the cause is likely to be a loose connection which overheated. | Plant/equipment | 18/02/2020 8:40 | 1 | Negligible: no ground fire | 15403 | Residential |  | 20200331UTD_01 | Infrastructure (network-based) | -38.0175 | 145.2212 | 1 | United Energy Distribution | Report | 19497 | 0.011215 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong South | Connection
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was cut. The service wire was replaced and supply was restored. | 190A BURKE ROAD, GLEN IRIS VIC 3146 | 2310635 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a hedge trimmer contractor has cut the service wire while gardening and the wire is broken in the middle with both ends still connected. | Service cable (insulated) | 0 | 0 | 0 |  | K2 | The person was working too close to the service line. | Loss of supply;No Go Zone (contact) | 31/03/2020 14:40 |  |  | 15413 | Residential |  | 20200401UTD_02 | Infrastructure (network-based) | -37.8589 | 145.0516 | 1 | United Energy Distribution | Report | 19525 | 0.00051968 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Other
Field crews attended site and replaced replaced the LV pole and all associated assets | 6 Rosine Ct, Doncaster VIC 3108, Australia | 7069742 |  |  |  | Mechanical breakdown |  | Phase to earth | 2 | UE received a customer report that a pole was on fire in front of 6 Rosine Court Doncaster, there was no smoke at this time - a crew was dispatched | Pole top;Service cable (insulated) | 0 | 0 | 0 |  | WD34 | An LV service rubbing against XArm strap cause over time has caused fire damage on the pole top. | Pole-top fire | 44136.4417 | 1 | Negligible: no ground fire | 15418 | Residential |  | 20200402UTD_01 | Infrastructure (network-based) | -37.7786 | 145.112 | 1 | United Energy Distribution | Report | 19526 | 0.0079433 | Low voltage AC (<1kV) | Moorabbin Airport | 3108 | Doncaster | Pole
Site made safe | 39 MASON STREET, RESERVOIR VIC 3073 | A057741 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address today with a Supply Order to abolish 1 phase underground supply and metering. When they arrived they found the electricity meter had already been disconnected and sitting inside the switchboard metering enclosure and all the meter panel wiring removed. The incoming line side of the service fuse was still live. | Smart meter;Switchboard;Customer wiring | 0 | 0 | 0 |  | CN7 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43865.6076 |  |  | 15425 | Residential |  | 20200403JEM_01 | Infrastructure (network-based) | -37.7283 | 145.0072 | 1 | Jemena | Report | 19534 | 0.032878 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
Attending LEI conducted voltage test between an independent earth and the meter panels at 13 and 14 Ruthven Close recording 230V at each of them indicating a broken neutral conductor. Upon investigation the LEI and attending faults crew were able to identify a broken neutral network neutral conductor at the pit feeding 13 and 14 Ruthven. The red phase IPC had melted away also exposing live terminals. The attending faults crew carried out a damage assessment of the network conductors and replaced all IPC's. The attending LEI conducted an insulation resistance (IR) test and damage assessment of the consumer mains feeding each property. 14 Ruthglen had no signs of damage, passed all insulation resistance tests and was right to reconnect. The consumer mains of 13 Ruthglen were damaged and due to this a defect notice was issued and it was left off supply. The street light fed out of the pit was also damaged and left off supply with the Jemena faults crew reporting to be repaired at a later date. Following reconnection all VESI tests at 14 Ruthglen passed, with 0 volts now present on the meter panel. The installation was left on supply. | 14 RUTHVEN CLOSE, HILLSIDE VIC 3037 | A075734 |  |  |  | Neutral fault |  |  | 2 | The residents at 14 Ruthven Close noticed there lights flickering and turning off, plus their appliances not working. At this stage they called an registered electrical contractor (REC) to investigate further. Upon arrival the REC Nick Kyriakov received an electric shock whilst making simultaneous contact with his are hand to the meter panel and the ground in which he was standing, he was wearing rubber sole work boots at the time. At this stage Jemena was called by the REC to report the electrical pit in front of property is "filled with mud and steam is coming out". REC also reported that the customer switchboard is live and he had received a minor tingle. | Cable;Connector/termination;Services pit (customer);Switchboard;Customer wiring | 0 | 0 | 0 |  | SHM22 | Broken neutral (network neutral conductor) in pit | Minor shock;Melting or smoking only | 43955.7292 |  |  | 15432 | Residential |  | 20200405JEM_01 | Infrastructure (customer connection) | -37.6856 | 144.7539 | 1 | Jemena | Report | 19541 | 0.0089051 | Low voltage AC (<1kV) | Melbourne Airport | 3037 | Hillside | UG Cable
Faulted Section isolated, repairs made and customers restored. | 23 BALLARTO ROAD, CLYDE VIC 3978 | 521036 & 521037 | Working too close to overhead lines | [5 empty] | 1 | Tip Truck contact HV line. | Conductor (bare) | 0 | 0 | 0 |  | CLN22 | Tip Truck contact HV open wire. Breach of No Go Zone. | Loss of supply | 43986.4931 |  |  | 15440 |  |  | 20200407SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19556 | 0.038995 | 22kV AC | Moorabbin Airport | 3978 | Clyde | Vehicle
live wires made safe and repairs initiated by maintenance crews | 1-15 BEDDISON ROAD, CRAIGIEBURN VIC 3064 | A090985 | Copper theft | [5 empty] | 2 | Copper theft of LV street light underground cable from public lighting circuit along Aitken Boulevard Craigieburn (opposite 13 Beddison Road) | Services cable | 0 | 0 | 0 |  | ST22 | Copper theft | Loss of supply;Damage to network assets | 44139.4215 |  |  | 15451 | Roadway |  | 20200411JEM_01 | Infrastructure (network-based) | -37.5782 | 144.9189 | 1 | Jemena | Report | 19571 | 0.0015706 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Found on arrival asset enclosure lock opened (not damaged) and 2 outside phase HV fuses opened @ LIS# 1224009. LV was isolated and HV fuses was replaced and customer supply restored. The removed HV fuses was tested and found OK. Reported to police. | 29 HOLLOWAY DRIVE, BAYSWATER VIC 3153 | 1224009 | Vandalism | [6 empty] | Vandalism, 22kV, Transformer HV fuses, HV fuses deliberately opened, LIS# 1224009. | Any other type | 0 | 0 | 0 |  | BWR22 | Vandalism. | Loss of supply | 44108.3396 |  |  | 15463 |  |  | 20200414SPN_02 | Infrastructure (network-based) | -37.8506 | 145.2814 | 1 | AusNet Services Distribution | Report | 19585 | 0.014949 | 22kV AC | Moorabbin Airport | 3153 | Bayswater | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the public lighting underground cable was damaged by third party digging. The site was isolated and made safe and the cable was repaired. | 104 MCCRAE STREET, DANDENONG VIC 3175 | 8812765 | Working too close to underground cables | [5 empty] | 1 | UE was advised that a contractor has hit an underground cable in the medium strip under tree roots. | Cable;Public lighting | 0 | 0 | 0 |  | DN6 | The person was working too close to the underground cable. | No Go Zone (contact) | 25/03/2020 12:00 |  |  | 15455 | Roadway |  | 20200414UTD_01 | Infrastructure (network-based) | -37.9929 | 145.2214 | 1 | United Energy Distribution | Report | 19575 | 0.021514 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong | Dug up
Faults crew attended the site to investigate. Upon inspection, it was identified that 2 LV poles were damaged and required replacements. Service lines to 2 premises were also damaged as well as the Telstra mains across the road. | 27 NEW STREET, BRIGHTON VIC 3186 | 1808474 | Working too close to overhead lines | [5 empty] | 1 | UE was advised that a truck with forklift (XV94HU) has hit lines with multiple lines down and the pole is leaning. | Conductor (bare) | 0 | 0 | 0 |  | MR32 | It is likely the person was working too close to the overhead lines. | Loss of supply;No Go Zone (contact) | 43865.4792 |  |  | 15464 | Roadway |  | 20200414UTD_03 | Infrastructure (network-based) | -37.9289 | 144.9937 | 1 | United Energy Distribution | Report | 19586 | 0.025388 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Vehicle
On arrival crew isolated supply and carried out repairs. | 41 GEELONG ROAD, BANNOCKBURN VIC 3331 | 32075596 | Working too close to overhead lines | [6 empty] | A contractor reported a crane contacted LV mains at the incident location. Upon arrival, a Powercor fault crew found a LV conductor on the ground. There was no fire, no no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GL012 | Crane unloading material struck LV | No Go Zone (contact) | 43894.4722 |  |  | 15475 | Roadway |  | 20200415PWA_03 | Infrastructure (network-based) | -38.045 | 144.1786 | 1 | Powercor | Report | 19601 | 0.0076354 | Low voltage AC (<1kV) | Avalon Airport | 3331 | Bannockburn | Vehicle
Network Operator carried out isolations to make safe. HV droppers and HV pin insulators were replaced. | 4 INTERNATIONAL SQUARE, TULLAMARINE VIC 3043 | A043158 | Blown detritus | Blown branch/vegetation |  |  |  | Phase to phase | 1 | Report of "explosion" from 67 Churchill Avenue, Tullamarine. HV conductors down on Churchill Avenue north of Janus Street at cable head pole (INTERNATIONAL 5-T'PARK substation), resulting in damage to HV bridges and cable head pole. Inspector confirmed HV injection into LV Airborne conductive debris of unknown description and unknown origin got across the bare HV mains, resulting in a flashover. There was no evidence of a bird or animal. There was a dead tree branch in the adjacent trees, but it is not conclusive if that was the source of debris. There is sufficient clearance between the trees and HV conductors. | Conductor (bare);Insulators;Dropper/bridge | 0 | 0 | 0 |  | AW4 | Vegetation: Trees Incident | HV injection;Damage to network assets | 16/04/2020 4:43 |  |  | 15477 | Commercial |  | 20200416JEM_01 | Infrastructure (network-based) | -37.6972 | 144.8713 | 1 | Jemena | Report | 19617 | 0.023264 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3043 | Tullamarine | Other
The low voltage underground cable was repaired and customers restored. No damage to the HV cable but conduit required repair. | 53 IRELAND STREET, WEST MELBOURNE VIC 3003 | 30182203 | Working too close to underground cables | [6 empty] | An underground faults team attended a low voltage fault. They located the fault site and excavated. They found that a third party had installed a bore through a CitiPower conduit bank and had damaged the low voltage cable resulting in cable failure. There was also a H.V cable that had to be isolated to be checked for damage, There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | LS016 | Horizontal bore through cable | No Go Zone (contact);Damage to network assets | 43925.7167 |  |  | 15487 | Roadway |  | 20200417PWA_02 | Infrastructure (network-based) | -37.8072 | 144.9446 | 1 | CitiPower | Report | 19616 | 0.033245 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Dug up
CFA called to extinguish fire. Isolated supply and made safe. U/G crew called to repair LV U/G. Switched circuits to restore supply to Queens St. On arrival found LV 185mm Bus cable melted and damage to transformer Isolators. Crew Completed isolation / arrange Back feed for all customer except Tafe and the Coffee shop at rail station. Crew carried out following repairs: Replace the 185MM from TX to LV Bus Isolators Replace 3 damaged Webber strip Restored supply this included replacing HV PFD 25 amp x 3 Note red phase blown | 112-118 QUEEN STREET, WARRAGUL VIC 3820 | 2717552 |  |  |  | Electrical breakdown |  |  | 2 | Fire at LV switchboard | Indoor | 0 | 0 | 0 |  | WGL15 | Likely cause electrical breakdown of insulation within the switchboard. | Plant/equipment | 43894.6986 | 1 | Negligible: no ground fire | 15488 | Commercial |  | 20200417SPN_01 | Infrastructure (network-based) | -38.1645 | 145.933 | 1 | AusNet Services Distribution | Report | 19619 | 0.012506 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3820 | Warragul | AF Other
On arrival crew isolated supply and carried out repairs. | 411 BROWN ROAD, ECHUCA VILLAGE VIC 3564 | 30125952 |  | Fallen;Property owner/customer | [5 empty] | Call from customer advising tree down on mains wires, sparking and starting to catch fire and CFA had been called. On arrival crew found a large branch had fallen. The tree is located on private property on the opposite side of the road from the HV line. HV conductor was down but no ground fire was evident. Burn marks identified on branch. No ground fire, no injuries, no third party damage. | Conductor (bare) | 2 | 2 | 2 |  | ECA005 | Vegetation: Trees Incident | Other vegetation | 18/04/2020 17:59 | 1 | Negligible: no ground fire | 15490 | Roadway |  | 20200420PWA_02 | Infrastructure (network-based) | -36.1485 | 144.8227 | 1 | Powercor | Report | 19621 | 0.040631 | 22kV AC | Shepparton Airport | 3564 | Echuca Village | Trees
On arrival crew isolated supply and carried out repairs. | 21 AZOLIA STREET, RED CLIFFS VIC 3496 | 32152465 |  |  |  | Leakage |  |  |  | Customer reported wooden x-arm on power pole has caught fire, wires do not look damaged yet, burning into pole. OK, customer will call Emergency Services. On arrival crew found pole fire was at king bolt of LV Xarm. Made safe, no ground fire, CFA attended. No reported injuries or third party property damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | RCT023 | Excessive leakage current | Pole-top fire | 23/04/2020 17:57 | 1 | Negligible: no ground fire | 15505 | Roadway |  | 20200424PWA_01 | Infrastructure (network-based) | -34.2927 | 142.1987 | 1 | Powercor | Report | 19643 | 0.023785 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Referred to ESV and worksafe | 284 DORCAS STREET, SOUTH MELBOURNE VIC 3205 | 30170726 | Building too close or within the No Go Zone | [5 empty] | 2 | Citipower crew identified scaffolding had encroached no go zone and custom cable covering had been fitted to servcie line/s | Service cable (insulated) | 0 | 0 | 0 |  | AP006 | Interference by scaffolding installer | No Go Zone (contact) | 24/04/2020 14:00 |  |  | 15507 | Construction |  | 20200424PWA_03 | Infrastructure (network-based) | -37.834 | 144.9566 | 1 | CitiPower | Report | 19648 | 0.039402 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Other
Crew made safe assets and reconnected cable, resupplying power to street light. | 275 RACECOURSE ROAD, SUNBURY VIC 3429 | A146748 | Copper theft | [5 empty] | 2 | Attempted copper theft of underground services cable at corner of Racecourse Road and Elizabeth Drive, Sunbury. Unknown persons had cut 2core 16mm cable but did not remove the cable. | Services cable;Services pit (network);Copper;Public lighting | 0 | 0 | 0 |  | SBY23 | Attempted copper theft | Damage to network assets | 25/04/2020 14:49 |  |  | 15512 | Roadway |  | 20200425JEM_01 | Infrastructure (network-based) | -37.5571 | 144.7341 | 1 | Jemena | Report | 19653 | 0.015383 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Tree Branch was removed under shutdown - no damage to conductors | 58-62 ALLISON ROAD, MOUNT ELIZA VIC 3930 | 3315364 |  | Blown branch/vegetation |  |  |  |  | 1 | Customer tree branch at 62 Alison Rd fell through HV and was resting on LV when crew arrived. Branch removed under shutdown. No damage to HV/LV conductors. CFA had reported sparking and flames. LIS 3315364 | Conductor (bare) | 0 | 0 | 0 |  | FSH 12 | Vegetation: Trees Incident | Other vegetation | 22/04/2020 9:37 | 1 | Negligible: no ground fire | 15517 | Residential |  | 20200427UTD_02 | Infrastructure (network-based) | -38.2002 | 145.1162 | 1 | United Energy Distribution | Report | 19659 | 0.013691 | 22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Trees
Faults crew attended the site to investigate. Upon inspection, it was identified that the cables were still live. The site was isolated and made safe. The pit was reinstalled and the cables were repaired. | 26 FROST STREET, CARRUM DOWNS VIC 3201 | 3448707 | Working too close to underground cables | [5 empty] | 1 | UE was advised that a bob cat has clipped the top of pit lid and pulled the pit out of the ground, exposing the cable. The pit was covered by rubbish and was not seen. | Services cable;Services pit (network) | 0 | 0 | 0 |  | CRM14 | the cause is working to close to underground assets and the pit was covered by rubbish and was not seen. | No Go Zone (contact) | 17/04/2020 15:15 |  |  | 15523 | Roadway |  | 20200428UTD_02 | Infrastructure (network-based) | -38.096 | 145.1777 | 1 | United Energy Distribution | Report | 19666 | 0.0026412 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Dug up
Faults crew attended the site to investigate. Upon inspection, it was identified that a private contractor engaged by Safety Beach Sailing Club damaged LV UG cable adjacent to MARINE SAILCLUB s/s. A NGZ request was not received for this site. The site was isolated and made safe. The cable was repaired. | 185 MARINE DRIVE, SAFETY BEACH VIC 3936 | 1302688 | Working too close to underground cables | [5 empty] | 1 | UE was advised drilling rig has hit u/g cable inside the sailing club which they suspect maybe HV cable. | Cable | 0 | 0 | 0 |  | DMA14 | the person was working too close to the underground cable. | No Go Zone (contact) | 23/04/2020 22:05 |  |  | 15527 | Other | sailing club | 20200428UTD_04 | Infrastructure (network-based) | -38.3076 | 144.9943 | 1 | United Energy Distribution | Report | 19672 | 0.0096725 | Low voltage AC (<1kV) | Moorabbin Airport | 3936 | Safety Beach | Dug up
Jemena has issued a defect on the property and will not connect it until the defect is resolved | 25 REGENT STREET, PRESTON VIC 3072 | A080687 | Unauthorised access |  |  |  | Unauthorised REC work |  | 2 | Metering and servicing crew went to site to perform abolishment for supply and metering, but could not complete works due to presence of asbestos The abolisment was rescheduled pending on the REC to provide a Certificate of Removal which he said would take him a couple of days Jemena connections officer called the REC who advised that the place has been demolished and that he has removed the meter. Jemena connections officer advised the REC that the meter is Jemenaâ€™s asset and that Jemena needs to make sure the site has been abolished safely to provide clear access for the removal of the overhead service line. REC called Jemena to advise that we can come and collect the meters, it appears that the customer had abolished the supply and metering themselves. | Aluminium twisted (grey);Smart meter | 0 | 0 | 0 |  | PTN15 | Unauthorised access / Unauthorised REC work | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44047.3993 |  |  | 15537 | Residential |  | 20200430JEM_01 | Infrastructure (network-based) | -37.7306 | 145.002 | 1 | Jemena | Report | 19682 | 0.0019838 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Crew Installed LV spreader and isolated LV Crew Replaced LV switch | 55-59 HOPKINS STREET, FOOTSCRAY VIC 3011 | A090499 |  |  |  | Overheated connection |  |  | 2 | LV Krone Box failed and burnt out | Disconnector/isolator | 0 | 0 | 0 |  | FE6 | Krone switch failure | Other electricity related | 44016.7083 | 1 | Negligible: no ground fire | 15551 | Roadway |  | 20200505JEM_02 | Infrastructure (network-based) | -37.8007 | 144.9048 | 1 | Jemena | Report | 19708 | 0.0051748 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Connection
Fault crews removed the service and meter from the site. It appears the house was being demolished while it was still supplied from street mains. | 34 WERE STREET, BRIGHTON VIC 3186 | 1805589 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | During the process of demolishing the house, the service wire was hit and has come down. people onsite have already touched it and they are okay. They have been advised to stay clear of the wire. | Conductor (insulated) | 0 | 0 | 0 |  | MR32 | The overhead service was not abolished before commencing works to demolish the house. | No Go Zone (contact) | 43956.4514 |  |  | 15553 | Residential |  | 20200506UTD_02 | Infrastructure (network-based) | -37.9248 | 144.9914 | 1 | United Energy Distribution | Report | 19714 | 0.030326 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Vehicle
Isolator replaced by fault crew | 422 CANTERBURY ROAD, FOREST HILL VIC 3131 | 7020345 |  |  |  | Corrosion;Electrical overload |  |  | 2 | A LV red phase fused isolator overheated and dropped hot molten metal into a small tree which caused some small scotch marks on the tree | Disconnector/isolator | 0 | 0 | 0 |  | NW33 | Likely cause was overload or corrosion on contacts | Other vegetation | 43956.766 | 1 | Localised: less than 10 sq.m | 15568 | Residential |  | 20200512UTD_01 | Infrastructure (network-based) | -37.8353 | 145.1759 | 1 | United Energy Distribution | Report | 19739 | 0.006581 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Forest Hill | Connection
Pole mounted FMB Replaced - | UNIT 1 1 ORMOND ESPLANADE, ELWOOD VIC 3184 | 2308954 |  |  |  | Corrosion |  |  |  | Emergency services reported a pole on fire - a UE fault crew attended fire and was extinguished | Connection box | 0 | 0 | 0 |  | EW12 | Near beach - Likely Corrosion | Plant/equipment | 43987.7924 | 1 | Negligible: no ground fire | 15569 | Residential |  | 20200512UTD_02 | Infrastructure (network-based) | -37.8821 | 144.9784 | 1 | United Energy Distribution | Report | 19738 | 0.019863 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | Connection
The crews have disconnected, abolished and made safe the existing overhead service line and completed the 2 x new group metering connections. | 385 BUCKLEY STREET, ABERFELDIE VIC 3040 | A001104 | Unauthorised access |  |  |  | Unauthorised REC work |  | 2 | M&S crews attended the above address today with Supply Orders for an abolishment of overhead supply and metering to a single residence in conjunction with 2 new connections for 2 dwellings (existing front dwelling and rear new dwelling), group metered from a new underground supply pit. When the crew arrived they found the existing overhead supply to the front dwelling had been fully enclosed and surround by a new extension to the existing front dwelling. The overhead service was passing through a new brick wall and into the ceiling space of the renovated property. The existing POA and FOLCB was completely inaccessible in the internal renovation and extension completed with the existing POA and FOLCB located somewhere within the ceiling cavity space. | Connection box;POA connection (network side) | 0 | 0 | 0 |  | ES16 | Unauthorised access / unauthorised REC work | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43956.6361 |  |  | 15576 | Residential |  | 20200514JEM_02 | Infrastructure (network-based) | -37.7546 | 144.8945 | 1 | Jemena | Report | 19750 | 0.033387 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Aberfeldie | Other
Crew sent to site, MFB on site extinguished fire - service line for light isolated and made safe. | 436-440 MAROONDAH HIGHWAY, CROYDON VIC 3136 | 1220282 |  |  |  | Electrical breakdown |  |  | 2 | Street light head fire | Public lighting | 0 | 0 | 0 |  | CYN32 | Dedregation of grey twisted service supplying the pole has made contact with the pole or conductors on the pole. | Pole-top fire | 13/05/2020 21:33 | 0 | Negligible: no ground fire | 15574 | Residential |  | 20200514SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19748 | 0.010243 | Low voltage AC (<1kV) | Moorabbin Airport | 3136 | Croydon | AF Other
FOLCB and leads replaced, supply restored | 276 TOMAHAWK CREEK ROAD, SIMPSON VIC 3266 | 33035709 |  |  |  | Overheated connection |  |  |  | person advd fuse box half way up pole has caught on fire, fuse box may need replacing, pole is near the dairy, cust and dairy, access ok. On arrival crew found leads fuse box had burn damaging leads. There was no ground fire, no reported injuries or third party property damage | Connection box | 0 | 0 | 0 |  | CDN001 | loose / overheated connection | Pole-top fire | 13/11/2019 7:58 | 1 | Negligible: no ground fire | 15586 | Agricultural |  | 20200515PWA_05 | Infrastructure (network-based) | -38.4967 | 143.2404 | 1 | Powercor | Report | 19763 | 0.006713 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3266 | Simpson | Connection
Crew attended and replaced cross-arm | 15 KIEWA STREET, NERRINA VIC 3350 | 30003432 |  |  |  | Leakage |  |  |  | Inspector reports burnt HV crossarm near HV fuse mount at incident location no ground fire | Crossarm (wood) | 0 | 0 | 0 |  | BAN011 | Leakage current presumed | Pole-top fire | 18/12/2019 11:52 | 1 | Negligible: no ground fire | 15594 | Roadway |  | 20200518PWA_01 | Infrastructure (network-based) | -37.5339 | 143.8841 | 1 | Powercor | Report | 19771 | 0.014595 | 22kV AC | Ballarat Aerodrome | 3350 | Nerrina | Crossarm
Line Isolated and cross-arm replaced | QUEEN STREET, ALTONA VIC 3018 | 32178028 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location no ground fire | Crossarm (wood) | 0 | 0 | 0 |  | LVN022 | attributed to leakage | Pole-top fire | 20/12/2019 14:28 | 1 | Negligible: no ground fire | 15596 | Roadway |  | 20200518PWA_03 | Infrastructure (network-based) | -37.8753 | 144.7953 | 1 | Powercor | Report | 19773 | 0.028809 | 22kV AC | Laverton Raaf | 3018 | Altona | Crossarm
Fuse holder replaced | 19 TOLSON STREET, SHELFORD VIC 3329 | 31034200 |  |  |  | Fuse failed to eject |  |  |  | Crew attending outage found Burnt off Edo fuse tube | EDO fuse | 0 | 0 | 0 |  | GL012 | Fuse Mal-Operation | Pole-top fire | 23/12/2019 7:25 | 1 | Negligible: no ground fire | 15606 | Roadway |  | 20200518PWA_08 | Infrastructure (network-based) | -38.0115 | 143.9728 | 1 | Powercor | Report | 19788 | 0.010615 | 22kV AC | Avalon Airport | 3329 | Shelford | Fuse
Crew made safe and restored supply | 1-3 VIEW ROAD, THE PATCH VIC 3792 | 1321440 |  |  |  | Candled fuse |  |  | 0 | Dimm Lights reported by customers in View rd the patch, Candled HV fuse at CAMMS PATCH S/S | Any other type | 0 | 0 | 0 |  | BGE11 | Found HV fuses were 6k BA Fuses and are wrong fuse rating f or a 200kva. Upgraded all 3 existing 6k HV fuses to 15e BA Fuses at Camm s'Patch S \S. Tested LV off load and on load volts were good | Pole-top fire;Loss of supply | 18/05/2020 6:30 | 1 | Negligible: no ground fire | 15602 | Residential |  | 20200518SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19917 | 0.038858 | 22kV AC | Moorabbin Airport | 3792 | The Patch | Fuse
Upon arrival crew made the area safe and isolated. pole replaced | Maryborough-st Arnaud Rd, Rathscar VIC 3465, Australia | 32024807 | Crane, excavator or other construction/farming equipment | [6 empty] | Vicfire advised of fire caused by tractor operator hitting pole and bringing it and the overhead conductors to the ground. Tractor operator advised to remain in tractor until PCA crew onsite. On arrival crew found that a tractor/sprayer had collided with a pole . Police and CFA on site There was a small grass fire , no reported in juries or third party proper try damage. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | MRO005 | Tractor hit pole | Grassfire | 18/05/2020 15:38 | 1 | Small: 10 - 1000 sq.m | 15615 | Agricultural |  | 20200519PWA_03 | Infrastructure (network-based) | -36.9653 | 143.5132 | 1 | Powercor | Report | 19802 | 0.011508 | 22kV AC | Ballarat Aerodrome | 3465 | Rathscar | Vehicle
Crew attended and replaced cross-arm | 249 PRINCES HIGHWAY, BOLWARRA VIC 3305 | 32135413 |  |  |  | Leakage |  |  |  | Customer reports fuse hanging off pole. On arrival crew found a cross-arm had burnt at the EDO mounting position | Crossarm (wood) | 0 | 0 | 0 |  | PLD001 | Leakage current | Pole-top fire | 44137.8986 | 1 | Negligible: no ground fire | 15620 | Roadway |  | 20200520PWA_02 | Infrastructure (network-based) | -38.281 | 141.6148 | 1 | Powercor | Report | 19807 | 0.01674 | 22kV AC | Portland (Cashmore Airport) | 3305 | Bolwarra | Crossarm
crew replaced fuse carrier | MUNGARA, 475 HUNTS ROAD, PARAPARAP VIC 3240 | 33045623 |  |  |  | Fuse failed to eject |  |  |  | crew responding to an outage found that a fuse had hung up and burnt | EDO fuse | 0 | 0 | 0 |  | WPD014 | Fuse mal-operation | Pole-top fire;Hung-up fuse only | 20/04/2020 22:46 | 1 | Negligible: no ground fire | 15631 | Roadway |  | 20200520PWA_13 | Infrastructure (network-based) | -38.2604 | 144.2001 | 1 | Powercor | Report | 19818 | 0.023986 | 22kV AC | Avalon Airport | 3240 | Paraparap | Fuse
CitiPower crew made safe by disconnecting the service. A defect notice was issued for the customer to replace the FOLCB. Installation was left OFF supply | 11 TOORAK ROAD, SOUTH YARRA VIC 3141 | 30162436 |  |  |  | Corrosion |  |  |  | Report received from MFB of fuse box fire at incident location. On arrival crew found fire a FOLCB had caught fire . There was no ground fire, no reported injuries or third party property damage | POA connection (network side) | 2 | 2 | 2 |  | R023 | overheated connection | Other electricity related | 22/05/2020 21:17 | 1 | Negligible: no ground fire | 15643 | Residential |  | 20200525PWA_01 | Infrastructure (customer connection) | -37.8382 | 144.9869 | 1 | CitiPower | Report | 19832 | 0.014319 | Low voltage AC (<1kV) | Essendon Airport | 3141 | South Yarra | Connection
On arrival crew isolated supply and carried out repairs | 27 Plante Ct, Strathdale VIC 3550, Australia | 60349574 |  |  |  | Mechanical breakdown |  |  |  | Customer reported electricity pit out front of property was on fire but had been extinguished. Customer reported a number of neighbors with no power and partial power. When crew arrive they found that there had been evidence of a fire in the service pit with melted assets inside. No injuries or third party damage. | Services pit (network) | 2 | 2 | 2 |  | BGO022 | Overheated | Grassfire | 22/05/2020 17:07 | 1 | Localised: less than 10 sq.m | 15645 | Roadway |  | 20200525PWA_03 | Infrastructure (network-based) | -36.7738 | 144.3114 | 1 | Powercor | Report | 19834 | 0.03438 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Strathdale | Connection
Powercor crew attended. A new pit position was excavated. A new LV pit was installed. Services re-terminated. | 2 Sundial Blvd, Tarneit VIC 3029, Australia | 60328844 | Working too close to underground cables | [6 empty] | Report received from Wyndham City Council. A civil sub-contracting party working for Wyndham Council on road extension/widening along Derrimut Rd struck and tore an LV pit out of the ground while using a bobcat. The forced removal of the LV pit tore some pit termination fittings off the cable ends, damaged the 16mm x 4c supply cable to the pit and left live exposed ends. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | LV001 | Excavation works using bobcat | No Go Zone (contact) | 19/05/2020 15:13 |  |  | 15656 | Roadway |  | 20200526PWA_02 | Infrastructure (network-based) | -37.8448 | 144.6892 | 1 | Powercor | Report | 19847 | 0.0019954 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Dug up
First aid was applied and all lines rectified, work was completed. | 1 LONG LANE, MANSFIELD VIC 3722 | 353 |  |  |  | Induced voltage;Other | Failure to use correct PPE;Lack of training | Phase to earth | 2 | Downer linesman received induction shock while breaking bridges on OH, HV conductors | Conductor (bare) | 0 | 0 | 0 |  | BN-MSD | At approximately 11am on the 14th May a Downer linesman was working on a 66/22kV pole with the 66kV alive and the two 22kV circuits on the pole under access permit. The lower circuit 22kV single phase line was earthed either side of the pole. They have also earthed the centre phase of the middle 22kv circuit. The two outer phase conductors of the middle 22kv circuit was also connected through bridgings to the lower 22kv circuit. The lineworker was attempting to break the bridges on one of the outside phases, when he has removed the bridge from the bottom circuit it appears likely that the three-phase circuit had a voltage induced from the live 66kV circuit above resulting in an electric shock. | Minor shock | 14/05/2020 15:47 |  |  | 15654 | Agricultural |  | 20200526SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19845 | 0.010145 | 22kV AC;66kV AC | Moorabbin Airport | 3722 | Mansfield | Other
The crew isolated the supply and carried out repairs. | 55A Belton St, Anglesea VIC 3230, Australia | 30066251 |  |  |  | Unknown technical factor |  |  |  | Vicfire reported a pole fire at the incident location. On arrival the crew found that an LV fused mains box had overheated and failed. The box dropped debris and melted plastic to the ground, but there was no ground fire. here was no other damage or injuries reported. | Connection box | 2 | 2 | 2 |  | WPD021 | Insufficient remains to determine cause | Pole-top fire | 26/05/2020 19:31 | 1 | Negligible: no ground fire | 15660 | Roadway |  | 20200527PWA_02 | Infrastructure (network-based) | -38.4117 | 144.1669 | 1 | Powercor | Report | 19852 | 0.023021 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
On arrival crew isolated supply and carried out repairs. | 76 High St, Koroit VIC 3282, Australia | 30271815 |  |  |  | Corrosion |  |  |  | Emergency services reported a pole fire at incident location. When crews arrived they found a HV insulated dropper lead to Pole type S/S "High-King 42" had failed and required replacement. No evidence or reports received of ground fire starts, injuries or third party property damage | Dropper/bridge | 2 | 2 | 2 |  | KRT013 | HV dropper lead failure | Pole-top fire | 30/05/2020 15:20 | 1 | Negligible: no ground fire | 15676 | Roadway |  | 20200602PWA_02 | Infrastructure (network-based) | -38.2955 | 142.3687 | 1 | Powercor | Notification | 19874 | 0.027381 | 22kV AC | Warrnambool Airport Ndb | 3282 | Koroit | AF Other
Crew sent to remove tree branch and reconnect supply | UNIT 1 2A PORTER STREET, ELTHAM VIC 3095 | 900633 |  | Blown branch/vegetation |  |  |  |  | 1 | Tree branch fell on HV between LIS 900633 - 900674. Feeder outage occurred on ELM34 Branch removed with EPV, chainsaw and traffic management. Reports from public and emergency services that when branch hit line there were sparks or flames and a loud bang. | Conductor (bare) | 0 | 0 | 0 |  | ELM34 | Vegetation: Trees Incident | Pole-top fire | 43925.6729 | 1 | Negligible: no ground fire | 15677 | Residential |  | 20200602SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19934 | 0.018876 | 22kV AC | Moorabbin Airport | 3095 | Eltham | Trees
Single site impacted, no injuries. Crew made safe by isolating supply to site. Reported to WorkSafe and Jemena Works Practices. Defect J01166. Removed service and meter. Meter: 0208914. No reading as customer had already disconnected power. | 35 SALISBURY STREET, NEWPORT VIC 3015 | A083633 | Unauthorised access |  |  |  |  | Phase to earth | 2 | Demolition worker reports equipment has hit service line; sparking & line hanging low (No abolisment SIO) access ok, onsite contact: Moe 0416610105 Third party tampered with LV service while demolishing property in Salisbury St, Newport. Preliminary report from Work Safe is attached and states the following: OnSpot Demolition is contracted to remove a residential property located at the address Upon Jemena's arrival to site they were informed an employee from OnSpot Demolition has struck the overhead power line causing the power line to disconnect from the property Whilst on site Jemena representatives secured the site, ensuring the line was not live and disconnected and removed the cable from the property. | Copper;Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | NT3 | Demolition worker reported that equipment has hit overhead service line Unauthorised access: Jemena concluded that the third party has tampered with LV overhead service while demolishing property | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43927.4069 |  |  | 15687 | Residential |  | 20200604JEM_01 | Infrastructure (network-based) | -37.8464 | 144.8746 | 1 | Jemena | Report | 19894 | 0.011616 | Low voltage AC (<1kV) | Laverton Raaf | 3015 | Newport | Other
Sent srew to investigate and repair | 25 HEAD ROAD, WANDIN EAST VIC 3139 | 1011429 |  |  |  | Fuse failed to eject;Candled fuse |  |  | 1 | Candled fuse at pole 1011429 | EDO fuse | 0 | 0 | 0 |  | LDL23 | Fuse operated as required but did not drop. | Pole-top fire | 43957.5049 | 0 | Negligible: no ground fire | 15700 | Residential |  | 20200605SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19910 | 0.0038924 | 22kV AC | Moorabbin Airport | 3139 | Wandin East | Fuse
PTN11 feeder patrolled and remnants of bark found on overhead lines and on ground in Foch St north Tyler St. Operator removed bark and feeder was restored. Jemena to send details to Darebin Council and work with the council in determining the best solution for cutting away trees from HV overhead lines | 741 and 751 PLENTY ROAD, RESERVOIR VIC 3073 | A031361 and A031364 |  | Within clearances |  |  |  |  | 1 | During daylight patrol of PTN11 feeder post-fault, found 2 locations where trees (responsibility of Darebin council) are growing through HV overhead lines. Trees show signs of burning. | Conductor (bare) | 0 | 0 | 0 |  | PTN11 | Vegetation: Trees Incident | Other vegetation | 43867.9333 | 1 | Negligible: no ground fire | 15710 | Roadway |  | 20200610JEM_02 | Infrastructure (network-based) | -37.7285 | 145.0182 | 1 | Jemena | Report | 19925 | 0.0032396 | 22kV AC | Essendon Airport | 3073 | Reservoir | Trees
On arrival crew isolated supplies, rec's engaged for POA repairs. | 55 McPherson St, Casterton VIC 3311, Australia | 32127817 | Vehicle | [6 empty] | Report received of multiple services on ground and damage to multiple points of attachments. It was reported by the media that a high load had struck multiple power lines. Police were on site directing traffic. Offending vehicle no where to be found. There was no fire, no reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | HTN006 | High load observed by customers | Significant disruption to the community;Damage to network assets | 44049.4972 |  |  | 15708 |  |  | 20200610PWA_01 | Infrastructure (network-based) | -37.5829 | 141.4018 | 1 | Powercor | Report | 19923 | 0.01375 | Low voltage AC (<1kV) | Hamilton Airport | 3311 | Casterton | Vehicle
The crew made the site safe and Isolated the LVABC and arranged repairs. | 9-19 LEAKES ROAD, LAVERTON NORTH VIC 3026 | 30264003 | Working too close to overhead lines | [6 empty] | William (road construction worker) advised wire down as a piece of machinery hit the wire. On arrival the PCA Faults Crew have advised that an excavator undertaking works for the Western Roads Upgrade Project, Winslows / Form 700 has misjudged and made contact with the LVABC running across Leakes Rd. The resultant impact by the excavator has caused the LVABC to snap and fall onto the ground below, The excavator also sustained burn / flash-marks where the impact occurred. There was no reported ground fire, , injury or shocks as a result of this incident. | Conductor (insulated) | 2 | 2 | 2 |  | ATSLV1 | Excavator struck overhead cable (abc) | No Go Zone (contact);Damage to network assets | 29/05/2020 16:14 |  |  | 15715 | Roadway |  | 20200611PWA_02 | Infrastructure (network-based) | -37.8435 | 144.7779 | 1 | Powercor | Report | 19930 | 0.015898 | Low voltage AC (<1kV) | Laverton Raaf | 3026 | Laverton North | Vehicle
On arrival crew isolated supply and carried out repairs. Oil cleanup organised. | 60 Barry St, Romsey VIC 3434, Australia | 32044790 |  | Fallen | [5 empty] | Report received of tree resting on conductors at incident location. There was no arcing or sparking. On arrival crew found one bay of HV and 4 bays of LV damaged. Stress on transformer caused bushing fracture and oil spill There was no ground fire or third party property damage. | Conductor (bare);Pole mounted | 2 | 1 | 2 |  | WND012 | Vegetation: Trees Incident | Damage to network assets | 30/05/2020 21:45 |  |  | 15716 | Roadway |  | 20200611PWA_03 | Infrastructure (network-based) | -37.3508 | 144.749 | 1 | Powercor | Notification | 19931 | 0.026451 | Low voltage AC (<1kV);22kV AC | Wallan (Kilmore Gap) | 3434 | Romsey | Trees
Powercor fault crew attended, made the site safe and removed the tractor before replacing the pole and restoring electricity supply to the area. | 50 Warracknabeal-Rainbow Rd, Rainbow VIC 3424 | 33048972 | Crane, excavator or other construction/farming equipment | [6 empty] | The manager of a farming property reported a wire down on a tractor after that tractor struck and knocked down a Powercor pole. The tractor operator jumped clear of the tractor. There is no injury, no fire and no damage other than the pole knocked down. | Pole (concrete) | 2 | 2 | 2 |  | NHL015 | Tractor struck pole | Loss of supply;Damage to network assets | 44141.6306 |  |  | 15727 | Agricultural |  | 20200612PWA_01 | Infrastructure (network-based) | -35.9144 | 142.158 | 1 | Powercor | Report | 19948 | 0.022463 | 12.7kV AC (SWER) | Horsham Aerodrome | 3424 | Rainbow | Vehicle
On arrival supply isolated and repairs carried out | 70 Littles Ln, Terang VIC 3264, Australia | 33056835 |  | Blown branch/vegetation | [5 empty] | Following report of a successful auto reclose on TRG002 fdr customers reported a wire down in paddock. On arrival crew found that bark had blown onto line and subsequent flashover had caused a conductor to fall to ground. There was no ground fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | TRG002 | Bark caused flashover | Loss of supply;Damage to network assets | 43957.2562 |  |  | 15729 | Agricultural |  | 20200612PWA_03 | Infrastructure (network-based) | -38.2303 | 142.9307 | 1 | Powercor | Report | 19950 | 0.026801 | 22kV AC | Warrnambool Airport Ndb | 3264 | Terang | Trees
HV underground cable isolated and Underground Crew carrying out repairs. | 8-14 ALBERT STREET, PRESTON VIC 3072 | A106678 | Working too close to underground cables |  |  |  |  | Phase to earth | 1 | Sewer Contractor operating machinery and digging near HV underground cable in front of 8-14 Albert St (Preston) "nicked" the cable and tripped EP35 6.6kV feeder. There was no request to attend this address to conduct a No Go Zone assessment or inspection, and therefore there was no Permit to Work (PTW) issued by Jemena for the work We did attend and issue a Site Inspection Report for 8-20 Albert St, Preston in December, 2018 but nothing since. City Circle Demolition and Excavation, (03) 9489 7600, 714/716 High St, Kew East VIC 3102, admin@citycirclegroup.com.au, http://citycirclegroup.com.au/ Excavator Operator, Nathan McKinnon, 0401101280 Site Manager, Tim Kenna, 0412569426 | Cable | 0 | 0 | 0 |  | EP35 | No Go Zone breach | Loss of supply;Damage to network assets | 15/06/2020 7:34 |  |  | 15734 | Industrial |  | 20200615JEM_01 | Infrastructure (network-based) | -37.7528 | 145.0215 | 1 | Jemena | Report | 19957 | 0.014815 | 6.6kV AC | Essendon Airport | 3072 | Preston | Dug up
On arrival crew isolated supply and carried out repairs. | 60 Stoney Rises Rd, Smeaton VIC 3364, Australia | 32000109 | Working too close to overhead lines | [6 empty] | A Powercor fault crew attending a fault found that a HV line on the ground at the incident location. After careful observation, the crew identified the power line had been hit by en excavator. The crew also able to identify the owner of the excavator and the person conceded that the damages were done by his excavator. There were extensive damages to pole and the overhead assets starting from LIS 26436 about five bays There were no injuries or fire. | Conductor (bare) | 2 | 2 | 2 |  | BAN009 | Excavator operation | No Go Zone (contact);Damage to network assets | 15/06/2020 18:30 |  |  | 15751 | Agricultural |  | 20200617PWA_01 | Infrastructure (network-based) | -37.2615 | 143.9606 | 1 | Powercor | Notification | 19978 | 0.0023507 | 22kV AC | Ballarat Aerodrome | 3364 | Smeaton | Vehicle
Service to be abolished, ESV (RO) advised | 52 FAIRVIEW AVENUE, NEWTOWN VIC 3220 | 30324001 | Working too close to overhead lines;Unauthorised work | [5 empty] | 2 | Powercor assessor attending site for request for battens to be fitted on service found Point of attachment had been interfered with during construction. | Service cable (insulated) | 0 | 0 | 0 |  | GL022 | interference during construction activities | No Go Zone (contact) | 22/06/2020 9:00 |  |  | 15764 | Construction |  | 20200622PWA_02 | Infrastructure (customer connection) | -38.1548 | 144.341 | 2 | Powercor | Report | 19994 | 0.00017361 | Low voltage AC (<1kV) | Avalon Airport | 3220 | Newtown
Fault crew arrived and isolated the circuits either side of the pillar in order to make safe. | 14 BEVAN COURT, PAKENHAM VIC 3810 | 5654494 | [7 empty] | CFA had reported an LV pillar was on fire | LV Pillar | 0 | 0 | 0 |  | OFR24 | Under Investigation | Other electricity related | 19/06/2020 10:26 | 0 | Negligible: no ground fire | 15767 | Residential |  | 20200622SPN_04 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19998 | 0.02839 | Low voltage AC (<1kV) | Moorabbin Airport | 3810 | Pakenham
Supply disconnected so repairs could be made by REC. | 1 PRINCES TERRACE, JAN JUC VIC 3228 | 30152278 |  |  |  | Overheated connection |  |  | 2 | CFA reported a meter box fire at the above address. The Crew attended and found the POA had faulted, causing a fire. Because of the damage to the POA the crew could not determine if the fault started on the customers side or supply side of the fuse box. | POA connection (customer side);POA connection (network side) | 0 | 0 | 0 |  | WPD032 | Malfunction inside FOLCB | Less than $50k damage;Other electricity related;Damage to network assets | 20/06/2020 6:16 | 0 | Negligible: no ground fire | 15771 | Residential |  | 20200623PWA_01 | Infrastructure (customer connection) | -38.3491 | 144.2995 | 1 | Powercor | Notification | 20004 | 0.034772 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Jan Juc
Removed birds nest from cross-arm and repaired damaged conductor | 46 MARTIN STREET, TATURA VIC 3616 | 33091887 |  | Bird |  |  |  |  | 2 | Asset inspector received an electric shock when he was placing a tag on a concrete pole | Conductor (bare);Aluminium twisted (XLPE);Service cable (insulated) | 0 | 0 | 0 |  | MNA021 | Bird Incident | Minor shock | 23/06/2020 15:51 |  |  | 15779 | Roadway |  | 20200624PWA_03 | Infrastructure (network-based) | -36.4463 | 145.2264 | 1 | Powercor | Notification | 20015 | 0.0024074 | Low voltage AC (<1kV) | Shepparton Airport | 3616 | Tatura
Site made safe | VACANT LAND, 206-300 WESTERN AVENUE, MELBOURNE AIRPORT VIC 3045 | A041484 |  | Bird |  |  |  |  | 2 | While investigating the cause of a feeder fault, operator found small grass fire in the HBRA being extinguished by firemen Photos attached | Pole top | 0 | 0 | 0 |  | AW14 | Bird Incident | Grassfire | 20/11/2019 12:12 | 1 | Small: 10 - 1000 sq.m | 14598 | Peri-urban |  | 20191206JEM_02 | Infrastructure (network-based) | -37.6738 | 144.8668 | 1 | Jemena | Report | 18423 | 0.018773 | 22kV AC | Melbourne Airport | 3045 | Melbourne Airport | Animal
On arrival crew carried out repairs | 259 COUNTY BOUNDARY EAST ROAD, CAMPERDOWN VIC 3260 | 30149131 |  |  |  | Leakage |  |  |  | Pole fire reported by Vicfire at incident location, Crew confirmed pole fire. Burn marks around crossarm straps only. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | CDN002 | Excessive leakage current | Pole-top fire | 43536.2083 | 1 | Negligible: no ground fire | 14601 | Roadway |  | 20191209PWA_02 | Infrastructure (network-based) | -38.2725 | 143.1516 | 1 | Powercor | Report | 18429 | 0.037278 | 22kV AC | Warrnambool Airport Ndb | 3260 | Camperdown | Crossarm
On arrival crew examined the assets for damage, none was found. | 704 Mt William Rd, Skipton VIC 3361, Australia | 32005223 | Vehicle | [6 empty] | A call was received from a customer that a trucks trailer had contact the HV line at the incident location. A Powercor crew attended and determined that a tipper trailer had contacted the HV SWER conductor near Pole 34 Skipnorth Line. The truck owner had been carrying out maintenance with the truck tipper up, when the truck rolled in the direction of the line. The truck sustained damage to its tyres. There was no injury, shock or ground fire start. | Conductor (bare) | 2 | 2 | 2 |  | BAS021 | Inadvertent movement of vehicle (Tip truck) | No Go Zone (contact) | 43689.5396 |  |  | 14604 | Agricultural |  | 20191209PWA_05 | Infrastructure (network-based) | -37.6416 | 143.293 | 1 | Powercor | Report | 18433 | 0.0070428 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3361 | Skipton | Vehicle
The earth was damaged and had to be replaced. | 122 Albert St, Brunswick VIC 3056, Australia | 30276763 | Copper theft | [6 empty] | The CitiPower Report Room received a report that a wire was hanging from a pole outside 122 Albert St, Brunswick. On arrival the CitiPower Crew found there was an attempted copper theft on a HV earth at cable head pole Lis-770938. The earth was damaged and had to be replaced. There was no witnesses, or evidence of shock or injury. | Earth/earthing | 2 | 2 | 2 |  | C023 | Attempted copper theft | Damage to network assets | 43749.6424 |  |  | 14612 | Roadway |  | 20191210PWA_05 | Infrastructure (network-based) | -37.7699 | 144.971 | 1 | CitiPower | Report | 18456 | 0.0092708 | Earthing cable | Essendon Airport | 3056 | Brunswick | Other
Fault crews attended the site to investigate. Upon inspection, a HV wooden cross-arm was burnt and the conductor rested on a tree. The site was made safe and the cross-arm was replaced and supply was restored. | 13-17 MALCOLM ROAD, BRAESIDE VIC 3195 | 616892 |  |  |  | Leakage |  |  | 1 | UE received calls that the power line near a gum tree, is sparking. | Conductor (bare) | 0 | 0 | 0 |  | MC5 | The cause for the cross-arm fire is tracking across the insulator. | Pole-top fire | 30/11/2019 12:05 | 1 | Negligible: no ground fire | 14618 | Roadway |  | 20191210UTD_02 | Infrastructure (network-based) | -38.0003 | 145.1068 | 1 | United Energy Distribution | Report | 18467 | 0.027655 | 22kV AC | Moorabbin Airport | 3195 | Braeside | Crossarm
On arrival crew isolated supply and carried out repairs. | A8, Trawalla VIC 3373, Australia | 30314654 | Copper theft | [6 empty] | Fault crew following up on Public Lighting fault found the underground Public Lighting cable had been pulled out between 2 Service Pits at incident location. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | BAS011 | copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 22/11/2019 9:31 |  |  | 14637 | Roadway |  | 20191212PWA_05 | Infrastructure (network-based) | -37.436 | 143.4622 | 1 | Powercor | Report | 18488 | 0.0074977 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3373 | Trawalla | Other
Crew issued a defect letter to the customer to get their REC to replace POA bracket. | 11 KOOYONGKOOT ROAD, HAWTHORN VIC 3122 | 30199187 | Working too close to overhead lines | [6 empty] | Operator of excavator reported hey have pulled down a wire down at the above incident location. On arrival, the crew found a Low Voltage (LV) overhead service cable had been pulled down by an excavator vehicle and fallen onto the ground. There was no ground fire and no reported injuries. | POA connection (customer side);Service cable (insulated) | 2 | 2 | 2 |  | CL033 | Excavator operating near service | No Go Zone (contact);Damage to network assets | 43508.5868 |  |  | 14642 | Residential |  | 20191213PWA_04 | Infrastructure (customer connection) | -37.8312 | 145.0388 | 1 | CitiPower | Report | 18493 | 0.025601 | Low voltage AC (<1kV) | Moorabbin Airport | 3122 | Hawthorn | Vehicle
The fault crew isolated the supply to the pole and removed the pole from the site. The pole will need to be re-installed at the completion of the trenching works. | 25 COVENTRY STREET, SOUTHBANK VIC 3006 | 30350007 | Building too close or within the No Go Zone | [6 empty] | Andrew from ICON Co (Aust) PTY LTD called to report that excavating works being carried out by Complete Plumbing at the incident location. It is effecting the integrity and stability of a streetlight pole. He arranged installation of a strap to stop the pole from falling over. On arrival the crew found that approx. 1.3 metres of soil had been removed from the street side of the streetlight pole, making it unstable. There was no reported injuries or electrical contact. | Pole (steel) | 2 | 2 | 2 |  | SO013 | Excavation around lighting pole | No Go Zone (contact);Damage to network assets | 43567.5312 |  |  | 14643 | Roadway |  | 20191213PWA_05 | Infrastructure (network-based) | -37.8291 | 144.9701 | 1 | CitiPower | Report | 18494 | 0.011654 | Low voltage AC (<1kV) | Essendon Airport | 3006 | Southbank | Dug up
On arrival crew made site safe and arranged for further testing of cables. | Astley Dr, Melton South VIC 3338, Australia | 30305877 | Vandalism;Copper theft | [6 empty] | MELTON CITY COUNCIL employee , Dale 0447169748, advised vandals have dug up cable at the incident location. Upon arrival, A Powercor crew found that the P/L UG cable pit was opened and thieves tried to pull out the cables. A damaged cable found but no cables were taken away. | Services cable;Services pit (network) | 2 | 2 | 2 |  | MLN021 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43597.3688 |  |  | 14644 | Roadway |  | 20191213PWA_06 | Infrastructure (network-based) | -37.7164 | 144.5988 | 1 | Powercor | Report | 18495 | 0.021238 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
Fault crews attended the site to investigate. Upon inspection, the EDO fuse on the pole was hung up and showed black marks on the tube. The fuse was subsequently replaced. | 46 GLENISLA DRIVE, MOUNT MARTHA VIC 3934 | 1103211 |  |  |  | Mechanical breakdown |  |  | 1 | UE received a call that there was no supply to the water pumping station. | EDO fuse | 0 | 0 | 0 |  | DMA24 | The cause is a hung up EDO fuse tube. | Plant/equipment | 43567.3333 | 1 | Negligible: no ground fire | 14645 | Roadway |  | 20191213UTD_01 | Infrastructure (network-based) | -38.2757 | 145.0132 | 1 | United Energy Distribution | Report | 18496 | 0.016163 | 22kV AC | Moorabbin Airport | 3934 | Mount Martha | Fuse
Fault crews attended the site to investigate. Upon inspection, an ampact has failed on the 66kV overhead conductors and sparking has caused a small grassfire. The site was made safe and the conductors and network were repaired. | 54 SUTHERLAND AVENUE, ASPENDALE GARDENS VIC 3195 | 3305055 |  |  |  | Corrosion |  |  | 1 | UE received a call that there's a small grass fire at the base of a pole caused by sparking. | Conductor (bare) | 0 | 0 | 0 |  | CRM35 | The cause is a failed ampact on the 66kV overhead conductor. | Grassfire | 43689.4688 | 1 | Localised: less than 10 sq.m | 14648 | Public space |  | 20191213UTD_04 | Infrastructure (network-based) | -38.0169 | 145.1184 | 1 | United Energy Distribution | Report | 18499 | 0.041082 | 66kV AC | Moorabbin Airport | 3195 | Aspendale Gardens | Connection
Substation was isolated LV and HV to make safe. | 124 MAFFRA STREET, COOLAROO VIC 3048 | A039319 | Copper theft | [5 empty] | 2 | Copper theft of LV and HV earths at pole-mounted substation Maffra St P36, resulting in blue phase LV open wire mains on ground | Conductor (bare);Earth/earthing | 0 | 0 | 0 |  | BD09 | Copper theft | Loss of supply | 17/12/2019 4:10 |  |  | 14651 | Industrial |  | 20191217JEM_01 | Infrastructure (network-based) | -37.6563 | 144.9394 | 1 | Jemena | Report | 18503 | 0.018119 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Coolaroo | Other
The crew made the site safe by repacking fresh sand and installed slabs over affected cable. The hole remained open and barricaded, however it remains unknown who performed the excavation and why | 27-51 LAKESIDE DRIVE, ROXBURGH PARK VIC 3064 | A138542 | Working too close to underground cables | [5 empty] | 2 | Zinfra crew attended a fault Saturday Night 7/12/19 in Lakeside Dr. While there they came across a site where an unknown third party had been excavating and have exposed Jemenaâ€™s HV and LV underground cables located adjacent to pole A138542. Cables were exposed as per attached photos and crew noted that for at least a couple of meters there was no sand around cables, but there was plenty of rock and bricks. | Cable | 0 | 0 | 0 |  | COO22 | No Go Zone breach | Damage to network assets | 43658.875 |  |  | 14654 | Public space |  | 20191217JEM_02 | Infrastructure (network-based) | -37.6286 | 144.935 | 1 | Jemena | Report | 18508 | 0.02224 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3064 | Roxburgh Park | Dug up
Fault crews attended the site to investigate. Upon inspection, it was identified that a contractor had dug through the underground LV service cable. The supply was isolated at the pole and the cable was repaired before supply was restored. | 15 MAYSBURY AVENUE, BRIGHTON VIC 3186 | 1805359 | Working too close to underground cables | [5 empty] | 1 | UE received a call that the customer heard a bang before losing power. | Services cable | 0 | 0 | 0 |  | MR32 | The cause was contractor had dug up the LV service cable. | Loss of supply;Damage to network assets | 43628.441 |  |  | 14655 | Residential |  | 20191217UTD_01 | Infrastructure (network-based) | -37.9229 | 144.9901 | 1 | United Energy Distribution | Report | 18509 | 0.013948 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Dug up
Fault crews attended the site to investigate. Upon inspection, it was identified that the HV crossarm was burnt and the overhead conductor dropped to the lower circuit. The site was isolated and the cross-arm was replaced. | 151 BEACH ROAD, SANDRINGHAM VIC 3191 | 1817434 |  |  |  | Leakage |  |  | 1 | UE received call that an overhead wire was resting on a cross-arm. MFB were on site. | Crossarm (wood) | 0 | 0 | 0 |  | SR11 | The cause for the cross-arm fire was tracking across the insulator. | Pole-top fire | 43750.5035 | 1 | Negligible: no ground fire | 14656 | Roadway |  | 20191217UTD_02 | Infrastructure (network-based) | -37.956 | 145.0075 | 1 | United Energy Distribution | Report | 18510 | 0.032602 | 11kV AC | Moorabbin Airport | 3191 | Sandringham | Crossarm
A voltage test between the sink and the conductive metallic tap showed a result of 16 Volts. Tests between the tap and various other points of the installation with reference to an independent earth, including the distribution assets, revealed that the service neutral conductor was corroded at the junction box on the CitiPower pole. Citipower linesman repaired the connection service at the pole. The CTA carried out N.S.T & Voltage tests following the repair and normal results were obtained. | 22 DAVIES STREET, BRUNSWICK VIC 3056 | 30159019 |  |  |  | Corrosion |  | Phase to earth |  | Joseph received an electric shock when he simultaneously contacted the Metallic tap with his hand and metallic sink with his other hand. | Connection box | 2 | 2 | 2 |  | BK011 | Corroded connection at connection box | Minor shock | 28/08/2019 13:00 |  |  | 14678 | Roadway |  | 20191219PWA_08 | Infrastructure (network-based) | -37.7568 | 144.9663 | 1 | CitiPower | Report | 18533 | 0.031027 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
A voltage test between the waste and the conductive metallic tap showed a result of 125 Volts. Tests between the tap and various other points of the installation with reference to an independent earth, including the distribution assets, revealed that the service neutral conductor was corroded at the junction box on the Powercor pole Powercor linesman replaced the service and the CTA carried out N.S.T & Voltage tests following the repairs, 0 Volts and normal results were obtained. | 13 DALPURA COURT, WERRIBEE VIC 3030 | 30119742 |  |  |  | Corrosion |  | Phase to earth |  | Bree received an electric shock when she simultaneously contacted the Metallic shower tap with her hand and metallic waste with her foot. | Connection box | 2 | 2 | 2 |  | WBE031 | Corroded connection | Minor shock | 29/09/2019 13:00 |  |  | 14679 | Roadway |  | 20191219PWA_09 | Infrastructure (network-based) | -37.9011 | 144.6342 | 1 | Powercor | Report | 18534 | 0.038878 | Low voltage AC (<1kV) | Laverton Raaf | 3030 | Werribee | Connection
Faults crew promptly attended and removed the single phase service and meter number 0636882. The house had already been demolished and the crew found the meter attached to the remaining building front with supply remaining on. | 365 NEPEAN HIGHWAY, CHELSEA VIC 3196 |  | Working too close to overhead lines | [5 empty] | 2 | Caller Dale (0450 604 468) advised that isolation is required for the fire damaged building as the service wire needs to be dropped to complete urgent repairs as wire is presently unsafe. (UE had no record of a fire at the premise). | Conductor (insulated);Network meter | 0 | 0 | 0 |  |  | Completing a home abolishment with no prior contact with a Retailer of Distributor. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43720.4375 |  |  | 14676 |  |  | 20191219UTD_02 | Infrastructure (customer connection) | -38.0494 | 145.1143 | 1 | United Energy Distribution | Report | 18531 | 0.011741 | Low voltage AC (<1kV) | Moorabbin Airport | 3196 | Chelsea | Other
On arrival crew checked assets no damage found | 20 Red Tank Rd, Strathfieldsaye VIC 3551, Australia | 33034128 |  | Bird | [5 empty] | CFA reported a ground fire has burnt pole, check for damage. Crew found a Magpie had caused a flash over, starting a 20m x 10m grass fire, There was no reported injuries , no property damage | ACR/OCR | 2 | 2 | 2 |  | BGO013 | Bird Incident | Grassfire | 20/12/2019 21:37 | 1 | Small: 10 - 1000 sq.m | 14688 | Roadway |  | 20191223PWA_02 | Infrastructure (network-based) | -36.8172 | 144.3434 | 1 | Powercor | Report | 18549 | 0.01785 | 22kV AC | Bendigo Airport | 3551 | Strathfieldsaye | Animal
On arrival crew isolated supply and replaced service line | 31 VILLIERS STREET, PORT FAIRY VIC 3284 | 31028939 |  | Within clearances | [5 empty] | Vic Fire reported wire down and sparking at incident address. When crews arrived they found a neutral screen Service wire had failed due to contact with a cust resp tree. A small ground (lawn) fire 2m x 2m in size had started on the front lawn area and was extinguished by Vic Fire. No injuries or property damage reported. | Service cable (insulated) | 2 | 2 | 2 |  | KRT022 | Vegetation: Trees Incident | Grassfire | 20/12/2019 13:36 | 1 | Localised: less than 10 sq.m | 14689 | Residential |  | 20191223PWA_03 | Infrastructure (customer connection) | -38.3814 | 142.2281 | 1 | Powercor | Report | 18550 | 0.014704 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3284 | Port Fairy | Trees
On arrival crew isolated supply and carried out repairs. | 105 WHITEHORSE ROAD, MOOLAP VIC 3224 | 30064947 |  |  |  | Overheated connection |  |  |  | Fire brigade reported pole fire and grass fire and incident address. When crews arrived confirmed a LV UG service cable on Transformer pole had failed at the connection box. There was a small 4 square spot fire at the base of the pole. There was no reported injuries or property damage. | Services cable;Connection box | 2 | 2 | 2 |  | GLE024 | Insufficient remains to determine cause | Grassfire | 20/12/2019 20:38 | 1 | Localised: less than 10 sq.m | 14691 | Roadway |  | 20191223PWA_05 | Infrastructure (network-based) | -38.1818 | 144.4379 | 1 | Powercor | Report | 18552 | 0.014483 | Low voltage AC (<1kV) | Avalon Airport | 3224 | Moolap | Connection
On arrival crew isolated supply and carried out repairs. | 230 Scenic Rd, Highton VIC 3216, Australia | 32086978 |  |  |  | Overheated connection |  |  |  | Fire Brigade reported pole fire at incident address. When crews arrived they found a small grass fire 4m2, had started due to a loose connection on a LV fused bus isol. No injury or property damage was reported | Disconnector/isolator | 2 | 2 | 2 |  | GL021 | Loose connection | Grassfire | 20/12/2019 20:11 | 1 | Localised: less than 10 sq.m | 14692 | Roadway |  | 20191223PWA_06 | Infrastructure (network-based) | -38.1551 | 144.3111 | 1 | Powercor | Report | 18553 | 0.028737 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
Crew replaced the damaged IPC. | 301 Mont Albert Rd, Surrey Hills VIC 3127, Australia | 30177913 |  |  |  | Overheated connection |  |  |  | Customer reported Wire is sparking and dripping molten bits to the ground and causing grass fires. Crew advise small burn marks on ground less than size of a dollar coin, Smoldering grass due to hot debris from overheated IPC There was no reported injuries or third party property damage. | Connector/termination | 2 | 2 | 2 |  | RD014 | connection failure | Grassfire | 20/12/2019 18:10 | 1 | Localised: less than 10 sq.m | 14695 | Roadway |  | 20191223PWA_08 | Infrastructure (network-based) | -37.8205 | 145.0996 | 1 | CitiPower | Report | 18556 | 0.026025 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | Connection
On arrival crew arranged isolation and replaced insulators | 39 London Rd, Stawell VIC 3380, Australia | 32095103 |  | Lightning | [5 empty] | Lightning has Struck the pole at incident location. There was damage to two Disc Insulators, there was a ground fire approx. 2 x 4m. There was no injuries reported or third party property damage. | Conductor (bare);Insulators | 2 | 2 | 2 |  | STL007 | Lightning struck pole | Grassfire | 21/12/2019 1:51 | 1 | Localised: less than 10 sq.m | 14696 | Roadway |  | 20191223PWA_09 | Infrastructure (network-based) | -37.0697 | 142.7925 | 1 | Powercor | Report | 18557 | 0.014623 | 22kV AC | Horsham Aerodrome | 3380 | Stawell | Lightning
High voltage conductors inspected, only minor damage supply restored. | 49 Bluff Rd, St Leonards VIC 3223, Australia | 30075007 | Vehicle | [5 empty] | 1 | Customer reports that a yacht had come into contact with OH Mains wire at waterfront infront of No.49 Bluff Road. Wire still connected, not lowered. Yacht has since left the incident everyone ok at site. Crew advise yacht travelling west down Bluff Road contacted the east conductor as the overhead passes over Bluff Road. The driver decamped the incident site. Minor / cosmetic damage to high voltage overhead conductor east side. There was no fire, no reported injuries . | Conductor (bare) | 2 | 2 | 2 |  | DDL013 | Yacht mast struck conductors | Loss of supply;No Go Zone (contact) | 20/12/2019 14:00 |  |  | 14697 | Roadway |  | 20191223PWA_10 | Infrastructure (network-based) | -38.1801 | 144.7151 | 1 | Powercor | Report | 18726 | 0.028366 | 22kV AC | Avalon Airport | 3223 | St Leonards | Vehicle
On arrival crew isolated supply and carried out repairs | 89 Lake Baker Rd, Lake Boga VIC 3584, Australia | 32159504 |  |  |  | Overheated connection |  |  |  | Vicfire reported grassfire involving Powercor assets. Upon arrival crew found that a small grassfire had occurred approximately 50m X 15m in area which had been extinguished by the CFA. There was also minor damage to the pole. There was no reported injuries. | Connection box | 2 | 2 | 2 |  | SHL005 | Connection failure | Grassfire | 19/12/2019 17:37 | 1 | Small: 10 - 1000 sq.m | 14698 | Roadway |  | 20191224PWA_01 | Infrastructure (network-based) | -35.4364 | 143.6211 | 1 | Powercor | Report | 18559 | 0.036443 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3584 | Lake Boga | Connection
On arrival crew isolated supply and carried out repairs | Murrabit W Rd, Benjeroop VIC 3579, Australia | 30255066 | [7 empty] | Vicfire called to advise that PCA assets could have been the possible cause of a grassfire. On arrival crew found a conductor had fallen and was on the ground at the incident location. CfA extinquished a small grass fire (100m x 5m) on roadside. There was no reported injuries | Conductor (bare) | 2 | 2 | 2 |  | KGT003 | to be determined | Grassfire | 22/12/2019 22:58 | 1 | Small: 10 - 1000 sq.m | 14699 | Roadway |  | 20191224PWA_02 | Infrastructure (network-based) | -35.4719 | 143.826 | 1 | Powercor | Notification | 18560 | 0.019579 | 22kV AC | Swan Hill Aerodrome | 3579 | Benjeroop | Conductor
Section of LV conductor cut away to make safe LV spreaders installed to prevent recurrence of conductor clashing Damaged LV mains conductor were replaced | 30 JERROLD STREET, FOOTSCRAY VIC 3011 | A039167 and A039166 |  | Wind |  | Conductor clashing |  |  | 2 | Red, blue and neutral phases of LV mains conductor came down between pole numbers A039167 and A039166 due to windy conditions which resulted in LV conductor clashing | Conductor (bare) | 0 | 0 | 0 |  | FE09 | Windy conditions resulting in LV conductor clashing | Loss of supply | 30/12/2019 18:18 |  |  | 14714 | Residential |  | 20191230JEM_02 | Infrastructure (network-based) | -37.7923 | 144.8901 | 1 | Jemena | Report | 18576 | 0.0084236 | Low voltage AC (<1kV) | Essendon Airport | 3011 | Footscray | Conductor
On arrival crew isolated supply and carried out repairs. LEI's attended to check for HVI | 20 OREGAN STREET, STAWELL VIC 3380 | 31016235 |  | Fallen | [5 empty] | Vic Fire reported a wire down and small fire at the incident location. On arrival the fault crew found that a branch had broken from a tree standing on the opposite side of the road from this property and had fallen onto the overhead distribution wires, bringing 3 bays of HV & LV conductors to the ground, and causing the small fire in the front yard of this residence. The fault crew also found evidence of High Voltage Injection damage to the electrical wiring and the switchboard at this residence. There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | STL005 | Vegetation: Trees Incident | HV injection;Grassfire | 29/12/2019 18:30 | 1 | Small: 10 - 1000 sq.m | 14711 | Roadway |  | 20191230PWA_08 | Infrastructure (network-based) | -37.0648 | 142.7932 | 1 | Powercor | Report | 18573 | 0.019589 | Low voltage AC (<1kV);22kV AC | Horsham Aerodrome | 3380 | Stawell | Trees
On arrival crew inspected assets and restored supply | Sleep Rd, Manangatang VIC 3546, Australia | 32140525 |  | Lightning | [5 empty] | Lightning Strike Pole # 6 & Pole #5 Winnambool Spur OYN003 30-40 Hectares burnt, Fault tamer fuse destroyed, fire ignited at pole 6 There was no reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | OYN003 | Lightning struck line | Grassfire | 29/12/2019 17:53 | 1 | Large: more than 10 ha | 14713 | Agricultural |  | 20191230PWA_09 | Infrastructure (network-based) | -35.0254 | 142.7935 | 1 | Powercor | Report | 18575 | 0.020928 | 12.7kV AC (SWER) | Swan Hill Aerodrome | 3546 | Manangatang | Lightning
On arrival crew isolated supply and carried out repairs. | 7 WILLIS STREET, BALWYN NORTH VIC 3104 | 30166282 |  | Blown branch/vegetation | [5 empty] | Customer reported a wire resting in the tree out the front of property and that caused a fire at property all the way up to front door. On arrival crew reported that an overhanging branch made contact with LV cables causing LV phases to make contact. This caused sparking as result the sparks fell upon the customers front lawn. The resulting fire was approx. 8 x 5m. There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | L001 | Limb clashed conductors | Grassfire | 30/12/2019 16:54 | 1 | Small: 10 - 1000 sq.m | 14722 | Roadway |  | 20191231PWA_08 | Infrastructure (network-based) | -37.8048 | 145.0632 | 1 | CitiPower | Report | 18584 | 0.020345 | Low voltage AC (<1kV) | Essendon Airport | 3104 | Balwyn North | Trees
PAL fault crew attended and disconnected and isolated this 66kV line prior the replacing the burned crossarm and restoring the line to supply. | 2 Apricot Ave, Horsham VIC 3400, Australia | 32116250 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had been burning at a bridging insulator, but the fire had been extinguished before the crossarm burned through. CFA attended and extinguished the crossarm fire. There was no ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | HOTS-HSM2 | Excessive leakage current | Pole-top fire | 30/12/2019 23:04 | 1 | Negligible: no ground fire | 14723 | Roadway |  | 20191231PWA_09 | Infrastructure (network-based) | -36.7335 | 142.2084 | 1 | Powercor | Report | 18585 | 0.041663 | 66kV AC | Horsham Aerodrome | 3400 | Horsham | Crossarm
On arrival crew isolated supply and carried out repairs. | 36 Vincent Ave, St Albans VIC 3021, Australia | 32163794 |  |  |  | Leakage |  |  |  | Customer reports sparking and buzzing noise coming from pole in front of his home, believes it is coming from the conductors at the top of the pole. still on supply at site, sparks not reaching the ground. Crew advise pole fire. Cross-arm on roadside of pole has burnt through at strap bolt cross-arm is broken, insulator has shattered and fallen onto nature strip below. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | SA007 | Excessive leakage current | Pole-top fire | 31/12/2019 6:41 | 1 | Negligible: no ground fire | 14733 |  |  | 20200102PWA_05 | Infrastructure (network-based) | -37.7424 | 144.8092 | 1 | Powercor | Report | 18595 | 0.014538 | 22kV AC | Melbourne Airport | 3021 | St Albans | Crossarm
On arrival crew isolated supply and carried out repairs. | 1 PRYORS ROAD, HORSHAM VIC 3400 | 30078377 |  |  |  | Leakage |  |  |  | Vic Fire reported a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through, dropping the outside conductor. There was no ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | HSM009 | Excessive leakage current | Pole-top fire | 31/12/2019 0:10 | 1 | Negligible: no ground fire | 14734 | Roadway |  | 20200102PWA_06 | Infrastructure (network-based) | -36.7043 | 142.2153 | 1 | Powercor | Report | 18596 | 0.038559 | 22kV AC | Horsham Aerodrome | 3400 | Horsham | Crossarm
On arrival crew isolated supply and carried out repairs. | 2 Skyline Dr, Keilor VIC 3036, Australia | 30108788 |  |  |  | Leakage |  |  |  | Vic fire reported crossarm on fire at incident location Crew advise pole fire originating at pin of bridging insulator. Cross arm has lost integrity and insulators have broken away causing fault on feeder and ACR to trip. No ground fire and no reported injury. | Crossarm (wood) | 2 | 2 | 2 |  | SA002 | Excessive leakage current | Pole-top fire | 31/12/2019 6:41 | 1 | Negligible: no ground fire | 14735 | Roadway |  | 20200102PWA_07 | Infrastructure (network-based) | -37.7241 | 144.8366 | 1 | Powercor | Report | 18597 | 0.021275 | 22kV AC | Melbourne Airport | 3036 | Keilor | Crossarm
On arrival crew isolated supply and carried out repairs. LEI Miles Tobias on site to test reconnect LV customers. | 229 St Albans Rd, St Albans VIC 3021, Australia | 30112999 |  |  |  | Leakage |  |  |  | Crew advise cross-arm burnt through on Red phase roadside HV isolator and fell into low voltage below, HV injection occurred. There was no ground fire or reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | SSE011 | Excessive leakage current | Pole-top fire;HV injection | 31/12/2019 5:30 | 1 | Negligible: no ground fire | 14738 |  |  | 20200102PWA_10 | Infrastructure (network-based) | -37.7644 | 144.8154 | 1 | CitiPower | Report | 18604 | 0.0039074 | 22kV AC | Essendon Airport | 3021 | St Albans | Crossarm
Site made safe and HV crossarm replaced | 19 TAGGERTY CRESCENT, MEADOW HEIGHTS VIC 3048 | A037360 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to earth leakage | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | BD14 | Earth leakage | Pole-top fire | 43831.9042 | 1 | Negligible: no ground fire | 14752 | Residential |  | 20200103JEM_07 | Infrastructure (network-based) | -37.6614 | 144.9211 | 1 | Jemena | Report | 19198 | 0.023921 | 22kV AC | Essendon Airport | 3048 | Meadow Heights | Crossarm
Site made safe Replaced HV crossarm and HV fuse units | 1 MOORE STREET, FOOTSCRAY VIC 3011 | A039191 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to earth leakage HV crossarm failed and fell onto LV conductors Photos are unavailable for this incident | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | FE06 | Earth leakage | Pole-top fire | 31/12/2019 5:15 | 1 | Negligible: no ground fire | 14753 | Residential |  | 20200103JEM_08 | Infrastructure (network-based) | -37.7953 | 144.9043 | 1 | Jemena | Report | 18619 | 0.037427 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3011 | Footscray | Crossarm
Site made safe HV isolators replaced | 34 WILLIAM STREET, GLENROY VIC 3046 | A092669 |  |  |  | Leakage |  |  | 1 | Pole top fire resulting in damage to HV isolators Photos are unavailable for this incident | Pole top;Disconnector/isolator | 0 | 0 | 0 |  | PV14 | Earth leakage | Pole-top fire | 31/12/2019 6:02 | 1 | Negligible: no ground fire | 14758 | Residential |  | 20200103JEM_13 | Infrastructure (network-based) | -37.7091 | 144.9091 | 1 | Jemena | Report | 18624 | 0.0085231 | 22kV AC | Essendon Airport | 3046 | Glenroy | Pole
Site made safe HV/LV pole replaced | 32 KERFERD STREET, ESSENDON NORTH VIC 3041 | A084805 |  |  |  | Leakage |  |  | 1 | HV crossarm caught fire as a result of earth leakage and resulted in pole top fire and damage to pole top | Pole (wood);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | ES26 | Earth leakage | Pole-top fire | 31/12/2019 11:07 | 1 | Negligible: no ground fire | 14759 | Residential |  | 20200103JEM_14 | Infrastructure (network-based) | -37.7408 | 144.9057 | 1 | Jemena | Report | 18625 | 0.013971 | 22kV AC | Essendon Airport | 3041 | Essendon North | Crossarm
Section was isolated and made safe Repairs to be made | 21 SIMCOCK AVENUE, SPOTSWOOD VIC 3015 | A058929 |  |  |  | Leakage |  |  | 1 | Three crossarms caught fire on pole A058929 due to earth leakage | Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | YVE12 | Earth leakage | Pole-top fire | 43952.6215 | 1 | Negligible: no ground fire | 14764 | Industrial |  | 20200106JEM_01 | Infrastructure (network-based) | -37.8285 | 144.892 | 1 | Jemena | Report | 18630 | 0.0021308 | 22kV AC | Essendon Airport | 3015 | Spotswood | Crossarm
Site made safe and HV crossarm replaced | 106-108 BAKERS ROAD, COBURG NORTH VIC 3058 | A031277 |  |  |  | Leakage |  | Phase to earth | 1 | HV crossarm fire on pole A031277 at HV isolators 11952 due to earth leakage Red phase HV conductor into LV conductor, no high voltage injection Photos are unavailable for this incident | Conductor (bare);Pole top;Crossarm (wood) | 0 | 0 | 0 |  | CN05 | Earth leakage | Pole-top fire | 43952.434 | 1 | Negligible: no ground fire | 14765 | Commercial |  | 20200106JEM_02 | Infrastructure (network-based) | -37.7261 | 144.9513 | 1 | Jemena | Report | 18631 | 0.02358 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3058 | Coburg North | Crossarm
Section isolated and repairs made | 1007 HIGH STREET, RESERVOIR VIC 3073 | A034223 |  |  |  | Leakage |  |  | 1 | High voltage crossarm fire due to earth leakage Photos are unavailable for this incident | Pole top;Crossarm (wood) | 0 | 0 | 0 |  | TT10 | Earth Leakage / Tracking | Pole-top fire | 43952.5 | 1 | Negligible: no ground fire | 14768 | Roadway |  | 20200106JEM_03 | Infrastructure (network-based) | -37.704 | 145.0099 | 1 | Jemena | Report | 18636 | 0.034611 | 22kV AC | Essendon Airport | 3073 | Reservoir | Crossarm
MFB had ensured extinguished fire. DAO took Photos. | 363-365 MT DANDENONG ROAD, CROYDON VIC 3136 | 1003440 |  | Blown branch/vegetation | [5 empty] | a thin branch snapped and fell towards the HV | Conductor (bare) | 0 | 0 | 0 |  | cyn33 | Vegetation: Trees Incident | Other vegetation | 29/12/2019 13:30 | 1 | Negligible: no ground fire | 14773 | Residential |  | 20200106SPN_06 | Infrastructure (network-based) | -37.8003 | 145.2956 | 1 | AusNet Services Distribution | Report | 18785 | 0.028185 | 22kV AC | Moorabbin Airport | 3136 | Croydon | Trees
Crew attended and made safe. | 860 SUMMERHILL ROAD, CRAIGIEBURN VIC 3064 | A105899 | Copper theft | [5 empty] | 2 | Underground mains stolen from pole A105899 Summerhill Rd Craigieburn. | Services cable;Copper | 0 | 0 | 0 |  | KLO22 | Copper theft | Damage to network assets | 43983.6597 |  |  | 14774 | Roadway |  | 20200107JEM_01 | Infrastructure (network-based) | -37.5699 | 144.9432 | 1 | Jemena | Report | 18650 | 0.0032303 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Crew attended and made safe. | 365 RIDDELL ROAD, SUNBURY VIC 3429 | A055258 | Copper theft | [5 empty] | 2 | Underground mains from LV krone to pit stolen from pole A055258 | Services cable;Copper | 0 | 0 | 0 |  | SBY23 | Copper theft | Damage to network assets | 44013.3993 |  |  | 14781 | Roadway |  | 20200107JEM_03 | Infrastructure (customer connection) | -37.5555 | 144.7014 | 1 | Jemena | Report | 18659 | 0.018304 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
Section isolated to make repairs, HV crossarm replaced | 281 GAFFNEY STREET, PASCOE VALE VIC 3044 | A092906 |  | Precipitation |  | Leakage |  |  | 2 | Pole top fire involving HV crossarm burning through at insulator No protection trip or loss of supply | Pole top;Crossarm (wood);Insulators | 0 | 0 | 0 |  | CS12 | Earth leakage from recent bushfire smoke and light rain | Pole-top fire | 44013.7847 | 1 | Negligible: no ground fire | 14797 | Roadway |  | 20200107JEM_04 | Infrastructure (network-based) | -37.7323 | 144.9457 | 1 | Jemena | Report | 18677 | 0.040295 | 22kV AC | Essendon Airport | 3044 | Pascoe Vale | Crossarm
Crew dispatched to investigate and make safe. Damaged krone box at the substation pole found, burnt grass at base of pole. Substation was then isolated via the HV fuses and made safe. Replaced krone box. | 60 BALD HILL ROAD, PAKENHAM VIC 3810 | 500411 |  |  |  | Overheated connection |  |  |  | Damaged krone box at the substation pole, burnt grass at base of pole. | Any other type | 0 | 0 | 0 |  | PHM21 | Poor connection (hot joint) resulting in LV fault and overheating of fuse unit. | Pole-top fire;Grassfire | 16/12/2019 15:13 | 1 | Localised: less than 10 sq.m | 14788 | Industrial |  | 20200107SPN_07 | Infrastructure (network-based) | -38.0846 | 145.494 | 1 | AusNet Services Distribution | Report | 18667 | 0.0031528 | Low voltage AC (<1kV) | Moorabbin Airport | 3810 | Pakenham | Connection
made safe | 160 Loch St, Yarragon VIC 3823, Australia | 2203214 |  | Animal | [5 empty] | HV BA fuse candled. Refer to the attached photos of the site. | Boric acid | 0 | 0 | 0 |  | moe22 | Animal Incident | Pole-top fire | 44013.4014 | 1 | Negligible: no ground fire | 14790 |  |  | 20200107SPN_08 | Infrastructure (network-based) | -38.2162 | 146.0583 | 1 | AusNet Services Distribution | Report | 19271 | 0.04031 | 22kV AC | Morwell (Latrobe Valley Airport) | 3823 | Yarragon | Fuse
Dispatched fault crew to investigate report of pillar being hit by vehicle, also dispatched DAO to investigate fire. Fire put out by CFA. Pillar was isolated, removed under permit and replaced. | 20 BARLOW RISE, BUNDOORA VIC 3083 | 5676481 | Vehicle | [6 empty] | Vehicle hit pillar, pillar caught fire and was put by MFB | LV Pillar | 0 | 0 | 0 |  | WT9 | Impact from vehicle causing LV pillar to catch fire. | Plant/equipment | 43811.7306 | 1 | Negligible: no ground fire | 14792 | Residential |  | 20200107SPN_09 | Infrastructure (network-based) | -37.7103 | 145.0522 | 1 | AusNet Services Distribution | Report | 18671 | 0.04063 | Low voltage AC (<1kV) | Essendon Airport | 3083 | Bundoora | Vehicle
The repair works are in progress | 83 Dohertys Rd, Laverton North VIC 3026, Australia | 30115730 | Working too close to overhead lines | [6 empty] | A company employee found a damaged pole at the incident location. The damage is done by a road construction vehicle as the road work is in progress in the area. The photo shows evidence of construction vehicle impact on the pole. There was no fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | BLTS-BMH | Earth moving equipment brushed pole | No Go Zone (contact) | 44013.5653 |  |  | 14799 |  |  | 20200108PWA_02 | Infrastructure (network-based) | -37.8289 | 144.7946 | 1 | Powercor | Report | 18681 | 0.0020822 | Low voltage AC (<1kV);22kV AC;66kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
On arrival crew isolated supply and carried out repairs. | 14 OGRADYS LANE, KOROIT VIC 3282 | 33099459 |  |  |  | Overheated connection |  |  |  | CFA reported a ground fire at the above location. Powercor crew attended and found the ground fire had been started by faulted FOLCB There was no reported injuries. | Connection box | 2 | 2 | 2 |  | KRT013 | corrossion | Grassfire | 43922.5917 | 1 | Small: 10 - 1000 sq.m | 14802 | Roadway |  | 20200108PWA_05 | Infrastructure (network-based) | -38.3074 | 142.3482 | 1 | Powercor | Report | 18686 | 0.027951 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3282 | Koroit | Connection
Crew isolated and repaired. | 614 WEARNE ROAD, PENTAL ISLAND VIC 3586 | 30102272 |  |  |  | Leakage |  |  |  | Customer reports broken cross-arm, low wire and grass fire at incident location. When crew arrived, they found that cross-arm had burnt at the road side HV insulator and the wire had dropped to approx. 1m height. Crew found that the fire had been extinguished by the person reporting the incident. There was no reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | KGT003 | Excessive leakage current | Grassfire;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43952.7125 | 1 | Small: 10 - 1000 sq.m | 14804 | Roadway |  | 20200108PWA_06 | Infrastructure (network-based) | -35.4448 | 143.7947 | 1 | Powercor | Report | 19004 | 0.014979 | 22kV AC | Swan Hill Aerodrome | 3586 | Pental Island | Crossarm
The service fuse has been removed at the BTS pole and a defect notice issued on site. A Faults truck is required to attend to disconnect the overhead service line from pole A016219 | 156 DALEY STREET, GLENROY VIC 3046 | A016219 | Unauthorised access | [5 empty] | 2 | Jemena Compliance have located another unauthorised illegal Builder's Temporary Supply (BTS) connection where the overhead service line and electricity meter has been relocated from a recently demolished property to a BTS pole by non-authorised non-Jemena representatives. Meter number: 0074355 Defect notice: J22703 Please disregard the incorrect address label on the meter panel. | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | PV21 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43720.6139 |  |  | 14836 | Residential |  | 20200110JEM_01 | Infrastructure (network-based) | -37.6961 | 144.9212 | 1 | Jemena | Report | 18729 | 0.019786 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | Other
Feeder turned off to isolate pole and MFB called to extinguish fire HV crossarm replaced On inspection, indoor substation / transformer was found with a large amount of oil expelled and was replaced as well | 10 MARION STREET, COBURG NORTH VIC 3058 | A044166 |  |  |  | Leakage |  |  | 2 | Pole top fire caused by atmospheric conditions damaged HV crossarm 40A powder-filled fused operated blue phase | Pole top;Transformer | 0 | 0 | 0 |  | CS12 | Electrical leakage / tracking due to atmospheric conditions | Pole-top fire | 44105.9208 | 1 | Negligible: no ground fire | 14844 | Roadway |  | 20200110JEM_02 | Infrastructure (network-based) | -37.731 | 144.9508 | 1 | Jemena | Report | 19197 | 0.0086424 | 22kV AC | Essendon Airport | 3058 | Coburg North | Pole
Crew arranged isolation and repair overnight. | 201 Yarrawalla S Rd, Yarrawalla VIC 3575, Australia | 32032629 |  |  |  | Leakage |  |  |  | Vic Fire reported ground fire started by our assets at incident location. When crew arrived, they found that the crossarm had burnt through at the roadside pin insulator and burnt grass underneath our assets in road reserve. There was no HVI No injuries or third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | CHA006 | Excessive leakage current | Pole-top fire;Grassfire | 43952.6833 | 1 | Medium: 1000 sq.m - 10 ha | 14824 | Roadway |  | 20200110PWA_01 | Infrastructure (network-based) | -36.1815 | 144.0319 | 1 | Powercor | Report | 18724 | 0.029656 | 22kV AC | Bendigo Airport | 3575 | Yarrawalla | Crossarm
On arrival crew isolated supply and carried out repairs. | 575 Gerang-Glenlee Rd, Gerang Gerung VIC 3418, Australia | 31015798 |  |  |  | Leakage |  |  |  | Report received of pole and ground fire at incident location. On arrival crew found Buck x arm fire and grass fire. There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | NHL015 | Excessive leakage current | Pole-top fire;Grassfire | 43952.4 | 1 | Localised: less than 10 sq.m | 14825 | Roadway |  | 20200110PWA_02 | Infrastructure (network-based) | -36.3236 | 141.8772 | 1 | Powercor | Report | 18714 | 0.00068866 | 22kV AC | Horsham Aerodrome | 3418 | Gerang Gerung | Crossarm
Supply isolated repairs carried out | 16 Sobeys Rd, Napoleons VIC 3352, Australia | 32013707 |  |  |  | Leakage |  |  |  | Report received of pole fire and broken crossarm . There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | BAS022 | Excessive leakage current | Pole-top fire | 43952.7396 | 1 | Negligible: no ground fire | 14830 | Agricultural |  | 20200110PWA_07 | Infrastructure (network-based) | -37.6616 | 143.8301 | 1 | Powercor | Report | 18719 | 0.032701 | 22kV AC | Ballarat Aerodrome | 3352 | Napoleons | Crossarm
Crew isolated and CFA extinguished. | 8655 Murray Valley Hwy, Boundary Bend VIC 3599, Australia | 32148923 |  |  |  | Leakage |  |  |  | Vic fire reported pole fire. Crew arrived to find one end of pole was burning. Crew isolated and CFA extinguished fire No ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | BBD021 | Excessive leakage current | Pole-top fire | 43952.8715 | 1 | Negligible: no ground fire | 14831 | Roadway |  | 20200110PWA_08 | Infrastructure (network-based) | -34.7201 | 143.1731 | 1 | Powercor | Report | 18720 | 0.0042396 | 22kV AC | Swan Hill Aerodrome | 3599 | Boundary Bend | Pole
Crew isolated and repaired | 44 POWELLS AVENUE, STRATHDALE VIC 3550 | 32041169 |  | Within clearances | [5 empty] | Customer reported tree branch is resting on service wire, has seen it spark a couple of times, spark falls to the ground. When crew arrived, they found service wire was going through treed area on customers property and had been rubbing against it. Crew noted minor burn marks to grey twisted service wire. No ground fire, no injury, no third party damage. | Service cable (insulated) | 2 | 2 | 2 |  | BET005 | Vegetation: Trees Incident | Singeing or local charring/blackening only | 43983.7347 |  |  | 14837 | Residential |  | 20200110PWA_13 | Infrastructure (customer connection) | -36.7552 | 144.3178 | 1 | Powercor | Report | 18730 | 0.029968 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | Strathdale | Trees
On arrival crew isolated supply and carried out repairs | 129 Kulkyne Way Iraak 3494 | 30097098 |  |  |  | Leakage |  |  |  | A Powercor fault crew attending a fault found that a pole fire at the incident location. There was no ground fire or third party damage. | Pole (wood) | 2 | 2 | 2 |  | RCT014 | excessive leakage current | Pole-top fire | 43983.875 | 1 | Negligible: no ground fire | 14838 | Roadway |  | 20200110PWA_14 | Infrastructure (network-based) | -34.4032 | 142.2811 | 1 | Powercor | Report | 18731 | 0.00016551 | 22kV AC | Mildura Airport | 3494 |  | Pole
Faults crew attended the site and made it safe. They replaced the pole and restored supply. | 22 DELIA STREET, OAKLEIGH SOUTH VIC 3167 | 2328854 |  | Lightning |  |  |  |  | 1 | UE received a call that a power pole was on fire from a lightning strike. | Pole (wood) | 0 | 0 | 0 |  | OR33 | The cause of the fire was a lightning strike. | Pole-top fire | 21/11/2019 15:25 | 1 | Negligible: no ground fire | 14839 | Roadway |  | 20200110UTD_01 | Infrastructure (network-based) | -37.9204 | 145.0856 | 1 | United Energy Distribution | Report | 18734 | 0.0027199 | Low voltage AC (<1kV) | Moorabbin Airport | 3167 | Oakleigh South | Lightning
Faults crew attended the site and upon inspection, it was identified that the wooden cross-arm was burnt. The site was isolated and made safe. The pole top structure was repaired and supply was restored. | 99 SOUTH ROAD, BRIGHTON VIC 3186 | 1805014 |  |  |  | Leakage |  |  | 1 | UE received a call from a customer that there was smoke and embers on the timber cross-arm. | Crossarm (wood) | 0 | 0 | 0 |  | MR13 | The cause of the fire was tracking across the insulator. | Pole-top fire | 26/11/2019 8:35 | 1 | Negligible: no ground fire | 14842 | Roadway |  | 20200110UTD_02 | Infrastructure (network-based) | -37.9285 | 144.9996 | 1 | United Energy Distribution | Report | 18740 | 0.041598 | 11kV AC | Moorabbin Airport | 3186 | Brighton | Crossarm
The LEI arrive on site and completed the inspection and COES and to assist the customer the crews remained on site and completed the reconnection. The crews have disconnected the existing neutral screen overhead service line and made the site and installation safe. The REC has been advised to contact Jemena Network Connections to arrange an After Hours reconnection appointment. | 28 AILSA GROVE, IVANHOE VIC 3079 | A109609 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the address for a single 1 hour Truck Appointment at 11.00am (SO: 100101235615) When they arrive the found the REC has already removed the service fuse, existing mains cables, existing meter panel and the distributors electricity meter disconnected removed and laying on the ground. | Meter board (including fuses);Smart meter | 0 | 0 | 0 |  | FF90 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43597.4583 |  |  | 14845 | Residential |  | 20200111JEM_01 | Infrastructure (network-based) | -37.7659 | 145.0396 | 1 | Jemena | Report | 18744 | 0.0088484 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Other
On arrival crew isolated supply and carried out repairs | 100 Coonawarra Dr, Avalon VIC 3212, Australia | 32085621 |  |  |  | Unknown technical factor |  |  |  | The crew were dispatched to a ground fire and blown transformer at the incident location. On arrival the crew found a 10kva transformer had failed causing debris to fall to the ground igniting grass below. Oil had also fallen to ground below . There was some damage to customers fencing and vegetation. No injuries were reported | Pole mounted | 2 | 1 | 2 |  | FNS032 | Transformer failure. | Grassfire | 44136.6875 | 1 | Small: 10 - 1000 sq.m | 14858 | Roadway |  | 20200114PWA_01 | Infrastructure (network-based) | -38.0383 | 144.4196 | 1 | Powercor | Report | 18762 | 0.0023148 | 22kV AC | Avalon Airport | 3212 | Avalon | AF Other
Faults crew attended the site and upon investigation, it was identified the service fuse on the pole had blown and there was a small grass fire at the base of the pole. The fuse and fuse holder was subsequently replaced before supply was restored. | 218B ESPLANADE, BRIGHTON VIC 3186 | 1806095 |  |  |  | Mechanical breakdown |  |  | 1 | UE received a call from a customer to advise of no supply. UE data analytics also identified abnormal voltage behavior at the property. | Connection box | 0 | 0 | 0 |  | NB33 | The cause of the small grass fire was a service fuse falling out of a fuse holder. | Grassfire | 27/11/2019 16:30 | 1 | Localised: less than 10 sq.m | 14861 | Roadway |  | 20200114UTD_01 | Infrastructure (network-based) | -37.9102 | 144.9864 | 1 | United Energy Distribution | Report | 18765 | 0.03169 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Fuse
Fault crews attended the site and upon inspection, it was identified that a branch from a council tree has fallen onto the HV lines, snapping the conductors and allowing them to contact the LV which caused a HVI. LEI attended the site and confirmed the HVI. The site was isolated and made safe. Field crews repaired the conductors and supply was restored. | 32 CORROBOREE PLACE, TEMPLESTOWE LOWER VIC 3107 | 7068494 |  | Fallen;Council |  |  |  |  | 1 | UE received a call that a tree was in power lines and UE protection has operated. | Conductor (bare) | 0 | 0 | 0 |  | BU6 | Vegetation: Trees Incident | HV injection | 20/12/2019 18:25 |  |  | 14882 | Roadway |  | 20200115UTD_03 | Infrastructure (network-based) | -37.7603 | 145.1082 | 1 | United Energy Distribution | Report | 18796 | 0.031293 | 11kV AC | Essendon Airport | 3107 | Templestowe Lower | Trees
Jemena fault crew attended and disconnected supply to street light pole from the pit and made safe. Also the construction workers at 74 Vermilion Drive had placed barriers around the incident site with warning signs. | 74 VERMILION DRIVE, GREENVALE VIC 3059 | A153097 | Vehicle |  |  |  |  | Phase to earth | 2 | Vehicle impacted steel street light pole A153097, causing pole to break. The impact caused the active supply in the pole to come in contact with steel pole, livening up the pole and car. Tow truck driver who was there to remove the car received a minor shock. The person who called it in was Daniel Waddell (mobile number 0477714718) from Metricon, the company which is constructing at 74 Vermilion Drive. | Pole (steel) | 0 | 0 | 0 |  | COO11 | The vehicle impact caused the active supply in the pole to come in contact with steel pole, livening up the pole and car. | Minor shock;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 16/01/2020 13:50 |  |  | 14885 | Residential |  | 20200116JEM_02 | Infrastructure (network-based) | -37.6342 | 144.9502 | 1 | Jemena | Report | 18802 | 0.0011192 | Low voltage AC (<1kV) | Essendon Airport | 3059 | Greenvale | Vehicle
Customer put fire out. Fire brigade on site. Crew dispatched, isolated substation. | 46 MOUNTAIN ROAD, COCKATOO VIC 3781 | 420544 |  | Lightning | [5 empty] | Pole fire | Dropper/bridge | 0 | 0 | 0 |  | BGE22 | Lightning hit substation pole. blue phase lv leads blown off, LV N down the pole as been on fire. 6 - 8 inches | Pole-top fire | 15/01/2020 19:25 | 1 | Negligible: no ground fire | 14883 | Residential |  | 20200116SPN_01 | Infrastructure (network-based) | -37.9247 | 145.5117 | 1 | AusNet Services Distribution | Report | 18799 | 0.013278 | Low voltage AC (<1kV) | Moorabbin Airport | 3781 | Cockatoo | AF Other
Supply isolated, pole replaced | 491 KERANG-KOONDROOK ROAD, KERANG VIC 3579 | 32029954 |  |  |  | Leakage |  |  |  | CFA reported pole fire and ground fire at the incident location, Upon arrival crew found that strain/angle pole "P50 Koondrook" had burnt through between pole top assembly and centre phase strain insulator hardware. Conductors remained suspended aloft, burning material however fell to ground and ignited a grass fire along the road verge, approximately 20M x 100M in size. There was no reported injuries | Pole (wood) | 2 | 2 | 2 |  | KGT003 | Excessive leakage current | Pole-top fire;Grassfire | 15/01/2020 19:07 | 1 | Medium: 1000 sq.m - 10 ha | 14892 | Agricultural |  | 20200117PWA_04 | Infrastructure (network-based) | -35.7421 | 143.9617 | 1 | Powercor | Report | 18810 | 0.0038021 | 22kV AC | Swan Hill Aerodrome | 3579 | Kerang | Pole
Asset inspected for servicability | 52 Bowyers Rd, Woodend North VIC 3442, Australia | 33024345 |  | Lightning | [5 empty] | CFA reported grass fire that commenced at base of pole, Upon arrival crew found evidence of lightning striking CHP "kyneton 1", a ground fire commenced from the base of the concrete pole and burnt 200M x 100M of grass, no 3rd party damage. | Pole (concrete) | 2 | 2 | 2 |  | WND014 | Lightning strike | Grassfire | 15/01/2020 17:00 | 1 | Medium: 1000 sq.m - 10 ha | 14894 | Roadway |  | 20200117PWA_05 | Infrastructure (network-based) | -37.3308 | 144.5192 | 1 | Powercor | Report | 18812 | 0.0072639 | 22kV AC | Wallan (Kilmore Gap) | 3442 | Woodend North | Lightning
Made safe and repairs completed. | 181 CECIL STREET, SOUTH MELBOURNE VIC 3205 | 30174143 |  |  |  | Corrosion |  |  |  | Customer report of powerline down, caused ground fire, MFB onsite. Crew found blue phase LV conductor on ground. Ground fire of approx. 250mm2 There was no reported injuries or property damage | Connector/termination | 2 | 2 | 2 |  | AP006 | overheated connection | Grassfire | 15/01/2020 10:53 | 1 | Localised: less than 10 sq.m | 14897 |  |  | 20200117PWA_06 | Infrastructure (network-based) | -37.8352 | 144.9589 | 1 | CitiPower | Report | 18815 | 0.029679 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Connection
On arrival crew isolated supply and carried out repairs | 385 Goochs Ln, Pastoria VIC 3444, Australia | 32046351 | Manned aircraft | [6 empty] | Report received of conductor on ground at incident location. Crew attended fault site and could see no apparent causal evidence for fault occurrence. Local landholder informed crew that a helicopter carrying out fire fighting operations in the area had contacted conductor causing conductor to fall to ground. There was no aircraft found at incident location. Emergency Management commissioner in his media briefing stated "A helicopter working on the fire hit a powerline on Monday morning, but caused only windscreen damage and forced the pilot, who escaped uninjured, to make an emergency landing". There was no fire start, no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | WND013 | Helicopter struck conductor | No Go Zone (contact);Damage to network assets | 20/01/2020 12:30 |  |  | 14914 | Agricultural |  | 20200121PWA_01 | Infrastructure (network-based) | -37.2232 | 144.5882 | 1 | Powercor | Report | 18841 | 0.02374 | 12.7kV AC (SWER) | Wallan (Kilmore Gap) | 3444 | Pastoria | Vehicle
On arrival crew isolated supply and kiosk replacement arranged. | 5 Chicquita Ct, Bacchus Marsh VIC 3340, Australia | PA0054540 |  |  |  | Electrical breakdown |  |  |  | While patrolling area following thunderstorms field crew were alerted by fore brigade of smoke emanating from kisok substation at incident location. On arrival crew of the substation it was established there was damaged HV cable and a possible damaged kiosk. There was no ground fire, no reported injuries or third party property damage. | Cable;Pad mounted equipment/kiosk | 2 | 2 | 2 |  | BMH004 | Cable faulted following electrical storm | Plant/equipment | 19/01/2020 19:19 | 1 | Negligible: no ground fire | 14921 |  |  | 20200121PWA_03 | Infrastructure (network-based) | -37.6732 | 144.4184 | 1 | Powercor | Report | 18849 | 0.036043 | 22kV AC | Avalon Airport | 3340 | Bacchus Marsh | OH Cable
Sent crew to make safe, investigate and repair. Site was made safe and fuse was replaced. | 1 WHITELAWS TRACK, DEVON NORTH VIC 3971 | 2621400 |  | Precipitation |  | Age;Candled fuse |  |  | 1 | Report of candled HV BA Fuse. Crew upon attendance found fuse in the up position and had candled. There was no evidence of a fire at ground level. Refer to attached site photos. | Boric acid | 0 | 0 | 0 |  | FTR12 | Candled fuse due to internal degradation. | Pole-top fire | 19/01/2020 15:59 | 1 | Negligible: no ground fire | 14918 |  |  | 20200121SPN_06 | Infrastructure (network-based) | -38.4973 | 146.5926 | 1 | AusNet Services Distribution | Report | 18846 | 0.02315 | 22kV AC | Morwell (Latrobe Valley Airport) | 3971 | Devon North | Fuse
Sent crew to make safe, investigate and repair. Site was made safe. Existing 100kVA transformer was replaced with a new 200kVA TX to cater for the load. | 1048 MOUNT DANDENONG TOURIST ROAD, MONTROSE VIC 3765 | 1001438 |  |  |  | Neutral fault;Electrical overload |  |  |  | Report of fire at the base of pole. Fire was observed at the base of a substation pole 1001438 located outside 1053 Mt Dandenong Tourist Rd. Fire area approx. 4m long x 1m wide. CFA extinguished fire and Fault crews attended site and made safe. Please refer to attached photos. | Pole mounted | 0 | 1 | 0 |  | CYN33 | Currently under investigation. Aluminium lug at the Neutral lead on the TX melted falling to the ground was the suspected cause of the small grass fire at the base of pole. This is consistent with the scorch marks found at the pole base. Possible overload on the TX due to number of customers connected. | Less than $50k damage;Grassfire | 19/01/2020 6:24 | 1 | Localised: less than 10 sq.m | 14919 | Residential |  | 20200121SPN_07 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18850 | 0.015653 | Low voltage AC (<1kV) | Moorabbin Airport | 3765 | Montrose | AF Other
Sent crew to make safe, investigate and repair. | 27A GREENWATTLE GAP ROAD, CORRYONG VIC 3707 | 5212236 |  |  |  | Fuse failed to eject |  |  | 2 | Report of candeling HV EDO fuse | EDO fuse | 0 | 0 | 0 |  | WOTS24 | Fuse hung up. No burn marks on fuse, pole or ground | Hung-up fuse only | 21/01/2020 14:52 |  |  | 14922 | Agricultural |  | 20200121SPN_08 | Infrastructure (network-based) | -36.2132 | 147.8693 | 1 | AusNet Services Distribution | Report | 18852 | 0.039405 | 22kV AC | Wangaratta Aero | 3707 | Corryong | Fuse
Site made safe and repairs made to restore supply LV spreader installed on 29 January 2020 | 3 McPherson St, Keilor East VIC 3033, Australia | A142249 |  | Wind |  | Conductor clashing |  | Phase to earth | 1 | Report of wires down and reported that was caused by workers in vicinity. On arrival crew found blue phase LV conductor on the ground. Unclear what caused fault but signs of clashing. Truck on site deemed not high enough to have contacted LV overhead conductor. No Go Zone breach has been ruled out. It was a windy day and there were signs of wind damage in the vicinity. | Conductor (bare) | 0 | 0 | 0 |  | AW08 | Report that concrete truck had brought down wires but no proof. It was very windy at time of incident, therefore it is suspected that strong wind gusts had caused conductor clashing. | Loss of supply | 22/01/2020 15:07 |  |  | 14942 | Residential |  | 20200122JEM_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | Jemena | Report | 18872 | 0.0066898 | Low voltage AC (<1kV) | Moorabbin Airport | 3033 | Keilor East | Conductor
Fault crews attended the site to investigate. Upon inspection, it was identified the HV cross-arm was burnt and the HV conductor hit the neutral wire. LV was ok and there was no evidence of HVI. ESV was notified, ref #13116347. The site was isolated and made safe. The pole top structure was repaired and supply was restored. | 20 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7037580 |  |  |  | Leakage |  |  | 1 | UE received call that customers had no power and UE protection operated. | Crossarm (wood) | 0 | 0 | 0 |  | EB11 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.3646 | 1 | Negligible: no ground fire | 14933 | Roadway |  | 20200122UTD_04 | Infrastructure (network-based) | -37.8507 | 145.0964 | 1 | United Energy Distribution | Report | 18863 | 0.025679 | 22kV AC | Moorabbin Airport | 3125 | Burwood | Crossarm
Faults crew patrolled the line to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. ESV was notified, ref# 13116340. The site was isolated and made safe. The pole top structure was repaired. | 33 ARTHUR STREET, CAULFIELD NORTH VIC 3161 | 9490012 |  |  |  | Leakage |  |  | 1 | UE protection on the 66kV line operated. | Crossarm (wood) | 0 | 0 | 0 |  | MTS-EL/EM | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.3993 | 1 | Negligible: no ground fire | 14934 | Roadway |  | 20200122UTD_05 | Infrastructure (network-based) | -37.8681 | 145.0279 | 1 | United Energy Distribution | Report | 18864 | 0.033434 | 66kV AC | Moorabbin Airport | 3161 | Caulfield North | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt and broken at the kingbolt. There was no evidence of HVI. ESV was notified, ref #13116335. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 4 WINDOO STREET, FRANKSTON NORTH VIC 3200 | 3316011 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply. | Crossarm (wood) | 0 | 0 | 0 |  | FTN13 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43952.4618 | 1 | Negligible: no ground fire | 14937 | Roadway |  | 20200122UTD_07 | Infrastructure (network-based) | -38.1203 | 145.1486 | 1 | United Energy Distribution | Report | 18867 | 0.0095567 | 22kV AC | Moorabbin Airport | 3200 | Frankston North | Crossarm
Operator dispatched to a report of flickering lights. Operator found SWER 6k BA fuse at BD251 had candelled. Fuse opened and replaced. | 2630 BENAMBRA-CORRYONG ROAD, BENAMBRA VIC 3900 | 1606823 |  |  |  | Candled fuse |  |  |  | Candled fuse. | Boric acid | 0 | 0 | 0 |  | BDL8 | CANDLED FUSE | Pole-top fire | 21/01/2020 9:50 | 1 | Negligible: no ground fire | 14943 | Agricultural |  | 20200123SPN_01 | Infrastructure (network-based) | -36.8928 | 147.7042 | 1 | AusNet Services Distribution | Report | 18874 | 0.011561 | 12.7kV AC (SWER) | Bairnsdale Airport | 3900 | Benambra | Fuse
Dispatched fault crew to make safe, investigate and repair. Crew replaced the EDO fuse and restored supply. | 69 BIRKINS ROAD, BETE BOLONG VIC 3888 | 1906294 |  |  |  | Candled fuse |  |  |  | Report of candling EDO fuse at pole1906294. Upon arrival crew found a burnt EDO fuse. No evidence of fire at the base of the pole. Refer to the attached photos of failed fuse unit. | EDO fuse | 0 | 0 | 0 |  | NLA32 | Candled fuse due to internal degradation. | Pole-top fire | 27/01/2020 13:27 | 1 | Negligible: no ground fire | 14954 | Agricultural |  | 20200128SPN_01 | Infrastructure (network-based) | -37.695 | 148.3901 | 1 | AusNet Services Distribution | Report | 18908 | 0.011662 | 22kV AC | Bairnsdale Airport | 3888 | Bete Bolong | Fuse
Dispataced fault crew to make safe, investigate and repair. Crew isolated the sub and replaced the Sub FOLCB restored the supply. | 31 ENNISVALE AVENUE, SANDY POINT VIC 3959 | 2021773 |  | Prone to salt deposition |  | Corrosion;Overheated connection |  |  |  | Report of Fuse Mains Box fire at pole 2021773. Crew observed a FOLCB on the sub had burnt out and slight burn mark on the Pole. No other burnt areas including the ground. Crew isolated the sub and replaced the Sub FOLCB restored the supply. Refer to attached photos. | Connection box | 0 | 0 | 0 |  | FTR21 | Plausible cause is a combination of corroded connection that resulted in an overheated onnection. | Pole-top fire | 27/01/2020 13:04 | 1 | Negligible: no ground fire | 14959 | Residential |  | 20200128SPN_02 | Infrastructure (network-based) | -38.8302 | 146.1315 | 1 | AusNet Services Distribution | Report | 18907 | 0.010721 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3959 | Sandy Point | Fuse
Sent fault crew to make safe, investigate and organise repairs. Small fire was already out and assets were checked for any damage. | 16 HILLSIDE AVENUE, BORONIA VIC 3155 | 1222987 |  | Blown branch/vegetation | [5 empty] | Report of tree branch hitting LV powerlines and falling to ground. Tree branch feel down across the line but it did not bringing the lines down. Small fire on the nature strip at the tree base. The area of of fire patch is about 10cm x 30 cm. Refer to the attached site photos. | Conductor (bare) | 0 | 0 | 0 |  | BWR13 | Vegetation: Trees Incident | Grassfire | 28/03/2020 15:46 | 1 | Localised: less than 10 sq.m | 14972 | Residential |  | 20200130SPN_01 | Infrastructure (network-based) | -37.8468 | 145.2903 | 2 | AusNet Services Distribution | Report | 19546 | 0.035447 | Low voltage AC (<1kV) | Moorabbin Airport | 3155 | Boronia | Trees
Sent crew to make safe, investigate and organise repairs. Work was undertaken to replace pole 5215484 with a taller pole and resag the low span of conductor. This work was completed on 04/02/20. A follow up action item was raised to assess trees within fire area beside line to see if in danger of falling on line. | 170 LUCYVALE ROAD, BERRINGAMA VIC 3691 | 5216793 |  | Wind;Fallen | [5 empty] | Report of fallen tree and grass fire. CFA had fire under control. Tree fell between spans 5216793 and 5215484 on the single phase 22kV line. Upstream ACR (CY006) tripped, but did not lock out. Refer to attached site photos. | Conductor (bare) | 0 | 0 | 0 |  | WOTS24 | Vegetation: Trees Incident | Grassfire | 43832.1361 | 1 | Medium: 1000 sq.m - 10 ha | 14996 | Agricultural |  | 20200202SPN_04 | Infrastructure (network-based) | -36.2366 | 147.6513 | 2 | AusNet Services Distribution | Report | 18948 | 0.021617 | 22kV AC | Wangaratta Aero | 3691 | Berringama | Trees
On arrival crew isolated supply and carried out repairs. LEI attended to check for HVI | 3 Spalding St, Ararat VIC 3377, Australia | 32113387 |  |  |  | Electrical breakdown |  |  |  | Report revived of smoke and sparks coming from top of pole at incident location. There was no ground fire, no reported injuries but report of third party damage due to HVI. | Dropper/bridge | 2 | 2 | 2 |  | ART034 | Insufficient HV dropper clearance | Pole-top fire;HV injection | 43832.1007 | 1 | Negligible: no ground fire | 15016 | Roadway |  | 20200204PWA_04 | Infrastructure (network-based) | -37.2835 | 142.9187 | 1 | Powercor | Report | 19413 | 0.0078067 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3377 | Ararat | AF Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was cut. The site was isolated and made safe. The service wire was replaced and supply was restored. | 48 STATION STREET, SOMERVILLE VIC 3912 | 1109969 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a vegetation trimmer has cut the customer's service wire while gardening and has lost supply. | Service cable (insulated) | 0 | 0 | 0 |  | HGS22 | The person was working too close to the service line. | Loss of supply;No Go Zone (contact) | 43924.4583 |  |  | 15313 | Residential |  | 20200318UTD_01 | Infrastructure (network-based) | -38.227 | 145.1762 | 1 | United Energy Distribution | Report | 19383 | 0.02462 | Low voltage AC (<1kV) | Moorabbin Airport | 3912 | Somerville | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was cut. The service wire was replaced and supply was restored. | 94 GAMBLE ROAD, CARRUM DOWNS VIC 3201 | 3321613 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a maintenance person has cut the service wire while gardening and the wire was laying across the road. | Service cable (insulated) | 0 | 0 | 0 |  | FTN25 | The person was working too close to the service line. | Loss of supply;No Go Zone (contact) | 44168.4583 |  |  | 15315 | Residential |  | 20200318UTD_03 | Infrastructure (network-based) | -38.1133 | 145.1934 | 1 | United Energy Distribution | Report | 19385 | 0.034463 | Low voltage AC (<1kV) | Moorabbin Airport | 3201 | Carrum Downs | Other
Crew re-terminated the existing O/H Service Cable at the Service Pole | 181 MUNTZS ROAD, ASHBOURNE VIC 3442 | 32047349 |  |  |  | Neutral fault |  |  |  | Person was in the bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metal shower taps and her bare feet while standing on the wet shower base. | Service cable (insulated) | 0 | 0 | 0 |  | WND011 | Connection malfunction | Minor shock | 19/11/2019 14:30 |  |  | 15320 | Residential |  | 20200319PWA_01 | Infrastructure (network-based) | -37.3789 | 144.4841 | 1 | Powercor | Report | 19393 | 0.032188 | Low voltage AC (<1kV) | Melbourne Airport | 3442 | Ashbourne | Connection
Crew replaced service | 5 WILLS COURT, GROVEDALE VIC 3216 | 33044119 |  | Blown branch/vegetation |  |  |  |  | 1 | Person was standing barefoot on wet concrete path, adjacent outside tap attached to the rear of the house. He received a minor tingle to his wet right hand whilst adjusting the garden tap. | Neutral screen | 0 | 0 | 0 |  | WPD012 | Vegetation: Trees Incident | Minor shock | 22/12/2019 16:00 |  |  | 15327 | Residential |  | 20200319PWA_08 | Infrastructure (network-based) | -38.2041 | 144.33 | 1 | Powercor | Report | 19401 | 0.010801 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Grovedale | Trees
Crew attended and made repairs | 33 VALENTINE GROVE, ARMADALE VIC 3143 | 30166209 |  |  |  | Corrosion |  |  |  | Person received an electric shock when he simultaneously contacted the Metallic tap with his hand and metallic waste with his foot. | Service cable (insulated) | 0 | 0 | 0 |  | AR007 | Corroded service neutral at FOLCB | Minor shock | 19/12/2019 16:00 |  |  | 15331 | Residential |  | 20200319PWA_12 | Infrastructure (network-based) | -37.8642 | 145.0253 | 1 | CitiPower | Report | 19405 | 0.028001 | Low voltage AC (<1kV) | Moorabbin Airport | 3143 | Armadale | OH Cable
re-terminated the existing O/H Service Cable | 36 DOMAILLE CRESCENT, SWAN HILL VIC 3585 | 33069262 |  |  |  | Corrosion |  |  |  | Person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower Tap and her bare feet while standing on the wet shower base and waste water outlet. | Service cable (insulated) | 0 | 0 | 0 |  | SHL007 | Corroded O/H Service Neutral Conductor termination at the Reticulation Sub Station Pole | Minor shock | 13/12/2019 8:00 |  |  | 15333 | Residential |  | 20200319PWA_14 | Infrastructure (network-based) | -35.3527 | 143.5474 | 1 | Powercor | Report | 19407 | 0.0025914 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
On arrival crew isolated supply and carried out repairs. | Hamilton-Chatsworth Rd, Penshurst VIC 3289, Australia | 31018721 | [6 empty] | 1 | Call received from Vic Fire advising of a fire Penshurst - approx 3k east Dunkeld-Penshurst rd . At this time NRB-HTN 66kv line operated to Lockout. On arrival crew advised that centre phase pole top assembly had dislodged resulting in a pole fire near the crossarm straps. Debris started a grass fire estimated to be 2000 sq m of roadside reserve. There was no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | NRB-HTN | Dislodged pole top assembly | Pole-top fire;Grassfire | 19/03/2020 13:55 | 1 | Medium: 1000 sq.m - 10 ha | 15340 | Roadway |  | 20200320PWA_03 | Infrastructure (network-based) | -37.7908 | 142.324 | 1 | Powercor | Notification | 19422 | 0.013115 | 66kV AC | Hamilton Airport | 3289 | Penshurst | Pole
Crew replaced the existing O/H Neutral Screened Service Cable | 32 PERTOBE ROAD, WARRNAMBOOL VIC 3280 | 33102264 |  |  |  | Corrosion |  |  |  | Person was in the Bathroom washing his hands at the Basin when he received an electric shock as he made simultaneous contact between his hand on the metal Tap and his bare feet while standing on the wet tiled floor. | Service cable (insulated) | 0 | 0 | 0 |  | WBL004 | Corroded O/H Service Neutral Conductor termination at the Pole Top Connection | Minor shock | 20/12/2019 9:00 |  |  | 15343 | Other | Caravan park | 20200320PWA_05 | Infrastructure (network-based) | -38.3953 | 142.4762 | 1 | Powercor | Report | 19427 | 0.03628 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Crew replaced the existing O/H Service Cable | 7 EAGLE AVENUE, ANGLESEA VIC 3230 | 32076538 |  |  |  | Corrosion |  |  |  | person was outside rinsing her Wet Suit at an external Tap when she received an electric shock as she made simultaneous contact with her hand on the metal Tap and her bare feet while standing on the wet ground. | Conductor (bare) | 0 | 0 | 0 |  | WPD021 | Corroded O/H Service Neutral Conductor termination at the Reticulation Pole and the Customers FOLCB. | Minor shock | 31/12/2019 14:00 |  |  | 15346 | Residential |  | 20200320PWA_08 | Infrastructure (network-based) | -38.4093 | 144.1682 | 1 | Powercor | Report | 19430 | 0.037837 | Low voltage AC (<1kV) | Avalon Airport | 3230 | Anglesea | Connection
On arrival crew isolated supply and carried out repairs. LEI attended | Bush Nursing Centre, 28 Ascot St, Dartmoor VIC 3304, Australia | 30089487 |  |  |  | Leakage |  |  |  | Vic fire reported smoldering pole at incident location. ON arrival crew found a crossarm has burnt through. The fire self extinguished. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | PLD003 | Excessive leakage current | Pole-top fire;HV injection | 20/03/2020 13:45 | 1 | Negligible: no ground fire | 15352 | Roadway |  | 20200323PWA_02 | Infrastructure (network-based) | -37.9239 | 141.2753 | 1 | Powercor | Report | 19437 | 0.021488 | 22kV AC | Portland (Cashmore Airport) | 3304 | Dartmoor | Crossarm
Zinfra crews made safe and completed repairs as follows: â€¢ Broke bridges at tee off pole A012091, moved excavator. â€¢ Tested and remade bridges at tee off pole. â€¢ Fuses already removed for customer, not sure why. | 7 THE BOULEVARD, MOONEE PONDS VIC 3039 | A011909 | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | Excavator contacted overhead powerlines, boom of the excavator was fused to the lines. Report of 1 large spark noticed from the contact at the time. 1 power line cable came down in carpark of Maribyrnong football club. No shock was received by excavator operator. No permit to work was logged. No details of responsible third party were available. | Conductor (bare);Aluminium | 1 | 0 | 0 |  | ES13 | No Go Zone breach | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 24/03/2020 14:46 |  |  | 15359 | Public space |  | 20200324JEM_01 | Infrastructure (network-based) | -37.768 | 144.9034 | 1 | Jemena | Report | 19654 | 0.0026655 | Low voltage AC (<1kV) | Essendon Airport | 3039 | Moonee Ponds | Vehicle
Site made safe | 5 KENWOOD COURT, PRESTON VIC 3072 | A066215 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the address today with 10 x Supply Orders to abolish 10 individual overhead service lines and metering to 10 Department of Health and Human Services properties. Please see attached abolishment application and photos of how the crews found the electrical installation and distributor's electricity meter for 5 Kenwood Court Preston. Energised service line was found still attached and connected, service fuse removed, customer wiring cut and exposed and electricity meter laying on the ground. This has been left in an unsafe manner by the contractor (Delta Demolition) on site working on behalf of the Victorian Government. | Aluminium;Aluminium twisted (grey);Smart meter | 0 | 0 | 0 |  | CS3 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/03/2020 10:02 |  |  | 15364 | Residential |  | 20200325JEM_02 | Infrastructure (network-based) | -37.7489 | 144.998 | 1 | Jemena | Report | 19450 | 0.030323 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the pole top construction was burnt. The site was isolated and made safe. The cross-arm and insulators were replaced and supply was restored. | 51A GOVERNOR ROAD, MORDIALLOC VIC 3195 | 1807866 |  |  |  | Leakage |  |  | 1 | UE received a call that there was a fire on the power pole. | Crossarm (wood) | 0 | 0 | 0 |  | MC3 | The cause of the fire was tracking across the insulator. | Pole-top fire | 20/03/2020 23:30 | 1 | Negligible: no ground fire | 15379 | Roadway |  | 20200327UTD_01 | Infrastructure (network-based) | -38.0087 | 145.0979 | 1 | United Energy Distribution | Report | 19470 | 0.0068623 | 22kV AC | Moorabbin Airport | 3195 | Mordialloc | Crossarm
Crews made appropriate repairs (reattached service at house end and FOLCB) | 9 TITUS COURT, RESERVOIR VIC 3073 | A048858 | Working too close to overhead lines | [5 empty] | 2 | Unknown tree cutting contractor of the council (City of Darebin) dropped a council tree branch onto the service line while trimming trees. This resulted in the service wire hanging very low within reach and raiser bracket on the ground. No permit to work was logged. No supply lost. | Aluminium twisted (XLPE);Connection box;Service cable (insulated) | 0 | 0 | 0 |  | TT3 | No Go Zone breach | No Go Zone (contact) | 23/03/2020 15:16 |  |  | 15385 | Residential |  | 20200330JEM_02 | Infrastructure (network-based) | -37.7005 | 145.0256 | 1 | Jemena | Report | 19477 | 0.028806 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
The Powercor crew made the area safe and isolated the HV line to repair the damaged conductors. | 6 KELLY STREET, WERRIBEE VIC 3030 | 30114401 | Working too close to overhead lines | [5 empty] | 1 | John, from Victrack (mob. 0455149154 ) reported that an excavator on a construction site at the corner of Cherry street and Railway Avenue had come into contact with an overhead 22KV line. The driver is still in the cab of the excavator and is currently ok. On arrival the crew found that an excavator had struck the 22kV overhead conductors between poles LIS-204135 and LIS-936626 located between Kelly Street and Railway Avenue, Werribee. The crew advised that the ambulance was on site assisting the operator who was physically well but in shock. There was no ground fire. | Conductor (bare) | 2 | 2 | 2 |  | WBE024 | Digger/Excavator contacted overhead line | No Go Zone (contact) | 28/03/2020 1:48 |  |  | 15387 | Public space |  | 20200330PWA_02 | Infrastructure (network-based) | -37.8983 | 144.6654 | 1 | Powercor | Notification | 19479 | 0.013779 | 22kV AC | Laverton Raaf | 3030 | Werribee | Vehicle
Field crews attended the site to investigate. Upon inspection, it was identified that the manual gas switch on the pole was damaged by lightning. The site was isolated and made safe. The gas switch was replaced and supply was restored. | 11-13 WESTPOOL DRIVE, HALLAM VIC 3803 | 639074 |  | Lightning |  |  |  |  | 1 | UE received a call from a customer that a transformer on a pole was hit by lightning and exploded. It was on fire for a short time but the fire is now out. UE feeder protection operated. | Any other type | 0 | 0 | 0 |  | DN08 | The cause of the fire was a lightning strike on the manual gas switch. | Plant/equipment | 18/02/2020 19:00 | 1 | Negligible: no ground fire | 15404 | Roadway |  | 20200331UTD_02 | Infrastructure (network-based) | -38.0146 | 145.2625 | 1 | United Energy Distribution | Report | 19499 | 0.030098 | 22kV AC | Moorabbin Airport | 3803 | Hallam | Lightning
ATTEND FAULT | Hume Highway, CHILTERN, VIC, 3683 | 5208203 |  |  |  | Electrical overload |  |  |  | lv cables on transformer caught fire | Pole mounted | 0 | 0 | 0 |  | BWA22 | lv cables on transformer caught fire | Pole-top fire | 30/03/2020 17:30 | 1 | Negligible: no ground fire | 15416 |  |  | 20200401SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19516 | 0.0088762 | 22kV AC | Moorabbin Airport | 3683 |  | AF Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was damaged by the excavator. The service wire was replaced and supply was restored. | 14 PEACE STREET, SPRINGVALE VIC 3171 | 29603 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that an excavator from next door has ripped down the service wire. | Service cable (insulated) | 0 | 0 | 0 |  | SV32 | It is likely the person was working too close to the service line. | Loss of supply;No Go Zone (contact) | 16/03/2020 18:50 |  |  | 15414 | Residential |  | 20200401UTD_03 | Infrastructure (network-based) | -37.9353 | 145.1527 | 1 | United Energy Distribution | Report | 19510 | 0.021742 | Low voltage AC (<1kV) | Moorabbin Airport | 3171 | Springvale | Vehicle
Site made safe The attending Licensed Electrical Inspector (LEI) checked distribution assets, customers metering and accessible switchboards for damage on the isolated circuits Control Room was notified that supply to be restored following works to replace damaged HV crossarm. No other damage was recorded. | 8 ORLEANS ROAD, AVONDALE HEIGHTS VIC 3034 | A025217 |  |  |  | Leakage |  |  | 2 | Pole and crossarm fire due to tracking (electrical leakage), resulting in failure of HV crossarm and HV open wire making contact with the LV open wires No signs of high voltage injection (attached TechSafe report confirms no HVI) No photos are available for this fire start incident | Crossarm (wood) | 0 | 0 | 0 |  | BY14 | Electrical leakage (tracking) | Pole-top fire | 13/03/2020 19:24 | 1 | Negligible: no ground fire | 15427 | Residential |  | 20200403JEM_02 | Infrastructure (network-based) | -37.7567 | 144.8611 | 1 | Jemena | Report | 19536 | 0.028061 | 22kV AC | Essendon Airport | 3034 | Avondale Heights | Crossarm
1 phase service replaced, tested and left on supply. | 58 BROADMEADOWS ROAD, TULLAMARINE VIC 3043 | A046410 | Working too close to overhead lines | [5 empty] | 2 | Garden contractor had accidentally clipped the overhead LV service, however was not on site when the crew arrived. Elderly customer at home. Crew were unable to obtain any details of responsible third-party garden contractor. It is unknown what tool or plant was being used by the garden contractor when the service was damaged. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | AW9 | Accidental LV line conductor contact by third party | Damage to network assets | 16/03/2020 11:29 |  |  | 15436 | Residential |  | 20200407JEM_01 | Infrastructure (network-based) | -37.703 | 144.8798 | 1 | Jemena | Report | 19647 | 0.031111 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Other
Site was made safe and underground crew to repair damaged cable | 9 TOTTENHAM STREET, CRAIGIEBURN VIC 3064 | A089705 and A089704 | Copper theft | [5 empty] | 2 | Copper theft of street light cable (approximately 40m, 4core 16mm) between A089705 and A089704 along Waterview Boulevard opposite 9 Tottenham Street, Craigieburn | Services cable | 0 | 0 | 0 |  | ST32 | Copper theft | Damage to network assets | 44078.5979 |  |  | 15446 | Roadway |  | 20200409JEM_02 | Infrastructure (network-based) | -37.5866 | 144.9067 | 1 | Jemena | Report | 19564 | 0.033961 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
REPLACED FUSE | 650 GEMBROOK-LAUNCHING PLACE ROAD, HODDLES CREEK VIC 3139 | FUSESAVER WT223F |  |  |  | Candled fuse |  |  |  | CANDLING FUSE | Any other type | 0 | 0 | 0 |  | WT223 | CANDLING FUSE | Pole-top fire | 44047.8785 | 1 | Negligible: no ground fire | 15447 |  |  | 20200409SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19565 | 0.036828 | 22kV AC | Moorabbin Airport | 3139 | Hoddles Creek | Fuse
Site made safe and repairs in hand with maintenance crews | 30 BLAIRGOWRIE DRIVE, CRAIGIEBURN VIC 3064 | A131561 | Copper theft | [5 empty] | 2 | Copper theft of underground public lighting services cable | Services cable;Copper | 0 | 0 | 0 |  | ST33 | Copper theft | Damage to network assets | 44108.6312 |  |  | 15449 | Residential |  | 20200410JEM_02 | Infrastructure (network-based) | -37.585 | 144.9055 | 1 | Jemena | Report | 19569 | 0.010678 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Cabling made safe and circuits reinstated | 18 GAUSSBERG WALK, ROXBURGH PARK VIC 3064 | A141396 and A141074 | Copper theft | [5 empty] | 2 | Copper theft of LV street light underground services cable from public lighting circuit along Aitken Boulevard, Greenvale (opposite 18 Gaussberg Walk Roxburgh Park) | Services cable;Copper;Public lighting | 0 | 0 | 0 |  | COO11 | Copper theft | Damage to network assets | 44108.4639 |  |  | 15452 | Roadway |  | 20200411JEM_02 | Infrastructure (network-based) | -37.633 | 144.9112 | 1 | Jemena | Report | 19572 | 0.038291 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Roxburgh Park | Other
worksafe attended 17/03 as proactive visit and issued prohibition notice. applicant then sought permit to work site issue identified 27/3 and reported to worksafe battening installed and PTW to be issued whilst worksafe on site | 104 IRELAND STREET, WEST MELBOURNE VIC 3003 | 30213672 | Building too close or within the No Go Zone;Working too close to overhead lines | [5 empty] | 2 | Citipower No Go Zone officer observed scaffolding in proximity of low voltage conductor without permit to work on issue. Builder advised he had installed battens on service cables but had overlooked proximity to overhead street mains. | Conductor (bare);Service cable (insulated) | 0 | 0 | 0 |  | LS016 | works undertaken without permit to work | No Go Zone (contact) | 27/03/2020 13:48 |  |  | 15462 | Construction |  | 20200414PWA_04 | Infrastructure (network-based) | -37.8065 | 144.943 | 1 | CitiPower | Report | 19598 | 0.009831 | Low voltage AC (<1kV) | Essendon Airport | 3003 | West Melbourne | Other
Truck on arrival found mesh fence cut away, Sub LV fuses found opened, and coppers cut through customer mains. Sub was isolated and earthed, fence was temporarily repaired, and incident was reported to cops. Customer was issued a defect. | 49 SCORESBY ROAD, BAYSWATER VIC 3153 | 1200106 | Vandalism | [6 empty] | Vandalism, 415V, Tranformer LV fuses, deliberately opened, LIS# 1200106 | Any other type;Pole mounted | 0 | 0 | 0 |  | BWR34 | Vandalism. | Loss of supply | 44108.3931 |  |  | 15461 |  |  | 20200414SPN_01 | Infrastructure (network-based) | -37.8454 | 145.2705 | 1 | AusNet Services Distribution | Report | 19583 | 0.034256 | Low voltage AC (<1kV) | Moorabbin Airport | 3153 | Bayswater | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the contractor had drilled through the LV underground cable- truck YVH641. The site was isolated and made safe. The cable was repaired. | FLAT 1 42 ELLIOTT AVENUE, CARNEGIE VIC 3163 | 2327700 | Working too close to underground cables | [5 empty] | 1 | UE was advised that a contractor from Glen Eira City Council who was cleaning storm water drain, has cut underground cable and there are scorch marks on his blade. There was no harm to the contractor. | Services cable | 0 | 0 | 0 |  | EM10 | The person was working too close to the underground cable. | Loss of supply;No Go Zone (contact) | 27/03/2020 10:45 |  |  | 15460 | Roadway |  | 20200414UTD_02 | Infrastructure (network-based) | -37.8916 | 145.0599 | 1 | United Energy Distribution | Report | 19580 | 0.034066 | Low voltage AC (<1kV) | Moorabbin Airport | 3163 | Carnegie | Dug up
on arrival crew carried out isolation and made site safe. Repairs arranged | 1017 OLD CALDER HIGHWAY, KEILOR VIC 3036 | 26810509 | Vehicle | [6 empty] | Customer advised that pillar at front of his property had caught fire. Crew attended onsite the fire brigade was at the incident location with the paralleling pillar taped off. A vehicle had ran the pillar over but no one had any details. The flashover caused a small fire on the nature strip. There was no reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | SA006 | Vehicle struck pillar | Grassfire | 13/04/2020 16:17 | 1 | Localised: less than 10 sq.m | 15472 | Roadway |  | 20200415PWA_02 | Infrastructure (network-based) | -37.7031 | 144.8061 | 1 | Powercor | Report | 19596 | 0.014161 | Low voltage AC (<1kV) | Melbourne Airport | 3036 | Keilor | Vehicle
Reported to ESV for site visit | 25A CROYDON ROAD, SURREY HILLS VIC 3127 | 30177841 | Building too close or within the No Go Zone;Working too close to overhead lines | [6 empty] | Citipower officer attending site for supply enquiry found scaffolding in close proximity of service line /BTS and conduit/ plywood affixed around servcie | Conductor (bare) | 0 | 0 | 0 |  | RD005 | interference during building works | No Go Zone (contact) | 15/04/2020 14:00 |  |  | 15476 | Construction |  | 20200415PWA_04 | Infrastructure (customer connection) | -37.8227 | 145.0892 | 2 | CitiPower | Report | 19603 | 0.0041551 | Low voltage AC (<1kV) | Moorabbin Airport | 3127 | Surrey Hills | Other
Section of cable isolated and made safe. Repaired supply to VicRoads and reconnected once generator was removed. | 54 SILVESTER PARADE, ROXBURGH PARK VIC 3064 | A149014 | Copper theft | [5 empty] | 2 | VicRoads reported exposed wires in pit affecting traffic lights It was found that there had been a copper theft involving 16mm copper underground street light service cable on Aitken Blvd (between Silverster Blvd and Somerton Rd) | Services cable;Services pit (network);Copper | 0 | 0 | 0 |  | COO14 | Copper theft | Damage to network assets | 16/04/2020 5:47 |  |  | 15478 | Residential |  | 20200416JEM_02 | Infrastructure (network-based) | -37.6281 | 144.9138 | 1 | Jemena | Report | 19605 | 0.030499 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Roxburgh Park | Other
Attended site and assisted statutory agencies | LAURENS STREET, NORTH MELBOURNE VIC 3051 | 33111961 | [7 empty] | Citipower was advised of a fatality within the 100 Laurens st substation in North Melbourne. | Indoor | 0 | 0 | 0 |  | LS016 | under investigation | Electrocution | 16/04/2020 16:30 |  |  | 15486 | Other | network enclosure | 20200417PWA_01 | Infrastructure (network-based) | -37.8024 | 144.9418 | 1 | CitiPower | Notification | 19614 | 0.0082986 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Other
On arrival crew found tipper had hit contacted conductors, no damage found. | 1784 ELMORE-RAYWOOD ROAD, KAMAROOKA VIC 3570 | 33022609 | Working too close to overhead lines | [5 empty] | 1 | Civil contractor reported that he hit the lines with his tipper truck but the lines did not come down and were not damaged in anyway at incident location. On arrival the crew found that the incident had occurred between poles 4 & 5 . There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | EHK024 | Tip truck contacted swer conductors | No Go Zone (contact) | 17/04/2020 10:06 |  |  | 15489 | Agricultural |  | 20200420PWA_01 | Infrastructure (network-based) | -36.4861 | 144.3978 | 1 | Powercor | Report | 19620 | 0.0082928 | 12.7kV AC (SWER) | Bendigo Airport | 3570 | Kamarooka | Vehicle
On arrival crew isolated supply and carried out repairs. | 62 TOOLLEEN ANGLE ROAD, TOOLLEEN VIC 3551 | 32040538 | Crane, excavator or other construction/farming equipment | [6 empty] | Report from customer of pole fallen onto boom of machinery in paddock and wires sparking. Agricultural sprayer collided with pole. Knocked pole over and conductors were on sprayer. Occupant remained in vehicle until crew arrived and isolated supply No injuries, no fire, no third party damage apart from damage to vehicle. | SWER conductor;Pole (wood) | 2 | 2 | 2 |  | EHK031 | Sprayer tractor collided with pole | Damage to network assets | 19/04/2020 17:26 |  |  | 15492 | Agricultural |  | 20200420PWA_03 | Infrastructure (network-based) | -36.6924 | 144.6508 | 1 | Powercor | Report | 19623 | 0.038353 | 12.7kV AC (SWER) | Bendigo Airport | 3551 | Toolleen | Vehicle
HV BA Fuse Unit on red phase and all 3 x 15E BA Fuses have been replaced | 5 BLACKWELLS LANE, BULLA VIC 3428 | A123600 |  |  |  | Candled fuse |  |  | 1 | Network Operator observed HV Boric Acid fuse unit candling then flashing over air gap, resulting in fire at gas switch 058001 | Boric acid;Disconnector/isolator | 0 | 0 | 0 |  | COO11 | HV fuse candling | Other electricity related | 44169.1292 | 1 | Negligible: no ground fire | 15502 | Peri-urban |  | 20200422JEM_01 | Infrastructure (network-based) | -37.7514 | 144.9668 | 1 | Jemena | Report | 19635 | 0.015457 | 22kV AC | Essendon Airport | 3428 | Bulla | Fuse
Faults crew attended the site and reattached the bracket on the street light pole. | 648 SOUTH ROAD, MOORABBIN VIC 3189 | 8829576 |  |  |  | loose connection;Other |  |  | 1 | UE was advised that a street light bracket which has been dislodged in the wind, is dangling over the main road. | Public lighting | 0 | 0 | 0 |  | HT8 | the cause is likely to be a loose connection. | no consequence;Other | 44139.5903 |  |  | 15500 | Roadway |  | 20200422UTD_03 | Infrastructure (network-based) | -37.9377 | 145.0695 | 1 | United Energy Distribution | Report | 19632 | 0.019112 | Low voltage AC (<1kV) | Moorabbin Airport | 3189 | Moorabbin | AF Other
site made safe and ASR | 3494 WARBURTON HIGHWAY, WARBURTON VIC 3799 | 1407922 |  |  |  | Candled fuse |  |  |  | c CANDLED FUSE | Any other type | 0 | 0 | 0 |  | wyk13 | Animal Incident | Pole-top fire | 22/04/2020 5:36 | 1 | Negligible: no ground fire | 15503 |  |  | 20200423SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19641 | 0.027419 | 22kV AC | Moorabbin Airport | 3494 | Warburton | Fuse
On arrival crew isolated supply and carried out repairs. | 2-4 ELEVENTH STREET, MILDURA VIC 3500 | 32155128 |  |  |  | Leakage |  |  |  | CFA reported a pole fire at incident location. Crew found that the top position HV xarm had burnt allowing the white phase insulator to drop down on the lower HV conductors, CFA attended and put out the fire. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MDA024 | Excessive leakage current | Pole-top fire | 23/04/2020 18:57 | 1 | Negligible: no ground fire | 15506 |  |  | 20200424PWA_02 | Infrastructure (network-based) | -34.2061 | 142.177 | 1 | Powercor | Report | 19646 | 0.024133 | 22kV AC | Mildura Airport | 3500 | Mildura | Crossarm
Emergency Switching undertaken, Pole replaced | 7 MCMAHONS ROAD, FRANKSTON VIC 3199 | 3306626 |  |  |  | Electrical breakdown;Leakage |  |  | 2 | ESV report #13834428 Fire report #6965 - Confirmed fire start, Fire is on pole, about 3M down from top of pole. LIS 3306626 | Pole (wood) | 0 | 0 | 0 |  | FTS-FTN | Suspected cause maybe 66kV tracking as brown insulator appeared broken | Pole-top fire | 17/04/2020 16:58 | 1 | Negligible: no ground fire | 15516 | Roadway |  | 20200427UTD_01 | Infrastructure (network-based) | -38.152 | 145.1333 | 1 | United Energy Distribution | Report | 19658 | 0.0072431 | 66kV AC | Moorabbin Airport | 3199 | Frankston | AF Other
Tree Trimmed by faults crew | 8 BARRY COURT, SCORESBY VIC 3179 | 619620 |  | Within clearances |  |  |  |  | 2 | Customer reported fronds from Palm tree were intermittently sparking/burning when touching wiresâ€¦â€¦.Tree trimmed. LIS 0619620 | Conductor (bare) | 0 | 0 | 0 |  | BRA 21 | Vegetation: Trees Incident | Other vegetation | 43894.4972 | 1 | Negligible: no ground fire | 15518 | Residential |  | 20200427UTD_03 | Infrastructure (network-based) | -37.8925 | 145.232 | 1 | United Energy Distribution | Report | 19660 | 0.020684 | 22kV AC | Moorabbin Airport | 3179 | Scoresby | Trees
â€¢ Network Operator contacted the Jemena Control Room to report the NGZ breach â€˜near missâ€™ incident â€¢ Network Operator reported incident to Worksafe Hotline as advised by Jemena Work Practices â€¢ HV overhead lines isolated to make safe, earthing permit to work issued â€¢ Jemena Control Room Coordinator granted permission to commence switching to isolate section to make safe and retract the concrete pumping boom from NGZ Red Zone | 144 PASCOE VALE ROAD, MOONEE PONDS VIC 3039 | A113502 | Working too close to overhead lines | [5 empty] | 2 | â€¢ A Network Operator discovered a concrete pump boom erected and operating within the No Go Zone of HV overhead lines (within 3000mm) opposite 144 Pascoe Vale Road, Moonee Ponds â€¢ Network Operator requested the concrete pump operator to cease works, but he did not â€¢ Network Operator advised the operator of the NGZ requirements and the breach of the concrete pump boom to the overhead HV conductors â€¢ No Permit To Work (PTW) had been issued to contractor prior to the incident or requested by contractor â€¢ No customer impacted, no damage to assets, no injuries. | Conductor (bare) | 0 | 0 | 0 |  | NS15 | No Go Zone infringement | No Go Zone (no contact) | 28/04/2020 11:45 |  |  | 15526 | Roadway |  | 20200428JEM_01 | Infrastructure (network-based) | -37.7604 | 144.9262 | 1 | Jemena | Report | 19671 | 0.038451 | 11kV AC | Essendon Airport | 3039 | Moonee Ponds | Other
Fault crews attended the site to investigate. Upon inspection, it was identified that the service line was damaged. The site was isolated and made safe. The service was replaced. | 109 SOUTH ROAD, BRIGHTON VIC 3186 | 1805017 | Working too close to overhead lines | [5 empty] | 1 | UE was advised that there is construction work onsite and the demolition crew have knocked the incoming service wire last night which has disconnected at pole end. | Conductor (insulated) | 0 | 0 | 0 |  | MR13 | The person was working too close to the service line. | No Go Zone (contact) | 17/04/2020 7:15 |  |  | 15524 | Residential |  | 20200428UTD_03 | Infrastructure (network-based) | -37.9286 | 145.0005 | 1 | United Energy Distribution | Report | 19667 | 0.03394 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Other
supply isolated and fuse replaced | 520 BACCHUS MARSH ROAD, LARA VIC 3212 | 33044700 |  |  |  | Corrosion |  |  |  | Following on from supply outage crew found hung up burnt edo fuse . There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | FNS011 | hangup fuse | Pole-top fire | 31/10/2019 15:14 | 1 | Negligible: no ground fire | 15540 | Roadway |  | 20200501PWA_02 | Infrastructure (network-based) | -38.0375 | 144.3562 | 1 | Powercor | Report | 19687 | 0.013568 | 22kV AC | Avalon Airport | 3212 | Lara | Fuse
Sent crew to Investigate and rectify. | 2 WELLESLEY ROAD, RINGWOOD NORTH VIC 3134 | 1202885 |  | Blown branch/vegetation |  |  |  |  | 2 | tree branch fell on HV and LV conductors evidence of burning on branch while resting on conductors. Area was isolated and made safe. | Conductor (bare) | 0 | 0 | 0 |  | RWN34 | Vegetation: Trees Incident | Other vegetation | 43866.9944 | 0 | Negligible: no ground fire | 15542 | Residential |  | 20200504SPN_01 | Infrastructure (network-based) | -37.7809 | 145.2354 | 1 | AusNet Services Distribution | Report | 19933 | 0.019691 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3134 | Ringwood North | Trees
Crew arrived on site and conducted all tests Linesman identified aluminum tails in 50 amp FOLCB in which they replaced with copper tails Linesman identified a poor connection at pole junction box which affected properties #6,8,11&13. Supply was isolated and cables repaired and the junction box terminals were reconnect. Linesman did all VESI test at #6,11,13 LEI did VESI tests at #8. #6,8,11&13 back on supply | 8 MERINO AVENUE, DALLAS VIC 3047 | A013283 |  | Bird |  |  |  |  | 2 | Home owner who was engaged in replacing guttering to home received a slight tingle/shock from fascia boards in vicinity of POA. The Incident happened early morning with condensation present on the fascia. During the day the condensation was not present. No volts were recorded around the location of the POA. Possible cause of shock was webs inside FOLCB and condensation at POA. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified 1 volt. The home owner did not report any shocks in home nor dimming lights. NST tests past low neutral impedance of 0.3 recorded. | POA connection (customer side);Connection box;Other customer electrical equipment | 2 | 2 | 2 |  | BD10 | Spiderwebs in FOLCB and condensation at POA | Minor shock | 43956.4396 |  |  | 15549 | Residential |  | 20200505JEM_01 | Infrastructure (network-based) | -37.6701 | 144.9292 | 1 | Jemena | Report | 19704 | 0.013556 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Dallas | Installation
Crews sent to investigate and make safe | 13 CHURCHILL PARK DRIVE, ENDEAVOUR HILLS VIC 3802 | 5746429 |  |  |  | Moisture ingress;Electrical breakdown |  |  | 2 | Cust was walking his dog, who allegedly got a shock from water bubbling up near the base of a pole. | Cable | 0 | 0 | 0 |  | LYD14 | Faulty connection in pit, pit full of mud and water | Shock to livestock, pet or companion animal | 43986.7417 |  |  | 15559 | Residential |  | 20200507SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19721 | 0.013132 | Low voltage AC (<1kV) | Moorabbin Airport | 3802 | Endeavour Hills | Connection
On arrival crew arranged isolation of supply and carried out repairs | 2 Banyan St, Warrnambool VIC 3280, Australia | 30135617 |  |  |  | Unknown technical factor |  |  |  | Report received of pole fire at incident location. On arrival a crew found a Krone box on fire . THere was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | WBL008 | Insufficient remains to identify cause | Pole-top fire | 44170.7257 | 1 | Negligible: no ground fire | 15572 |  |  | 20200513PWA_02 | Infrastructure (network-based) | -38.3879 | 142.4838 | 1 | Powercor | Report | 19743 | 0.024098 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Looking at the photos, Jemena Compliance Officer Jason Ford advised Control Room to call ESV straight away and advise them of unsafe and illegal wiring and request their on call inspector attend. ESV notification 13911455 A Faults truck will attend to disconnect and make safe the installation and issue a defect notice. | 7 DOVER ROAD, WILLIAMSTOWN VIC 3016 | A059209 | Unauthorised access | [5 empty] | 2 | Anonymous person (via Mondo) reported illegal wiring to property around POA Bulilding site house getting rebuilt with original POA hanging there and wires going to meter. House has been gutted. No access (locked up) so can't access to check meter per the meter investigation report (attachment which contains photos) Possible compliance issues: POA been moved without Jemenaâ€™s involvement (possibly no CES issued) Cabling exposed to open air No meter box | POA connection (network side);Customer wiring | 0 | 0 | 0 |  | NT4 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 26/04/2020 9:43 |  |  | 15575 | Residential |  | 20200514JEM_01 | Infrastructure (network-based) | -37.8566 | 144.8995 | 1 | Jemena | Report | 19749 | 0.04147 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown | Other
Crews sent out tominvestigate, repair and make safe. | 210 OHERNS ROAD, EPPING VIC 3076 | TBA | Working too close to underground cables | [6 empty] | contractor using excavator dug up u/g cable | Cable | 0 | 0 | 0 |  | TBA | under investigation | No Go Zone (contact) | 14/05/2020 8:35 |  |  | 15577 | Roadway |  | 20200514SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19751 | 0.0025683 | Low voltage AC (<1kV) | Moorabbin Airport | 3076 | Epping | Dug up
On arrival crew isolated supply and carried out repairs. | 81 Haires Ln, Bullengarook VIC 3437, Australia | 32043236 | Working too close to overhead lines | [6 empty] | Following GSB11 feeder going to lockout a report was received of a customer removing trees has fallen a tree across conductors at the incident location. On arrival the crew found a customer was engaged in tree clearing and has fallen a tree across the line bring a conductor to ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GSB011 | Vegetation: Trees Incident | No Go Zone (contact);Damage to network assets | 25/04/2020 15:09 |  |  | 15583 | Agricultural |  | 20200515PWA_03 | Infrastructure (network-based) | -37.495 | 144.5172 | 1 | Powercor | Report | 19760 | 0.013358 | 22kV AC | Melbourne Airport | 3437 | Bullengarook | Other
supply isolated pole replaced | Springvale Rd, Cooma VIC 3616, Australia | 30566780 |  |  |  | Leakage |  |  |  | Customer advised Pole on Fire corner of Midland Highway and Springvale rd, Shepparton. Wires across the road. Emergency services have been called . On arrival crew found the top had been burnt off the pole. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 0 | 0 | 0 |  | SHP014 | Excessive leakage current | Pole-top fire | 26/11/2019 7:49 | 1 | Negligible: no ground fire | 15587 | Roadway |  | 20200515PWA_06 | Infrastructure (network-based) | -36.428 | 145.1137 | 1 | Powercor | Report | 19764 | 0.021507 | 22kV AC | Shepparton Airport | 3616 | Cooma | Pole
crew attended crossarm replaced | 507 LAKE ROAD, WOORINEN VIC 3589 | 50033988 |  |  |  | Leakage |  |  |  | Pole fire at incident location | Crossarm (wood) | 0 | 0 | 0 |  | SHL004 | leakage current | Pole-top fire | 43477.7542 | 1 | Negligible: no ground fire | 15589 | Roadway |  | 20200515PWA_08 | Infrastructure (network-based) | -35.2818 | 143.4548 | 1 | Powercor | Report | 19766 | 0.039362 | 22kV AC | Swan Hill Aerodrome | 3589 | Woorinen | Crossarm
crew attended cross-arm replaced | 4 MILLEWA ROAD, WERRIMULL VIC 3496 | 30567057 |  |  |  | Leakage |  |  |  | Powercor received a report of a Pole fire at LIS 215, Just off Millewa Rd. | Crossarm (wood) | 0 | 0 | 0 |  | RCT023 | Leakage current | Pole-top fire | 43508.65 | 1 | Negligible: no ground fire | 15591 | Roadway |  | 20200515PWA_10 | Infrastructure (network-based) | -34.3807 | 141.6552 | 0 | Powercor | Report | 19768 | 0.03125 | 22kV AC | Mildura Airport | 3496 | Werrimull | Crossarm
Crew attended and replaced service | 804 TALBOT STREET S, REDAN VIC 3350 | 31001148 |  |  |  | Corrosion |  |  |  | Service on the ground neutral screen service had burnt to the ground leaving some burns on some customer grass. | Service cable (insulated) | 0 | 0 | 0 |  | BAS012 | apparent corrosion | Grassfire | 20/12/2019 15:27 | 1 | Localised: less than 10 sq.m | 15595 | Roadway |  | 20200518PWA_02 | Infrastructure (network-based) | -37.5776 | 143.8396 | 1 | Powercor | Report | 19772 | 0.026145 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Redan | OH Cable
SWER ACR RB7329 was opened by NCC to enable fuse change on the 22kV side of ACR. Fuse and barrel replaced | 164 CAPE SCHANCK ROAD, CAPE SCHANCK VIC 3939 | 1312552 |  |  |  | Fuse failed to eject |  |  | 0 | Crew replaced 10A EDO fuse at CAPE SCHANCK -ISO S/S B phase. Fuse had candled on the 22kV incoming. - fire report #6832, no ground fire. - ESV ref 13971860. LIS 1312552 | EDO fuse | 0 | 0 | 0 |  | RBD21 | Candled fuse | Plant/equipment | 13/05/2020 15:48 | 1 | Negligible: no ground fire | 15598 | Agricultural |  | 20200518UTD_01 | Infrastructure (network-based) | -38.4724 | 144.8947 | 1 | United Energy Distribution | Report | 19775 | 0.020949 | 22kV AC | Moorabbin Airport | 3939 | Cape Schanck | Fuse
Crews attended, isolated the supply and performed repairs. | 189 Imries Ln, Illabarook VIC 3351, Australia | 33000427 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer called to report that her husband had contacted a power line with his truck. On arrival the crew found that the farmer Neil Rizzola was using his tipper truck o dump his load just inside the gate of his property and pulled the truck forward contacting the bare LV OH conductor running along the road easement. The active conductor remained draped over the truck, and Mr Rizzola remained in the vehicle until crews isolated the supply. There were no injuries, and there was no third party damage. | Conductor (bare) | 2 | 2 | 2 |  | BAS021 | Tipper drove into conductors | No Go Zone (contact) | 18/05/2020 11:17 |  |  | 15614 | Roadway |  | 20200519PWA_02 | Infrastructure (network-based) | -37.8394 | 143.6509 | 1 | Powercor | Report | 19800 | 0.018972 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Illabarook | Vehicle
Crew and inspector sent to site to investergate and repair | 298 EDGARS ROAD, LALOR VIC 3075 | 909429 |  |  |  | Electrical breakdown;Mechanical breakdown |  |  | 2 | Customer reported power point/ appliance damage. Fault truck and Inspector sent to investigate | Pole mounted | 0 | 0 | 0 |  | TT9 | property damage on the LV, 240V, bare conductor, neutral burnt off at TX, LIS 909429 | Pole-top fire;Damage to network assets | 18/05/2020 19:42 | 0 | Negligible: no ground fire | 15610 | Residential |  | 20200519SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19794 | 0.036992 | Low voltage AC (<1kV) | Moorabbin Airport | 3075 | Lalor | Conductor
Crew attended and replaced fuse carrier | 1255 COCAMBA ROAD, OUYEN VIC 3490 | 32147058 |  |  |  | Fuse failed to eject |  |  |  | customer reported fuse down One arrival crew found EDO tube had burnt in half | EDO fuse | 0 | 0 | 0 |  | OYN005 | Fuse mal-operation | Pole-top fire | 21/02/2020 10:35 | 1 | Negligible: no ground fire | 15621 | Agricultural |  | 20200520PWA_03 | Infrastructure (network-based) | -35.1082 | 142.4872 | 1 | Powercor | Report | 19808 | 0.023329 | 12.7kV AC (SWER) | Mildura Airport | 3490 | Ouyen | Fuse
crew attended and replaced cross-arm | 228 JOHNS WAY, RED CLIFFS VIC 3496 | 32152209 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location. | Crossarm (wood) | 0 | 0 | 0 |  | RCT014 | excessive leakage | Pole-top fire | 43924.6326 | 1 | Negligible: no ground fire | 15623 | Roadway |  | 20200520PWA_05 | Infrastructure (network-based) | -34.353 | 142.2835 | 1 | Powercor | Report | 19810 | 0.0075718 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Transformer replaced | 215 HOBSON ROAD, NYAH WEST VIC 3595 | 33069006 |  | Lightning | [5 empty] | Report received of a transformer struck by lighting. Transformer was on fire, now smoking | Transformer | 0 | 0 | 0 |  | SHL002 | Lightning struck substation | Pole-top fire | 44078.3354 | 1 | Negligible: no ground fire | 15630 | Roadway |  | 20200520PWA_12 | Infrastructure (network-based) | -35.2041 | 143.3632 | 1 | Powercor | Report | 19817 | 0.017578 | 22kV AC | Swan Hill Aerodrome | 3595 | Nyah West | Lightning
On arrival crew isolated supply and carried out repairs. LEI called to asses damage at 64 Tom Johns Rd | 39 Tom Jones Rd, Ross Creek VIC 3351, Australia | 33001323 |  | Lightning | [5 empty] | Following fault calls a crew attended the incident location. On arrival crew found a substation pole had been struck by lightning. There was some transformer damage. Suspected HVI at one premises. There was no fire or reported injuries. | Pole mounted | 2 | 2 | 2 |  | BAS021 | Lightning strike | HV injection | 20/05/2020 10:26 |  |  | 15635 | Roadway |  | 20200521PWA_02 | Infrastructure (network-based) | -37.6242 | 143.7993 | 1 | Powercor | Report | 19823 | 0.032853 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3351 | Ross Creek | Lightning
A Faults truck attended site to disconnect and remove supply and issue a defect notice | 24 OVENS STREET, YARRAVILLE VIC 3013 | A052822 | Unauthorised access | [5 empty] | 2 | Report of illegal wiring around the POA and unauthorised tampering with POA at a house construction site Very similar to the incident 20200514JEM_01 @ 7 Dover Road, Williamstown | POA connection (network side);Customer wiring | 0 | 0 | 0 |  | YVE24 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44017.525 |  |  | 15640 | Construction |  | 20200522JEM_02 | Infrastructure (network-based) | -37.8182 | 144.8922 | 1 | Jemena | Report | 19828 | 0.019164 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Other
On arrival crew isolated supply and carried out repairs | 8 CRAVEN STREET, PRAHRAN VIC 3181 | 30169029 |  |  |  | Corrosion |  |  |  | Report received of pole fire at incident location. On arrival crew found a LV bridge had overheated and insulation had caught fire. There was no ground fire, no reported injuries or third party property damage. | Dropper/bridge | 2 | 2 | 2 |  | B C013 | Overheated connection | Pole-top fire | 21/05/2020 18:40 | 1 | Negligible: no ground fire | 15636 | Roadway |  | 20200522PWA_01 | Infrastructure (network-based) | -37.8557 | 145.0029 | 1 | CitiPower | Report | 19824 | 0.0064826 | Low voltage AC (<1kV) | Moorabbin Airport | 3181 | Prahran | Connection
Crew attanded and arranged repairs | 249 Princes Hwy, Bolwarra VIC 3305, Australia | 31033424 |  |  |  | Leakage |  |  |  | A tree clearing crew reported that a PTA (pole top assembly) had burnt off the pole at the incident location, P519X KRT-PLD No2 R. On arrival the crew found that a bridging insulator had caused a section of the top of the pole to be burnt There was no ground fire, and no other reported damage or injuries. | Pole (wood) | 2 | 2 | 2 |  | PLD001 | Excessive l;leakage current | Pole-top fire | 22/05/2020 16:10 | 1 | Negligible: no ground fire | 15644 | Roadway |  | 20200525PWA_02 | Infrastructure (network-based) | -38.2813 | 141.6155 | 1 | Powercor | Report | 19833 | 0.0020127 | 22kV AC | Portland (Cashmore Airport) | 3305 | Bolwarra | Pole
On arrival crew isolated circuit and arranged repairs. | 1-17 FLINDERS STREET, MELBOURNE VIC 3000 | 30278959 | Working too close to underground cables | [6 empty] | Employee working on behalf of Citywide advised he has cut an u/g LV cable (believes to street light) in Wellington Pde just btw Spring st & Lansdowne St near the tram stop. On arrival crew found that while reconstructing footpath and concrete crossovers a LV cable (public lighting) had been damaged by an excavator. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MP062 | Cable damaged by excavator | No Go Zone (contact) | 17/05/2020 22:15 |  |  | 15655 | Roadway |  | 20200526PWA_01 | Infrastructure (network-based) | -37.8156 | 144.9743 | 1 | CitiPower | Report | 19846 | 0.015654 | Low voltage AC (<1kV) | Essendon Airport | 3000 | Melbourne | Dug up
Supply isolated and repairs undertaken to LV conductor. | 7 ST ALBANS ROAD, ST ALBANS VIC 3021 | 30117559 |  |  |  | Overheated connection |  |  |  | While preforming maintenance work in the St Albans area a work crew were required to create an LV parallel between two adjancent substations. After completing this task the work crew was informed of a possible fault in the area. A crew attended the scene and found a white phase conductor had fallen to the ground. The MFB were onsite and scene managed. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | SSE031 | Connection degradation | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/05/2020 13:31 |  |  | 15659 | Roadway |  | 20200527PWA_01 | Infrastructure (network-based) | -37.7469 | 144.8021 | 1 | Powercor | Report | 19851 | 0.040965 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | St Albans | Connection
Crew attended, isolated the supply and performed repairs. | 1 Rowe St, Hamlyn Heights VIC 3215, Australia | 32069696 |  |  |  | Corrosion |  |  |  | A customer and Vicfire both reported a fire on a pole at the incident location. On arrival the crew found that an LV FSD isolator had overheated and caught fire. There was no ground fire, other damage or injuries reported. | Disconnector/isolator | 2 | 2 | 2 |  | GL013 | Overheated connection | Pole-top fire | 26/05/2020 18:03 | 1 | Negligible: no ground fire | 15661 | Roadway |  | 20200527PWA_03 | Infrastructure (network-based) | -38.1149 | 144.3224 | 1 | Powercor | Report | 19853 | 0.035662 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Hamlyn Heights | Connection
On arrival crew isolated supply and carried out repairs | 467 Paynes Rd, Rockbank VIC 3335, Australia | 33076291 |  | Lightning | [5 empty] | MFB reported a pole fire at incident location. On arrival crew found a transformer had failed and caught fire briefly. There was no ground fire, no reported injuries or third party property damage.. | Pole mounted | 2 | 1 | 2 |  | MLN021 | Transformer failure | Pole-top fire | 29/05/2020 19:34 | 1 | Negligible: no ground fire | 15675 | Agricultural |  | 20200602PWA_01 | Infrastructure (network-based) | -37.7396 | 144.6395 | 1 | Powercor | Report | 19873 | 0.0051968 | 22kV AC | Laverton Raaf | 3335 | Rockbank | AF Other
At LIS 1000617, a tree brought down HV conductor which resulted in a 0.5m x 0.5m ground fire which also affected Telstra cable. HV conductor was live on the ground when fault crew arrived on site. De-energised remotely and made safe. Crew made safe and repaired HV conductor and re energised. | 4 NORTH AVENUE, MOUNT EVELYN VIC 3796 | 1000617 |  | Fallen |  |  |  |  | 0 | A tree brought down HV conductor which resulted in a 0.5m x 0.5m ground fire which also affected Telstra cable. | Conductor (bare) | 0 | 0 | 0 |  | LDL21 | Vegetation: Trees Incident | Grassfire | 43836.8569 | 1 | Negligible: no ground fire | 15679 | Residential |  | 20200602SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19880 | 0.0090127 | 22kV AC | Moorabbin Airport | 3796 | Mount Evelyn | Trees
Jemena sent a faults truck to disconnect the overhead service, quarantine the meter and take photographic evidence | 4 ROCKE STREET, IVANHOE VIC 3079 | A110393 | Unauthorised access | [5 empty] | 0 | We currently have Meter 138391 linked to NMI 6001030676 at address 42 LOCH STREET / COBURG. Meter was remotely De-Energised on 12.07.2018. It is suspected that a third party has illegally removed Jemena's meter from 42 LOCH STREET / COBURG and installed it at the new location of 4 ROCKE STREET / IVANHOE without any involvement from Jemena. The meter is at 4 ROCKE STREET / IVANHOE is confirmed to be a BTS meter. We have no records of a New Connection for this location. This issue was first brought to our attention when we started receiving New Connection requests for units at this location. We had never received an Abolishment request for the site. We requested an Abolishment to be raised so we could remove the meter, but the customer was adamant no meter was on site. UIQ had the meter as communicating, and doing a device location search we identified it was communicating around 4 ROCKE STREET / IVANHOE (as we could tell the meter was not at the property, we allowed the new connections to continue while we investigated this meter further). | Smart meter;Temporary supply pole | 0 | 0 | 0 |  | HB15 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/05/2020 8:26 |  |  | 15683 | Residential |  | 20200603JEM_03 | Infrastructure (network-based) | -37.7723 | 145.0398 | 0 | Jemena | Report | 19887 | 0.01414 | Low voltage AC (<1kV) | Essendon Airport | 3079 | Ivanhoe | Other
Replaced single phase service, tested and left on supply | 8 LYTTLE AVENUE, ESSENDON VIC 3040 | A111668 | Working too close to overhead lines | [5 empty] | 2 | Customer at 8 Lyttle Avenue had service line damaged by excavator working next door on building construction The overhead service line broke at the breakaway device and fell to ground No electric shocks were received. Construction firm: Collinder Electrics. Email: info@collinder.com.au Excavator driver details: Brad Collinder 0437024429 | Conductor (ABC);Service cable (insulated) | 0 | 0 | 0 |  | NS08 | No Go Zone breach | No Go Zone (contact) | 43927.6424 |  |  | 15688 | Residential |  | 20200604JEM_02 | Infrastructure (network-based) | -37.7479 | 144.9277 | 1 | Jemena | Report | 19958 | 0.030181 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Vehicle
Cable repaired and returned to service. | 663-697 NEALE ROAD, DEANSIDE VIC 3336 | 30562785 | Working too close to underground cables | [6 empty] | During road works a contractor has disturbed an underground cable. Cable does not appear to be damaged but conduit has been pulled out of the ground. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | MLN021 | Excavation work | No Go Zone (contact);Damage to network assets | 28/05/2020 15:48 |  |  | 15697 | Roadway |  | 20200605PWA_02 | Infrastructure (network-based) | -37.7409 | 144.7007 | 1 | Powercor | Report | 19904 | 8.4491e-05 | Low voltage AC (<1kV) | Laverton Raaf | 3336 | Deanside | Dug up
Sent crew and inspector to investigate and make safe | 27 STEPHENSON STREET, SALE VIC 3850 | 0 |  |  |  | Electrical breakdown |  |  | 0 | Customer states recieving shocks from shower taps | Pole mounted | 0 | 0 | 0 |  | SLE11 | Transformer was found to be faulty and was replaced | Minor shock | 23/04/2020 10:52 |  |  | 15701 | Residential |  | 20200605SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19911 | 0.003441 | Low voltage AC (<1kV) | Moorabbin Airport | 3850 | Sale | AF Other
Jemena work party replaced service supplying #49 Hales Crescent, Broadmeadows | 49 HALES CRESCENT, JACANA VIC 3047 | A072721 | Working too close to overhead lines | [5 empty] | 2 | Jemena received advice from customer of All Supply Failure. Crew found service line supplying customer at #49 was pulled down by third party excavator working at #51 There was no request to attend this address to conduct a No Go Zone assessment or inspection, and therefore there was no Permit to Work (PTW) issued by Jemena for the work Responsible third party is RNB CONSTRUCTION PTY LTD ABN: 58612443893, Truck Registration 1JY 7XR | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | BMS23 | No Go Zone breach | No Go Zone (contact) | 44110.4521 |  |  | 15707 | Residential |  | 20200610JEM_01 | Infrastructure (network-based) | -37.686 | 144.9144 | 1 | Jemena | Report | 19921 | 0.031639 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Jacana | Vehicle
Faults Crew attended. Damaged sections isolated, supply restored to unaffected customers. Approximately 100 customers will remain off for whilst further repairs take place. | 2 KANOWNA STREET, WILLIAMSTOWN VIC 3016 | A060025 | Working too close to overhead lines | [5 empty] | 1 | A non-Jemena mobile crane truck has made contact with HV and LV overhead lines in Kanowna St, 2 poles north of Cecil St, resulting conductor damage. LV neutral conductor is on the ground causing a secondary fault at HV GAC Sw#11730 where the Centre phase HV conductor has also fallen to the ground. 2,534 Customers interrupted. No Permit to Work had been issued by Jemena. | Conductor (bare) | 0 | 0 | 0 |  | NT15 | No Go Zone breach | No Go Zone (contact) | 43896.5986 |  |  | 15711 | Construction |  | 20200610JEM_03 | Infrastructure (network-based) | -37.866 | 144.9095 | 1 | Jemena | Report | 19926 | 0.032318 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3016 | Williamstown | Vehicle
Despatched crew and inspector to investigate and rectify | 5 SUGAR GUM COURT, UPPER FERNTREE GULLY VIC 3156 | 1317737 |  |  |  | Electrical overload |  | Neutral to earth | 2 | Electric shock from shower taps | Pole mounted | 0 | 1 | 0 |  | fgy23 | a voltage supply issue caused by substation overloading or voltage drop in the reticulation due to cable sizing and or length. | Minor shock | 43867.559 |  |  | 15709 | Residential |  | 20200610SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19924 | 0.012308 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Upper Ferntree Gully | AF Other
Pole being replaced under access permit Formal incident investigation is being undertaken | 9-11 OLD HEIDELBERG ROAD, ALPHINGTON VIC 3078 | A133669 |  |  |  | Rot |  |  | 2 | While switching programmed works LV/HV Pole snapped at base and fell over. It appears that it was an unassisted in-service pole failure and the pole had failed due to rot. | Pole (wood) | 0 | 0 | 0 |  | HB15 | Under investigation | Damage to network assets | 24/05/2020 16:29 |  |  | 15726 | Roadway |  | 20200611JEM_03 | Infrastructure (network-based) | -37.7791 | 145.0359 | 1 | Jemena | Report | 19947 | 0.0074213 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3078 | Alphington | Pole
On arrival crew isolated carried out repairs | 490 Davis Rd, Tarneit VIC 3029, Australia | 30306909 | Working too close to underground cables | [6 empty] | Report received of excavator digging up cable. On arrival crew found that an excavator had exposed and broken a HV earth wire at incident location. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Earth/earthing | 2 | 2 | 2 |  | TNA023 | Excavation work | Damage to network assets | 28/05/2020 12:37 |  |  | 15714 | Roadway |  | 20200611PWA_01 | Infrastructure (network-based) | -37.8227 | 144.6555 | 1 | Powercor | Report | 19929 | 0.036639 | Earthing cable | Laverton Raaf | 3029 | Tarneit | Dug up
On arrival crew isolated supply and carried out repairs. | 180 Flinders Ave, Lara VIC 3212, Australia | 30076324 | Working too close to underground cables | [6 empty] | A contractor reported that his excavator has hit underground cable at the incident location. Upon arrival, a Powercor crew found that the UG service and the conduit had been damaged. There were no injuries or fire. | Services cable | 2 | 2 | 2 |  | FNS022 | Excavation operating on nature reserve | No Go Zone (contact);Damage to network assets | 43867.3542 |  |  | 15721 | Roadway |  | 20200611PWA_04 | Infrastructure (network-based) | -38.0121 | 144.4146 | 1 | Powercor | Report | 19940 | 0.0087303 | Low voltage AC (<1kV) | Avalon Airport | 3212 | Lara | Dug up
Crews attended, isolated the supply and performed repairs. | 11 Jasper Ave, Barwon Heads VIC 3227, Australia | 30072968 |  |  |  | Corrosion |  |  |  | Vicfire called to report a pole fire at the incident location. On arrival the crew found that the red phase connection of an FSD Krone box on the substation pole had overheated and burnt out. There was no ground fire or any reported injuries or other damage. | Connection box | 2 | 2 | 2 |  | GLE013 | Overheated connection | Pole-top fire | 44171.2694 | 1 | Negligible: no ground fire | 15728 | Roadway |  | 20200612PWA_02 | Infrastructure (network-based) | -38.2774 | 144.4898 | 1 | Powercor | Report | 19949 | 0.0008669 | Low voltage AC (<1kV) | Avalon Airport | 3227 | Barwon Heads | Connection
On arrival crew isolated supply and carried out repairs. | 119 Lowan Ave, Red Cliffs VIC 3496, Australia | 32152450 | Vehicle | [6 empty] | CFA reported low wires at the incident location. Upon arrival crew discovered ( from Police in attendance ) that vehicle had brought down 2 poles in an alleged self harm attempt, driver of the late model Nissan Navara first stuck wood pole Millewa 25 breaking it off at ground level, driver then proceeded to drive at concrete pole 23 Millewa, also resulting in pole failure due to impact, RCT023 feeder supply remained uninterrupted, however conductors over Milewa Rd ( wood pole LIS 32113 ) were approximately 5.0M, and 2.0M above a vineyard in proximity to concrete pole ( LIS 777275 ). There was no fire. | Pole (concrete) | 2 | 2 | 2 |  | RCT023 | Vehicle struck poles | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43988.3986 |  |  | 15730 | Roadway |  | 20200612PWA_04 | Infrastructure (network-based) | -34.3289 | 142.1616 | 1 | Powercor | Report | 19951 | 0.034571 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Vehicle
Sent crew to Investigate and repair | 342 OLD CALLIGNEE ROAD, CALLIGNEE VIC 3844 | 2605584 |  | Animal |  |  |  |  | 0 | Report of Candling Fuse | EDO fuse | 0 | 0 | 0 |  | TGN23 | Animal Incident | Pole-top fire | 13/06/2020 22:47 | 0 | Negligible: no ground fire | 15733 | Agricultural |  | 20200615SPN_03 | Infrastructure (network-based) | -38.331 | 146.5799 | 1 | AusNet Services Distribution | Report | 19956 | 0.039215 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Callignee | Fuse
Jemena inspected assets and reported minor damage to LV mains, other damage from other historical clashing. All Ok, every body on supply, trees clear | 4 WILLOW COURT, BELLFIELD VIC 3081 | A096401 | Working too close to overhead lines | Council |  |  |  | Phase to phase | 2 | Active Tree Services (ATS) tree clearer working for Banyule City Council caused LV mains to clash in the process of tree clearing ATS HSEQ Adviser (Andrew Searles) provided the key parts of the incident as follows: â€¢ The crew prepared to cut the tree outside 4 Willow Court, there was a parked car near the tree â€¢ The crew knocked on the door of property but there was no answer and so they could not get the car moved â€¢ The crew assessed they could still cut the tree and so setup the EWP and the site â€¢ Trevor the EWP operator started to cut the tree on the footpath side so that he could work back toward the road, that way he could control all of the foliage away from the parked car â€¢ Trevor decided to step cut a branch so that he could control it and avoid the car, he snapped off the step cut branch â€¢ When he snapped off the branch the whole tree shook â€¢ A branch that was closer to the middle of the tree was above the powerlines, this pushed one phase into the other phase causing a clash | Conductor (bare) | 0 | 0 | 0 |  | EP34 | No Go Zone breach | No Go Zone (contact) | 17/06/2020 9:54 |  |  | 15753 | Residential |  | 20200617JEM_01 | Infrastructure (network-based) | -37.7518 | 145.0342 | 1 | Jemena | Report | 19983 | 0.038332 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Bellfield
Crew isolated, replaced pole and made repairs | 33 Waitara Grove, Norlane VIC 3214, Australia | 30065788 | Vehicle | [6 empty] | CFA advised car hit pole and conductors sparking. On arrival crew found pole broken at base but still upright. 1 phase of the LV conductor had broken and was alive on the ground. Other phases were alive and hung up in a tree. Multiple LV services were ripped from the fascia of houses and on the ground also. There was no fire or reported injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | CRO022 | Car hit pole | Damage to network assets | 14/06/2020 21:10 |  |  | 15752 | Roadway |  | 20200617PWA_02 | Infrastructure (network-based) | -38.095 | 144.3479 | 1 | Powercor | Report | 19982 | 0.033022 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Norlane | Vehicle
On arrival crew isolated supply and carried out repairs. | 3538 FOXHOW-BERRYBANK ROAD, BERRYBANK VIC 3323 | 30049762 |  |  |  | Leakage |  |  |  | GRAINCORP OPERATIONS reported pole on fire and wire down. Crew found a damaged pole due to a pole fire, needs to be replaced, There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | CDN004 | Excessive leakage current | Pole-top fire | 17/06/2020 8:43 | 1 | Negligible: no ground fire | 15754 | Public space |  | 20200618PWA_01 | Infrastructure (network-based) | -37.9834 | 143.4908 | 1 | Powercor | Report | 19984 | 0.023174 | 22kV AC | Ballarat Aerodrome | 3538 | Berrybank | Pole
Site made safe and pole-mounted transformer replaced | 561 KEILOR ROAD, NIDDRIE VIC 3042 | A057021 |  |  |  | Leakage |  |  | 1 | Pole top fire resulting in pole burnt halfway down, pole top at 90 degrees to normal and damage to pole-mounted transformer Photos are unavailable for this incident | Conductor (bare);Transformer | 0 | 0 | 0 |  | AW07 | Earth leakage | Pole-top fire | 31/12/2019 6:44 | 1 | Negligible: no ground fire | 14750 | Industrial |  | 20200103JEM_05 | Infrastructure (network-based) | -37.7331 | 144.8809 | 1 | Jemena | Report | 18616 | 0.014225 | Low voltage AC (<1kV);22kV AC | Essendon Airport | 3042 | Niddrie | Pole
Site made safe and replaced HV crossarm | 13 SAGES ROAD, GLENROY VIC 3046 | A035908 |  |  |  | Leakage |  |  | 1 | HV crossarm fire due to earth leakage | Crossarm (wood) | 0 | 0 | 0 |  | CN04 | Earth leakage | Pole-top fire | 31/12/2019 5:11 | 1 | Negligible: no ground fire | 14751 | Residential |  | 20200103JEM_06 | Infrastructure (network-based) | -37.7029 | 144.9588 | 1 | Jemena | Report | 18617 | 0.02242 | 22kV AC | Essendon Airport | 3046 | Glenroy | Crossarm
On arrival crew isolated supply and carried out repairs | 68 BERKSHIRE ROAD, SUNSHINE NORTH VIC 3020 | 30102782 |  |  |  | Leakage |  |  |  | Report received of pole fire at incident location. Crew advised a HV tee off crossarm has broken due to a pole fire. The conductors have come to rest across parked trucks at the premises There was no ground fire or reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | SSE032 | Excessive leakage current | Pole-top fire | 31/12/2019 7:12 | 1 | Negligible: no ground fire | 14739 | Commercial |  | 20200103PWA_01 | Infrastructure (network-based) | -37.7645 | 144.8397 | 1 | Powercor | Report | 18605 | 0.039598 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Crossarm
On arrival crew isolated supply and commenced repairs. LEI despatched to test for HVI | 546 MORELAND ROAD, BRUNSWICK WEST VIC 3055 | 30157029 |  |  |  | Leakage |  |  |  | Report recieved of a crossarm fire at incident location. On arrival crew found HV crossarm burnt through causing conductors to clash. There was reports of HVI at several premises There was no ground fire or injuries. | Crossarm (wood) | 2 | 2 | 2 |  | NS010 | Excessive leakage current | Pole-top fire;HV injection | 31/12/2019 6:54 | 1 | Negligible: no ground fire | 14740 | Roadway |  | 20200103PWA_02 | Infrastructure (network-based) | -37.752 | 144.9348 | 1 | CitiPower | Report | 18606 | 0.020431 | Low voltage AC (<1kV);11kV AC | Essendon Airport | 3055 | Brunswick West | Crossarm
On arrival crew isolated supply and carried out repairs. LEI despatched to check premises for HVI | 69 Cawood Dr, Sunshine West VIC 3020, Australia | 31023754 |  |  |  | Leakage |  |  |  | Crew reported pole fire at incident location. A high voltage isolator has broken off due to a crossarm fire and is now resting on the LV conductors below. There is reports of HVI There was no ground fire or reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | SSE033 | Excessive leakage current | Pole-top fire;HV injection | 31/12/2019 4:17 | 1 | Negligible: no ground fire | 14741 | Roadway |  | 20200103PWA_03 | Infrastructure (network-based) | -37.8006 | 144.8109 | 1 | Powercor | Report | 18607 | 0.012063 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3020 | Sunshine West | Crossarm
new covers and new Las installed | 3 NEFERTITI COURT, TRARALGON VIC 3844 | 2605832 |  |  |  | Electrical breakdown |  |  | 1 | CFA reported wire down and possible grass fire - crew attended and found surge arrestors burnt out - Raychem cover dropped to ground - small grass fire in the area | Surge diverter | 0 | 0 | 0 |  | TGN31 | The cause of the incident was a loose connection on the cable head. | Grassfire | 25/12/2019 23:00 | 1 | Localised: less than 10 sq.m | 14767 | Residential |  | 20200106SPN_01 | Infrastructure (network-based) | -38.1884 | 146.5601 | 1 | AusNet Services Distribution | Report | 18637 | 0.035387 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Connection
crew dispatched to investigate and make safe | Monash way cnr Porters rd Morwell | 2626406 | [7 empty] | Burnt bridge. Fire found at base of pole. | Dropper/bridge | 0 | 0 | 0 |  | mwl24 | TBA | Grassfire | 27/12/2019 14:30 | 1 | Localised: less than 10 sq.m | 14770 |  |  | 20200106SPN_03 | Infrastructure (network-based) | -38.2543 | 146.4235 | 1 | AusNet Services Distribution | Notification | 18641 | 0.011898 | 22kV AC | Morwell (Latrobe Valley Airport) |  |  | AF Other
crew investigated and made safe. | 4 ARTHURS CREEK ROAD, HURSTBRIDGE VIC 3099 | 925795 |  | Animal | [5 empty] | Dead Possum found near ACR-GB021. Grass fire found at base pole. | Circuit breaker | 0 | 0 | 0 |  | drn23 | Animal Incident | Grassfire | 31/12/2019 1:02 | 1 | Localised: less than 10 sq.m | 14771 | Commercial |  | 20200106SPN_04 | Infrastructure (network-based) | -37.6374 | 145.1939 | 1 | AusNet Services Distribution | Report | 18645 | 0.00044097 | 22kV AC | Essendon Airport | 3099 | Hurstbridge | Animal
Crew isolated supply and carried out repairs | 130 CORNISH ROAD, ARDMONA VIC 3629 | 33092737 |  | Bird | [5 empty] | CFA reported grass fire around our assets in road reserve. On arrival crew found a fire approx. 80m x 15m along road reserve. Crew identified possible bird flashover and a bridge burnt through. Crew found bird at base of pole. There was a small grass fire, no reported injuries, minor damage to a fence. | Conductor (bare);Dropper/bridge | 2 | 2 | 2 |  | MNA014 | Bird Incident | Grassfire | 43862.7451 | 1 | Medium: 1000 sq.m - 10 ha | 14780 | Roadway |  | 20200107PWA_03 | Infrastructure (network-based) | -36.3632 | 145.3261 | 1 | Powercor | Report | 18657 | 0.015003 | 22kV AC | Shepparton Airport | 3629 | Ardmona | Animal
On arival crew isolated supply and carried out repairs | 80 Gray St, Swan Hill VIC 3585, Australia | 33070600 |  |  |  | Corrosion |  |  |  | Vic Fire reported ground fire at base of pole at above address. When crew arrived, they found that a cable between pole transformer and isolator had melted. Molten material had ignited the grass below. There was no injuries or third party property damage. | Disconnector/isolator;Connector/termination | 2 | 2 | 2 |  | SHL007 | Overheated connection | Grassfire | 43862.8014 | 1 | Small: 10 - 1000 sq.m | 14784 | Roadway |  | 20200107PWA_04 | Infrastructure (network-based) | -35.3466 | 143.5472 | 1 | Powercor | Report | 18663 | 0.010169 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3585 | Swan Hill | Connection
LEI attended site and checked 3 of 4 residences and no evidence of damage. 4th premises was unoccupied but no damage found at switchboard. LEI left appropriate note for owners of property and left them off supply. Crew isolated supply and carried out repairs | 67 Ellandee Cres, Macedon VIC 3440, Australia | 32050356 |  |  |  | Leakage |  |  |  | Crew reported possible HVI from burnt cross-arm. Cross arm had burnt through on one side and HV conductor had landed on red phase of LV. There was no ground fire or reported injuries. | Conductor (bare);Crossarm (wood) | 2 | 2 | 2 |  | GSB014 | Excessive leakage current | Pole-top fire;HV injection | 43862.8708 | 1 | Negligible: no ground fire | 14786 | Roadway |  | 20200107PWA_05 | Infrastructure (network-based) | -37.4294 | 144.5482 | 1 | Powercor | Report | 18665 | 0.035032 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3440 | Macedon | Crossarm
On arrival crew isolated supply and restored supply. | 411 CAMBERWELL ROAD, CAMBERWELL VIC 3124 | 30174779 |  | Blown branch/vegetation | [5 empty] | MFB reported wire down and ground fire in front of the above incident location. On arrival, crew noticed the ground fire was already put out and the found a broken tree branch had fallen onto an Low Voltage (LV) overhead service cable. There was a ground fire (6x4mts) in customers front yard. There was no reported injuries and minor damage to customers side fence. | Service cable (insulated) | 2 | 2 | 2 |  | CL011 | Vegetation: Trees Incident | Grassfire | 43891.8771 | 1 | Small: 10 - 1000 sq.m | 14789 | Residential |  | 20200107PWA_06 | Infrastructure (customer connection) | -37.8363 | 145.0626 | 1 | CitiPower | Report | 18668 | 0.0042025 | Low voltage AC (<1kV) | Moorabbin Airport | 3124 | Camberwell | Trees
Fuse Box replaced. New fuse box commissioned. | INVERLOCH HOLIDAY PARK, 2 CUTTRISS STREET, INVERLOCH VIC 3996 | 2809629 |  |  |  | Electrical overload |  |  |  | 100A Fuse Box faulty. FMB melted on the pole. | Any other type | 0 | 0 | 0 |  | wgi24 | overload | Pole-top fire | 28/12/2019 7:33 | 1 | Negligible: no ground fire | 14777 | Residential |  | 20200107SPN_01 | Infrastructure (network-based) | -38.6346 | 145.7422 | 1 | AusNet Services Distribution | Report | 18751 | 0.012181 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Fuse
Pole replaced. | 26 CLAREDALE ROAD, DANDENONG VIC 3175 | 524123 |  |  |  | Electrical breakdown |  |  |  | Tracking at top of pole. Top of pole found to be smouldering/burnt. | Pole top | 0 | 0 | 0 |  | ERTS-HPK | Tracking activity at top of pole likely due to pollution/dust on centre phase disks/eyebolt causing top of pole to smoulder/burn. | Pole-top fire | 16/12/2019 7:02 | 1 | Negligible: no ground fire | 14793 | Industrial |  | 20200107SPN_10 | Infrastructure (network-based) | -37.9981 | 145.2279 | 1 | AusNet Services Distribution | Report | 18672 | 0.032745 | 66kV AC | Moorabbin Airport | 3175 | Dandenong | Pole
Made safe and replaced the burnt out fuse unit. | 3 UPPER GRIEVE ROAD, AVONSLEIGH VIC 3782 | 420243 |  |  |  | Candled fuse |  |  |  | Candled fuse (EDO) on pole. | EDO fuse | 0 | 0 | 0 |  | BGE22 | Candled fuse (fuse failure) | Pole-top fire | 43477.9333 | 1 | Negligible: no ground fire | 14794 | Residential |  | 20200107SPN_11 | Infrastructure (network-based) | -37.9222 | 145.4756 | 1 | AusNet Services Distribution | Report | 18673 | 0.0092847 | 22kV AC | Moorabbin Airport | 3782 | Avonsleigh | Fuse
MFB called to report smoking pit. Crew dispatched and confirmed pillar was fire damaged. UG crew confirmed fault at cable joint. Service cable repaired, supply restored. | 27 CARBORA DALE, GREENSBOROUGH VIC 3088 | 5662202 |  |  |  | Electrical breakdown |  |  |  | LV pillar fire damaged | LV Pillar | 0 | 0 | 0 |  | ELM31 | Cable joint on service cable failed. | Plant/equipment | 44013.8403 | 1 | Negligible: no ground fire | 14806 | Residential |  | 20200108SPN_02 | Infrastructure (network-based) | -37.6912 | 145.1119 | 1 | AusNet Services Distribution | Report | 18690 | 0.031856 | Low voltage AC (<1kV) | Essendon Airport | 3088 | Greensborough | Connection
Crew attended and replaced the fuse. No grass fire. | 1 ONEILLS ROAD, LAKES ENTRANCE VIC 3909 | 1902142 |  |  |  | Candled fuse |  |  |  | Candled fuse. | Boric acid | 0 | 0 | 0 |  | BDL41 | Candled fuse. | Pole-top fire | 43952.8229 | 1 | Negligible: no ground fire | 14809 | Residential |  | 20200108SPN_03 | Infrastructure (network-based) | -37.8689 | 147.9964 | 1 | AusNet Services Distribution | Report | 18694 | 0.0087731 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | Fuse
Customer rang with all supply failure, found hv edo fuse burnt in half. Replace with new tube and fuse element. | WINDY RIDGE, 340 CAMPAGNOLOS ROAD, MANSFIELD VIC 3722 | 3913642 |  |  |  | Candled fuse |  |  |  | Burnt EDO fuse. | EDO fuse | 0 | 0 | 0 |  | MSD2 | Candled fuse. | Pole-top fire | 43952.7306 | 1 | Negligible: no ground fire | 14810 | Residential |  | 20200108SPN_04 | Infrastructure (network-based) | -37.111 | 145.9838 | 1 | AusNet Services Distribution | Report | 18696 | 0.018367 | 22kV AC | Wangaratta Aero | 3722 | Mansfield | Fuse
On arrival crew isolated supply and carried out repairs. | 365 Dunbar Rd, Lancaster VIC 3620, Australia | 30130749 |  |  |  | Leakage |  |  |  | Passer by reported broken cross arm and low wires at incident location. On arrival crew found that the cross arm had burn marks on it and had broken at the cross arm strap bolt. 66kV conductor had fallen and was hanging low. No ground fire, no third party damage, no injuries. | Crossarm (wood) | 2 | 2 | 2 |  | SHTS-KYM1 | Excessive leakage current | Pole-top fire | 43952.7472 | 1 | Negligible: no ground fire | 14812 | Roadway |  | 20200109PWA_01 | Infrastructure (network-based) | -36.3306 | 145.1036 | 1 | Powercor | Report | 18698 | 0.040778 | 66kV AC | Shepparton Airport | 3620 | Lancaster | Crossarm
Crew isolated and repaired. | 58 Letcher Rd, Nanneella VIC 3561, Australia | 30120913 |  |  |  | Leakage |  |  |  | Reports from customer of cross arm on fire. Crew attended site and found that the wooden cross arm had burnt around the area of one of the EDO fuse arms and the fuse unit had fallen from the cross-arm. No ground fire at site. No injuries no third party damage. | Crossarm (wood) | 2 | 2 | 2 |  | KYM001 | Excessive leakage current | Pole-top fire | 43952.3285 | 1 | Negligible: no ground fire | 14814 | Agricultural |  | 20200109PWA_02 | Infrastructure (network-based) | -36.3628 | 144.7942 | 1 | Powercor | Report | 18700 | 0.0081331 | 22kV AC | Bendigo Airport | 3561 | Nanneella | Crossarm
Crew isolated and repaired | 2 Lalbert Rd, Lake Boga VIC 3584, Australia | 30101817 |  |  |  | Leakage |  |  |  | CFA reported pole fire in Lalbert Rd near Station Street. When crew arrived they found that cross arm had burnt through at the cross arm strap. No ground fire confirmed by crew. No injuries or third party damage. CFA extinguished fire. | Crossarm (wood) | 2 | 2 | 2 |  | KGT004 | Excessive leakage current | Pole-top fire | 43952.7451 | 1 | Negligible: no ground fire | 14820 | Roadway |  | 20200109PWA_07 | Infrastructure (network-based) | -35.4625 | 143.6324 | 1 | Powercor | Report | 18707 | 0.018348 | 22kV AC | Swan Hill Aerodrome | 3584 | Lake Boga | Crossarm
The investigations on customers' installation are in progress | 4154 Hattah-Robinvale Rd, Wemen VIC 3549, Australia | 15370865 |  |  |  | Electrical breakdown |  |  |  | The 22kV feeders at the Wemen zone substation reported high voltage causing damages on many of the customers' installations that are connected to WMN 22kV feeders. A number of third party assets and Powercor LV assets impacted. No electrical shocks, fire or injuries have been reported. However, some customers' equipment damages have been identified. | Zone substation | 2 | 2 | 2 |  | WMN | Both transmission transformers at WETS faulted causing subtransmission system abnormal. A transient fault subsequently caused major load loss and voltage swings | Significant disruption to the community | 44044.5653 |  |  | 14840 | Roadway |  | 20200110PWA_15 | Infrastructure (network-based) | -34.7539 | 142.6833 | 1 | Powercor | Report | 18736 | 0.017277 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3549 | Wemen | AF Other
The investigations on customers' installation are in progress | 106 Anzac Rd, Robinvale Irrigation District Section C VIC 3549, Australia | 15369152 |  |  |  | Electrical breakdown |  |  |  | The 22kV feeders at the Robinvale zone substation reported high voltage to RVL 22kV feeders. A number of third party assets and Powercor LV assets impacted. . No electrical shocks, fire or injuries have been reported. However, some customers' equipment damages have been identified. | Zone substation | 2 | 2 | 2 |  | RVL | Both transmission transformers at WETS faulted causing subtransmission system abnormal. A transient fault subsequently caused major load loss and voltage swings | Significant disruption to the community | 44044.566 |  |  | 14841 |  |  | 20200110PWA_16 | Infrastructure (network-based) | -34.6217 | 142.7665 | 1 | Powercor | Report | 18738 | 0.025906 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section C | AF Other
Candled fuse. Crew send to investigate and make safe. EDO unit and fuse tube replaced to restore supply. | 305 KORUMBURRA-BENA ROAD, KORUMBURRA VIC 3950 | 2009391 |  | Lightning | [5 empty] | Candled fuse due to lightning on pole. No ground fire, and no other damage. | EDO fuse | 0 | 0 | 0 |  | LGA24 | Lightning at pole. | Pole-top fire | 43862.6625 | 1 | Negligible: no ground fire | 14843 | Agricultural |  | 20200110SPN_01 | Infrastructure (network-based) | -38.4122 | 145.8082 | 1 | AusNet Services Distribution | Report | 18742 | 0.013791 | 22kV AC | Morwell (Latrobe Valley Airport) | 3950 | Korumburra | Fuse
On arrival crew crew isolated supply and carried out repairs. | 856 Coradjil Rd, Simpson VIC 3266, Australia | 31032683 |  |  |  | Electrical breakdown |  |  |  | Crew were sectionalizing line to locate a feeder fault on CDN001. When restoring line, a lighting arrester failed on LIS-964946 "HEYJILL 2" S/S. The debris fell to the ground causing fire approximately 20m x 20m. The CFA and farmer assisted containing the fire. No damage to customer's property or assets identified. Fire burnt underneath wooden fence and around water tank. There was no reported injuries | Surge diverter | 2 | 2 | 2 |  | CDN001 | Surge diverter ruptured | Grassfire | 44075.6979 | 1 | Small: 10 - 1000 sq.m | 14847 | Agricultural |  | 20200113PWA_02 | Infrastructure (network-based) | -38.4685 | 143.3075 | 1 | Powercor | Report | 18746 | 0.017002 | 22kV AC | Warrnambool Airport Ndb | 3266 | Simpson | AF Other
Crew isolated for CFA to extinguish internal burning, pole & earth to be replaced the next morning | 3460 BENDIGO-MARYBOROUGH ROAD, LAANECOORIE VIC 3463 | 30019863 |  |  |  | Earth fault |  |  |  | CFA reported pole fire at incident address, Upon arrival crew found that ISO pole "Waanyarra P4" was burning internally, Crew isolated for CFA to extinguish internal burning. No ground fire, no injuries or 3rd party damage. | Pole (wood) | 2 | 2 | 2 |  | MRO007 | high impedance HV earth. | Pole-top fire | 44075.8681 | 1 | Negligible: no ground fire | 14852 | Agricultural |  | 20200113PWA_04 | Infrastructure (network-based) | -36.8426 | 143.8797 | 1 | Powercor | Report | 18756 | 0.017032 | 12.7kV AC (SWER) | Bendigo Airport | 3460 | Laanecoorie | Pole
Pole replaced, supply restored | 1050 Middle Rd, Rushworth VIC 3612, Australia | 30127001 |  |  |  | Leakage |  |  |  | Rushworth P119 ACR tripped to lockout, Upon arrival fault crew found that P184 Rushworth had burnt through between HV x-arm kingbolt & stay eyebolt, the pole top assembly dislodged from pole and landed on roadway. No ground fire or 3rd party damage. | Pole (wood);Crossarm (wood) | 2 | 2 | 2 |  | SHP014 | Excessive leakage current | Pole-top fire | 44105.8486 | 1 | Negligible: no ground fire | 14853 | Roadway |  | 20200113PWA_05 | Infrastructure (network-based) | -36.5207 | 145.0138 | 1 | Powercor | Report | 18757 | 0.038149 | 22kV AC | Shepparton Airport | 3612 | Rushworth | Crossarm
replaced burnt off cable that connects the over head to the underground | 240 MONASH WAY, MORWELL VIC 3840 | 2626406 |  | Bird | [5 empty] | Burnt off bridge | Cable sealing end | 0 | 0 | 0 |  | mwl24 | Bird Incident | Grassfire | 27/12/2019 14:30 | 1 | Small: 10 - 1000 sq.m | 14849 |  |  | 20200113SPN_01 | Infrastructure (network-based) | -38.2544 | 146.4235 | 1 | AusNet Services Distribution | Report | 18754 | 0.017839 | 22kV AC | Morwell (Latrobe Valley Airport) | 3840 | Morwell | Animal
On arrival crew confirmed site safe and no asset damage | 6-12 PLUMMER ROAD, LAVERTON NORTH VIC 3026 | 30114962 | Working too close to overhead lines | [6 empty] | An REC not on site, called to report that a truck and trailer had contacted overhead wires at the incident location. On arrival the crew found that a tipper truck (Rego-UNIMIX) had the tipper in the raised position and was reversing to allow for washing out the back, when the tipper contacted the overhead 22kV HV conductors. The driver was not injured as he had remained in the truck cabin. The HV conductors suffered only minor damage and remained in the air. The truck sustained damage to the tyres, which some required replacement. The protection operated. There were no injuries and no fires reported. | Conductor (bare) | 2 | 2 | 2 |  | SU034 | Tipper struck conductors | No Go Zone (contact) | 14/01/2020 7:05 |  |  | 14867 | Industrial |  | 20200114PWA_06 | Infrastructure (network-based) | -37.8165 | 144.8107 | 1 | Powercor | Report | 18773 | 0.0087002 | 22kV AC | Laverton Raaf | 3026 | Laverton North | Vehicle
Faults crew attended the site and upon inspection, it was identified that the HV cross-arm was burnt at the king bolt and broke. The site was isolated and made safe. The crossarm was replaced. | 821 SPRINGVALE ROAD, MULGRAVE VIC 3170 | 619973 |  |  |  | Leakage |  |  | 1 | UE received a call there was a small fire at the top of the pole and the fire authorities have just arrived. | Crossarm (wood) | 0 | 0 | 0 |  | SVW53 | The cause of the fire was tracking across the insulator. | Pole-top fire | 14/12/2019 10:15 | 1 | Negligible: no ground fire | 14864 | Roadway |  | 20200114UTD_03 | Infrastructure (network-based) | -37.9253 | 145.1568 | 1 | United Energy Distribution | Report | 18769 | 0.03915 | 22kV AC | Moorabbin Airport | 3170 | Mulgrave | Crossarm
Faults crew attended the site and upon investigation, it was identified the ampact connection at the pole substation had melted and dropped to the ground which caused a small grass fire at the base of the pole. The site was isolated and made safe. The ampact connections were replaced before supply was restored. | 11 DOROTHY STREET, RYE VIC 3941 | 1305665 |  |  |  | Overheated connection |  |  | 1 | UE received a call that there are white sparks from a pole falling to the ground and supply is lost. | Connector/termination | 0 | 0 | 0 |  | STO21 | The cause was an overheated ampact connection which melted and dropped to the ground. | Grassfire | 21/12/2019 11:50 | 1 | Localised: less than 10 sq.m | 14865 | Roadway |  | 20200114UTD_04 | Infrastructure (network-based) | -38.3876 | 144.7895 | 1 | United Energy Distribution | Report | 18770 | 0.022954 | Low voltage AC (<1kV) | Avalon Airport | 3941 | Rye | Connection
Faults crew attended the site and upon inspection, it was identified the cross-arm was burnt at one end. There was no fire on the ground. ESV was notified, ref #13055912. The site was isolated and made safe. The cross-arm was replaced. | 550-570 HEATHERTON ROAD, CLAYTON SOUTH VIC 3169 | 610198 |  |  |  | Leakage |  |  | 1 | UE received a call that a cross-arm is burnt. | Crossarm (wood) | 0 | 0 | 0 |  | SS21 | The cause of the fire was tracking across the insulator. | Pole-top fire | 24/12/2019 10:10 | 1 | Negligible: no ground fire | 14869 | Roadway |  | 20200114UTD_06 | Infrastructure (network-based) | -37.9588 | 145.122 | 1 | United Energy Distribution | Report | 18775 | 0.025889 | 22kV AC | Moorabbin Airport | 3169 | Clayton South | Crossarm
Fault crews attend the site and upon inspection, it was identified that the cross-arm was burnt and broken. The site was isolated and made safe. The cross-arm was subsequently replaced. | 500 STATION STREET, BOX HILL VIC 3128 | 7027380 |  |  |  | Leakage |  |  | 1 | UE received a call that there was a broken cross-arm. | Crossarm (wood) | 0 | 0 | 0 |  | BH23 | The cause of the fire was tracking across the insulator. | Pole-top fire | 30/12/2019 14:55 | 1 | Negligible: no ground fire | 14872 | Roadway |  | 20200114UTD_09 | Infrastructure (network-based) | -37.8245 | 145.1228 | 1 | United Energy Distribution | Report | 18778 | 0.040657 | 22kV AC | Moorabbin Airport | 3128 | Box Hill | Crossarm
Tree / Tree-Branch was cut clear and removed from the HV Conductors. | 315-317 MCGRATH ROAD, WYNDHAM VALE VIC 3024 | 33071271 |  | Blown branch/vegetation |  |  |  |  | 1 | A number of residents in the area reported arcing/sparking loud bangs before the power went out. Upon arrival, the Powercor Field Crew advised that a tree branch from a private customers large gum tree iat the incident location has snapped/broken in the high wind and fallen across the HV Conductors. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | WBE014 | Vegetation: Trees Incident | Loss of supply | 30/12/2019 16:14 |  |  | 14878 | Roadway |  | 20200115PWA_03 | Infrastructure (network-based) | -37.8897 | 144.6302 | 1 | Powercor | Report | 18791 | 0.020955 | 22kV AC | Laverton Raaf | 3024 | Wyndham Vale | Trees
Crews attended and performed inspections and repairs. CFA attended to ensure the fire was safe. | 7 CHUCK ROAD, SHEPPARTON VIC 3630 | 33095419 |  | Bird | [5 empty] | A Customer who wished to remain anonymous reported that a bird caused an "explosion" on the pole opposite 7 Chuck St and fell to the ground causing a small grassfire. On arrival the crew found that a bird had caused a flashover on the HV fuses of the Substation at the incident location, and had fallen to the ground igniting a grassfire on the nature strip of approx. 2m x 4m. There were no reported injuries or third party damage. | Pole mounted | 2 | 2 | 2 |  | STN022 | Bird Incident | Grassfire | 14/01/2020 11:30 | 1 | Localised: less than 10 sq.m | 14880 | Roadway |  | 20200115PWA_05 | Infrastructure (network-based) | -36.401 | 145.3994 | 1 | Powercor | Report | 18793 | 0.0030775 | 22kV AC | Shepparton Airport | 3630 | Shepparton | Animal
Sent crew to investigate and make safe. Neutral had burnt off, there was 7 volts on neutral to earth. Neutral was repaired NO volts on neutral to earth when retested. All tests completed. | 8 Bigola St, Ringwood VIC 3134, Australia | 1209154 |  |  |  | Neutral fault |  |  | 2 | Electric shock: customer on site received a tingle inside the property | Service cable (insulated) | 0 | 0 | 0 |  | RWN33 | Damaged neutral | Minor shock | 13/01/2020 12:27 |  |  | 14891 | Residential |  | 20200117SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19322 | 0.041029 | Low voltage AC (<1kV) | Moorabbin Airport | 3134 | Ringwood | OH Cable
Sent out a servicing crew to isolate supply and check all connection. The IPC for the neutral has been replaced. An inspector has tesed prior to power being restore and then conducted all required live VESI tests. | 11 Forest View Ln, Upper Ferntree Gully VIC 3156, Australia | 1302270 |  |  |  | Age | Poor workmanship |  |  | Electric Shock: person received an electric shock from shower head. Refer the to photo of failed connection. | Conductor (insulated) | 0 | 0 | 0 |  | FGY13 | Poor neutral connection: The IPCâ€™s for each of the active conductors has made a good connection, the IPC for the neutral conductor has made a poor connection. This has resulted in a â€˜floating neutralâ€™ situation. | Minor shock | 44136.5625 |  |  | 14895 | Residential |  | 20200117SPN_05 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18813 | 0.038853 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Upper Ferntree Gully | Connection
DE ENERGISED LINE VIA UPSTREAM ACR, ISOLATED S/S AND RESTORED REST OF NETWORK | 5 ODONNELL DRIVE, LAKES ENTRANCE VIC 3909 | O'Donnell Tranquil S/S |  | Fire |  |  |  |  | 2 | O'DONNELL-TRANQUIL KIOSK S/S FIRE. | Pad mounted equipment/kiosk | 2 | 2 | 2 |  | BDL41 | Findings by Crew Small fire inside the Kiosk at the LV Bush end It appears the grass has grown up into the LV bus Mainly Smoke damage and little scarring of the LV weber strip Kiosk checked and restored | Grassfire;Plant/equipment | 17/01/2020 14:33 | 1 | Localised: less than 10 sq.m | 14899 | Residential |  | 20200117SPN_06 | Infrastructure (network-based) | -37.854 | 147.995 | 1 | AusNet Services Distribution | Report | 18818 | 0.037328 | 22kV AC | Bairnsdale Airport | 3909 | Lakes Entrance | AF Other
Crew attended and re-fitted stay wire. | 772 Princes Hwy, Garvoc | 33098550 |  |  |  | Corrosion |  | Phase to earth | 1 | A crew patrolling following an outage found that at P1277 TRG-WBL Line (LIS-408458) the 66kV stay had parted at the helical termination. The stay contacted a HV conductor and the ground. A small grass fire of approx. 22m x 13m = 286m2 in size was found on the road reserve nearby. There was an area of 1/2 m2 fire private property burnt, and no reported injuries. | Guy wire | 0 | 0 | 0 |  | TRG004 | Buried components of stay assembly had corroded | Grassfire | 16/01/2020 20:32 | 1 | Small: 10 - 1000 sq.m | 14902 | Agricultural |  | 20200120PWA_01 | Infrastructure (network-based) | -38.2935 | 142.8491 | 1 | Powercor | Report | 18822 | 0.01997 | 22kV AC;66kV AC | Warrnambool Airport Ndb |  |  | AF Other
On arrival crew isolated supply and carried out repairs. | 20 CAMPBELL ROAD, COBRAM VIC 3644 | 30122729 | Working too close to overhead lines | [6 empty] | Customer reported making contact with service wire with Pole Hedge trimmer, no shocks/tingles, no smoking/sparking, supply on. Damage sustained to cable There was no fire or reported injuries. | Service cable (insulated) | 2 | 2 | 2 |  | CME021 | Accidental contact of service line with hedge trimmer. | No Go Zone (contact);Damage to network assets | 43689.391 |  |  | 14903 |  |  | 20200120PWA_02 | Infrastructure (customer connection) | -35.9209 | 145.6601 | 1 | Powercor | Report | 18823 | 0.024788 | Low voltage AC (<1kV) | Shepparton Airport | 3644 | Cobram | Other
On arrival crew made safe and carried out repairs | 1222-1254 MOUNT COTTRELL ROAD, STRATHTULLOH VIC 3338 | 30345280 | Copper theft | [6 empty] | Report received of open pits at incident location. On arrival the PCA Faults Crew have advised that an unknown person(s) have opened up the LV Service Pit at the base of PL Lighting Pole NPL2 LIS-852205 and cut through the 4c16mm LV Service Cable. Crew advised that the LV cables were found to be ALIVE, however no cable was stolen or taken from site. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. | Services cable | 2 | 2 | 2 |  | MLN011 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43781.6028 |  |  | 14904 | Roadway |  | 20200120PWA_03 | Infrastructure (network-based) | -37.7364 | 144.615 | 1 | Powercor | Report | 18824 | 0.040825 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Strathtulloh | Other
Crew sent to make safe, investigate and repair. The attending service crew isolated the supply and made safe. LEI inspected affected properties on Yarra St (and affected side streets) and found evidence of HVI. | 29 Yarra St, Warrandyte VIC 3113, Australia | 1206118 |  | Fallen | [5 empty] | Report of High Voltage Injection cuased by falling tree. Tree came down into HV which in turn contacted LV. | Conductor (bare) | 0 | 0 | 0 |  | RWN34 | Vegetation: Trees Incident | HV injection | 19/01/2020 18:00 |  |  | 14917 | Residential |  | 20200121SPN_05 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 18844 | 0.010123 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3113 | Warrandyte | Trees
On arrival crew isolated supply and carried out repairs. | 74 Barkly St, Warrnambool VIC 3280, Australia | 30544142 |  |  |  | Leakage |  |  |  | A customer reported to the fire brigade that a pole fire had occurred at the incident location. On arrival the crew found that following misty rain, the pole had burnt through at the eye bolt for the centre phase HV discs. There was no ground fire, and there were no injuries or third party damage reported. | Pole (wood) | 2 | 2 | 2 |  | WBL008 | Excessive leakage current | Pole-top fire | 20/01/2020 0:00 | 1 | Negligible: no ground fire | 14925 | Roadway |  | 20200122PWA_03 | Infrastructure (network-based) | -38.3859 | 142.4916 | 1 | Powercor | Report | 18855 | 0.040347 | 22kV AC | Warrnambool Airport Ndb | 3280 | Warrnambool | Pole
On arrival crew isolated supply and carried out repairs. | 37 Happy Valley Rd, Robinvale Irrigation District Section D VIC 3549, Australia | 32143806 |  |  |  | Leakage |  |  |  | Following a call from customers Crew found a burnt cross-arm at incident location. There was a small ground fire caused by fallen debris. | Crossarm (wood) | 2 | 2 | 2 |  | RVL001 | Excessive leakage current | Pole-top fire;Grassfire | 20/01/2020 16:19 | 1 | Localised: less than 10 sq.m | 14927 |  |  | 20200122PWA_05 | Infrastructure (network-based) | -34.6239 | 142.7654 | 1 | Powercor | Report | 18857 | 0.041318 | 22kV AC | Mildura Airport | 3549 | Robinvale Irrigation District Section D | Crossarm
On arrival crew isolated supply and carried out repairs. | 1256 BROUGHTON ROAD, KANIVA VIC 3419 | 32100850 |  |  |  | Leakage |  |  |  | A customer reported a pole fire at the incident locaton. On arrival the fault crew found that a HV crossarm had burned through at the kingbolt, and had dropped down with the HV conductors remaining attached to the crossarm, Th\re was no ground fire, no reported injuries or third party property damage | Crossarm (wood) | 2 | 2 | 2 |  | NHL031 | Excessive leakage current | Pole-top fire | 20/01/2020 14:15 | 1 | Negligible: no ground fire | 14929 | Agricultural |  | 20200122PWA_06 | Infrastructure (network-based) | -36.287 | 141.3028 | 1 | Powercor | Report | 18859 | 0.00063889 | 22kV AC | Horsham Aerodrome | 3419 | Kaniva | Crossarm
Crew Isolate section to replace the faulty IPC and re-attached LV cable head conductor tie to get the customers back on supply. | 135 Albert St, Windsor VIC 3181, Australia | 30217885 |  |  |  | Corrosion |  |  |  | MFB reported pole fire at the above incident location. On arrival, the crew found an Low Voltage (LV) cable head pole conductor tie (red phase) had broken due to faulty Insulation Piercing Connector (IPC) overheating, caught on fire . There was a minor fire on the pole at the point of IPC but no ground fire. There was no third party damaged and no reported injuries. | Connector/termination | 2 | 2 | 2 |  | BC020 | Overheated connection | Pole-top fire | 21/01/2020 15:19 | 1 | Negligible: no ground fire | 14936 |  |  | 20200122PWA_08 | Infrastructure (network-based) | -37.8562 | 144.9903 | 1 | CitiPower | Report | 18866 | 0.022979 | Low voltage AC (<1kV) | Essendon Airport | 3181 | Windsor | Connection
Fault crews attended the site to investigate. Upon inspection, it was identitifed the cross-arm was burnt. ESV was notified, ref #13107094. The site was isolated and made safe and the cross-arm was replaced. | 759 NEPEAN HIGHWAY, BRIGHTON EAST VIC 3187 | 1805698 |  |  |  | Leakage |  |  | 1 | UE received a call that there was a broken cross-arm. | Crossarm (wood) | 0 | 0 | 0 |  | MR31 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43891.6736 | 1 | Negligible: no ground fire | 14930 | Roadway |  | 20200122UTD_02 | Infrastructure (network-based) | -37.9193 | 145.0218 | 1 | United Energy Distribution | Report | 18860 | 0.00614 | 22kV AC | Moorabbin Airport | 3187 | Brighton East | Crossarm
On arrival crew isolated supply repairs carried out | 4475 MURRAY VALLEY HIGHWAY, GUNBOWER VIC 3566 | 30029617 |  |  |  | Leakage |  |  |  | VIC FIRE reported pole fire at incident location. Crew found Pole fire was put out by fire brigade at Leitchville P121, LIS 704306, burnt around centre phase tee off insulator eye bolt, pole OK, no ground fire. No reported injuries | Pole (wood) | 2 | 2 | 2 |  | CHA005 | Excessive leakage current | Pole-top fire | 23/01/2020 2:38 | 1 | Negligible: no ground fire | 14947 | Roadway |  | 20200123PWA_01 | Infrastructure (network-based) | -35.9553 | 144.3567 | 1 | Powercor | Report | 18881 | 0.0048056 | 22kV AC | Bendigo Airport | 3566 | Gunbower | Pole
Crew dispatched to investigate and make safe. Fire was out on arrival. Crew upon arrival identified a tree had contacted the conductor and the weight caused the conductor to sag to the ground. They advised a fire had started however was out when they arrived. They also advised it was a hot & windy day but the fire did not spread any greater than the attached photo's. Crew removed the tree and confirmed the sag was ok and restored power. | 2395 MCKILLOPS ROAD, TUBBUT VIC 3888 | 5767736 |  | Dead | [5 empty] | Report of grass fire due to conductor down. | Conductor (bare) | 0 | 0 | 0 |  | BM8B31 | Vegetation: Trees Incident | Grassfire | 23/01/2020 11:32 | 1 | Localised: less than 10 sq.m | 14949 | Agricultural |  | 20200124SPN_01 | Infrastructure (network-based) | -37.1007 | 148.6182 | 1 | AusNet Services Distribution | Report | 18886 | 0.0095255 | 22kV AC | Bairnsdale Airport | 3888 | Tubbut | Trees
Jemena fault crew attended and made repairs to damaged underground cable in pit and issued defect to damaged customer mains cable. | 65 GREEN STREET, BULLA VIC 3428 | A022910 | Copper theft | [5 empty] | 2 | Attempted copper theft outside Bulla Recreational Reserve. Vandals caused minor damage to Jemena assets in electricity pit and also damaged customer's mains cable. | Cable | 0 | 0 | 0 |  | COO11 | Copper theft. Vandals attempting to steal copper from underground electricity pit. | Damage to network assets | 25/01/2020 7:44 |  |  | 14950 | Public space |  | 20200125JEM_01 | Infrastructure (network-based) | -37.6325 | 144.807 | 1 | Jemena | Report | 18887 | 0.0014306 | Low voltage AC (<1kV) | Melbourne Airport | 3428 | Bulla | Other
Substation isolated LV circuit and HV (HV fuse open and live line clamps lifted) to allow for repairs and tranformer replacement. Substation replaced with a 50 kVA unit HV fuse ratings OK and were not replaced. | 115 DUNCANS LANE, DIGGERS REST VIC 3427 | A005100 | Copper theft | [5 empty] | 2 | Fault crews found pole-mounted substation (DUNCANS LA STH-P3) leaking oil due to vandalism. Crew advise it needs to be replaced. This substation was previously damaged during a copper theft incident (see OSIRIS incident report 20191124JEM_01) | Transformer | 0 | 0 | 0 |  | SHM11 | Copper theft or vandalism | Loss of supply;Damage to network assets | 24/01/2020 10:06 |  |  | 14956 | Peri-urban |  | 20200128JEM_01 | Infrastructure (network-based) | -37.6405 | 144.7432 | 1 | Jemena | Report | 18892 | 0.038529 | Low voltage AC (<1kV) | Melbourne Airport | 3427 | Diggers Rest | Other
Supply isolated and repairs carried out One customer defect issued on their customer mains | 835 SUMMERHILL ROAD, CRAIGIEBURN VIC 3064 | A006294 | Copper theft | [5 empty] | 2 | Attempted (unsuccessful) Copper theft of LV underground service cable | Services cable;Neutral screen | 0 | 0 | 0 |  | KLO22 | Attempted copper theft using rope around LV conductor to try and pull out LV underground service cable | Damage to network assets | 44105.4549 |  |  | 14960 | Peri-urban |  | 20200128JEM_02 | Infrastructure (customer connection) | -37.5702 | 144.9456 | 1 | Jemena | Report | 18896 | 0.018234 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt and broken. The HV conductor had dropped into the LV. LEI attended the site to investigate and confirmed HVI. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 5 BELLERIVE AVENUE, MOUNT WAVERLEY VIC 3149 | 2300779 |  |  |  | Leakage |  |  | 1 | UE received calls that customers have no supply. | Crossarm (wood) | 0 | 0 | 0 |  | NO7 | The cause of the fire was tracking across the insulator. | Pole-top fire | 43750.2882 | 1 | Negligible: no ground fire | 14955 | Roadway |  | 20200128UTD_01 | Infrastructure (network-based) | -37.8979 | 145.1232 | 1 | United Energy Distribution | Report | 18891 | 0.039225 | 22kV AC | Moorabbin Airport | 3149 | Mount Waverley | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the HV wires were on the ground which was caused by a possum on the cable terminations on the pole. LEI attended the site to investigate and confirmed the HVI. The site was isolated and made safe. The pole top construction was repaired and supply was restored. | 32 MELROSE STREET, PARKDALE VIC 3195 | 1808569 |  | Animal |  |  |  |  | 1 | UE received a call that the wire was down and MFB were on site. | Conductor (bare) | 0 | 0 | 0 |  | MC6 | Animal Incident | HV injection | 19/12/2019 3:05 |  |  | 14957 | Roadway |  | 20200128UTD_02 | Infrastructure (network-based) | -37.9976 | 145.0854 | 1 | United Energy Distribution | Report | 18893 | 0.0090104 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3195 | Parkdale | Animal
Faults crew attended the site to investigate. Upon inspection, it was identified that a customer's tree had fallen into the LV conductors and the neutral was wrapped around the white phase conductor. LEI attended the site to investigate and confirmed the presence of HVI. The site was isolated and made safe. The pole top construction was repaired and supply was restored. | 1 WILL STREET, FOREST HILL VIC 3131 | 7033466 |  | Fallen;Property owner/customer |  |  |  |  | 1 | UE data analytics identified low volts at multiple premises. | Conductor (bare) | 0 | 0 | 0 |  | NW14 | Vegetation: Trees Incident | HV injection | 30/12/2019 14:50 |  |  | 14958 | Roadway |  | 20200128UTD_03 | Infrastructure (network-based) | -37.8339 | 145.1764 | 1 | United Energy Distribution | Report | 18894 | 0.039266 | Low voltage AC (<1kV) | Moorabbin Airport | 3131 | Forest Hill | Trees
On arrival crew cut limb away from line | 13 GRAY STREET, NUMURKAH VIC 3636 | 33078990 |  | Within clearances | [5 empty] | CFA reported wire stared grass fire at incident location, fire now out, On arrival crew found a small branch had contacted LV conductors. Burnt particles fell to ground starting a small grass fire. There was no injuries reported or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | NKA004 | Vegetation: Trees Incident | Grassfire | 22/01/2020 21:38 | 1 | Small: 10 - 1000 sq.m | 14964 | Public space |  | 20200129PWA_01 | Infrastructure (network-based) | -36.0916 | 145.4466 | 1 | Powercor | Report | 18900 | 0.031432 | Low voltage AC (<1kV) | Shepparton Airport | 3636 | Numurkah | Trees
Fire attended by MFB. Crew dispatched to make safe. Repaired IPC connection at LV ABC T-off. | 104 BRACKENBURY STREET, WARRANDYTE VIC 3113 | 1206322 |  |  |  | Defective component |  |  |  | Report of grass fire due to white phase LV ABC IPC connector failed causing hot plastic and metal falling on the ground. | Conductor (ABC);Pole top | 0 | 0 | 0 |  | RWN34 | Failed ABC IPC connector. | Grassfire | 31/01/2020 21:47 | 1 | Localised: less than 10 sq.m | 14993 | Residential |  | 20200202SPN_01 | Infrastructure (network-based) | -37.7381 | 145.221 | 1 | AusNet Services Distribution | Report | 18942 | 0.016459 | Low voltage AC (<1kV) | Moorabbin Airport | 3113 | Warrandyte | Connection
Crew dispatched to investigate and make safe. CFA attended. Spur fuses blown at switch 881299. Isolated supply. Jointers carried out repairs. | 1135 ARTHURS CREEK ROAD, ARTHURS CREEK VIC 3099 | 5637993 |  | Lightning;Wind | [5 empty] | HV ABC conductor broke mid-span between poles #5637993 & #5637994 due to possible extreme weather activity and remained suspended by its catenary supporting cable, with holt molten aluminium and plastic falling to the ground suspected to have caused an approx. 200 sqm grass fire damaging parts of private property rural fencing and trees. | Conductor (ABC) | 0 | 0 | 0 |  | DRN14 | Extreme storms and weather related event. | Grassfire | 31/01/2020 20:22 | 1 | Small: 10 - 1000 sq.m | 14994 |  |  | 20200202SPN_02 | Infrastructure (network-based) | -37.5702 | 145.1783 | 1 | AusNet Services Distribution | Report | 18945 | 0.028514 | 22kV AC | Wallan (Kilmore Gap) | 3099 | Arthurs Creek | Conductor
Sent fault crew to make safe, investigate and organise repairs. Crew arrived onsite and observed blown 6K BA fuses, including one candled fuse with no evidance of fire present. Cre replaced the fuses and the single phase transformer. | 6525 SOUTH GIPPSLAND HIGHWAY, LOCH VIC 3945 | 2000595 |  | Humidity |  | Age |  |  |  | Report of candling fuse at a single phase substation (16kVA). Further blown fuses were found upstream. No photos of the site is available. | Boric acid | 0 | 0 | 0 |  | LLG12 | Plausible cuases are age and humidity. | Pole-top fire | 43832.1153 | 1 | Negligible: no ground fire | 14995 | Agricultural |  | 20200202SPN_03 | Infrastructure (network-based) | -38.3658 | 145.6704 | 1 | AusNet Services Distribution | Report | 18946 | 0.038385 | 22kV AC | Moorabbin Airport | 3945 | Loch | Fuse
Sent crew to make safe, investigate and organise repairs. Crew arrived at site and made safe. | 271 LOWER HEART ROAD, SALE VIC 3850 | 2503160 |  | Bird |  | Candled fuse |  |  |  | Report of candling HV fuse at 2503160. Sent fault crew to make safe, investigate and organise repairs. No Fire or damage to any other equipment/ property was observed. Crew found dead crow at downstream fuse location at sbustation pole 2503280. Crew replaced multiple fuses. No site photos availalbe. | Boric acid | 0 | 0 | 0 |  | SLE31 | Bird Incident | Pole-top fire | 25/11/2019 7:55 | 1 | Negligible: no ground fire | 14999 |  |  | 20200203SPN_03 | Infrastructure (network-based) | -38.1182 | 147.1229 | 1 | AusNet Services Distribution | Report | 18954 | 0.032983 | 22kV AC | Bairnsdale Airport | 3850 | Sale | Fuse
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt and broken and dropped onto the HV t-off cross-arm. LEI attended the site and confirmed there was no evidence of HVI. ESV was notified, ref #13151279. The site was isolated and made safe. The cross-arm was replaced and supply was restored | 18 LINDSAY STREET, FRANKSTON NORTH VIC 3200 | 3309505 |  |  |  | Leakage |  |  | 1 | UE received calls from customers advising of no supply and UE feeder circuit breaker operated. | Crossarm (wood) | 0 | 0 | 0 |  | FTN13 | The cause of the fire was tracking across the insulator. | Pole-top fire | 44105.6736 | 1 | Negligible: no ground fire | 15005 | Roadway |  | 20200204UTD_01 | Infrastructure (network-based) | -38.1196 | 145.1539 | 1 | United Energy Distribution | Report | 18961 | 0.02987 | 22kV AC | Moorabbin Airport | 3200 | Frankston North | Crossarm
On arrival crew isolated supply and carried out repairs. | 39 BANDYS ROAD, SMYTHESDALE VIC 3351 | 33002842 | [7 empty] | Vic fire reported a grass fire (8ha) at incident location. On arrival crew found a overheated FOLCB with one fuse base on the ground. There was no reported injuries, Damage sustained to pasture and fencing. | Connection box | 2 | 2 | 2 |  | BAS021 | Overheated connection box | Grassfire | 31/01/2020 16:11 | 1 | Medium: 1000 sq.m - 10 ha | 15019 | Agricultural |  | 20200205PWA_01 | Infrastructure (network-based) | -37.6552 | 143.6713 | 1 | Powercor | Notification | 18978 | 0.010495 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3351 | Smythesdale | Connection
On arrival crew isolated supply and carried out repairs. | 69 Wilson Rd, Melton South VIC 3338, Australia | 30110756 | Working too close to underground cables | [6 empty] | Following a fdr operation a call was received that a boring machine has contacted underground cables at the incident location (AL IMAN College). There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | MLN011 | Vertical boring | Loss of supply;No Go Zone (contact) | 43923.334 |  |  | 15023 | Public space |  | 20200205PWA_02 | Infrastructure (network-based) | -37.7083 | 144.5657 | 1 | Powercor | Report | 18985 | 0.012751 | 22kV AC | Laverton Raaf | 3338 | Melton South | Dug up
Faults crew attended the site to investigate. Upon inspection, it was identified that there was a fire on the wooden pole, between the HV and LV cross-arms. The fire was extinguished by CFA and site was made safe. The pole is to be replaced. | 47 HEALEY ROAD, DANDENONG SOUTH VIC 3175 | 623699 |  |  |  | Leakage |  |  | 1 | UE received a call that a pole was on fire and smoldering. | Pole (wood) | 0 | 0 | 0 |  | DVY32 | The cause of the fire was tracking across the insulator. | Pole-top fire | 20/01/2020 5:35 | 1 | Negligible: no ground fire | 15018 | Roadway |  | 20200205UTD_01 | Infrastructure (network-based) | -38.0277 | 145.2238 | 1 | United Energy Distribution | Report | 18977 | 0.031395 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3175 | Dandenong South | Pole
Faults crew attended the site to investigate. Upon inspection, it was identified that the IPC was burnt. The site was isolated and made safe. The conductors were repaired and supply was restored. | 12 JARRAH DRIVE, BRAESIDE VIC 3195 | 207327 |  |  |  | Overheated connection |  |  | 1 | UE received a call that there were flames coming from the top of the pole and the factory has lost supply. | Connector/termination | 0 | 0 | 0 |  | MC10 | The cause was a burnt out IPC. | Plant/equipment | 20/01/2020 8:05 | 1 | Negligible: no ground fire | 15020 | Roadway |  | 20200205UTD_02 | Infrastructure (network-based) | -38.0032 | 145.1105 | 1 | United Energy Distribution | Report | 18979 | 0.002566 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Braeside | Connection
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt and broken. The site was isolated and made safe. The cross-arm was replaced. | 101 ELDER STREET S, CLARINDA VIC 3169 | 2331012 |  |  |  | Leakage |  |  | 1 | UE received a call that the wooden cross-arm was broken and the insulator was drooping. | Crossarm (wood) | 0 | 0 | 0 |  | MC10 | The cause of the fire was tracking across the insulator. | Pole-top fire | 27/01/2020 9:35 | 1 | Negligible: no ground fire | 15021 | Roadway |  | 20200205UTD_03 | Infrastructure (network-based) | -37.9414 | 145.1022 | 1 | United Energy Distribution | Report | 18980 | 0.0084051 | 22kV AC | Moorabbin Airport | 3169 | Clarinda | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 13 BELLBIRD ROAD, MOUNT ELIZA VIC 3930 | 3311834 |  |  |  | Leakage |  |  | 1 | UE was advised by MFB that pole was on fire. | Crossarm (wood) | 0 | 0 | 0 |  | FSH12 | The cause of the fire was tracking across the insulator. | Pole-top fire | 20/01/2020 21:50 | 1 | Negligible: no ground fire | 15024 | Roadway |  | 20200205UTD_04 | Infrastructure (network-based) | -38.1996 | 145.1041 | 1 | United Energy Distribution | Report | 18987 | 0.023214 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3930 | Mount Eliza | Crossarm
Inspector dispatched to site. Found lighting strike to single phase 25kVA substation pole. 2 x customers effected. No damage found at meters. Blown 100A Tx isolator fuse and blown 80A fuse at house POA - fed via OH service. OH Service and installation wiring tested - OK. Smart meters tested - OK. Pole and transformer replaced prior to testing by inspector. One circuit of power unable to be reset on customers side. Sealed off in open position by inspector and customer advised to seek REC to rectify. | 695 KORUMBURRA SOUTH ROAD, KORUMBURRA SOUTH VIC 3950 | 2005484 |  | Lightning | [5 empty] | HV Injection | Conductor (bare) | 0 | 0 | 0 |  | LGA23 | Lightning strike to pole substation. | HV injection | 22/11/2019 7:30 |  |  | 15039 |  |  | 20200206SPN_01 | Infrastructure (network-based) | -38.4938 | 145.8313 | 1 | AusNet Services Distribution | Report | 19009 | 0.0016528 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3950 | Korumburra South | Lightning
The M&S crew have disconnected the overhead supply and issued a defect notice on site. | 14 MORAY STREET, FAWKNER VIC 3060 | A021606 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crew attended the address with a new connection service order for a 1 phase overhead Builders Temporary Supply (BTS). When the crew arrived they located another unauthorised and illegal BTS connection by non-authorised Jemena personal with the BTS already connected and on supply via a new black twisted overhead service cable. The BTS had a meter installed with the display on the meter not functioning (supply was live), the metering labels had been removed and a CitiPower/PowerCor sticker label located on the meter. There were also Jemena seals installed. | Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | CN04 | Unauthorised access a. Confirm whether or not the oh service line supplying the BTS pole was installed by Jemena Jemena response: No, this was not installed by Jemena or any authorised Jemena personnel. Jemena has no record of any Overhead BTS connection or metering at this address. ESV feedback: Based on Jemena response, the black twisted cable running from pole A021606 to the BTS pole was not installed by Jemena. b. Confirm whether or not the customerâ€™s installation was supplied by Jemena network; (all necessary wiring between the meter to customerâ€™s wiring was done?) Jemena response: Please clarify or rephrase this question because it does not make sense. A BTS pole with customer installation wiring and a foreign electricity meter was installed at the property and connected via an Overhead service line to the Jemena Electricity Distribution Network. This connection was not made by Jemena or an authorised Jemena representative. ESV feedback: I am seeking the following information, confirmation: â€¢ Was the customer installation (power sockets) connected and received supply from Jemena when Jemena arrived on site? â€¢ Had all necessary wiring work (including service fuses was inserted) been done to electrically connect the meter outgoing terminals to the customerâ€™s mainswitch? c. Clarification is required on Jemena seal which was mentioned in the attached OSIRIS report; is the meter seal? Is there an identification number? History record associated with the seal identification number. Jemena response: There was a Jemena seal installed on the electricity meter and meter panel. The seal number was not recorded at the time this was identified. ESV feedback: Nil. d. Confirm whether the smart meter belongs to Jemena or Powercor Jemena response: It is unknown who the smart meter belongs to. The meter data sticker including the meter number had been removed from the meter. The meter terminals cover had a CitiPower Powercor sticker indicating the meter belonged to that Distribution Network. ESV feedback: It is assumed that Jemena could not locate any identification (part number, manufacturer series number, etcâ€¦) on the meter. (i.e The label/plate on the meter was removed). Is there any other ways to identify the origin of the meter? Would VESI metering specialists be able to download the identity of the meter? e. If the smart meter belongs to Jemena, please provide the service history of the meter (detail of the last time in service). Jemena response: Please see above. f. Detail of any investigation taken by Jemena to the unauthorised interference with Jemena assets. Jemena response: The REC on the EWR application and COES is A Polidoro and the responsible person on the EWR is Roman Polidoro. Roman Polidoro is an ex-Jemena employee who is widely known for completing hundreds of unauthorised and illegal connections, disconnections and abolishment on the Jemena Electricity Distribution Network. Numerous complaints have been made by the Jemena/Zinfra compliance team regarding his activities and behaviours on the Jemena Electricity Distribution Network. ESV feedback: ESV would appreciate if Jemena provide evidence of â€œunacceptedâ€ electrical work that was alleged to be done by Roma Polidoro | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44014.6903 |  |  | 15055 | Residential |  | 20200207JEM_02 | Infrastructure (network-based) | -37.7092 | 144.9628 | 1 | Jemena | Report | 19466 | 0.040535 | Low voltage AC (<1kV) | Essendon Airport | 3060 | Fawkner | Other
On arrival crew isolated supply and carried out repairs. | 1567 LONGWOOD-SHEPPARTON ROAD, MOORILIM VIC 3610 | 33088592 | [7 empty] | Following a call from customer a Crew attended low wire at above address at Murchison pole 156. On arrival crew found a low conductor and burnt area underneath pole (4/10 sq mtr) There was no injuries, no third party property damage. | Insulator tie wires/connections | 2 | 2 | 2 |  | MNA034 | Conductor tie | Grassfire | 43984.7674 | 1 | Small: 10 - 1000 sq.m | 15060 | Agricultural |  | 20200210PWA_04 | Infrastructure (network-based) | -36.6217 | 145.3096 | 1 | Powercor | Notification | 19035 | 0.0064653 | 12.7kV AC (SWER) | Shepparton Airport | 3610 | Moorilim | Connection
Crew made site safe and reconnected cables in each pit affected. | MIDLAND HIGHWAY, MOUNT ROWAN VIC 3352 | 30554139 | Copper theft | [5 empty] | 2 | ESV reports a member of public advised them that cables were exposed at roundabout intersecting the Midland Hwy and the off/on ramps to the Western Hwy, Mount Rowan. | Cable | 0 | 0 | 0 |  | BAN009 | Third party vandalism / copper theft | Damage to network assets | 15/12/2019 10:14 |  |  | 15072 | Roadway |  | 20200211PWA_07 | Infrastructure (network-based) | -37.5183 | 143.8444 | 1 | Powercor | Report | 19175 | 0.0056748 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Mount Rowan | Other
On arrival crew isolated supply and carried out repairs. | 933 Sandilong Ave, Irymple VIC 3498, Australia | 30095918 |  |  |  | Leakage |  |  |  | Customer reported wire down at property. ON arrival crew found that a crossarm had burnt through. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | MDA023 | Excessive leakage current | Pole-top fire | 44076.384 | 1 | Negligible: no ground fire | 15073 | Agricultural |  | 20200211PWA_08 | Infrastructure (network-based) | -34.2334 | 142.1509 | 1 | Powercor | Report | 19052 | 0.010065 | 22kV AC | Mildura Airport | 3498 | Irymple | Crossarm
The crew made site safe and a Fault Follow Up was raised. | 237 BRIDGE ROAD, Melton South VIC 3338 | 811748 | Copper theft | [5 empty] | 2 | Streetlight cable has been cut away at the incident location. Upon arrival, a Powercor crew found that the UG pit lids were opened and 60m of P/L cables had been stolen between LIS 811748 and LIS 811747. | Cable | 0 | 0 | 0 |  | MLN021 | Copper theft | Damage to network assets | 18/12/2019 9:33 |  |  | 15079 | Roadway |  | 20200211PWA_13 | Infrastructure (network-based) | -37.7162 | 144.5967 | 1 | Powercor | Report | 19059 | 0.041102 | Low voltage AC (<1kV) | Laverton Raaf | 3338 | Melton South | Other
On arrival crew isolated supply and made arrangements to replace pole. LEI attended to check for HVI Inspector found some circuit breakers had operated but no evidence of damage. | 798 Karadoc Ave, Irymple VIC 3498, Australia | 32148297 |  |  |  | Leakage |  |  |  | Vic Fire reported wires sparking at corner of Karadoc and Fourteenth St. When crew arrived, they found a HV/LV wooden pole had burnt through at the LV king bolt, and the top of the pole had broken off and wires were low. Suspected HVI, inspector called to investigate. No ground fire, no third party damage or injuries. | Pole (wood) | 2 | 2 | 2 |  | MDA023 | Excessive leakage current | Pole-top fire | 44076.3125 | 1 | Negligible: no ground fire | 15080 | Roadway |  | 20200211PWA_14 | Infrastructure (network-based) | -34.2241 | 142.1749 | 1 | Powercor | Report | 19060 | 0.03017 | Low voltage AC (<1kV);22kV AC | Mildura Airport | 3498 | Irymple | Pole
Crew removed hazards, organized repairs and made site safe. | 273 MONT ALBERT ROAD, SURREY HILLS VIC 3127 | 16561 |  | Within clearances |  |  |  |  | 1 | Tree branch made contact with HV conductors causing the phases to touch resulting in sparks and outage. As a result it was reported that 166 customer s where offline. | Conductor (bare) | 0 | 0 | 0 |  | RD014 | Vegetation: Trees Incident | Damage to network assets | 30/12/2019 22:02 |  |  | 15081 | Residential |  | 20200211PWA_15 | Infrastructure (network-based) | -37.82 | 145.0949 | 1 | Powercor | Report | 19061 | 0.025461 | 11kV AC | Moorabbin Airport | 3127 | Surrey Hills | Trees
On arrival crew isolated supply and arranged repairs. LEI engaged to check for HVI | 26 Edgar St, Werribee VIC 3030, Australia | 32167520 |  |  |  | Leakage |  |  |  | A passer-by reported a HV wire on LV wires at the incident location. Upon arrival a Powercor fault crew found that a cross arm bunt through and fallen HV conductor caused HVI. There was no ground fire and no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | WBE033 | Excessive leakage current | Pole-top fire;HV injection | 44106.3431 | 1 | Negligible: no ground fire | 15082 |  |  | 20200211PWA_16 | Infrastructure (network-based) | -37.8975 | 144.6483 | 1 | Powercor | Report | 19062 | 0.023299 | Low voltage AC (<1kV);22kV AC | Laverton Raaf | 3030 | Werribee | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the ampact connection was burnt and dropped to the ground. The site was isolated and made safe. The connector was replaced and supply was restored. | 1-3 ALBION ROAD, BOX HILL VIC 3128 | 7023862 |  |  |  | Overheated connection |  |  | 1 | UE received a call from customer that there was sparking from the bottom of the insulator which started a fire at the bottom of the pole and they had no supply. Feeder circuit breaker protection operated. | Connector/termination | 0 | 0 | 0 |  | BH23 | The cause of the fire was a failed ampact. | Grassfire | 30/12/2019 12:45 | 1 | Localised: less than 10 sq.m | 15087 | Roadway |  | 20200211UTD_04 | Infrastructure (network-based) | -37.8242 | 145.1233 | 1 | United Energy Distribution | Report | 19067 | 0.0061227 | 22kV AC | Moorabbin Airport | 3128 | Box Hill | Connection
Deployed Inspector to investigate. | UNIT 4 125 LLOYD STREET, MOE VIC 3825 | moe24 |  | water ingress into the meter board;Other | [5 empty] | Electric Shock | Smart meter | 0 | 0 | 0 |  | meeter | Water ingress into the meter board caused damage | Minor shock | 43658.4521 |  |  | 15103 |  |  | 20200212SPN_01 | Infrastructure (network-based) | -38.18 | 146.2513 | 1 | AusNet Services Distribution | Report | 19084 | 0.01106 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3825 | Moe | Installation
On arrival crew isolated supply and commenced repairs. LEI investigating potential HVI damage | 205 C391, Shepparton East VIC 3631, Australia | 33092064 | Vehicle | [6 empty] | CFA reported truck hit pole and wires on truck at incident location. When crew arrived, truck had impacted at pole 25 and caused damage at poles 24 and 26 also. Site made safe, truck driver safe. There was no fire, no reported injuries, suspected HVI. | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | STN024 | Truck collided with pole | HV injection;Loss of supply;Damage to network assets | 44106.2736 |  |  | 15112 | Roadway |  | 20200214PWA_01 | Infrastructure (network-based) | -36.384 | 145.4319 | 1 | Powercor | Report | 19097 | 0.040691 | Low voltage AC (<1kV);22kV AC | Shepparton Airport | 3631 | Shepparton East | Vehicle
On arrival crew isolated supply and carried out repairs. | 170 DIGGERS ROAD, WERRIBEE SOUTH VIC 3030 | 30109960 |  |  |  | Leakage |  |  |  | MFB called to report a pole fire at LIS-203084. On arrival crew found that tracking had caused the dressing down crossarm to burn in half. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | WBE034 | Excessive leakage current | Pole-top fire | 44167.959 | 1 | Negligible: no ground fire | 15113 | Roadway |  | 20200214PWA_02 | Infrastructure (network-based) | -37.9331 | 144.6913 | 1 | Powercor | Report | 19098 | 0.032403 | 22kV AC | Laverton Raaf | 3030 | Werribee South | Crossarm
On arrival crew isolated supply and replaced FOLCB | 25 Paw Paw Rd, Brooklyn VIC 3012, Australia | 30103015 |  |  |  | Corrosion |  |  |  | Report received from customer of part supply. There appears to be a fault with the box on pole and small grass fire started below. On arrival crew found that a FOLCB had burnt out and hot debris had fallen into grass below starting a small fire (0.2x0.2 sqm). There was no injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BLT016 | Overheated connection | Grassfire | 14/02/2020 20:03 | 1 | Localised: less than 10 sq.m | 15128 | Roadway |  | 20200217PWA_02 | Infrastructure (network-based) | -37.8224 | 144.8326 | 1 | Powercor | Report | 19115 | 0.029535 | Low voltage AC (<1kV) | Laverton Raaf | 3012 | Brooklyn | Connection
crew replaced service | 5 MAVIS CRESCENT, KINGS PARK VIC 3021 | 31025244 |  |  |  | Corrosion |  |  |  | person reported shocks from meter enclosure. Crew found Corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located on the Reticulation Pole. | Service cable (insulated) | 0 | 0 | 0 |  | SSE031 | Corroded O/H Service Neutral Conductor termination | Minor shock | 17/02/2019 17:00 |  |  | 15135 | Residential |  | 20200217PWA_05 | Infrastructure (network-based) | -37.7333 | 144.779 | 1 | Powercor | Report | 19125 | 0.029424 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Kings Park | Connection
Crew attended and replaced service cable | UNIT 1 126 MERRI STREET, WARRNAMBOOL VIC 3280 | 32197678 |  |  |  | Corrosion |  |  |  | Plumber was removing a Water Meter at the property when she received an electric shock as she made simultaneous contact between her hand on the metallic Water Meter and her knees while kneeling on the wet ground. | Service cable (insulated) | 0 | 0 | 0 |  | WBL008 | Corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box located at the Reticulation Pole. | Minor shock | 24/10/2019 0:00 |  |  | 15137 | Residential |  | 20200217PWA_07 | Infrastructure (network-based) | -38.3878 | 142.4826 | 1 | Powercor | Report | 19127 | 0.016251 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Connection
Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a corroded O/H Neutral Screened Service Conductor termination at the Pole Top Connection Box located at the Reticulation Pole, which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the O/H Neutral Screened Service Cable Crossing South Valley Road with a Four Wire Twisted Service Cable and completed an NST Test which confirmed a Pass result. A final NST Test was carried out on the installation by the attending LEI which also confirmed a Pass result. | 76 NORTH VALLEY ROAD, HIGHTON VIC 3216 | 30061034 |  |  |  | Corrosion |  | Phase to earth |  | Ms Lauren Steele was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hands on the shower taps and her bare feet whilst standing on the wet shower base and waste water outlet. | Connection box;Service cable (insulated) | 2 | 2 | 2 |  | WPD033 | Corroded connection in junction box | Minor shock | 27/09/2019 0:00 |  |  | 15138 | Roadway |  | 20200217PWA_08 | Infrastructure (customer connection) | -38.1643 | 144.3204 | 1 | Powercor | Report | 19128 | 0.029296 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Highton | Connection
Sent fault crew to make safe, investigate and orgainse repairs. | 570 STRATH CREEK ROAD, BROADFORD VIC 3658 | 4703408 |  |  |  | Candled fuse |  |  | 0 | Report of candling HV Fuse. | Boric acid | 0 | 0 | 0 |  | SMR22 | fuse found candling due to lightning strike. no ground fire | Pole-top fire | 15/02/2020 3:48 | 1 | Negligible: no ground fire | 15130 |  |  | 20200217SPN_01 | Infrastructure (network-based) | -37.2205 | 145.1118 | 1 | AusNet Services Distribution | Report | 19118 | 0.034027 | 22kV AC | Wallan (Kilmore Gap) | 3658 | Broadford | Fuse
Sent Crew and Electricl Inspector to make safe, investigate and orgainse repairs. | LUCASOMBE LODGE, 973 GREAT ALPINE ROAD, FREEBURGH VIC 3741 | 4507449 |  |  |  | Neutral fault |  |  | 2 | Report of customer receiving electric shock when reaching for roof gutter. | Service cable (insulated) | 0 | 0 | 0 |  | BRT21 | Customers main neutral was faulty causing high impedance. | Minor shock | 15/02/2020 13:12 |  |  | 15132 |  |  | 20200217SPN_02 | Infrastructure (network-based) | -36.7763 | 147.0318 | 1 | AusNet Services Distribution | Report | 19121 | 0.0029491 | Low voltage AC (<1kV) | Wangaratta Aero | 3741 | Freeburgh | OH Cable
On arrival crew isolated supply. Crew issued a defect notice. REC required to repair damage on customer's installation before supply can be reconnected. | 5 MALONGA COURT, CAULFIELD NORTH VIC 3161 | 30219937 |  |  |  | Unknown technical factor |  |  |  | Following call from customer fault crew attended incident location. On arrival crew found burnt out FMB at customer point of attachment. Damage was sustained to mains box and customers fascia board. There was no ground fire, no reported injuries | POA connection (customer side);POA connection (network side);Service cable (insulated) | 2 | 2 | 2 |  | AR004 | Insufficient remains to determine cause | Other electricity related | 31/01/2020 18:30 | 1 | Negligible: no ground fire | 15033 | Residential |  | 20200205PWA_05 | Infrastructure (customer connection) | -37.8643 | 145.02 | 1 | CitiPower | Report | 19000 | 0.0086956 | Low voltage AC (<1kV) | Moorabbin Airport | 3161 | Caulfield North | Installation
On arrival crew isolated supply and carried out repairs | 1037 GUNAMALARY ROAD, MURRAYVILLE VIC 3512 | 32152937 |  |  |  | Leakage |  |  |  | Vicfire advised they had just extinguished a small pole fire at the incident location. On arrival crew found there had been a crossarm fire. There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | OYN001 | Excessive leakage current | Pole-top fire | 31/01/2020 22:52 | 1 | Negligible: no ground fire | 15035 |  |  | 20200205PWA_06 | Infrastructure (network-based) | -35.3169 | 141.2151 | 1 | Powercor | Report | 19003 | 0.00099884 | 22kV AC | Mildura Airport | 3512 | Murrayville | Crossarm
HV overhead line inspected and no damage found ARC suppressed due to working on feeder for planned works Feeder restored | 153-163 BARRY ROAD, CAMPBELLFIELD VIC 3061 | A099753 | Working too close to overhead lines | [5 empty] | 1 | Customer reported Garbage truck hit High Voltage overhead lines and and has caused a feeder outage. Garbage truck registration 1FZ8HR | Conductor (bare) | 0 | 0 | 0 |  | BD16 | No Go Zone breach | No Go Zone (contact) | 28/01/2020 14:09 |  |  | 15054 | Roadway |  | 20200207JEM_01 | Infrastructure (network-based) | -37.668 | 144.9633 | 1 | Jemena | Report | 19026 | 0.034957 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Vehicle
On arrival crew isolated supply and carried out repairs. | 103 Palmer St, Richmond VIC 3121, Australia | 30195068 |  |  |  | Corrosion |  |  |  | Report received of arcing and sparking and small ground fire at incident location. On arrival crew found that a D connection had overheated showering hot debris igniting grass below. There was no reported injuries or third party property damage. | Connector/termination | 2 | 2 | 2 |  | NR002 | Overheated connection | Grassfire | 30/01/2020 16:40 | 1 | Localised: less than 10 sq.m | 15045 | Roadway |  | 20200207PWA_05 | Infrastructure (network-based) | -37.8189 | 145.0089 | 1 | CitiPower | Report | 19017 | 0.035983 | Low voltage AC (<1kV) | Essendon Airport | 3121 | Richmond | Connection
On arrival crew isolated supply and arranged for repairs. | 1781 Barrabool Rd, Gnarwarre VIC 3221, Australia | 33041740 | Vehicle | [6 empty] | Powercor received customer reports of no supply. Additional reports were also received of a fire at the incident location. When crews arrived they found a vehicle accident with a HV pole had occurred resulting in pole failure and coming to ground together with HV conductors. The vehicle had come to rest on its roof and was engulfed in flames together with a 400m section of vegetation along the road side reserve. The fire area followed in the vicinity of the fallen HV conductors. Emergency services confirmed the driver had been killed in the accident | Conductor (bare);Pole (concrete) | 2 | 2 | 2 |  | WPD011 | car hit pole | Grassfire;Not involving electrocution;Damage to network assets | 29/01/2020 15:45 | 1 | Small: 10 - 1000 sq.m | 15048 | Roadway |  | 20200207PWA_07 | Infrastructure (network-based) | -38.1713 | 144.1417 | 1 | Powercor | Report | 19020 | 0.040787 | 22kV AC | Avalon Airport | 3221 | Gnarwarre | Vehicle
On arrival crew checked conductors, no damage found | 1787 Nareen Rd, Nareen VIC 3315, Australia | 32126181 | Working too close to overhead lines | [6 empty] | Report received of a grassfire at the incident location. Crew were told that a tip truck with its carrier raised had contacted the overhead line which caused arcing and debris from this incident started the grass fire (10 by 10meters burnt). The truck and its owner had left the site and no details were forthcoming. CFA attended site There was no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | HTN006 | Unknown tipper hit line | Grassfire | 29/01/2020 12:30 | 1 | Small: 10 - 1000 sq.m | 15049 | Agricultural |  | 20200207PWA_08 | Infrastructure (network-based) | -37.3863 | 141.5639 | 1 | Powercor | Report | 19021 | 0.025451 | 22kV AC | Hamilton Airport | 3315 | Nareen | Vehicle
On arrival supply isolated and arrangements made to replace pole | Green Gums, 1279 Edenhope-Penola Rd, Langkoop VIC 3318, Australia | 30084121 |  |  |  | Leakage |  |  |  | Customer reported pole burning at the top of pole, dry grass at the base, was on fire, customer has put that out, he is calling fire brigade. On arrival crew found pole fire had occurred and debris had ignited grass. There was a 40 15 sq mtr fire, no reported injuries. | Pole (wood) | 2 | 2 | 2 |  | CHM011 | Excessive leakage current | Pole-top fire;Grassfire | 23/01/2020 12:38 | 1 | Small: 10 - 1000 sq.m | 15051 | Agricultural |  | 20200207PWA_10 | Infrastructure (network-based) | -37.0862 | 141.1435 | 1 | Powercor | Report | 19023 | 0.014744 | 22kV AC | Hamilton Airport | 3318 | Langkoop | Pole
On arrival supply was isolated The connection on the LV bushing terminal was remade and tightened. | Dunbars Rd, Heytesbury Lower VIC 3268, Australia | 32056642 |  |  |  | Overheated connection |  |  |  | Fire emergency services reported a pole & ground fire at incident address. On arrival crew found a 20 x 30 mtr grass fire. On examination of substation it was determined that fire was caused by a "hot" joint on the substation 'b' phase. There was no reported injuries. | Connector/termination | 2 | 2 | 2 |  | TRG005 | loose connection | Grassfire | 25/01/2020 15:53 | 1 | Small: 10 - 1000 sq.m | 15052 | Agricultural |  | 20200207PWA_11 | Infrastructure (network-based) | -38.5714 | 142.903 | 1 | Powercor | Report | 19024 | 0.02516 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3268 | Heytesbury Lower | Connection
On arrival crew isolated supply and carried out repairs. | 8A Sherdley Green, Caroline Springs VIC 3023, Australia | 30110149 |  |  |  | Electrical breakdown |  |  |  | Vic fire reported fire start at above incident location. On arrival crew found a following a transformer fault one HV BA fuse had ruptured, debris has started a small grass fire. There was a small oil leak. There was no reported injuries or third party property damage. | Boric acid;Pole mounted | 2 | 2 | 2 |  | SU035 | BA fuse unit ruptured following transformer failure | Grassfire | 43984.6264 | 1 | Small: 10 - 1000 sq.m | 15061 | Roadway |  | 20200210PWA_05 | Infrastructure (network-based) | -37.7557 | 144.7387 | 1 | Powercor | Report | 19037 | 0.038506 | 22kV AC | Laverton Raaf | 3023 | Caroline Springs | Fuse
Metering & Servicing crew disconnected, made safe and abolished the 1 phase overhead supply line and 1 phase meter and completed the new 3 phase underground supply and metering. | 33 DAVIS STREET, COBURG VIC 3058 | A048772 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crew attended the above address this morning with a supply order (SO) for a new 3 phase undergroun supply in conjunction with an abolishment SO for an existing 1 phase overhead supply and metering. When they arrived on site they located another unauthorised and illegal overhead connection where the overhead supply line and 1 phase meter had been had been relocated from the previous residential property to a builders temporary supply (BTS) pole. It was noted by the crew that Jemena seals were installed on the meter. | Neutral screen;Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | CS02 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44137.6319 |  |  | 15088 | Residential |  | 20200211JEM_01 | Infrastructure (network-based) | -37.7409 | 144.9508 | 1 | Jemena | Report | 19068 | 0.0093056 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
On arrival crew isolated supply and arranged pole replacement. | Hiscocks Track, Netherby VIC 3418, Australia | 32099082 |  |  |  | Leakage |  |  |  | Report relieved of a pole fire at the incident location. On arrival crew found pole top burnt , CFA attended and extinguished the fire. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | NHL016 | Excessive leakage current | Pole-top fire | 44014.7875 | 1 | Negligible: no ground fire | 15062 | Agricultural |  | 20200211PWA_01 | Infrastructure (network-based) | -36.0399 | 141.5761 | 1 | Powercor | Report | 19038 | 0.032007 | 12.7kV AC (SWER) | Horsham Aerodrome | 3418 | Netherby | Pole
On arrival crew isolated supply and carried out repairs. | 175 Belar Ave Ext, Red Cliffs VIC 3496, Australia | 30098049 |  |  |  | Leakage |  |  |  | Report received of pole fire at incident location. On arrival crew found crossarm burnt off and conductor down There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | RCT021 | Excessive leakage current | Pole-top fire | 44076.3153 | 1 | Negligible: no ground fire | 15064 | Agricultural |  | 20200211PWA_02 | Infrastructure (network-based) | -34.2759 | 142.1776 | 1 | Powercor | Report | 19040 | 0.039538 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Crossarm
Sent Electrical Inspector to make safe, investigate and repair. | 8 Cooba Ct, Wangaratta VIC 3677, Australia | 5107180 | [7 empty] | Report of electric shock incident. | Service cable (insulated) | 0 | 0 | 0 |  | WN4 | Currently under investigation. | Minor shock | 44045.7333 |  |  | 15063 |  |  | 20200211SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19039 | 0.022313 | Low voltage AC (<1kV) | Moorabbin Airport | 3677 | Wangaratta | OH Cable
Sent fault crew to make safe, investigare and orgainse repairs. Crew repaired the broken steel conductor between poles 2627005 and 2623531 (at B). No photos of the site is available. | 805 WHITELAWS TRACK, YINNAR SOUTH VIC 3869 | 2627005 |  | Fallen | [5 empty] | Report of conductor down. Upon arrival crew observed HV Steel Conductor on the ground (at B as per attached spatial mark up) cuased by tree. The upstream BA15E line Fuse (at A) had blown that fed the conductor, however the conductor was being back fed through a single phase termination transformer (at C). Refer to the attached spatial mark up of the site. No sign of fire only smoke was observed. Site was isolated to make safe and carry out repairs. | Conductor (bare) | 0 | 0 | 0 |  | MWL25 | Vegetation: Trees Incident | Grassfire | 44106.6736 | 1 | Negligible: no ground fire | 15065 |  |  | 20200211SPN_02 | Infrastructure (network-based) | -38.3962 | 146.3604 | 1 | AusNet Services Distribution | Report | 19042 | 0.0034977 | 22kV AC | Morwell (Latrobe Valley Airport) | 3869 | Yinnar South | Conductor
Faults crew patrolled the line to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. The site was isolated and made safe. The cross-arm was replaced. | 18 THE PARADE, CLARINDA VIC 3169 | 2333349 |  |  |  | Leakage |  |  | 1 | UE 66kV line circuit breaker protection operated. | Crossarm (wood) | 0 | 0 | 0 |  | CDA-SVTS | The cause of the fire was tracking across the insulator. | Pole-top fire | 43750.2882 | 1 | Negligible: no ground fire | 15084 | Roadway |  | 20200211UTD_01 | Infrastructure (network-based) | -37.9302 | 145.1018 | 1 | United Energy Distribution | Report | 19064 | 0.019755 | 66kV AC | Moorabbin Airport | 3169 | Clarinda | Crossarm
Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. ESV was notified, ref #13086105. The site was isolated and made safe. The cross-arm was replaced. | 111 UNION STREET, BRIGHTON EAST VIC 3187 | 2333173 |  |  |  | Leakage |  |  | 1 | UE 66kV line circuit breaker protection operated and faults crew patrolled the line to investigate and found a pole fire. | Crossarm (wood) | 0 | 0 | 0 |  | bt-nb | The cause of the fire was tracking across the insulator. | Pole-top fire | 31/12/2019 8:30 | 1 | Negligible: no ground fire | 15085 | Roadway |  | 20200211UTD_02 | Infrastructure (network-based) | -37.9094 | 145.02 | 1 | United Energy Distribution | Report | 19212 | 0.027815 | 66kV AC | Moorabbin Airport | 3187 | Brighton East | Crossarm
Upon inspection, it was identified that the wooden cross-arm was burnt. There was no evidence of HVI. ESV was notified, ref #13086092. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 317 HIGH STREET, TEMPLESTOWE LOWER VIC 3107 | 7058574 |  |  |  | Leakage |  |  | 1 | UE HV feeder protection operated and faults crew patrolled the line to investigate and found a pole top fire. | Crossarm (wood) | 0 | 0 | 0 |  | BU1 | The cause of the fire was tracking across the insulator. | Pole-top fire | 31/12/2019 4:50 | 1 | Negligible: no ground fire | 15086 | Roadway |  | 20200211UTD_03 | Infrastructure (network-based) | -37.7635 | 145.1187 | 1 | United Energy Distribution | Report | 19214 | 0.03397 | 22kV AC | Essendon Airport | 3107 | Templestowe Lower | Crossarm
The attending LEI carried out all subsequent testing procedures, including:- Voltage tests from independent earth spike to metallic plumbing fixtures, neutral/earth bar at the customers main switchboard and to the point in which the victim reported receiving the electric shock, recording up to 30 volts on the installations earthing system. NST at the installation main switchboard recorded a failed test result. The attending LEI identified a severely corroded neutral screened cable at POA. Supply to installation was isolated at customers FOLCB. At this stage the attending LEI notified the report room that a truck will be required to replace the overhead service line and an inspector required to conduct follow up tests and and confirm the fault has been cleared upon reconnection. | 42 ANDREW STREET, GLENROY VIC 3046 | A019519 |  |  |  | Corrosion |  |  | 2 | Paul received an electric shock by making simultaneous contact with the metallic tap in bathroom. Customer also reported dimmed lights under load. Voltage tests between an independent earth and various points of the electrical installation, including the distribution assets, identified a defective (severely corroded) service neutral conductor at the POA. The neutral conductor of the neutral screened aluminium service cable was corroded. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise on the water piping system. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | PV23 | Defective (severely corroded) service neutral conductor at the POA | Minor shock | 31/01/2020 19:15 |  |  | 15096 | Residential |  | 20200212JEM_01 | Infrastructure (network-based) | -37.696 | 144.9459 | 1 | Jemena | Report | 19076 | 0.003765 | Low voltage AC (<1kV) | Essendon Airport | 3046 | Glenroy | OH Cable
Isolated and made safe, REC to repair and organise reconnection. | 1658 CALDER HIGHWAY, TARADALE VIC 3447 | 31007172 | Copper theft | [5 empty] | 2 | Reported exposed wires at service Pit at Telstra Tower, looks to be due to vandalism/theft, No Fire, no reported injuries. | Services cable | 2 | 2 | 2 |  | CMN001 | Copper Theft | Damage to network assets | 24/01/2020 14:49 |  |  | 15095 | Roadway |  | 20200212PWA_05 | Infrastructure (customer connection) | -37.1477 | 144.3516 | 1 | Powercor | Report | 19075 | 0.01651 | Low voltage AC (<1kV) | Bendigo Airport | 3447 | Taradale | Other
Crews ensured the area was isolated, and performed repairs | 1260 CAMPERDOWN-LISMORE ROAD, KARIAH VIC 3260 | 32059880 |  |  |  | Leakage |  |  |  | A customer called to report a pole fire and a wire down at the incident location. On arrival the crew found a HV wooden termination cross arm on the substation pole had burnt off. There was a small 5 sq m grass fire There was no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CDN004 | Excessive leakage current | Pole-top fire;Grassfire | 44137.5417 | 1 | Localised: less than 10 sq.m | 15097 | Agricultural |  | 20200212PWA_06 | Infrastructure (network-based) | -38.1526 | 143.2371 | 1 | Powercor | Report | 19077 | 0.034502 | 22kV AC | Warrnambool Airport Ndb | 3260 | Kariah | Crossarm
Crew organized repairs and made site safe. | 57 ROHS ROAD, EAST BENDIGO VIC 3550 | 30028633 | Working too close to overhead lines | [5 empty] | 2 | Customer called to advise that they had brought down a service with the crane on his dumpster removal truck while navigating up his driveway. The service was deemed by crew to require replacing since it had sustained a broken neutral. The service was a 2c/25mmÂ² lv abc service. | Service cable (insulated) | 0 | 0 | 0 |  | EHK021 | Crane on his dumpster removal truck contacted service in driveway. | Damage to network assets | 22/12/2019 19:57 |  |  | 15101 | Residential |  | 20200212PWA_07 | Infrastructure (network-based) | -36.7398 | 144.3165 | 1 | Powercor | Report | 19081 | 0.023007 | Low voltage AC (<1kV) | Bendigo Airport | 3550 | East Bendigo | Vehicle
Crews attended, isolated supply and performed repairs. | 248-250 DORCAS STREET, SOUTH MELBOURNE VIC 3205 | 30170708 | Vehicle | [5 empty] | 1 | Vic Fire reported a truck has contacted wires at the incident location. Upon arrival CitiPower crew found that the truck contacted LV mains and damaging conductors. The conductors fell on to cars below and some damages were done. There were no injuries or fire. The truck was driven away and no details available. | Conductor (bare) | 0 | 0 | 0 |  | AP006 | Truck hit overhead conductors | Less than $50k damage;Damage to network assets | 44013.6403 |  |  | 15102 | Roadway |  | 20200212PWA_08 | Infrastructure (network-based) | -37.8334 | 144.9589 | 1 | CitiPower | Report | 19272 | 0.038171 | Low voltage AC (<1kV) | Essendon Airport | 3205 | South Melbourne | Vehicle
Inspector sent to site after crew attended to check for possible HVI. HVI confirmed. Site made clear. | 54-56 ENNISMORE CRESCENT, PARK ORCHARDS VIC 3114 | 1205432 |  | Fallen | [5 empty] | HVI CONFIRMED DUE TO TREE branch falling over bare conductors. | Conductor (bare) | 0 | 0 | 0 |  | RWN26 | Vegetation: Trees Incident | HV injection | 44167.659 |  |  | 15104 |  |  | 20200212SPN_02 | Infrastructure (network-based) | -37.785 | 142.2158 | 1 | AusNet Services Distribution | Report | 19085 | 0.0013866 | 22kV AC | Hamilton Airport | 3114 | Park Orchards | Trees
Sent Electrical Inspector to make safe, investigate and orgainse repairs. | 24 PEARL PLACE, FERNTREE GULLY VIC 3156 | 1312395 | [6 empty] | 2 | Report of electric shock. | Service cable (insulated) | 0 | 0 | 0 |  | FGY32 | Currently under investigation. | Minor shock | 17/02/2020 11:28 |  |  | 15147 | Residential |  | 20200217SPN_06 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19139 | 0.03631 | Low voltage AC (<1kV) | Moorabbin Airport | 3156 | Ferntree Gully | OH Cable
supply isolated, construction crew attended Span replaced | Cranbourne Racecourse, Ballarto rd, Cranbourne 3977 | 2601629635 | Vandalism | [6 empty] | Tip truck pulled HV cable off pole | Cable | 0 | 0 | 0 |  | CRE32 | Tip truck pulled down HV at rear of racecourse | Damage to network assets | 13/12/2019 20:37 |  |  | 15151 |  |  | 20200218SPN_01 | Infrastructure (network-based) | -38.1226 | 145.2696 | 1 | AusNet Services Distribution | Report | 19146 | 0.02083 | 22kV AC | Moorabbin Airport | 3977 |  | Vehicle
Protection operation on No2 Transformer cleared the fault within 88 milliseconds | 279-329 CHRISTIES ROAD, RAVENHALL VIC 3023 |  |  | Unknown environment factor | Highly unlikely | Earth fault;Electrical breakdown;Unknown technical factor |  | Phase to earth | 1 | 220kV Cable Failure within Deer Park Terminal Station | Cable | 1 | 0 | 0 |  | No2 Transformer - White Phase Cable | Suspected manufacturing and/or installation defect | Melting or smoking only | 15/02/2020 15:44 |  |  | 15149 | Industrial |  | 20200218TGD_01 | Infrastructure (network-based) | -37.7764 | 144.7369 | 1 | Transgrid | Report | 19144 | 0.0048102 | 220kV AC | Laverton Raaf | 3023 | Ravenhall | UG Cable
Site made safe and HV12 crossarm replaced | 38 BORDEAUX STREET, AVONDALE HEIGHTS VIC 3034 | A025384 |  |  |  | Leakage |  |  | 2 | Pole top fire due to tracking | Pole top | 0 | 0 | 0 |  | BY14 | Tracking / electrical leakage | Pole-top fire | 16/07/2019 17:21 | 1 | Negligible: no ground fire | 15185 | Residential |  | 20200224JEM_02 | Infrastructure (network-based) | -37.7546 | 144.8642 | 1 | Jemena | Report | 19194 | 0.033551 | 22kV AC | Essendon Airport | 3034 | Avondale Heights | Pole
A visual inspection and voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a deteriorated Neutral Screen Conductor of an O/H Aluminium Neutral Screened Service Cable which was identified as the cause of the high impedance within the neutral service conductor. The attending Powercor Fault Crew replaced the corroded O/H Neutral Screened Service Cable to the premises and completed an NST Test which confirmed a Pass result. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 12 BARKLY STREET, MARYBOROUGH VIC 3465 | 30019965 |  |  |  | Corrosion |  | Phase to earth |  | Mr Kowen Ribbons was in the Bathroom showering when he reportedly received an electric shock as he made simultaneous contact with his hand on the metal Shower Rose and his bare feet whilst standing on the the wet shower base and waste water outlet. | Service cable (insulated) | 2 | 2 | 2 |  | MRO004 | Deteriorated Neutral Screen Conductor | Minor shock | 15/09/2019 23:00 |  |  | 15173 | Roadway |  | 20200224PWA_01 | Infrastructure (customer connection) | -37.0455 | 143.7308 | 1 | Powercor | Report | 19180 | 0.02242 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3465 | Maryborough | Conductor
Made safe and EDO fuse replaced. | 22 West St, Daylesford VIC 3460, Australia | 33004683 |  |  |  | Fuse failed to eject |  |  |  | Customer reported a pole outside their property is making arching sounds and he can see smoke and small sparks near conductor(white/blue) on the mains wire, On arrival crew found a hung up EDO fuse, no ground fire or any other damage, There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 2 | 2 | 2 |  | BAN008 | Hung up EDO fuse | Pole-top fire | 15/01/2020 10:09 | 1 | Negligible: no ground fire | 15178 | Roadway |  | 20200224PWA_06 | Infrastructure (network-based) | -37.3335 | 144.1373 | 1 | Powercor | Report | 19185 | 0.025354 | 22kV AC | Ballarat Aerodrome | 3460 | Daylesford | Fuse
REC has disconnected power | 15 SARNO COURT, CRANBOURNE VIC 3977 |  |  |  |  | Unidentified customer fault |  |  |  | Electric Shock claimed by customer | Customer wiring | 0 | 0 | 0 |  |  | under investigation | Minor shock (unconfirmed) | 25/02/2020 16:34 |  |  | 15197 |  |  | 20200225SPN_05 | Infrastructure (customer connection) | -38.108 | 145.2675 | 2 | AusNet Services Distribution | Notification | 19219 | 0.0068889 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne | Installation
Sent crew to make safe, investigate and organise repairs. Crew replaced the fuse and re-energised transformer. | 730 LINDENOW-GLENALADALE ROAD, LINDENOW SOUTH VIC 3875 | 1607114 |  |  |  | Age;Candled fuse |  |  |  | Report of candled HV BA (6K) Fuse found at substation. Crew replaced fuse and re-energised transformer to restore supply. No fire was observed at ground level or on the pole. Refer to the attached photo of candled HV Fuse. | Boric acid | 0 | 0 | 0 |  | BDL44 | Plausible cuase is combination of age and condition. | Pole-top fire | 23/02/2020 17:33 | 1 | Negligible: no ground fire | 15213 | Agricultural |  | 20200227SPN_02 | Infrastructure (network-based) | -37.8155 | 147.4366 | 1 | AusNet Services Distribution | Report | 19240 | 0.038905 | 22kV AC | Bairnsdale Airport | 3875 | Lindenow South | Fuse
Fire brigade extinguished fire and fuse replaced | 2752 BROADFORD-FLOWERDALE ROAD, FLOWERDALE VIC 3717 | 4703935 |  |  |  | Candled fuse |  |  |  | Candled fuse. Ground fire observed at pole location. | Any other type | 0 | 0 | 0 |  | SMR14 | candled fuse | Grassfire | 26/02/2020 20:46 | 1 | Small: 10 - 1000 sq.m | 15214 | Roadway |  | 20200227SPN_03 | Infrastructure (network-based) | -37.2897 | 145.2861 | 1 | AusNet Services Distribution | Report | 19242 | 0.022016 | 22kV AC | Wallan (Kilmore Gap) | 3717 | Flowerdale | Fuse
Fuse replaced and supply restored | 42 FEELYS ROAD, WILLUNG VIC 3847 | 2611076 |  |  |  | Candled fuse |  |  |  | Candled fuse | EDO fuse | 0 | 0 | 0 |  | TGN41 | Candled fuse | Pole-top fire | 26/02/2020 22:02 | 1 | Negligible: no ground fire | 15215 | Agricultural |  | 20200227SPN_04 | Infrastructure (network-based) | -38.242 | 146.792 | 1 | AusNet Services Distribution | Report | 19244 | 0.028023 | 22kV AC | Morwell (Latrobe Valley Airport) | 3847 | Willung | Fuse
Arrangements mad for HV crossarm replacement. | 167 VICTORIA STREET, ALTONA MEADOWS VIC 3028 | 30118483 |  |  |  | Leakage |  |  |  | Asset inspector found HV crossarm straps burnt off at HV crossarm, resting on LV crossarm straps There was no ground fire, no reported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | LVN022 | Excessive leakage current | Pole-top fire | 13/01/2020 13:38 | 1 | Negligible: no ground fire | 15221 | Roadway |  | 20200228PWA_03 | Infrastructure (network-based) | -37.8803 | 144.7857 | 1 | Powercor | Report | 19253 | 0.0085683 | 22kV AC | Laverton Raaf | 3028 | Altona Meadows | Crossarm
Crew replaced the existing O/H Twisted Service Cable | 32 PANNOO ROAD, LOCKINGTON VIC 3563 | 31025944 |  |  |  | Corrosion |  |  | 2 | person was in the front yard watering, when he received an electric shock as he made simultaneous contact between his arm on the metallic fence and his bare feet wearing thongs while standing on the wet ground. | Service cable (insulated) | 0 | 0 | 0 |  | SHP012 | Corroded O/H Service Neutral Conductor termination | Minor shock | 23/10/2019 9:00 |  |  | 15225 | Residential |  | 20200228PWA_04 | Infrastructure (network-based) | -36.2711 | 144.5316 | 1 | Powercor | Report | 19258 | 0.0092512 | Low voltage AC (<1kV) | Bendigo Airport | 3563 | Lockington | Connection
Top cut off pole new pole cap installed | 48 President Rd, Albanvale VIC 3021, Australia | 32163922 |  | Lightning | [5 empty] | Report received from vic fire of pole fire. there was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | SSE031 | Attributed to lightning | Pole-top fire | 15/01/2020 18:11 | 1 | Negligible: no ground fire | 15227 |  |  | 20200228PWA_05 | Infrastructure (network-based) | -37.7481 | 144.7721 | 1 | Powercor | Report | 19260 | 0.0059595 | Low voltage AC (<1kV) | Melbourne Airport | 3021 | Albanvale | Lightning
Crossarm replaced | 27 Pascoe St, Apollo Bay VIC 3233, Australia | 30051538 |  |  |  | Leakage |  |  |  | Crossarm fire reported by inspector. On arrival crew found bottom crossarm burnt off There was no ground fire, no re[ported injuries or third party property damage. | Crossarm (wood) | 2 | 2 | 2 |  | CLC013 | Excessive leakage current | Pole-top fire | 24/01/2020 16:01 | 1 | Negligible: no ground fire | 15231 |  |  | 20200228PWA_06 | Infrastructure (network-based) | -38.7541 | 143.6674 | 1 | Powercor | Report | 19266 | 0.00059375 | 22kV AC | Avalon Airport | 3233 | Apollo Bay | Crossarm
Sent fault crew to make safe, investigate, and organise repairs. | 465 HESLOP ROAD, ST CLAIR VIC 3995 | 2812177 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | Customer reported that trck has taken down HV overhead conductors in paddock of property. As per report, a tip truck drove underneath the 3 phase 22kV line with the tipper up. The truck hit the bottom conductor adjacent to an angle type 3. The tyres blew out but there was no sign of fire. Conductor height at contact is approximately 7 metres from ground level. Please refer to the attached site photos and truck details. No truck driver details are available. | Conductor (bare) | 0 | 0 | 0 |  | WGI34 | A tip truck drove underneath the 3 phase 22kV line with the tipper up on his dog trailer. The truck hit the bottom cable adjacent to an angle type 3. The tyres blew out but there was no sign of fire. Photos attached. Struck Conductor between Lis No 2612177 and LIs 2804561. Note Fuses x 2 Blew at Lis No 2612177 (SW 820478) . Controller isolated CB WGI 34FDR and WGI zone for crew access to Sw 820478) Zoom in on the one with the driveway. It shows the load that had been emptied behind the trailer. The truck had turned around after dumping the load in order to find his exit point and drove under the 22kV with the dog trailer elevated. Conductor height of conductor struck is 7 metres from ground level. Fuse switch 3 Phase Switch blew 2 BA 25 e fuses WGI34FDR CB opened off by Controller for access to the Switch 820478. No Injuries, damage to vehicles | No Go Zone (contact) | 23/03/2020 15:26 |  |  | 15218 | Agricultural |  | 20200228SPN_01 | Infrastructure (network-based) | -38.5832 | 145.615 | 1 | AusNet Services Distribution | Report | 19784 | 0.033625 | 22kV AC | Moorabbin Airport | 3995 | St Clair | Vehicle
Crew attended and replaced pole | 40 PRICES LANE, HEYWOOD VIC 3304 | 30556949 | [7 empty] | Customers reported Low volts, motors not running properly, lights are dimming, attending crew found HV earth (ISO) damaged and pole base burnt. pole required replacement | Pole (wood) | 0 | 0 | 0 |  | PLD001 | TBC | Grassfire | 43833.4111 | 1 | Localised: less than 10 sq.m | 15234 | Roadway |  | 20200302PWA_02 | Infrastructure (network-based) | -38.1366 | 141.6767 | 1 | Powercor | Notification | 19269 | 0.0043437 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3304 | Heywood | AF Other
Fault Crew re-terminated the existing O/H Service Cable Neutral Conductor at the FOLCB | 33 VICTORIA STREET, ALTONA MEADOWS VIC 3028 | 32177759 |  |  |  | Corrosion |  |  |  | person as in the Bathroom Showering when he received an electric shock as he made simultaneous contact with his hand on the metal Shower Tap and his bare feet whilst standing on the wet shower base. | Service cable (insulated) | 0 | 0 | 0 |  | LVN022 | Corroded and loose O/H Service Neutral Conductor termination at the FOLCB | Minor shock | 31/10/2019 8:55 |  |  | 15240 | Residential |  | 20200302PWA_08 | Infrastructure (network-based) | -37.8672 | 144.7873 | 1 | Powercor | Report | 19279 | 0.025902 | Low voltage AC (<1kV) | Laverton Raaf | 3028 | Altona Meadows | Connection
Corroded IPC connector and a neutral bridge cable at pole end replaced by Powercor Faults crew on site | INEXTERIOR COFFEE LOUNGE, 401 MAIR STREET, BALLARAT CENTRAL VIC 3350 | 33004401 |  |  |  | Corrosion |  |  |  | Plumber was replacing water hose at the time in the Restaurants kitchen he received an electric shock when he made simultaneous contact with the metallic water tap and the metallic (earthed) kitchen oven with his hands. | Conductor (insulated) | 0 | 0 | 0 |  | BAN005 | Corroded neutral connection | Minor shock | 43810.375 |  |  | 15241 |  |  | 20200302PWA_09 | Infrastructure (network-based) | -37.5594 | 143.8548 | 1 | Powercor | Report | 19280 | 0.0039433 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Ballarat Central | Connection
Jemena fault crew made site safe, followed by permanent repairs the following day. Repairs were also conducted on nearby pole-mounted substation RIDDELL RD-P65E on pole no. A105856 | 580 RIDDELL ROAD, SUNBURY VIC 3429 | A042516 | Copper theft | [5 empty] | 2 | Jemena public lighting fault crew found copper theft of underground cable at corner of Dalrymple Rd and Riddell Rd near pole no. A042516. Damage was also done to nearby pole-mounted substation RIDDELL RD-P65E on pole no. A105856 | Cable | 0 | 0 | 0 |  | SBY23 | Copper theft | Damage to network assets | 43864.25 |  |  | 15256 | Roadway |  | 20200303JEM_02 | Infrastructure (network-based) | -37.5462 | 144.69 | 1 | Jemena | Report | 19299 | 0.026622 | Low voltage AC (<1kV) | Melbourne Airport | 3429 | Sunbury | Other
On arrival crew arranged isolation. Small fire extinguished, low voltage pillar requires replacement totally destroyed. | 34 MCTAVISH BOULEVARD, HORSHAM VIC 3400 | 30228434 | Vehicle | [6 empty] | MR BRIAN HARMER, REC Steve 0407 340 836 adv concrete truck has nudged pillar on nature strip in front of property. Te Pillar was smoking and making noise. On arrival crew found that pillar had been dislodged causing shorting and overheating which scorched the ground underneath There was no injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | HSM009 | Concrete truck struck pillar | Grassfire | 43864.4583 | 1 | Localised: less than 10 sq.m | 15242 | Roadway |  | 20200303PWA_01 | Infrastructure (network-based) | -36.7287 | 142.1988 | 1 | Powercor | Report | 19281 | 0.026355 | Low voltage AC (<1kV) | Horsham Aerodrome | 3400 | Horsham | Vehicle
Tightened connection at group meter position | UNIT 2 18 MARRIOTT STREET, ST KILDA VIC 3182 | 30211544 |  |  |  | Neutral fault |  |  |  | Person was showering at the time, she received an electric shock when she made simultaneous contact between the metallic shower tap with her hand and the metallic shower grate with her foot. | Meter board (including fuses) | 0 | 0 | 0 |  | BC015 | Loose connection in group meter position | Minor shock | 43780.375 |  |  | 15244 | Residential |  | 20200303PWA_02 | Infrastructure (customer connection) | -37.8645 | 144.9878 | 1 | CitiPower | Report | 19283 | 0.014434 | Low voltage AC (<1kV) | Moorabbin Airport | 3182 | St Kilda | Connection
On arrival crew isolated supply and carried out repairs. | 43 HOUSTON STREET, DONALD VIC 3480 | 32019828 | Working too close to overhead lines | [6 empty] | Customer reported their tractor has hit service wire, wire broken off at house end, still connected to pole. On arrival crew found a damaged service line caused by customer removing tree using tractor. There was no fire, no reported injuries or third party property damage. | Service cable (insulated) | 2 | 2 | 2 |  | CTN006 | Vegetation: Trees Incident | Damage to network assets | 18/01/2020 10:12 |  |  | 15246 | Roadway |  | 20200303PWA_04 | Infrastructure (customer connection) | -36.3716 | 142.987 | 1 | Powercor | Report | 19285 | 0.016933 | Low voltage AC (<1kV) | Horsham Aerodrome | 3480 | Donald | Vehicle
Crew capped off live underground cable ends with IPC connections, closed pit lids and made safe. | 255 MARATHON BOULEVARD, CRAIGIEBURN VIC 3064 | A129079 | Copper theft | [5 empty] | 2 | Craigieburn Police advised street lights out and wires cut along Marathon Way, corner of Taransay Way in Craigieburn. Jemena fault crew found 3 pit lids open, with exposed live wires and 2 bays of underground cable stolen by vandals along Marathon Blvd, between Tamarin St and Taransay Way betwen poles A129079 and A129081. No customers impacted but some street lights are out in the area. | Cable;Services pit (network) | 0 | 0 | 0 |  | ST33 | Copper theft | Damage to network assets | 43924.475 |  |  | 15266 | Residential |  | 20200304JEM_01 | Infrastructure (network-based) | -37.5845 | 144.9027 | 1 | Jemena | Report | 19310 | 0.030036 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
On arrival crew isolated supply and arranged repairs. | 2307 C325, Romsey VIC 3434, Australia | 33027914 | Working too close to underground cables | [6 empty] | Civil contractor undertaking road widening activities called to advise LV UG had been hit in the process of excavating for the road works. Upon arrival crew confirmed that Contractor had contacted an LV underground cable. There was no fire, no reported injuries or third party property damage. Site supervisor, Dmytro, admitted that they were aware of the UG cable and had arrangements to undertake a deep bore under the roadway to relocate next week, | Services cable | 2 | 2 | 2 |  | WND012 | Excavation works | No Go Zone (contact) | 25/02/2020 10:53 |  |  | 15261 | Roadway |  | 20200304PWA_03 | Infrastructure (network-based) | -37.3936 | 144.748 | 1 | Powercor | Report | 19305 | 0.0031817 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3434 | Romsey | Dug up
Faults crew attended the site to investigate. Upon inspection, it was identified that there was evidence of fire damage on the wooden cross-arm and it was broken. The site was isolated and made safe. The cross-arm was replaced. | 2 SHELLEY STREET, ELWOOD VIC 3184 | 2306140 |  |  |  | Leakage |  |  | 1 | UE received a call from a customer that there was a broken cross arm on a pole. | Crossarm (wood) | 0 | 0 | 0 |  | EW12 | The cause of the fire was tracking across the insulator. | Pole-top fire | 44136.8021 | 1 | Negligible: no ground fire | 15259 | Roadway |  | 20200304UTD_01 | Infrastructure (network-based) | -37.8809 | 144.9856 | 1 | United Energy Distribution | Report | 19303 | 0.022296 | 11kV AC | Moorabbin Airport | 3184 | Elwood | AF Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the wooden cross-arm was burnt. The site was isolated and made safe. The cross-arm was replaced and supply was restored. | 1037 NEPEAN HIGHWAY, MOORABBIN VIC 3189 | 1815697 |  |  |  | Leakage |  |  | 1 | UE received a call that there is fire damage on a wooden crossarm. | Crossarm (wood) | 0 | 0 | 0 |  | MR24 | The cause of the fire was tracking across the insulator. | Pole-top fire | 27/02/2020 9:10 | 1 | Negligible: no ground fire | 15265 | Roadway |  | 20200304UTD_06 | Infrastructure (network-based) | -37.9398 | 145.0399 | 1 | United Energy Distribution | Report | 19636 | 0.012856 | 11kV AC | Moorabbin Airport | 3189 | Moorabbin | AF Other
Zinfra have temporarily restored the stay with a concrete block, which will need capital works to restore the stay. Yarra Valley Water would need to be contacted to be advised of the No Go Zone breach and cost recovery for the repair works | 76 BELL STREET, PRESTON VIC 3072 | A005251 | Building too close or within the No Go Zone | [5 empty] | 2 | Zinfra had a job on the weekend where it appears Yarra Valley Water may have removed the bed log and stay wire ground connection and left the stay wire flapping against the LV overhead conductor. Zinfra was not aware of any work to be performed. There were two previous NGZ Inspection Reports where permits were not requested: â€¢ J007917 16/01/20 attached. â€œdidnâ€™t want usâ€ â€¢ J008027 11/07/20 attached. â€œjob on holdâ€ | Pole (wood) | 0 | 0 | 0 |  | EP37 | No Go Zone breach | No Go Zone (contact) | 43833.3333 |  |  | 15267 | Roadway |  | 20200305JEM_01 | Infrastructure (network-based) | -37.7479 | 145.0299 | 1 | Jemena | Report | 19312 | 0.020668 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | Other
Site made safe and MFB called. HV crossarm re-fitted and temporary pole brace attached until the pole can be planned to replace. | 13 IMAROO STREET, FAWKNER VIC 3060 | A022864 |  |  |  | Defective component |  |  | 1 | King bolt failed at dual circuit HV crossarm at HV pole in parkland near Merri Creek Trail, resulting in conductor moving against pole and causing section to burn. | Conductor (bare);Pole (wood);Crossarm (wood) | 0 | 0 | 0 |  | CN04 | King bolt failed at dual circuit HV crossarm | Other electricity related | 19/02/2020 14:03 | 1 | Negligible: no ground fire | 15274 | Public space |  | 20200305JEM_02 | Infrastructure (network-based) | -37.7188 | 144.9779 | 1 | Jemena | Report | 19321 | 0.016616 | 22kV AC | Essendon Airport | 3060 | Fawkner | Crossarm
On arrival supply disconnected by isolating supply at pole end. Defect notice issued due to condition of installation | 128 FORREST STREET, ARDEER VIC 3022 | 32172721 | Unauthorised work;Unauthorised access | [6 empty] | Sgt Bryan 0431 953 997 from police request Powercor assistance for a possible unauthorised works on service cable. Sergeant Bryan advised that a member of the public driving along Forrest St Ardeer, called crime-stoppers to advise that they had witnessed suspicious activity at this property, Sergeant Bryan from the Police Public Order Response Team attended site and advised that he witnessed, a van parked underneath the POA with the two gentlemen (non-verbal/non english-speaking), having disconnected the existing 2/c 25mm LVABC s/c from the POA/FOLCB and were in the process of installing a new FOLCB, with the LIVE PCA service cable dangling in the air, supported by the POA attached to the fascia. I advised that our field crews would require someone to be on site, due to safety-issues at this property, Sergeant Bryan advised that he would organize, a local Police member to be present on site. There was no fire, no reported injuries or third party property damage | POA connection (customer side) | 2 | 2 | 2 |  | SU015 | Interference by non-licensed electrician | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43864.8056 |  |  | 15268 |  |  | 20200305PWA_01 | Infrastructure (customer connection) | -37.7832 | 144.8081 | 1 | Powercor | Report | 19313 | 0.029418 | Low voltage AC (<1kV) | Laverton Raaf | 3022 | Ardeer | Other
Burnt LV fuses at the sub LIS# 1407375. Truck sent to isolate and replace | 3045 WARBURTON HIGHWAY, MILLGROVE VIC 3799 | 1407375 |  |  |  | Fuse failed to eject |  |  |  | LV Fuse, Burnt | Any other type | 0 | 0 | 0 |  | WYK13 | LV FUSE FAILED | Pole-top fire | 43924.4743 | 1 | Negligible: no ground fire | 15273 |  |  | 20200305SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19320 | 0.036469 | Low voltage AC (<1kV) | Moorabbin Airport | 3045 | Millgrove | Fuse
Fault crews attended the site to investigate. Upon inspection , it was identified that the crimp connection on the service was burnt and melted. ESV was notified, ref #13517982. The site was isolated and made safe. The service was replaced. | 15 MATIPO STREET, DOVETON VIC 3177 | 23092 |  |  |  | Overheated connection |  |  | 1 | UE received a call that the service to a house was on fire. | Connector/termination | 0 | 0 | 0 |  | DN11 | the cause was a overheated crimp connection. | Plant/equipment | 43864.5 | 1 | Negligible: no ground fire | 15275 | Residential |  | 20200306UTD_01 | Infrastructure (network-based) | -37.9937 | 145.2353 | 1 | United Energy Distribution | Report | 19638 | 0.00027431 | Low voltage AC (<1kV) | Moorabbin Airport | 3177 | Doveton | Connection
Operator switched out HV and LV to make safe and investigate damage and repair. | 28 McCubbin Dr, Taylors Lakes VIC 3038 | A002958 | Working too close to underground cables | [5 empty] | 2 | Third Party fencing contractor made contact with an Earth Rod pushing it into a Red Phase Low Voltage circuit at McCubbin-Wentworth Kiosk Substation in Taylors Lakes. Earth wire pulled Kiosk slightly on pad. This has caused an interruption to customers on one circuit of the kiosk. 102 customers were affected and remained off supply for the duration of repair. There was no injury. NGZ inspection was conducted in March 2019, customer had wanted Jemena to share 50% costs of new boundary fence, next to McCubbin-Wentworth Kiosk substation. Another NGZ enquiry was made by customer on 6 March 2020, but Permit to Work was not issued by Jemena. | Cable;Pad mounted equipment/kiosk;Earth/earthing | 0 | 0 | 0 |  | SHM12 | No Go Zone breach | Loss of supply;No Go Zone (contact) | 44107.6493 |  |  | 15292 | Residential |  | 20200310JEM_02 | Infrastructure (network-based) | -37.6935 | 144.7747 | 1 | Jemena | Report | 19350 | 0.030994 | Low voltage AC (<1kV) | Melbourne Airport | 3038 | Taylors Lakes | Other
ON arrival crew made safe and arranged repairs | 2-4 SMITH STREET, MELTON VIC 3337 | 30322147 |  | Bird | [5 empty] | MFB reported sparking pole near 68 reserve road melton. On arrival crew advised that a dead-crow at the base of HVCHP P3 LIS-828102 appears to have caused a large -flashover across all 3 phases, resulting in damage to all 3 phases of the HVCHP terminations / HV UG cable, There was no reported grass-fire, HVI, injury or shocks as a result of this incident. | Surge diverter;Dropper/bridge | 2 | 2 | 2 |  | MLN023 | Bird Incident | Pole-top fire | 44077.7965 | 1 | Negligible: no ground fire | 15285 | Public space |  | 20200310PWA_04 | Infrastructure (network-based) | -37.6856 | 144.5863 | 1 | Powercor | Report | 19342 | 0.028943 | 22kV AC | Laverton Raaf | 3337 | Melton | Animal
On arrival crew isolated supply and carried out repairs. | Sunset Views Bvd/Leakes Rd, Tarneit VIC 3029, Australia | 30317704 | Working too close to underground cables | [6 empty] | Report received of LV pit and conductors dug up by earthmoving machinery at incident location. On arrival crew found that a low voltage underground pit has been dug up and displaced by excavator owned and operated by Winslow Constuctions. The LV cable was still alive . There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | TNA013 | Excavation works | No Go Zone (contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43864.4375 |  |  | 15291 | Roadway |  | 20200310PWA_05 | Infrastructure (network-based) | -37.835 | 144.6945 | 1 | Powercor | Report | 19348 | 0.009191 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Tarneit | Dug up
site visit and made safe. ESV inspected the HV SWER conductors with stabilised binoculars and did not see any evidence on the conductors | 1150 WALKERVILLE ROAD, TARWIN LOWER VIC 3956 | LIS2806919 | Working too close to overhead lines |  |  |  | Not followed |  |  | ESV attended site and reported the following: â€¢Plumber was installing battens to the roof of the stables. â€¢A 7m long batten is assumed to of contacted the HV overhead line. â€¢There is evidence of a flash on the stable structure. â€¢Injured person has suffered burns and suffered fractures following a fall from his working position â€¢ESV inspected the HV SWER conductors with stabilised binoculars and did not see any evidence on the conductors. | Conductor (bare) | 0 | 0 | 0 |  | WGI24 | ESV attended site and reported the following: â€¢Plumber was installing battens to the roof of the stables. â€¢A 7m long batten is assumed to of contacted the HV overhead line. â€¢There is evidence of a flash on the stable structure. â€¢Injured person has suffered burns and suffered fractures following a fall from his working position â€¢ESV inspected the HV SWER conductors with stabilised binoculars and did not see any evidence on the conductors. | Medical attention (first aid/doctor/hospital) | 28/02/2020 11:00 |  |  | 15281 |  |  | 20200310SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19335 | 0.032447 | 12.7kV AC (SWER) | Moorabbin Airport | 3956 | Tarwin Lower | Other
Crew attended and made safe | 243 BALDS ROAD, GREENWALD VIC 3304 | 30095338 | Working too close to overhead lines | [5 empty] | 1 | A tree harvester cut down a tree branch on to SWER line. On arrival, a Powercor fault crew found that the tree branch on the conductors and small ground fire about 10 Sqm. The crew made the place safe. | Conductor (bare) | 0 | 0 | 0 |  | PLD003 | apparent loss of control during harvesting | Grassfire | 44107.5458 | 1 | Localised: less than 10 sq.m | 15293 | Forest - plantation |  | 20200311PWA_01 | Infrastructure (network-based) | -37.9478 | 141.3686 | 1 | Powercor | Notification | 19352 | 0.033728 | 12.7kV AC (SWER) | Portland (Cashmore Airport) | 3304 | Greenwald | Trees
On arrival crew isolated line and removed branch. | 1602 Pyrenees Hwy, Amphitheatre VIC 3468, Australia | 32022861 | [7 empty] | Vic fire reported wires down and grass fire at incident location. On arrival found a large tree branch had fallen across HV conductors. Conductors still in the air and a ground fire started undermeath line. There was no injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MRO008 | Vegetation: Trees Incident | Grassfire | 13/03/2020 20:02 | 1 | Localised: less than 10 sq.m | 15303 | Agricultural |  | 20200316PWA_01 | Infrastructure (network-based) | -37.1929 | 143.3727 | 1 | Powercor | Notification | 19370 | 0.026293 | 22kV AC | Ballarat Aerodrome | 3468 | Amphitheatre | Trees
Sent fault crew to make safe, investigate and organise repairs. Crew replaced the fuse after line patrol and restored supply. | 178 MT RIDDELL ROAD, HEALESVILLE VIC 3777 | 1409956 |  |  |  | Age;Candled fuse |  |  |  | Report of Candling HV Fuse. Crew found 15E HV BA Fuse candled. No photos of the site is available. | Boric acid | 0 | 0 | 0 |  | WYK24 | Plausible cause is degradation due to age. | Pole-top fire | 28/03/2020 23:56 | 1 | Negligible: no ground fire | 15304 | Residential |  | 20200316SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19547 | 0.012564 | 22kV AC | Moorabbin Airport | 3777 | Healesville | Fuse
Crews attended, isolated supply, made the site safe and performed repairs. | C148, Mortlake VIC 3272, Australia | 32061459 | Vehicle |  |  | Overheated connection |  |  |  | At 13:31 the Woorndoo P84 ACR went to lockout. While patrolling, the fault crew found that the HV conductors wrapped together between poles 140-140E Woorndo line. Line appears to have been struck by an unknown vehicle. The fault current at the ACR caused molten metal to be ejected from the ACR connections igniting grass belo, resulting in 20x100m of roadside reserve being burnt. The fire site was approximately 7.5 km's from the conductor contact site. there were no reported injuries or third party property damage. | Conductor (bare);Connector/termination | 2 | 2 | 2 |  | TRG002 | Suspected vehicle contact with conductors, ejected debris following fault current caused fire | Grassfire | 16/03/2020 8:03 | 1 | Medium: 1000 sq.m - 10 ha | 15311 | Roadway |  | 20200317PWA_02 | Infrastructure (network-based) | -38.0094 | 142.8136 | 1 | Powercor | Report | 19381 | 0.01222 | 22kV AC | Warrnambool Airport Ndb | 3272 | Mortlake | Vehicle
Crews attended and ensured the site was safe. | 65 Gas Works Rd, Paaratte VIC 3268, Australia | 33034786 | Working too close to overhead lines | [6 empty] | Colin from National Australian Pipelines reported that an excavator onsite had contacted the overhead line at the incident location. On arrival the crew found that the excavator owned by National Australian Pipelines had contacted the 22kV HV OH conductors. The fault crew said that the crew onsite claimed that they had a safety observer, but he was not looking at the time of the contact. Conductors not damage and remained intact. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | TRG005 | Excavator working near line | No Go Zone (contact) | 17/03/2020 13:30 |  |  | 15316 | Construction |  | 20200318PWA_01 | Infrastructure (network-based) | -38.5579 | 142.9561 | 1 | Powercor | Report | 19386 | 0.034763 | 22kV AC | Warrnambool Airport Ndb | 3268 | Paaratte | Vehicle
Crews attended, isolated supply and made the site safe. Branch was removed with no apparent conductor damage. | 276 Bolitho Rd, Kyabram VIC 3620, Australia | 30130988 | [7 empty] | Vicfire reported a wire down and a grassfire at the incident location. On arrival the crew found that a large branch from a tree had fallen onto the 66kV OH HV conductors resulting in a ground fire of approx. 30m x 10m= 300m2 of road reserve. The HV conductors did not fall to the ground. There was no reported injuries or third party damage. | Conductor (bare) | 2 | 2 | 2 |  | SHTS-KYM1 | Vegetation: Trees Incident | Grassfire | 17/03/2020 12:44 | 1 | Small: 10 - 1000 sq.m | 15318 | Agricultural |  | 20200318PWA_02 | Infrastructure (network-based) | -36.3231 | 145.068 | 1 | Powercor | Notification | 19389 | 0.029412 | 66kV AC | Shepparton Airport | 3620 | Kyabram | Trees
On arrival crew isolated supply and carried out repairs. | 310 Grampians Rd, Halls Gap VIC 3381, Australia | 30333974 |  | Blown branch/vegetation | [5 empty] | Vic Fire reported a tree has bought down wires across road and caused grass fire at incident location. Emergency services on site. Crew found a tree damaged LV ABC between LIS: 840255 and LIS: 74877, bringing down 4 x bays of 95mm and 150mm cable, The transformer HV bushing also damaged, There was a a 8m x 6m grass fire, 2 x private vehicles damaged by falling cable. There was no reported injuries. | Conductor (ABC) | 2 | 2 | 2 |  | STL005 | Vegetation: Trees Incident | Grassfire;Damage to network assets | 18/03/2020 11:21 | 1 | Small: 10 - 1000 sq.m | 15322 | Public space |  | 20200319PWA_03 | Infrastructure (network-based) | -37.1568 | 142.5282 | 1 | Powercor | Notification | 19395 | 0.031153 | Low voltage AC (<1kV) | Horsham Aerodrome | 3381 | Halls Gap | Trees
Crews attended, isolated supply, made the site safe and performed repairs. | 140 WANGOOM ROAD, WARRNAMBOOL VIC 3280 | 30135820 | Working too close to underground cables | [6 empty] | Roger Constructions advised that a grader has dug up a cable at the incident location. On arrival the crew found that the grader belonging to Roger Constructions working on a new development site, had dug up a 4 x 16mm underground service cable. The UG cable and pit used to feed a timber workshop and a house, both of which were removed years ago, however the supply to the pit was never abolished. There was no fire, no reported injuries or third party property damage. | Services cable;Services pit (network) | 2 | 2 | 2 |  | WBL005 | Grader struck service cable | No Go Zone (contact);Damage to network assets | 43924.5069 |  |  | 15324 | Roadway |  | 20200319PWA_05 | Infrastructure (customer connection) | -38.3592 | 142.5175 | 1 | Powercor | Report | 19398 | 0.02483 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3280 | Warrnambool | Dug up
Crew replaced the Pole Top Connection Box and re-terminated the existing O/H Service Cable | 33 WARRANOOKE STREET, WILLAURA VIC 3379 | 30079839 |  |  |  | Corrosion |  |  |  | Person was in the Kitchen washing dishes when she received an electric shock as she made simultaneous contact between her hand on the Kitchen Tap and her arm on the metal sink. | Service cable (insulated) | 0 | 0 | 0 |  | ART033 | Corroded O/H Service Neutral Conductor termination at the Pole Top Connection Box | Minor shock | 23/11/2019 17:00 |  |  | 15325 | Residential |  | 20200319PWA_06 | Infrastructure (network-based) | -37.5432 | 142.7384 | 1 | Powercor | Report | 19399 | 0.01887 | Low voltage AC (<1kV) | Hamilton Airport | 3379 | Willaura | Connection
Repaired the existing service cable connection | 74 DAVIES STREET, BRUNSWICK VIC 3056 | 30159857 |  |  |  | Neutral fault |  |  |  | person was showering at the time; he received an electric shock when he made simultaneous contact between the metallic shower tap with his hand and the metallic shower grate with his foot. | POA connection (network side) | 0 | 0 | 0 |  | BK003 | Loose neutral connection at FMJB | Minor shock | 16/12/2019 11:30 |  |  | 15338 | Residential |  | 20200320PWA_01 | Infrastructure (network-based) | -37.7575 | 144.9701 | 1 | CitiPower | Report | 19420 | 0.0065498 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Connection
Damage circuit isolated, underground cable repaired, supply restored. | 175 CUTHBERTS ROAD, ALFREDTON VIC 3350 | 33106166 | Working too close to underground cables | [6 empty] | MR TOM MATHEW, excavator has struck UG wire supply, excavator has moved from wire, everyone onsite is ok and have created an exclusion zone for safety, company responsible is Pipcon Excavators, workers are onsite to meet crews. Crew advise low voltage mains damaged by excavator at the incident location, no injury, no fire. Contractor had exposed the cable before lunch break and had permits on site. However forgot about the cable after lunch break and proceeded to excavate damaging the Powercor asset. | Services cable | 2 | 2 | 2 |  | BAS024 | Excavator struck cable | No Go Zone (no contact) | 20/03/2020 15:00 |  |  | 15353 | Roadway |  | 20200323PWA_03 | Infrastructure (network-based) | -37.5525 | 143.7898 | 1 | Powercor | Report | 19438 | 0.020753 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Alfredton | Dug up
Crew replaced 2core service and left customer on supply | 8 OPHIR STREET, BROADMEADOWS VIC 3047 | A137396 | Working too close to overhead lines | [5 empty] | 2 | Customer living at the premise was using an excavator during building works for rear unit. The operator pulled down the service line with the excavator and broke the breakaway device. Service line fell to ground lying in the front yard. No permit to work was logged. | Neutral screen | 0 | 0 | 0 |  | BMS12 | No Go Zone breach | No Go Zone (contact) | 23/03/2020 15:44 |  |  | 15362 | Residential |  | 20200324JEM_04 | Infrastructure (network-based) | -37.6928 | 144.9335 | 1 | Jemena | Report | 19448 | 0.039683 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Broadmeadows | Vehicle
Incident notified to Jemena Works Practices and reported to ESV | 37A MADDOX ROAD, NEWPORT VIC 3015 | A025973 | Unauthorised access | [5 empty] | 2 | At approximately 5.30pm yesterday afternoon 24 March 2020 one of our Metering & Servicing crew members was driving past the address during their own private time and witnessed an ex-Jemena employee (Roman) abolishing an overhead service line. The crew member advised that he was working alone by himself, was working from his private ute and was dressed in the older style Jemena uniform. The crew member tried to get videos as best as he could, but was in a hurry to attend a private appointment. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | TH22 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 24/03/2020 17:30 |  |  | 15363 | Residential |  | 20200325JEM_01 | Infrastructure (network-based) | -37.7923 | 144.8573 | 2 | Jemena | Report | 19449 | 0.017226 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Other
Work Safe was contacted immediately. Work Safe Inspector Jeff (Ph: 0466 744 296) was assigned the report. Work Safe issued a cease work order. | 25 Seagull Avenue, Altona, VIC, 3018 | 30107390 | Building too close or within the No Go Zone | [6 empty] | Customer submitted a No Go Zone application for a site inspection to be completed when scaffolding contractor informed the builder that the scaffold to be erected will be to close without a Permit to Work in place. An appointment was arranged with the builder for a site visit to discuss the scaffold to be erected (Site visit date: Friday the 6th of December). When PAL employee arrived on site, a scaffold handrail had already been installed around the corner town house to be able to install the roof with a clearance of approximately 600mm to he bare low voltage conductors. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | AL007 | builder erected scaffold without permits in place | No Go Zone (no contact) | 43628.375 |  |  | 15366 | Construction |  | 20200325PWA_01 | Infrastructure (network-based) | -37.8687 | 144.8089 | 1 | Powercor | Report | 19452 | 0.027584 | Low voltage AC (<1kV) | Laverton Raaf | 3018 |  | Other
Fault crews attended the site to investigate. Upon inspection, it was identified that the street light head was on fire. The site was isolated and made. The street light head was replaced. | 5 MITCHAM ROAD, DONVALE VIC 3111 | 7066918 |  |  |  | Overheated connection |  |  | 1 | UE received a call that a street light pole was on fire. | Public lighting | 0 | 0 | 0 |  | NW13 | the cause is likely to be a loose connection which overheated. | Pole-top fire | 44138.1979 | 1 | Negligible: no ground fire | 15367 | Roadway |  | 20200325UTD_01 | Infrastructure (network-based) | -37.7909 | 145.1742 | 1 | United Energy Distribution | Report | 19744 | 0.025977 | Low voltage AC (<1kV) | Moorabbin Airport | 3111 | Donvale | Connection
Supply isolated and repairs carried out | 443-445 OLD GEELONG ROAD, HOPPERS CROSSING VIC 3029 | 30330075 | Working too close to underground cables | [6 empty] | Contractor involved with the Western Roads Upgrade (WRU) works called to report of damage to a Powercor cable. Cable was dug up by an excavator carrying out drainage works. The fault crew reported MOCS/Plans were on site and contained cable details. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | LV008 | Excavation works | No Go Zone (contact) | 21/03/2020 13:40 |  |  | 15411 | Roadway |  | 20200401PWA_01 | Infrastructure (network-based) | -37.8685 | 144.7317 | 1 | Powercor | Report | 19506 | 0.026412 | Low voltage AC (<1kV) | Laverton Raaf | 3029 | Hoppers Crossing | Dug up
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was cut. The service wire was replaced. | UNIT 3 50 RIVIERA STREET, MENTONE VIC 3194 | 1813011 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a hedge trimmer has cut the service wire while gardening. There was no shock. | Service cable (insulated) | 0 | 0 | 0 |  | M34 | It is likely the person was working too close to the service line. | No Go Zone (contact) | 26/03/2020 11:05 |  |  | 15412 | Residential |  | 20200401UTD_01 | Infrastructure (network-based) | -37.977 | 145.0737 | 1 | United Energy Distribution | Report | 19507 | 0.029566 | Low voltage AC (<1kV) | Moorabbin Airport | 3194 | Mentone | Other
Upon arrival the attending LEI conducted a voltage test between an independent earth and various parts of the electrical installation including distribution assets recording a reading of 0.8 volts under no load and 1.2 volts when the installation was put under load. A further NST was conducted at the installation switchboard which recorded a pass result. Following further investigation the attending LEI was able to identify that the neutral screen service line feeding the installation was showing signs of deterioration. At this point a truck was called to replace the service line. Upon the faults crew completing works an NST and follow up voltage tests were carried out, all which recorded a pass result. The installation was left on supply. | 87 CHIRNSIDE STREET, KINGSVILLE VIC 3012 | A048145 |  |  |  | Age |  |  | 2 | Licensed Electrical Inspector (LEI) requested to attend site following the customer hearing a loud noise coming from the FOLCB at the front of their property. It was reported that a witness on the street had also seen a bright flash come from this point (Note: no electric shock was received). | Neutral screen;Connection box;Service cable (insulated) | 2 | 2 | 2 |  | FW08 | Damaged neutral screen service line | Singeing or local charring/blackening only | 43865.3882 |  |  | 15421 | Residential |  | 20200402JEM_01 | Infrastructure (network-based) | -37.8082 | 144.8828 | 1 | Jemena | Report | 19529 | 0.028303 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Kingsville | OH Cable
Site has been made safe Underground crew to replace cable | 848 AITKEN BOULEVARD, CRAIGIEBURN VIC 3064 | A090758 | Copper theft | [5 empty] | 2 | Copper theft of street light underground cable, no impact to customer supply. | Cable | 2 | 2 | 2 |  | ST11 | Copper theft by unknown persons | Damage to network assets | 43865.5944 |  |  | 15422 | Roadway |  | 20200402JEM_02 | Infrastructure (network-based) | -37.5839 | 144.9123 | 1 | Jemena | Report | 19530 | 0.033618 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Crew arrived on the scene and advised the control room that the line needed to be de-energised immediately. The line was de-energised remotely in order to make the area safe before the crew began isolating the area so that customers could be put back on. SW 810625 pole 12.5 CONC. Conductor size 3/2.75 SCGZ. Arrived on site to discover 2 small burnt patches in grass measuring approx. 200cm x 1m each, what seemed to be where the conductor had fallen to the ground and bounced. The burnt grass was between poles 2623514 & 2623515. Conductor repaired from insulator on pole 2623514 and fuse replaced. | 55 FOX AND FANCKES ROAD, BOOLARRA SOUTH VIC 3870 | 2623514 |  |  |  | Mechanical breakdown |  |  |  | A conductor broke and started a small grass fire on a wet day. | Conductor (bare) | 0 | 0 | 0 |  | MWL11 | A mechanical failure of the conductor. | Grassfire | 43865.3063 | 1 | Localised: less than 10 sq.m | 15423 |  |  | 20200402SPN_01 | Infrastructure (network-based) | -38.4088 | 146.3028 | 1 | AusNet Services Distribution | Report | 19691 | 0.017034 | 22kV AC | Morwell (Latrobe Valley Airport) | 3870 | Boolarra South | Conductor
Section isolated and fire put out. HV crossarm replaced. | 68 BALLARAT ROAD, MAIDSTONE VIC 3012 | A035670 |  |  |  | Leakage |  |  | 1 | Pole and crossarm fire due to electrical leakage (tracking) No photos were available for this incident | Crossarm (wood) | 0 | 0 | 0 |  | BY12 | Electrical leakage (tracking) | Pole-top fire | 13/03/2020 21:35 | 1 | Negligible: no ground fire | 15428 | Residential |  | 20200403JEM_03 | Infrastructure (network-based) | -37.7868 | 144.8793 | 1 | Jemena | Report | 19537 | 0.018223 | 22kV AC | Essendon Airport | 3012 | Maidstone | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was damaged by the customer while making a new driveway. The service wire was replaced and the customer was issued with a defect and advised 4.6m clearance is required over driveway. | 21 CLARENDON DRIVE, SOMERVILLE VIC 3912 | 1104153 | Working too close to overhead lines | [5 empty] | 1 | UE was notified that an excavator has hit the service wire and it is still connected at house end but not at pole end. The driver is ok. | Service cable (insulated) | 0 | 0 | 0 |  | HGS22 | It is likely the person was working too close to the service line. | No Go Zone (contact) | 28/01/2020 12:00 |  |  | 15429 | Residential |  | 20200403UTD_01 | Infrastructure (network-based) | -38.2234 | 145.1599 | 1 | United Energy Distribution | Report | 19538 | 0.010685 | Low voltage AC (<1kV) | Moorabbin Airport | 3912 | Somerville | Vehicle
The fault crew isolated the LV circuit by opening the LV fuses at the distribution substation, and proceeded to make repairs under isolated conditions. | 22 GREENLEAF COURT, KEYSBOROUGH VIC 3173 | 636795 |  |  |  | Mechanical breakdown |  |  | 0 | United Energy received a call of a wire down in Greenleaf Crt Keysborough. On attendance, the UE fault crew found a bare LV OH conductor was live on the ground. | Conductor (bare) | 0 | 0 | 0 |  |  | The cause of the conductor failure is being attributed to the wearing of the conductor at the location of an LV spreader. The cause of the non operation of the LV fuse attributed to relatively high fault impedance at the location where the line was contacting the ground such that the fault current was not high enough to operate the fuse. The red phase HV fuse had operated and would have restricted available fault current on the LV side, further contributing to the non operation of the LV fuse. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 14/06/2020 20:00 |  |  | 15755 | Roadway |  | 20200618UTD_01 | Infrastructure (network-based) | -37.9957 | 145.1635 | 1 | United Energy Distribution | Report | 19985 | 0.017344 | Low voltage AC (<1kV) | Moorabbin Airport | 3173 | Keysborough | Conductor
Crew put a tiger mat over the service as asked, just as a temporary measure Jemena is currently developing options to rectify the situation and will work with the residents of no. 86 and no.88 in doing so Incident reported to WorkSafe reference number ID-34555 | 86 FRANCIS STREET, YARRAVILLE VIC 3013 | A052037 | Building too close or within the No Go Zone | [5 empty] | 2 | Faults truck was called to a job at 86 Francis St where the customer was reporting sparking wires. On arrival the crew found the site as per photos attached. They checked all connections and found no sign of anything to suggest there was sparking wires at all. It seems like they want us to drop the service. The problem is an old set up and the house (no. 88 Francis Street) next door feeds off this Point of Attachment. There are no LV mains on this side of the road. 86 Francis St is vacant and under construction and renovation. 88 Francis St is occupied and there is no easy solution for re-servicing this customer. Jemena has not received a request to attend 86 Francis St, Yarraville and there is no NGZ Permit to Work on issue | Conductor (ABC);POA connection (customer side);Service cable (insulated) | 0 | 0 | 0 |  | YVE24 | No Go Zone breach | No Go Zone (contact) | 19/06/2020 11:18 |  |  | 15760 | Residential |  | 20200619JEM_01 | Infrastructure (network-based) | -37.8212 | 144.8918 | 1 | Jemena | Report | 19990 | 0.024544 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Other
The crew attended site, the LV and HV fuses were opened and the area made safe. | 295-297 YARRA ROAD, WONGA PARK VIC 3115 | 1203571 | [7 empty] | crew arrived on site and found the YARRA ST JOHNS s/s had a candling fuse | Boric acid | 0 | 0 | 0 |  | CPK11 | Under Investigation | Pole-top fire | 21/06/2020 0:35 | 0 | Negligible: no ground fire | 15769 | Residential |  | 20200622SPN_05 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 20001 | 0.020969 | 22kV AC | Moorabbin Airport | 3115 | Wonga Park
Sent fault crew to make safe, investigate and organise repairs. Cre replaced the BA Fuse units. | 782 DARNUM-SHADY CREEK ROAD, SHADY CREEK VIC 3821 | 2706945 |  |  |  | Candled fuse |  |  |  | Report of cancling HV Fuse. No photos of the site is available. | Boric acid | 0 | 0 | 0 |  | WGL24 | Plausible cuase is combination of age and condition. | Pole-top fire | 16/02/2020 18:46 | 1 | Negligible: no ground fire | 15133 |  |  | 20200217SPN_03 | Infrastructure (network-based) | -38.136 | 146.0536 | 1 | AusNet Services Distribution | Report | 19123 | 0.010175 | 22kV AC | Morwell (Latrobe Valley Airport) | 3821 | Shady Creek | Fuse
Sent fault crew to make safe, investigate and organise repairs. | 91 BALMATTUM NORTH ROAD, EUROA VIC 3666 | 3903299 |  |  |  | Electrical breakdown |  |  | 2 | Report of bushing failure on the HV CAP EUROA 309 HV Cap Bank. | Pole mounted | 0 | 1 | 0 |  | BN1 | Failure of CAP Bank blue phase bushing resulted in a grass fire of 100m x 50m. no clear cause but most likely moisture ingress CFA extinguished fire CAP bank left isolated and tagged do not operate | Grassfire | 16/02/2020 23:33 | 1 | Localised: less than 10 sq.m | 15134 |  |  | 20200217SPN_04 | Infrastructure (network-based) | -36.7412 | 145.5898 | 1 | AusNet Services Distribution | Report | 19131 | 0.020395 | 22kV AC | Shepparton Airport | 3666 | Euroa | AF Other
Fault crews attended the site to investigate. Upon inspection, it was identified that the krone box on the pole was burnt and the leads were damaged. The site was isolated and made safe. The switch and leads were replaced and the supply was restored. | 6 KERFERD ROAD, GLEN IRIS VIC 3146 | 2310294 |  |  |  | Overheated connection |  |  | 1 | UE received a call from a customer that the pole top transformer was on fire. | Disconnector/isolator | 0 | 0 | 0 |  | K13 | The cause of the fire was a burnt out connection. | Grassfire | 44014.0347 | 1 | Localised: less than 10 sq.m | 15157 | Roadway |  | 20200218UTD_02 | Infrastructure (network-based) | -37.8585 | 145.0659 | 1 | United Energy Distribution | Report | 19152 | 0.033495 | Low voltage AC (<1kV) | Moorabbin Airport | 3146 | Glen Iris | Connection
Fault crews attended the site to investigate. Upon inspection, it was identified that a branch from a private tree broke and made contact with the HV. CFA witnessed the fire but were not on site when the crew arrived. The site was isolated and made safe. The conductors were repaired and supply was restored. | 769 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1309797 |  | Fallen;MEC |  |  |  |  | 1 | UE received a call that the power wire was on fire and UE feeder protection operated. | Conductor (bare) | 0 | 0 | 0 |  | DMA21 | Vegetation: Trees Incident | Other vegetation | 13/02/2020 8:55 | 1 | Localised: less than 10 sq.m | 15159 | Roadway |  | 20200218UTD_04 | Infrastructure (network-based) | -38.3525 | 144.9177 | 1 | United Energy Distribution | Report | 19154 | 0.014527 | 22kV AC | Moorabbin Airport | 3939 | Rosebud | Trees
Line Patrol deployed to inspect | 34 ELLASVILLE ROAD, NICHOLSON VIC 3882 | 1611011 | Unauthorised work | [6 empty] | Possible Truck into SWER | Conductor (bare) | 0 | 0 | 0 |  | BD6 | Patrol found large pile of gravel under SWER line between LIS # 1611011 & 1611012 which may of had tip truck contact SWER line. TBC after investigation. | Loss of supply | 18/02/2020 12:24 |  |  | 15161 |  |  | 20200219SPN_01 | Infrastructure (network-based) | -37.8207 | 147.7559 | 2 | AusNet Services Distribution | Notification | 19157 | 0.018918 | 12.7kV AC (SWER) | Bairnsdale Airport | 3882 | Nicholson | Vehicle
Crew sent & inspector sent to investigate. The attending LEI visually checked the condition all conductors and terminations between the distribution system and the Point of attachment of the installation. This did not reveal any defective conditions or equipment. The installation passed an NST test performed by the attending Attending LEI. Installation left ON supply. independant earth to affected phone charger showed 0v at time of site visit | 22 EMMER GREEN RETREAT, CRANBOURNE EAST VIC 3977 | 5814043 |  | Lightning | [5 empty] | electric shock . Customer reported electric shock happened last night after lightning hit street light pole. Daughter Miss Kaileen Pope was using mobile phone whilst on charge when she at the time received a sensation she believed to be an electric shock during lightning strike to light pole outside home. | Customer wiring | 0 | 0 | 0 |  | CLN12 | lightning hit street light pole. independant earth to affected phone charger showed 0v at time of site visit | Medical attention (first aid/doctor/hospital) | 19/02/2020 8:08 |  |  | 15163 | Residential |  | 20200219SPN_03 | Infrastructure (customer connection) | -38.1068 | 145.2979 | 2 | AusNet Services Distribution | Report | 19163 | 0.014052 | Low voltage AC (<1kV) | Moorabbin Airport | 3977 | Cranbourne East | Lightning
Crew attended and replaced insulator MFB on site to extinguish fire in paddock adjacent fault site. | 69 Horsburgh Dr, Altona North | 30271646 | [7 empty] | Grass fire was reported near base of pole, attending crew found center phase 66kV insulator has broken off its mount. The conductor was resting on the 66kV steel cross-arm and evidence of current passing through the wooden pole to earthed 11kV bracket was found. | Pole (wood);Crossarm (steel);Insulators | 0 | 0 | 0 |  | BLTS-AL | TBC - probable insulator stud broken | Grassfire | 19/02/2020 14:23 | 1 | Small: 10 - 1000 sq.m | 15166 | Roadway |  | 20200220PWA_02 | Infrastructure (network-based) | -37.8471 | 144.8098 | 1 | Powercor | Notification | 19168 | 0.036928 | 11kV AC;66kV AC | Laverton Raaf |  |  | AF Other
Crew sent to investigate. Found street light head (250W HPS) had caught fire and needs to be replaced. Crew made the site safe and replaced the street light head. | JACK RYANS IRISH BAR, 154 RAYMOND STREET, SALE VIC 3850 | 2501996 |  |  |  | Overheated connection |  |  | 2 | Report of street light head fire. S/light head burnt and no other damage to the sourrounds. Unfortunately, photos of the burnt light is not availalble; only photo of the replaced light is availalbe. Refer to the attached photos of repaired lights. | Public lighting | 0 | 0 | 0 |  | SLE11 | Possible over heated connection due to blown glone and no timing mechanism on ignitors (earlier models of HPS lights). Most likely due to the capacitor or the ballast igniting over and over resulting in overheating. | Pole-top fire | 22/02/2020 21:51 | 1 | Negligible: no ground fire | 15182 | Residential |  | 20200224SPN_01 | Infrastructure (network-based) | -38.1095 | 147.0662 | 1 | AusNet Services Distribution | Report | 19689 | 0.039726 | Low voltage AC (<1kV) | Bairnsdale Airport | 3850 | Sale | AF Other
On arrival crew isolated supply and carried out repairs. | 329 Sebastopol-Smythesdale Rd, Smythesdale VIC 3351, Australia | 33006114 |  | Lightning | [5 empty] | Customer reported pole hit by lightning and on fire. Crew arrived and found customers U/G fuse box on pole had melted and dropped hot debris to the ground starting a ground fire of 1m2 at base of pole. CFA attended and extinguished fire. There was no injuries or third party property damage. | Connection box;Pole (concrete) | 2 | 2 | 2 |  | BAS021 | Lightning strike | Grassfire | 24/02/2020 19:00 | 1 | Localised: less than 10 sq.m | 15188 | Agricultural |  | 20200225PWA_02 | Infrastructure (network-based) | -37.6396 | 143.7219 | 1 | Powercor | Report | 19200 | 0.0041285 | 12.7kV AC (SWER) | Ballarat Aerodrome | 3351 | Smythesdale | Lightning
FOLCB replaced, supply restored | 44 WESTERN ROAD, COHUNA VIC 3568 | 33022821 |  |  |  | Overheated connection |  |  |  | CFA reported pole fire at the incident location. Upon arrival fault crew found that a FOLCB had faulted and burnt the box. No ground fire or damage to concrete pole, CFA attended. | Connection box | 2 | 2 | 2 |  | CHA006 | connection failure | Pole-top fire | 24/02/2020 5:44 | 1 | Negligible: no ground fire | 15189 | Roadway |  | 20200225PWA_03 | Infrastructure (customer connection) | -35.8062 | 144.2095 | 1 | Powercor | Report | 19201 | 0.030712 | Low voltage AC (<1kV) | Swan Hill Aerodrome | 3568 | Cohuna | Connection
The attending Powercor Fault Crew removed the Pole Top Connection Box and re-terminated the existing O/H Twisted Service Cable directly to the O/H Reticulation system | 35 MERNDA PARADE, BELMONT VIC 3216 | 32081950 |  |  |  | Corrosion |  |  | 2 | person was in the Bathroom having a bath when he experienced a sensation that he believed may have been a slight electric shock or fright when he contacted the metallic taps with his hands whilst being submerged in the Bath Tub full of water. | Service cable (insulated) | 0 | 0 | 0 |  | GLE012 | Corroded connection | Minor shock | 29/10/2019 9:00 |  |  | 15191 | Residential |  | 20200225PWA_04 | Infrastructure (network-based) | -38.1828 | 144.3403 | 1 | Powercor | Report | 19204 | 0.029451 | Low voltage AC (<1kV) | Avalon Airport | 3216 | Belmont | Connection
Made safe and repaired. | 14 Hobson St, Queenscliff VIC 3225, Australia | 30288947 |  |  |  | Overheated connection |  |  |  | MFB reported sparking wire. Crew found HV centre phase cable head termination failed at LA bracket, made safe, minimal fire damage on ground. No reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | DDL012 | connection failure | Grassfire | 21/02/2020 9:48 | 1 | Localised: less than 10 sq.m | 15192 | Roadway |  | 20200225PWA_05 | Infrastructure (network-based) | -38.2667 | 144.6604 | 1 | Powercor | Report | 19205 | 0.0026285 | 22kV AC | Avalon Airport | 3225 | Queenscliff | Connection
TBA | 98 LANES ROAD, GELLIONDALE VIC 3971 | 2608195 | Working too close to overhead lines | [6 empty] | Tip truck in close proximity to 22kV conductor | Conductor (bare) | 0 | 0 | 0 |  | FTR23 | Tip truck came with about 1 metre of 22kV O/H conductors while tipping rock | No Go Zone (no contact) | 25/02/2020 15:44 |  |  | 15196 |  |  | 20200225SPN_04 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19217 | 0.030257 | 22kV AC | Moorabbin Airport | 3971 | Gelliondale | Vehicle
Fault crews attended the site to investigate. Upon inspection, it was identified that the krone box was burnt. MFB was on site but had left the scene when the crew arrived. The krone box was replaced and supply was restored. | 1090 WELLINGTON ROAD, ROWVILLE VIC 3178 | 3413682 |  |  |  | Overheated connection |  |  | 1 | UE received a call that there is no supply at the premise and there was a transformer fire up the road about 1 hour ago and the MFB attended. | Disconnector/isolator | 0 | 0 | 0 |  | FGY21 | The cause was a burnt out krone box. | Plant/equipment | 14/02/2020 18:15 | 1 | Negligible: no ground fire | 15208 | Commercial |  | 20200226UTD_01 | Infrastructure (network-based) | -37.9275 | 145.251 | 1 | United Energy Distribution | Report | 19475 | 0.03761 | Low voltage AC (<1kV) | Moorabbin Airport | 3178 | Rowville | Connection
Fault crews attended the site to investigate. Upon inspection, it was identified that the transformer on the pole substation had rusted and may have caused a LVI. LEI attended the site and confirmed evidence of LVI- Internal fault within the TX caused a LVI and caused switchboard and appliance damage to the single customer premise that it supplies. The transformer was replaced. | 37 DANDENONG STREET, DANDENONG VIC 3175 | 634953 |  |  |  | Corrosion |  |  | 1 | UE received a call from a customer that their appliances have been damaged and suspect it was caused by the electricity network. | Pole mounted | 0 | 0 | 0 |  | KBH31 | The cause was a internal fault within the transformer on the pole. | HV injection | 43984.5278 |  |  | 15209 | Residential |  | 20200226UTD_02 | Infrastructure (network-based) | -37.9937 | 145.1998 | 1 | United Energy Distribution | Report | 19417 | 0.0017014 | Low voltage AC (<1kV) | Moorabbin Airport | 3175 | Dandenong | AF Other
The crew have disconnected, removed and made safe the existing neutral screen overhead supply line The REC will be be calling Network Controllers to arrange an After Hours appointment. Customer is off supply. | 11 TOORADIN AVENUE, DALLAS VIC 3047 | A099663 | Unauthorised access | [5 empty] | 2 | Crews attended the above address today for a Truck Appointment for a customer 1phase - 1phase mains upgrade. When the crew arrived the Registered Electrical Contractor (REC) had already removed the service fuse, removed all the existing customer wiring and equipment and the distributors electricity meter. Unfortunately the RECâ€™s new installation did not comply where he has altered and modified a VESI approved raiser bracket by cutting and welding and making adjustments to the bracket himself and the LEI did not issue a Certificate of Electrical Safety (COES). | Conductor (insulated);Neutral screen;Smart meter;Customer wiring | 0 | 0 | 0 |  | BD07 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 28/02/2020 12:02 |  |  | 15226 | Residential |  | 20200228JEM_01 | Infrastructure (network-based) | -37.6656 | 144.9296 | 1 | Jemena | Report | 19259 | 0.019729 | Low voltage AC (<1kV) | Essendon Airport | 3047 | Dallas | Other
Jemena reported it to the ESV call centre (reference no. 13501591) and site was made safe. ESV Work Practices Advisor Robert Oldfield (0400 767 104) attended site before repairs were undertaken, spoke to relevant parties and obtained photos. Robert seized Jemena fuse boxes and customer cable. TechSafe Electrical Inspector Vescovi Venanzio attended site to investigate the electric shock and advised exposed deteriorated LV mains above veranda. Zinfra IMT Incident Manager Shawn Caines liaised with ESVâ€™s representative. The Zinfra crew found that the customerâ€™s consumer mains (Red Lead Cloth covered cable load side of the fuse box) entering the premise had deteriorated insulation exposing the active copper conductor. Zinfra made safe and issued a defect notice JEN 08896. Zinfra made repairs to remove the faÃ§ade mounted LV ABC out of the roofing gutter as the required clearances were not maintained, and forwarded photos to ESV at 10:36pm. Zinfra returned the following day and made further repairs | 310 HIGH STREET, PRESTON VIC 3072 |  |  |  |  | Unidentified customer fault |  | Phase to earth | 2 | On Friday 28/02/20, a Plumber received an electric shock from the consumerâ€™s unmetered LV mains while working above the shop veranda to making repairs as part of an insurance claim. The Plumber made contact with the bare active copper conductor as a result of deteriorated insulation. Zinfra faults crew received a call from the report room at approximately 2:30pm. The plumber was working on the iron sheets above canopy veranda of a shop. The plumber was working in close proximity of the above veranda network wiring when his knee came into contact with the bare copper conductor supplying the porcelain fuses feeding the installation. The insulation of the conductor had deteriorated, leaving the bare live conductor exposed. The person who received the shock was admitted to hospital over night for medical treatment as a precautionary measure. ESV spoke to the injured person Saturday morning while he was still in hospital experiencing some irregularities with his heart beat, he was improving and is now okay. In March 2015, Jemena had attended the property to install AMI smart meter and found exposed wiring under switchboard and main earth not on its correct terminal. There was a gap large enough that someone can put hands behind switchboard panel. A Level 2 defect was issued to the customer because of their unsafe installation but the customer has not done anything about it up until this incident occurred in February 2020. | Conductor (ABC) | 0 | 0 | 0 |  |  | Deteriorated insulation of LV Consumer Mains (above veranda wiring) | Medical attention (first aid/doctor/hospital) | 28/02/2020 13:50 |  |  | 15232 | Commercial |  | 20200228JEM_02 | Infrastructure (customer connection) | -37.7415 | 145.0014 | 1 | Jemena | Report | 19311 | 0.031692 | Low voltage AC (<1kV) | Essendon Airport | 3072 | Preston | OH Cable
On arrival crew isolated supply and arranged repairs | 58 Barclay St, Heywood VIC 3304, Australia | 32125133 |  |  |  | Leakage |  |  |  | Customer reported seeing flames coming from top of pole and sparks falling to the ground into paddock. On arrival, the crew identified the centre phase bridging insulator has burnt through the pole. No ground fire was evident (wet ground), no damage to property, no shocks or injuries reported. | Pole (wood) | 2 | 2 | 2 |  | PLD001 | Excessive leakage current | Pole-top fire | 26/02/2020 5:47 | 1 | Negligible: no ground fire | 15233 | Roadway |  | 20200302PWA_01 | Infrastructure (network-based) | -38.1362 | 141.6188 | 1 | Powercor | Report | 19268 | 0.0099109 | 22kV AC | Portland (Cashmore Airport) | 3304 | Heywood | AF Other
Site made safe and information gathered for reporting to ESV | 8 BLENHEIM ROAD, NEWPORT VIC 3015 | A080774 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crew attended the above address today with an alteration service order (100101273655) to remove an existing 1ph OH supply and metering and convert to a 3-phase UG supply and metering (NMI 6001120797). When the crew arrived they found the existing building had been demolished, no overhead service line, a newly constructed building and the existing 1 phase meter sitting inside the new 3 phase switchboard metering enclosure. | Conductor (ABC);Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | NT03 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43864.6764 |  |  | 15243 | Residential |  | 20200303JEM_01 | Infrastructure (network-based) | -37.8471 | 144.8635 | 1 | Jemena | Report | 19282 | 0.0025382 | Low voltage AC (<1kV) | Laverton Raaf | 3015 | Newport | Other
Crew dispatched. Site made safe. Fuse replaced and restored supply. | 75 PALMER ROAD, JINDIVICK VIC 3818 | 2718060 |  |  |  | Candled fuse |  |  |  | Candled fuse at Palmer P003 substation 6K BA pole #2718060. | Boric acid | 0 | 0 | 0 |  | WGL24 | Candled fuse. | Pole-top fire | 19/02/2020 16:57 | 1 | Negligible: no ground fire | 15253 |  |  | 20200303SPN_02 | Infrastructure (network-based) | -38.0112 | 145.9131 | 1 | AusNet Services Distribution | Report | 19294 | 0.015293 | 22kV AC | Morwell (Latrobe Valley Airport) | 3818 | Jindivick | Fuse
Crew made safe by removing and replacing this fuse and restore supply. No fire. | BELLBIRD HOTEL, 3872 PRINCES HIGHWAY, BELLBIRD CREEK VIC 3889 | 1910588 |  |  |  | Candled fuse |  |  |  | fuse candling. Crew arrived onsite and observed burnt/candled BA fuse at LIs NO 1910588 | Boric acid | 0 | 0 | 0 |  | CNR3 | Candled 6A BA fuse | Pole-top fire | 43893.6194 | 1 | Negligible: no ground fire | 15254 |  |  | 20200303SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19296 | 0.038875 | 22kV AC | Moorabbin Airport | 3872 | Bellbird Creek | Fuse
tba | 2 MURRAY ROAD, YALLOURN NORTH VIC 3825 | 2216471 |  |  |  | Defective component |  |  |  | LV WIRE FOUND ON THE GROUND | Conductor (bare) | 0 | 0 | 0 |  | MOE14 | UNDER INVESTIGATION | Loss of supply | 26/01/2020 11:00 |  |  | 15255 |  |  | 20200303SPN_04 | Infrastructure (network-based) | -38.1178 | 144.9177 | 2 | AusNet Services Distribution | Notification | 19297 | 0.024744 | Low voltage AC (<1kV) | Moorabbin Airport | 3825 | Yallourn North | Conductor
On arrival crew isolated supply and carried out repairs | 47 HEATH STREET, RED CLIFFS VIC 3496 | 31019780 |  |  |  | Leakage |  |  |  | Customer advised pole outside is on fire. CFA attended and extinguished fire. On arrival crew found pole had been on fire near the king bolt position. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | RCT022 | Excessive leakage current | Pole-top fire | 43924.2326 | 1 | Negligible: no ground fire | 15270 | Roadway |  | 20200305PWA_03 | Infrastructure (network-based) | -34.3104 | 142.1899 | 1 | Powercor | Report | 19315 | 0.033252 | 22kV AC | Mildura Airport | 3496 | Red Cliffs | Pole
Referred to ESV, determining action in consultation with ESV/Worksafe | 15 AMESS STREET, CARLTON NORTH VIC 3054 | 30182123 | Working too close to overhead lines | [5 empty] | 2 | Tiger tails (battens) have been installed by a third party (not CitiPower) and a scaffold has been erected without a permit to work. | Service cable (insulated) | 0 | 0 | 0 |  | BQ022 | Interference | No Go Zone (contact) | 43985.4792 |  |  | 15276 | Residential |  | 20200306PWA_01 | Infrastructure (network-based) | -37.7874 | 144.9734 | 1 | CitiPower | Notification | 19325 | 0.024369 | Low voltage AC (<1kV) | Essendon Airport | 3054 | Carlton North | Other
Crew dispatched to investigate. Site made safe and pole was replaced. | 401 GREENSBOROUGH ROAD, WATSONIA VIC 3087 | 904031 |  | Lightning | [5 empty] | Received report for pole top fire. Crew dispatched found broken pole resulting in pole top fire. | Pole (wood) | 0 | 0 | 0 |  | WT13 | Pole was hit by lightning on a stormy day resulting in broken pole. | Pole-top fire | 43985.7035 | 1 | Negligible: no ground fire | 15278 | Public space |  | 20200306SPN_01 | Infrastructure (network-based) | -37.7126 | 145.0828 | 1 | AusNet Services Distribution | Report | 19331 | 0.024672 | 22kV AC | Essendon Airport | 3087 | Watsonia | Pole
Inspector arrived and conducted tests and identified a Neutral fault. Inspector called the OH fault truck to attend and investigate the pole end. The service was replaced and all tests conducted after the service was replaced with results within code. | 86 SURF PARADE, INVERLOCH VIC 3996 | 2810231 |  |  |  | Neutral fault |  |  |  | Electric Shock from tap. | POA connection (network side) | 0 | 0 | 0 |  | WGI31 | Faulty neutral connection between installation overhead to ABC LV span. | Minor shock | 24/01/2020 21:00 |  |  | 15290 | Residential |  | 20200310SPN_06 | Infrastructure (network-based) | -38.6451 | 145.7101 | 1 | AusNet Services Distribution | Report | 19371 | 0.014792 | Low voltage AC (<1kV) | Morwell (Latrobe Valley Airport) | 3996 | Inverloch | Connection
Candled HV fuse at LIS 516186. Caused by a bird. Isolated transformer LV and HV. Replaced candled fuse and closed transformer back into service. | 40 HOBSON ROAD, RYTHDALE VIC 3810 | 516186 |  | Bird | [5 empty] | Candled BA fuse | Boric acid | 0 | 0 | 0 |  | PHM22 | Bird Incident | Pole-top fire | 13/03/2020 12:00 | 1 | Negligible: no ground fire | 15302 |  |  | 20200313SPN_01 | Infrastructure (network-based) | -38.1467 | 145.4585 | 1 | AusNet Services Distribution | Report | 19369 | 0.040837 | 22kV AC | Moorabbin Airport | 3810 | Rythdale | Animal
On arrival crew isolated supply and carried out repairs. LEI aattended to test for HVI, which was confirmed. | 501 Sherrard St, Black Hill VIC 3350, Australia | 32012126 |  |  |  | Leakage |  |  |  | A crossarm fire resulted in the high voltage conductor falling with the insulator coming to rest on the low voltage x arm . There was reported to be a HVI. There was no ground fire, no reported injuries. | Crossarm (wood) | 2 | 2 | 2 |  | BAN007 | Excessive leakage current | Pole-top fire;HV injection | 13/03/2020 20:31 | 1 | Negligible: no ground fire | 15308 |  |  | 20200316PWA_03 | Infrastructure (network-based) | -37.5518 | 143.8686 | 1 | Powercor | Report | 19378 | 0.033123 | Low voltage AC (<1kV);22kV AC | Ballarat Aerodrome | 3350 | Black Hill | Crossarm
Faults crew attended the site to investigate. Upon inspection, it was identified that the service wire was damaged. The service wire was replaced and supply was restored. | 4 HASLEMERE ROAD, MITCHAM VIC 3132 | 7036943 | Working too close to overhead lines | [5 empty] | 1 | UE received a call that a customer has hit the service wire with a hedge trimmer, causing a flash and severing part of the wire. There is no supply. | Service cable (insulated) | 0 | 0 | 0 |  | RWT24 | The person was working too close to the service line | Loss of supply;No Go Zone (contact) | 44046.4861 |  |  | 15314 | Residential |  | 20200318UTD_02 | Infrastructure (network-based) | -37.8251 | 145.1919 | 1 | United Energy Distribution | Report | 19384 | 0.030387 | Low voltage AC (<1kV) | Moorabbin Airport | 3132 | Mitcham | Other
On arrival crew isolated supply and carried out repairs | 1 BICKHAMS COURT, ST KILDA EAST VIC 3183 | 30219586 | Working too close to underground cables | [6 empty] | REC reported that digger had hit and underground service at the incident location. There was no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | BC012 | While installing other assets digger struck underground service cable | No Go Zone (contact) | 13/03/2020 12:40 |  |  | 15329 | Residential |  | 20200319PWA_10 | Infrastructure (customer connection) | -37.8686 | 145.003 | 1 | CitiPower | Report | 19403 | 0.021865 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | St Kilda East | Dug up
Immediate Actions â€¢ Memo to be communicated to all stakeholders reinforcing the NGZ requirements. â€¢ Network Owner/Zinfra to review a sample of recent PTWâ€™s that have been issued to identify if there are any other instances where PTWâ€™s are in conflict with the Scope of work, conditions, Instructions and that works are compliant JEM /Work Safe NGZ Procedures. â€¢ Following self-reporting by the Jemena Project team, The Work Practices Manager reported the NGZ breach in March to Energy Safe Victoria and recorded the incidents in OSIRIS. Energy Safe have visited the site and met with CPBJH as result of the March incident. â€¢ An incident report is to be provided by Jemena Work Practices overview of the incidents. Underground faults crew attended after call from Control Room, took photos and made site safe Jemena Works Practices reported the incident to ESV and have undertaken a formal investigation (see attachment) A number of corrective actions to prevent a recurrence have been identified and will be completed. | 57 WEMBLEY AVENUE, YARRAVILLE VIC 3013 | A133136 | Working too close to underground cables | [5 empty] | 2 | On Thursday 12 March 2020 Jemena was advised of a No Go Zone breach where civil workers from the West Gate Tunnel project as part of Package 2, undertook a large excavation to install a storm water drain under the HV feeder cable and left the Live HV cable suspended as shown in the pictures attached. | Cable | 0 | 0 | 0 |  | FE5 | No Go Zone breach | No Go Zone (no contact) | 44168.8222 |  |  | 15342 | Construction |  | 20200320JEM_01 | Infrastructure (network-based) | -37.8241 | 144.8734 | 1 | Jemena | Report | 19822 | 0.031259 | 22kV AC | Essendon Airport | 3013 | Yarraville | Dug up
Section of LV and HV was isolated to make safe for repair of HV conductors | 270 SUSSEX STREET, PASCOE VALE VIC 3044 | A034909 | Vehicle | [5 empty] | 1 | Vehicle impact to pole caused CN5 22kV Feeder Circuit Breaker to open to lockout. 2 HV conductors down, no HV injection. Secondary fault - burnt off HV bridges on HV isolators which are also currently under Access Permit and getting repaired. | Conductor (bare);Dropper/bridge | 0 | 0 | 0 |  | CN5 | Vehicle impact into pole | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 20/03/2020 17:34 |  |  | 15348 | Residential |  | 20200320JEM_02 | Infrastructure (network-based) | -37.7211 | 144.9514 | 1 | Jemena | Report | 19432 | 0.02472 | 22kV AC | Essendon Airport | 3044 | Pascoe Vale | Vehicle
Following a thorough damage assessment of installations the attending LEI was able to identify that the properties had been affected by a HV injection. At this stage all the properties were isolated from supply. Once the supply to the arterial lines of the affected circuit was returned to supply attending electrical inspectors visited all affected properties and issued cards for all properties attended for damage, no access and no damage also. At the time of writing, three properties remain off supply due to no access. | 50 BRIDGEWATER ROAD, CRAIGIEBURN VIC 3064 | A022025 | Vehicle | [5 empty] | 1 | The attending Licensed Electrical Inspector (LEI) was informed by witnesses that a garbage collection truck (Tip Truck with crane) had made contact with the overhead powerlines on Bridgewater Rd (corner Axminster Drive opposite no. 50 Bridgewater Rd) due to the truck driving with its forks in the up position. The forks of the trucks came in contact with the HV and LV conductors simultaneously resulting in a HV injection into the LV circuit. No damage to conductors. | Conductor (bare) | 0 | 0 | 0 |  | ST32 | Third party vehicle (in driving mode) impact with LV and HV conductors | HV injection;Loss of supply | 20/03/2020 10:38 |  |  | 15349 | Residential |  | 20200320JEM_03 | Infrastructure (network-based) | -37.6035 | 144.9289 | 1 | Jemena | Report | 19712 | 0.0139 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3064 | Craigieburn | Vehicle
Crew replaced the existing O/H Service Cable | 32 PARK STREET, WENDOUREE VIC 3355 | 30013980 |  |  |  | Corrosion |  |  |  | person was in the Bathroom showering when she received an electric shock as she made simultaneous contact between her hand on the metallic Shower tap and her bare feet while standing on the wet shower base and waste water outlet. | Service cable (insulated) | 0 | 0 | 0 |  | BAN001 | Corroded O/H Service Neutral Conductor termination at the Reticulation Service Pole. | Minor shock | 18/12/2019 8:00 |  |  | 15341 | Residential |  | 20200320PWA_04 | Infrastructure (network-based) | -37.5359 | 143.8257 | 1 | Powercor | Report | 19425 | 0.019336 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3355 | Wendouree | Connection
Fault crew re-made a loose and corroded termination | 58 WOODLANDS DRIVE, OCEAN GROVE VIC 3226 | 32077447 |  |  |  | Corrosion;Neutral fault |  |  |  | Person was standing barefoot on wet concrete path, adjacent outside shower attached to the rear of the house. He received a minor tingle to his wet right hand whilst adjusting the shower tap | Services cable | 0 | 0 | 0 |  | DDL011 | Loose and corroded in neutral terminal of FOLCB on pole. | Minor shock | 20/12/2019 19:00 |  |  | 15344 | Residential |  | 20200320PWA_06 | Infrastructure (network-based) | -38.2571 | 144.5337 | 1 | Powercor | Report | 19428 | 0.025749 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Crew replaced the existing O/H service cable from the pole to new FOLCB installed by REC | 25 BILSON STREET, COLAC VIC 3250 | 32064494 |  |  |  | Overheated connection |  |  |  | person was in the rear yard turning on the external garden tap when he received an electric shock as she made simultaneous contact between her hand on the metal tap and her bare feet while standing on the wet ground. | POA connection (customer side) | 0 | 0 | 0 |  | CLC002 | FOLCB Defective | Minor shock | 29/12/2019 22:00 |  |  | 15345 | Residential |  | 20200320PWA_07 | Infrastructure (customer connection) | -38.331 | 143.5688 | 1 | Powercor | Report | 19429 | 0.0041586 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3250 | Colac | Connection
Isolated in pit. CFA extinguished fire. Notification raised to replace with new. | VISY BOARD, 299 MCKOY STREET, WEST WODONGA VIC 3690 | 5652435 |  |  |  | Overheated connection |  |  |  | Street light head on fire | Public lighting | 0 | 0 | 0 |  | WO13 | Deterioration of connection. | Pole-top fire | 19/03/2020 20:54 | 1 | Negligible: no ground fire | 15337 |  |  | 20200320SPN_01 | Infrastructure (network-based) | -36.106 | 146.8319 | 1 | AusNet Services Distribution | Report | 19419 | 0.035166 | Low voltage AC (<1kV) | Wangaratta Aero | 3690 | West Wodonga | AF Other
The REC has advised that he has a truck appointment booked for 19 March 2020. Jemena Portal confirms that this is the case. Metering & Servicing crew attended 19 March 2020 for the 9.30am Truck Appointment REC did not attend Truck Appointment. Customer and LEI on site called REC. REC arrived on site at 10.15am LEI did not certify the installation and provide a COES. REC needs to install a 900mm raiser bracket to increase service heights over customer driveway to maximum height. Customer still off supply. REC and customer will call Network Connections for an After Hours appointment. A new COES is required. | 55 GWELO STREET, WEST FOOTSCRAY VIC 3012 | A142485 | Unauthorised access | [5 empty] | 2 | Jemena Compliance Officer Jason Ford received a phone call and attached photos from a Techsafe Licensed Electrical Inspector who is currently on site for a prescribed inspection and he has advised that the REC has disconnected the existing supply by removing the service fuse, removing the existing Jemena metering equipment and the existing customer consumer mains are currently just hanging from the wall exposed and unterminated (reinserting the service fuse will make these live). The Compliance Officer believes the REC has made this installation unsafe and a Faults crew needs to attend to disconnect supply and make safe and issue a Level 1 defect. | Smart meter;Service cable (insulated);Customer wiring | 0 | 0 | 0 |  | TH11 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 18/03/2020 14:33 |  |  | 15360 | Residential |  | 20200324JEM_02 | Infrastructure (network-based) | -37.8015 | 144.8626 | 1 | Jemena | Report | 19446 | 0.010331 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Other
â€¢ NGZ Assessor Allen McKee and Team Leader Brian Smith attended site and found the 22kV direct buried cable had been uncovered and was sitting on top of rocks and not covered at all. â€¢ A worker was in the trench still cleaning the trench out, Brian told him to cease work and get out of the trench. â€¢ Brian Smith spoke to the Project Manager, Leigh Delongville and informed him to cease all works in the vicinity of the trench immediately and to barricade the trench and install signs saying 'No Entry' until this is all sorted out. He agreed and confirmed this with an email. â€¢ Brian Smith contacted the Control Room and reported the No Go Zone breach. â€¢ Control room contacted Sam Sozzi to attend site and assess the cable condition. | 265 DUKE STREET, SUNSHINE NORTH VIC 3020 | A104678 | Working too close to underground cables | [5 empty] | 2 | No Go Zone breach involving dig up of HV underground cable, details are as follows: â€¢ The third party civil contractors were installing a gas pipe for Ausnet/Downer and have opened a trench where a 22kV Direct buried cable was installed. â€¢ The contractors had been dealing with Gerry Mendez and Reynold Bangayan from Jemena prior to this breach where 22kv cables were joined and terminated, which are the same 22kv cable as the one in the attached photos. â€¢ The contractors were informed by Gerry before they started, that if they kept 500mm away from the 22kV buried cable and installed a timber wall in their trench, then they would be ok and didnâ€™t need to contact Jemena. â€¢ Once the contractors started digging and located the cable, they contacted Reynold who informed the contactors the Jemena No Go Zone team. â€¢ The contractor contacted the No Go Zone Team on Tuesday 23rd March. â€¢ It appears they have not followed what Gerry instructed and didnâ€™t install a timber barricade, hence the reason the wall collapsed. | Cable | 2 | 2 | 2 |  | BY11 | No Go Zone breach | No Go Zone (no contact) | 26/03/2020 10:08 |  |  | 15371 | Roadway |  | 20200326JEM_01 | Infrastructure (network-based) | -37.7669 | 144.8496 | 1 | Jemena | Report | 19458 | 0.0096887 | 22kV AC | Essendon Airport | 3020 | Sunshine North | Dug up
Site made safe and incident reported to ESV | 24 RYLANDES DRIVE, GLADSTONE PARK VIC 3043 | A056132 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crew attended the address today with an abolishment Supply Order to abolish 1 phase overhead service line and meter. When the crew arrived the existing house was already demolished with the overhead service line and meter already removed and no longer on site. | Aluminium;Aluminium twisted (grey);Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | AW9 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 25/03/2020 12:42 |  |  | 15373 | Residential |  | 20200326JEM_02 | Infrastructure (network-based) | -37.6844 | 144.8849 | 1 | Jemena | Report | 19461 | 0.0093241 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Gladstone Park | Other
MADE SAFE AND RESTORED SUPPLY | 28 METERY ROAD, ELTHAM VIC 3095 | 921885 |  |  |  | Candled fuse |  |  |  | CANDLED FUSE, HV ON DECK | Conductor (bare) | 0 | 0 | 0 |  | ELM34 | CANDLED FUSE. UNDER INVESTIGATION. | Pole-top fire | 24/03/2020 2:50 | 1 | Negligible: no ground fire | 15372 |  |  | 20200326SPN_01 | Infrastructure (network-based) | -37.7271 | 145.1492 | 1 | AusNet Services Distribution | Notification | 19459 | 0.00011111 | 22kV AC | Essendon Airport | 3095 | Eltham | Fuse
Site made safe. CB locked out. | 453 SHANLEY STREET, WANGARATTA SOUTH VIC 3678 | 5104064 | [7 empty] | FIRE IN VICINITY OF APPARATUS | Yet to be determined | 0 | 0 | 0 |  | WN4 | TBA | Bushfire | 25/03/2020 8:00 | 1 | Localised: less than 10 sq.m | 15374 |  |  | 20200326SPN_02 | Infrastructure (network-based) | -36.3695 | 146.2373 | 1 | AusNet Services Distribution | Notification | 19462 | 0.015027 | 22kV AC | Wangaratta Aero | 3678 | Wangaratta South | AF Other
Crew made site safe | 393 PASCOE VALE ROAD, STRATHMORE VIC 3041 | A111530 | Unauthorised access | [5 empty] | 2 | Property has had wiring done, near meter hinged panel. REC had removed tails from FOLCB and left them live over the live service line. REC made the mistake of assuming that the service was disconnected from the service pole, and disconnected the overhead service line from the point of attachment. REC had no idea that the disconnection of this service was in fact "live", nor was he aware that this work was illegal at the time he carried this out. REC accepts full responsibility and any consequences, refer to email attachment | Aluminium twisted (XLPE);Connection box;Service cable (insulated) | 2 | 2 | 2 |  | NS17 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/03/2020 15:54 |  |  | 15382 | Residential |  | 20200327JEM_01 | Infrastructure (customer connection) | -37.7382 | 144.927 | 1 | Jemena | Report | 19473 | 0.028097 | Low voltage AC (<1kV) | Essendon Airport | 3041 | Strathmore | Other
Crews attended, isolated supply, made the site safe and performed repairs | 65-69 KYLE ROAD, ALTONA NORTH VIC 3025 | 32198802 |  |  |  | Leakage |  |  |  | MFB reported powerlines down and wires were sparking. On arrival the crew found that multi circuit pole BLTS-NT Pole 6 (LIS-957045) had a pole fire mid way up the pole causing the top section to fall over but remain in the air. Two cars were reported as having damage caused by small pieces of molten aluminium and pieces of charcoal. There were no reported injuries, HVI or ground fire. | Pole (wood) | 2 | 2 | 2 |  | BLT020 | Excessive leakage current | Pole-top fire | 26/03/2020 11:45 | 1 | Negligible: no ground fire | 15378 | Roadway |  | 20200327PWA_01 | Infrastructure (network-based) | -37.8264 | 144.8574 | 1 | Powercor | Report | 19469 | 0.014855 | 22kV AC;66kV AC | Laverton Raaf | 3025 | Altona North | Pole
Faults crew attended the site to investigate. Upon inspection, it was identified that the LV cable termination inside the LV pillar blew up. The site was isolated and made safe. The termination was repaired. | 8 NICHOLSON CLOSE, ENDEAVOUR HILLS VIC 3802 | 638519 |  |  |  | Overheated connection |  |  | 1 | UE received a call from a customer who has been away for a couple weeks and upon their return, has noticed the service box on the front yard appears to have self-ignited/caught fire during the time he was away. There were blackened char marks on his fence next to it. | LV Pillar | 0 | 0 | 0 |  | LD2 | the cause is likely to be a loose connection which overheated. | Grassfire | 17/03/2020 2:30 | 1 | Localised: less than 10 sq.m | 15380 | Roadway |  | 20200327UTD_02 | Infrastructure (network-based) | -37.9746 | 145.2489 | 1 | United Energy Distribution | Report | 19471 | 0.015486 | Low voltage AC (<1kV) | Moorabbin Airport | 3802 | Endeavour Hills | Connection
Site was made safe by cutting back tails at service fuses. Underground crew to return and conduct repairs | 875 MICKLEHAM ROAD, GREENVALE VIC 3059 | A044599 | Copper theft | [5 empty] | 2 | Off shift linesman was driving past and noticed copper conductor swinging in breeze and looks like it is an attempted copper theft job. Pole type substation Somerton Rd-P83A is only feeding this customer, but the premises are currently vacant. | Services cable | 0 | 0 | 0 |  | COO11 | Copper theft | Damage to network assets | 29/03/2020 18:53 |  |  | 15383 | Roadway |  | 20200330JEM_01 | Infrastructure (network-based) | -37.6348 | 144.8809 | 1 | Jemena | Report | 19474 | 0.01692 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
The attending Jemena Fault Crew replaced the grey twisted over head service. Following this the attending Licensed Electrical Inspector (LEI) conducted further voltage tests between an independent earth and various parts of the electrical installation including distribution assets, which now recorded a reading of 0.9 volts AC. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 35 STATION STREET, CLARKEFIELD VIC 3430 | A038310 |  |  |  | Neutral fault |  | Phase to earth | 2 | Ms. Jeanette Freeman received an electric shock to her hand when she made contact with the kitchen sink. Ms Freeman also reported lights dimming and appliances not functioning correctly in the days leading up to the incident. Voltage tests from an independent earth to various parts of the electrical installation including distribution assets identified a broken neutral service conductor at the connection point to the overhead ABC reticulation line. The condition caused current to flow through the installation MEN connection, the main earthing conductor, and conductive parts of the electrical installation. The increased impedance to the flow of the installation return current through the general mass of earth was sufficient to cause a voltage rise of 27.0 Volts AC between points of contact. | Conductor (ABC);Service cable (insulated);Customer appliance | 0 | 0 | 0 |  | MISC | Broken neutral service conductor at the connection point to the overhead ABC reticulation line | Minor shock | 30/03/2020 11:35 |  |  | 15386 | Residential |  | 20200330JEM_03 | Infrastructure (customer connection) | -37.4831 | 144.7484 | 1 | Jemena | Report | 19478 | 0.041377 | Low voltage AC (<1kV) | Melbourne Airport | 3430 | Clarkefield | Connection
Powercor ordered all works on site to stop until risk assessment of the damage wall of Indoor Substation is completed. | 140-146 KING STREET, MELBOURNE VIC 3000 | 33111959 | Unauthorised work | [6 empty] | City Circle Demolition reported their excavator had hit an indoor substation wall at the above incident location. On arrival, the crew found significant damaged to an indoor substation wall by the excavator. Fortunately, there was no damaged to any internal electrical equipment but was very close the switchgear. There was no reported injuries. | Indoor | 2 | 2 | 2 |  | JA027 | Demolition works | Damage to network assets | 27/03/2020 15:30 |  |  | 15384 | Construction |  | 20200330PWA_01 | Infrastructure (network-based) | -37.8165 | 144.9563 | 1 | CitiPower | Report | 19476 | 0.025417 | Not applicable | Essendon Airport | 3000 | Melbourne | Vehicle
Crew made site safe and organised repairs. | Aitken Boulevard Roxburgh Park (behind 9 ADELIE COURT, ROXBURGH PARK VIC 3064) | A141395 | Copper theft | [5 empty] | 2 | Copper theft on Aitken Blvd, North of Somerton Rd, and South of Silvester Parade impacting street lights only. Between poles A141395 and A141394 (5 bays, approximately 80 metres each, of 50mm 4 core cable). No customers off supply. | Cable | 0 | 0 | 0 |  | COO11 | Copper theft | Damage to network assets | 30/03/2020 10:00 |  |  | 15396 | Roadway |  | 20200331JEM_01 | Infrastructure (network-based) | -37.6348 | 144.9111 | 1 | Jemena | Report | 19489 | 0.027286 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Roxburgh Park | Other
Replaced damaged equipment and surge diverters. Non-standard surge diverters upgraded to current design | 7 AMCOR WAY, CAMPBELLFIELD VIC 3061 | A025498 | Vandalism | [5 empty] | 2 | Pole mounted substation (AMCOR-JESICA) vandalised, chain has been thrown to the top of transformer and red phase HV fuse blown. | Boric acid;Pole mounted;Surge diverter | 0 | 1 | 0 |  | ST34 | Vandalism | Damage to network assets | 28/02/2020 6:33 |  |  | 15408 | Industrial |  | 20200331JEM_02 | Infrastructure (network-based) | -37.6568 | 144.9588 | 1 | Jemena | Report | 19502 | 0.011081 | 22kV AC | Essendon Airport | 3061 | Campbellfield | Other
advised ESV Crew instructed to continue with service height works and remove attachment, Advise customer this is breach and may be followed up by regulator | 29 HITCHCOCK STREET, BREAKWATER VIC 3219 | 32068368 | Unauthorised work | [5 empty] | 2 | Crew preparing for service height rectification works found floodlight had been installed in tree with flexible 3 core lead cable tied along service cable. | Conductor (insulated) | 0 | 0 | 0 |  | GLE011 | Interference by third party | No Go Zone (contact) | 30/03/2020 14:00 |  |  | 15391 | Residential |  | 20200331PWA_02 | Infrastructure (network-based) | -38.1787 | 144.3772 | 1 | Powercor | Report | 19521 | 0.016719 | Low voltage AC (<1kV) | Avalon Airport | 3219 | Breakwater | Other
LEI's were dispatched to the area following reports of customer appliance & equipment damage. 104. accounts off Substation were left off supply awaiting LEI checks. only minor equipment damage found in a number of houses at the time of this report | 13 DUNDUNDRA DRIVE, CLIFTON SPRINGS VIC 3222 | 30061500 |  | Lightning | [5 empty] | During a lightning storm DDL022 experienced a number of successful auto reclosers. Shortly after Powercor started to receive calls from customers, particularly in Dundundra Dr, of appliance and equipment damage in their homes due to a power surge. When crews arrived they found evidence of a lighting strike on Dundundra Dr P4. There was no fire or reported injuries | Conductor (bare) | 2 | 2 | 2 |  | DDL022 | Lightning strike on assets | HV injection | 29/03/2020 13:43 |  |  | 15392 | Roadway |  | 20200331PWA_03 | Infrastructure (network-based) | -38.1523 | 144.5795 | 1 | Powercor | Report | 19485 | 0.038921 | Low voltage AC (<1kV);22kV AC | Avalon Airport | 3222 | Clifton Springs | Lightning
REPLACED FUSE | 1839 Euroa-Mansfield Rd | 3918898 |  |  |  | Candled fuse |  |  |  | CANDLED FUSE | Any other type | 0 | 0 | 0 |  | BN1 | CANDLED FUSE | Pole-top fire | 30/03/2020 19:55 | 1 | Negligible: no ground fire | 15415 |  |  | 20200401SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19514 | 0.0034549 | 22kV AC | Moorabbin Airport |  |  | Fuse
REPLACED FUSE | 30 SHIELDS ROAD, LUCKNOW VIC 3875 | 1612084 |  |  |  | Candled fuse |  |  |  | FUSE CANDLED | Any other type | 0 | 0 | 0 |  | BD225 | CANDLED FUSE | Pole-top fire | 43834.2292 | 1 | Negligible: no ground fire | 15417 |  |  | 20200401SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19518 | 0.033788 | 22kV AC | Moorabbin Airport | 3875 | Lucknow | Fuse
On arrival crew isolates supply. substation no longer in service so HV span removed. | 169 Todd Rd, Port Melbourne VIC 3207, Australia | 300196752 |  |  |  | Corrosion |  |  |  | Following HV fdr FB20 tripping to lockout a line patrol was initiated. On arrival crew found a one phase of a HV span on the ground. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | FB020 | Conductor pre formed wrap on corroded | Damage to network assets | 43865.0813 |  |  | 15420 | Roadway |  | 20200402PWA_02 | Infrastructure (network-based) | -37.8284 | 144.912 | 1 | CitiPower | Report | 19528 | 0.0012836 | 11kV AC | Essendon Airport | 3207 | Port Melbourne | Conductor
On arrival crew arranged isolating and earthing of cables. Testing to be arranged and repairs organised. | 217 Canning St, Carlton VIC 3053, Australia | 30179787 | Working too close to underground cables | [6 empty] | Report of excavator damaging HV cable conduits, cable damage to be determined by test. BQ042 & BQ51 HV cables isolated and earthed awaiting testing. There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | BQ042 | Excavator damaged conduits | No Go Zone (contact);Damage to network assets | 43865.4701 |  |  | 15426 | Roadway |  | 20200403PWA_01 | Infrastructure (network-based) | -37.7932 | 144.9735 | 1 | CitiPower | Report | 19535 | 0.041666 | 11kV AC | Essendon Airport | 3053 | Carlton | Vehicle
On arrival crew arranged isolation and carried out repairs. | 14 BELL STREET, HEYWOOD VIC 3304 | 3026900 |  |  |  | Leakage |  |  |  | A powercor crew attending a fault located a pole fire at the incident location. The pole was half burnt through at the crossarm brace position. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | PLD003 | Excessive leakage current | Pole-top fire | 43894.3125 | 1 | Negligible: no ground fire | 15434 | Roadway |  | 20200406PWA_01 | Infrastructure (network-based) | -38.1236 | 141.6372 | 1 | Powercor | Report | 19543 | 0.015556 | 22kV AC | Portland (Cashmore Airport) | 3304 | Heywood | Pole
On arrival crew arranged isolation and CFA. pole replaced | 78 Gum Lagoon Rd, Gunbower VIC 3566, Australia | 32033196 |  |  |  | Leakage |  |  |  | Following an all supply failure, a crew found a pole fire at incident location. NAO arranged for CFA to attend to extinguish fire. There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | CHA005 | Excessive leakage current | Pole-top fire | 43865.084 | 1 | Negligible: no ground fire | 15435 | Agricultural |  | 20200406PWA_02 | Infrastructure (network-based) | -35.9281 | 144.3658 | 1 | Powercor | Report | 19544 | 0.006331 | 22kV AC | Bendigo Airport | 3566 | Gunbower | Pole
Site was made safe and in hand with maintenance to have underground cable repaired | CORNER OF AITKEN BLVD AND SOMERTON ROAD, GREENVALE VIC 3059 | A141394 and A141395 | Copper theft | [5 empty] | 2 | Copper theft of underground cable between pole A141394 and A141395 | Cable;Copper | 0 | 0 | 0 |  | COO11 | Copper theft | Damage to network assets | 44078.3465 |  |  | 15443 | Roadway |  | 20200409JEM_01 | Infrastructure (network-based) | -37.6371 | 144.9104 | 1 | Jemena | Report | 19560 | 0.018495 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Other
BA Fuse Barrell Replaced - Supply Restored | 101 STANLEYS ROAD, RED HILL SOUTH VIC 3937 | 1318468 |  |  |  | Candled fuse |  |  | 0 | RPh BA at RB0510 was found broken in 1/2 with obvious signs of candling... Replaced barrell... LIS#1318468... 1Ph supply. | Boric acid | 1 | 0 | 0 |  | DAM13 | B?A Fuse did not operate correctly resulting in the "Barrell" melting | Pole-top fire | 17/03/2020 12:15 | 1 | Negligible: no ground fire | 15444 | Agricultural |  | 20200409UTD_02 | Infrastructure (network-based) | -38.3746 | 145.0514 | 1 | United Energy Distribution | Report | 19562 | 0.03827 | 22kV AC | Moorabbin Airport | 3937 | Red Hill South | Fuse
Tree Branch removed - Supply restored | 46 LOWER DANDENONG RD MENTONE VIC 3194, | 1822639 |  | Blown branch/vegetation |  |  |  |  | 1 | Tree branch from #46 Lower Dandenong Rd fell over HV conductors. Secondary damage to Bph HV isol at CH6334. MFB reported a fire | Conductor (bare) | 0 | 0 | 0 |  | M33 | Vegetation Limb Failure | Other vegetation | 43924.0778 | 1 | Localised: less than 10 sq.m | 15445 | Residential |  | 20200409UTD_03 | Infrastructure (network-based) | -37.9831 | 145.08 | 1 | United Energy Distribution | Report | 19563 | 0.033072 | 11kV AC | Moorabbin Airport | 3194 |  | Trees
The Faults crew disconnected and removed the overhead service line, made safe the installation and issued a level 1 defect on site. The REC and customer now have to complete their customer initiated works to satisfy current standards and provide a prescribed COES (i.e. a new raiser, FOLCB and mains will now need their old meter panel and fuse board also upgraded) | 30 WINIFRED STREET, ESSENDON VIC 3040 | A115817 | Unauthorised access |  |  |  | Unauthorised REC work |  | 2 | Jemena/Zinfra Faults crew attended site and when they arrived they found the Jemena overhead service line has been cut and disconnected live from the point of supply and consumers terminals and the customer mains disconnected and removed and a new raiser bracket, FOLCB and customer mains installed. Shortly after the crew arriving an REC arrived at the property. Jemena/Zinfra compliance officer (Jason Ford) spoke to the REC on the phone and when asking the REC why has this all occurred, the REC openly admitted that he cut and disconnected the the distribution assets because the owner wanted the connection off the fascia and a new raiser bracket installed. The REC also openly admitted that there was no fault on the installation and the property was on supply without issue. The REC had no reason or explanation for doing what he did. The Control Room had advised the Faults crews that the REC had called Jemena recently enquiring about a service/mains upgrade. Faults crew advised that the overhead service line, SEC fuse assemblies, point of supply connection point and customer mains showed no signs of deterioration and looked in very good condition for its age. Installing a new raiser bracket, FOLCB and mains cabling is customer initiated prescribed installation work and the REC did not have a prescribed COES, he only had a non prescribed COES. CES No. 506450125 REC Name Sam Aiasecca REC No. and Licence No. A7051 REC Address 18 Woolart St Strathmore Phone No. 0402580827 | Neutral screen;POA connection (customer side);Connection box;Service cable (insulated);Customer wiring | 0 | 0 | 0 |  | NS08 | Unauthorised access / Unauthorised REC work REC disconnected supply to customers installation to make repairs to/replace FOLCB without reference to Jemena or retailer | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44108.4854 |  |  | 15448 | Residential |  | 20200410JEM_01 | Infrastructure (customer connection) | -37.7438 | 144.9121 | 1 | Jemena | Report | 19568 | 0.012175 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Essendon | Other
Fault crew was sent to make safe, investigate and organise repairs. Crew repaired damaged conductors. Further customer side damage details: Service fuse blown at customers meter box and Meter damage was consistent with HVI. Meter was replaced, NST passed, circuits checked, and 4 appliances were found to have damaged. | 5469 SOUTH GIPPSLAND HIGHWAY, AGNES VIC 3962 | 2013543 |  | Wind |  | HV injection |  |  | 2 | Report of HVI, crew was sent to investigate and make safe. During storms, a tree limb from road reserve (refer to attached photo) along the South Gippsland Hwy (outside 45 Ewans Road, Agnes) fell and broke a 22kV 19/3.25 ACC (bare conductor) and LV 7/0.080 CU (bare conductor) causing a High Voltage Injection. Damage to a smart meter and some appliances (Water pump, microwave, Gas Hot water unit & NBN modem) at 5469 South Gippsland Highway, Agnes appears to be the only customer affected. | Conductor (bare) | 0 | 0 | 0 |  | FTR12 | Vegetation: Trees Incident | HV injection | 16/04/2020 14:36 |  |  | 15466 | Residential |  | 20200415SPN_01 | Infrastructure (network-based) | -38.6701 | 146.3813 | 2 | AusNet Services Distribution | Report | 19890 | 0.030745 | Low voltage AC (<1kV);22kV AC | Morwell (Latrobe Valley Airport) | 3962 | Agnes | Conductor
Damaged assets replaced by faults crew | 11 THE GROVE, COBURG VIC 3058 | A067165 |  |  |  | Leakage |  |  | 1 | HV crossarm broken, HV isolator 11843 De Carle corner The Grove fell onto LV crossarm and started a pole top fire. No HV injection and no loss of supply. | Crossarm (wood);Disconnector/isolator | 0 | 0 | 0 |  | CS5 | Electrical leakage (tracking) | Pole-top fire | 44169.1292 | 1 | Negligible: no ground fire | 15491 | Residential |  | 20200420JEM_01 | Infrastructure (network-based) | -37.7514 | 144.9668 | 1 | Jemena | Report | 19622 | 0.0099433 | 22kV AC | Essendon Airport | 3058 | Coburg | Crossarm
The attending Licensed Electrical Inspector (LEI) instructed the Jemena fault crew to check the condition of the service cable feeding the installations. Upon close investigation the fault crew was able to identify a damaged service neutral screened cable. The attending fault crew replaced the single phase overhead neutral screened service cable and completed an NST test which recorded a pass result. At this stage the attend LEI performed voltage test between an independent earth and neutral bar at the main switchboard and the point where the victim received the electric shock, now recording a steady 0.2 Volts. A final NST was carried out on the installation by the attended LEI that indicated a PASS result. The installation was left ON supply | 455 UPPER HEIDELBERG ROAD, HEIDELBERG HEIGHTS VIC 3081 | A098687 |  |  |  | Neutral fault |  |  | 2 | Lynne Tait received an electric shock when going to mover her portable heater and making simultaneously contact with both her hands to the frame. Lynne also reported noticing dimmed lights, her fridge and air conditioner not working properly. Voltage tests between an independent earth and the portable heater and the distribution assets recorded 79 volts. | Copper;Neutral screen | 2 | 2 | 2 |  | NH17 | Damaged service neutral screened cable | Minor shock | 20/04/2020 14:00 |  |  | 15493 | Residential |  | 20200420JEM_02 | Infrastructure (network-based) | -37.7544 | 145.0563 | 1 | Jemena | Report | 19624 | 0.032304 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg Heights | OH Cable
On arrival supply isolated and repairs carried out. | 86 EVANS STREET, BRUNSWICK VIC 3056 | 30158615 |  | Wind | [5 empty] | Member of the Public reported a metal pipe has fallen on mains wires, pipe can be touched from ground, SES on site. On arrival crew reported that a standing sewer pipe (stink pipe) was damaged and made contact with the LV bare mains. There was no injury or other third party damage reported. | Conductor (bare) | 2 | 2 | 2 |  | CO023 | Sewer pipe dislodged in high winds | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44139.5993 |  |  | 15494 | Roadway |  | 20200421PWA_01 | Infrastructure (network-based) | -37.7703 | 144.9688 | 1 | CitiPower | Report | 19625 | 0.0067303 | Low voltage AC (<1kV) | Essendon Airport | 3056 | Brunswick | Other
M&S crew disconnected, abolished and made safe the overhead service line and removed the 3 phase electricity meter. | 66 ROSS STREET, COBURG VIC 3058 | A070557 | Unauthorised access | [5 empty] | 2 | Metering & Service (M&S) crew attended the above address yesterday with a supply order for an abolishment of 3 phase service line and 3 phase metering. When they arrived they found the overhead service line still attached and connected, the service fuses removed and taped to the overhead service line, all the customer wiring cut and stripped out and the electricity meter sitting in the old fire hydrant. | Smart meter;Service cable (insulated);Customer wiring | 0 | 0 | 0 |  | CS13 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/04/2020 7:41 |  |  | 15511 | Residential |  | 20200424JEM_01 | Infrastructure (network-based) | -37.7357 | 144.9651 | 1 | Jemena | Report | 19652 | 0.036053 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Other
Fuse and Barrel replaced, supply restored | 240 TUCKS ROAD, SHOREHAM VIC 3916 | 8827052 |  |  |  | Fatigue;Mechanical breakdown;Fuse failed to eject |  |  | 0 | A HV EDO fuse tube at RB0486 Tucks Rd on spur to CARSON TUCKS S/Stn failed mechanically. The fuse tube was blackened internally but the was no evidence of ant external blackening or fire on the ground - hence not a F-Factor reportable event | EDO fuse | 0 | 0 | 0 |  | DMA 23 | Likely the deterioration of of fuse tube internally over many operations led to mechanical failure | Hung-up fuse only;Singeing or local charring/blackening only | 22/04/2020 17:59 |  |  | 15519 | Agricultural |  | 20200427UTD_04 | Infrastructure (network-based) | -38.4067 | 144.9997 | 1 | United Energy Distribution | Report | 19754 | 0.0017326 | 22kV AC | Moorabbin Airport | 3916 | Shoreham | Fuse
Replaced 3 phase 400Amp Krone Box and Blades - These were LV S/Stn Isols | 6-8 KALIMNA DRIVE, MORNINGTON VIC 3931 | 1100802 |  |  |  | Corrosion;Overheated connection |  |  | 1 | CFA advise approx halfway down pole was on fire, but now out. LV Isolator krone box melted suspect due to corrosion & loose connection. 1/2 sqm fire at base of pole fire report #6831 LIS 1100802 | Disconnector/isolator | 0 | 0 | 0 |  | MTN 35 | Corrosion/Loose Connection | Grassfire | 15/04/2020 18:28 | 1 | Localised: less than 10 sq.m | 15520 | Residential |  | 20200427UTD_05 | Infrastructure (network-based) | -38.2114 | 145.0506 | 1 | United Energy Distribution | Report | 19662 | 0.0089769 | Low voltage AC (<1kV) | Moorabbin Airport | 3931 | Mornington | Connection
Cap Bank isolated and out of service | 94 QUEENS AVENUE, CAULFIELD EAST VIC 3145 | 2327650 |  |  |  | Electrical breakdown |  |  | 2 | Customer reported box on pole on fire. Structure was "Queen Derby" Cap Bank. There was no fire on ground - fire report #08024. LIS 2327650 | Pole Mounted Cap Bank;Other | 0 | 1 | 0 |  | CFD 24 | Unknown at this point | Pole-top fire | 44078.5028 | 1 | Negligible: no ground fire | 15521 | Residential |  | 20200427UTD_06 | Infrastructure (network-based) | -37.8797 | 145.0444 | 1 | United Energy Distribution | Report | 19663 | 0.029073 | 11kV AC | Moorabbin Airport | 3145 | Caulfield East | AF Other
Jemena fault crew have made site safe and carried out repairs | 126 SLATER PARADE, KEILOR EAST VIC 3033 | A093607 | Copper theft | [5 empty] | 2 | Copper theft from ground-type substation 2 metres of earth wire has been cut away by unknown persons from GFB pole at ground-type substation (slater-tunnecliffe) No customers were impacted. | Outdoor;Earth/earthing | 0 | 0 | 0 |  | AW8 | Copper theft | Damage to network assets | 28/04/2020 14:19 |  |  | 15530 | Industrial |  | 20200428JEM_02 | Infrastructure (network-based) | -37.7293 | 144.862 | 1 | Jemena | Report | 19675 | 0.0061725 | earth conductor;Other | Essendon Airport | 3033 | Keilor East | Other
Crew dispatched to make safe. Appropriate repairs carried out including new wood pole. | 100 SAVIGES ROAD, MOE VIC 3825 | 2205266 | Vehicle | [6 empty] | A car has collided with and broken pole 2205266. A guy wire from 2205266 has made contact with HV 2205278 as a result of the collision. | Pole (wood) | 0 | 0 | 0 |  | MOE32 | Car collided with pole. | Loss of supply | 24/04/2020 23:05 |  |  | 15525 |  |  | 20200428SPN_01 | Infrastructure (network-based) | -38.1715 | 146.2522 | 1 | AusNet Services Distribution | Report | 19670 | 0.011264 | 22kV AC | Morwell (Latrobe Valley Airport) | 3825 | Moe | Vehicle
UE fault crews attended and isolated the section, and undertook repairs to the broken conductor under access authority conditions. ESV was notified by phone call, ref 13883152. | 233A MAIN CREEK ROAD, MAIN RIDGE VIC 3928 | 1308636 | Crane, excavator or other construction/farming equipment | [5 empty] | 1 | An Excavator was back filling dam and inadvertantly undermined a gum tree which fell onto overhead HV lines. A 3/12 steel conductor broke mid-span with both ends faling to ground. A 15A BA line fuse upstream of the fault operated to de-energise the line. However, the load side of the broken conductor was live as it was back-fed via the unbroken phase through a single phase transformer. | Conductor (bare) | 0 | 0 | 0 |  | DMA23 | Vegetation: Trees Incident | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 27/04/2020 12:57 |  |  | 15532 | Agricultural |  | 20200429UTD_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | United Energy Distribution | Report | 19677 | 0.0086586 | 22kV AC | Moorabbin Airport | 3928 | Main Ridge | Other
On arrival supply isolated and repairs carried out | 77 LAVENDER ROAD, GUNBOWER VIC 3566 | 32032440 |  |  |  | Corrosion |  |  |  | Following a report of an outage at the incident location crew attended site. On arrival crew found an EDO fuse burnt in half. There was no ground fire, no reported injuries or thrid party property damage. | EDO fuse | 2 | 2 | 2 |  | CHA005 | EDO fuse Failure | Pole-top fire | 28/10/2019 8:32 | 1 | Negligible: no ground fire | 15539 | Agricultural |  | 20200501PWA_01 | Infrastructure (network-based) | -35.973 | 144.3967 | 1 | Powercor | Report | 19686 | 0.00661 | 22kV AC | Bendigo Airport | 3566 | Gunbower | Fuse
Faults crew attended the site to investigate. Upon inspection, it was identified that U/G street light cable was dug up and damaged by external work party. The site was isolated and made safe. The cable was repaired and supply was restored. | 858 BLACKBURN ROAD, CLAYTON VIC 3168 | 8806170 | Working too close to underground cables | [5 empty] | 1 | UE was notified that contractors were digging up the median strip for a residential development using an excavator and damaged u/g conduit to public lighting which was sparking. | Cable | 0 | 0 | 0 |  | SVW41 | It is likely the person was working too close to the assets. | No Go Zone (contact) | 44076.3611 |  |  | 15430 | Roadway |  | 20200403UTD_02 | Infrastructure (network-based) | -37.9196 | 145.1398 | 1 | United Energy Distribution | Report | 19545 | 0.010104 | Low voltage AC (<1kV) | Moorabbin Airport | 3168 | Clayton | Dug up
Faults Crew dumped Low Voltage circuit and made safe Faults crew replaced LV termination crossarm and reattached LV mains conductor Senior asset performance engineer inspected the crossarm and concluded that the crossarm had failed due to rot | 1 INVERNESS MEWS, GREENVALE VIC 3059 | A041962 |  |  |  | Rot |  | Phase to earth | 2 | Crew attended report of wire down and found LV crossarm deteriorated resulting in blue phase Insulator coming out of crossarm and blue phase bare LV mains conductor falling to ground. | Conductor (bare);Crossarm (wood);Aluminium;Insulators | 0 | 0 | 0 |  | COO21 | LV crossarm failure (rot) | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43925.3313 |  |  | 15431 | Residential |  | 20200404JEM_01 | Infrastructure (network-based) | -37.6455 | 144.8872 | 1 | Jemena | Report | 19540 | 0.027256 | Low voltage AC (<1kV) | Melbourne Airport | 3059 | Greenvale | Crossarm
The Krone box was replaced | 141 Beach Rd, Parkdale VIC 3195, Australia | 1808847 |  |  |  | Overheated connection |  |  | 2 | MFB reported a fire outside 141 Beach Rd, Parkdale, crew attended and a LV Krone box caught fire- .Fire report # 03749, LIS = 1808847. ESV Ref #13753960 | Disconnector/isolator | 0 | 0 | 0 |  | M25 | The cause was most likely related to loose connection or corrosion on within the box | Pole-top fire | 43986.2181 | 1 | Negligible: no ground fire | 15433 | Residential |  | 20200406UTD_01 | Infrastructure (network-based) | -37.9984 | 145.0742 | 1 | United Energy Distribution | Report | 19542 | 0.022214 | Low voltage AC (<1kV) | Moorabbin Airport | 3195 | Parkdale | Connection
Live damaged cable put back in pit | 5 TOTTENHAM STREET, CRAIGIEBURN VIC 3064 | A089703 | Copper theft | [5 empty] | 2 | Attempted copper theft, live wires left outside pit | Cable | 2 | 2 | 2 |  | ST33 | Attempted copper theft | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 44016.2993 |  |  | 15437 | Residential |  | 20200407JEM_02 | Infrastructure (network-based) | -37.5856 | 144.9061 | 1 | Jemena | Report | 19550 | 0.0027234 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Crew attended and repaired Powercor assets | 192 AMOS ROAD, CAPE BRIDGEWATER VIC 3305 | 30240878 |  |  |  | Insulator |  |  | 0 | Powercor crew attending to outage in area became aware of a pole fire on shared pole. | Conductor (bare) | 0 | 0 | 1 | Pacific Hydro | P3CCBW 354, PLD006 | dislodged 66 KV conductor tbc | Pole-top fire | 43955.7604 | 0 | Negligible: no ground fire | 15438 | Roadway |  | 20200407PWA_01 | Infrastructure (network-based) | -38.3532 | 141.4075 | 1 | Powercor | Notification | 19552 | 0.023265 | 22kV AC;66kV AC | Portland (Cashmore Airport) | 3305 | Cape Bridgewater | Conductor
UE Fault crews attended the site and assisted regulators and emergence services where they could. | 19 Mt Pleasant Drive, Glen Waverley | 605348 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment |  |  |  |  | Phase to earth | 1 | UE received alarm of an ACR reclose and lockout. Fault crew attendance found a concrete pumping boom had made accidental contact with live bare HV conductors in Mt Pleasant Drive Glen Waverley. UE called ESV - reference 13763830. ESV officer Loc Vuong attended the site, along with WorkSafe. Police were also in attendance. A worker from the site was taken to hospital by Ambulance. | Conductor (bare) | 2 | 2 | 2 |  | GW3 | The work being undertaken was repaving of the footpath at this location. The cause of the incident was the concrete pumping boom was working within the No Go Zone of the existing live bare HV conductors in Mt Pleasant Drive. There was no request received by UE for No Go Zone permission for these works. | Medical attention (first aid/doctor/hospital) | 43986.4146 |  |  | 15442 | Roadway |  | 20200409UTD_01 | Infrastructure (network-based) | -37.8845 | 145.1324 | 1 | United Energy Distribution | Report | 19559 | 0.03389 | 22kV AC | Moorabbin Airport |  |  | Other
Underground cable pits made safe. Pole A141399 reconnected as safe to do so. | 9 ADELIE COURT, ROXBURGH PARK VIC 3064 | A141394 | Copper theft | [5 empty] | 2 | Copper theft of LV underground service cable for public lighting circuit between poles A141399 to A141394 near 9 ADELIE COURT, ROXBURGH PARK VIC 3064) along Aitken Boulevard, Greenvale | Cable | 0 | 0 | 0 |  | COO11 | Copper theft | Loss of supply;Damage to network assets | 13/04/2020 9:00 |  |  | 15453 | Roadway |  | 20200413JEM_01 | Infrastructure (network-based) | -37.6361 | 144.91 | 0 | Jemena | Report | 19573 | 0.0065706 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Roxburgh Park | Other
Field crew arrived on site and isolated section of underground cables and made area safe Repairs are underway | 14 CASPIAN DRIVE, CRAIGIEBURN VIC 3064 | A146948 | Working too close to underground cables | [5 empty] | 1 | Non-Jemena Civil Crew was drilling holes for installation of bollards and inadvertently made contact with high voltage and low voltage underground cables near CASPIAN-MILLAU kiosk substation. 14245 total customers impacted (5300 sustained, 9045 momentary). No injuries. As per attached photos, the underground cables were installed appropriately by Jemena with: â€¢ 100mm of bedding sand above/below direct-buried cable â€¢ 750mm to the cable from ground level â€¢ Mechanical protection | Cable | 0 | 0 | 0 |  | ST32 | No Go Zone breach | No Go Zone (contact) | 14/04/2020 11:52 |  |  | 15456 | Residential |  | 20200414JEM_01 | Infrastructure (network-based) | -37.5849 | 144.8958 | 1 | Jemena | Report | 19600 | 0.037973 | Low voltage AC (<1kV);22kV AC | Melbourne Airport | 3064 | Craigieburn | Dug up
ON arrival crew isolated supply arranged for transformer replacement | 1108 BOLINDA-DARRAWEIT ROAD, DARRAWEIT GUIM VIC 3756 | 33025397 |  |  |  | Unknown technical factor |  |  |  | Report received of pole and transformer on fire at incident location. On arrival the crew found that fire had been extinguished by CFA. There was no ground fire, no reported injuries or third party property damage. | Pole (wood);Pole mounted | 2 | 1 | 2 |  | GSB012 | Transformer failure | Pole-top fire | 44078.7903 | 1 | Negligible: no ground fire | 15454 | Roadway |  | 20200414PWA_01 | Infrastructure (network-based) | -37.4266 | 144.8627 | 1 | Powercor | Report | 19574 | 0.015965 | 22kV AC | Wallan (Kilmore Gap) | 3756 | Darraweit Guim | AF Other
On arrival crew isolated supply and carried out repairs. | 1230 LILFORD ROAD, MERRIGUM VIC 3618 | 30130456 |  |  |  | Mechanical breakdown |  |  |  | Report received of small grass fire and wire down at the incident location. On arrival crew found that a conductor had fractured at the 22kv insulator and fallen to the ground starting a small grass fire. There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | KYM003 | fractured conductor | Grassfire | 44139.8153 | 1 | Small: 10 - 1000 sq.m | 15457 | Roadway |  | 20200414PWA_02 | Infrastructure (network-based) | -36.3431 | 145.1749 | 1 | Powercor | Report | 19577 | 0.0035694 | 22kV AC | Shepparton Airport | 3618 | Merrigum | Conductor
additional permit to work issued for installation of hoarding prior to allowing works from scaffolding, worksafe to monitor | 2 HAINES STREET, NORTH MELBOURNE VIC 3051 | 30180478 | Working too close to overhead lines | [5 empty] | 2 | Outage created and permit to work issued for the erection of scaffolding. when site was re-visited for supply restoration it was found that hoarding was not adequate. Worksafe requested and attended, case #V1044200068L | Conductor (bare) | 0 | 0 | 0 |  | VM040 | non compliance with Permit arrangements | No Go Zone (no contact) | 44078.5021 |  |  | 15458 | Construction |  | 20200414PWA_03 | Infrastructure (customer connection) | -37.7987 | 144.9499 | 1 | CitiPower | Report | 19578 | 0.031089 | Low voltage AC (<1kV) | Essendon Airport | 3051 | North Melbourne | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that the service line was damaged at the POA by a third party. The site was isolated and made safe and the line was repaired. | 32 MILTON AVENUE, CLAYTON SOUTH VIC 3169 | 629001 | Working too close to overhead lines | [5 empty] | 1 | UE was advised that the service line was damaged by the customer's hedge trimmer. | Service cable (insulated) | 0 | 0 | 0 |  | SV16 | The person was working too close to the service line. | No Go Zone (contact) | 44016.5278 |  |  | 15470 | Residential |  | 20200415UTD_01 | Infrastructure (network-based) | -37.9375 | 145.1309 | 1 | United Energy Distribution | Report | 19594 | 0.019681 | Low voltage AC (<1kV) | Moorabbin Airport | 3169 | Clayton South | Other
Faults crew attended the site to investigate. Upon inspection, it was identified that live bare LV conductors were in contact with the car. ESV were notified- ref # 13761640. The ambulance had already left - it is believed the driver had only minor injuries. The site was isolated and made safe. The pole was replaced and the lines were repaired. | 760 NORTH ROAD, PEARCEDALE VIC 3912 | 3301737 | Vehicle | [5 empty] | 1 | UE was advised that car has hit a pole and the wires are down on the car. Emergency services - police and fire brigade were on site. | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | LWN21 | the cause is a car hitting a power pole | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons);Damage to network assets | 43955.7194 |  |  | 15473 | Roadway |  | 20200415UTD_02 | Infrastructure (network-based) | -38.1727 | 145.2528 | 1 | United Energy Distribution | Report | 19597 | 0.014897 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3912 | Pearcedale | Vehicle
On arrival crew isolated supply and carried out repairs | 3200 Foxhow-Berrybank Rd, Berrybank VIC 3323, Australia | 30049834 | [7 empty] | A customer called to report a service wire broken mid-span and a small grass fire. On arrival the crew found that a grey service cable had ruptured mid span and fallen to the ground. The live end of the service cable ignited a small grass fire of around 40 sq metres. There was no injuries or third party property damage reported. | Service cable (insulated) | 2 | 2 | 2 |  | CDN004 | To be established | Grassfire | 14/04/2020 14:45 | 1 | Small: 10 - 1000 sq.m | 15479 | Agricultural |  | 20200416PWA_01 | Infrastructure (network-based) | -38.0133 | 143.482 | 1 | Powercor | Notification | 19606 | 0.037066 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3200 | Berrybank | OH Cable
Crew Isolated the Sub and arranged and re traced the leads from the Transformer to establish correct phasing The 160amp ABC box was replaced The Crew wired up the new ABC box to suit the LV leads out the back of the transformer in a standard configuration and completed a phase rotation on the load side of the 160amp ABC fuse box during the restoration This result showed corrected phasing Phase plate fitted Customer / engage REC changed phasing on their side to correct | 30 WALKERVILLE ROAD, WALKERVILLE VIC 3956 | LIS 2021569 |  |  |  | Reverse polarity |  |  |  | Phase Rotation at ABC Krone Box | Connection box | 0 | 0 | 0 |  | FTR21 | Crew arrived onsite and found a burnt out ABC Krone Box making phasing identification at the box impossible Crew was dispatched and advised the LV krone box on LIS 2021569 was replaced on the 15/02/2020. Suspect phase rotation did not go back as found when LV krone box was replaced on 15/02/2020. | Pole-top fire | 25/02/2020 16:38 | 1 | Negligible: no ground fire | 15484 |  |  | 20200416SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19612 | 0.011675 | Low voltage AC (<1kV) | Moorabbin Airport | 3956 | Walkerville | Connection
Faults crew attended the site to investigate. Upon inspection, it was identified that the neutral connection at the POA was damaged by the owner. The site was isolated and made safe and the neutral connection was repaired. | 1 HUMMERSTONE ROAD, SEAFORD VIC 3198 | 3305497 | Working too close to overhead lines | [5 empty] | 1 | UE was advised that an excavator has hit and damaged an overhead service line. | Service cable (insulated) | 0 | 0 | 0 |  | FTN14 | The cause is likely to be working too close to the overhead service. | No Go Zone (contact) | 22/03/2020 16:30 |  |  | 15498 | Residential |  | 20200422UTD_01 | Infrastructure (network-based) | -38.1063 | 145.1361 | 1 | United Energy Distribution | Report | 19630 | 0.013065 | Low voltage AC (<1kV) | Moorabbin Airport | 3198 | Seaford | Vehicle
Crew arrived, made safe, replaced service and restored supply | 22 TRACEY STREET, RESERVOIR VIC 3073 | A010680 | Working too close to overhead lines | [5 empty] | 2 | Customer reports cutting service wire going to his property while trimming a tree at the front. No injury sustained | Aluminium;Service cable (insulated) | 0 | 0 | 0 |  | TT08 | Vegetation: Trees Incident | Damage to network assets | 22/04/2020 16:58 |  |  | 15504 | Residential |  | 20200423JEM_01 | Infrastructure (network-based) | -37.704 | 144.9963 | 1 | Jemena | Report | 19642 | 0.024179 | Low voltage AC (<1kV) | Essendon Airport | 3073 | Reservoir | Other
confirmed line isolated and disptached fault crew to access damage to poles. wires and supply reinstated. | 370 Bells rd clyde vic 3978 | 13817568 | Working too close to overhead lines | [6 empty] | contractor contacted de energised HV | Conductor (covered uninsulated) | 0 | 0 | 0 |  | CLN22 | Excavator hit HV and pulled cables to the ground. | Loss of supply;No Go Zone (contact) | 15/04/2020 16:26 |  |  | 15510 |  |  | 20200424SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19651 | 0.023558 | 22kV AC | Moorabbin Airport | 3978 |  | Vehicle
The crews have disconnected and removed the overhead service line, made site safe and completed the underground supply alteration connection with a COES P1003110538 | 34 ALLAN STREET, ABERFELDIE VIC 3040 | A109245 | Unauthorised access | [5 empty] | 2 | Metering & Servicing crews attended the above address today for an 11.00am Truck Appointment with a Supply Order for a 1 phase overhead supply and metering alteration to 1 phase underground supply and metering. When they arrived they found the 1 phase overhead supply and metering arrangement as per the attached pictures where the builder has removed the entire front faÃ§ade of the existing dwelling and constructed an extension to the front of the existing dwelling interfering and encroaching on the Jemena overhead service line and metering equipment. When the crews questioned the builder on site as to why he has constructed this extension in the manner he has and interfered with and encroached on the Jemena metering equipment and service line, he replied â€œI didnâ€™t want to waitâ€ | Aluminium;Smart meter;Service cable (insulated) | 0 | 0 | 0 |  | ES12 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/04/2020 11:00 |  |  | 15535 | Residential |  | 20200429JEM_01 | Infrastructure (network-based) | -37.7603 | 144.8926 | 1 | Jemena | Report | 19680 | 0.025502 | Low voltage AC (<1kV) | Essendon Airport | 3040 | Aberfeldie | Other
Operator attended and made safe, found candled fuse at transformer, replaced fuse and energized, no damage found | 25 MOUNTAIN VIEW ROAD, MOUNTAIN VIEW VIC 3988 | 2005050 |  |  |  | Candled fuse |  |  | 2 | Candled fuse | EDO fuse | 0 | 0 | 0 |  | LGA24 | Candling fuse. | Melting or smoking only | 28/04/2020 9:31 |  |  | 15531 | Residential |  | 20200429SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19676 | 0.017384 | 22kV AC | Moorabbin Airport | 3988 | Mountain View | Fuse
On arrival crew isolated supply and carried out repairs | 240 FISCHER STREET, TORQUAY VIC 3228 | 30346842 |  |  |  | Unknown technical factor |  |  |  | Report received of pillar fire at incident location. On arrival crew found an lv pillar had been destroyed and small patch of burnt ground. There was no reported injuries or third party property damage. | LV Pillar | 2 | 2 | 2 |  | WPD022 | insufficient remains to determine cause | Grassfire | 29/04/2020 11:00 | 1 | Localised: less than 10 sq.m | 15536 |  |  | 20200430PWA_01 | Infrastructure (customer connection) | -38.3072 | 144.3298 | 1 | Powercor | Report | 19681 | 0.0032164 | Low voltage AC (<1kV) | Avalon Airport | 3228 | Torquay | AF Other
On arrival crew isolated supply and carried out repairs. | 42 KELLETT STREET, NORTHCOTE VIC 3070 | 30192711 |  |  |  | Corrosion |  |  |  | Report retrieved of pole fire at incident location. On arrival crew found an overheated Krone box had caught fire. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | NC006 | Overheated connection | Pole-top fire | 29/04/2020 11:00 | 1 | Negligible: no ground fire | 15538 | Roadway |  | 20200430PWA_02 | Infrastructure (network-based) | -37.7673 | 145.0082 | 1 | CitiPower | Report | 19683 | 0.030876 | Low voltage AC (<1kV) | Essendon Airport | 3070 | Northcote | Connection
UE fault crew isolated the substation and undertook repairs to the damaged LV conductor under access authority conditions. The crew also made safe the damaged Optus cable. Optus were notified. ESV were notified - ref 13898640. | 26 DEHNERT STREET, DONCASTER EAST VIC 3109 | 7063157 | Working too close to overhead lines |  |  |  |  | Phase to neutral | 1 | A high vehicle demolition bin truck hit optus wire which flicked up into blue phase lv conductor above, resulting in the LV bare conductor falling to the ground alive. The damaged conductor was in the bus section of substation Dehnert-Murphy, and was protected by the substation HV fuses. | Conductor (bare) | 0 | 0 | 0 |  | DC4 | A demolition bin truck attending the site at 25 Dehnert St Doncaster East hit and damaged an Optus cable which flicked up and contacted the bare LV conductor above. The bare LV conductor fell to the ground. It is believed that the impedance of the conductor on the ground was relatively high such that the fault current was not high enough to operate the upstream HV protection. | Loss of supply;Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 30/04/2020 11:46 |  |  | 15545 | Roadway |  | 20200504UTD_01 | Infrastructure (network-based) | -37.785 | 145.149 | 1 | United Energy Distribution | Report | 19696 | 0.038874 | Low voltage AC (<1kV) | Moorabbin Airport | 3109 | Doncaster East | Vehicle
crew completed isolations and then replaced pole and earthing system | 2 CADDYS LANE, TYLDEN VIC 3444 | 30342390 |  |  |  | Earth fault |  |  | 1 | Fault crew investigating an outage found substation pole burning at ground level. Crew was preparing to isolate supply at tee off further up the line when burnt pole fell. | Pole (wood);Pole mounted | 0 | 0 | 0 |  | WND024 | Under Investigation | Pole-top fire | 43835.2917 | 1 | Negligible: no ground fire | 15547 | Agricultural |  | 20200505PWA_01 | Infrastructure (network-based) | -37.3458 | 144.4404 | 1 | Powercor | Report | 19701 | 0.027975 | 12.7kV AC (SWER);22kV AC | Melbourne Airport | 3444 | Tylden | Pole
crew attended and made repairs to conductor | 1 SHIRALEA COURT, CALIFORNIA GULLY VIC 3556 | 30025941 |  | Within clearances |  |  |  |  | 1 | Tree branch cut and contacted HV Line | Conductor (bare) | 0 | 0 | 0 |  | EHK023 | Vegetation: Trees Incident | Loss of supply;Damage to network assets | 43956.3938 |  |  | 15548 | Roadway |  | 20200505PWA_02 | Infrastructure (network-based) | -36.7295 | 144.2662 | 1 | Powercor | Notification | 19702 | 0.01256 | 22kV AC | Bendigo Airport | 3556 | California Gully | Trees
Faults crew attended the site and replaced the service. | 35 CUTHBERT STREET, BULLEEN VIC 3105 | 7056965 | Working too close to overhead lines | [5 empty] | 1 | Excavator has pulled down the overhead service wire. Wire is broken and resting on a pile of rubble in the front yard. | Conductor (insulated) | 0 | 0 | 0 |  | WD36 | The person was working too close to the overhead line | No Go Zone (contact) | 27/03/2020 10:50 |  |  | 15552 | Residential |  | 20200506UTD_01 | Infrastructure (network-based) | -37.7731 | 145.0914 | 1 | United Energy Distribution | Report | 19713 | 0.0034074 | Low voltage AC (<1kV) | Essendon Airport | 3105 | Bulleen | Vehicle
defect 02176 issued on customer mains, isolated at LV mains pillar, inside boundary | 84 QUINN GROVE, KEILOR EAST VIC 3033 | A056755 | Working too close to underground cables | [5 empty] | 1 | Workers installing new underground lines have struck conduit with borer and pulled out several metres of wire resulting in blown fuses in electrical pillar No Permit to Work from Jemena was requested from the responsible third party or issued by Jemena No details of responsible third party are available | Services cable | 0 | 0 | 0 |  | AW06 | No Go Zone breach | No Go Zone (contact) | 44170.6514 |  |  | 15570 | Public space |  | 20200512JEM_01 | Infrastructure (network-based) | -37.7386 | 144.8727 | 1 | Jemena | Report | 19740 | 0.029929 | Low voltage AC (<1kV) | Essendon Airport | 3033 | Keilor East | Dug up
Sent crew out to make safe, replace pole and re energize | 2 peir street port albert | 2624373 |  | Prone to salt deposition |  | Corrosion |  |  | 1 | Concrete pole broke off in the ground- LV alive on the ground | Conductor (bare);Pole (concrete) | 0 | 0 | 0 |  | FDR 23 | Pole is situated in a swampy, damp area in close proximity to sea water. Constant moisture around the pole has caused the steel reinforcement to deteriorate causing the pole fail. The pole fail has occurred approximately 600 to 700mm below ground. This level is well below the required 300mm excavation depth conducted by AusNet Asset Inspectors. | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44109.5847 |  |  | 15567 | Residential |  | 20200512SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19735 | 0.014016 | Low voltage AC (<1kV) | Moorabbin Airport |  |  | Pole
Powercor fault crew attended, checked safe for the operator to alight from the cultivator machine prior to the machine being removed from the location to enable the pole to be replaced. | 687 GOAD LANE, BEULAH VIC 3395 | 32107625 | Crane, excavator or other construction/farming equipment | [6 empty] | The manager of a farming property reported that a "Air Seeder / Cultivator working on his property had struck a Powercor pole . The overhead line had come down on the machine, with operator inside. THere was no fire, no reported injuries or third party property damage. | SWER conductor;Pole (wood) | 2 | 2 | 2 |  | HSM003 | Air seeder/cultivator collided with pole | Damage to network assets | 44109.8486 |  |  | 15571 | Agricultural |  | 20200513PWA_01 | Infrastructure (network-based) | -36.0125 | 142.367 | 1 | Powercor | Report | 19742 | 0.028516 | 12.7kV AC (SWER) | Horsham Aerodrome | 3395 | Beulah | Vehicle
Crew attended and replaced cross-arm | Chinkapook-Mittyack Rd, Chinkapook VIC 3546, Australia | 30304554 |  |  |  | Leakage |  |  |  | Crew reports burnt wooden HV crossarm on pole 238 - small ground fire | Crossarm (wood) | 0 | 0 | 0 |  | OYN003 | leakage current | Pole-top fire;Grassfire | 43477.5396 | 1 | Small: 10 - 1000 sq.m | 15590 | Forest - native (not park) |  | 20200515PWA_09 | Infrastructure (network-based) | -35.1811 | 142.9225 | 1 | Powercor | Report | 19767 | 0.017175 | 22kV AC | Swan Hill Aerodrome | 3546 | Chinkapook | Crossarm
Crew advised the CEOT and isolated the spur . Issued EAP and repaired the broken conductor and restrung Cancelled EAP and restored the supply to the spur SM RP created follow up NOTI 180day to have the Conductor inspected due to its condition (rusty 3/12 conductor) | MARSHALLS ROAD, TRARALGON VIC 3844 | 2606437 |  |  |  | Corrosion |  |  | 0 | HV conductor broke from load side of HV fuses 814677 and fell to the ground. Insufficient current to blow fuses or trip SEF. | Conductor (bare) | 0 | 0 | 0 |  | TGN11 | Crew arrived onsite found HV conductor had broken about a metre out from the end of a sleeve 3/12 steel ( Note 3/12 quite rusty) HV conductor on ground alive due back feed from subs on the spur (no fuses blown) | Damage to network assets | 14/05/2020 7:30 |  |  | 15579 | Roadway |  | 20200515SPN_01 | Infrastructure (network-based) | -38.1783 | 146.5429 | 1 | AusNet Services Distribution | Report | 19795 | 0.02223 | 22kV AC | Morwell (Latrobe Valley Airport) | 3844 | Traralgon | Conductor
on arrival crew isolated supply ans carried out repairs. | 22 ALBERT STREET, POINT LONSDALE VIC 3225 | 30071219 |  |  |  | Corrosion |  |  |  | Report received of a pole fire in Albert st Point Lonsdale. On arrival the crew found that an overheated FOLCB had resulted in a pole fire. Falling debris also resulted in a small ground fire. | Connection box | 2 | 2 | 2 |  | DDL012 | Overheated connection | Pole-top fire;Grassfire | 15/05/2020 22:38 | 1 | Localised: less than 10 sq.m | 15603 | Roadway |  | 20200518PWA_05 | Infrastructure (network-based) | -38.2825 | 144.6123 | 1 | Powercor | Report | 19783 | 0.02367 | Low voltage AC (<1kV) | Avalon Airport | 3225 | Point Lonsdale | Connection
supply isolated pole replaced | BEN MOOR, 750 LEXTON-ARARAT ROAD, AMPHITHEATRE VIC 3468 | 30567768 |  |  |  | External fire;Other |  |  |  | Emergency services report damage to powercor assets from fire, requesting crew to attend. crew found powercor assets had been damaged by an external bushfire | Pole (wood) | 0 | 0 | 0 |  | MRO008 | External fire damaged network assets | Damage to network assets | 22/12/2019 16:49 |  |  | 15604 | Agricultural |  | 20200518PWA_06 | Infrastructure (network-based) | -37.2559 | 143.445 | 1 | Powercor | Report | 19785 | 0.036602 | 22kV AC | Ballarat Aerodrome | 3468 | Amphitheatre | Other
Crew attended and replaced fuse holder | 120 CRUICKSHANKS ROAD, GLENORMISTON NORTH VIC 3265 | 30042218 |  |  |  | Fuse failed to eject |  |  |  | crew attending outage found burnt off edo fuse at incident location | EDO fuse | 0 | 0 | 0 |  | TRG001 | Fuse mal-operation | Pole-top fire | 22/12/2019 12:37 | 1 | Negligible: no ground fire | 15605 | Roadway |  | 20200518PWA_07 | Infrastructure (network-based) | -38.1439 | 142.9853 | 1 | Powercor | Report | 19787 | 0.0050891 | 22kV AC | Warrnambool Airport Ndb | 3265 | Glenormiston North | Fuse
Attending crew replaced fuse mount | 155 WORMBETE STATION ROAD, WURDIBOLUC VIC 3241 | 33040998 |  |  |  | Fuse failed to eject |  |  |  | Following supply failure crew found an edo fuse had hung up and burnt in half. | EDO fuse | 0 | 0 | 0 |  | WIN022 | Fuse mal-Operation | Pole-top fire | 27/12/2019 5:25 | 1 | Negligible: no ground fire | 15607 | Roadway |  | 20200518PWA_09 | Infrastructure (network-based) | -38.3159 | 144.0311 | 1 | Powercor | Report | 19789 | 0.015884 | 22kV AC | Avalon Airport | 3241 | Wurdiboluc | Fuse
Attending crew replaced fuse | 400 BOUNDARY ROAD, PINE LODGE VIC 3631 | 32192679 |  |  |  | Fuse failed to eject |  |  |  | Following report of supply failure crew found a burnt out EDO fuse unit. | EDO fuse | 0 | 0 | 0 |  | STN024 | Fuse mal-operation | Pole-top fire | 43984.5556 | 1 | Negligible: no ground fire | 15608 | Agricultural |  | 20200518PWA_10 | Infrastructure (network-based) | -36.3712 | 145.4984 | 1 | Powercor | Report | 19790 | 0.038745 | 22kV AC | Shepparton Airport | 3631 | Pine Lodge | Fuse
Tree branch removed, assets inspected, line returned to service. | 305 Dhurringile Rd, Tatura VIC 3616, Australia | 33093071 |  | Blown branch/vegetation | [5 empty] | MNA013 Feeder went to lockout. On arrival crew found a small branch (200mm long) had blown onto the line on the west side of pole 65 Tatura line. There was signs of a flashover to crossarm and small burn marks on the branch. There was no ground fire , no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | MNA013 | Vegetation: Trees Incident | Other vegetation | 13/05/2020 14:10 | 1 | Negligible: no ground fire | 15616 | Roadway |  | 20200520PWA_01 | Infrastructure (network-based) | -36.4391 | 145.241 | 1 | Powercor | Report | 19803 | 0.0045683 | 22kV AC | Shepparton Airport | 3616 | Tatura | Trees
Immediate Actions â€¢ Memo to be communicated to all stakeholders reinforcing the NGZ requirements. â€¢ Network Owner/Zinfra to review a sample of recent PTWâ€™s that have been issued to identify if there are any other instances where PTWâ€™s are in conflict with the Scope of work, conditions, Instructions and that works are compliant JEM /Work Safe NGZ Procedures. â€¢ Following self-reporting by the Jemena Project team, The Work Practices Manager reported the NGZ breach in March to Energy Safe Victoria and recorded the incidents in OSIRIS. Energy Safe have visited the site and met with CPBJH as result of the March incident. â€¢ A formal investigation was undertaken with corrective actions to prevent recurrence identified and will be completed. | 57 WEMBLEY AVENUE, YARRAVILLE VIC 3013 | A133136 | Working too close to underground cables | [5 empty] | 2 | NGZ PTW (J037275) issued on 9 Sept 2019 to the CPBJH Site Engineer (EY), for civil workers to install a storm water drain in the vicinity of JEN underground assets. The PTW instructions were for civil works to maintain the NGZ minimum clearances and not to disturb the live 22kv cable/conduit or protective warning covers. The Jemena Major Project CM assessed the work to be done applied to have automatic reclose suppressed on FE5 and elected to act as the Spotter and supervised the CPBJH civil workers for the excavation and installation of a beam and conduit supports. Civil workers undertook mechanical trenching and non-destructive digging to a depth of 1.5 m underneath the live Footscray East 22kV (FE5) conduit /cable, fully exposing the conduit across a 5 meter wide trench. The minimum NGZ clearances were not maintained and VESI trained and authorised personal were not engaged to complete the trenching and installation of temporary cable supports. Additionally a PTW should not have been issued where the description, precautions, and instructions are in conflict with the intended 3rd party scope of work. As a result this incident was considered a noncompliance to JEM NGZ Procedures ELE PR 0100. Note: PTW J037275 expired on 20 Dec 2019, however work continued through to the 6 Feb. Due to encountering rock, the trench was backfilled and excavation reprogrammed for March 2020. | Cable | 0 | 0 | 0 |  | FE5 | No Go Zone breach | No Go Zone (no contact) | 16/01/2020 19:44 |  |  | 15634 | Construction |  | 20200521JEM_01 | Infrastructure (network-based) | -37.8241 | 144.8734 | 1 | Jemena | Report | 19821 | 0.016899 | 22kV AC | Essendon Airport | 3013 | Yarraville | Dug up
Fuses replaced supply restored | 112 MAXWELL ROAD, FINGAL VIC 3939 | 1318609 |  |  |  | Candled fuse |  |  | 0 | Punshon Maxwell S/S 2 HV B/A fuses candled, R and W phase , single phase S/S ,P/P ,conc pole, 6K BA fuses, fire report 1983 and ESV Ref 14001255 - LIS = 1318609 | Boric acid | 0 | 0 | 0 |  | STO14 | Fuse or Fuse unit failure | Plant/equipment | 20/05/2020 10:07 | 1 | Negligible: no ground fire | 15633 | Agricultural |  | 20200521UTD_01 | Infrastructure (network-based) | -38.4232 | 144.8761 | 1 | United Energy Distribution | Report | 19820 | 0.0053472 | 22kV AC | Moorabbin Airport | 3939 | Fingal | Fuse
Overhead service cable was detached at pole end as a result of the incident. The service cable was subsequently removed from the house end and completely removed. | 3 DREW STREET, YARRAVILLE VIC 3013 | A030341 | Working too close to overhead lines |  |  |  |  | Phase to earth | 1 | Excavator working under LV open wires at 3 Drew St Yarraville property have hit the overhead service wire supplying 5 Drew St Yarraville, pulling it down together with the raiser bracket. Supply lost. Overhead service wire down in front yard of property. Defect #08339 issued. Breakaway device operated to de-energise the LV service. Responsible third party is Innercity Excavations, Excavator Registration: XV30-GF | Service cable (insulated) | 0 | 0 | 0 |  | FW5 | No Go Zone breach | Loss of supply;No Go Zone (contact) | 25/05/2020 15:18 |  |  | 15649 | Residential |  | 20200525JEM_01 | Infrastructure (network-based) | -37.8164 | 144.8764 | 1 | Jemena | Report | 19838 | 0.0077824 | Low voltage AC (<1kV) | Essendon Airport | 3013 | Yarraville | Vehicle
Council has cut back council tree form service line to block of units - crew has dropped service to make safe - re-issue to 2nd crew to replace 25 metres of 35mm 4c service | 128 GLEN HUNTLY ROAD, ELWOOD VIC 3184 | 2311320 |  | Within clearances | [5 empty] | Customer advises service line rubbing up against tree at pole end & had sparks & flames from it. | Service cable (insulated) | 0 | 0 | 0 |  | EW02 | Vegetation: Trees Incident | Other vegetation;Plant/equipment | 21/05/2020 11:13 | 1 | Localised: less than 10 sq.m | 15647 | Residential |  | 20200525UTD_01 | Infrastructure (network-based) | -37.8831 | 144.9901 | 1 | United Energy Distribution | Report | 19836 | 0.038213 | Low voltage AC (<1kV) | Moorabbin Airport | 3184 | Elwood | Trees
Crews attended isolated the supply and performed repairs. | 67 Tooram Rd, Allansford VIC 3277, Australia | 33104135 | Working too close to underground cables | [6 empty] | Josh from Duggan Civil called to report that they had dug up a wire during excavation work at the incident location. On arrival the crew found that the excavator had hooked a 35mm 4 core LV UG cable, approx. 2.5m from P1A . There was no fire, no reported injuries or third party property damage. | Cable | 2 | 2 | 2 |  | WBL012 | Excavator disturbed underground service | No Go Zone (contact) | 25/05/2020 14:28 |  |  | 15657 | Roadway |  | 20200526PWA_03 | Infrastructure (network-based) | -38.3901 | 142.5956 | 1 | Powercor | Report | 19848 | 0.024993 | Low voltage AC (<1kV) | Warrnambool Airport Ndb | 3277 | Allansford | Dug up
Sent crews to investergate and repair | SHEEP PEN CREEK ESTATE, 1506 DOOKIE-VIOLET TOWN ROAD, KOONDA VIC 3669 | 3904189 |  | Lightning |  | Mechanical breakdown |  |  | 2 | pole damaged by lightning, hv conductor down. 3 dead horses & 2 dead cows in vicinity | SWER conductor;Pole (wood) | 0 | 0 | 0 |  | BN2 | Animal Incident | Fatality of livestock, pet or companion animal | 24/05/2020 12:00 |  |  | 15653 | Agricultural |  | 20200526SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19844 | 0.037895 | 6.6kV AC | Moorabbin Airport | 3669 | Koonda | Lightning
Faults called and repairs have taken place | CORNER BEATTYS ROAD AND CROWN DRIVE FRASER RISE VIC 3336 | A154569 | Working too close to underground cables |  |  |  |  | Phase to phase | 2 | â€¢ Customer obtained PTW from NGZ Assessor on 26/05/2020 to allow installation of electrical conduit along Beattyâ€™s Rd, Plumpton (Fraser Rise) â€¢ NGZ Inspection Report â€“ J 009576 issued 26/05/2020 (see attached) â€¢ PTW â€“ J 035173 issued 26/05/2020 (see attached) â€¢ Customer was using a contractor, Ginsan Construction to carry out the trenching to install the conduits â€¢ Contractor was taken through the PTW and its conditions by the customer and also informed to finish the trenching and conduit run no closer than 1m from a Telstra pit, which was in the nature strip â€¢ Contractor has stopped the trenching and conduit run some 4m away from the Telstra pit on the North side, but decided to did right next to the Telstra pit on the South side. â€¢ Excavator has dug up LV underground and supply lost â€¢ Contractor knew Live LV Cables were below as ground was marked and DBYD were on site â€¢ New estate. No shocks received. No sparking noticed. | Cable;Copper | 0 | 0 | 0 |  | SHM14 | No Go Zone infringement | No Go Zone (contact) | 27/05/2020 12:48 |  |  | 15662 | Roadway |  | 20200527JEM_01 | Infrastructure (network-based) | -37.6957 | 144.7202 | 1 | Jemena | Report | 19885 | 0.016936 | Low voltage AC (<1kV) | Melbourne Airport | 3336 |  | Dug up
Faults crew arrived and replaced LV open wire with ABC and replaced Pole A049169 (relabelled as A153765) | 63 ROSE STREET, COBURG VIC 3058 | A049169 | Working too close to overhead lines |  |  |  |  | Phase to earth | 2 | A rubbish truck has hit the Optus cable between poles A049169 and A048459 This has in turn brought down 1 bay of low voltage overhead open wire bare conductor in Rose St tee into Munro St Coburg between poles A049169 to A048459 The incident also moved pole A049169, leaving it in a dangerous position Details of rubbish truck or driver are unavailable There was no permit to work on issue | Conductor (bare);Pole (wood);Communication cable/equipment | 0 | 0 | 0 |  | CS02 | No Go Zone infringement | No Go Zone (contact);Damage to network assets | 27/05/2020 13:15 |  |  | 15664 | Residential |  | 20200527JEM_02 | Infrastructure (network-based) | -37.7431 | -37.7431 | 1 | Jemena | Report | 19879 | 0.0049965 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3058 | Coburg | Vehicle
Crew sent to investigate and repair | Cnr Bengworden Rd and Hagans Rd Cobains | 2503447 |  |  |  | Candled fuse |  |  | 0 | Candling fuse | Boric acid | 0 | 0 | 0 |  | SLE32 | Fuse was candling with significant tracking when crews arrived onsite, fuse then burnt through and 'operated' in that the circuit was Deenergised but the fuse didn't operate traditionally in dropping out. Crew inspected the site and found nothing else Tube had burnt through about 20 mm from top of the fuse , but no other evidence of burning found | Pole-top fire | 28/05/2020 10:38 | 1 | Negligible: no ground fire | 15668 |  |  | 20200529SPN_02 | Infrastructure (network-based) | -38.0963 | 147.0836 | 1 | AusNet Services Distribution | Report | 19861 | 0.020017 | 22kV AC | Bairnsdale Airport |  |  | Fuse
Crew sent to investigate and repair | 99 DARNUM-SHADY CREEK ROAD, DARNUM VIC 3822 | 2706177 | Caused by contractor | [5 empty] | 1 | an excavator removing trees on customers property felled a tree that impacted 2 X 22kV conductors that hit the ground | Conductor (bare) | 0 | 0 | 0 |  | WGL15 | Vegetation: Trees Incident | No Go Zone (contact) | 29/05/2020 15:12 |  |  | 15669 | Roadway |  | 20200529SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19863 | 0.0073796 | 22kV AC | Moorabbin Airport | 3822 | Darnum | Vehicle
Fault crews attended the site and performed emergency high voltage switching to minimise the number of customers affected and the repairs were completed. LEI attended the site and confirmed evidence of HVI - no damage to AMI meters, only appliances. | 39 CALLANANS ROAD, RED HILL SOUTH VIC 3937 | 1307910 |  | Wind;Fallen |  |  |  |  | 1 | During high winds, a large tree has fallen onto a pole substation as well as bringing down the HV and LV wires. The ACR on the feeder operated. | Conductor (bare) | 0 | 0 | 0 |  | DMA15 | Vegetation: Trees Incident | HV injection | 30/05/2020 15:10 |  |  | 15678 | Roadway |  | 20200602UTD_01 | Infrastructure (network-based) | -38.3816 | 145.0267 | 1 | United Energy Distribution | Report | 19877 | 0.030727 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3937 | Red Hill South | Trees
On arrival crew isolated supply and carried out repairs. | 65 Whites Rd, Cardigan VIC 3352, Australia | 33002226 |  |  |  | Unknown technical factor |  |  |  | VicFire reported a pole fire at incident location. On arrival the crew found that a FOLCB has overheated and melted. CFA in attendance. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | BAS011 | Insufficient remains to determine cause. | Pole-top fire | 43896.5278 | 1 | Negligible: no ground fire | 15685 | Roadway |  | 20200604PWA_01 | Infrastructure (network-based) | -37.5298 | 143.7406 | 1 | Powercor | Report | 19889 | 0.01509 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3352 | Cardigan | Connection
On arrival crew inspected conductors for damage. repairs carried out. | 2 Wexford Ct, Corio VIC 3214, Australia | 32083694 | Working too close to overhead lines | [6 empty] | report recieved of powerline outside property had white sparks for 15 seconds before power went off. On arrival crew received information that a customer may have been trimming trees on private property and contacted LV conductors. There was evidence of LV having clashed and a connection was burnt off on adjacent pole. It is believed the customer at 2 WEXFORD COURT have been cutting a tree down and a branch has hit the LV . The customer did not admit actions may have contributed to outage. There was no tree clearing operations at site when crew attended. There was no fire, no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | CRO034 | Vegetation: Trees Incident | Damage to network assets | 27/05/2020 13:54 |  |  | 15692 | Roadway |  | 20200605PWA_01 | Infrastructure (network-based) | -38.0723 | 144.3504 | 1 | Powercor | Report | 19899 | 0.0077419 | Low voltage AC (<1kV) | Avalon Airport | 3214 | Corio | Other
The crew isolated the LV service cable and proceed to do the required repairs.16mm 4C Service cable to pit between #9 and #11 was replaced. | 9 St Georges Ave, Caroline Springs VIC 3023, Australia | 34016033 | Working too close to underground cables | [6 empty] | Mrs Sue Caruana and REC Anton, Ph: 0403050699, reported there are some road works being done at St Georges avenue in Caroline springs On arrival the crew found that a contractor MIEPOL, (Contact: Michael Bowler (GM), Ph: 0431 170 713), were doing some civil works on the road and when they drove a metal stake in the ground they hit a LV underground service cable causing damage to the cable. The REC measured the voltage on metal stake and recorded 220 volts. There was no fire, no reported injuries or third party property damage. | Services cable | 2 | 2 | 2 |  | SU022 | Stake driven through service line | No Go Zone (contact);Damage to network assets | 18/06/2020 17:31 |  |  | 15762 | Roadway |  | 20200622PWA_01 | Infrastructure (network-based) | -37.7426 | 144.7305 | 1 | Powercor | Report | 19992 | 0.003478 | Low voltage AC (<1kV) | Laverton Raaf | 3023 | Caroline Springs | Dug up
On arrival crew isolated supply and carried out repairs. | 120 Blair St, Portland VIC 3305, Australia | 33060158 |  |  |  | Unknown technical factor |  |  |  | CFA reported a pole fire at the above address. The crew attended and found a faulted Krone box on the sub pole. It had overheated and melted. No ground fire was involved. CFA attended the incident. There was no ground fire, no reported injuries or third party property damage. | Connection box | 2 | 2 | 2 |  | PLD004 | Insufficient remains to determine cause | Pole-top fire | 20/06/2020 23:48 | 1 | Negligible: no ground fire | 15768 |  |  | 20200622PWA_03 | Infrastructure (network-based) | -38.339 | 141.5989 | 1 | Powercor | Report | 19999 | 0.011182 | Low voltage AC (<1kV) | Portland (Cashmore Airport) | 3305 | Portland
Despatched crew to Investigate and repair | HAWTHORN LANE, BRIGHT VIC 3741 | 5725930 | [7 empty] | LV ABC fault caused HVI and associated damage to appliances. | Conductor (ABC) | 0 | 0 | 0 |  | BRT11 | Under Investigation | HV injection | 19/06/2020 16:58 |  |  | 15766 | Residential |  | 20200622SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19996 | 0.014141 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3741 | Bright
Despatched crew to investigate and repair | 858 Sale-Heyfield Rd Denison | 2509280 |  |  |  | Mechanical breakdown |  |  | 1 | Suspect HV Conductor sleeve let go and conductor fell to the ground blowing HV fuses. | Conductor (bare) | 0 | 0 | 0 |  | 22 | Crew found that the sleeves used for this type conductor 3/4/2.50 ACSR/GZ (raisin) were incorrect ( Compression used) MUST be helical splice Note these sleeves were install in the conductor about a week ago Crew repaired the conductors using the correct Sleeves ( Helical splice) Crew cancel EAP and restored the line | Loss of supply | 16/06/2020 21:46 |  |  | 15773 | Roadway |  | 20200623SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 20007 | 0.016622 | 22kV AC | Moorabbin Airport
crew attended and replaced insulated leads | 1768 ODEA ROAD, STRATHALLAN VIC 3622 | 31025963 |  |  |  | Electrical breakdown |  |  | 1 | Powercor crew responded to advice of a pole that was on fire. On arrival the crew identified that the high voltage transformer leads have malfunctioned. | Conductor (insulated);Dropper/bridge | 0 | 0 | 0 |  | ECA005 | Outer covering of leads broke down | Pole-top fire | 22/06/2020 23:49 | 1 | Negligible: no ground fire | 15780 | Roadway |  | 20200624PWA_04 | Infrastructure (network-based) | -36.2558 | 144.8163 | 1 | Powercor | Notification | 20017 | 0.0033958 | 22kV AC | Shepparton Airport | 3622 | Strathallan
Sent crew to Investigate and clean up | 205-207 Johnston Street/Station Street maffra | MFA ZSS | [7 empty] | MFA TX no 1 failure resulting in ZSS BLACK, oil expulsion and ground fire | Zone substation | 0 | 1 | 0 |  | MFA zss | Tap changer ruptured due to an internal fault which led to the oil release | Grassfire | 24/06/2020 23:37 | 1 | Localised: less than 10 sq.m | 15783 | Residential |  | 20200625SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 20022 | 0.023086 | 22kV AC | Moorabbin Airport
Incident reported to ESV | UNIT 1 13 FARM STREET, NEWPORT VIC 3015 | A059439 | Unauthorised access | [5 empty] | 2 | A customer has removed their own overhead service line to try and speed up Jemena issuing SOC, so they can get an occupancy certificate. An after hours appointment had been booked for 5 May 2020, but the customer did not want to wait. It is unclear how the overhead service line was removed by the customer. Name, phone number and email address of customer is included in the "Other information sources" section. | Aluminium;Aluminium twisted (XLPE);Service cable (insulated) | 0 | 0 | 0 |  | NT16 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 23/04/2020 16:37 |  |  | 15546 | Residential |  | 20200504JEM_03 | Infrastructure (network-based) | -37.8421 | 144.8911 | 1 | Jemena | Report | 19705 | 0.0036586 | Low voltage AC (<1kV) | Essendon Airport | 3015 | Newport | Other
Fire self extinguished, CFA in attendance but didn't need to dose. Crew replaced FOLCB & restored supply. | 9 MARTIN AVENUE, OUYEN VIC 3490 | 32148103 |  |  |  | Unknown technical factor |  |  |  | CFA reported a pole fire at the incident location, Upon arrival the fault crew found that a 3 phase LV FOLCB had burnt resulting in an all supply fail. There was no ground fire or 3rd party damage. | Connection box | 2 | 2 | 2 |  | OYN007 | Insufficient remains to determine cause | Pole-top fire | 30/04/2020 21:50 | 1 | Negligible: no ground fire | 15541 | Roadway |  | 20200504PWA_01 | Infrastructure (network-based) | -35.0652 | 142.3152 | 1 | Powercor | Report | 19692 | 0.0078079 | Low voltage AC (<1kV) | Mildura Airport | 3490 | Ouyen | Connection
Crew wassent to make safe, investigate and orgainse repairs. Fuse link and carrier were replaced and supply restored. | 40 DWYER ROAD, BASS VIC 3991 | 2803195 |  | Prone to salt deposition |  | Moisture ingress |  |  |  | Report of candling HV EDO Fuse. No gound fire and only burn marks in fuse holder. Fuse is still intact as per photo. Refer to the attachd site photo. | EDO fuse | 0 | 0 | 0 |  | LLG13 | Possible cause is salt air corrosion and moisture inside fuse holder. | Pole-top fire | 27/04/2020 11:23 | 1 | Negligible: no ground fire | 15554 | Residential |  | 20200506SPN_01 | Infrastructure (network-based) | -38.4576 | 145.475 | 1 | AusNet Services Distribution | Report | 19716 | 0.037058 | 22kV AC | Moorabbin Airport | 3991 | Bass | Fuse
Fault crew sent to make safe, investigate and orgnise repairs. No Fire was observed. Crew inspected the asset, replaced EDO 6K Fuse and restored supply. No photos of the site is availalble. | 4945 TRARALGON-MAFFRA ROAD, TINAMBA VIC 3859 | 5723936 |  |  |  | Candled fuse |  |  | 2 | Report of Candled HV EDO Fuse. On arrival crew found candled EDO fuse at pole 5723936 (3 phase Substation). No Fire was observed. Crew inspected the asset, replaced EDO 6K Fuse and restored supply. No photos of the site is availalble. | EDO fuse | 0 | 0 | 0 |  | MFA22 | Plausible cause is age of the EDO Fuse. | Pole-top fire | 43986.3125 | 1 | Negligible: no ground fire | 15560 |  |  | 20200508SPN_01 | Infrastructure (network-based) | -37.9846 | 146.887 | 1 | AusNet Services Distribution | Report | 19757 | 0.020078 | 22kV AC | Morwell (Latrobe Valley Airport) | 3859 | Tinamba | Fuse
Faults crew replaced a property crossing service to the house #29. | 29 ASHLEY STREET, BOX HILL NORTH VIC 3129 | 7024184 | Working too close to overhead lines;Crane, excavator or other construction/farming equipment | [5 empty] | 1 | A construction company has advised they have hit and cut a service wire running to the address. The cable is cut in half and is on the ground but still connected to both ends. It appears that an excavator whilst digging a driveway outside # 27 Ashley St Box hill Nth has pulled down the service to #29. | Conductor (insulated) | 0 | 0 | 0 |  | DC7 | The plant was working too close to the overhead line. | No Go Zone (contact) | 43926.3785 |  |  | 15561 | Residential |  | 20200508UTD_01 | Infrastructure (network-based) | -37.8106 | 145.1364 | 1 | United Energy Distribution | Report | 19724 | 0.016976 | Low voltage AC (<1kV) | Moorabbin Airport | 3129 | Box Hill North | Vehicle
LEI attended the site and confirmed there was evidence of HVI. Fault crews isolated the site and made it safe. The service was replaced and the HV lines were repaired. | 32 GREENWAYS ROAD, GLEN WAVERLEY VIC 3150 | 197984 |  | Fallen |  |  |  |  | 1 | Tree at 34 Greensway has fallen onto the service to 32 and HV conductors, causing the HV to fall into the LV. | Conductor (bare) | 0 | 0 | 0 |  | GW8 | Vegetation: Trees Incident | HV injection | 43956.125 |  |  | 15562 | Roadway |  | 20200508UTD_02 | Infrastructure (network-based) | -37.8835 | 145.1526 | 1 | United Energy Distribution | Report | 19725 | 0.02245 | Low voltage AC (<1kV);2.2kV AC | Moorabbin Airport | 3150 | Glen Waverley | Trees
Crews sent out to ivestigate and repair. | 35 BENSON STREET, BELGRAVE VIC 3160 | 1307747 |  | Fallen |  | Conductor clashing |  |  | 2 | HVI Injection | Conductor (bare) | 0 | 0 | 0 |  | BGE23 | Vegetation: Trees Incident | HV injection | 44017.4868 |  |  | 15564 | Residential |  | 20200511SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19731 | 0.00069097 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3160 | Belgrave | Trees
Crew sent out to investigate and repair | 6 WYNETTE AVENUE, UPPER FERNTREE GULLY VIC 3156 | 1314048 |  | Fallen |  | Conductor clashing |  |  |  | tree fell on hv line, caused hv injection and property damage | Conductor (bare) | 0 | 0 | 0 |  | FGY33 | Vegetation: Trees Incident | HV injection | 44048.0583 |  |  | 15565 | Residential |  | 20200511SPN_02 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19730 | 0.041183 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3156 | Upper Ferntree Gully | Trees
Faults crew found fascia on the ground with live service still attached. They isolated the service at the pole end. It appears that the house is being demolished but the service hasn't been abolished. The NGZ officer attended the site the following day and notified Worksafe and ESV. The service and meter were subsequently abolished. | 32 TYNE STREET, BOX HILL NORTH VIC 3129 | 7000267 | Working too close to overhead lines | [5 empty] | 1 | A passerby reported that a tree had fallen onto the service line of a house and the wire was still attached and sparking. | Conductor (insulated) | 0 | 0 | 0 |  | DC6 | the contractor was working too close to the overhead lines. | No Go Zone (no contact);Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44170.7847 |  |  | 15573 | Residential |  | 20200513UTD_01 | Infrastructure (network-based) | -37.8106 | 145.1276 | 1 | United Energy Distribution | Report | 19745 | 0.0082292 | Low voltage AC (<1kV) | Moorabbin Airport | 3129 | Box Hill North | Other
Crew arrived and replaced the UE owned porcelain box which was believes to have ignited the small fire as well as the neutral service with black 2/c service. Closest LIS 2304444 | 19 THE AVENUE, BALACLAVA VIC 3183 | 2304444 |  |  |  | Corrosion |  |  | 2 | MFB reported a minor fire at the POA. | Connection box | 0 | 0 | 0 |  | BC11 | Likely Corrosion | Plant/equipment | 44079.7653 | 1 | Negligible: no ground fire | 15578 | Residential |  | 20200514UTD_01 | Infrastructure (network-based) | -37.8714 | 144.9962 | 1 | United Energy Distribution | Report | 19752 | 0.027219 | Low voltage AC (<1kV) | Moorabbin Airport | 3183 | Balaclava | Connection
fuse replaced supply restored. | 5475 GOULBURN VALLEY FREEWAY, MOORILIM VIC 3610 | 31027823 |  |  |  | Fuse failed to eject |  |  | 2 | Customer called can see fuse down hanging down on substation On arrival crew found fuse had candled and burnt in half There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 0 | 0 | 0 |  | MNA034 | EDO fuse mal-operation | Pole-top fire | 43566.7375 | 1 | Negligible: no ground fire | 15580 | Roadway |  | 20200515PWA_01 | Infrastructure (network-based) | -36.6133 | 145.3034 | 1 | Powercor | Report | 19756 | 0.024924 | 12.7kV AC (SWER) | Shepparton Airport | 3610 | Moorilim | Fuse
Fuse replaced supply restored | 455 CENTRAL ROAD, KYNETON SOUTH VIC 3444 | 33029664 |  |  |  | Fuse failed to eject |  |  | 2 | Customer reports fuse arcing and sparking, sparks nor reaching the ground. On arrival crew found burnt hung up edo fuse. There was no ground fire, no reported injuries. | EDO fuse | 0 | 0 | 0 |  | WND024 | Fuse mal-operation | Pole-top fire | 43596.8778 | 1 | Negligible: no ground fire | 15582 | Agricultural |  | 20200515PWA_02 | Infrastructure (network-based) | -37.2972 | 144.4411 | 1 | Powercor | Report | 19759 | 0.035457 | 22kV AC | Wallan (Kilmore Gap) | 3444 | Kyneton South | Fuse
fuse replaced supply restored | 31 MURRAY STREET, ANGLESEA VIC 3230 | 32072743 |  |  |  | Fuse failed to eject |  |  | 2 | Calls received of supply failure at incident location. On arrival crew found EDO fuse burnt. There was no ground fire, no reported injuries or third party property damage. | EDO fuse | 0 | 0 | 0 |  | WPD021 | Fuse mal-operation | Pole-top fire | 43688.5299 | 1 | Negligible: no ground fire | 15584 | Roadway |  | 20200515PWA_04 | Infrastructure (network-based) | -38.4111 | 144.1832 | 0 | Powercor | Report | 19761 | 0.00044444 | 22kV AC | Avalon Airport | 3230 | Anglesea | Fuse
supply isolated crossarm replaced | 88 CUMMINGS ROAD, PATCHEWOLLOCK VIC 3491 | 32151395 |  |  |  | Leakage |  |  |  | Report Received of cross-arm fire at incident location. On arrival crew found strain cross-arm had been burnt. | Crossarm (wood) | 0 | 0 | 0 |  | OYN005 | Excessive leakage current | Pole-top fire | 30/11/2019 3:00 | 1 | Negligible: no ground fire | 15588 | Commercial |  | 20200515PWA_07 | Infrastructure (network-based) | -35.3845 | 142.1877 | 1 | Powercor | Report | 19765 | 0.027793 | 22kV AC | Mildura Airport | 3491 | Patchewollock | Crossarm
Crew replaced fuse tube | 431 DIGGERS REST-COIMADAI ROAD, COIMADAI VIC 3340 | 32168128 |  |  |  | Fuse failed to eject |  |  |  | Crew attending a fault found that the end had burnt off edo fuse tube no ground fire | EDO fuse | 0 | 0 | 0 |  | MLN022 | HV Fuse mal-operation | Pole-top fire | 43689.0535 | 1 | Negligible: no ground fire | 15592 | Agricultural |  | 20200515PWA_11 | Infrastructure (network-based) | -37.6272 | 144.5176 | 1 | Powercor | Report | 19769 | 0.036505 | 22kV AC | Melbourne Airport | 3340 | Coimadai | Fuse
Crew attended and branch removed Customers poa repaired service replaced, supply restored | 25 SULLIVAN ROAD, ROCHESTER VIC 3561 | 33083749 |  | Blown branch/vegetation | [5 empty] | Branch fell breaking service line and causing a small fire. | Service cable (insulated) | 0 | 0 | 0 |  | KYM001 | Vegetation: Trees Incident | Grassfire | 43720.566 | 1 | Localised: less than 10 sq.m | 15593 |  |  | 20200515PWA_12 | Infrastructure (network-based) | -36.3509 | 144.713 | 1 | Powercor | Report | 19770 | 0.020311 | Low voltage AC (<1kV) | Bendigo Airport | 3561 | Rochester | Trees
The site was isolated and made safe. LEI attended the site and confirmed evidence of HVI. Faults crew repaired the conductors and pole tops. | 37 KINGSLEY CRESCENT, MONT ALBERT VIC 3127 | 7029595 |  | Fallen |  |  |  |  | 1 | A tree branch fell onto the HV conductors which caused the crossarm to break and allow the HV conductors to make contact with the LV. | Conductor (bare) | 0 | 0 | 0 |  | DC5 | Vegetation: Trees Incident | HV injection | 44017.0521 |  |  | 15581 | Roadway |  | 20200515UTD_01 | Infrastructure (network-based) | -37.814 | 145.1138 | 1 | United Energy Distribution | Report | 19758 | 0.019289 | Low voltage AC (<1kV);22kV AC | Moorabbin Airport | 3127 | Mont Albert | Trees
Crew attended site, fuses had blown, blown street cct was isolated, fire extinguished and pillar repaired | TEDDINGTON WAY, WANTIRNA VIC 3152 | Teddington Brentwood - Mariemon Cct |  |  |  | Electrical breakdown |  |  | 1 | LV pillar fire | LV Pillar | 0 | 0 | 0 |  | BRA32 | Electrical breakdown,fuses operated due to electrical and mechanical breakdown of the pillar due to the fire. | Other electricity related | 24/04/2020 14:00 | 0 | Negligible: no ground fire | 15597 | Residential |  | 20200518SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19776 | 0.0082477 | Low voltage AC (<1kV) | Moorabbin Airport | 3152 | Wantirna | AF Other
Crew replaced a 6 Amp BA on White phase, cause fuse candled | 166 FOXEYS ROAD, TUERONG VIC 3915 | 1105620 |  |  |  | Candled fuse |  |  | 0 | A HV fuse at "Ellerina P5-Junction" s/stn has candled.S/S is fully animal proofed. Fire report #6841 - no ground fire start - ESV ref 13971883 - LIS 1105620 | Boric acid | 0 | 0 | 0 |  | MTN32 | Candled BA Fuse | Plant/equipment | 14/05/2020 13:43 | 1 | Negligible: no ground fire | 15599 | Agricultural |  | 20200518UTD_02 | Infrastructure (network-based) | -38.3092 | 145.0698 | 1 | United Energy Distribution | Report | 19777 | 0.031296 | 22kV AC | Moorabbin Airport | 3915 | Tuerong | Fuse
Crew replaced transformer isolator (3phases) and replaced blue phase transformer lead. Restored supply/tested ok and sending photos to NCC Dispatch. Emer Mgr adv of outcome, compl details/photos emailed. | 54 LESLIE ST, ELSTERNWICK 3185 | 2303150 |  |  |  | Electrical overload;Overheated connection |  |  |  | MFB was on site at "Morton-Leslie" S/Stn when crew arrived and reported fire on assets but had gone out on its own - Source of fire at red phase isolator. ESV advised ref # 13978228 - LIS 2303150 | Disconnector/isolator | 0 | 0 | 0 |  | EL13 | Crew investigated and unable ascertain exact cause - but likely overload | Plant/equipment | 14/05/2020 17:48 | 1 | Negligible: no ground fire | 15600 | Residential |  | 20200518UTD_03 | Infrastructure (network-based) | -37.8822 | 145.0111 | 1 | United Energy Distribution | Report | 19778 | 0.0071539 | Low voltage AC (<1kV) | Moorabbin Airport | 3185 |  | AF Other
Crew attended and ensured the site was safe. | 51 MCRAE STREET, PORT CAMPBELL VIC 3269 | 33037157 | Working too close to underground cables | [6 empty] | A Fulton Hogan crew were installing an underground cable near substation pole at the incident location, The crew had carefully exposed underground cable nearby. They had DBYD plans but in process of excavation exposed the LV earthing system. There was no fire, no reported injuries or third party property damage. | Earth/earthing | 2 | 2 | 2 |  | TRG003 | inadvertent uncovering of earthing | No Go Zone (contact) | 44170.3986 |  |  | 15612 | Roadway |  | 20200519PWA_01 | Infrastructure (network-based) | -38.6197 | 143.0051 | 1 | Powercor | Report | 19798 | 0.0026007 | Earthing cable | Warrnambool Airport Ndb | 3269 | Port Campbell | Dug up
Crew replaced fuse carrier | 1753-1769 MOUNT COTTRELL ROAD, MOUNT COTTRELL VIC 3024 | 30106376 |  |  |  | Fuse failed to eject |  |  |  | Crew responding to a report of power outage found an EDO fuse had burnt in half | EDO fuse | 0 | 0 | 0 |  | MLN011 | Fuse mal-operation | Pole-top fire | 25/02/2020 0:27 | 1 | Negligible: no ground fire | 15622 | Roadway |  | 20200520PWA_04 | Infrastructure (network-based) | -37.7695 | 144.6093 | 1 | Powercor | Report | 19809 | 0.029222 | 22kV AC | Laverton Raaf | 3024 | Mount Cottrell | Fuse
Crew replaced cross-arm | 133 GOULBURN ROAD, ECHUCA VIC 3564 | 30123584 |  |  |  | Leakage |  |  |  | Powercor crew responding to a report of a pole fire found cross-arm had burnt | Crossarm (wood) | 0 | 0 | 0 |  | ECA003 | Excessive leakage current | Pole-top fire | 43924.5646 | 1 | Negligible: no ground fire | 15624 | Roadway |  | 20200520PWA_06 | Infrastructure (network-based) | -36.1282 | 144.762 | 1 | Powercor | Report | 19811 | 0.012606 | 22kV AC | Shepparton Airport | 3564 | Echuca | Crossarm
Crew replaced substation pole | Baker Cres, Stanhope VIC 3623 | 30222928 |  |  |  | Leakage |  |  |  | Report of pole fire at incident location, attending crew found pole burnt above transformer. | Pole (wood) | 0 | 0 | 0 |  | SHP021 | Excessive leakage current | Pole-top fire | 43954.6646 | 1 | Negligible: no ground fire | 15625 | Industrial |  | 20200520PWA_07 | Infrastructure (network-based) | -36.49 | 144.9704 | 1 | Powercor | Report | 19812 | 0.024491 | 22kV AC | Shepparton Airport | 3623 | Stanhope | Pole
crew replaced fuse carrier | 20 OLD NEUK ROAD, MOGGS CREEK VIC 3231 | 32070006 |  |  |  | Fuse failed to eject |  |  |  | Crew attending to an outage found fuse carrier had burnt. | EDO fuse | 0 | 0 | 0 |  | WPD014 | Fuse mal-operation | Pole-top fire;Hung-up fuse only | 15/03/2020 2:53 | 1 | Negligible: no ground fire | 15626 | Roadway |  | 20200520PWA_08 | Infrastructure (network-based) | -38.4659 | 144.0652 | 1 | Powercor | Report | 19813 | 0.034247 | 22kV AC | Avalon Airport | 3231 | Moggs Creek | Fuse
crew replaced fuse carrier | 1636 LILFORD ROAD, LANCASTER VIC 3620 | 32189439 |  |  |  | Fuse failed to eject |  |  |  | crew attending a Report of part supply found arcing EDO fuse | EDO fuse | 0 | 0 | 0 |  | KYM003 | fuse mal-operation | Pole-top fire;Hung-up fuse only | 15/03/2020 19:31 | 1 | Negligible: no ground fire | 15627 | Roadway |  | 20200520PWA_09 | Infrastructure (network-based) | -36.343 | 145.1333 | 1 | Powercor | Report | 19814 | 0.039013 | 22kV AC | Shepparton Airport | 3620 | Lancaster | Fuse
crew replaced cross-arm | CHINKAPOOK-NYAH WEST ROAD, CHINKAPOOK VIC 3546 | 32157434 |  |  |  | Leakage |  |  |  | crew responding to a Report of a pole fire found found HV crossarm burnt | Crossarm (wood) | 0 | 0 | 0 |  | SHL002 | excessive leakage current | Pole-top fire | 43925.5396 | 1 | Negligible: no ground fire | 15628 | Agricultural |  | 20200520PWA_10 | Infrastructure (network-based) | -35.1861 | 143.316 | 1 | Powercor | Report | 19815 | 0.0043762 | 22kV AC | Swan Hill Aerodrome | 3546 | Chinkapook | Crossarm
Crew attended and replaced cross-arm | 2754 OLD MELBOURNE ROAD, DUNNSTOWN VIC 3352 | 30004990 |  |  |  | Leakage |  |  |  | Report received of a pole fire On arrival crew found cross-arm burnt at EDO mounting position | Crossarm (wood) | 0 | 0 | 0 |  | BAS023 | excessive leakage current | Pole-top fire | 44078.4618 | 1 | Negligible: no ground fire | 15629 | Agricultural |  | 20200520PWA_11 | Infrastructure (network-based) | -37.5906 | 143.9655 | 1 | Powercor | Report | 19816 | 0.012234 | 22kV AC | Ballarat Aerodrome | 3352 | Dunnstown | Crossarm
Fault crews repaired the overhead service and supply was restored. | 38 RETREAT ROAD, HAMPTON VIC 3188 | 1813659 | Working too close to overhead lines | [5 empty] | 1 | Customer advised that an arborist has cut the consumer mains at the POA and supply is lost. | Conductor (insulated) | 0 | 0 | 0 |  | SR23 | The person was working too close to the overhead service | No Go Zone (contact) | 19/05/2020 12:40 |  |  | 15617 | Residential |  | 20200520UTD_01 | Infrastructure (network-based) | -37.941 | 145.0152 | 1 | United Energy Distribution | Report | 19804 | 0.022289 | Low voltage AC (<1kV) | Moorabbin Airport | 3188 | Hampton | Other
Isolations were conducted, the site was made safe and repairs were made. | 30 Grove Rd, Marshall VIC 3216, Australia | 31013080 |  | Fallen | [5 empty] | Customers called in to report a conductor brought down by tree branch. The crew attended and confirmed all 3 phases had been brought down by a tree branch. There was a small burn mark on the ground next to the conductors There was no reported injuries or third party property damage. | Conductor (bare) | 2 | 2 | 2 |  | GL013 | Vegetation: Trees Incident | Grassfire | 19/05/2020 19:00 | 1 | Localised: less than 10 sq.m | 15632 | Roadway |  | 20200521PWA_01 | Infrastructure (network-based) | -38.1951 | 144.3567 | 1 | Powercor | Report | 19819 | 0.0091354 | 22kV AC | Avalon Airport | 3216 | Marshall | Trees
Site made safe and repairs made | MARATHON BOULEVARD near CORNER OF REGATTA DRIVE, CRAIGIEBURN VIC 3064 | A090241 | Copper theft | [5 empty] | 2 | Attempted copper theft of cable cut upstream in pit adjacent pole no. A090241 | Cable;Services pit (network);Copper | 0 | 0 | 0 |  | ST33 | Attempted copper theft | Damage to network assets | 15/04/2020 0:00 |  |  | 15639 | Roadway |  | 20200522JEM_01 | Infrastructure (network-based) | -37.5853 | 144.9093 | 1 | Jemena | Report | 19827 | 0.014461 | Low voltage AC (<1kV) | Melbourne Airport | 3064 | Craigieburn | Other
Jason Ford has checked the Jemena Portal and there is no customer applications for this address. The property is unoccupied and no one living at the address. As discussed and agreed the Faults crew did not connect supply to the new arrangement. The REC needs to make an application via the EWR or Portal process for customer initiated supply and metering alteration works. The REC should also be directed to the compliance line to discuss the alteration works before a Metering & Servicing crew attends to ensure he has complied with the relevant requirements of the VSIRâ€™s and the Jemena overhead service policies and procedures. What should have been a pretty straight forward BH TA and fee is now probably going to cost a BH Faults fee + an AH Faults fee + an BH TA fee + a report to ESV + a delay in supply connection however itâ€™s really the only way they will learn. | 9 MOLESWORTH COURT, WEST FOOTSCRAY VIC 3012 | A061621 | Unauthorised access |  |  |  | Unauthorised REC work |  | 2 | Faults crew contacted Jason Ford (Compliance Officer) today for a customer call complaining about voltage and supply issues at 9 Molesworth Court West Footscray (NMI: 6001047661 Meter: 0188381). When they arrived they found a house under full construction and renovation with the overhead service line and POA still attached to the old section of the fascia board stapled to the new renovated section of the dwelling. They also observed that an REC had already installed a new 900mm raiser bracket in a completely new location, new customer mains, new metering enclosure in a new location and a new MSB (complete re-wire mains upgrade) The crew disconnected the existing unsafe overhead service line and issued a defect notice. The crew advised that tonight they received a job to return to the site to reconnect supply. When they arrived a new prescribed COES was on site (which has been dated 6.5.20 and 9.5.20 by the REC and LEI) and the old POA and fsacia previously stapled to the new re-build was laying on the ground at the front of the property. It is very evident and clear from the information from the crews and the attached photos they provided that this is a construction site and house under full renovation and very evident and clear that this is customer initiated wiring upgrades and the existing unsafe wiring and installation was created on site as part of the renovation works. | Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | FW16 | Unauthorised access / Unauthorised REC work | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 44140.85 |  |  | 15641 | Construction |  | 20200522JEM_03 | Infrastructure (network-based) | -37.7946 | 144.8742 | 1 | Jemena | Report | 19829 | 0.027037 | Low voltage AC (<1kV) | Essendon Airport | 3012 | West Footscray | Other
Crew sent to make safe, investigate and repair. | 11 FURZE COURT, CRANBOURNE WEST VIC 3977 | T60 | [7 empty] | CFA reported Telstra hut/optic cable on fire under transmission tower. CBTS-TBTS #2 220kv line tower number 60 in Cranbourne West (end of Furze Crt). First responder dispatched. Fire put out by CFA and fire of cable from hut to antennas on top of tower was put out by Tower Line worker with line de-energised. | Tower | 0 | 0 | 0 |  | CBTS-TBTS #2 220kv | Currently under invstigation. Suspected third party damage. | Pole-top fire | 22/05/2020 1:50 | 0 | Localised: less than 10 sq.m | 15642 |  |  | 20200522SPN_01 | Infrastructure (customer connection) | -38.0967 | 145.2642 | 1 | AusNet Services Transmission | Notification | 19830 | 0.0066053 | 220kV AC | Moorabbin Airport | 3977 | Cranbourne West | Other
Crews isolated all affected premises, and inspected and restored as access became available, and meters could be replaced. LEI attended incident 8 premises were identified to have the 3 phase meters replaced. blown circuit breakers on a machine at 185 Station St, and blown surge protectors at 177 Station St. | 185 Station St, Corio VIC 3214, Australia | 33045478 |  | Bird | [5 empty] | Crew attended the incident location following fault reports from two customers. On arrival the crew found that a HVI had occurred where a crow had caused a flashover of the 66kV insulators of P77 GTS-SRC Line. The subsequent fault current traveled through the concrete pole and exited the pole into the mounting bracket of an LV UG FOLCB. 8 premises were identified to have the 3 phase meters replaced. A number of premises had electrical damage. There was no fire or reported injuries. | Conductor (bare);Insulators | 2 | 2 | 2 |  | GTS-SRC | Bird Incident | HV injection | 23/05/2020 15:13 |  |  | 15646 | Roadway |  | 20200525PWA_04 | Infrastructure (network-based) | -38.0806 | 144.3684 | 1 | Powercor | Report | 19835 | 0.033637 | Low voltage AC (<1kV);66kV AC | Avalon Airport | 3214 | Corio | Animal
Crews attended, isolated the supply and performed repairs. | 3174 MORTLAKE-ARARAT ROAD, WOORNDOO VIC 3272 | 32060550 |  |  |  | Leakage |  |  |  | Powercor Employee was driving on the road at the incident location, when he noticed a burn mark on the cross-arm of P263 Woorndoo Line. On closer inspection, it was found that the crossarm had burnt most of the way through at the strap bolt. All of the conductors were still in position, and there was no ground fire. | Crossarm (wood) | 2 | 2 | 2 |  | TRG002 | Excessive leakage current | Pole-top fire | 23/05/2020 15:30 | 1 | Negligible: no ground fire | 15648 | Roadway |  | 20200525PWA_05 | Infrastructure (network-based) | -37.8063 | 142.8023 | 1 | Powercor | Report | 19837 | 0.031053 | 22kV AC | Warrnambool Airport Ndb | 3174 | Woorndoo | Crossarm
Site made safe by isolating supply in fuse box. Luminaire to be replaced. | 70 PEARSON STREET, BRUNSWICK WEST VIC 3055 | 30155687 |  |  |  | Moisture ingress |  |  |  | Customer reported Street light on cnr of Pearson St and Victoria St on fire at top of pole. Small flames and debris falling to ground. MFB attended. There was no ground fire, no reported injuries or third party property damage. | Public lighting | 2 | 2 | 2 |  | WB002 | Overheated | Pole-top fire | 23/05/2020 4:50 | 1 | Negligible: no ground fire | 15650 | Roadway |  | 20200525PWA_06 | Infrastructure (network-based) | -37.7656 | 144.9492 | 1 | CitiPower | Report | 19839 | 0.0062002 | Low voltage AC (<1kV) | Essendon Airport | 3055 | Brunswick West | Connection
Crews isolated the supply and installed a new fuse to another part of the board, and covered the damaged section. | UNIT 3 89 ROLLINS ROAD, BELL POST HILL VIC 3215 | 30070328 |  |  |  | Corrosion |  |  |  | A fault crew attended an all supply failure at the incident location. On arrival the crew found that a meter board fuse had overheated and burnt a small area of the meter board. There was no other fire or damage reported. | Meter board (including fuses) | 2 | 2 | 2 |  | GL015 | Overheated meter board fuse | Meter board | 24/05/2020 8:08 | 1 | Negligible: no ground fire | 15651 | Residential |  | 20200525PWA_07 | Infrastructure (customer connection) | -38.099 | 144.3229 | 1 | Powercor | Report | 19840 | 0.02316 | Low voltage AC (<1kV) | Avalon Airport | 3215 | Bell Post Hill | Installation
The crew isolated the supply and performed repairs. | 29 Field St N, Ocean Grove VIC 3226, Australia | 32076059 |  |  |  | Corrosion |  |  |  | MFB Communications reported a pole fire at the incident location. On arrival the crew found that a transformer LV isolator overheated, causing the attached lead insulation to catch fire, melt and fall to the ground. There were no reported injuries, ground fire or other damage. | Disconnector/isolator | 2 | 2 | 2 |  | DDL011 | Overheated connection | Pole-top fire | 26/05/2020 17:54 | 1 | Negligible: no ground fire | 15663 | Roadway |  | 20200527PWA_04 | Infrastructure (network-based) | -38.2579 | 144.5214 | 1 | Powercor | Report | 19855 | 0.012973 | Low voltage AC (<1kV) | Avalon Airport | 3226 | Ocean Grove | Connection
Supply isolated repairs carried out LEI checked for HVI - non found | 23 Wybellenna Dr, Fairhaven VIC 3231, Australia | 30144590 |  |  |  | Mechanical breakdown;Overheated connection |  |  |  | Lines crew where switching out Bimbadeen spur under instruction. The crew opened road side HV fuse successfully and on the opening of the center phase HV fuse, a large arc occurred and flashed over across the previously opened fuse unit (Switch 16176). Following this event a HV conductor at LIS 939779 fell to the ground. The ACR controlling this line tripped. There was no fire, no reported injuries or third party property damage No HVI. | Conductor (bare) | 2 | 2 | 2 |  | WPD014 | Fault current ruptured connection | Loss of supply;Damage to network assets | 27/05/2020 14:18 |  |  | 15666 | Roadway |  | 20200529PWA_01 | Infrastructure (network-based) | -38.4647 | 144.0912 | 1 | Powercor | Report | 19858 | 0.035939 | 22kV AC | Avalon Airport | 3231 | Fairhaven | Connection
isolated supply and initiated investigations | UNIVERSITY DRIVE, MOUNT HELEN VIC 3350 | PA0073688 | [7 empty] | Civil crew were completing directional bore work for HV cable replacement and contacted customers underground cables. | Customer wiring | 0 | 0 | 0 |  | BAS013 | Directional boring in area | Minor shock (unconfirmed);Loss of supply | 20/05/2020 15:30 |  |  | 15670 | Other | University Grounds | 20200529PWA_02 | Infrastructure (network-based) | -37.6267 | 143.8942 | 1 | Powercor | Notification | 19864 | 0.024124 | Low voltage AC (<1kV) | Ballarat Aerodrome | 3350 | Mount Helen | Dug up
Broken pole and LV crossarm were replaced by faults crew. Control room required Licensed Electrical Inspectors (LEI's) to investigate possible high voltage injection following multiple properties reporting damage following a car colliding with a pole on the corner of Douch St and Melbourne Rd. Following arrival the attending LEI's completed a thorough damage assessment of several properties on the affected circuit including the properties that had reported the damage and was able to confirm that a high voltage injection had occurred into the LV south circuit of the Latrobe-Yarra substation. All installations on the affected circuit were isolated on the morning of the incident. Following the Jemena faults crew completing repair works to the network infrastructure, the circuit was re-energised and a number of LEI's began to inspect the accessible installations, re-energise the properties and issue damage cards where required. All properties were attended on the day of the incident with the properties unattended left with no-access cards. | 195 MELBOURNE ROAD, WILLIAMSTOWN VIC 3016 | A051339 | Vehicle |  |  |  |  | Phase to earth | 1 | High Voltage Injection occurred due to car collinding with pole no. A051339 at Melbourne Rd corner with Douch St, Williamstown VIC 3016 Techsafe licensed electrical inspectors attended and confirmed high voltage injection The pole broke as a result of the vehicle impact Crew found a further LV Crossarm on Melbourne Rd opposite Yarra St that was broken as a result of car impact and are replacing this crossarm as well | Conductor (bare);Pole (wood) | 0 | 0 | 0 |  | NT11 | Car into pole | HV injection;Loss of supply;Damage to network assets | 31/05/2020 0:52 |  |  | 15671 | Roadway |  | 20200531JEM_01 | Infrastructure (network-based) | -37.8513 | 144.8889 | 1 | Jemena | Report | 19886 | 0.0071875 | 22kV AC | Essendon Airport | 3016 | Williamstown | Vehicle
Sent crew to Investigate and repair | 960 YANNATHAN ROAD, NYORA VIC 3987 | 2006256 |  |  |  | Age;Candled fuse |  |  | 0 | Candled fuse, 22kV, Fuse, LIS# 2006256 | Boric acid | 0 | 0 | 0 |  | LLG12 | Crew arrived onsite and found Burnt off BA tube at Lis NO 2006256 top half of tube laying on the ground the other half still in the holder Note no evidence of fire on the ground , Tube had burnt marks where it had come in half. It was an older deteriated fuse | Pole-top fire | 29/05/2020 20:20 | 0 | Negligible: no ground fire | 15672 | Agricultural |  | 20200601SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19869 | 0.038003 | 22kV AC | Moorabbin Airport | 3987 | Nyora | Fuse
Sent crew to invesyigate and rectify | 181 CHAPEL LANE, DOREEN VIC 3754 | 919037 |  |  |  | Candled fuse |  |  | 1 | Fuse found hung up and candling - no ground fire or other damage to assets | Boric acid | 0 | 0 | 0 |  | DRN14 | Degradation of the fuse | Pole-top fire | 20/05/2020 19:52 | 1 | Negligible: no ground fire | 15674 |  |  | 20200601SPN_03 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19939 | 0.0015127 | 6.6kV AC | Moorabbin Airport | 3754 | Doreen | Fuse
The attending Jemena Fault Crew repaired broken neutral connection at the pole junction box of the two wire aluminum overhead service cable. Subsequent voltage tests between an independent earth and various parts of the electrical installation, including the MEN at the Main Switchboard, metallic water pipe system, distribution assets and between the points of contact confirmed 1 volt following repair of the broken neutral conductor. A final NST test was carried out on the installation by the attending LEI which also confirmed a Pass result. The Installation was left ON supply. | 189 BELL STREET, COBURG VIC 3058 | A048209 |  |  |  | Neutral fault |  |  | 2 | REC reported that customer (Monique Martin) received an electric shock when she was in the bathroom showering as she made simultaneous contact with her hand on the shower tap and her bare feet whilst standing on the wet shower base. Voltage tests between an independent earth and various parts of the electrical installation, including the distribution assets, identified a broken neutral connection at the pole junction box of the two wire aluminium overhead service cable. This condition caused current to flow through the installation MEN connection, main earthing conductor, water pipe earth bond conductor and the metallic water pipes. This increased impedance to the flow of the installation return current through the general mass of earth and the metallic water pipe system was sufficient to cause a voltage rise of up to 50 volts on the water piping system and between the points of contact. | Connection box | 0 | 0 | 0 |  | CS2 | Broken neutral in pole box | Minor shock | 43867.375 |  |  | 15680 | Residential |  | 20200602JEM_01 | Infrastructure (network-based) | -37.7406 | 144.9577 | 1 | Jemena | Report | 19881 | 0.0014641 | Low voltage AC (<1kV) | Essendon Airport | 3058 | Coburg | Connection
Jemenaâ€™s Senior Customer Care Consultant spoke with the driver to confirm his health and wellbeing. With this confirmed the consultant furnished the driver with information to prepare and submit a claim. | SHARPS ROAD EAST OF BANKSIA GROVE, TULLAMARINE VIC 3043 | A046346 | Vehicle | [5 empty] | 2 | A driver passing steel public lighting pole A046346 on the morning of Friday 1 May 2020 alleges the pole failed and struck his car enroute to work. There is no evidence presented to Jemena or observed for this investigation supported this claim. Before emergency services arrived on site a photo (presumably taken by the claimant) taken at 7:49am shows the pole laying completely in the median strip with the outreach brackets extending perpendicularly into the east and west bound lanes. The lantern for the west bound lanes was missing while the lantern for the east bound lanes was missing the lens but otherwise intact, refer to Photo 1. Information provided by the driver and witness is evidence that conflicts with the known pole failure causes and assessment of the assets at the Tullamarine depot where it was returned and quarantined by field crews after the incident; these are conflicting sets of evidence. This investigation found that the pole was assisted to fall, i.e. from a vehicle impact and not from an unassisted asset failure as alleged, the pole reacted as designed after impact by a vehicle. In the process of the pole falling the vehicle drove into the falling outreach bracket attached at the top of the pole, resulting in damage to the vehicleâ€™s windshield and A-pillar. | Pole (steel) | 0 | 0 | 0 |  | AW09 | The most common cause of this type of accident is a vehicle losing control and striking a pole in wet windy weather conditions which were present at and immediately before the event. It is not in scope for this investigation to determine why the driver lost control of the vehicle and struck the pole. | Damage to network assets | 43835.3257 |  |  | 15682 | Roadway |  | 20200603JEM_02 | Infrastructure (network-based) | -37.7085 | 144.884 | 1 | Jemena | Report | 19884 | 0.041359 | Low voltage AC (<1kV) | Essendon Airport | 3043 | Tullamarine | Vehicle
Defect issued, isolated at pit | 24 JANSON STREET, MAIDSTONE VIC 3012 | A032310 | Working too close to underground cables | [5 empty] | 2 | Third party excavator has hit underground customer cable from pip to meter enclosure. Also damaged enclosure. Details of third party or photos are unavailable. | Services cable | 0 | 0 | 0 |  | BY15 | No Go Zone breach | No Go Zone (no contact);Less than $50k damage | 43896.5958 |  |  | 15684 | Construction |  | 20200603JEM_04 | Infrastructure (customer connection) | -37.7848 | 144.8686 | 1 | Jemena | Report | 19888 | 0.027672 | Low voltage AC (<1kV) | Essendon Airport | 3012 | Maidstone | Dug up
Sent crew to make safe and repair crossarm and conductors | THE BEECHWORTH HOSPITAL, 5 WARNER ROAD, BEECHWORTH VIC 3747 | 4502523 | Working too close to overhead lines | [5 empty] | 1 | Treecutter inadvertently caused branch to make contact with LV conductors. Results was LV conductors were brought down 2 foot from the ground and a broken LV xarm. Isolated and made safe. Fuses operated and overhead cables were deenergised at time of the incident | Conductor (bare);Crossarm (wood) | 0 | 0 | 0 |  | MYT12 | Vegetation: Trees Incident | Loss of supply;No Go Zone (no contact) | 30/05/2020 14:20 |  |  | 15686 | Residential |  | 20200604SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19922 | 0.034584 | Low voltage AC (<1kV) | Moorabbin Airport | 3747 | Beechworth | Other
Underground crew to replace and/or repair damaged earths as required LV/HV wooden pole and pole-mounted substation have been removed on 7/08/19 | 117-121 BONDS LANE, GREENVALE VIC 3059 | A054312 | Working too close to underground cables | [5 empty] | 2 | Unknown third-party excavator has dug up and damaged HV and LV earths at Bonds-Somerton pole mounted substation. Details of the third party are not available | Earth/earthing | 0 | 0 | 0 |  | COO11 | No Go Zone breach | No Go Zone (contact) | 21/02/2019 18:43 |  |  | 15699 | Peri-urban |  | 20200605JEM_01 | Infrastructure (network-based) | -37.6364 | 144.8756 | 1 | Jemena | Report | 19916 | 0.028226 | Earthing cable | Melbourne Airport | 3059 | Greenvale
The downed wire was in the construction site and was barricaded The service wire was put back up | 27 LYONS STREET, WILLIAMSTOWN VIC 3016 | A041683 | Working too close to overhead lines | [5 empty] | 2 | Third party construction workers have clipped an overhead service line with an excavator Service was to street light in park Details of third party are unavailable | Copper;Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | NT11 | No Go Zone breach | No Go Zone (contact) | 26/07/2019 8:53 |  |  | 15702 | Public space |  | 20200605JEM_02 | Infrastructure (network-based) | -37.8596 | 144.896 | 1 | Jemena | Report | 19912 | 0.0058831 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown
â€¢ Faults crew dispatched to disconnect the service line. Defect # 00951. â€¢ Covers installed and site made safe â€¢ The REC was satisfied that the scaffold NGZ breach had been rectified, service re-sagged and supply was restored to the customer at 18:45 12/09/19. â€¢ PTW issued 12/09/20 #J037261. | 87 RAILWAY PLACE, WILLIAMSTOWN VIC 3016 | A0145886 | Building too close or within the No Go Zone | [5 empty] | 2 | â€¢ Zinfra Lineworker reported No Go Zone breach involving scaffolding and the overhead service line. â€¢ No PTW on record and request not received. â€¢ Site inspection took place 26/07/2019. | Copper;Neutral screen;Service cable (insulated) | 0 | 0 | 0 |  | NT15 | No Go Zone breach | No Go Zone (contact) | 43808.4771 |  |  | 15703 | Residential |  | 20200605JEM_03 | Infrastructure (network-based) | -37.8612 | 144.8918 | 1 | Jemena | Report | 19913 | 0.025929 | Low voltage AC (<1kV) | Essendon Airport | 3016 | Williamstown
Sent crew to investigate and repair | 100 SCOTT AND FAHEYS ROAD, KORUMBURRA VIC 3950 | 2006290 |  |  |  | Candled fuse |  |  | 1 | Candelled Fuse on pole 2006290 | Boric acid | 0 | 0 | 0 |  | LGA12 | Crew arrived onsite and found blown 6 K BA fuse at Scott ESTATE Pole 1 LIS no 2006290 - fuse had candle showing burn marks crew advised CEOT of findings Crew inspected the sight no fire on the ground and no cause found | Pole-top fire | 43957.534 | 0 | Negligible: no ground fire | 15698 |  |  | 20200605SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Report | 19908 | 0.026436 | 22kV AC | Moorabbin Airport | 3950 | Korumburra | Fuse
Electrical inspector tested gas meter stand pipe alive at 240V. Sent truck to isolate the circuit and sent U/G crew to investigate | 116 KELBERG ROAD, KALKALLO VIC 3064 | 2601732211 |  |  |  | Unknown technical factor |  |  | 2 | Potential to electrocute, 240V, gas meter stand pipe, alive, | Services pit (network) | 0 | 0 | 0 |  | KLO14 | Under investigation | Potential to Electrocute;Other | 44018.9785 |  |  | 15704 | Residential |  | 20200609SPN_01 | Infrastructure (network-based) | -37.5341 | 144.9657 | 1 | AusNet Services Distribution | Notification | 19914 | 0.0020301 | Low voltage AC (<1kV) | Wallan (Kilmore Gap) | 3064 | Kalkallo | AF Other
Crew attended site on 5 May 2020 to rehang meter Defect J08809 placed on house as of 5 May 2020 Jemena has contacted DHHS to locate a care worker for the customer Called REC to provide a copy of the defect notice Left a voicemail on customer's answering machine to advise that when the REC has finished working on the house and she was ready to get the electricity connected, to call Jemena Faults number on 131626 | 9 BELLBRAE COURT, MEADOW HEIGHTS VIC 3048 | A060714 | Unauthorised access | [5 empty] | 2 | Customer (Barbara Hernandez 0426883504) has pulled the meter and switchboard from the wall. Customer is possibly unwell mentally and has made comments on Jemena social media page. NMI â€“ 6001015498 REC (Jarrod Harbison 0417 039 634) called Jemena and said the following: â€¢ He is a REC for the Department of Health and Human Services (DHHS) â€¢ Customer is in their late 40â€™s â€¢ Customer has done this 3 times previously, which is incredibly dangerous â€¢ She has cut up her switchboard with plyers â€¢ Very determine not to have electricity â€¢ The water has been turn off â€¢ The gas was disassembled last week and is now back working â€¢ REC thinks we should call DHHS - DHHS Broadmeadows Housing Office 3909 1255 to locate a carer â€¢ REC has also done this to reach out to a carer â€¢ REC says it would be safer is she didnâ€™t have electricity. | Smart meter;Switchboard | 0 | 0 | 0 |  | COO13 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 43956.6361 |  |  | 15724 | Residential |  | 20200611JEM_01 | Infrastructure (network-based) | -37.6571 | 144.917 | 1 | Jemena | Report | 19945 | 0.020221 | Low voltage AC (<1kV) | Essendon Airport | 3048 | Meadow Heights | Other
Customer was issued a defect notice and the attending truck crew removed the overhead service line. REC to rectify defect and provide a certificate of electrical safety before Jemena reconnecting supply. | 151 SOUTHERN ROAD, HEIDELBERG WEST VIC 3081 | A107760 | Unauthorised access | [5 empty] | 2 | Licensed Electrical Inspector attended site to investigate an illegal wiring which had been reported by an attending truck crew. Upon inspection it was found that illegal wiring had been connected before the meter to the line side of the of the customer's FOLCB. The tails had been cut and left live inside the roof at the time of attendance with no load connected to them. No other illegal wiring was evident. Illegal wiring has most likely been present in the past to this property and has now been disconnected. Current residents of the property are students who have been renting there for the past 3 months. | Customer wiring | 0 | 0 | 0 |  | EPN33 | Unauthorised access | Serious risk to public safety (e.g. live conductor on ground or live asset accessible to unauthorised persons) | 29/05/2020 10:00 |  |  | 15725 | Residential |  | 20200611JEM_02 | Infrastructure (network-based) | -37.7418 | 145.0425 | 1 | Jemena | Report | 19946 | 0.03605 | Low voltage AC (<1kV) | Essendon Airport | 3081 | Heidelberg West | Other
Despatched crew to investigate and repair | 33 RAGLAN STREET, WALLAN VIC 3756 | 912897 |  |  |  | Electrical breakdown |  |  |  | Received call from Fire Brigade for house fire. Crew sent to investigate. Found service burnt out mid span. | Service cable (insulated) | 0 | 0 | 0 |  | KLO24 | Under investigation | Pole-top fire | 44141.3125 | 0 | Negligible: no ground fire | 15722 | Residential |  | 20200611SPN_04 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19941 | 0.018875 | Low voltage AC (<1kV) | Moorabbin Airport | 3756 | Wallan | OH Cable
Despatched crew and inspector to investigate and repair | 115 WILLIAMS ROAD, WOODLEIGH VIC 3945 | 2000461 |  |  |  | Defective component |  |  | 1 | HV dropper has come away from the HV fuse unit and come in contact with the TX neutral. | Pole mounted | 0 | 0 | 0 |  | LLG12 | Under investigation | HV injection | 44141.5896 |  |  | 15723 | Agricultural |  | 20200611SPN_05 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19943 | 0.0027292 | 12.7kV AC (SWER) | Moorabbin Airport | 3945 | Woodleigh | AF Other
Crew attended site and made safe and replaced a fire damaged 3 phase 100A FOLCB at the pole. | 42 CENTRAL AVENUE, BLAIRGOWRIE VIC 3942 | 1304267 |  |  |  | Overheated connection |  |  | 2 | A resident at number 45 Central Ave Blairgowrie advised she saw something on the pole on fire. On arrival the crew identified a fire damaged FOLCB outside # 42 Central Ave | Connection box | 0 | 0 | 0 |  | STO21 | The crew believe the cause was a loose connection within the FOLCB | Plant/equipment | 43988.7667 | 1 | Negligible: no ground fire | 15717 | Residential |  | 20200611UTD_01 | Infrastructure (network-based) | -38.3657 | 144.7593 | 1 | United Energy Distribution | Report | 19932 | 0.00053356 | Low voltage AC (<1kV) | Avalon Airport | 3942 | Blairgowrie | Connection
The crew replaced a 3 phase FOLCB on the pole | 301 ST KILDA STREET, BRIGHTON VIC 3186 | 1806162 |  |  |  | Earth fault |  |  | 2 | A report came in to UE of a FMB sparking at 310 St Kilda St, Brighton. On arrival the crew identified a fire damaged FOLCB on pole LIS 1806162. An EIO was called to assess the cause. | Connection box | 0 | 0 | 0 |  | NB33 | The likely cause was determined by EIO to be a earthing defect within the customers installation The EIO issued a defect for #301 St Kilda St | Plant/equipment | 44080.7771 | 1 | Negligible: no ground fire | 15718 | Residential |  | 20200611UTD_02 | Infrastructure (network-based) | -37.9053 | 144.9881 | 1 | United Energy Distribution | Report | 19935 | 0.013824 | Low voltage AC (<1kV) | Moorabbin Airport | 3186 | Brighton | Connection
Conductor repaired at point of contact. | 48 Banks Rd, Mount Wallace VIC 3342, Australia | 30555208 | Working too close to overhead lines | [6 empty] | Report received from a resident to advise that a crane had made contact with a powerline and that power was out. Wire appears fine and crane no longer in contact. Upon arrival the fault crew found that the crane driver from Metcalf Crane Services had made contact with the 3/12St SWER overhead conductor between LIS-875955 and LIS-104756 while moving gantry equipment associated with the Moorabool windfarm project. The crane was taken away from site for testing. There was no fire and no reported injuries. | Conductor (bare) | 2 | 2 | 2 |  | BMH003 | Crane struck line | No Go Zone (contact);Damage to network assets | 44171.5847 |  |  | 15744 | Agricultural |  | 20200615PWA_01 | Infrastructure (network-based) | -37.7077 | 144.1999 | 1 | Powercor | Report | 19968 | 0.015201 | 12.7kV AC (SWER) | Avalon Airport | 3342 | Mount Wallace | Vehicle
On arrival crew isolated supply and arranged pole replacement. | 196 VALLANCE ROAD, OUYEN VIC 3490 | 32151770 |  |  |  | Leakage |  |  |  | Report received of pole fire at incident location. On arrival crew found top burnt off SWER pole. Fire extinguished There was no ground fire, no reported injuries or third party property damage. | Pole (wood) | 2 | 2 | 2 |  | OYN003 | Excessive leakage current | Pole-top fire | 14/06/2020 15:32 | 1 | Negligible: no ground fire | 15748 | Agricultural |  | 20200616PWA_01 | Infrastructure (network-based) | -34.9788 | 142.3654 | 1 | Powercor | Report | 19972 | 0.027285 | 22kV AC | Mildura Airport | 3490 | Ouyen | Pole
On arrival crew isolated supply and carried out repairs | Ford Rd, Ultima VIC 3544, Australia | 32158284 | Crane, excavator or other construction/farming equipment | [6 empty] | A customer called to report a tractor had hit a wire and brought it down to the ground. On arrival at the incident location, the crew found that the tractor rego: XV-99CE had been towing large rollers around the paddock and turned sharply, contacting the pole with the rollers and causing it to break off and fall over. The 22kV HV single phase conductors fell onto the tractor, causing the protection to operate, isolating the supply. The tractor driver exited the vehicle before the crew arrived, and reportedly received no shocks and was not injured. There was no other reported damage, fires or injuries. | Conductor (bare);Pole (wood) | 2 | 2 | 2 |  | SHL001 | Farm equipment hit pole | Damage to network assets | 15/06/2020 12:17 |  |  | 15749 | Agricultural |  | 20200616PWA_02 | Infrastructure (network-based) | -35.4781 | 143.2285 | 1 | Powercor | Report | 19973 | 0.0015405 | 22kV AC | Swan Hill Aerodrome | 3544 | Ultima | Vehicle
Despatched crew and inspector to investigate and repair | 5 DANE PLACE, WODONGA VIC 3690 | 5202302 | [6 empty] | 2 | concrete electrical cover outside of front of house gave clients dog an electric shock during rain | Services pit (network) | 0 | 0 | 0 |  | WOTS12 | Under Investigation | Shock to livestock, pet or companion animal | 15/06/2020 17:10 |  |  | 15750 | Residential |  | 20200617SPN_01 | Infrastructure (network-based) | -38.1178 | 144.9177 | 1 | AusNet Services Distribution | Notification | 19976 | 0.005397 | Low voltage AC (<1kV) | Moorabbin Airport | 3690 | Wodonga | AF Other